## Sheet1
No. | Outage | Outage Month | Outage Hour | Outage Timing | Outage Day | Outage Days | Outage Date | Year | Re/Patrol | Feeder / Unit | Area | Ops Area | Weather | Cause | Loss | R E M A R K | OutageCount
1 | 2020-01-10 07:25 | January | 7:25 | Morning | Friday | Weekdays | 10 | 2020 | 2020-01-10 07:25 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 07:25 MGT#5 trip, by alarm Bus Under voltage. 08:10 S/U MGT#5, then On Line the unit at 08:17. | 1
2 | 2020-01-10 07:25 | January | 7:25 | Morning | Friday | Weekdays | 10 | 2020 | 2020-01-10 07:25 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Lightning | Animal | 75 | 07:25 Minas ACB fdr#6 T/LO Ctr:207-209 R/F:51@2@3. 08:55 Patrolled the line & found Dead Squirrel on TOP Well 7E-56. 09:30 Blocked & Closed Minas ACB fdr#6, then release trhe block. Cause: Animal (Squirrel). | 1
3 | 2020-01-10 13:30 | January | 13:30 | Afternoon | Friday | Weekdays | 10 | 2020 | 2020-01-10 13:30 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Rain | Unidentified | - | 4D fdr#3 T/R 1x Ctr:307-308 R/F:51@2@3. Not checked yet. | 1
| 2020-01-10 13:30 | January | 13:30 | Afternoon | Friday | Weekdays | 10 | 2020 | 2020-05-10 17:03 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Rain | Unidentified | - | Checked And Found 4DSB OCB3 Fdr #8 Ctr 307-308, R/F 51 Patrolled The Line On 02-Oct-2020 But Found Nothing On Phase @2,3, Cause: Unidentified | 1
4 | 2020-01-10 14:00 | January | 14:00 | Afternoon | Friday | Weekdays | 10 | 2020 | 2020-01-10 14:00 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Rain and Lightning | Lightning Arrester | - | Duri Community ACB fdr#3 T/R 1x. Not checked yet. | 1
| 2020-01-10 14:00 | January | 14:00 | Afternoon | Friday | Weekdays | 10 | 2020 | 2020-05-10 08:00 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Rain and Lightning | Lightning Arrester | - | Checked & found Duri Community fdr#3 T/R 1x Ctr:114-115 R/F:51@1@2@3. Patrolled the line & found @1@2@3 Broken LA o/p 2R4. Cause : Lightning Arrester. | 1
5 | 2020-01-10 15:44 | January | 15:44 | Afternoon | Friday | Weekdays | 10 | 2020 | 2020-01-10 15:44 | 13.8KV DARLING VCB FEEDER #4 | Duri | PGT North | Rain and Lightning | Circuit Breaker | 7 | 15:44 Darling VCB fdr#4 T/LO Ctr:151-154 R/F:51@1@2@3. 16:50 Patrolled the line & found Broken Jumper LA o/p 05-M5-14. 17:09 Blocked & closed Darling VCB fdr#4, but failure. Checked & found Broken 4160V MCC at CSS#6, then isolated. Open Recloser of 6500KVA TX and checked the TX, OK. 18:40 Blocked & closed Darling VCB fdr#4, then release the block. Cause: Broken MCC. | 1
6 | 2020-02-10 08:41 | February | 8:41 | Morning | Monday | Weekdays | 10 | 2020 | 2020-02-10 08:41 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 22 | Ketigul fdr#1 T/R 1x. Not checked yet. | 1
| 2020-02-10 08:41 | February | 8:41 | Morning | Monday | Weekdays | 10 | 2020 | 2020-05-10 15:16 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 22 | Checked And Found PKTGL VCB1 Fdr #8 Ctr 243-244, R/F 51 Patrolled The Line On 05-Oct-2020 And Found Broken Dead End On Phase @1,2, Pole N/A Tilan #03 Cause: Dead End Insulator | 1
7 | 2020-02-10 10:40 | February | 10:40 | Morning | Monday | Weekdays | 10 | 2020 | 2020-02-10 10:40 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | S/U CGT#5, then on line the unit at 11:06. | 1
8 | 2020-02-10 20:38 | February | 20:38 | Night | Monday | Weekdays | 10 | 2020 | 2020-02-10 20:38 | 4.16KV NO RUMBAI FEEDER #2 | Rumbai | PGT South | Lightning | Dead End Insulator | - | N.Rumbai 4.16Kv VCB #2 T/R 1x. Not checked yet. | 1
| 2020-02-10 20:38 | February | 20:38 | Night | Monday | Weekdays | 10 | 2020 | 2020-05-10 08:38 | 4.16KV NO RUMBAI FEEDER #2 | Rumbai | PGT South | Lightning | Dead End Insulator | - | Checked & found N.Rumbai fdr#2 T/R 1x Ctr:367-368 R/F:51N. Patrolled the line & found Broken Dead End Insulator o/p 2RD-10. Cause : Dead End Insulator. | 1
9 | 2020-02-10 21:52 | February | 21:52 | Night | Monday | Weekdays | 10 | 2020 | 2020-02-10 21:52 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Rain and Lightning | Pin Insulator | - | Duri commy 13.8Kv ACB #26 fdr #3 T/R 1x. Not checked yet. | 1
| 2020-02-10 21:52 | February | 21:52 | Night | Monday | Weekdays | 10 | 2020 | 2020-06-10 23:36 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Rain and Lightning | Pin Insulator | - | Checked and found DCM ACB fdr #3 T/ R 1x, ctr: 115 - 116, R/F: 51N Patrolled the line and found broken pin insulator @1 o/p 3-DD-17 Cause : Pin Insulator | 1
10 | 2020-03-10 02:17 | March | 2:17 | Night | Tuesday | Weekdays | 10 | 2020 | 2020-03-10 02:17 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Lightning | Lightning Arrester | - | N.Duri 13.8Kv VCB #1 T/R 1x. Not checked yet. | 1
| 2020-03-10 02:17 | March | 2:17 | Night | Tuesday | Weekdays | 10 | 2020 | 2020-06-10 23:36 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Lightning | Lightning Arrester | - | Checked and found ND VCB fdr #1 T/R 1x, ctr: 349 - 350, R/F: 51N Patrolled the line and found broken LA @2 o/p NC-03 Cause : Lightning Arrester | 1
11 | 2020-03-10 05:40 | March | 5:40 | Morning | Tuesday | Weekdays | 10 | 2020 | 2020-03-10 05:40 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Rain and Lightning | Unidentified | 298 | 05:40 Liabo fdr#2 Load dropped 34A (56-22A). 12:40 It was reported no power at Hitan field. Checked & found Recl. 23BW02 T/SO Ctr: Blank. Patrolled the line but not founding. 14:40 Blocked & closed Recl. 23BW02, then release the block. Cause: Unidentified. | 1
12 | 2020-03-10 05:45 | March | 5:45 | Morning | Tuesday | Weekdays | 10 | 2020 | 2020-03-10 05:45 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Cloudy | Capasitor Bank - Fuse holder of Cap Bank. | - | C.Duri feeder # 6 T/R 3X R/F 51G 50 @2,3 ctr:524-527 Not checked yet. | 1
| 2020-03-10 05:45 | March | 5:45 | Morning | Tuesday | Weekdays | 10 | 2020 | 2020-06-10 07:17 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Cloudy | Capasitor Bank - Fuse holder of Cap Bank. | - | Checked and found: CDRSG-13.8ACB23 T/R, Counter : 524 - 527, Relay Flag : 51 Patrolled the line found : Temuan broken capacitor bank and holder Cause : Capasitor Bank | 1
13 | 2020-03-10 06:41 | March | 6:41 | Morning | Tuesday | Weekdays | 10 | 2020 | 2020-03-10 06:41 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Cloudy | Lightning | - | NKB Feeder # 1 T/R 1X and GFPC Not Checked yet. | 1
| 2020-03-10 06:41 | March | 6:41 | Morning | Tuesday | Weekdays | 10 | 2020 | 2020-05-10 08:41 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Cloudy | Lightning | - | Checked & found NKBS fdr#1 T/R 1x Ctr:297-298 R/F:50N,51@3. Patrolled the line & found Broken LA on TOP KB#173. Cause : Lightning. | 1
14 | 2020-03-10 08:24 | March | 8:24 | Morning | Tuesday | Weekdays | 10 | 2020 | 2020-03-10 08:24 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | - | 08:24 Sintong VCB fdr#1 Load dropped 50A (95-45). 09:50 Checked & found Recl. 25AD26 T/R 1x Ctr:1009-1010. Patrolled the line but found nothing. Cause: Unidentified. | 1
15 | 2020-03-10 09:09 | March | 9:09 | Morning | Tuesday | Weekdays | 10 | 2020 | 2020-03-10 09:09 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Cloudy | Unidentified | 6 | 09:09 It was reported No power at 07-U1-19 (D.Field fdr#2). 10:05 Checked & found Recl. 07-U1-19 T/SO Ctr:84-85, Patrolled the line but found nothing. Cause: Unidentified. | 1
16 | 2020-04-10 22:38 | April | 22:38 | Night | Friday | Weekdays | 10 | 2020 | 2020-04-10 22:38 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Fair | Recloser - Control Recloser | 48 | 22:38 Libo Feeder #2 Load drop 38A (56-18A) 00:16 it was reported no power at Hitam Area 01:50 Checked and found recloser 23BW02 T/SO ( control Blank ),patrol the line but found nothing. 03:00 Blocked and closed the recloser Ok Cause: Control recloser failure. | 1
17 | 2020-05-10 08:08 | May | 8:08 | Morning | Sunday | Weekends | 10 | 2020 | 2020-05-10 08:08 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 28 | 08:08 It was reported no power at 09-M3-02 (C.Duri feeder #1) 11:47 Checked & Found Recl 09-M3-01 T/O (Block position) Ctr: 127-128. Patrolled the line but found nothing. 11:55 Blocked & closed recl 09-M3-01 , then release block. Cause : Unidentified. | 1
18 | 2020-05-10 08:18 | May | 8:18 | Morning | Sunday | Weekends | 10 | 2020 | 2020-05-10 08:18 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Unidentified | - | C.Duri 13.8Kv ACB #33 fdr #7 T/R 1x. Not checked yet. | 1
| 2020-05-10 08:18 | May | 8:18 | Morning | Sunday | Weekends | 10 | 2020 | 2020-07-10 08:20 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Unidentified | - | Checked and found CD ACB-33 fdr #7 T/R 1x, ctr: 569 - 570, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
19 | 2020-05-10 08:58 | May | 8:58 | Morning | Sunday | Weekends | 10 | 2020 | 2020-05-10 08:58 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Fair | Unidentified | 34 | Minas 13.8Kv ACB #1 fdr#4 T/R 1x. Not checked yet. | 1
| 2020-05-10 08:58 | May | 8:58 | Morning | Sunday | Weekends | 10 | 2020 | 2020-07-10 14:46 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Fair | Unidentified | 34 | Checked and found: MNSSG-13.8ACB01 T/R, Counter : 132 - 133, Relay Flag : 51N Finding Patrolled the line found : Not Found Cause : Unidentified | 1
20 | 2020-05-10 09:55 | May | 9:55 | Morning | Sunday | Weekends | 10 | 2020 | 2020-05-10 09:55 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 09:55 S/U CDGT #2 then online the unit at 10:24. | 1
21 | 2020-05-10 14:01 | May | 14:01 | Afternoon | Sunday | Weekends | 10 | 2020 | 2020-05-10 14:01 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 14:01 S/U CDGT #2 then online the unit at 14:24. | 1
22 | 2020-05-10 15:00 | May | 15:00 | Afternoon | Sunday | Weekends | 10 | 2020 | 2020-05-10 15:00 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 15:00 S/D Off line and S/D MGT #5. | 1
23 | 2020-06-10 15:00 | June | 15:00 | Afternoon | Wednesday | Weekdays | 10 | 2020 | 2020-06-10 15:00 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 15:00 Off line CGT #2 then S/D for maintenance. | 1
24 | 2020-06-10 18:17 | June | 18:17 | Afternoon | Wednesday | Weekdays | 10 | 2020 | 2020-06-10 18:17 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Rain and Lightning | Powerline - Jumper | - | 18:17 Duri Commy 13.8Kv ACB #30 fdr #2 T/LO. 19:00 Checked and found R/F 51 @1 & 51N Ctr:132-135 19:04 Patrol the line found broken conductor at 13.8 kV Recloser 20:04 Open LBS BKS #12 and Closed LBs # 1-BD-2 20:10 Block DCM Fdr#1 and Closed LBS SY 07 20:18 Closed LBS LKT - 24 22:24 Blocked and closed DCM Fdr#2 22:41 Closed LBS 2-F-15 22:41 Open LBS BKS-12 22:45 Closed LBS 1-DB-2 22:47 Open LBS SY-07 22:53 Closed LBS KRC-20 22:55 Open LBS LKT-24. Closed 13.8kV Recl Mini IT subs on block but failed ( Will be continued) Cause : Broken Conductor. | 1
25 | 2020-06-10 18:19 | June | 18:19 | Afternoon | Wednesday | Weekdays | 10 | 2020 | 2020-06-10 18:19 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Lightning Arrester | - | N.Duri 13.8Kv VCB#1 T/R 1x. Not checked yet. | 1
| 2020-06-10 18:19 | June | 18:19 | Afternoon | Wednesday | Weekdays | 10 | 2020 | 2020-08-10 15:19 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Lightning Arrester | - | Checked and found ND VCB fdr #1 T/R 1x, ctr: 350 - 351, R/F: 51N Patrolled the line and found broken LA @3 o/p 12-F3-23 Cause : Lightning Arrester | 1
26 | 2020-06-10 18:38 | June | 18:38 | Afternoon | Wednesday | Weekdays | 10 | 2020 | 2020-06-10 18:38 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Rain and Lightning | Tree | - | C.Duri feeder #14 load dropped 89A (152-63A). Not checked yet. | 1
| 2020-06-10 18:38 | June | 18:38 | Afternoon | Wednesday | Weekdays | 10 | 2020 | 2020-08-10 08:38 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Rain and Lightning | Tree | - | Checked and found RCL 06-P8-02 T/R 1x, Counter: 301 - 302, R/F: None Patrolled the line and found fallen tree that had touch the power line o/p 05-P1-01 Cause : Tree | 1
| 2020-06-10 18:38 | June | 18:38 | Afternoon | Wednesday | Weekdays | 10 | 2020 | 2020-08-10 08:38 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Rain and Lightning | Tree | - | Checked and found: RCL 06-P8-02 T/R, Counter : 301 - 302, Relay Flag : NONE Patrolled the line found : ditemukan pohon tumbang sudah jatuh ke tanah menyebabkan pin insulator miring Cause : Tree | 1
27 | 2020-07-10 09:42 | July | 9:42 | Morning | Friday | Weekdays | 10 | 2020 | 2020-07-10 09:42 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 0 | 09:42 Manual Open LBS 5C-121B, closed at 16:26 To connect jumper o/p 6D-505 Planned Maintenance | 1
28 | 2020-07-10 09:44 | July | 9:44 | Morning | Friday | Weekdays | 10 | 2020 | 2020-07-10 09:44 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Fair | Lightning | 35 | 09:44 3D VCB fdr #2 T/R 1x 3D feeder #3 dropped 25 A (73 - 48 A) 3D feeder #4 dropped 32 A (166 - 134 A) Not Checked Yet | 1
| 2020-07-10 09:44 | July | 9:44 | Morning | Friday | Weekdays | 10 | 2020 | 2020-11-10 16:10 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Fair | Lightning | 35 | Checked and found 3D OCB fdr #2 T/R 1x, Counter: 392 - 393, R/F: 51N Patrolled the line and found broken LA @1, 2, 3 o/p 3E-34 Cause : Lightning | 1
29 | 2020-07-10 10:00 | July | 10:00 | Morning | Friday | Weekdays | 10 | 2020 | 2020-07-10 10:00 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 417 | 10:00 Manual Open VCB BKO fdr #4, closed at 14:07 Maintenance jobs: - Repair Hot Spot at I/S of TX at Benar GS - Repair Hot Spot at RCL 29-Y-23B - Change Out Insulators Planned Maintenance | 1
30 | 2020-07-10 17:52 | July | 17:52 | Afternoon | Friday | Weekdays | 10 | 2020 | 2020-07-10 17:52 | 13.8KV CENTRAL DURI FEEDER #4 | Duri | PGT North | Cloudy | Pin Insulator | 48 | 17:52 CD ACB-21 feeder #4 T/LO, ctr: 534 - 538, R/F: 51P @1, 50P @2 17:55 Call TDO crew to check facilities and field d/s CD fdr #4 18:30 Patrolled the line but found nothing 18:36 Block and manual close CD fdr #4, OK, then release the block. Not Patrolled Yet | 1
| 2020-07-10 17:52 | July | 17:52 | Afternoon | Friday | Weekdays | 10 | 2020 | 2020-08-10 07:36 | 13.8KV CENTRAL DURI FEEDER #4 | Duri | PGT North | Cloudy | Pin Insulator | 48 | Patrolled the line and found broken pin insulator @3 o/p 09 R8 10 Cause: Pin Insulator | 1
31 | 2020-08-10 09:21 | August | 9:21 | Morning | Monday | Weekdays | 10 | 2020 | 2020-08-10 09:21 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Powerline - Jumper | 97 | 09:21 It was reported no power at road 08-L7-xx (pole 08-L7-37) d/s CD fdr #16 (no load dropped indication at CD fdr #16) 09:22 Call TDO crew to perform field verification 09:50 Checked and found RCL 08-L7-38 in close position and some wells d/s of RCL are ON/ACTIVE (suspect unbalance voltage) Patrolled the line but found nothing 11:50 Manual close LBS 08-L8-02 (also d/s CD fdr #16) 14:40 Re-patrolled the power line and found - broken jumper @1 on source side of RCL 09-L5-20. - b/o fuse link of PT for control of RCL 09-L5-20 15:30 MTCE team repair the broken jumper and b/o fuse PT of RCL 09-L5-20 17:10 Block and manual close RCL 09-L5-20 and then release the block. 17:18 Manual open LBS 09-L5-01. Cause: Conductor - Jumper | 1
32 | 2020-08-10 17:07 | August | 17:07 | Afternoon | Monday | Weekdays | 10 | 2020 | 2020-08-10 17:07 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Cloudy | Others | 28 | 17:07 Minas ACB fdr #3 T/LO, ctr: 189 - 191, R/F: 51P @2 @3 Minas fdr #1 dropped 54 A (168 - 114 A) Minas fdr #2 dropped 7 A (106 - 99 A) Minas fdr #1 dropped 34 A (181 - 147 A) 17:11 Call TDO Crew (Andri) 17:50 Complete to patrol the power line but found nothing, also reported some villagers just play kite near the power line of MNS fdr #3. 17:51 Block and then manual close MNS ACB fdr #3, OK then release the block Cause: Other (kite) | 1
33 | 2020-09-10 05:20 | September | 5:20 | Morning | Thursday | Weekdays | 10 | 2020 | 2020-09-10 05:20 | 13.8KV MINAS FEEDER #2 | Minas | PGT South | Fair | Unidentified | 13 | Minas 13.8Kv ACB #13 fdr #2 T/R 1x. Ctr: 97-98 R/f: 51N. Not checked yet. | 1
| 2020-09-10 05:20 | September | 5:20 | Morning | Thursday | Weekdays | 10 | 2020 | 13-10-2020 14:55 | 13.8KV MINAS FEEDER #2 | Minas | PGT South | Fair | Unidentified | 13 | Checked And Found MNSSG ACB13 Fdr #8 Ctr 97-98, R/F 51N Patrolled The Line On 12-Oct-2020 But Found Nothing Cause: Unidentified | 1
34 | 2020-09-10 10:25 | September | 10:25 | Morning | Thursday | Weekdays | 10 | 2020 | 2020-09-10 10:25 | 13.8KV 8D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 15 | 10:25 Manual Open 8D OCB fdr #2, closed at 11:06 MTCE team to repair hotspot at location 8E-54N Planned Maintenance | 1
35 | 2020-09-10 16:44 | September | 16:44 | Afternoon | Thursday | Weekdays | 10 | 2020 | 2020-09-10 16:44 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Fair | Unidentified | 23 | 16:44 Libo VCB fdr #2 T/R 1x (no indication at DSC due to RTU failed at 16:30) Libo fdr #1 load dropped 38 A (76 - 38 A), also no indication at DSC. Not Checked Yet | 1
| 2020-09-10 16:44 | September | 16:44 | Afternoon | Thursday | Weekdays | 10 | 2020 | 2020-12-10 12:47 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Fair | Unidentified | 23 | Checked And Found LBOSB OCB2 Fdr #8 Ctr 530-531, R/F 50 Patrolled The Line On 12-Oct-2020 But Found Nothing On Phase @2 Pole 23 Bw 02 Cause: Unidentified | 1
36 | 2020-10-10 09:13 | October | 9:13 | Morning | Saturday | Weekends | 10 | 2020 | 2020-10-10 09:13 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 0 | 09:13 Manual Open LBS 28-AL-21, Closed at 10:45. Purpose to replace broken pin insulator on pole 28-AK-02 and 29-AK-01. Planned Maintenance. | 1
37 | 2020-10-10 10:53 | October | 10:53 | Morning | Saturday | Weekends | 10 | 2020 | 2020-10-10 10:53 | CENTRAL DURI POWER PLANT | Duri | PGT North | Fair |  | - | 10:53 CDGT #2 S/U and then Online at 11:12 Running test to base load after M/O 17:30 HRSG CDGT #2 activated | 1
38 | 2020-10-10 13:06 | October | 13:06 | Afternoon | Saturday | Weekends | 10 | 2020 | 2020-10-10 13:06 | 4.16KV NO RUMBAI FEEDER #2 | Rumbai | PGT South | Fair | Planned Maintenance | 0 | 13:06 Manual Open VCB North Rumbai fdr #2, closed at 14:59 MTCE team to cut high trees and replace insulator o/p 2RD-10, 2RA-3 Planned Maintenance | 1
39 | 2020-10-10 14:30 | October | 14:30 | Afternoon | Saturday | Weekends | 10 | 2020 | 2020-10-10 14:30 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:30 CDGT #4 Offline and then Shut Down at 14:39 for standby | 1
40 | 2020-10-10 18:18 | October | 18:18 | Afternoon | Saturday | Weekends | 10 | 2020 | 2020-10-10 18:18 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 9 | ROKAN VCB fdr #2 T/R 1x Not Checked Yet | 1
| 2020-10-10 18:18 | October | 18:18 | Afternoon | Saturday | Weekends | 10 | 2020 | 2020-11-10 13:30 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 9 | Checked and found RKN VCB fdr #2 T/R 1c, counter: 1350 - 1351, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
41 | 2020-11-10 19:45 | November | 19:45 | Night | Tuesday | Weekdays | 10 | 2020 | 2020-11-10 19:45 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Lightning | Lightning | 70 | Minas 13.8Kv ACB #1 fdr #4 T/R 1x. Not checked yet. | 1
| 2020-11-10 19:45 | November | 19:45 | Night | Tuesday | Weekdays | 10 | 2020 | 13-10-2020 14:55 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Lightning | Lightning | 70 | Checked And Found MNSSG ACB01 Fdr #8 Ctr 97-98, R/F 51N Patrolled The Line On 12-Oct-2020 And Found Broken Dead End @2 On Pole 7D-105 Near Gang Saiyo Ujung On Phase @2 Pole 7D-105 Cause: Lightning | 1
42 | 2020-12-10 08:24 | December | 8:24 | Morning | Thursday | Weekdays | 10 | 2020 | 2020-12-10 08:24 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Broken Fuse Cut Out | 0 | South Balam fdr #1 load dropped 95 A (152 - 57 A) Not Checked Yet | 1
43 | 2020-10-13 10:10 | October | 10:10 | Morning | Tuesday | Weekdays | 13 | 2020 | 13-10-2020 10:10 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 36 | 10:10 Manual Open LBS 6C-21A, closed at 11:39 10:19 Manual Open LBS 5C-121B, closed at 11:32 MTCE team to repair LBS o/p 5C-59 Planned Maintenance | 1
44 | 2020-10-10 12:25 | October | 12:25 | Afternoon | Saturday | Weekends | 10 | 2020 | 13-10-2020 12:25 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Cloudy | Unidentified | 10 | NKBS VCB feeder #1 T/R 1x NKBS GFPC Recloser T/R 1x Not Checked Yet | 1
| 2020-10-13 12:25 | October | 12:25 | Afternoon | Tuesday | Weekdays | 13 | 2020 | 14/10/2020 11:09 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Cloudy | Unidentified | 10 | Checked And Found NKBKSB OCB1 Fdr #8 Ctr 298/299, R/F 50N Patrolled The Line On 14/Oct/2020 But Found Nothing Cause: Unidentified | 1
45 | 2020-10-13 14:32 | October | 14:32 | Afternoon | Tuesday | Weekdays | 13 | 2020 | 13/10/2020 14:32 | 13.8KV NORTH DURI FEEDER #11 | Duri | PGT North | Fair | Unidentified | 78 | 14:32 It was reported no power along road 13/F10/xx 14:35 Call TDO crew to check the problem at location 15:00 Checked and found RCL 13/F3/49 T/O (on block), ctr: 100, R/F: 51P @3 Continue to patrol the line but found nothing. 16:07 Manual close RCL 13/F3/49 and then release the block. Unidentified | 1
46 | 2020-10-14 07:59 | October | 7:59 | Morning | Wednesday | Weekdays | 14 | 2020 | 14/10/2020 07:59 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Fair | Animal | 0 | Bangko GFPC T/R 1X Bangko Feeder # 4 Load drop 92A ( 189/97A ) Not Checked yet. | 1
| 2020-10-14 07:59 | October | 7:59 | Morning | Wednesday | Weekdays | 14 | 2020 | 16/10/2020 10:12 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Fair | Animal | 0 | Checked And Found / RCL 25/Z/01 T/R 1x, Ctr 146/147, R/F: 51N / 13.8KVBKO_GFPC Fdr #4 Ctr 257/258, R/F 51N Patrolled the Line On 15/Oct/2020 and found died animal (Eagle) at BKO #267 On Phase @2,3 (flash over bushing), Pole 23 Y 12 Cause: Animal | 1
47 | 2020-10-14 15:26 | October | 15:26 | Afternoon | Wednesday | Weekdays | 14 | 2020 | 14/10/2020 15:26 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Tree | 0 | Sintong Feeder #2 load drop 165A ( 252/87A ) Not Checked yet. | 1
| 2020-10-14 15:26 | October | 15:26 | Afternoon | Wednesday | Weekdays | 14 | 2020 | 16/10/2020 10:26 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Tree | 0 | Checked And Found: / RCL 28/AF/02 T/R 1x, Ctr 1568/1569, R/F: None / GFPC RCL T/R 2x, Ctr 1236/1238, R/F 51N Patrolled The Line On 15/Oct/2020 And Found Suspected High Tree (Laban) On Pole 29/Al/08 Cause: Tree | 1
48 | 2020-10-14 18:28 | October | 18:28 | Afternoon | Wednesday | Weekdays | 14 | 2020 | 14/10/2020 18:28 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 23 | Pinang Feeder #1 T/R 1X Not Checked yet. | 1
| 2020-10-14 18:28 | October | 18:28 | Afternoon | Wednesday | Weekdays | 14 | 2020 | 20/10/2020 07:38 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 23 | Checked And Found PNGSB OCB1 Fdr #8 Ctr 473/474, R/F 51N Patrolled The Line On 16/Oct/2020 And Found Dead End Flashover On Phase @3 Pole 13 H 07 Cause: Unidentified | 1
49 | 2020-10-15 10:31 | October | 10:31 | Morning | Thursday | Weekdays | 15 | 2020 | 15/10/2020 10:31 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Fair | Unidentified | 16 | 10:31 4D fdr #3 T/LO. 11:00 Checked & found 4D feeder #3 T/LO. 12:03 Patrolled the line but found nothing. 12:08 Blocked & closed ///>Ok. Cause: unidentified 4D feeder #1 load dropped 135A (263/128A). 4D feeder #2 load dropped 67A (113/46A). | 1
| 2020-10-15 10:31 | October | 10:31 | Morning | Thursday | Weekdays | 15 | 2020 | 2020-10-19 09:21 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Fair | Unidentified | 16 | Checked And Found 4DSB OCB3 Fdr #8 Ctr 308/312, R/F 51 Patrolled The Line On 16/Oct/2020 But Found Nothing On Phase @2,3, Cause: Unidentified | 1
50 | 2020-10-15 14:01 | October | 14:01 | Afternoon | Thursday | Weekdays | 15 | 2020 | 15/10/2020 14:01 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 221 | 14:01 Menggala feeder #1 load dropped 125A (199/74A) Menggala GFPC T/R 1x. 16:05 Checked & found / Recloser 19/AN/04 T/O (On blocked). Ctr : 828 / 829, R/F: 51N / Patrolled the line & found died animal (animal) at Meno #11 / Burned out fuse link @2,@3 for 300 kVA Tx at Meno #11. Cause : Animal (chicken) | 1
51 | 2020-10-15 13:22 | October | 13:22 | Afternoon | Thursday | Weekdays | 15 | 2020 | 16/10/2020 13:22 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 9 | Rokan 13.8Kv VCB fdr #2 T/R 1x. Not checked yet. | 1
| 2020-10-16 13:22 | October | 13:22 | Afternoon | Friday | Weekdays | 16 | 2020 | 2020-10-19 07:15 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 9 | Checked And Found RKNSB VCB2 Fdr #8 Ctr 1351/1352, R/F 51N Patrolled The Line On 18/Oct/2020 And Found Insulator Pecah On Phase @2 Pole 28 A 13 C Cause: Dead End Insulator | 1
52 | 2020-10-16 17:05 | October | 17:05 | Afternoon | Friday | Weekdays | 16 | 2020 | 16/10/2020 17:05 | MINAS POWER PLANT | Minas | PGT South | Fair |  | - | 17:05 S/U MGT #5 17:22 O/L. | 1
53 | 2020-10-16 17:26 | October | 17:26 | Afternoon | Friday | Weekdays | 16 | 2020 | 16/10/2020 17:26 | MINAS POWER PLANT | Minas | PGT South | Fair |  | - | 17:26 S/D MGT # 4 | 1
54 | 2020-10-16 17:43 | October | 17:43 | Afternoon | Friday | Weekdays | 16 | 2020 | 16/10/2020 17:43 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Cloudy | Unidentified | 20 | Libo 13.8Kv OCB fdr #1 T/R 1x. Not checked yet. | 1
| 2020-10-16 17:43 | October | 17:43 | Afternoon | Friday | Weekdays | 16 | 2020 | 2020-10-19 13:32 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Cloudy | Unidentified | 20 | Checked And Found LBOSB OCB1 Fdr #8 Ctr 609/610, R/F 51N Patrolled The Line On 19/Oct/2020 But Found Nothing Cause: Unidentified | 1
55 | 2020-10-17 07:10 | October | 7:10 | Morning | Saturday | Weekends | 17 | 2020 | 2020-10-17 07:10 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Duri commy 13.8Kv ACB #25 fdr #1 T/R 1x. Not checked yet. | 1
| 2020-10-17 07:10 | October | 7:10 | Morning | Saturday | Weekends | 17 | 2020 | 2020-10-22 09:07 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Checked And Found DCSG ACB25 Fdr #8 Ctr 159/160, R/F 51N Patrolled The Line On 19/Oct/2020 But Found Nothing Cause: Unidentified | 1
56 | 2020-10-17 09:26 | October | 9:26 | Morning | Saturday | Weekends | 17 | 2020 | 2020-10-17 09:26 | 13.8KV MBL SUBSTATION 1 DURI FEEDER #1 | Duri | PGT North | Fair | Under investigation | 82 | 09:29 Bangko MSU #1 fdr #1 T/R 3x. (while transfer load Bangko fdr #1 to MSU fdr#1 by closed LBS 24/X/01) Followed by: ////////////// Pinang load dropped 13A (82/69A). S.Balam feeder #1 load dropped 52A (157/105A). S.Balam feeder #4 load dropped 109A (214/105A). Nella feeder #1 load dropped 121A (210/265A). Nella feeder #2 load dropped 22A (69/47A). Bangko feeder #1 load dropped 146A (158/12A). Bangko feeder #2 load dropped 229A (251/22A). Bangko feeder #3 load dropped 194A (231/37A). Sintong feeder #1 load dropped 10A (89/79A). Sintong feeder #2 load dropped 113A (250/137A). Menggala feeder #1 load dropped 10A (199/189A). Menggala feeder #2 load dropped 139A (166/27A). Ketigul feeder #1 load dropped 11A (132/121A). Ketigul feeder #2 load dropped 24A (73/49A). Ketigul feeder #3 load dropped 10A (32/22A). 10:00 Checked & found Bangko MSU fdr #1 T/R 3x Ctr:...... R/f : 50 @1, @2. and also found Recloser 23/X/08 burntout. 10:40 Patrolled the line but found noting. 10:42 Manually open Bangko fdr #1 to by pass recloser 23/X/08. 11:12 Blocked & closed Bangko fdr #1 Ok. Under investigation. | 1
57 | 2020-10-17 12:13 | October | 12:13 | Afternoon | Saturday | Weekends | 17 | 2020 | 2020-10-17 12:13 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 29 | C.Duri 13.8Kv ACB #11 fdr #1 T/R 1x. Not checked yet. | 1
| 2020-10-17 12:13 | October | 12:13 | Afternoon | Saturday | Weekends | 17 | 2020 | 2020-10-21 08:49 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 29 | Checked And Found CDRSG ACB11 Fdr #8 Ctr 291/291, R/F 51N Patrolled The Line On 17/Oct/2020 But Found Nothing Cause: Unidentified | 1
58 | 2020-10-18 06:37 | October | 6:37 | Morning | Sunday | Weekends | 18 | 2020 | 2020-10-18 06:37 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Fair | Others | - | 13.8 kV ACB/25 DCM feeder #1 T/R 1x Not Checked Yet | 1
| 2020-10-18 06:37 | October | 6:37 | Morning | Sunday | Weekends | 18 | 2020 | 2020-10-20 07:29 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Fair | Others | - | Checked And Found DCSG ACB25 Fdr #8 Ctr 159/160, R/F 51N Patrolled The Line On 19/Oct/2020 But Found Nothing On Phase @3 Cause: Others | 1
59 | 2020-10-18 07:39 | October | 7:39 | Morning | Sunday | Weekends | 18 | 2020 | 2020-10-18 07:39 | 13.8KV 8D FEEDER #1 | Minas | PGT South | Fair | Unidentified | - | 8D/Feeder #1 T/R 1X Not Checked yet. | 1
| 2020-10-18 07:39 | October | 7:39 | Morning | Sunday | Weekends | 18 | 2020 | 2020-10-21 07:36 | 13.8KV 8D FEEDER #1 | Minas | PGT South | Fair | Unidentified | - | Checked And Found 8DSB OCB1 Fdr #8 Ctr 354/355, R/F 50N Patrolled The Line On 20/Oct/2020 But Found Nothing Cause: Unidentified | 1
60 | 2020-10-18 18:14 | October | 18:14 | Afternoon | Sunday | Weekends | 18 | 2020 | 2020-10-18 18:14 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 40 | Sintong Feeder #1 T/R 1X Not checked yet. | 1
| 2020-10-18 18:14 | October | 18:14 | Afternoon | Sunday | Weekends | 18 | 2020 | 2020-10-23 07:33 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 40 | Checked and found: STGSB/13.8OCB1 T/R, Counter : 1238 / 1240, Relay Flag : 51N. Patrolled the line found : Pin Insulator Broken 5% Cause : Unidentified | 1
61 | 2020-10-19 03:34 | October | 3:34 | Night | Monday | Weekdays | 19 | 2020 | 2020-10-19 03:34 | 13.8KV 8D FEEDER #3 | Minas | PGT South | Drizzle | Lightning | 11 | 03:34 8D OCB fdr #3 T/R 1x. Cause : Not Checked Yet. | 1
| 2020-10-19 03:34 | October | 3:34 | Night | Monday | Weekdays | 19 | 2020 | 2020-10-21 07:40 | 13.8KV 8D FEEDER #3 | Minas | PGT South | Drizzle | Lightning | 11 | Checked And Found 8DSB OCB3 Fdr #8 Ctr 281/282, R/F 50N Patrolled The Line On 20/Oct/2020 And Found Broken La On Phase @1,3, Pole Recl. 8D/30 Cause: Lightning | 1
62 | 2020-10-19 12:51 | October | 12:51 | Afternoon | Monday | Weekdays | 19 | 2020 | 2020-10-19 12:51 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Pin Insulator | 0 | New Kotabatak Feeder # 1 and GFPC T/R 1X Not checked yet. | 1
| 2020-10-19 12:51 | October | 12:51 | Afternoon | Monday | Weekdays | 19 | 2020 | 2020-10-21 08:12 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Pin Insulator | 0 | Checked And Found NKBKSB OCB1 Fdr #8 Ctr 299/300, R/F 51N Patrolled The Line On 20/Oct/2020 And Found Broken Pin Insulator O/P 37 Cv 23 On Phase @2 Pole 37 Cv 23 Cause: Pin Insulator | 1
63 | 2020-10-19 14:44 | October | 14:44 | Afternoon | Monday | Weekdays | 19 | 2020 | 2020-10-19 14:44 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Unidentified | 65 | 14:44 New Kotabatak Feeder #2 and GFPC T/R 1X. 17:15 Checked and found Recl 38/CW/08 T/SO ctr:125/126. Blocked and closed the Recloser. Ok then released block. Continued patrol the line under Recl. 38/CX/25. OK. Not checked yet. | 1
| 2020-10-19 14:44 | October | 14:44 | Afternoon | Monday | Weekdays | 19 | 2020 | 2020-10-21 08:16 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Unidentified | 65 | Checked And Found NKBKSB OCB2 Fdr #8 Ctr 99952/99953, R/F 51N Patrolled The Line On 20/Oct/2020 But Found Nothing Cause: Unidentified | 1
64 | 2020-10-20 00:54 | October | 0:54 | Night | Tuesday | Weekdays | 20 | 2020 | 2020-10-20 00:54 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Rain | Unidentified | 74 | 00:54 RGU feeder #2 load dropped 95 A (147 / 52 A) RGU feeder #1 load dropped 11 A ( 56 / 45 A) 01:34 Call TDO crew to check to field 03:15 Checked and found RCL 23/BD/01 on Close position there is indication T/R 5x, ctr: 442 / 447, R/F: 51P @2 Check load of RCL, normal (26/25/24 A) 03:40 Random check well d/s of RCL, Normal (Pelita #04) 03:59 Checked metering at Substation Rangau, Normal reading Informed to Rangau GS : Rudi. Not Patrolled Yet | 1
| 2020-10-20 00:54 | October | 0:54 | Night | Tuesday | Weekdays | 20 | 2020 | 2020-10-23 08:37 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Rain | Unidentified | 74 | Checked and found: 5440/R.23BD01 Unknown, Counter : 442 / 447, Relay Flag : NONE. Patrolled the line found : Tidak ditemukan Cause : Unidentified | 1
65 | 2020-10-20 08:21 | October | 8:21 | Morning | Tuesday | Weekdays | 20 | 2020 | 2020-10-20 08:21 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | North Duri Feeder #1 T/R 1X Not checked yet. | 1
| 2020-10-20 08:21 | October | 8:21 | Morning | Tuesday | Weekdays | 20 | 2020 | 2020-10-23 07:24 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found : NDRSB/13.8VCB1 T/R, Counter : 351 / 352, Relay Flag : 51N Patrolled the line found : No Findings Cause : Unidentified | 1
66 | 2020-10-20 11:44 | October | 11:44 | Morning | Tuesday | Weekdays | 20 | 2020 | 2020-10-20 11:44 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 0 | C.duri Feeder # 16 Load drop 163 A ( 196 / 33A ) Not checked yet. | 1
| 2020-10-20 11:44 | October | 11:44 | Morning | Tuesday | Weekdays | 20 | 2020 | 2020-10-21 16:35 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 0 | Checked And Found RCL 09/M4/01 Fdr #8 Ctr 54/55, Patrolled The Line On 21/Oct/2020 But Found Nothing Cause: Unidentified | 1
67 | 2020-10-20 12:27 | October | 12:27 | Afternoon | Tuesday | Weekdays | 20 | 2020 | 2020-10-20 12:27 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Unidentified | 11 | Rangau Feeder # 2 Load drop 118A ( 130 / 12A ) Not checked yet. | 1
| 2020-10-20 12:27 | October | 12:27 | Afternoon | Tuesday | Weekdays | 20 | 2020 | 2020-10-23 08:32 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Unidentified | 11 | Checked and found: 5440/R.23BD01 Unknown, Counter : 442 / 447, Relay Flag : NONE. Patrol led the line found: tidak ditemukan Cause : Unidentified | 1
68 | 2020-10-21 06:35 | October | 6:35 | Morning | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 06:35 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Fair | Unidentified | - | 06:35 44 kV GCB #1 ND / DUMAI T/R 1x. 13:00 Checked & found 44Kv Line N.Duri GCB#44 T/R 1x Ctr:175/176 R/F:51N Patrolled the line but found nothing. Cause : Unidentified. | 1
| 2020-10-21 06:35 | October | 6:35 | Morning | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 11:56 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Fair | Unidentified | - | Checked And Found 44KVNDGCB#44 Fdr #8 Ctr 175/176, R/F 51N Patrolled The Line On 21/Oct/2020 But Found Nothing Cause: Unidentified | 1
69 | 2020-10-21 08:42 | October | 8:42 | Morning | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 08:42 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Unidentified | - | Darling VCB fdr#3 T/R 1x. Not checked yet. | 1
| 2020-10-21 08:42 | October | 8:42 | Morning | Wednesday | Weekdays | 21 | 2020 | 2020-10-23 07:30 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Unidentified | - | Checked and found : DRLG3/13.8VCB3 T/R, Counter : 280 / 281, Relay Flag : 51N. Patrolled the line found : No Findings Cause : Unidentified | 1
70 | 2020-10-21 11:00 | October | 11:00 | Morning | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 11:00 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 11:00 S/U CGT#5, then On Line the unit at 11:30. | 1
71 | 2020-10-21 12:10 | October | 12:10 | Afternoon | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 12:10 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 12:10 MGT #9 Emergency S/D, due to Fire below Exhaust. Cause : Lube oil leak. | 1
72 | 2020-10-21 13:30 | October | 13:30 | Afternoon | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 13:30 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 13:30 S/U CGT#4, then on line the unit at 14:11. | 1
73 | 2020-10-21 14:15 | October | 14:15 | Afternoon | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 14:15 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 14:15 S/U MGT#11, then on line the unit at 14:33. | 1
74 | 2020-10-21 14:18 | October | 14:18 | Afternoon | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 14:18 | 13.8KV DURI FIELD FEEDER #1 | Duri | PGT North | Rain and Lightning | Unidentified | - | 14:18 It was reported No drop at 07/U1/19 (D. Field frd#1). Checked & found Recl. 07/U1/19 T/O (Bloack Position) Ctr:29/30. Patrolled the line but found nothing. 15:35 Blocked & Closed Recl. 07/U1/19, then release the block. Cause: Unidentified. | 1
75 | 2020-10-21 14:38 | October | 14:38 | Afternoon | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 14:38 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Rain and Lightning | Recloser / Control Recloser | 328 | 14:38 C.Duri fdr#6 Load dropped 120A (151/31A). 15:30 Checked & found Recl. 02/01/01 T/O (Block position). Ctr:29/30. Patrolled the line but found nothing. 15:35 Blocked & closed Recl. 02/01/01 but failed (Cntrol Recl Problem). Un Plug Recl. 02/01/01. 16:35 Blocked & closed Recl. 03/03/42, then release the block. (Feed from fdr#7). Cause: Control Recloser. | 1
76 | 2020-10-21 14:43 | October | 14:43 | Afternoon | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 14:43 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Unidentified | 3 | 14:43 N.Duri VCB fdr#2 T/O (Blocked Position). 14:53 Blocked & closed N.Duri VCB fdr#2. Not checked yet. | 1
| 2020-10-21 14:43 | October | 14:43 | Afternoon | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 17:50 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Unidentified | 3 | Checked And Found RCL 13/F11/03 Fdr #8 Ctr 58/59, Patrolled The Line On 21/Oct/2020 But Found Nothing Cause: Unidentified | 1
77 | 2020-10-21 14:52 | October | 14:52 | Afternoon | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 14:52 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Pin Insulator | - | C.Duri fdr#1 Load dropped 59A (72/13A). Not checked yet. | 1
| 2020-10-21 14:52 | October | 14:52 | Afternoon | Wednesday | Weekdays | 21 | 2020 | 2020-10-23 17:32 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Pin Insulator | - | Checked and found: 5441/R.38AS09 Unknown, Counter : 454 / 454, Relay Flag : NONE. Patrolled the line and found : Pin Flash Over di puncak #35. Counter Recloser tidak berubah, tetapi ada record event di waktu yang sama dengan info patrol checklist Cause : Pin Insulator | 1
78 | 2020-10-21 15:45 | October | 15:45 | Afternoon | Wednesday | Weekdays | 21 | 2020 | 2020-10-21 15:45 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Recloser / Control Recloser | - | 15:45 It was reported no power at 13/F11/02 ( N.Duri fdr#2). 17:02 Checked & found Recl 13/F11/03 T/O (Blocked Position) Ctr:58/59. Patrolled the line but found nothing. 18:10 Blocked & closed Recl. 13/F11/03, then release the block. Cause: Unidentified. | 1
79 | 2020-10-22 11:21 | October | 11:21 | Morning | Thursday | Weekdays | 22 | 2020 | 2020-10-22 11:21 | SINABUNG MINI SUBSTATION | Duri | PGT North | Cloudy | Unidentified | - | 11:21 It was reported no power at Duri Water Plan. 12:00 Checked & found 13.8 Kv Recl Mini Subst T/O Ctr:249/250. 12:15 Opened 4160V Recl Sinabung Mini Subst. 12:19 Blocked & Closed 13,8Kv Recl. for 2500KVA tx at Sinabung Mini Subst. Cause: Unidentified. | 1
80 | 2020-10-22 13:40 | October | 13:40 | Afternoon | Thursday | Weekdays | 22 | 2020 | 2020-10-22 13:40 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Lightning | 7 | So. Balam fdr#1 Load dropped 99A (153/54A). Not checked yet. | 1
81 | 2020-10-22 14:05 | October | 14:05 | Afternoon | Thursday | Weekdays | 22 | 2020 | 2020-10-22 14:05 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Cloudy | Planned Maintenance | 108 | 14:05 Manually Opened Minas ACB fdr#3. Replaced Recloser o/p 7D/93. Repaired Cross Arm o/p 7D/71. 18:06 Block & closed Minas ACB fdr#3, then release the block. Cause: Plan Maintenance. | 1
82 | 2020-10-22 14:52 | October | 14:52 | Afternoon | Thursday | Weekdays | 22 | 2020 | 2020-10-22 14:52 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Cloudy | Animal | 66 | N.Duri VCB fdr#1 T/R 1x. Not checked yet. | 1
| 2020-10-22 14:52 | October | 14:52 | Afternoon | Thursday | Weekdays | 22 | 2020 | 2020-10-23 07:28 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Cloudy | Animal | 66 | Checked and found: 5441/R.10/L1/44 T/O, Counter : 146 / 147, Relay Flag : NONE. Patrol led the line found: ditemukan monyet mati dan broken bushing recloser Cause : Animal | 1
83 | 2020-10-22 15:01 | October | 15:01 | Afternoon | Thursday | Weekdays | 22 | 2020 | 2020-10-22 15:01 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Cloudy | Animal | - | 15:01 It was reported at 10/L1/35 (N.Duri fdr#1). 15:30 Checked & found Recl. 10/L1/44 T/O (Block position) Ctr:146/147. Dead Monkey o/p 10/L144. Broken Bushing Recl. 10/L1/44. 16:49 Manually Open N. Duri fdr#1, then closed at 17:00. Closed by pass Recl. 10/L1/44. Cause: Animal (Monkey). | 1
84 | 2020-10-23 08:33 | October | 8:33 | Morning | Friday | Weekdays | 23 | 2020 | 2020-10-23 08:33 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Unidentified | 8 | 08:33 It was reported no power at recloser 07/U1/19 (Duri field feeder #2). 09:30 Checked & found Recloser 07/U1/19 (Block position) Ctr :89/90. Patrolled the line but found nothing. 09:32 Block & close recloser 07/U1/19. Cause: Unidentified. | 1
85 | 2020-10-24 05:26 | October | 5:26 | Morning | Saturday | Weekends | 24 | 2020 | 2020-10-24 05:26 | LIBO SUBSTATION | Libo | PGT South | Fair | Animal | 219 | 05:26 Libo 115Kv C/S T/O ( No alarm to DSC ) Libo RTU failure and back to normal at 05:27 06:30 Checked and found Libo 115Kv C/S T/O R/F 86T and 87T Ctr 382/383 TX Oil temp 59F. Manually open Libo fdr #1 ,The closed 07:20. Manually open Libo fdr #2 ,The closed 07:21. 07:17 Closed Libo 115Kv C/S,Ok. Cause: Animal (Lizard) | 1
86 | 2020-10-24 06:35 | October | 6:35 | Morning | Saturday | Weekends | 24 | 2020 | 2020-10-24 06:35 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 5 | So Balam Feeder #1 Load drop 100A ( 153/53A) Not checked yet. | 1
87 | 2020-10-24 09:23 | October | 9:23 | Morning | Saturday | Weekends | 24 | 2020 | 2020-10-24 09:23 | LIBO SUBSTATION | Libo | PGT South | Fair | Animal | 114 | 09:23 Libo 115Kv C/S T/O ( No alarm to DSC ) Libo RTU failure and back to normal at 05:27 09:40 Checked and found Libo 115Kv C/S T/O R/F 86T and 87T Ctr 383/384 TX Oil temp 59F. 10:05 Manually open Libo fdr #1 ,The closed 10:19. Manually open Libo fdr #2 ,The closed 10:20. 10:14 Closed Libo 115Kv C/S,Ok. Cause: Animal (Lizard). | 1
88 | 2020-10-24 10:09 | October | 10:09 | Morning | Saturday | Weekends | 24 | 2020 | 2020-10-24 10:09 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 150 | 10:09 Manually open Ketigul feeder #1. Replaced pin insulation o/p 33/AL/25. Replaced deaden insulation on top tilan #03. Replaced recloser 32/AK/16. 13:00 Blocked & closed Ketigul feeder #1, The released the block. Cause: plan maintenance. | 1
89 | 2020-10-24 11:06 | October | 11:06 | Morning | Saturday | Weekends | 24 | 2020 | 2020-10-24 11:06 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 11:06 S/U MGT#4, then on line the unit at 11:35. | 1
90 | 2020-10-24 18:02 | October | 18:02 | Afternoon | Saturday | Weekends | 24 | 2020 | 2020-10-24 18:02 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 58 | Menggala 13.8Kv VCB fdr #1 T/R 1x. Menggala GFPC T/O. Menggala feeder #2 load dropped 163A (170/7A). Not checked yet. | 1
91 | 2020-10-24 18:21 | October | 18:21 | Afternoon | Saturday | Weekends | 24 | 2020 | 2020-10-24 18:21 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Static Wire | 327 | 18:21 Batang 13.8Kv OCB fdr #3 T/R 1x. Batang GFPC T/R. Not checked yet. 18:36 Batang 13.8Kv OCB fdr #3 T/R 1x. Batang GFPC T/R. Not checked yet. 18:40 Batang 13.8Kv OCB fdr #3 T/R 1x. Batang GFPC T/R. Not checked yet. 19:00 Checked and patrol the line Found nothing R/F Time OC 1 Ctr: 421/424 GFPC Ctr: 1078/1085 21:56 Blocked and closed GFPC and Batang Feeder #3 ..Ok Then release the block Couse unidentified. | 1
| 2020-10-24 18:21 | October | 18:21 | Afternoon | Saturday | Weekends | 24 | 2020 | 2020-10-24 18:21 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Static Wire | 327 | 18:21 Batang 13.8Kv OCB fdr #3 T/R 1x. Batang GFPC T/R. Not checked yet. 18:36 Batang 13.8Kv OCB fdr #3 T/R 1x. Batang GFPC T/R. Not checked yet. 18:40 Batang 13.8Kv OCB fdr #3 T/R 1x. Batang GFPC T/R. Not checked yet. 19:00 Checked and patrol the line Found nothing R/F Time OC 1 Ctr: 421/424 GFPC Ctr: 1078/1085 21:56 Blocked and closed GFPC and Batang Feeder #3 ..Ok Then release the block Couse unidentified. | 1
92 | 2020-10-24 21:11 | October | 21:11 | Night | Saturday | Weekends | 24 | 2020 | 2020-10-24 21:11 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain | Lightning | - | 3Delta Feeder #2 T/R 1X Not checked yet. | 1
| 2020-10-24 21:11 | October | 21:11 | Night | Saturday | Weekends | 24 | 2020 | 2020-10-27 17:11 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain | Lightning | - | Checked and found 3D fdr #2, counter: 393 / 394, R/F: 51P Patrolled the line but found nothing Cause : Lightning | 1
93 | 2020-10-25 05:53 | October | 5:53 | Morning | Sunday | Weekends | 25 | 2020 | 2020-10-25 05:53 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Pin Insulator | 32 | Petani Feeder #2 T/R 1X Petani Feeder #1 Load drop 37A ( 230/193A ) Not Checked yet. | 1
| 2020-10-25 05:53 | October | 5:53 | Morning | Sunday | Weekends | 25 | 2020 | 2020-10-25 16:42 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Pin Insulator | 32 | Checked and found: PTNSB/13.8OCB2 T/R, Counter : 333 / 334, Relay Flag : 50N. Patrolled the line and found: Pin Insulator Broken Cause : Pin Insulator | 1
94 | 2020-10-25 09:54 | October | 9:54 | Morning | Sunday | Weekends | 25 | 2020 | 2020-10-25 09:54 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Fair | Planned Maintenance | 52 | 09:54 Manually open LBS 7E/40A ( Minas feeder #6). Replaced broken recloser 7E/67A (10 well off ). 12:15 Closed LBS 7E/40A, Ok. Cause; Plan maintenance. | 1
95 | 2020-10-25 17:38 | October | 17:38 | Afternoon | Sunday | Weekends | 25 | 2020 | 2020-10-25 17:38 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Rain | Unidentified | - | 44Kv line N.Duri////> Dumai GCB #1 T/R 1x. Not checked yet. | 1
| 2020-10-25 17:38 | October | 17:38 | Afternoon | Sunday | Weekends | 25 | 2020 | 2020-10-28 09:45 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Rain | Unidentified | - | Checked and found 44 kV GCB #1 ND T/R 1x, Ctr: 176 / 177, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
96 | 2020-10-26 01:56 | October | 1:56 | Night | Monday | Weekdays | 26 | 2020 | 2020-10-26 01:56 | 13.8KV 3D FEEDER #8 | Minas | PGT South | Cloudy | Unidentified | 37 | 3 Delta feeder #8 T/R 1X 3 Delta feeder #6 load drop 60A ( 122/62A ) not checked yet. | 1
| 2020-10-26 01:56 | October | 1:56 | Night | Monday | Weekdays | 26 | 2020 | 2020-10-27 17:11 | 13.8KV 3D FEEDER #8 | Minas | PGT South | Cloudy | Unidentified | 37 | Checked and found 3D VCB feeder #8 T/R 1x, Counter: 340 / 341 Patrolled the line but found nothing Cause : Unidentified | 1
97 | 2020-10-26 07:38 | October | 7:38 | Morning | Monday | Weekdays | 26 | 2020 | 2020-10-26 07:38 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Fair | Unidentified | 70 | Minas 13.8Kv ACB #1 fdr#4 T/R 1x. Ctr:134/135 R/f: 51N Not checked yet. | 1
| 2020-10-26 07:38 | October | 7:38 | Morning | Monday | Weekdays | 26 | 2020 | 2020-10-30 07:20 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Fair | Unidentified | 70 | Checked and found MNS ACB fdr #4 T/R 1x, counter: 134 / 135, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
98 | 2020-10-26 10:54 | October | 10:54 | Morning | Monday | Weekdays | 26 | 2020 | 2020-10-26 10:54 | IT MINI SUBSTATION | Duri | PGT North | Fair | Under investigation | - | 10:54 It was reported no power at WTP plant. 11:42 Checked & found 13.8Kv recloser 2500Kva mini substation T/O Ctr: 250/251. Open 4160v recloser Mini substation ( Trouble shout ). 12:23 Closed 13.8Kv recloser at IT Mini substation. 12:24 Closed 4160v recloser at IT Mini substation Cause: Under investigation. | 1
99 | 2020-10-26 17:11 | October | 17:11 | Afternoon | Monday | Weekdays | 26 | 2020 | 2020-10-26 17:11 | 13.8KV CENTRAL DURI FEEDER #15 | Duri | PGT North | Fair | Unidentified | - | C.Duri 13.8Kv ACB #18 fdr #15 T/R 1x. Niot checked yet. | 1
| 2020-10-26 17:11 | October | 17:11 | Afternoon | Monday | Weekdays | 26 | 2020 | 2020-10-27 15:35 | 13.8KV CENTRAL DURI FEEDER #15 | Duri | PGT North | Fair | Unidentified | - | Checked and found ACB/18 CD fdr #15 T/R 1x, ctr: 420 / 421, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
100 | 2020-10-27 06:18 | October | 6:18 | Morning | Tuesday | Weekdays | 27 | 2020 | 2020-10-27 06:18 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 31 | Ketigul feeder#2 T/R 1X Not checked yet. | 1
| 2020-10-27 06:18 | October | 6:18 | Morning | Tuesday | Weekdays | 27 | 2020 | 2020-10-28 17:27 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 31 | Checked and found: KTGL VCB fdr #2 T/R 1x, Counter : 411 / 412, R/F : 51N. Patrolled the line found : flas deadand Cause : Dead End Insulator | 1
101 | 2020-10-28 09:47 | October | 9:47 | Morning | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 09:47 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 3 | 09:47 Manual Open RCL 6D/200, manual closed at 10:40 MTCE team to replace broken pin insulator o/p 6D/106 Planned Maintenance | 1
102 | 2020-10-28 14:43 | October | 14:43 | Afternoon | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 14:43 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 12 | 14:43 Manual Open RCL 16/Z/88, Closed at 17:12 MTCE team to repair corroded pole at Terminal pole So. BLM #12 Planned Maintenance | 1
103 | 2020-10-28 20:00 | October | 20:00 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 20:00 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Tree | - | C.Duri feeder #1 load dropped 59A (67/8A). Not checked yet. | 1
| 2020-10-28 20:00 | October | 20:00 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-31 15:49 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Tree | - | Checked and found Rec 38/AS/09 T/R 3x, R/F: 51N, Counter: 454/457. Patrolled the line and found palm tree touching powerline. Cause : Tree. | 1
104 | 2020-10-28 20:04 | October | 20:04 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 20:04 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Rain and Lightning | Unidentified | - | CKBS feeder #5 load dropped 169A (211/42A). CKBS feeder #2 load dropped 55A (327/272A). Not checked yet. | 1
| 2020-10-28 20:04 | October | 20:04 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-30 14:40 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Rain and Lightning | Unidentified | - | Checked and found 5443/RCL T/R 1x R/F: NONE Counter: 336/337. Patrolled the line and found nothing. Cause: Unidentified. | 1
105 | 2020-10-28 20:10 | October | 20:10 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 20:10 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Rain and Lightning | Lightning Arrester | - | N.Duri 13.8Kv ACB #7 T/R 1x. Not checked yet. | 1
| 2020-10-28 20:10 | October | 20:10 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-31 07:34 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Rain and Lightning | Lightning Arrester | - | Checked and found NDRSB/13.8VCB7 T/R 1x, R/F 51N, Counter: 147/148. Patrolled the line and found broken L/A on pole 10/L1/23. Cause: Lightning Arrester | 1
106 | 2020-10-28 20:10 | October | 20:10 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 20:10 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Unidentified | - | N.Duri feeder #2 load dropped 171A (215/44A). Not checked yet. | 1
| 2020-10-28 20:10 | October | 20:10 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-31 07:35 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Unidentified | - | Checked and found REC NC 04 T/R 1x, R/F: 51, Counter: 95/96. Patrolled the line and found nothing. Cause : Unidentified. | 1
107 | 2020-10-28 20:16 | October | 20:16 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 20:16 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 20:16 CDG #2 Trip by Alarm Compose Trip. | 1
108 | 2020-10-28 20:16 | October | 20:16 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 20:16 | 13.8KV CENTRAL DURI FEEDER #4 | Duri | PGT North | Rain and Lightning | Pin Insulator | - | C.Duri 13.8Kv ACB #21 fdr #4 T/R 1x. Not checked yet. | 1
| 2020-10-28 20:16 | October | 20:16 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-01-11 13:23 | 13.8KV CENTRAL DURI FEEDER #4 | Duri | PGT North | Rain and Lightning | Pin Insulator | - | Checked and found CDRSG/13.8ACB21 T/R 1x R/F: 51N Counter: 538/539. Patrolled the line and found broken dead end insulator on pole 09/P8/01 and broken pin insulator on pole 09/R8/10. Cause: Broken Insulator. | 1
109 | 2020-10-28 20:20 | October | 20:20 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 20:20 | 13.8KV CENTRAL DURI FEEDER #8 | Duri | PGT North | Rain and Lightning | Unidentified | - | C.Duri 13.8Kv ACB #32 fdr #8 T/R 1x. Not checked yet. | 1
| 2020-10-28 20:20 | October | 20:20 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-31 15:52 | 13.8KV CENTRAL DURI FEEDER #8 | Duri | PGT North | Rain and Lightning | Unidentified | - | Checked and found CDRSG/13.8ACB32 T/R 1x R/F: 51N Counter: 489/490. Patrolled the line and found nothing. Cause : Unidentified. | 1
110 | 2020-10-28 20:24 | October | 20:24 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 20:24 | 115KV DURI / DARLING SUBST LINE | Duri | PGT North | Rain and Lightning | Unidentified | - | 20:24 115 kV line DRB / N. Duri GCB #29 & GCB #31 T/R 1x. 115/kV line N. Duri / DRB GCB #2 T/R 1X. Not checked yet. | 1
| 2020-10-28 20:24 | October | 20:24 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-29 08:08 | 115KV DURI / DARLING SUBST LINE | Duri | PGT North | Rain and Lightning | Unidentified | - | Checked and found : / GCB #2 ND T/R 1x, counter: 96 / 97, R/F: 87L / GCB #1 DRL T/R 1x, counter: 203 / 204, 87L / GCB #2 DRL T/R 1x, counter: 186 / 187, 87L / GCB #29 DRB T/R 1x, counter: 156 / 157, R/F: 87L / GCB #31 DRB T/R 1x, counter: 229 / 230, R/F: 87L Patrolled the line but found nothing Cause: Unidentified | 1
111 | 2020-10-28 20:26 | October | 20:26 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 20:26 | NORTH DURI SUBSTATION | Duri | PGT North | Rain and Lightning | Unidentified | - | 44Kv line N.Duri/////>Dumai GCB #1 T/R 1x. Not checked yet. | 1
| 2020-10-28 20:26 | October | 20:26 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-31 15:34 | NORTH DURI SUBSTATION | Duri | PGT North | Rain and Lightning | Unidentified | - | Checked and found 44KVNDGCB#44 T/R 1x R/F: 51N Counter: 177/178. Patrolled the line and found nothing. Cause : Unidentified. | 1
112 | 2020-10-28 20:29 | October | 20:29 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 20:29 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Unidentified | - | N.Duri 13.8Kv VCB fdr #1 T/R 1x. Not checked yet. | 1
| 2020-10-28 20:29 | October | 20:29 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-31 07:37 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Unidentified | - | Checked and found NDRSB/13.8VCB1 T/R 1x, R/F: 51, Counter: 354/355. Patrolled the line and found nothing. Cause : Unidentified. | 1
113 | 2020-10-28 21:12 | October | 21:12 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 21:12 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Unidentified | 52 | 3D 13.8Kv OCB fdr #2 T/R 1x. Not checked yet. | 1
| 2020-10-28 21:12 | October | 21:12 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-31 16:48 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Unidentified | 52 | Checked and found 3DSB/13.8OCB2 T/R 1x R/F: 50 Counter: 394/395. Patrolled the line and found nothing. Cause: Unidentified. | 1
114 | 2020-10-28 21:15 | October | 21:15 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 21:15 | 13.8KV 5B FEEDER #3 | Minas | PGT South | Rain and Lightning | Circuit Breaker | 71 | 21:15 5B 13.8Kv OCB fdr #3 T/SO. Ctr: On operated R/f: 51 @2. 22:22 Checked & found 5B fdr#3 T/SO Ctr:Not Operated R/F:51@2. Blocked & closed 5B fdr#3, but failed. Patrolled the line but found nothing. 23:00 Open LBS 4C/45, then closed at 23:45 checked 5B fdr#3 Breaker not charge, them recharge. 23:37 Blocked & closed 5B feeder #3, Ok then released the block. Cause: Circuit Breaker. | 1
115 | 2020-10-28 21:19 | October | 21:19 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 21:19 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Rain and Lightning | Dead End Insulator | 21 | 4D 13.8Kv OCB fdr #3 T/R 1x. Not checked yet. | 1
| 2020-10-28 21:19 | October | 21:19 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-30 16:16 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Rain and Lightning | Dead End Insulator | 21 | Checked and found 4DSB/13.8OCB3 T/R 1x R/F: 51 Counter: 312/313. Patrolled the line and found broken deadend on pole 4C/38. Cause : Broken Deadend | 1
116 | 2020-10-28 21:21 | October | 21:21 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-28 21:21 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain and Lightning | Unidentified | - | 3D fdr#4 Load dropped 51A (141/90A). Not checked yet. | 1
| 2020-10-28 21:21 | October | 21:21 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-29 06:35 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain and Lightning | Unidentified | - | 06:35 Checked & found Recl. 2D/33 T/SO Ctr:63/64. 06:42 Blocked & closed Recl 2D/33, then release the block. Not patrolled yet. | 1
| 2020-10-28 21:21 | October | 21:21 | Night | Wednesday | Weekdays | 28 | 2020 | 2020-10-30 16:14 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain and Lightning | Unidentified | - | Checked and found 5442/R.2D33 T/R 1x R/F: 51 Counter: 63/64. Patrolled the line and found nothing. Cause: Unidentified. | 1
117 | 2020-10-29 06:11 | October | 6:11 | Morning | Thursday | Weekdays | 29 | 2020 | 2020-10-29 06:11 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 80 | 06:11 South Balam VCB feeder #1 T/R 1X . Not checked yet. 14:00 Checked and found South Balam VCB feeder #1 T/R 1X . R/F : 51N Counter: 422/423. Patrolled the line nothing found. Cause: Unidentified. | 1
118 | 2020-10-29 08:45 | October | 8:45 | Morning | Thursday | Weekdays | 29 | 2020 | 2020-10-29 08:45 | 13.8KV NORTH DURI FEEDER #6 | Duri | PGT North | Fair | Lightning | 29 | 08:45 It was reported no power at road 12/F5/xx 09:53 Checked and found RCL 12/F5/02 T/LO, ctr: 109 / 110, R/F: 51P @1 Patrolled the line and found broken LA @1 o/p 12/F5/06 10:17 Blocked and manual close RCL 12/F5/02, OK. then release the block. Cause: Lightning (LA) | 1
119 | 2020-10-29 10:31 | October | 10:31 | Morning | Thursday | Weekdays | 29 | 2020 | 2020-10-29 10:31 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | - | 10:31 It was reported no power along road 09/L7/xx 11:15 Checked and found RCL 09/L7/01 T/LO, ctr: 252 / 253, R/F: SGF Patrolled the line but found nothing. 11:29 Block and manual close RCL 09/L7/01, OK. then release the block. Cause: unidentified. | 1
120 | 2020-10-29 20:43 | October | 20:43 | Night | Thursday | Weekdays | 29 | 2020 | 2020-10-29 20:43 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | MSU fdr #1 (Bangko fdr #1) T/R 1x. Not checked yet. | 1
121 | 2020-10-29 21:05 | October | 21:05 | Night | Thursday | Weekdays | 29 | 2020 | 2020-10-29 21:05 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | - | Ketigul feeder #1 load dropped 105A (132/27A). Not checked yet. | 1
| 2020-10-29 21:05 | October | 21:05 | Night | Thursday | Weekdays | 29 | 2020 | 2020-10-31 15:43 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | - | Checked and found 5441/R.32AK04 Unknown R/F None Counter: 172/172. Patrolled the line and found nothing. Cause: Unidentified. | 1
122 | 2020-10-30 09:46 | October | 9:46 | Morning | Friday | Weekdays | 30 | 2020 | 2020-10-30 09:46 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Planned Maintenance | 15 | 09:46 Manual Open RCL 06/R5/02 (DF fdr #2), closed at 11:25 MTCE team to change out 112.5 kVA TX on pole 06/R5/07 Planned Maintenance | 1
123 | 2020-10-30 10:56 | October | 10:56 | Morning | Friday | Weekdays | 30 | 2020 | 2020-10-30 10:56 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | 101 | 10:56 South Balam VCB load dropped 46 A (215 / 169 A) South Balam GFPC T/R 1x 12:35 Checked and found RCL 19/AA/07 operate 1x, ctr: 113 / 114, R/F: 51P @2 Indication 79 (L/O relay) was illuminate at control recloser (type SEL). 13:05 Complete patrol the line, but found nothing 13:08 Block and Manual close RCL 19/AA/01, OK and then release the block. Cause: Unidentified | 1
124 | 2020-10-30 13:46 | October | 13:46 | Afternoon | Friday | Weekdays | 30 | 2020 | 2020-10-30 13:46 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 13:46 S/U CDGT/2 and then Online at 14:08 To support MW due to plan shut down of NDC CT/2 | 1
125 | 2020-10-30 14:11 | October | 14:11 | Afternoon | Friday | Weekdays | 30 | 2020 | 2020-10-30 14:11 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Recloser / Control Recloser | 3 | 14:11 It was reported no power at Road 07/U1/xx, no load dropped at DF fdr #2 14:35 Checked and found RCL 07/U1/19 T/O (on block for PT WKS clean up canals) 14:41 Manual Close the RCL 07/U1/19, OK and then release the block. 15:09 Unplug cable control of RCL 07/U1/19, purpose for troubleshoot. Cause: Not Patrolled Yet | 1
| 2020-10-30 14:11 | October | 14:11 | Afternoon | Friday | Weekdays | 30 | 2020 | 2020-10-31 09:21 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Recloser / Control Recloser | 3 | Patrolled the line but found nothing. Cause: Control Recloser. | 1
126 | 2020-10-30 15:55 | October | 15:55 | Afternoon | Friday | Weekdays | 30 | 2020 | 2020-10-30 15:55 | 13.8KV CENTRAL DURI FEEDER #10 | Duri | PGT North | Fair | Lightning Arrester | 33 | 15:55 CD ACB/42 feeder #10 Operate 3x, ctr: 380 / 383, R/F: 51N 16:45 Patrolled the line and found broken LA o/p 05/N5/09 and the jumper touch to pole/ground 16:50 Manual Open LBS 05/N5/25 to isolate power line along road 05/N5/xx 17:00 Manual close ACB/42 CD fdr #10, OK. waiting MTCE team to isolate jumper of broken LA 18:25 Change out LA on pole 05/N5/09 has finished 18:26 Manual Close LBS 05/N5/25, OK. Cause: Lightning Arrester | 1
127 | 2020-10-31 06:13 | October | 6:13 | Morning | Saturday | Weekends | 31 | 2020 | 2020-10-31 06:13 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Unidentified | 9 | 06:13 Petani fdr#2 T/R 1x 14:06 Checked and found PTNSB/13.8OCB2 T/R 1x R/F: 50 Counter: 334/335. Patrolled the line but found nothing. Cause: Unidentified. | 1
128 | 2020-10-31 08:53 | October | 8:53 | Morning | Saturday | Weekends | 31 | 2020 | 2020-10-31 08:53 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Voltage regulator failure | 287 | 08:53 Sintong feeder #2 load dropped 179 A (244 / 65 A) Sintong GFPC T/R 1x Call to Benar GS, no power from Sintong fdr #2 side 09:33 Checked and found RCL 28/AF/02 operate 3x, indication lock out was lights up. Counter 1569 / 1572, R/F: 51P @2. 09:57 Patrolled the line and found broken bushing @2 of line VR Benar 11:20 Bypass and isolated the VR 11:35 Block and close the RCL 28/AF/02, Ok then release the block. Cause: Burned out Bushing VR (auto transformer) | 1
129 | 2020-10-31 14:18 | October | 14:18 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-10-31 14:18 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 484 | 14:18 Manual Open BKO VCB fdr #1, closed at …… Purpose for maintenance team to change out RCL 23/X/08 Planned Maintenance | 1
130 | 2020-10-31 14:51 | October | 14:51 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-10-31 14:51 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | 14:51 CD ACB/23 fdr #6 T/R 1x, ctr: 528 / 529, R/F: 51N, 51G Not Patrolled Yet | 1
| 2020-10-31 14:51 | October | 14:51 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-01-11 13:17 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | Checked and found CDRSG/13.8ACB23 T/R 1x R/F: 51N Counter: 528/529. Patrolled the line but found nothing. Cause: Unidentified. | 1
131 | 2020-10-31 14:51 | October | 14:51 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-10-31 14:51 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | CDGT/2 Trip by alarm DC power supply under voltage | 1
132 | 2020-10-31 15:11 | October | 15:11 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-10-31 15:11 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | 15:11 CD VCB fdr #2 T/O (block for BMS/03A / permit valid for 29 oct / 5 nov) Counter: 408 0 409, R/F 51P @1, @2, @3 15:15 Call RIG BMS/03A, all on normal condition (by Hendra) 15:19 Close CD ACB/12 fdr #2, OK. still on block for BMS/03A Cause: Not Patrolled Yet | 1
| 2020-10-31 15:11 | October | 15:11 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-01-11 13:14 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | Checked and found CDRSG/13.8ACB12 T/O R/F: 51 Counter: 408/409. Patrolled the line but found nothing. Cause: Unidentified. | 1
133 | 2020-10-31 15:17 | October | 15:17 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-10-31 15:17 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Rain and Lightning | Pin Insulator | 0 | North Duri VCB fdr #7 T/R 1x Not Checked Yet | 1
| 2020-10-31 15:17 | October | 15:17 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-01-11 14:20 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Rain and Lightning | Pin Insulator | 0 | Checked and found NDRSB/13.8VCB7 T/R 1x R/F: 51N Counter: 148/149. Patrolled the line and found flash pin insulator on pole 10/K6/27. Cause: Pin Insulator. | 1
134 | 2020-10-31 15:17 | October | 15:17 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-10-31 15:17 | 13.8KV NORTH DURI FEEDER #8 | Duri | PGT North | Rain and Lightning | Others | 0 | North Duri VCB fdr #8 T/R 1x Not Checked Yet | 1
| 2020-10-31 15:17 | October | 15:17 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-01-11 14:25 | 13.8KV NORTH DURI FEEDER #8 | Duri | PGT North | Rain and Lightning | Others | 0 | Checked and found NDRSB/13.8VCB8 T/R 1x R/F: 51N Counter: 120/121. Patrolled the line and found broken insulator at bypass switch on pole 10/K2/02. Cause: Bypass switch support insulator | 1
135 | 2020-10-31 15:45 | October | 15:45 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-10-31 15:45 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 45 | Batang VCB fdr #3 T/R 1x Not Checked Yet | 1
| 2020-10-31 15:45 | October | 15:45 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-02-11 15:36 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 45 | Checked and found BTG VCB fdr #3 had operated 1x, ctr: 425/426, R/F: 50N Patrolled the line but found nothing Cause : Unidentified | 1
136 | 2020-10-31 17:11 | October | 17:11 | Afternoon | Saturday | Weekends | 31 | 2020 | 2020-10-31 17:11 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 17:11 NDC/CD/3 S/U and then online at 17:40 | 1
1 | 2020-09-14 05:50 | September | 5:50 | Morning | Monday | Weekdays | 14 | 2020 | 2020-01-09 09:32 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 52 | 09:32 Manual Open RCL 28-AF-17, closed at 11:22 MTCE team to replace insulator o/p 29-AG-07 and 28-AF-28 Planned Maintenance | 1
2 | 2020-09-14 05:50 | September | 5:50 | Morning | Monday | Weekdays | 14 | 2020 | 2020-01-09 10:08 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 0 | 10:08 Manual Open LBS 36-DN-13 (4D fdr #3), closed at 12:05 MTCE team to replace insulator o/p 4D-71 and 3D-228 Planned Maintenance | 1
3 | 2020-09-14 05:50 | September | 5:50 | Morning | Monday | Weekdays | 14 | 2020 | 2020-01-09 17:04 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Fair | Others | - | Checked and found Recloser GS-1 T/SO. Cause: Under Investigation | 1
| 2020-09-14 17:39 | September | 17:39 | Afternoon | Monday | Weekdays | 14 | 2020 | 2020-07-09 08:38 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Fair | Others | - | Checked and found: 5442-R.GS1 T/SO, Counter : 101 - 102, Relay Flag : NONE Patrolled the line found: Display Recl. GS-1 Cause : Others | 1
4 | 2020-09-14 17:39 | September | 17:39 | Afternoon | Monday | Weekdays | 14 | 2020 | 2020-01-09 17:18 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Lightning | 9 | Rokan VCB fdr #2 T/R 1x Not Checked Yet | 1
5 | 2020-09-14 18:34 | September | 18:34 | Afternoon | Monday | Weekdays | 14 | 2020 | 2020-01-09 18:46 | 13.8KV CENTRAL DURI FEEDER #15 | Duri | PGT North | Cloudy | Unidentified | - | 18:46 CD ACB fdr #15 T/R 1x, ctr: R/F: Not Checked Yet | 1
| 2020-09-14 18:34 | September | 18:34 | Afternoon | Monday | Weekdays | 14 | 2020 | 2020-04-09 07:19 | 13.8KV CENTRAL DURI FEEDER #15 | Duri | PGT North | Cloudy | Unidentified | - | Checked and found: CDRSG-13.8ACB18 T/R, Counter : 419 - 420, Relay Flag : 50. Patrolled the line found : No Findings Cause : Unidentified | 1
6 | 2020-09-14 19:07 | September | 19:07 | Night | Monday | Weekdays | 14 | 2020 | 2020-02-09 09:07 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Lightning | 1 | 09:07 Sintong 13.8Kv OCB fdr #1 T/R. Sintong GFPC T/R. 12:28 Checked and found STG VCB fdr #1 T/R 1x Patrolled the line and found broken pin insulator @3 o/p 25-AE-15 Cause : Lightning | 1
7 | 2020-09-14 19:42 | September | 19:42 | Night | Monday | Weekdays | 14 | 2020 | 2020-02-09 10:33 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Animal | 72 | NKBS 13.8Kv OCB fdr#2 T/R 1x. NKBS GFPC T/R. Not checked yet. | 1
| 2020-09-14 19:42 | September | 19:42 | Night | Monday | Weekdays | 14 | 2020 | 2020-03-09 15:36 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Animal | 72 | Checked and found: NKBKSB-13.8OCB2 T/R, Counter : 99949 - 99950, Relay Flag : 50N Patrol led the line found: was found dead monkey near KB 260 pad trafo Cause : Animal | 1
8 | 2020-09-15 18:38 | September | 18:38 | Afternoon | Tuesday | Weekdays | 15 | 2020 | 2020-02-09 11:24 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 229 | 11:24 Manually open Sintong feeder #1. Repair broken cross arm o/p 25-AD-26. Cutting jumper o/p 25-AD-25 & 25-AD-27. 12:29 Closed LBS 25-AC-33 part load sintong feeder #1 transfer to BKO fdr #4. 14:14 Closed Sintong feeder #1 Ok. Cause : Planned Maintenance. | 1
| 2020-09-15 18:38 | September | 18:38 | Afternoon | Tuesday | Weekdays | 15 | 2020 | 2020-05-09 11:40 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 229 | 11:40 Manual Open LBS 25-AL-33 (two way fdr BKO fdr #4 and STG fdr #1) to repair jumper o/p 25-AD-27 12:08 Open LBS 26-AE-06 to repair jumper o/p 25-AD-25 12:43 Closed LBS 26-AE-06 to normalize load STG fdr #1 Today production Loss = 84 Bbls / 30 wells Planned Maintenance | 1
9 | 2020-09-15 18:38 | September | 18:38 | Afternoon | Tuesday | Weekdays | 15 | 2020 | 2020-02-09 13:40 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 13:40 MGT #6 S/U online the unit 17:04. | 1
10 | 2020-09-15 18:53 | September | 18:53 | Afternoon | Tuesday | Weekdays | 15 | 2020 | 2020-02-09 16:30 | 13.8KV 8C FEEDER #5 | Minas | PGT South | Rain and Lightning | Others | - | 8C 13.8Kv VCB fdr #5 T/R 1x. Not checked yet. | 1
| 2020-09-15 18:53 | September | 18:53 | Afternoon | Tuesday | Weekdays | 15 | 2020 | 2020-05-09 09:22 | 13.8KV 8C FEEDER #5 | Minas | PGT South | Rain and Lightning | Others | - | Checked and found 8C OCB fdr #5 T/R 1x, ctr: 538 - 539, R/F: 50P Patrolled the line but found nothing Cause : Others | 1
11 | 2020-09-15 19:14 | September | 19:14 | Night | Tuesday | Weekdays | 15 | 2020 | 2020-02-09 17:14 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 17:14 MGT #10 S/D then offline the unit of S/B. | 1
12 | 2020-09-15 19:40 | September | 19:40 | Night | Tuesday | Weekdays | 15 | 2020 | 2020-02-09 17:25 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Rain and Lightning | Emergency | - | 17:25 Manually open Minas 13.8Kv ACB #2 fdr#3. Requested Operator GS#2 | 1
13 | 2020-09-15 19:40 | September | 19:40 | Night | Tuesday | Weekdays | 15 | 2020 | 2020-02-09 17:36 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Fair | Capasitor Bank | - | C.Duri feeder #9 load dropped 40A (175-135A) Not checked yet. | 1
| 2020-09-15 20:00 | September | 20:00 | Night | Tuesday | Weekdays | 15 | 2020 | 2020-05-09 10:53 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Fair | Capasitor Bank | - | Checked and found RCL 04-6-05 T/R 1x, ctr: 127 - 128, R/F: None Patrolled the line and found broken bushings of cap bank o/p 04-6-14 Cause : Capasitor Bank | 1
14 | 2020-09-16 05:49 | September | 5:49 | Morning | Wednesday | Weekdays | 16 | 2020 | 2020-02-09 18:56 | 13.8KV 8D FEEDER #3 | Minas | PGT South | Rain and Lightning | Emergency | - | 18:56 Manually open 13.8Kv ACB #2 8D fdr#3. Requested Operator GS#2. | 1
15 | 2020-09-16 05:49 | September | 5:49 | Morning | Wednesday | Weekdays | 16 | 2020 | 2020-03-09 01:19 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Fair | Emergency | - | 01:19 Manual Open 3D fdr #4 Emergency request for temporary shut down operation of GS-5 (AFRIANTO) Cause: Emergency | 1
| 2020-09-16 09:32 | September | 9:32 | Morning | Wednesday | Weekdays | 16 | 2020 | 2020-04-09 13:04 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Fair | Emergency | - | 13:40 Closed 3D 13.8KV OCB fdr #4. (Normalized load to GS -5 req. by Jajang). Emergency. | 1
16 | 2020-09-16 15:02 | September | 15:02 | Afternoon | Wednesday | Weekdays | 16 | 2020 | 2020-03-09 01:23 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 01:22 CDGT-5 Offline and then shut down at 01:23 for standby related to reducing load at GS-5 Minas | 1
17 | 2020-09-16 16:01 | September | 16:01 | Afternoon | Wednesday | Weekdays | 16 | 2020 | 2020-03-09 01:43 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Fair | Emergency | - | 01:43 Manual Open 4D fdr #3 Emergency request for temporary shut down operation of GS-5 (AFRIANTO) Cause: Emergency | 1
| 2020-09-16 16:01 | September | 16:01 | Afternoon | Wednesday | Weekdays | 16 | 2020 | 2020-04-09 13:41 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Fair | Emergency | - | 13:41 Closed 13.8KV 4D OCB fdr #3. (Normalized load to GS-5 as per req. Jajang). Emergency. | 1
18 | 2020-09-16 16:26 | September | 16:26 | Afternoon | Wednesday | Weekdays | 16 | 2020 | 2020-03-09 01:50 | 13.8KV 3D FEEDER #3 | Minas | PGT South | Fair | Emergency | - | 01:50 Manual Open 3D fdr #3 Emergency request for temporary shut down operation of GS-5 (AFRIANTO) Cause: Emergency | 1
| 2020-09-16 17:05 | September | 17:05 | Afternoon | Wednesday | Weekdays | 16 | 2020 | 2020-04-09 13:39 | 13.8KV 3D FEEDER #3 | Minas | PGT South | Fair | Emergency | - | 13:39 Closed 13.8KV OCB 3D fdr #3 (Nornalized Load of GS-5 Req. by Jajang) Cause: Emergency. | 1
19 | 2020-09-17 10:23 | September | 10:23 | Morning | Thursday | Weekdays | 17 | 2020 | 2020-03-09 13:18 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Cloudy | Animal | 4 | Rangau Fdr#2 Load Drop 134 A ( 148 - 14A ) Not Checked yet. | 1
| 2020-09-17 16:41 | September | 16:41 | Afternoon | Thursday | Weekdays | 17 | 2020 | 2020-04-09 11:01 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Cloudy | Animal | 4 | Checked and found RCL 23-BD-01 T/R 2x, ctr: 437 - 439, R/F: None Patrolled the line and found death animal (monkey) at TXD Jorang #25 Cause : Animal (monkey) | 1
20 | 2020-09-17 16:41 | September | 16:41 | Afternoon | Thursday | Weekdays | 17 | 2020 | 2020-03-09 16:56 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | - | So.Balam Feeder # 1 Load Drop 90A ( 178 - 88A) Not Checked Yet. | 1
| 2020-09-17 19:08 | September | 19:08 | Night | Thursday | Weekdays | 17 | 2020 | 2020-05-09 09:35 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | - | Checked and found RCL 16-Z-25 T/R 1x, ctr: 141 - 142, R/F: None Patrolled the line but found nothing Cause : Unidentified | 1
21 | 2020-09-18 15:05 | September | 15:05 | Afternoon | Friday | Weekdays | 18 | 2020 | 2020-04-09 18:22 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Cloudy | Unidentified | 74 | New Kotabatak Feeder #2 T/R 1X Not Checked yet. | 1
| 2020-09-18 15:05 | September | 15:05 | Afternoon | Friday | Weekdays | 18 | 2020 | 2020-08-09 11:37 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Cloudy | Unidentified | 74 | Checked and found: NKBKSB-13.8OCB2 T/R, Counter : 99950 - 99951, Relay Flag : 50N Patrolled the line found : Not Found Cause : Unidentified | 1
22 | 2020-09-18 19:17 | September | 19:17 | Night | Friday | Weekdays | 18 | 2020 | 2020-05-09 01:20 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Drizzle | Recloser | 231 | 01:20 4B feeder #1 T/LO. 4B feeder #2 load dropped 32 A (39-7 A). 4B feeder #3 load dropped 110 A (112-2 A). 02:34 Checked and found 4B OCB fdr #1 operate 11 x, ctr: 404 - 415, R/F: 51P Patrolled the line and found RCL 4B-101 T/SO 03:56 Block and manual close 4B OCB fdr #1, OK but trip again after a few second Re-patrol the line and found RCL 4B-101 burned out 04:36 Open LBS 4B-90 04:37 Block and close 4B OCB fdr #1, OK then release the block 12:01 Close LBS 4B-90, OK 12:09 Blocked and close RCL 4B-101, OK then release the block Cause: Recloser (burned out) | 1
23 | 2020-09-18 19:17 | September | 19:17 | Night | Friday | Weekdays | 18 | 2020 | 2020-05-09 06:12 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Cloudy | Unidentified | 0 | Batang GFPC T/R 2x no indication load dropped at any feeders | 1
| 2020-09-18 19:17 | September | 19:17 | Night | Friday | Weekdays | 18 | 2020 | 2020-12-09 06:12 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Cloudy | Unidentified | 0 | Batang GFPC T/R 3x Ctr:1053-1056 R/F:50N. Patrolled the line but found nothing. Cause : Unidentified. | 1
24 | 2020-09-18 20:15 | September | 20:15 | Night | Friday | Weekdays | 18 | 2020 | 2020-05-09 13:58 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | CDGT #5 S/U and then online at 14:14 | 1
25 | 2020-09-18 20:15 | September | 20:15 | Night | Friday | Weekdays | 18 | 2020 | 2020-05-09 19:57 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Rain | Lightning | 75 | Minas ACB feeder #3 T/R 1x, 51P@2, Counter: 174 - 175 Not Patrolled Yet | 1
| 2020-09-19 11:35 | September | 11:35 | Morning | Saturday | Weekends | 19 | 2020 | 2020-12-09 09:57 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Rain | Lightning | 75 | Checked & found Minas fdr#3 T/R 1x Ctr:174-175 R/F51@2. Patrolled the line but found nothing. Cause : Lightning. | 1
26 | 2020-09-19 11:35 | September | 11:35 | Morning | Saturday | Weekends | 19 | 2020 | 2020-05-09 19:57 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Rain | Lightning | 35 | Minas ACB fdr #4 T/R 1x, R/F: 51P @2 @3, counter: 125 - 126 Not Patrolled Yet | 1
| 2020-09-19 14:11 | September | 14:11 | Afternoon | Saturday | Weekends | 19 | 2020 | 2020-12-09 09:57 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Rain | Lightning | 35 | checked & found Minas fdr#4 T/R 1x, Ctr:125 - 126, R/F: 51P @3 @2. Patrolled the line but found nothing. Cause: Lightning. | 1
27 | 2020-09-19 14:11 | September | 14:11 | Afternoon | Saturday | Weekends | 19 | 2020 | 2020-06-09 06:24 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Fair | Lightning | 16 | 06:24 Libo VCB fdr #1 T/R 1x Libo feeder #2 load dropped 6 A (64 - 58 A) Not Checked Yet | 1
| 2020-09-19 17:48 | September | 17:48 | Afternoon | Saturday | Weekends | 19 | 2020 | 2020-12-09 08:24 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Fair | Lightning | 16 | Checked & found Libo VCB fdr#1 T/R 1x Ctr:606-607 R/F:51N. Patrolled the line but found nothing. Cause : Lightning. | 1
28 | 2020-09-20 11:08 | September | 11:08 | Morning | Sunday | Weekends | 20 | 2020 | 2020-06-09 11:00 | MINAS POWER PLANT | Minas | PGT South | Fair |  | - | 11:00 Minas GT # 9 S/U then O/L at 11:22 11:33 Off line and S/D Minas GT # 11 for repair Cross fire tube leakage. | 1
29 | 2020-09-20 17:40 | September | 17:40 | Afternoon | Sunday | Weekends | 20 | 2020 | 2020-06-09 15:07 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Recloser | 6 | 15:07 Recloser 07 U1 19 T/O. ( counter can not be read ) 16:32 Block and closed recloser then release the block Not checked yet. | 1
| 2020-09-20 17:40 | September | 17:40 | Afternoon | Sunday | Weekends | 20 | 2020 | 2020-07-09 17:34 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Recloser | 6 | Checked and found RCL 07-U1-19 TT/SO, ctr: xxx (display error), R/F: None Patrolled the line but found nothing Cause : Recloser | 1
30 | 2020-09-20 17:42 | September | 17:42 | Afternoon | Sunday | Weekends | 20 | 2020 | 2020-06-09 17:50 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 30 | C. Duri 13.8KV ACB fdr #1 T/R 1X ctr:291 (not changed) R/F:51G. (No indication feeder tripped appeared). Not patrolled yet. | 1
| 2020-09-20 17:42 | September | 17:42 | Afternoon | Sunday | Weekends | 20 | 2020 | 2020-12-09 07:50 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 30 | Checked & found Recl. 41-AW-62 Ctr:356-357. Patrolled the line but found nothing. Cause : Unidentified. | 1
31 | 2020-09-20 17:42 | September | 17:42 | Afternoon | Sunday | Weekends | 20 | 2020 | 2020-06-09 19:28 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Others | 24 | 19:28 Pinang fdr #1 load dropped 17 A (89 - 72 A) Pinang Bus Voltage dropped from 13.5 - 12.4 21:42 Checked and found VR Pinang SS at Neutral Position, AUTO Mode Indicator high band is illuminate. 21:45 Manual adjust voltage setting and tapping VR of Pinang SS Last position at Rise 13 (stuck) and on AUTO mode. Cause: Others | 1
32 | 2020-09-20 17:42 | September | 17:42 | Afternoon | Sunday | Weekends | 20 | 2020 | 2020-07-09 10:00 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Fair | Planned Maintenance | 16 | 10:00 Manual open LBS 03-07-03 D/S CD #5 Replace broken p/ins o/p 03-07-12 11:07 Closed LBS 03-07-03. Cause planed maintenance. | 1
33 | 2020-09-20 17:42 | September | 17:42 | Afternoon | Sunday | Weekends | 20 | 2020 | 2020-07-09 18:44 | 5 BRAVO SUBSTATION | Minas | PGT South | Fair | Lightning | 248 | 18:44 115KV 5B GCB #23 and GCB #24 T/O. 5B fdr #6 T/SO. (No power to 5B fdr #1, #2, #3 and #6). 19:15 Manual Open 6D VCB fdr #2 (To maintain level tank at GS-4) 19:20 Manual Open 3D VCB fdr #2 / 4D fdr #4 (To maintain level tank at GS-4) 20:20 Checked and found TXP-1 5B SS was OFF/Shut down - 115 kV GCB #23 5B SS T/O, ctr: 182 - 183, R/F: 51G - 115 kV GCB #24 5B SS T/O, ctr: 673 - 674, R/F: 51G - 6D VCB fdr #6 T/R 1x, ctr: 269 - 270 R/F:51N. 20:25 Manual Open VCB fdr #1, #2, #3, #6 20:34 Manual Close 115 kV GCB #23, OK (TXP-1 re-energize) Checked TXP-1, all on Normal condition 20:37 Manual Close 115 kV GCB #24, OK 20:43 Blocked and manual close 5B VCB fdr #6, OK then release the block 21:05 Blocked and manual close 3D VCB fdr #2, OK then release the block 21:06 Blocked and manual close 6D VCB fdr #2, OK, then release the block 21:29 Blocked and manual close 5B fdr #1, OK then release the block, ctr: 284 21:30 Blocked and manual close 5B fdr #2, OK then release the block, ctr: 358 21:31 Blocked and manual close 5B fdr #3, OK then release the block, ctr: 455 Production loss : GS-6 = 50 Bbls / 10 wells GS-4 = 405 Bbls / 95 wells Not Patrolled Yet. | 1
| 2020-09-20 17:42 | September | 17:42 | Afternoon | Sunday | Weekends | 20 | 2020 | 2020-12-09 08:44 | 5 BRAVO SUBSTATION | Minas | PGT South | Fair | Lightning | 248 | Checked & found 5B fdr#6 T/R 1x Ctr:269-270 R/F: 51N. Patrolled the line but found nothing. Cause : Lightning. | 1
34 | 2020-09-20 17:43 | September | 17:43 | Afternoon | Sunday | Weekends | 20 | 2020 | 2020-08-09 09:26 | PEMATANG MAIN SUBSTATION | Bekasap | PGT North | Fair | Planned Maintenance | 216 | 09:26 Manual Open 13.8KV Rangau OCB fdr #1, --->Closed at 13:26. 09:27 Manual Open 13.8KV Rangau OCB fdr #2, --->Closed at 13:28.. 09:28 Manual Open 44KV Pematang OCB #2, --->Closed at 13:25. (No power to Rangau Substation). The have done: Repair Corrosion cross arm o/p 26-BC-12 and RGU-99. Replace Flash over Suspension o/p RGU-91. Replaced broken LA at Rangau #15. Installed Platform at Jurong #13. Cause: Plan Maintenance. | 1
35 | 2020-09-20 17:43 | September | 17:43 | Afternoon | Sunday | Weekends | 20 | 2020 | 2020-08-09 10:10 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Planned Maintenance | - | 10:10 Manually Open LBS 38-CW-36. Dismantled 1 spen power ling at KB #121. 6 (six) wells off during the JOB. Plan Maintenance. 10:37 Closed LBS | 1
36 | 2020-09-21 01:36 | September | 1:36 | Night | Monday | Weekdays | 21 | 2020 | 2020-08-09 10:29 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Planned Maintenance | 4 | 10:29 Manual open 5B Feeder #7 Install new L/A 11:03 Closed 5B-Fdr#7 , Cancel install L/A welding mechine problem. | 1
37 | 2020-09-21 01:36 | September | 1:36 | Night | Monday | Weekdays | 21 | 2020 | 2020-09-09 23:59 | CPI POWER SYSTEM |  |  |  |  | - | 23:59 CPI Power system was Normal Operation. | 1
38 | 2020-09-21 03:10 | September | 3:10 | Night | Monday | Weekdays | 21 | 2020 | 2020-10-09 01:02 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | - | Central Duri feeder # 16 T/R 1X R/F 51N Phase : 1 and 2 Ctr: 394 - 395 Not checked yet. | 1
| 2020-09-21 09:37 | September | 9:37 | Morning | Monday | Weekdays | 21 | 2020 | 2020-12-09 14:09 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | - | Checked and found: CDRSG-13.8ACB28 T/R, Counter : 394 - 395, Relay Flag : 51N. Patrolled the line found : No Finding Cause : Unidentified | 1
39 | 2020-09-21 15:18 | September | 15:18 | Afternoon | Monday | Weekdays | 21 | 2020 | 2020-10-09 08:48 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified (L/A) | 42 | Sintong 13.8Kv OCB fdr#1 T/R 1x. Sintong GFPC T/R. Sintong feeder #2 load dropped 181A (258-77A). Not checked yet. | 1
| 2020-09-21 15:18 | September | 15:18 | Afternoon | Monday | Weekdays | 21 | 2020 | 2020-11-09 08:48 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified (L/A) | 42 | Checked & found Sintong VCB fdr#1 T/R 1x Ctr:435-436 R/F:51@1. Patrolled and found @1 broken LA o/p 25 AD 25 at Seruni GS. Cause: Lightning. | 1
40 | 2020-09-21 15:18 | September | 15:18 | Afternoon | Monday | Weekdays | 21 | 2020 | 2020-10-09 09:44 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Cloudy | Unidentified | - | 09:44 Minas 13.8Kv ACB #18 fdr #6 T/O. 09:46 Blocked & closed Minas feeder #6, 10:58 Checked & found recloser 7E-67A T/O, Ctr : 103-104. 11:00 Blocked & closed recloser 7E-67A, the released the block. Not patrolled yet. | 1
| 2020-09-21 15:18 | September | 15:18 | Afternoon | Monday | Weekdays | 21 | 2020 | 15-09-2020 17:07 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Cloudy | Unidentified | - | Checked and found MNS ACB fdr #6 T/O, ctr: 206 - 207, R/F: None Patrolled the line but found nothing Cause : Unidentified | 1
41 | 2020-09-21 15:19 | September | 15:19 | Afternoon | Monday | Weekdays | 21 | 2020 | 2020-10-09 17:40 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Lightning Arrester | - | C.Duri feeder #1 load dropped 56A (73-18A). Not checked yet. | 1
| 2020-09-21 15:19 | September | 15:19 | Afternoon | Monday | Weekdays | 21 | 2020 | 2020-12-09 14:52 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Lightning Arrester | - | Checked and found: 5441-R.41-AW-62 T/R, Counter : 357 - 358, Relay Flag : NONE. Patrolled the line found : LA broken Cause : Lightning Arrester | 1
42 | 2020-09-21 15:19 | September | 15:19 | Afternoon | Monday | Weekdays | 21 | 2020 | 2020-11-09 09:55 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Fair | Planned Maintenance | 62 | 09:55 Manually open 8C feeder #6. Replaced recloser o/p 8C-94. 11:50 Blocked &closed 8C feeder #6, then release block. Cause : Plain maintenance. | 1
43 | 2020-09-21 15:19 | September | 15:19 | Afternoon | Monday | Weekdays | 21 | 2020 | 2020-11-09 14:47 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 14:47 S/U MGT #5 then online the unit at 15:10. | 1
44 | 2020-09-21 15:40 | September | 15:40 | Afternoon | Monday | Weekdays | 21 | 2020 | 2020-11-09 15:18 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 15:18 Off line MGT #3 then S/D the unit for S/B. | 1
45 | 2020-09-21 16:15 | September | 16:15 | Afternoon | Monday | Weekdays | 21 | 2020 | 2020-11-09 17:42 | 4.16KV SO RUMBAI FEEDER #2 | Rumbai | PGT South | Lightning | Unidentified | - | 17:42 SO. Rumbai 4.16Kv VCB fdr #2 T/R. 18:15 Checked & found SO. Rumbai feeder #2 T/O Ctr: 799 R/f 51 @2. 18:19 Blocked & closed SO.Rumbai feeder #2 OK, the released block. Cause :Not patrolled yet. | 1
| 2020-09-21 16:15 | September | 16:15 | Afternoon | Monday | Weekdays | 21 | 2020 | 13-09-2020 07:42 | 4.16KV SO RUMBAI FEEDER #2 | Rumbai | PGT South | Lightning | Unidentified | - | Patrolled the line but found nothing. Cause : Unidentified. | 1
46 | 2020-09-21 19:54 | September | 19:54 | Night | Monday | Weekdays | 21 | 2020 | 2020-11-09 20:13 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Rain and Lightning | Lightning | 50 | 8C Feeder #6 T\R 1X 8C Feeder #5 Load Drop 143A ( 149-6A ) 8C Feeder #4 Load Drop 219A ( 235-16A ) Not checked yet. | 1
| 2020-09-21 19:54 | September | 19:54 | Night | Monday | Weekdays | 21 | 2020 | 15-09-2020 09:04 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Rain and Lightning | Lightning | 50 | Checked and found: 8CSB-13.8VCB6 T/R, Counter : 644 - 645, Relay Flag : 51 Patrolled the line found : Broken Dead end @1,2 Cause : Lightning | 1
47 | 2020-09-22 07:03 | September | 7:03 | Morning | Tuesday | Weekdays | 22 | 2020 | 2020-12-09 02:41 | 13.8KV CENTRAL DURI FEEDER #8 | Duri | PGT North | Fair | Recloser - Ligtning Arrester Recloser | 6 | 02:41 C.Duri fdr#8 Load dropped 7A (172-166A). 08:02 It was reported no power at CGS#4. 09:00 Checked & found Recl. 3-5-32 T/LO Ctr:238-242. Patrolled the line & found @1 Broken LA at Recl. 03-5-32. 11:19 Blocked & Closed Recl. 03-5-32, then release the block. Cause: Lightning Arrester. | 1
48 | 2020-09-22 07:03 | September | 7:03 | Morning | Tuesday | Weekdays | 22 | 2020 | 2020-12-09 20:47 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Fair | Unidentified | - | Bekasap Feeder #3 T/R 1X Not Checked yet. | 1
| 2020-09-22 07:19 | September | 7:19 | Morning | Tuesday | Weekdays | 22 | 2020 | 13-09-2020 16:32 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Fair | Unidentified | - | Checked and found: BKSMSB-13.8VCB3 T/R, Counter : 99508 - 99509, Relay Flag : 51N. Patrolled the line found : Nothing Found Cause : Unidentified | 1
49 | 2020-09-22 07:19 | September | 7:19 | Morning | Tuesday | Weekdays | 22 | 2020 | 2020-09-14 05:50 | 115KV NELLA SW. STA / PINANG LINE | Bangko-Balam | PGT North | Fair | Voltage regulator failure | 218 | 05:50 Nella/Pinang 115KV GCB #27 T/O. (No power at Pinang Substation). 09:30 Checked & found 115Kv Nella GCB#27 T/O Ctr:256/257 R/F 86T, 51@2@3. 09:45 Opened Pinang VCB fdr#1, then closed at 10:58. 10:43 Closed 115Kv Nella GCB#27. Cause: Under investigation. 20:23 Nella 115kv GCB#27 T/O Power to Pinang Substation. 23:59 Checked & found 115Kv Nella GCB#27 T/O Ctr:257/258 R/F86T. ( No power at Pinang substation). Continued on Sept 15. | 1
| 2020-09-22 07:49 | September | 7:49 | Morning | Tuesday | Weekdays | 22 | 2020 | 2020-09-15 00:25 | 115KV NELLA SW. STA / PINANG LINE | Bangko-Balam | PGT North | Fair | Voltage regulator failure | 218 | 00:25 Opened Pinang OCB feeder # 1. 13:37 Transformer Turn Ratio test the Voltage Regulator found : / Phase #1 = 0.9104. / Phase #2 = 0.9104. / Phase #3 = 0.9103. Isolation test the Voltage Regulator found : / Source to Ground = 1.8 Giga ohm. / Load to Ground = 1.2 Giga ohm. And then isolate Voltage Regulator. VR will be replaced tomorrow.” 13:39 Closed 115Kv Nella GCB#27 ( Energize Power Transformer Pinang ). 13:43 Blocked and closed Pinang OCB feeder #1 and then released the block. Power TX and Pinang feeder #1 are energized without VR to supply 3 wells as booster to prevent congeal, 24 wells are still shutdown. Cause: Voltage Regulator Failure. | 1
| 2020-09-22 07:49 | September | 7:49 | Morning | Tuesday | Weekdays | 22 | 2020 | 2020-09-16 15:02 | 115KV NELLA SW. STA / PINANG LINE | Bangko-Balam | PGT North | Fair | Voltage regulator failure | 218 | 15:02 Manually Opened Pinang VCB feeder #1. closed at 19:08 15:03 Manually Opened 115 KV GCB #27 Nella. closed at 18:58. Due to replaced Voltage Regulator at Pinang Substation. 18:58 Manually closed 115 KV GCB #27 Nella //> Success. 19:08 Manually blocked and closed Pinang VCB feeder #1 and released the block. Pinang Substation back to normal condition. Cause: Voltage Regulator Failure. | 1
50 | 2020-09-22 07:51 | September | 7:51 | Morning | Tuesday | Weekdays | 22 | 2020 | 2020-09-14 17:39 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Animal | 385 | 17:39 C.Duri fdr#1 Load dropped 63A (74/11A). 20:05 Checked and found Recl. 38/AS/09 T/LO ctr:446/452 R/F: 51N, 51@1. 21:50 Open LBS 37/AQ/08, ////>Closed at 00:41. 21:52 Blocked and closed Recl. 38/AS/09, Ok. Patrolled the line and found Dead Monkey o/p 37/AO/32 (Puncak #19), then removed dead Monkey. Cause: Animal (Monkey). | 1
| 2020-09-22 07:51 | September | 7:51 | Morning | Tuesday | Weekdays | 22 | 2020 | 2020-09-15 09:38 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Animal | 385 | Checked and found: 5441/R.38AS09 T/LO, Counter : 446 / 452, Relay Flag : 51N Patrolled the line found : ditemukan monyet mati di pin phase 1 tiang 37/AO/32 Cause : Animal | 1
51 | 2020-09-22 11:06 | September | 11:06 | Morning | Tuesday | Weekdays | 22 | 2020 | 2020-09-14 18:34 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Cloudy | Unidentified | 61 | Pematang VCB fdr#2 T/R 1x. Pematang fdr#1 Load dropped 175A (206/31A). Not checked yet. | 1
| 2020-09-22 17:54 | September | 17:54 | Afternoon | Tuesday | Weekdays | 22 | 2020 | 2020-09-15 17:23 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Cloudy | Unidentified | 61 | Checked and found PMT OCB fdr #2 T/R 1x, ctr: 571 / 572, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
52 | 2020-09-23 13:26 | September | 13:26 | Afternoon | Wednesday | Weekdays | 23 | 2020 | 2020-09-14 19:07 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | 19:07 S.Balam feeder #1 load dropped 110A (155/45A). 20:30 Checked & found Recloser 16/Z/25 T/R 1x. Not patrolled yet. | 1
53 | 2020-09-23 13:26 | September | 13:26 | Afternoon | Wednesday | Weekdays | 23 | 2020 | 2020-09-14 19:42 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Tree | 43 | Batang Feeder # 3 T/R 8 X and GFPC T/R 8X Not checked yet. | 1
| 2020-09-23 17:00 | September | 17:00 | Afternoon | Wednesday | Weekdays | 23 | 2020 | 2020-09-16 07:44 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Tree | 43 | Checked and found BTG VCB fdr #3 T/R 7x, ctr: 411 / 418, R/F: 51N, 51P @3 Patrolled the line and found high palm trees at Candi field Cause : Tree | 1
54 | 2020-09-23 18:13 | September | 18:13 | Afternoon | Wednesday | Weekdays | 23 | 2020 | 2020-09-15 18:38 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Fair | Tree | 448 | 18:38 MGT #5 Trip. Minas 13.8Kv VCB #2 fdr #3 T/LO ctr:80175/80177 R/F: 51@1, @2 and @3. Minas 13.8Kv VCB #1 fdr #4 T/LO ctr:126/129 R/F: 51N. Minas feeder #1 load dropped 120A (174/54A). Minas feeder #2 load dropped 22A (102/80A). Minas feeder #6 load dropped 44A (111/68A). 19:14 Started Up Minas GT #5 and On line at 19:36. 21:43 Patrolled the line and found Tree, Palm branch and Bamboo touch power line under Minas fdr #3 and 4 o/p: n/n, then removed it. 23:19 Blocked and closed Minas fdr #3, Ok then released block. 23:20 Blocked and closed Minas fdr #4, Ok then released block. Cause: Tree. | 1
55 | 2020-09-23 18:13 | September | 18:13 | Afternoon | Wednesday | Weekdays | 23 | 2020 | 2020-09-15 18:38 | 4.16KV NO RUMBAI FEEDER #3 | Rumbai | PGT South | Rain and Lightning | Powerline / Broken Lightning Aresster Line. | - | 18:38 S.Rumbai VCB #3 T/O. 19:23 Checked & found R/f 51N. Blocked & closed trip again. 20:15 Open LBS 3RF/7. 21:55 Block & closed OK, normalized block. Not patrolled yet. | 1
| 2020-09-23 19:56 | September | 19:56 | Night | Wednesday | Weekdays | 23 | 2020 | 2020-09-16 11:50 | 4.16KV NO RUMBAI FEEDER #3 | Rumbai | PGT South | Rain and Lightning | Powerline / Broken Lightning Aresster Line. | - | Patrolled the line found @2 broken Lightning Arrester on pole 3/RG/23. Cause: Lightning Arrester. | 1
56 | 2020-09-23 19:56 | September | 19:56 | Night | Wednesday | Weekdays | 23 | 2020 | 2020-09-15 18:53 | 13.8KV 8C FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 13 | 8C 13.8Kv VCB fdr #2 T/R. Not checked yet. | 1
| 2020-09-23 20:24 | September | 20:24 | Night | Wednesday | Weekdays | 23 | 2020 | 2020-09-17 10:11 | 13.8KV 8C FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 13 | Checked and found: 8CSB/13.8VCB2 T/R, Counter : 578 / 579, Relay Flag : 51. Patrol led the line found: not found Cause : Lightning | 1
57 | 2020-09-23 20:24 | September | 20:24 | Night | Wednesday | Weekdays | 23 | 2020 | 2020-09-15 19:14 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 19:14 S/U MGT #5 then online the unit 19:36. | 1
58 | 2020-09-23 22:02 | September | 22:02 | Night | Wednesday | Weekdays | 23 | 2020 | 2020-09-15 19:40 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Tree | 52 | 19:40 Batang 13.8Kv VCB fdr #3 T/R 4x. Batang GFPC T/R 4x. 19:52 Batang fdr #3 T/LO. 21:59 Checked and found Batang fdr #3 T/LO ctr:41/421 R/F: 51N, 51@2, @3. Patrolled the line and found Palm branch touch power line o/p: NN (Between Pemburu#10 to Pemburu# 22) Removed Palm branch from power line. 01:15 Blocked and closed Batang fdr #3, OK then released the block. Cause: Tree (Palm Branch). | 1
| 2020-09-23 22:02 | September | 22:02 | Night | Wednesday | Weekdays | 23 | 2020 | 2020-09-16 07:40 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Tree | 52 | Checked and found: BTGSB/13.8OCB3 T/LO, Counter : 419 / 421, Relay Flag : 51N Patrolled the line found : Relay Flag 51 N and 51 Phase B dan 51C pohon sawit menyentoh line di candi Cause : Tree | 1
59 | 2020-09-24 07:48 | September | 7:48 | Morning | Thursday | Weekdays | 24 | 2020 | 2020-09-15 20:00 | 44KV PEMATANG MAIN / RANGAU LINE | Bekasap | PGT North | Rain and Lightning | Unidentified | 179 | 20:00 Pematang Main 44Kv line OCB #2 T/R 1X. Rangau 13.8Kv ACB fdr#1 load dropped 59A (59/0A) Rangau 13.8Kv ACB fdr#2 load dropped 147A (147/0A) Pematang feeder #1 load dropped 169A (204/35A). Pematang feeder #2 load dropped 19A (109/90A). Petani feeder #1 load dropped 138A (210/72A). Petani feeder #2 load dropped 18A (71/53A). 20:46 load Rangau fdr #2 still 0A. 22:00 Checked and found Recloser 23/BD/01 T/SO (ctrl malfunction) ctr:239/240. Patrolled the line but found nothing. 23:35 Blocked and closed Recloser 23/BD/01, Ok then released block. Cause: Unidentified. | 1
60 | 2020-09-24 07:48 | September | 7:48 | Morning | Thursday | Weekdays | 24 | 2020 | 2020-09-16 05:49 | 13.8KV 8D FEEDER #1 | Minas | PGT South | Fair | Lightning | 39 | 8Delta feeder #1 T/R 1X Not Checked yet. | 1
| 2020-09-24 10:05 | September | 10:05 | Morning | Thursday | Weekdays | 24 | 2020 | 2020-09-17 10:20 | 13.8KV 8D FEEDER #1 | Minas | PGT South | Fair | Lightning | 39 | Checked and found: 8DSB/13.8OCB1 T/R,Counter : 353 / 354, Relay Flag : 51 Patrolled the line found : Not Found Cause : Lightning | 1
61 | 2020-09-24 13:15 | September | 13:15 | Afternoon | Thursday | Weekdays | 24 | 2020 | 2020-09-16 09:32 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Planned Maintenance | 217 | 09:38 Manual Open RCL 41/AW/62, closed at 11:33 MTCE team to replace insulator o/p 40 AW/20 and 41/AW/15 Planned Maintenance | 1
62 | 2020-09-24 15:25 | September | 15:25 | Afternoon | Thursday | Weekdays | 24 | 2020 | 2020-09-16 15:02 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 174 | 15:02 Manual Open Pinang VCB fdr #1, closed at 19:08 15:03 Manual Open 115 KV GCB #27 Nella, closed at 18:58 MTCE team to repair/replace control of VR Pinang Subst. Planned Maintenance | 1
63 | 2020-09-24 17:03 | September | 17:03 | Afternoon | Thursday | Weekdays | 24 | 2020 | 2020-09-16 16:01 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | 16:01 ND VCB fdr #1 T/O 1x (block for BMS #03A) 16:04 Confirmed to BMS #03, condition OK/Normal 16:07 Manual Close ND VCB fdr #1, OK, then release the blcok Not Checked Yet | 1
| 2020-09-24 17:20 | September | 17:20 | Afternoon | Thursday | Weekdays | 24 | 2020 | 2020-09-17 07:13 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found ND fdr #1 Operate 1x, ctr: 348 / 349, R/F: 51N Patrolled the line and found broken LA @3 on NN pole Cause : Unidentified | 1
64 | 2020-09-25 03:30 | September | 3:30 | Night | Friday | Weekdays | 25 | 2020 | 2020-09-16 16:26 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 107 | 10:50 it was reported broken F/O cable at pole 44 kV line to Rangau Checked and found broken static wire at pole RGU/15 and broken suspension insulator o/p RGU/13 16:26 Manual Open RGU VCB fdr #2, closed at 18:29 16:27 Manual Open RGU VCB fdr #1, closed at 18:28 16:28 Manual Open 44kV GCB #2 PMTM, closed at 18:27 for MTCE team to isolate broken static wire o/p RGU/10 through to RGU/15 and repair broken suspension insulator o/p RGU/13 Planned Maintenance | 1
65 | 2020-09-25 05:50 | September | 5:50 | Morning | Friday | Weekdays | 25 | 2020 | 2020-09-16 17:05 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 194 | 17:05 Nella VCB fdr #1 T/O (on block for Rig HPS #08 at BKO #96) Confirmed to RIG HPS #08, condition OK/Normal 17:48 Patrolled the line but found nothing 17:49 Manual Close Nella VCB fdr #1, OK (still block for Rig HPS #08 Not Patrolled Yet | 1
66 | 2020-09-25 09:50 | September | 9:50 | Morning | Friday | Weekdays | 25 | 2020 | 2020-09-17 10:23 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Planned Maintenance | 12 | 10:23 Manual Open LBS 4C/138 (part load 5B fdr #7 are down) for mtce team to re/connect jumper o/p 4C/20 11:16 Manual Close lBS 4C/14 (5B fdr #7 back to normal) Planned Maintenance | 1
67 | 2020-09-25 09:50 | September | 9:50 | Morning | Friday | Weekdays | 25 | 2020 | 2020-09-17 16:41 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 31 | 16:41 Ketigul VCB fdr #2 T/R 1x Ketigul fdr #1 load dropped 40 A (133 / 93 A) Ketigul fdr #3 load dropped 8 A (33 / 25 A) Not Checked Yet | 1
| 2020-09-25 10:37 | September | 10:37 | Morning | Friday | Weekdays | 25 | 2020 | 2020-09-19 08:03 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 31 | Checked and found KTGL VCB fdr #2 T/R 1x, ctr: 406 / 407, R/F: 51N Patrolled the line and found broken dead end @3 o/p 29/AM/02 Cause : Dead End Insulator | 1
68 | 2020-09-25 10:37 | September | 10:37 | Morning | Friday | Weekdays | 25 | 2020 | 2020-09-17 19:08 | 13.8KV PETAPAHAN FEEDER #3 | Petko | PGT South | Fair | Emergency | - | 19:08 Manual Open PTP VCB fdr #3, closed at 19:52. Manual Open PTP VCB fdr #4, closed at 19:52. Emergency request by PTP GS due to HPS WIP down Cause: Emergency | 1
69 | 2020-09-25 12:07 | September | 12:07 | Afternoon | Friday | Weekdays | 25 | 2020 | 2020-09-18 15:05 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 34 | KETIGUL VCB feeder #2 T/R 1x Not Checked Yet | 1
| 2020-09-25 12:07 | September | 12:07 | Afternoon | Friday | Weekdays | 25 | 2020 | 2020-09-19 08:04 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 34 | Checked and found KTGL VCB fdr #2 T/R 1x, ctr: 407 / 408, R/F: 51N Patrolled the line and found broken dead end @3 o/p 29/AM/02 Cause : Dead End Insulator | 1
70 | 2020-09-25 12:30 | September | 12:30 | Afternoon | Friday | Weekdays | 25 | 2020 | 2020-09-18 19:17 | 13.8KV 3D FEEDER #6 | Minas | PGT South | Rain and Lightning | Lightning | 61 | 19:17 3D OCB fdr#6 T/R 1x. 3D GFPC Tx/2 T/O Ctr:564/565 R/F:51@1. 3D fdr#7 Load dropped 144A (153/9A). 3D fdr#8 Load dropped 59A (60/10A). 20:40 Closed 3D GFPC Tx/2, but failed. 23:00 By pass 3D GFPC Tx/2. Cause: Not checked yet. | 1
| 2020-09-25 12:30 | September | 12:30 | Afternoon | Friday | Weekdays | 25 | 2020 | 2020-09-23 13:07 | 13.8KV 3D FEEDER #6 | Minas | PGT South | Rain and Lightning | Lightning | 61 | Checked And Found 3DSB OCB6 Fdr #8 Ctr 312/314, R/F 50 Patrolled The Line On 21/Sep/2020 But Found Nothing Cause: Lightning | 1
71 | 2020-09-25 12:42 | September | 12:42 | Afternoon | Friday | Weekdays | 25 | 2020 | 2020-09-18 19:17 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 30 | 19:17 3D OCB fdr#4 T/LO. 3D fdr#2 Load dropped 103A (148/45A). 3D fdr#3 Load dropped 51A (73/22A). 20:40 Checked & found 3D OCB fdr#4 T/LO6/133 R/F:51@2,50@2@3. Patrolled the line but found nothing. 21:36 Blocked & Closed 3D OCB fdr#4, then release the block. Cause: lightning | 1
72 | 2020-09-25 12:42 | September | 12:42 | Afternoon | Friday | Weekdays | 25 | 2020 | 2020-09-18 20:15 | 4.16KV NO RUMBAI FEEDER #2 | Rumbai | PGT South | Rain and Lightning | Unidentified | - | 4.16KV NO RUMBAI FEEDER #2. Not checked yet. | 1
| 2020-09-25 12:51 | September | 12:51 | Afternoon | Friday | Weekdays | 25 | 2020 | 2020-09-23 09:09 | 4.16KV NO RUMBAI FEEDER #2 | Rumbai | PGT South | Rain and Lightning | Unidentified | - | Checked And Found NRBSB/4.16VCB2 Fdr #8 Ctr 336/337, R/F 51 Patrolled The Line On 21/Sep/2020 And Found Dahan Hampir Menyentuh Power Line Cause: Unidentified | 1
73 | 2020-09-25 13:42 | September | 13:42 | Afternoon | Friday | Weekdays | 25 | 2020 | 2020-09-19 11:35 | 13.8KV NORTH DURI FEEDER #9 | Duri | PGT North | Fair | Unidentified | 9 | 14:11 It was reported no power at road 11/H5/XX d/s ND fdr#9. 12:12 Check and found Rec. 11/H5/03 T/SO. 12:27 Patrolled the line and found nothing. 12:31 Blocked and manual close Rec. 11/H5/03, then released the block. Cause : Not Checked Yet | 1
| 2020-09-25 13:42 | September | 13:42 | Afternoon | Friday | Weekdays | 25 | 2020 | 2020-09-22 07:22 | 13.8KV NORTH DURI FEEDER #9 | Duri | PGT North | Fair | Unidentified | 9 | Checked and found RCL 11/H3/03 T/SO, counter: 195 / 197, R/F: None Patrolled the line but found nothing Cause : Unidentified | 1
74 | 2020-09-26 06:39 | September | 6:39 | Morning | Saturday | Weekends | 26 | 2020 | 2020-09-19 14:11 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Unidentified | 5 | 14:11 It was reported no power at road 07/U1/XX d/s DF fdr #2. 14:30 Checked and found Rec. 07/U1/19 T/SO (display blur) 14:45 Patrolled the line and found nothing. 14:56 Blocked and manual close Rec. 07/U1/19, then released the block. Cause : Not Checked Yet. | 1
| 2020-09-26 06:39 | September | 6:39 | Morning | Saturday | Weekends | 26 | 2020 | 2020-09-22 07:24 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Unidentified | 5 | Patrolled the line but found nothing Cause : Unidentified | 1
75 | 2020-09-26 09:22 | September | 9:22 | Morning | Saturday | Weekends | 26 | 2020 | 2020-09-19 17:48 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Fair | Tree | - | 17:48 It was reported no power at Facility New NDP (3D fdr#2). 20:20 Checke3d & found Recl 2F/11 T/LO Ctr:649/652 (3D fdr#2). Patrolled the line & found Danger trees Between Pole 2FJ/06 / 2FL/07. Blocked & closed Recl. 2F/11, then release the block. Cause: Tree. | 1
76 | 2020-09-26 17:03 | September | 17:03 | Afternoon | Saturday | Weekends | 26 | 2020 | 2020-09-20 11:08 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 33 | Nella fdr #2 T/R 1x. Not Checked Yet. | 1
77 | 2020-09-26 17:30 | September | 17:30 | Afternoon | Saturday | Weekends | 26 | 2020 | 2020-09-20 17:40 | 13.8KV 4D FEEDER #4 | Minas | PGT South | Rain and Lightning | Unidentified | 1 | 4D fdr #4 load dropped 56 A (75 / 19 A) Not Checked Yet | 1
| 2020-09-26 20:15 | September | 20:15 | Night | Saturday | Weekends | 26 | 2020 | 2020-09-23 09:19 | 13.8KV 4D FEEDER #4 | Minas | PGT South | Rain and Lightning | Unidentified | 1 | Checked And Found 5442/R.4D51A Fdr #8 Ctr 107/108, Patrolled The Line On 22/Sep/2020 But Found Nothing Cause: Unidentified | 1
78 | 2020-09-26 20:38 | September | 20:38 | Night | Saturday | Weekends | 26 | 2020 | 2020-09-20 17:42 | 13.8KV 5B FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | 20 | 5B VCB fdr #1 T/R 1x 5B fdr #4 load dropped 46 A (55 / 9 A) 5B fdr #5 load dropped 7 A (12 / 5 A) 5B fdr #7 load dropped 14 A (17 / 3 A) Not Checked Yet | 1
| 2020-09-26 20:38 | September | 20:38 | Night | Saturday | Weekends | 26 | 2020 | 2020-09-23 10:10 | 13.8KV 5B FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | 20 | Checked And Found 5BSB OCB1 Fdr #8 Ctr 284/285, R/F 51 Patrolled The Line On 21/Sep/2020 And Found Flash Over Dead End Insulator On Phase @2,3, Pole 5B/04 Cause: Lightning | 1
79 | 2020-09-27 23:59 | September | 23:59 | Night | Sunday | Weekends | 27 | 2020 | 2020-09-20 17:42 | 13.8KV 5B FEEDER #8 | Minas | PGT South | Rain and Lightning | Lightning | 0 | 5B VCB fdr #8 T/R 1x Not Checked Yet | 1
| 2020-09-29 23:59 | September | 23:59 | Night | Tuesday | Weekdays | 29 | 2020 | 2020-09-23 09:56 | 13.8KV 5B FEEDER #8 | Minas | PGT South | Rain and Lightning | Lightning | 0 | Checked And Found 5BSB OCB8 Fdr #8 Ctr 49/50, R/F 51 Patrolled The Line On 21/Sep/2020 And Found Broken La On Phase @2 Pole Area Gs Iv Cause: Lightning | 1
80 | 2020-09-29 06:40 | September | 6:40 | Morning | Tuesday | Weekdays | 29 | 2020 | 2020-09-20 17:42 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Unidentified | 8 | 3D OCB fdr #2 T/R 1x 3D fdr #4 load dropped 46 A (155 / 119 A) Not Checked Yet | 1
| 2020-09-29 15:17 | September | 15:17 | Afternoon | Tuesday | Weekdays | 29 | 2020 | 2020-09-23 10:11 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Unidentified | 8 | Checked And Found 3DSB OCB2 Fdr #8 Ctr 391/392, Patrolled The Line On 22/Sep/2020 And Found Hlc Broken (Lepas) On Pole 4D/30 Cause: Unidentified | 1
81 | 2020-09-29 15:17 | September | 15:17 | Afternoon | Tuesday | Weekdays | 29 | 2020 | 2020-09-20 17:43 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Rain and Lightning | Lightning Arrester | 0 | DCM VCB fdr #2 (VCB/30) T/R 1x Not Checked Yet | 1
| 2020-09-30 09:34 | September | 9:34 | Morning | Wednesday | Weekdays | 30 | 2020 | 2020-09-21 14:54 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Rain and Lightning | Lightning Arrester | 0 | checked and found: DCSG/13.8ACB30 T/R, Counter : 132 / 133, Relay Flag : 51N Patrolled the line found : jumper LA putus Cause : Lightning Arrester | 1
82 | 2020-09-30 12:00 | September | 12:00 | Afternoon | Wednesday | Weekdays | 30 | 2020 | 2020-09-21 01:36 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Cloudy | Unidentified | 38 | 01:36 C.Duri ACB fdr#14 Load dropped 90A (156/66A). 03:20 Checked & found Recl. 06/P8/02 T/SO Ctr:300/301 R/F:51N. 03:39 Blocked & closed Recl. 06/P8/02, then release the block. Not patrolled yet. | 1
| 2020-09-30 14:18 | September | 14:18 | Afternoon | Wednesday | Weekdays | 30 | 2020 | 2020-09-21 14:58 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Cloudy | Unidentified | 38 | Checked and found RCL06/P8/02 T/SO, Counter : 300 / 301, Relay Flag : 51N Patrolled the line found : BROKEN PT RECLOSER. Checked recloser and PT by maintenance and all found Normal Cause : Unidentified | 1
83 | 2020-09-30 14:18 | September | 14:18 | Afternoon | Wednesday | Weekdays | 30 | 2020 | 2020-09-21 03:10 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Cloudy | Unidentified | 0 | 03:10 Darling VCB fdr#7 T/LO. 04:00 Checked & found Darling VCB fdr#7 T/LO Ctr:194/199 R/F:51@1@2. 05:35 Patrolled the line but found nothing. 05:46 Blocked & closed Darling VCB fdr#7, then release the block. Cause: Unidentified. | 1
84 | 2019-11-13 20:07 | November | 20:07 | Night | Wednesday | Weekdays | 13 | 2019 | 2020-09-21 09:37 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 36 | 09:37 Manual Open RCL 23/W/12 MTCE team to c/o LA on pole 23/W/26; 23/W/22A and 23/W/15 11:21 Manual Close RCL 23/W/12, OK Planned Maintenance | 1
85 | 2019-11-13 21:16 | November | 21:16 | Night | Wednesday | Weekdays | 13 | 2019 | 2020-09-21 15:18 | 13.8KV 6D FEEDER #6 | Minas | PGT South | Rain and Lightning | Unidentified | 0 | 6D fdr #6 T/R 1x Not Checked Yet | 1
| 2019-11-13 21:16 | November | 21:16 | Night | Wednesday | Weekdays | 13 | 2019 | 2020-09-25 07:51 | 13.8KV 6D FEEDER #6 | Minas | PGT South | Rain and Lightning | Unidentified | 0 | Checked and found: 6D OCB fdr #6 T/R, Counter : 614 / 615, Relay Flag : 50. Patrolled the line found : Not Found Cause : Unidentified | 1
86 | 2019-11-13 21:16 | November | 21:16 | Night | Wednesday | Weekdays | 13 | 2019 | 2020-09-21 15:18 | 13.8KV 6D FEEDER #3 | Minas | PGT South | Rain and Lightning | Lightning | 0 | 6D VCB fdr #3 T/R 1x Not Checked Yet | 1
| 2019-11-13 21:16 | November | 21:16 | Night | Wednesday | Weekdays | 13 | 2019 | 2020-09-25 07:47 | 13.8KV 6D FEEDER #3 | Minas | PGT South | Rain and Lightning | Lightning | 0 | Checked and found: 6D OCB fdr #3 T/R, Counter : 217 / 217, Relay Flag : 50. Patrolled the line found : Flash over Dead end insulator o/p 6D/191 Cause : Lightning | 1
87 | 2019-11-13 23:36 | November | 23:36 | Night | Wednesday | Weekdays | 13 | 2019 | 2020-09-21 15:19 | 13.8KV 5B FEEDER #3 | Minas | PGT South | Rain and Lightning | Lightning | 6 | 5B VCB fdr #3 T/R 1x Not Checked Yet | 1
| 2019-11-13 23:36 | November | 23:36 | Night | Wednesday | Weekdays | 13 | 2019 | 2020-09-25 07:54 | 13.8KV 5B FEEDER #3 | Minas | PGT South | Rain and Lightning | Lightning | 6 | Checked and found: 5B OCB fdr #3 T/R, Counter : 456 / 457, Relay Flag : 50. Patrolled the line found : Broken Deadend phase 3 o/p 4C/10 Cause : Lightning | 1
88 | 2019-11-14 03:26 | November | 3:26 | Night | Thursday | Weekdays | 14 | 2019 | 2020-09-21 15:19 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Rain and Lightning | Unidentified | 21 | 4D VCB fdr #3 T/R 1x Not Checked Yet | 1
| 2019-11-14 03:26 | November | 3:26 | Night | Thursday | Weekdays | 14 | 2019 | 2020-09-25 07:55 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Rain and Lightning | Unidentified | 21 | Checked and found: 4D OCB fdr #3 T/R, Counter : 306 / 307, Relay Flag : 51. Patrolled the line found : Not Found Cause : Unidentified | 1
89 | 2019-11-14 11:02 | November | 11:02 | Morning | Thursday | Weekdays | 14 | 2019 | 2020-09-21 15:40 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Cloudy and Lightning | Unidentified | 7 | 15:40 It was reported no power along road 07/U1/xx (no load drop at DSC) load at DF fdr #1 still 139 A (no load dropped) 16:50 Checked and found RCL 07/U1/19 T/O (on block for WKS clean up canals) 17:07 Patrolled the line completed but found nothing 17:10 Manual close the RCL and then release the block. Cause: Unidentified | 1
90 | 2019-11-14 19:15 | November | 19:15 | Night | Thursday | Weekdays | 14 | 2019 | 2020-09-21 16:15 | 13.8KV MBL SUBSTATION 1 DURI FEEDER #2 | Duri | PGT North | Rain | Unidentified | 78 | 16:15 MSU fdr #2 (BKS Main fdr #2) dropped 162 A (254 / 92 A) Not Checked Yet | 1
| 2019-11-15 03:36 | November | 3:36 | Night | Friday | Weekdays | 15 | 2019 | 2020-09-22 16:22 | 13.8KV MBL SUBSTATION 1 DURI FEEDER #2 | Duri | PGT North | Rain | Unidentified | 78 | Checked And Found RCL 38 BD 39 Fdr #8 Ctr 0/0, Patrolled The Line On 22/Sep/2020 And Found Control Recloser Error Cause: Unidentified | 1
91 | 2019-11-15 03:36 | November | 3:36 | Night | Friday | Weekdays | 15 | 2019 | 2020-09-21 19:54 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Fair | Static Wire | 28 | 19:34 It was reported Broken Static near well 5D/42 (5B fdr#2). 23:00 Checked & found Broken Static o/p 5C/09. 23:07 Opened Rcl. 5C/07. | 1
| 2019-11-15 07:14 | November | 7:14 | Morning | Friday | Weekdays | 15 | 2019 | 2020-09-22 02:09 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Fair | Static Wire | 28 | 02:09 Opened LBS 5C/01, then closed at 03:51 03:22 Closed Recl. 5C/07. Cause: Broken Static. | 1
92 | 2019-11-15 07:14 | November | 7:14 | Morning | Friday | Weekdays | 15 | 2019 | 2020-09-22 07:03 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Cloudy | Capasitor Bank / Fuse holder of Cap Bank. | 0 | 8C VCB fdr #1 T/R 1x Not Checked Yet | 1
| 2019-11-15 09:24 | November | 9:24 | Morning | Friday | Weekdays | 15 | 2019 | 2020-09-25 07:42 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Cloudy | Capasitor Bank / Fuse holder of Cap Bank. | 0 | Checked and found: 8C VCB fdr #1 T/R, Counter : 727 / 728, Relay Flag : 50. Patrolled the line found : Broken fuse holder on pole 9D/54 Cause : Capasitor Bank / Fuse holder of Cap Bank. | 1
93 | 2019-11-15 09:24 | November | 9:24 | Morning | Friday | Weekdays | 15 | 2019 | 2020-09-22 07:19 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Animal | 40 | KETIGUL VCB fdr #2 T/R 1x KETIGUL fdr #1 load dropped 113 A (124 / 11 A) KETIGUL fdr #3 load dropped 33 A (33 / 0 A) Not Checked Yet | 1
| 2019-11-15 09:55 | November | 9:55 | Morning | Friday | Weekdays | 15 | 2019 | 2020-09-23 16:48 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Animal | 40 | checked and found KTGL VCB fdr #2 T/R 3x, ctr: 408 / 411 Patrolled the line and found death animal (monkey) hanging on @3 o/p 31/AN/20 Cause : Animal | 1
94 | 2019-11-15 09:55 | November | 9:55 | Morning | Friday | Weekdays | 15 | 2019 | 2020-09-22 07:49 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Animal | 9 | ROKAN VCB feeder #2 T/R 1x Not Checked Yet | 1
| 2019-11-16 18:02 | November | 18:02 | Afternoon | Saturday | Weekends | 16 | 2019 | 2020-09-24 18:05 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Animal | 9 | Checked And Found RKNSB VCB2 Fdr #8 Ctr 1348/1349, Patrolled The Line On 24/Sep/2020 And Found Setelah Dipatrol Namun Tidak Ada Temuan (Relay Flag Tidak Ada Dijumpai) Cause: Animal | 1
95 | 2019-11-16 18:02 | November | 18:02 | Afternoon | Saturday | Weekends | 16 | 2019 | 2020-09-22 07:51 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Cloudy | Unidentified | 19 | LIBO VCB feeder #1 T/R 1x LIBO feeder #2 load dropped 7 A (55 / 48 A) Not Checked Yet | 1
| 2019-11-16 18:02 | November | 18:02 | Afternoon | Saturday | Weekends | 16 | 2019 | 2020-09-24 08:15 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Cloudy | Unidentified | 19 | Checked And Found LBOSB OCB1 Fdr #8 Ctr 607/608, R/F 51N Patrolled The Line On 23/Sep/2020 But Found Nothing Cause: Unidentified | 1
96 | 2019-11-16 18:02 | November | 18:02 | Afternoon | Saturday | Weekends | 16 | 2019 | 2020-09-22 11:06 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 11:06 CDGT #2 S/U and then online at 11:35 for Running Test | 1
97 | 2019-11-17 08:15 | November | 8:15 | Morning | Sunday | Weekends | 17 | 2019 | 2020-09-22 17:54 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 17:54 CDGT #5 Offline and then Shut Down at 17:55 for standby | 1
98 | 2019-11-17 08:15 | November | 8:15 | Morning | Sunday | Weekends | 17 | 2019 | 2020-09-23 13:26 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Fair | Unidentified | - | Duri Community Feeder # 3 T/R 1X Not checked yet. | 1
| 2019-11-17 09:45 | November | 9:45 | Morning | Sunday | Weekends | 17 | 2019 | 2020-09-24 18:06 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Fair | Unidentified | - | Checked And Found DCSG ACB26 Fdr #8 Ctr 111/134, R/F 51 Patrolled The Line On 24/Sep/2020 But Found Nothing Cause: Unidentified | 1
99 | 2019-11-17 17:50 | November | 17:50 | Afternoon | Sunday | Weekends | 17 | 2019 | 2020-09-23 17:00 | MINAS POWER PLANT | Minas | PGT South | Fair |  | - | 16:10 MGT # 8 S/U and On Line at 16:45 for testing 17:30 offline and Shutdown for standby. | 1
100 | 2019-11-17 17:50 | November | 17:50 | Afternoon | Sunday | Weekends | 17 | 2019 | 2020-09-23 18:13 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Fair | Others | 124 | CKBS 13.8KV VCB fdr #5 T/R 1X. CKBS fdr #2 load dropped 178A (208/30A). Not checked yet. | 1
| 2019-11-18 10:51 | November | 10:51 | Morning | Monday | Weekdays | 18 | 2019 | 2020-09-25 13:52 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Fair | Others | 124 | Checked and found CKBS VCB fdr #5 T/R, Counter : 201 / 202, Relay Flag : 51N. Patrolled the line found : Not Found Cause : Others | 1
101 | 2019-11-18 11:00 | November | 11:00 | Morning | Monday | Weekdays | 18 | 2019 | 2020-09-23 19:56 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Rain and Lightning | Others | 79 | Minas ACB fdr #4 T/R 1x. Not Checked Yet. | 1
| 2019-11-18 12:21 | November | 12:21 | Afternoon | Monday | Weekdays | 18 | 2019 | 2020-09-25 07:31 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Rain and Lightning | Others | 79 | Checked and found: MNS ACB/1 fdr #4 T/R 1x, Counter : 129 / 130, R/F : 51 Patrolled the line but found nothing Cause : Others | 1
102 | 2019-11-18 14:50 | November | 14:50 | Afternoon | Monday | Weekdays | 18 | 2019 | 2020-09-23 20:24 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Rain | Lightning | 0 | 20:24 Bangko fdr #1 load dropped 36A (154/118A ). 21:43 Checked and found Recloser 23/W/12 T/O (block for HPS #08). 22:02 Patrolled the line completed but found nothing. 22:04 Manual closed the Recloser 23/W/12 , OK. Counter: 334 Cause : Not checked yet. | 1
| 2019-11-18 17:23 | November | 17:23 | Afternoon | Monday | Weekdays | 18 | 2019 | 2020-09-24 07:45 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Rain | Lightning | 0 | Checked And Found 5440/R.23W12 Fdr #8 Ctr 334/335, R/F 51N Patrolled The Line On 23/Sep/2020 But Found Nothing Cause: Lightning | 1
103 | 2019-11-18 17:23 | November | 17:23 | Afternoon | Monday | Weekdays | 18 | 2019 | 2020-09-23 22:02 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Rain and Lightning | Tree | 221 | 13:00 It was reported no power at well 9D/57N and 12 wells D/S 8C Fdr #1 14:30 Checked and found Rec 9D/25 T/LO Ctr: 124/131. Patrol the line & found branch tree touch Power Line at well 9D/29,then removed it. 15:00 Blocked & Closed Recl 9D/25...Ok Couse : Tree | 1
| 2019-11-18 17:23 | November | 17:23 | Afternoon | Monday | Weekdays | 18 | 2019 | 2020-09-23 22:02 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Rain and Lightning | Tree | 221 | 22:02 8C Feeder #1 load drop 45A ( 127/82A ) Not Checked yet. | 1
104 | 2019-11-18 17:23 | November | 17:23 | Afternoon | Monday | Weekdays | 18 | 2019 | 2020-09-24 07:48 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Lightning | 98 | South Balam Feeder # 1 T/R 1X Not Checked Yet. | 1
| 2019-11-18 17:40 | November | 17:40 | Afternoon | Monday | Weekdays | 18 | 2019 | 2020-09-25 15:10 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Lightning | 98 | Checked and found: SBLM VCB fdr #1 T/R 1x, Ctr : 421 / 422, R/F : 51N. Patrolled the line but found nothing Cause : Lightning | 1
105 | 2019-11-18 17:40 | November | 17:40 | Afternoon | Monday | Weekdays | 18 | 2019 | 2020-09-24 10:05 | 13.8KV PETAPAHAN FEEDER #7 | Petko | PGT South | Fair | Planned Maintenance | 0 | 10:05 Manual open Petapahan fdr#7 Connected new cable at Petapahan GS. | 1
106 | 2019-11-18 21:34 | November | 21:34 | Night | Monday | Weekdays | 18 | 2019 | 2020-09-24 13:15 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Planned Maintenance | 47 | 13:15 Manual Open Recloser 38CX25 Replace Recloser 40 CY 16 15:08 Closed Recloser 38CX25 Planned Maintenance | 1
107 | 2019-11-19 05:31 | November | 5:31 | Morning | Tuesday | Weekdays | 19 | 2019 | 2020-09-24 15:25 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Planned Maintenance | 5 | 15:25 Manual open LBS 37/CW/49 d/s NKB fdr #2 Purpose to Repair Hotspot Cause: Planned Maintenance | 1
108 | 2019-11-19 09:02 | November | 9:02 | Morning | Tuesday | Weekdays | 19 | 2019 | 2020-09-24 17:03 | CENTRAL DURI POWER PLANT | Duri | PGT North | Fair |  | - | 17:03 CDGT # 2 Off/Line and S/D | 1
109 | 2019-11-19 09:02 | November | 9:02 | Morning | Tuesday | Weekdays | 19 | 2019 | 2020-09-24 17:20 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Planned Maintenance | 0 | 17:20 Open LBS 07/T5/15 D/S D.Filed Fdr#4 Isolated By Pass switch o/p 07/T5/19 18:16 Closed LBS 07/T5/15. | 1
110 | 2019-11-19 13:04 | November | 13:04 | Afternoon | Tuesday | Weekdays | 19 | 2019 | 2020-09-25 03:30 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain | Pin Insulator | 0 | 03:30 CD fdr #1 load dropped 62 A (72 / 10 A) 14:52 Checked and found RCL 38/AS/09 operate 2x, Ctr : 453 / 454, R/F : None Patrolled the line found : Broken Pin Insulator @2 o/p 38/AR/23 Cause : Pin Insulator | 1
111 | 2019-11-19 13:04 | November | 13:04 | Afternoon | Tuesday | Weekdays | 19 | 2019 | 2020-09-25 05:50 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Rain | Unidentified | 123 | 05:50 Petani fdr #1 load dropped 84 A (208 / 124 A) Petani fdr #2 load dropped 10 A (72 / 62 A) 06:38 Reported no power for some wells at Petani field (ex PTN #113) Call TDO crew to check the problem 15:14 Checked and found RCL 33/AY/47 T/O (on block), Ctr: 212/213, R/F: NONE. Patrol the line but found nothing Cause : Unidentified | 1
112 | 2019-11-19 13:04 | November | 13:04 | Afternoon | Tuesday | Weekdays | 19 | 2019 | 2020-09-25 09:50 | 13.8KV NORTH DURI FEEDER #5 | Duri | PGT North | Rain | Lightning | 0 | North Duri Fdr#5 T/R 1X Not Checked yet. | 1
| 2019-11-19 13:04 | November | 13:04 | Afternoon | Tuesday | Weekdays | 19 | 2019 | 2020-09-29 18:36 | 13.8KV NORTH DURI FEEDER #5 | Duri | PGT North | Rain | Lightning | 0 | Checked and found ND VCB fdr #5 Operate (T/R), Counter: 159 (not counting / counter problem), R/F: 51N Patrolled the line but found nothing Cause : Lightning | 1
113 | 2019-11-19 14:08 | November | 14:08 | Afternoon | Tuesday | Weekdays | 19 | 2019 | 2020-09-25 10:37 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Lightning | 0 | ND VCB fdr #2 T/R 1x Not Checked Yet | 1
| 2019-11-19 16:30 | November | 16:30 | Afternoon | Tuesday | Weekdays | 19 | 2019 | 2020-09-26 18:10 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Lightning | 0 | Checked and found ND VCB fdr #2 T/R 1x, Counter: 291 / 292, R/F: 51P @1 @2 Patrolled the line and found broken LA @2 o/p NF/07/F2 Cause : Lightning | 1
114 | 2019-11-20 09:42 | November | 9:42 | Morning | Wednesday | Weekdays | 20 | 2019 | 2020-09-25 12:07 | 13.8KV 3D FEEDER #8 | Minas | PGT South | Rain and Lightning | Unidentified | 17 | 3 Delta Fdr#8 T/R 1X Not Checked yet. | 1
| 2019-11-20 20:04 | November | 20:04 | Night | Wednesday | Weekdays | 20 | 2019 | 2020-09-27 17:21 | 13.8KV 3D FEEDER #8 | Minas | PGT South | Rain and Lightning | Unidentified | 17 | Checked and found 3D OCB fdr #8 T/R 1x, counter: 339 / 340, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
115 | 2019-11-20 20:04 | November | 20:04 | Night | Wednesday | Weekdays | 20 | 2019 | 2020-09-25 12:30 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 210 | 12:30 Minas 13.8KV ACB vfr #4 T/LO, ctr: 131 / 132 Followed by Tripped of MGT #5. Not checked yet. | 1
| 2019-11-21 14:11 | November | 14:11 | Afternoon | Thursday | Weekdays | 21 | 2019 | 2020-09-27 08:39 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 210 | Checked and found MNS VCB fdr #4 T/SO, ctr: 131 / 132, R/F: 50G, 50N 50P @1 Patrolled the line but found nothing Cause : Lightning | 1
116 | 2019-11-21 14:11 | November | 14:11 | Afternoon | Thursday | Weekdays | 21 | 2019 | 2020-09-25 12:42 | 13.8KV 5B FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 30 | 5B 13.8KV VCB fdr #4 T/R 1X. 5B fdr 5 load dropped 69A (89/20A). 5B fdr 57load dropped 10A (17/7A). Not checked yet. | 1
| 2019-11-21 14:27 | November | 14:27 | Afternoon | Thursday | Weekdays | 21 | 2019 | 2020-09-27 17:22 | 13.8KV 5B FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 30 | Checked and found 5B VCB fdr #4 T/R 1x, R/F: 719 / 720 Patrolled the line and found broken dead end @1 @3 o/p 4C/128 Cause : Lightning | 1
117 | 2019-11-21 16:50 | November | 16:50 | Afternoon | Thursday | Weekdays | 21 | 2019 | 2020-09-25 12:51 | MINAS POWER PLANT | Minas | PGT South | Fair |  | - | 12:51 S/U MGT # 5 then O/L at 13:00. | 1
118 | 2019-11-21 17:30 | November | 17:30 | Afternoon | Thursday | Weekdays | 21 | 2019 | 2020-09-25 13:42 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Rain and Lightning | Lightning | 44 | Libo Feeder # 2 Load drop 48A ( 56/8A ) Libo Feeder # 1 Load drop 30A ( 78/48A ) Not checked yet. | 1
| 2019-11-21 17:56 | November | 17:56 | Afternoon | Thursday | Weekdays | 21 | 2019 | 2020-09-27 07:31 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Rain and Lightning | Lightning | 44 | Checked and found LBO VCB fdr #2 operate 2x, ctr: 528 / 530, R/F: 51N Patrolled the line but found nothing Cause : Lightning | 1
119 | 2019-11-22 08:44 | November | 8:44 | Morning | Friday | Weekdays | 22 | 2019 | 2020-09-26 06:39 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Others | 10 | Rokan Fdr#2 T/R 1X R/F 51N Ctr: 1349/1350 Check and found Broken Disconnect Switch Bushing @2 o/p 28/AV/13 Cause : Other | 1
| 2019-11-22 17:10 | November | 17:10 | Afternoon | Friday | Weekdays | 22 | 2019 | 2020-09-26 06:39 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Others | 10 | Rokan Fdr#2 T/R 1X R/F 51N Ctr: 1349/1350 Check and found Broken Disconnect Switch Bushing @2 o/p 28/AV/13 Cause : Other | 1
120 | 2019-11-22 19:00 | November | 19:00 | Night | Friday | Weekdays | 22 | 2019 | 2020-09-26 09:22 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Animal | - | 09:22 Central Duri Fdr#16 T/R 1X 09:30 Reported from HO dispatcher found monkey o/p 09/N4/06 09:35 Check and found Recl 09/N4/08 T/R 2X Ctr: 242/244 R/F 51 @2 and broken fuse for 750KVA transformer @2 Cause : Animal | 1
121 | 2019-11-22 19:00 | November | 19:00 | Night | Friday | Weekdays | 22 | 2019 | 2020-09-26 17:03 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Rain | Planned Maintenance | - | 17:03 Manual open Recl 09/N4/08 D/S CD #16. Replace broken FCO o/p 09/N4/06 for Test station Area 9 and CVC 17:23 Close recl 09/N4/08 Plan maintenance | 1
122 | 2019-11-22 19:00 | November | 19:00 | Night | Friday | Weekdays | 22 | 2019 | 2020-09-26 17:30 | CENTRAL DURI POWER PLANT | Duri | PGT North | Fair |  | - | CDGT # 2 Stand By | 1
123 | 2019-11-22 19:00 | November | 19:00 | Night | Friday | Weekdays | 22 | 2019 | 2020-09-26 20:15 | 13.8KV PETAPAHAN FEEDER #4 | Petko | PGT South | Drizzle | Others | 147 | 20:15 PTP VCB fdr #4 T/R 1x (no indication at DSC / only load dropped) PTP fdr #3 load dropped 144 A (160 / 16 A), suspect by over voltage PTP fdr #2 load dropped 136 A (158 / 22 A), suspect by over voltage 20:23 Manual Open PTP VCB fdr #3 (indication still Close at DSC), closed at 20:52 20:26 Manual Open PTP VCB fdr #4 (indication still Close at DSC) 20:27 Manual Open PTP VCB fdr #6, closed at 20:45 request by PTP GS due to high level tank at PTP GS 20:28 It was reported kite line hanging on power line at Kampung Aceh 20:45 Checked PTP Subst. and found VCB fdr #3 and fdr #4 OPEN PTP VCB fdr #3 counter: 386 / 387 PTP VCB fdr #4 counter: 387 / 389, R/F: 51P @1, @2, @3 PTP VCB fdr #6 counter: 393 / 394 20:52 Manual Close PTP VCB fdr #3, OK then release the block 21:24 Checked and found kite hanging on power line near pole 29/CX/1E/F 22:12 The kite line completely removed from power line 22:20 Manual Block and Close PTP VCB fdr #4, OK and then release the block. Cause: Others (kite) | 1
124 | 2019-11-22 19:00 | November | 19:00 | Night | Friday | Weekdays | 22 | 2019 | 2020-09-26 20:38 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Fair | Animal | 18 | LIBO VCB feeder #1 T/R 1x Not Checked Yet | 1
| 2019-11-22 19:00 | November | 19:00 | Night | Friday | Weekdays | 22 | 2019 | 2020-09-29 07:28 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Fair | Animal | 18 | Checked and found LIBO VCB fdr #1 T/R 1x, Counter: 608 / 609, R/F: 51N Patrolled the line and found death animal (eagle) near pole 34/CA/04 Cause : Animal | 1
125 | 2019-11-23 23:59 | November | 23:59 | Night | Saturday | Weekends | 23 | 2019 | 2020-09-27 23:59 | CPI POWER SYSTEM |  |  | Fair | Normal Condition | - | CPI Power System in Normal Condition | 1
126 | 2019-11-24 08:23 | November | 8:23 | Morning | Sunday | Weekends | 24 | 2019 | 2020-09-29 23:59 | CPI POWER SYSTEM |  |  | Fair | Normal Condition | - | CPI Power System On Normal Condition | 1
127 | 2019-11-24 08:23 | November | 8:23 | Morning | Sunday | Weekends | 24 | 2019 | 2020-09-29 06:40 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Unidentified | 4 | 06:40 Duri field feeder #2 load dropped 11A (143/132A). 11:08 It was reported no power on road 07/U1/17. 11:30 Checked & found recloser 07/U1/19 T/O ( On block). Patrolled the line but found nothing. 11:45 Blocked & closed recloser 07/U1/19 Ok. Cause: United field. | 1
128 | 2019-11-24 08:53 | November | 8:53 | Morning | Sunday | Weekends | 24 | 2019 | 2020-09-29 15:17 | 13.8KV CENTRAL DURI FEEDER #4 | Duri | PGT North | Fair | Pin Insulator | 0 | C.Duri 13.8Kv ACB #21 fdr #4 T/R 1x. Ctr: 533/534 R/f: 51N. Not checked yet. | 1
| 2019-11-24 09:37 | November | 9:37 | Morning | Sunday | Weekends | 24 | 2019 | 2020-09-30 16:19 | 13.8KV CENTRAL DURI FEEDER #4 | Duri | PGT North | Fair | Pin Insulator | 0 | Checked and found: CDRSG/13.8ACB21 T/R, Counter : 533 / 534, Relay Flag : 51N Patrolled the line found : Pin Support Broken Cause : Pin Insulator | 1
129 | 2019-11-25 01:15 | November | 1:15 | Night | Monday | Weekdays | 25 | 2019 | 2020-09-30 09:34 | 13.8KV BEKASAP FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 357 | 09:34 Manually opened Recl 37BD12 (Bekasap fdr#2). Replaced Broken Pin Insulator o/p 37BD16, 38BD34, 38BD106. Replaced broken Dead End Insulator on TOP Bekasap #09. 12:18 Blocked & closed Recl 37BD12, then release the block. Cause: Plan Maintenance. | 1
130 | 2019-11-25 07:55 | November | 7:55 | Morning | Monday | Weekdays | 25 | 2019 | 2020-09-30 12:00 | 13.8KV NEW KOTABATAK FEEDER #4 | Petko | PGT South | Fair | Others | - | 12:00 It was reported No Power at6 KB GS. 12:10 Manually Opened CKBS fdr#6, then Closed at 13:02. (Maintain Level Tank). Checked & found Recl TX/2/3 T/O. 12:45 Blocked & closed Recl. TX 2/3. Cause: Other (EQR Team Maintenance Pump). | 1
131 | 2019-11-25 07:55 | November | 7:55 | Morning | Monday | Weekdays | 25 | 2019 | 2020-09-30 14:18 | NELLA SWITCHING STATION | Bangko-Balam | PGT North | Cloudy | Unidentified | - | 115 Kv Line Nella Pinang GCB#27 T/R 1x. Not checked yet. | 1
| 2019-11-25 13:43 | November | 13:43 | Afternoon | Monday | Weekdays | 25 | 2019 | 2020-05-10 07:18 | NELLA SWITCHING STATION | Bangko-Balam | PGT North | Cloudy | Unidentified | - | Checked & found 115Kv Line Nella/Pinang GCB#27 T/R 1x Ctr:259/260 R/F:67N. Patrolled the line & found Danger trees between pole DP305/DP306. Cause : Unidentified. | 1
1 | 2019-11-25 16:36 | November | 16:36 | Afternoon | Monday | Weekdays | 25 | 2019 | 2019-01-11 06:37 | 13.8KV 3D FEEDER #6 | Minas | PGT South | Rain and Lightning | Unidentified | - | 3D fdr#6 T/R 1x. Not checked yet. | 1
| 2019-11-25 17:54 | November | 17:54 | Afternoon | Monday | Weekdays | 25 | 2019 | 2019-03-11 20:37 | 13.8KV 3D FEEDER #6 | Minas | PGT South | Rain and Lightning | Unidentified | - | Checked & found 3D OCB fdr#6 T/R 1x Ctr:300-301 R/F:51N. Patrolled the line not found nothing. Cause : Unidentified. | 1
2 | 2019-11-25 17:54 | November | 17:54 | Afternoon | Monday | Weekdays | 25 | 2019 | 2019-01-11 09:43 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Fair | Planned Maintenance | 11 | 09:43 Open LBS: 04-01-01. Relocated 112.5KVA TX o/p: 04-00-13. (33 wells off during the JOB). 10:53 Closed LBS: 04-01-01. Plan Maintenance. | 1
3 | 2019-11-25 17:54 | November | 17:54 | Afternoon | Monday | Weekdays | 25 | 2019 | 2019-01-11 16:18 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Unidentified | 0 | NKBS 13.8 kv VCB fdr#2 T/R 1x. NKBS fdr#3 load dropped 50A (109-59A). Not checked yet. | 1
| 2019-11-25 17:54 | November | 17:54 | Afternoon | Monday | Weekdays | 25 | 2019 | 2019-05-11 08:03 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Unidentified | 0 | Checked and found: NKBKSB-13.8OCB2 T/R, Counter : 99924 - 99925, Relay Flag : 51N Patrolled the line found : Nothing Found Cause : Unidentified | 1
4 | 2019-11-25 17:54 | November | 17:54 | Afternoon | Monday | Weekdays | 25 | 2019 | 2019-01-11 16:19 | 13.8KV PETAPAHAN FEEDER #6 | Petko | PGT South | Fair | Others | - | Petapahan fdr#6 load dropped 23A (65-42A). Not checked yet. | 1
| 2019-11-25 17:54 | November | 17:54 | Afternoon | Monday | Weekdays | 25 | 2019 | 2019-06-11 07:17 | 13.8KV PETAPAHAN FEEDER #6 | Petko | PGT South | Fair | Others | - | Checked and found: PHNSB-13.8VCB6 None, Counter : 379 - 379, Relay Flag : NONE Patrolled the line found : Not found Cause : Others | 1
5 | 2019-11-25 17:54 | November | 17:54 | Afternoon | Monday | Weekdays | 25 | 2019 | 2019-02-11 13:30 | 44KV NORTH DURI - DUMAI LINE | Duri | PGT North | Drizzle | Tree | 0 | 44 kV GCB #1 ND (line to Dumai) T/R 1x Not Checked Yet | 1
| 2019-11-25 17:54 | November | 17:54 | Afternoon | Monday | Weekdays | 25 | 2019 | 2019-06-11 08:44 | 44KV NORTH DURI - DUMAI LINE | Duri | PGT North | Drizzle | Tree | 0 | Checked and found: 44KVNDGCB#44 T/R, Counter : 143 - 144, Relay Flag : 50 Patrolled the line found : Pohon menyentuh line Cause : Tree | 1
6 | 2019-11-25 17:54 | November | 17:54 | Afternoon | Monday | Weekdays | 25 | 2019 | 2019-02-11 14:32 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 307 | 14:32 BLM fdr #1 dropped 90 A (148 - 58 A) 15:10 Reported no power at locations d/s RCL 16-Z-25 15:14 Informed to TDO Crew to check So BLM fdr #1 17:00 Checked and found RCL 16-Z-25 T/SO, ctr: 46 - 49, R/F: 51P @2 Patrolled the line and found dead monkey at primary source RCL 16-Z-41 17:05 Blocked and Close RCL 16-Z-25, OK then release the block Cause: Animal (monkey) | 1
7 | 2019-11-25 19:02 | November | 19:02 | Night | Monday | Weekdays | 25 | 2019 | 2019-02-11 16:59 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Fair | Construction Job | 340 | 16:59 Manual Open RCL 36-DN-32A (6DN fdr #1) RIG ACS #05 working at 5D-27 Cause: Planned Maintenance (other team) | 1
| 2019-11-25 19:02 | November | 19:02 | Night | Monday | Weekdays | 25 | 2019 | 2019-05-11 14:01 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Fair | Construction Job | 340 | 14:11 Manual Closed LBS: 5D-13 d/s: 6D feeder #5. Transfer part load 6DN feeder #1 to 6D feeder #5 (due to Recl. 36DN-32A failed to close). Plan Maintenance (Other team). | 1
8 | 2019-11-25 19:08 | November | 19:08 | Night | Monday | Weekdays | 25 | 2019 | 2019-03-11 20:15 | 115KV CENTRAL DURI - BATANG LINE | Duri | PGT North | Fair | Dead End Insulator | 38 | 115Kv Line C.Duri - Batang GCB#31 T/R 1x. 115Kv Line C.Duri - Batang GCB#33 T/R 1x. 115Kv Line Sintong - Batang GCB#25 T/R 1x. Batang fdr#1, fdr#2 & fdr#3 no power. Not checked yet. | 1
| 2019-11-25 19:08 | November | 19:08 | Night | Monday | Weekdays | 25 | 2019 | 2019-06-11 17:31 | 115KV CENTRAL DURI - BATANG LINE | Duri | PGT North | Fair | Dead End Insulator | 38 | Checked and found: - GCB #31 CD T/R 1x, Counter : 46 - 47, R/F 21P Z1, 51N - GCB #33 CD T/R 1x, Counter : 652 - 653, R/F 21P Z1, 51N - GCB #25 STG T/R 1x, Counter : 319 - 320, R/F: 21P Z1, 21G Z1 Patrolled the line found : - Broken Dead end, @2, o/p BTG #67 - Broken Dead end, @1, o/p BTG #44 - Broken Dead end, @3, o/p BTG #21 Cause : Dead End Insulator | 1
9 | 2019-11-25 19:16 | November | 19:16 | Night | Monday | Weekdays | 25 | 2019 | 2019-04-11 06:53 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Cloudy | Lightning | 0 | N.Duri VCB fdr#1 T/R 1x. Not checked yet. | 1
| 2019-11-25 19:16 | November | 19:16 | Night | Monday | Weekdays | 25 | 2019 | 2019-08-11 08:50 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Cloudy | Lightning | 0 | Checked and found: NDRSB-13.8VCB1 T/R, Counter : 319 - 320, Relay Flag : 51N Patrolled the line found : Deadend Flash Cause : Lightning | 1
10 | 2019-11-25 19:42 | November | 19:42 | Night | Monday | Weekdays | 25 | 2019 | 2019-04-11 08:21 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Dead End Insulator | 0 | Darling fdr #3 T/R 1x Not Checked Yet | 1
| 2019-11-25 19:42 | November | 19:42 | Night | Monday | Weekdays | 25 | 2019 | 2019-06-11 17:34 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Dead End Insulator | 0 | Checked and found DRL fdr #3 T/R 1x, ctr: 263-264, R/F: 51P @1 Patrolled the line and found flash over dead end insulator o/p 05-N1-17 Cause : Dead End Insulator | 1
11 | 2019-11-26 09:03 | November | 9:03 | Morning | Tuesday | Weekdays | 26 | 2019 | 2019-04-11 10:32 | 13.8KV 8D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 1 | 10:32 Manual open VCB 8D fdr #2, closed at 10:58 MTCE team to c/o TX at 8E-26 (using crane) Cause: Planned Maintenance | 1
12 | 2019-11-26 09:03 | November | 9:03 | Morning | Tuesday | Weekdays | 26 | 2019 | 2019-04-11 15:30 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 15:30 S/U MGT #1, then online the unit at 17:20 for running test. 17:51 Off line MGT #1, then S/D for S/B | 1
13 | 2019-11-26 10:26 | November | 10:26 | Morning | Tuesday | Weekdays | 26 | 2019 | 2019-05-11 02:59 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Powerline - Conductor | 0 | Duri Field ACB fdr#4 T/R 1x. Not checked yet. | 1
| 2019-11-26 18:06 | November | 18:06 | Afternoon | Tuesday | Weekdays | 26 | 2019 | 2019-06-11 17:25 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Powerline - Conductor | 0 | Checked and found DF fdr #4 T/R 1x, ctr: 570-571, R/F: 51N Patrolled the line and found broken conductor @1, @2 o/p 07-T3-01 Cause : Conductor | 1
14 | 2019-11-27 06:34 | November | 6:34 | Morning | Wednesday | Weekdays | 27 | 2019 | 2019-05-11 10:04 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 0 | 10:04 Manually Open LBS: 250AF-39 d/s: Sintong feeder #2. De-Energized 1000KVA TX at Sect Peeding -1. Replaced Pin Insulator o/p: 24-AI-06. 11:10 Closed Line Switch: 23-AI-01 d/s Menggala feeder #1. (To Energized 1000KVA TX at Sect Peeding -1). Plan Maintenance. | 1
15 | 2019-11-27 06:34 | November | 6:34 | Morning | Wednesday | Weekdays | 27 | 2019 | 2019-05-11 10:45 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 5 | 10:45 Manually Open LBS: 4D-229E d/s: 4D feeder #3. Replaced Dead End o/p: 4D-230 and 4D-242. 13:26 Closed LBS: 4D-229E. Plan Maintenance. | 1
16 | 2019-11-27 10:14 | November | 10:14 | Morning | Wednesday | Weekdays | 27 | 2019 | 2019-05-11 15:57 | 13.8KV CENTRAL DURI FEEDER #4 | Duri | PGT North | Fair | Planned Maintenance | 39 | 15:57 Manual Open RCL 09-Q1-06 (CD fdr #4), closed at 17:29 Repair broken guy wire and touching the secondary of TX o/p 09-R2-01 Off about 58 wells for 2 hrs with estimation loss 35.4 Bbls Cause: Emergency. | 1
17 | 2019-11-27 14:02 | November | 14:02 | Afternoon | Wednesday | Weekdays | 27 | 2019 | 2019-06-11 06:22 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 38 | 06:22 Sintong 13.8KV VCB fdr#1 T/R 1x Sintong GFPC T/R 1x 11:40 Checked and found Sintong VCB Feeder #1 T/R 1X ctr: 411-412 R/F : 51N. Sintong GFPC T/R 2X ctrr: 1190-1192 R/F : 51N. Patrolled the line but found nothingn. (Also found some Monkey near well Kerang 06). Cause: Animal (Suspect Monkey). | 1
18 | 2019-11-27 15:20 | November | 15:20 | Afternoon | Wednesday | Weekdays | 27 | 2019 | 2019-06-11 15:55 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 20 | 15:55 C. Duri 13.8KV ACB fdr #16 T/LO. Checked and found C. Duri 13.8KV ACB fdr #16 T/LO ctr: 360-364 R/F: %!@1, @2. 16:10 Patrolled the line but found nothing. Blocked and closed C. duri fdr #16, OK then released the block. Cause: Un identified. | 1
19 | 2019-11-27 17:46 | November | 17:46 | Afternoon | Wednesday | Weekdays | 27 | 2019 | 2019-06-11 16:18 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 16:18 MGT #4 Trip , by alarm Loss of flame trip. | 1
20 | 2019-11-27 17:46 | November | 17:46 | Afternoon | Wednesday | Weekdays | 27 | 2019 | 2019-07-11 08:30 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Cloudy | Unidentified | 119 | CKBS 13.8KV VCB fdr#5 T/R 1x. Not checked yet. | 1
| 2019-11-27 18:33 | November | 18:33 | Afternoon | Wednesday | Weekdays | 27 | 2019 | 2019-08-11 13:54 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Cloudy | Unidentified | 119 | Checked and found : CKBSSB-13.8VCB5 T/R, Counter : 174 - 175, Relay Flag : 51N Patrolled the line : Nothing Found Cause : Unidentified | 1
21 | 2019-11-27 18:33 | November | 18:33 | Afternoon | Wednesday | Weekdays | 27 | 2019 | 2019-07-11 09:12 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 14 | 09:12 It was reported o/p 09-M3-01 No power. 09:30 Checked & found recloser 09-M3-01 d/s C.Duri fdr#1 T/SO. 09:59 Manually blocked & closed recloser 09-M3-01 d/s C.Duri fdr#1. and then release the block. Cause: Not Patrolled Yet. | 1
| 2019-11-28 09:40 | November | 9:40 | Morning | Thursday | Weekdays | 28 | 2019 | 2019-10-11 08:12 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 14 | Checked and found RCL 09-M3-01 T/SO, ctr: 80-81, R/F: None Patrolled the line but found nothing Cause : Unidentified | 1
22 | 2019-11-28 10:12 | November | 10:12 | Morning | Thursday | Weekdays | 28 | 2019 | 2019-07-11 15:17 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 15:17 S/U MGT #4 and then on line at: 15:30. | 1
23 | 2019-11-28 16:15 | November | 16:15 | Afternoon | Thursday | Weekdays | 28 | 2019 | 2019-07-11 21:09 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 25 | Pinang fdr #1 T/R 1x Not Checked Yet | 1
| 2019-11-29 10:15 | November | 10:15 | Morning | Friday | Weekdays | 29 | 2019 | 14-11-2019 08:43 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 25 | Checked and found: PNGSB-13.8VCB1 T/R, Counter : 454 - 456, Relay Flag : 51N. Patrolled the line found : Broken Pin Insulator 10% Cause : Lightning | 1
24 | 2019-11-29 16:00 | November | 16:00 | Afternoon | Friday | Weekdays | 29 | 2019 | 2019-07-11 21:58 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 48 | Menggala fdr #1 load dropped 144 A (190 - 46 A) Menggala fdr #2 load dropped 123 A (171 - 48 A) Menggala GFPC T/R 1x Not Checked Yet | 1
25 | 2019-11-29 17:05 | November | 17:05 | Afternoon | Friday | Weekdays | 29 | 2019 | 2019-07-11 22:42 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Pin Insulator | 142 | Nella fdr #1 T/R 1x Nella GFPC T/R 1x Nella Recl for Cap Bank T/O Not Checked Yet | 1
| 2019-11-29 18:43 | November | 18:43 | Afternoon | Friday | Weekdays | 29 | 2019 | 2019-11-11 08:01 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Pin Insulator | 142 | Checked & found Nella VCB fdr#1 T/R 1x Ctr:562-563 R/F:51N Nella GFPC T/R 3x Ctr:1119-1121. Patrolled the line & found : Broken Pin Insulator Cause : Pin Insulator | 1
26 | 2019-11-29 18:43 | November | 18:43 | Afternoon | Friday | Weekdays | 29 | 2019 | 2019-08-11 00:49 | NEW PETAPAHAN SUBSTATION | Petko | PGT South | Rain and Lightning | Under investigation | 363 | 00:49 New Petapahan TX-2 tripped 115 kV GCB #3 New PTP T/O 115 kV GCB #5 New PTP T/O 13.8 kV VCB fdr #6, fdr #7 and fdr #8 loss of Power 01:25 Manual open VCB fdr #4, request by PTP GS due to pump problem 01:29 Manual open VCB fdr #3, request by PTP GS due to pump problem 01:30 Crew checked and found: - No relay flag for TX-2 - TX-2 Visually normal - TX-2 Winding temp normal - TX-2 Liquid temp normal - TX-2 87T normal (not operate) - TX-2 86T normal (not operate) - TX-2 86HR operate - GCB #3 T/O, 86S normal, ctr: 193 - 194 - GCB #5 T/O, 86S normal, ctr: 80 - 81 01:38 Manual open VCB fdr #6, closed at 02:16 (locally due to RTU failed) 01:39 Manual open VCB fdr #8, closed at 02:12 (locally due to RTU failed) 01:42 Manual open VCB fdr #7 (locally), closed at 02:06 (locally due to RTU failed) 01:57 Manual Close 115 kV GCB #3, OK, TX-2 energized 01:59 Manual Close 115 kV GCB #5 but failed (remotely and locally) 02:05 RTU New PTP and SURAM Failed 02:45 Manual open PTP VCB fdr #6 (req. by Andi due to WIP problem) 03:58 Manual block and close PTP VCB fdr #3, OK, then release the block (Eri) 04:00 Manual block and close PTP VCB fdr #4, OK, then release the block (Eri) 04:33 Manual block and close PTP VCB fdr #6, OK, then release the block (Eri) Cause: Under Investigation | 1
27 | 2019-11-30 23:59 | November | 23:59 | Night | Saturday | Weekends | 30 | 2019 | 2019-08-11 01:33 | 13.8KV 3D FEEDER #8 | Minas | PGT South | Rain and Lightning | Lightning | 42 | 3D 13.8KV OCB fdr #8 T/T 1X. Not checked yet. | 1
| 2019-12-13 05:52 | December | 5:52 | Morning | Friday | Weekdays | 13 | 2019 | 2019-12-11 23:11 | 13.8KV 3D FEEDER #8 | Minas | PGT South | Rain and Lightning | Lightning | 42 | Checked and found 8D fdr #8 T/R 1x, ctr: 334-335, R/F: 50P Patrolled the line and found flash over pin @1, @2 o/p 2D-29 Cause : Lightning | 1
28 | 2019-12-13 05:52 | December | 5:52 | Morning | Friday | Weekdays | 13 | 2019 | 2019-08-11 01:38 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | - | Minas 13.8KV ACB fdr #1 T/R 2X ctr:86-88 R/F: 51 @1, @2. Not checked yet. | 1
| 2019-12-14 09:12 | December | 9:12 | Morning | Saturday | Weekends | 14 | 2019 | 2019-12-11 23:18 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | - | Checked and found MNS fdr #1 T/R 2x, ctr: 86 - 88, R/F: 51P @1 Patrolled the line but found nothing Cause : Lightning | 1
29 | 2019-12-14 09:12 | December | 9:12 | Morning | Saturday | Weekends | 14 | 2019 | 2019-08-11 09:16 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Dead End Insulator | 0 | Rangau fdr#2 load dropped 135A (185-50A). Not checked yet. | 1
| 2019-12-15 23:59 | December | 23:59 | Night | Sunday | Weekends | 15 | 2019 | 2019-12-11 12:06 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Dead End Insulator | 0 | Checked and found: 5440-R.23BD01 T/R, Counter : 408 - 416, Relay Flag : 51 Patrolled the line found : Dead end pecah Phase : 3 Pole : 19-AZ-20 Date Patrol : 11-NOV-2019 Operated Device : 5440-R.23BD01 T/R Counter : 408 - 416 Relay Flag : 51 Finding Patrol : Dead end flash over Phase : 1 Pole : 20-BB-01 Date Patrol : 11-NOV-2019 Operated Device : 5440-R.23BD01 T/R Counter : 408 - 416 Relay Flag : 51 Finding Patrol : Insulator bypass pecah Phase : 3 Pole : 22-BD-11 Cause : Dead End Insulator | 1
30 | 2019-12-16 11:33 | December | 11:33 | Morning | Monday | Weekdays | 16 | 2019 | 2019-08-11 10:22 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Planned Maintenance | 12 | 10:22 Manually Open D.field fdr #4. Open by pass recloser 06-R7-19. Replaced Trafo at o/p 06-R7-11. 10:26 Manually block & Closed D.Field fdr #4 11:47 Closed LBS 06-R7-02 (Transfer load at 06-R7-xx to D.Field fdr#2). Cause: Plannned maintenance. | 1
31 | 2019-12-16 11:33 | December | 11:33 | Morning | Monday | Weekdays | 16 | 2019 | 2019-09-11 06:17 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | 18 | CD fdr #1 T/R 1x, counter: 269 (not change), R/F: 51P @2, 51G Not Patrolled Yet | 1
| 2019-12-16 14:04 | December | 14:04 | Afternoon | Monday | Weekdays | 16 | 2019 | 2019-12-11 13:17 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | 18 | Checked and found CD ACB fdr #1 T/R 1x, ctr : 269 (not change) R/F: 51P @2 Patrolled the line but found nothing Cause : Unidentified | 1
32 | 2019-12-16 14:04 | December | 14:04 | Afternoon | Monday | Weekdays | 16 | 2019 | 2019-09-11 11:11 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 21 | Ketigul 13.8 Kv VCB fdr #2 T/R 1X. Ketigul fdr #1 load dropped 57A (96-39A). Ketigul fdr #3 load dropped 8A (32-24A). Not checked yet. | 1
| 2019-12-16 14:56 | December | 14:56 | Afternoon | Monday | Weekdays | 16 | 2019 | 13-11-2019 10:42 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 21 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 358 - 360, Relay Flag : 51 Patrolled the line found: Dead end flash over Cause : Dead End Insulator | 1
33 | 2019-12-16 14:56 | December | 14:56 | Afternoon | Monday | Weekdays | 16 | 2019 | 2019-09-11 19:46 | 13.8KV 8C FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 13 | 8C fdr #2 T/R 1x Not Checked Yet | 1
| 2019-12-16 15:08 | December | 15:08 | Afternoon | Monday | Weekdays | 16 | 2019 | 2019-12-11 23:18 | 13.8KV 8C FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 13 | Checked and found 8C VCB fdr #2 T/R 1x, ctr: 528 - 529, R/F: 51P Current counter is 530 after manual open the VCB on 11 Nov at 15:46 Patrolled the line but found nothing Cause : Lightning | 1
34 | 2019-12-16 15:08 | December | 15:08 | Afternoon | Monday | Weekdays | 16 | 2019 | 2019-09-11 20:18 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Rain and Lightning | Transformer Failure | 2180 | 20:18 8C fdr #6 T/R 2x 8C fdr #4 load dropped 202 (227 - 25 A) 8C fdr #5 load dropped 222 (243 - 21 A). 20:51 Reported no power for GS-2 control room (PLC off) IP Phone is failed at GS-2 due to IT devices was OFF Also reported there are b/o fuse 3 pcs for PGT TX Call TDO Crew to check the problem at GS-2. 20:54 Manual Open Minas fdr #3 to maintain level tank at GS-2 (tank over flow) 21:50 Call SMO maintenance call center (14622) to inform that GS-2 Minas have a problem and need maintenance team. 22:20 Checked and found b/o fuse on @3 for 150 kVA TX (for CR) Also found b/o fuse 3 pcs for 2500 kVA TX (for WIP) Waiting MTCE team to replace the b/o fuse (The weather still rain). 23:34 Informed by TL PGT OPS North that situation at GS-2 still on control by production team and still waiting the rain to stop to replace b/o fuse. JDE Number = 0 | 1
| 2019-12-17 09:47 | December | 9:47 | Morning | Tuesday | Weekdays | 17 | 2019 | 2019-10-11 12:48 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Rain and Lightning | Transformer Failure | 2180 | 12:48 Manually opened 8D OCB fdr#3. -----> Closed at:20:51. To maintain Tank Level due to GS#2 HMI Problem. (No power to GS-2 control building due to Transformer problem). 13:00 Manually opened 8C OCB fdr#3. -----> Closed at :20:22. To maintain Tank Level due to GS#2 HMI Problem. (No power to GS-2 control building due to Transformer problem). 13:30 Manually opened 8C OCB fdr#1. -----> Closed at :23:34. To maintain Tank Level due to GS#2 HMI Problem. (No power to GS-2 control building due to Transformer problem). Production loss 10 Nov : 1262 Bbls / 80 wells | 1
| 2019-12-17 13:06 | December | 13:06 | Afternoon | Tuesday | Weekdays | 17 | 2019 | 2019-11-11 15:37 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Rain and Lightning | Transformer Failure | 2180 | 15:37 Manually open 13.8 kV 8D OCB fdr #3. -----> Closed at: 20:18 15:37 Manually open 13.8 kV 8C OCB fdr #3. -----> Closed at:19:59. 15:38 Manually open 13.8 kV 8C OCB fdr #1. -----> Closed at:19:18. 15:40 Manually open 13.8 kV MNS ACB fdr #1 -----> Closed at:19:18. 15:46 Manually open 13.8 kV 8C OCB fdr #2. -----> Closed at: 19:28 15:52 Manually open 13.8 kV MNS ACB fdr #4 -----> Closed at: 20:57 16:24 Manually open 13.8 kV 8C OCB fdr #4. -----> Closed at:18:32. 16:40 Manually open 13.8 kV 8C OCB fdr #5. -----> Closed at:18:29. 16:40 Manually open 13.8 kV 8C OCB fdr #6. -----> Closed at:17:55. Purpose : to change out 150 KVA TX at GS#2. 17:58 Energize 150 KVA TX at GS#2. Cause: Transformer failure. Production loss 9 Nov : 0 Production loss 10 Nov : 1262 Bbls // 80 wells Production loss 11 Nov : 918 Bbls // 92 wells ---------------------------------------------------------- Grand Total : 2180 Bbls // 172 wells | 1
35 | 2019-12-17 13:06 | December | 13:06 | Afternoon | Tuesday | Weekdays | 17 | 2019 | 2019-09-11 20:54 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Rain and Lightning | Emergency | 252 | Manual Open Minas feeder #3 ----->Closed at:20:57. (11Nov 2019) To maintain level tank at GS-2 (tank over flow) due to WIP failed to started (d/s 8C fdr #6) Cause: Emergency | 1
36 | 2019-12-17 15:18 | December | 15:18 | Afternoon | Tuesday | Weekdays | 17 | 2019 | 2019-09-11 21:27 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Rain | Dead End Insulator | 52 | BKS Main fdr #6 T/R 1x Not Checked Yet | 1
| 2019-12-17 15:18 | December | 15:18 | Afternoon | Tuesday | Weekdays | 17 | 2019 | 13-11-2019 10:45 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Rain | Dead End Insulator | 52 | Checked and found: BKSMSB-13.8VCB6 T/R, Counter : 383 - 384, Relay Flag : 51 Date Patrol : 12-NOV-2019 Patrolled the line found: Dead end flash over Cause : Dead End Insulator | 1
37 | 2019-12-17 22:19 | December | 22:19 | Night | Tuesday | Weekdays | 17 | 2019 | 2019-10-11 12:48 | 13.8KV 8D FEEDER #3 | Minas | PGT South | Fair | Emergency | 0 | 12:48 Manually opened 8D OCB fdr#3. -----> Closed at:20:51. To maintain Tank Level due to GS#2 HMI Problem. (No power to GS-2 control building due to Transformer problem). | 1
38 | 2019-12-17 22:19 | December | 22:19 | Night | Tuesday | Weekdays | 17 | 2019 | 2019-10-11 13:00 | 13.8KV 8C FEEDER #3 | Minas | PGT South | Fair | Emergency | - | 13:00 Manually opened 8C OCB fdr#3. -----> Closed at :20:22. To maintain Tank Level due to GS#2 HMI Problem. (No power to GS-2 control building due to Transformer problem). | 1
39 | 2019-12-18 08:37 | December | 8:37 | Morning | Wednesday | Weekdays | 18 | 2019 | 2019-10-11 13:30 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Fair | Emergency | - | 13:30 Manually opened 8C OCB fdr#1. -----> Closed at :23:34. To maintain Tank Level due to GS#2 HMI Problem. (No power to GS-2 control building due to Transformer problem). Cause: Emergency. Production loss (8D fdr #3 + 8C fdr #3 + 8C fdr #1) : 1262 Bbls / 80 wells | 1
40 | 2019-12-18 08:37 | December | 8:37 | Morning | Wednesday | Weekdays | 18 | 2019 | 2019-11-11 10:08 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Emergency | - | 10:08 Manually open Ketigul VCB fdr #1.----->Closed at:20:48. 10:08 Manually open Ketigul VCB fdr #2.----->Closed at:18:50. 10:09 Manually open Ketigul VCB fdr #3.----->Closed at:18:51. Due to Repair Check Valve 16" Production line at Pagar GS. Cause: Emergency. | 1
41 | 2019-12-18 16:40 | December | 16:40 | Afternoon | Wednesday | Weekdays | 18 | 2019 | 2019-11-11 15:30 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 6 | 15:30 It was reported No power at Genting Field. 16:11 Checked & found recloser 29-Z-13A d/s Sintong fdr#2 T/O. ctr: 211 - 212. 16:15 Manually blocked & closed recloser 29-Z-13A d/s Sintong fdr#2. and then release the block. Cause: Not Patrolled Yet. | 1
| 2019-12-18 18:02 | December | 18:02 | Afternoon | Wednesday | Weekdays | 18 | 2019 | 13-11-2019 13:16 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 6 | Checked and found: 5440-R.29Z13A T/O, Counter : 211 - 212, Relay Flag : NONE. Patrolled the line found : None Cause : Unidentified | 1
42 | 2019-12-18 18:02 | December | 18:02 | Afternoon | Wednesday | Weekdays | 18 | 2019 | 2019-12-11 07:05 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Tree | 83 | C.Duri ACB fdr@1 T/R 1x. Not checked yet. | 1
| 2019-12-18 21:26 | December | 21:26 | Night | Wednesday | Weekdays | 18 | 2019 | 17-11-2019 07:05 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Tree | 83 | Checked & found C.Duri fdr#1 T/R 1x Ctr:269-269 R/F:51@2. Patrolled the line & found Danger tree at well Kulin#62. Cause : Tree. | 1
43 | 2019-12-18 21:26 | December | 21:26 | Night | Wednesday | Weekdays | 18 | 2019 | 2019-12-11 18:29 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Rain and Lightning | Lightning | 0 | CKB 13.8 Kv VCB fdr #5 Load dropped 166A (208-42A). CKB 13.8 Kv VCB fdr #6 Load dropped 11A (201-190A). Not checked yet. | 1
| 2019-12-19 09:40 | December | 9:40 | Morning | Thursday | Weekdays | 19 | 2019 | 15-11-2019 07:11 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Rain and Lightning | Lightning | 0 | Checked and found: 5443-RCL T/R, Counter : 327 - 328, Relay Flag : NONE Patrolled the line found : Nothing Found Cause : Lightning | 1
44 | 2019-12-20 16:30 | December | 16:30 | Afternoon | Friday | Weekdays | 20 | 2019 | 2019-11-13 20:07 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 20:07 CDGT#4 Offline and then S/D the unit for S/B. | 1
45 | 2019-12-20 16:33 | December | 16:33 | Afternoon | Friday | Weekdays | 20 | 2019 | 2019-11-13 21:16 | 13.8KV 8D FEEDER #1 | Minas | PGT South | Cloudy and Lightning | Unidentified | 35 | 8D OCB feeder#1 T/R 1x. 8D feeder#2 load dropped 23A (109/86A). 8D feeder#3 load dropped 19A (89/79A). 8D feeder#4 load dropped 50A (156/106A).WIP 8D feeder#5 load dropped 30A (156/126A).WIP Not checked yet. | 1
| 2019-12-20 17:45 | December | 17:45 | Afternoon | Friday | Weekdays | 20 | 2019 | 2019-11-18 16:08 | 13.8KV 8D FEEDER #1 | Minas | PGT South | Cloudy and Lightning | Unidentified | 35 | Checked and found: 8DSB/13.8OCB1 T/R, Counter : 325 / 326, Relay Flag : 50 Patrolled the line found : Not found Cause : Unidentified | 1
46 | 2019-12-20 18:45 | December | 18:45 | Afternoon | Friday | Weekdays | 20 | 2019 | 2019-11-13 21:16 | 13.8KV 8D FEEDER #10 | Minas | PGT South | Cloudy and Lightning | Unidentified | 24 | 8D OCB feeder#10 T/R 1x. 8D feeder#9 load dropped 41A (53/12A). 8D feeder#11 load dropped 24A (132/108A). Not checked yet. | 1
| 2019-12-20 19:40 | December | 19:40 | Night | Friday | Weekdays | 20 | 2019 | 2019-11-18 16:10 | 13.8KV 8D FEEDER #10 | Minas | PGT South | Cloudy and Lightning | Unidentified | 24 | Checked and found: 8DSB/13.8OCB10 T/R, Counter : 272 / 273, Relay Flag : 50 Patrolled the line found : Not found Cause : Unidentified | 1
47 | 2019-12-20 20:51 | December | 20:51 | Night | Friday | Weekdays | 20 | 2019 | 2019-11-13 23:36 | 13.8KV PETAPAHAN FEEDER #8 | Petko | PGT South | Rain and Lightning | Lightning | 24 | Petapahan VCB feeder#8 T/R 1x. Petapahan feeder 7 load dropped 87A (87/0A).WIP Petapahan feeder 2 load dropped 43A (43/0A).WIP Petapahan feeder 6 load dropped 54A (65/11A). Not checked yet. | 1
| 2019-12-20 21:48 | December | 21:48 | Night | Friday | Weekdays | 20 | 2019 | 2019-11-15 14:18 | 13.8KV PETAPAHAN FEEDER #8 | Petko | PGT South | Rain and Lightning | Lightning | 24 | Checked and found: PHNSB/13.8VCB8 T/R, Counter : 369 / 370, Relay Flag : 51N Patrol led the line found: Deadend FlashOver Cause : Lightning | 1
48 | 2019-12-21 06:35 | December | 6:35 | Morning | Saturday | Weekends | 21 | 2019 | 2019-11-14 03:26 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Rain | Lightning | 0 | NKBS feeder #2 load dropped 209A (255/46A). Not checked yet. | 1
| 2019-12-21 06:35 | December | 6:35 | Morning | Saturday | Weekends | 21 | 2019 | 2019-11-15 14:32 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Rain | Lightning | 0 | Checked and found : 5443/R.38CX25 T/R, Counter : 340 / 341, Relay Flag : 51N Patrolled the line found : Nothing Found Cause : Lightning | 1
49 | 2019-12-21 07:05 | December | 7:05 | Morning | Saturday | Weekends | 21 | 2019 | 2019-11-14 11:02 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 |  |  | Fair | Theft | 456 | 11:02 It was reported no power at Jambon Field MSU BKS fdr#2 Load dropped 110A (268/158A). 12:00 Patrolled the Line, found LBS 38 BD36 Open, and Broken Pad Lock 15:33 Block MSU fdr#2, and Closed LBS 38 BD 36, then Released the Block (Bekasap Fdr#2 Carried Part Bekasap fdr#3 Until Recl 38 BD18) Cause : Theft (Vandalism). | 1
50 | 2019-12-21 07:05 | December | 7:05 | Morning | Saturday | Weekends | 21 | 2019 | 2019-11-14 19:15 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Fair | Emergency | - | 19:15 Manually Open Minas ACB 14 feeder #1. Due to burnt out DB#31/32 Pump. 21:20 Manually Open LBS M/5B/5 for Energize to FIRE Shop. 21:25 Manually Closed Minas ACB 14 feeder #1. 14:18 Manually Closed LBS M/5B/5. Cause: Emergency. | 1
51 | 2019-12-21 21:57 | December | 21:57 | Night | Saturday | Weekends | 21 | 2019 | 2019-11-15 03:36 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 0 | N.Duri 13.8Kv VCB fdr #2 T/R 1X. Not checked yet. | 1
| 2019-12-21 21:57 | December | 21:57 | Night | Saturday | Weekends | 21 | 2019 | 2019-11-17 08:36 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 0 | Checked & found N.Duri VCB fdr#2 T/R 1x Ctr:284/285 R/R:51N. Patrolled the line but found nothing. Cause : Unidentified. | 1
52 | 2019-12-21 23:49 | December | 23:49 | Night | Saturday | Weekends | 21 | 2019 | 2019-11-15 07:14 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Cloudy | Lightning Arrester | 54 | 5B OCB fdr#7 T/R 1x. Not checked yet. | 1
| 2019-12-21 23:49 | December | 23:49 | Night | Saturday | Weekends | 21 | 2019 | 2019-11-18 16:42 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Cloudy | Lightning Arrester | 54 | Checked and found: 5BSB/13.8OCB7 T/R, Counter : 147 / 147, Relay Flag : 51N Patrolled the line found: Not found Cause : Lightning Arrester | 1
53 | 2019-12-21 23:49 | December | 23:49 | Night | Saturday | Weekends | 21 | 2019 | 2019-11-15 09:24 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain | Tree | 38 | Menggala VCB fdr#1 T/R 1x. Menggala GFPC T/R 1x. Not checked yet. | 1
| 2019-12-21 23:49 | December | 23:49 | Night | Saturday | Weekends | 21 | 2019 | 2019-11-20 14:17 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain | Tree | 38 | Checked and found: MGLSB/13.8OCB1 T/R, Counter : 577 / 578, Relay Flag : 51N Patrol led the line pound: Pohon sawit menyentuh line Cause : Tree | 1
54 | 2019-12-21 23:49 | December | 23:49 | Night | Saturday | Weekends | 21 | 2019 | 2019-11-15 09:55 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Lightning Arrester | 0 | C.Duri ACB fdr#16 T/R 1x Ctr:364/365 R/F:51@1@2. Not patrolled yet. | 1
| 2019-12-22 00:57 | December | 0:57 | Night | Sunday | Weekends | 22 | 2019 | 2019-11-17 09:55 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Lightning Arrester | 0 | Patrolled the line & found @2 Broken LA o/p 08/N4/08. Cause : Lightning Arrester. | 1
55 | 2019-12-22 00:57 | December | 0:57 | Night | Sunday | Weekends | 22 | 2019 | 2019-11-16 18:02 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 56 | Bangko VCB fdr#4 T/R 1x. Bangko GFPC T/R 1x. Bangko fdr#1 Load dropped 35A (155/120A). Bangko fdr#2 Load dropped 233A (252/19A), Pump Off. Bangko fdr#3 Load dropped 206A (226/20A), Pump Off. Not checked yet. | 1
| 2019-12-22 08:54 | December | 8:54 | Morning | Sunday | Weekends | 22 | 2019 | 2019-11-20 14:25 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 56 | Checked and found: BKOSB/13.8OCB4 T/R, Counter : 74 / 75, Relay Flag : 51N Patrolled the line found : Broken Pin Support Cause : Lightning | 1
56 | 2019-12-22 08:54 | December | 8:54 | Morning | Sunday | Weekends | 22 | 2019 | 2019-11-16 18:02 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 0 | Nella fdr#1 Load dropped 115A (210/95A). Nella fdr#2 Load dropped 52A (72/20A). Nella GFPC T/R 1x. Not checked yet. | 1
57 | 2019-12-22 16:05 | December | 16:05 | Afternoon | Sunday | Weekends | 22 | 2019 | 2019-11-16 18:02 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 0 | So.Balam fdr#1 Load dropped 29A (148/119A). So.Balam fdr#2 Load dropped 50A (195/145A), Pump Off. Not checked yet. | 1
58 | 2019-12-22 17:01 | December | 17:01 | Afternoon | Sunday | Weekends | 22 | 2019 | 2019-11-17 08:15 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Fair | Unidentified | 103 | CKBS 13.8KV VCB fdr#5 T/R 1x. Not checked yet. | 1
| 2019-12-22 17:24 | December | 17:24 | Afternoon | Sunday | Weekends | 22 | 2019 | 2019-11-19 06:58 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Fair | Unidentified | 103 | Checked and found: CKBSSB/13.8VCB5 T/R, Counter : 175 / 176, Relay Flag : 51N Patrolled the line found : Nothing Found Cause : Unidentified | 1
59 | 2019-12-22 17:24 | December | 17:24 | Afternoon | Sunday | Weekends | 22 | 2019 | 2019-11-17 09:45 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Fair | Planned Maintenance | 15 | 09:45 Manually opened Recl.3/6/03 ( C.Duri fdr#5). Replaced 112.5 Kva Tx with the same size o/p 03/6/25. 11:12 Blocked & closed Recl. 03/6/03, then release the block. Cause: Plan maintenance. | 1
60 | 2019-12-22 18:25 | December | 18:25 | Afternoon | Sunday | Weekends | 22 | 2019 | 2019-11-17 17:50 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Cloudy | Dead End Insulator | 42 | Batang 13.8KV OCB fdr#3 T/R 1x. Not checked yet. | 1
| 2019-12-22 20:26 | December | 20:26 | Night | Sunday | Weekends | 22 | 2019 | 2019-11-18 14:30 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Cloudy | Dead End Insulator | 42 | Checked and found: BTGSB/13.8OCB3 T/R, Counter : 383 / 385, Relay Flag : 51 Patrolled the line found : broken dead end Cause : Dead End Insulator | 1
61 | 2019-12-23 10:56 | December | 10:56 | Morning | Monday | Weekdays | 23 | 2019 | 2019-11-18 10:51 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Fair | Planned Maintenance | 9 | 10:51 Manually open LBS 06/Q3/21 (C.Duri fdr#14). Install HLC,Tie in o/p 06/Q3/08 & 09. 12:00 Manually closed LBS 06/Q3/21. Cause: Planned maintenance. (due to Falldown Tree) | 1
62 | 2019-12-23 17:05 | December | 17:05 | Afternoon | Monday | Weekdays | 23 | 2019 | 2019-11-18 11:00 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Fair | Unidentified | 0 | 11:00 It was reported no power at Kerinci house #17,18.19& 20. Checked & found @1,@2 B/O fuse at Tx Kerinci#03. 15:00 Blocked recloser Kerinci#17 to replaced B/O fuse. Blocked & closed recloser Kerinci#17. Cause: Unidentified | 1
63 | 2019-12-23 23:59 | December | 23:59 | Night | Monday | Weekdays | 23 | 2019 | 2019-11-18 12:21 | 13.8KV CENTRAL DURI FEEDER #15 | Duri | PGT North | Fair | Planned Maintenance | 40 | 12:21 Manually open Recloser 06/Q3/02 (C.Duri fdr#15). Install HLC,Tie in o/p 06/Q3/05. 12:00 Manually closed Recloser 06/Q3/02 Cause: Planned maintenance. | 1
64 | 2019-12-24 06:33 | December | 6:33 | Morning | Tuesday | Weekdays | 24 | 2019 | 2019-11-18 14:50 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain | Lightning | 0 | Sintong fdr#2 load dropped 80A (194/114A). Sintong GFPC T/R 1x. Not checked yet, | 1
65 | 2019-12-24 06:33 | December | 6:33 | Morning | Tuesday | Weekdays | 24 | 2019 | 2019-11-18 17:23 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #2 |  |  | Rain and Lightning | Static Wire | - | MSU1 fdr#2 T/R 1x. Not checked yet. | 1
| 2019-12-24 09:08 | December | 9:08 | Morning | Tuesday | Weekdays | 24 | 2019 | 2019-11-26 12:24 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #2 |  |  | Rain and Lightning | Static Wire | - | Checked and found: MBL1BKS/13.8VCB2 T/R, Counter : 319 / 320, Relay Flag : 51N. Patrolled the line found : Broken static wire Cause : Static Wire | 1
66 | 2019-12-24 09:08 | December | 9:08 | Morning | Tuesday | Weekdays | 24 | 2019 | 2019-11-18 17:23 | 13.8KV 5B FEEDER #8 | Minas | PGT South | Rain and Lightning | Static Wire | 887 | 17:23 5B OCB fdr#8 (5B fdr#8+6D fdr#4) T/O. 17:26 Blocked & closed 5B fdr#8, but failed. To maintain water level. GS # 4 request to Manually open feeders: 17:28 Manually Open 4D fdr#4 (4D fdr#4+3D fdr#2). * Production loss 4D feeder #4 = 58 Bbls / 11 wells. * Production loss 3D feeder #2 = 39 Bbls / 8 wells. 17:29 Manually open 6D fdr#5 (6D fdr#5+6D fdr#2). *Production loss 6D feeder #5 = 300 Bbls / 33 wells. *Production loss 6D feeder #2 = 112 Bbls / 13 wells. 17:48 Manually open MSU1 fdr#1 (5B fdr#2+5B fdr#3). *Production loss 5B feeder #2 = 100 Bbls / 10 wells. *Production loss 5B feeder #3 = 152 Bbls / 17 wells. 18:03 Manually open 5B fdr#5 (5B fdr#5+5B fdr#1). *Production loss 5B feeder #5 = 24 Bbls / 4 wells. *Production loss 5B feeder #1 = 102 Bbls / 13 wells. Grand total Production loss = 887 Bbls / 109 wells. 18:35 Checked and found 5B OCB feeder #8 T/LO. Counter: 34/39 R/F: 51@1 & 51N. 18:39 Manually blocked and closed 5B OCB feeder #8 but failed again. 20:21 Patrolled the line found broken Static Wire between poles : 5B6D/15 to M5B/31. | 1
| 2019-12-24 09:32 | December | 9:32 | Morning | Tuesday | Weekdays | 24 | 2019 | 2019-11-19 00:22 | 13.8KV 5B FEEDER #8 | Minas | PGT South | Rain and Lightning | Static Wire | 887 | 00:22 Manually opened MSU feeder #2 (5B feeder #6 + 6D feeder #4). Dismantle broken static wire. 00:32 Manually blocked and closed MSU feeder #2 (5B feeder #6 + 6D feeder #4) //> OK. and then released the block. 00:35 Manually blocked and closed 5B OCB feeder #8 //> OK. and then released the block. 00:36 Manually blocked and closed 6D OCB feeder #5 + 6D OCB feeder #2 //> OK . and then released the block. 00:51 Manually blocked and closed 4D OCB feeder 4 + 3D OCB feeder #2 //> OK and then released the block. 00:55 Manually blocked and closed 5B OCB feeder #5 + 5B OCB feeder #1 //> OK and then released the block. Cause: Broken Static Wire. | 1
67 | 2019-12-24 09:32 | December | 9:32 | Morning | Tuesday | Weekdays | 24 | 2019 | 2019-11-18 17:40 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Pin Insulator | 21 | Pungut VCB fdr#2 T/R 1x. Pungut fdr#1 Load dropped 62A (71/9A). Not checked yet. | 1
| 2019-12-24 10:09 | December | 10:09 | Morning | Tuesday | Weekdays | 24 | 2019 | 2019-11-22 08:35 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Pin Insulator | 21 | Checked and found: PNTSB/13.8OCB2 T/R, Counter : 432 / 433, Relay Flag : 51N. Patrolled the line found : Pin Pecah Operated Device : PNTSB/13.8OCB2 T/R Counter : 432 / 433 Relay Flag : 51N Finding Patrol : LA Putus Phase : 2, 3, Pole : 48/BO/6 Cause : Pin Insulator | 1
68 | 2019-12-24 10:09 | December | 10:09 | Morning | Tuesday | Weekdays | 24 | 2019 | 2019-11-18 21:34 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Fair | Theft | - | 21:34 It was reported No Power at Talang Complex Food Cound. 23:04 Checked and found Secondary Cable from Pole mounted TX to Breaker Lost. Cause: Theft. | 1
69 | 2019-12-24 12:31 | December | 12:31 | Afternoon | Tuesday | Weekdays | 24 | 2019 | 2019-11-19 05:31 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 19 | Nella feeder #1 load dropped 56A (208/152A) Nella feeder #2 load dropped 12A (72/60A). Nella GFPC T/R 1x (fault alarm on Nella feeder #1). Not checked yet. | 1
70 | 2019-12-24 12:31 | December | 12:31 | Afternoon | Tuesday | Weekdays | 24 | 2019 | 2019-11-19 09:02 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Cloudy | Lightning Arrester | 0 | C.Duri 13.8KV ACB fdr#9 T/R 1x. R/f:51N/G Ctr:405/406. Not checked yet. | 1
| 2019-12-25 08:34 | December | 8:34 | Morning | Wednesday | Weekdays | 25 | 2019 | 2019-11-22 15:38 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Cloudy | Lightning Arrester | 0 | Checked and found : CDRSG/13.8ACB41 T/R, Counter : 405 / 406, Relay Flag : 51N. Patrolled the line found : LA Broken Cause : Lightning Arrester | 1
71 | 2019-12-25 08:34 | December | 8:34 | Morning | Wednesday | Weekdays | 25 | 2019 | 2019-11-19 13:04 | 13.8KV 6DN FEEDER #3 | Minas | PGT South | Rain and Lightning | Lightning | 0 | 6DN 13.8KV OCB fdr#3 T/R 1x. 6DN fdr#1 load dropped 65A (159/94A). 6DN fdr#2 load dropped 62A (261/199A). Not checked yet. | 1
| 2019-12-25 09:06 | December | 9:06 | Morning | Wednesday | Weekdays | 25 | 2019 | 2019-11-21 17:23 | 13.8KV 6DN FEEDER #3 | Minas | PGT South | Rain and Lightning | Lightning | 0 | Checked and found: 6DNSB/13.8OCB3 T/R, Counter : 1136 / 1138, Relay Flag : 50. Patrolled the line found : Not Found Cause : Lightning | 1
72 | 2019-12-25 09:06 | December | 9:06 | Morning | Wednesday | Weekdays | 25 | 2019 | 2019-11-19 13:04 | 13.8KV 6DN FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 0 | 6DN fdr#4 load dropped 157A (159/2A). 6DN fdr#5 load dropped 57A (181/124A). 6DN fdr#6 load dropped 10A (184/174A). Not checked yet. | 1
| 2019-12-25 09:10 | December | 9:10 | Morning | Wednesday | Weekdays | 25 | 2019 | 2019-11-21 17:28 | 13.8KV 6DN FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 0 | Checked and found: Counter : 0 / 0, Relay Flag : NONE Patrolled the line found : NONE Cause : Lightning | 1
73 | 2019-12-25 14:15 | December | 14:15 | Afternoon | Wednesday | Weekdays | 25 | 2019 | 2019-11-19 14:08 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:08 S/U CDGT #4 and then on line at: 14:25. | 1
74 | 2019-12-26 06:10 | December | 6:10 | Morning | Thursday | Weekdays | 26 | 2019 | 2019-11-19 16:30 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 16:30 CDGT#2 offline at S/D for S/B. | 1
75 | 2019-12-26 06:10 | December | 6:10 | Morning | Thursday | Weekdays | 26 | 2019 | 2019-11-20 09:42 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #2 |  |  | Fair | Planned Maintenance | - | 09:42 Manual Open 13.8 kV VCB MSU fdr #2 (5B fdr #6), closed at 09:47 MTCE team to cutting jumper o/p 5C/122 (impacted 1 well off, 5C/85) purpose: repair base pole 5C/122. Planned Maintenance | 1
76 | 2019-12-26 14:08 | December | 14:08 | Afternoon | Thursday | Weekdays | 26 | 2019 | 2019-11-20 20:04 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Tree | 16 | Rokan VCB fdr#2 T/R 1x. Not checked yet. | 1
| 2019-12-26 14:08 | December | 14:08 | Afternoon | Thursday | Weekdays | 26 | 2019 | 2019-11-24 07:22 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Tree | 16 | Checked and found: RKNSB/13.8VCB2 T/R,Counter : 1311 / 1312, Relay Flag : 51N. Patrolled the line found : High tree Cause : Tree | 1
77 | 2019-12-26 20:35 | December | 20:35 | Night | Thursday | Weekdays | 26 | 2019 | 2019-11-21 14:11 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Drizzle | Lightning | 25 | 14:11 Sintong fdr #2 T/R 1x Sintong fdr #1 dropped 63 A (85 / 22 A) Not Checked Yet | 1
| 2019-12-27 04:48 | December | 4:48 | Morning | Friday | Weekdays | 27 | 2019 | 2019-11-25 11:44 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Drizzle | Lightning | 25 | Checked and found: STGSB/13.8OCB2 T/R, Counter : 497 / 498, Relay Flag : 51N Patrolled the line found : Broken LA Cause : Lightning | 1
78 | 2019-12-27 06:04 | December | 6:04 | Morning | Friday | Weekdays | 27 | 2019 | 2019-11-21 14:27 | NEW PETAPAHAN SUBSTATION | Petko | PGT South | Fair | Planned Maintenance | 61 | 14:27 Manual Shut Down TXP/2 PTP SS Manual Open 115 kV GCB #3 PTP Manual Open 115 kV GCB #5 PTP PTP fdr #7 transferred to PTP fdr #2 PTP fdr #6 off (83 / 0 A), closed at 14:43 PTP fdr #8 off (64 / 0 A), closed at 14:43 Planned Maintenance | 1
79 | 2019-12-27 06:04 | December | 6:04 | Morning | Friday | Weekdays | 27 | 2019 | 2019-11-21 16:50 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 16:50 S/U CDGT/2 and then online at 17:10 for HRSG Operation | 1
80 | 2019-12-27 11:13 | December | 11:13 | Morning | Friday | Weekdays | 27 | 2019 | 2019-11-21 17:30 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 17:30 MGT/7 Offline and then S/D | 1
81 | 2019-12-27 11:31 | December | 11:31 | Morning | Friday | Weekdays | 27 | 2019 | 2019-11-21 17:56 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Unidentified | 113 | 17:56 Duri Field ACB fdr #4 T/LO 18:36 Checked and found Duri Field ACB fdr #4 T/LO Ctr:572/576 R/F: 51N, 51@1@2@3. 19:20 Patrolled the line but found nothing. 19:25 Blocked & Closed D.Field fdr#4 the release the block. Cause: Unidentified. | 1
82 | 2019-12-27 11:31 | December | 11:31 | Morning | Friday | Weekdays | 27 | 2019 | 2019-11-22 08:44 | CENTRAL DURI POWER PLANT | Duri | PGT North | Fair | Under investigation | - | 08:44 CDGT#3 T/O,Open generator breaker. by Alarm AVR FAULT (Gen Freq Transducer Failed) 09:14 Closed Tie Breaker ACB#39 09:51 Opened Tie Breaker ACB#39, then Synchronize CGT#3 Cause Under investigate | 1
83 | 2019-12-28 23:59 | December | 23:59 | Night | Saturday | Weekends | 28 | 2019 | 2019-11-22 17:10 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Rain and Lightning | Lightning | - | C.Duri 13.8KV ACB fdr#6 T/R 1x. R/f: 51G Ctr:509/510. Not checked yet. | 1
84 | 2019-12-29 17:31 | December | 17:31 | Afternoon | Sunday | Weekends | 29 | 2019 | 2019-11-22 19:00 | 13.8KV NEW KOTABATAK FEEDER #3 | Petko | PGT South | Rain and Lightning | Others | 0 | NKBS 13.8KV VCB fdr#3 T/R 1x. Not checked yet. (KBGS) | 1
| 2019-12-29 17:31 | December | 17:31 | Afternoon | Sunday | Weekends | 29 | 2019 | 2019-11-26 06:54 | 13.8KV NEW KOTABATAK FEEDER #3 | Petko | PGT South | Rain and Lightning | Others | 0 | Checked and found: NKBKSB/13.8OCB3 T/R, Counter : 323 / 324, Relay Flag : 51N. Patrolled the line found: Nothing Found Cause : Others | 1
85 | 2019-12-30 02:00 | December | 2:00 | Night | Monday | Weekdays | 30 | 2019 | 2019-11-22 19:00 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Rain and Lightning | Unidentified (L/A) | 0 | NKBS 13.8KV VCB fdr#2 T/R 1x. Not checked yet. | 1
| 2019-12-30 17:35 | December | 17:35 | Afternoon | Monday | Weekdays | 30 | 2019 | 2019-11-26 06:51 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Rain and Lightning | Unidentified (L/A) | 0 | Checked and found: NKBKSB/13.8OCB2 T/R, Counter : 99926 / 99927, Relay Flag : 51N. Patrolled the line found : Deadend FlashOver Cause : Unidentified (L/A) | 1
86 | 2019-12-30 18:00 | December | 18:00 | Afternoon | Monday | Weekdays | 30 | 2019 | 2019-11-22 19:00 | 13.8KV CENTRAL KOTABATAK FEEDER #2 | Petko | PGT South | Rain and Lightning | Others | - | CKBS fdr#2 load dropped 160A (264/104A). Not checked yet. | 1
| 2019-12-31 18:51 | December | 18:51 | Afternoon | Tuesday | Weekdays | 31 | 2019 | 2019-11-26 09:16 | 13.8KV CENTRAL KOTABATAK FEEDER #2 | Petko | PGT South | Rain and Lightning | Others | - | Checked and found : CKBSSB/13.8VCB2 None, Counter : 99 / 99, Relay Flag : NONE. Patrolled the line found : Feeder to GS, Ada Pompa GS yg Dimatikan Cause : Others | 1
87 | 2020-01-13 18:05 | January | 18:05 | Afternoon | Monday | Weekdays | 13 | 2020 | 2019-11-23 23:59 | CPI POWER SYSTEM |  |  |  | Normal Condition | - | Normal System Condition. | 1
88 | 2020-01-13 18:05 | January | 18:05 | Afternoon | Monday | Weekdays | 13 | 2020 | 2019-11-24 08:23 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Lightning | 28 | 5B 13.8KV GCB fdr #7 T?R 1X. Not checked yet. | 1
| 2020-01-14 06:35 | January | 6:35 | Morning | Tuesday | Weekdays | 14 | 2020 | 2019-11-26 08:27 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Lightning | 28 | Checked and found: 5BSB/13.8OCB7 T/R, Counter : 147 / 147, Relay Flag : 51N. Patrolled the line found: Nothing found Cause : Lightning | 1
89 | 2020-01-14 06:35 | January | 6:35 | Morning | Tuesday | Weekdays | 14 | 2020 | 2019-11-24 08:53 | 13.8KV 8D FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 0 | 08:53 Manuall Open LBS: 8E/02, ////Closed at 09:39. Replaced Recloser at GS # 1. Plan Maintenance. | 1
90 | 2020-01-14 06:51 | January | 6:51 | Morning | Tuesday | Weekdays | 14 | 2020 | 2019-11-24 09:37 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 19 | 09:37 Manual Open LBS: 45BS/02, ////Closed at 15:42. Repaired Buck Arm o/p 46/BX=01 Replaced Pin Insulator o/p...….. Isolated LA o/p 43/BZ/10 Plan Maintenance. | 1
91 | 2020-01-14 06:51 | January | 6:51 | Morning | Tuesday | Weekdays | 14 | 2020 | 2019-11-25 01:15 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Rain and Lightning | Under investigation | 0 | 01:15 N.Duri 44Kv Line Duri/Dumai GCB#1 T/R 1x. N.Duri 13.8Kv VCB#14 (Tx/14) T/O. 02:45 N.Duri 44Kv Line Duri/Dumai GCB#1 T/R 1x Ctr:144/145 R/F:51N. N.Duri 13.8Kv VCB#14 (Tx/14) T/O Ctr:166/167. Checked Visual Tx/14 Normal. Patrolled the line but found nothing. 03:17 Manually opened 44Kv GCB#1, then closed at 03:38. 03:38 Closed 13.8Kv VCB#14 (Tx/14 Energized). Cause: Unidentified. | 1
92 | 2020-01-14 07:09 | January | 7:09 | Morning | Tuesday | Weekdays | 14 | 2020 | 2019-11-25 07:55 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Animal | - | CD fdr #1 T/R 1x, ctr: 269 (not change), R/F: 51G; 51N Not Patrolled Yet | 1
| 2020-01-14 07:09 | January | 7:09 | Morning | Tuesday | Weekdays | 14 | 2020 | 2019-11-28 09:14 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Animal | - | Patrolled the line and found dead squirrel on transformer at Kulin #79 Cause : Animal | 1
93 | 2020-01-14 09:35 | January | 9:35 | Morning | Tuesday | Weekdays | 14 | 2020 | 2019-11-25 13:43 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 186 | 13:43 Manual Open RANGAU VCB fdr #2, closed at MTCE team to repair broken cross arm o/p 23/BC/05 Planned Maintenance | 1
94 | 2020-01-14 09:35 | January | 9:35 | Morning | Tuesday | Weekdays | 14 | 2020 | 2019-11-25 16:36 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 96 | Ground fault alarm from S. Balam feeder #2. Ground fault alarm from S. Balam feeder #4. S. Balam Feeder #4 load dropped 96A (194/98A). S. Balam Feeder #3 load dropped 33A (100/67A). S. Balam Feeder #1 load dropped 20A (110/200A). Not checked yet. | 1
95 | 2020-01-14 10:20 | January | 10:20 | Morning | Tuesday | Weekdays | 14 | 2020 | 2019-11-25 17:54 | 115KV MINAS / 5B LINE | Minas | PGT South | Rain and Lightning | Dead End Insulator | 84 | 17:54 115 kV Line Minas SY – 5B tripped, frequency reach to 60,41 Hz 5B / Minas 115KV OCB #25 T/R 1X. 5B / Minas115KV OCB #22 T/SO, /////>Closed at 21:15 Minas / 5B 115KV OCB #53 T/R 1X, R/F: 87L @2, @3; 21P @2, @3 Minas / 5B 115KV OCB #51 T/SO. 3D fdr #8 dropped 25 A (342 / 317 A) 4D fdr #1 dropped 8 A (179 / 171 A) 4D fdr #2 dropped 24 A (96 / 72 A) 4D fdr #4 T/SO ////>>> closed at 18:12 5B fdr #4 dropped 35 A (70/35 A) 5B fdr #5 dropped 59 A (160 / 101 A) 5B fdr #7 dropped 51 A (118 / 67 A) 5B fdr #8 T/R 1x 6D fdr #3 dropped 22 A ( 133 / 111 A) 8C fdr #6 dropped 31 A ( 226 / 194 A) CKB fdr #1 dropped 20 A (224 / 200 A) CKB fdr #2 dropped 182 A (252 / 70 A) PTP fdr #2 dropped 127 A (127 / 0 A) PTP fdr #4 dropped 112 A (146 / 34 A) PTP fdr #6 dropped 22 A (64 / 42 A) PTP fdr #8 dropped 12 A (79 / 67 A) SURAM fdr #2 dropped 6 A (40 / 34 A) ND fdr #8 dropped 10 A (80 / 70 A) ND fdr #4 dropped 54 A (85 / 31 A) NLA fdr #1 dropped 16 A (217 / 203 A) PMT fdr #1 dropped 10 A (212 / 202 A) RGU fdr #2 dropped 20 A (184 / 164 A) KTG fdr #1 dropped 7 A (110 / 103 A) PGT fdr #1 dropped 11 A (70 / 59 A) PGT fdr #2 T/R 1x LBO fdr #1 dropped 6 A (80 / 74 A) LBO fdr #2 dropped 9 A (65 / 56) Not Checked Yet | 1
| 2020-01-14 10:56 | January | 10:56 | Morning | Tuesday | Weekdays | 14 | 2020 | 2019-11-26 14:07 | 115KV MINAS / 5B LINE | Minas | PGT South | Rain and Lightning | Dead End Insulator | 84 | Checked and found Minas 115 OCB #51 T/SO (Minas / 5B Line) Closed Minas 115KV OCB #51. OK. Not Patrolled yet. | 1
| 2020-01-14 14:41 | January | 14:41 | Afternoon | Tuesday | Weekdays | 14 | 2020 | 2019-11-27 14:24 | 115KV MINAS / 5B LINE | Minas | PGT South | Rain and Lightning | Dead End Insulator | 84 | Checked and found: MNSSY/115GCB51 T/SO, Counter : 190 / 191, Relay Flag : 21P @2, @3 Patrolled the line found and Broken dead end @2 o/p: M5B30. Cause : Dead End Insulator. | 1
96 | 2020-01-14 14:41 | January | 14:41 | Afternoon | Tuesday | Weekdays | 14 | 2020 | 2019-11-25 17:54 | 13.8KV 4D FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 5 | 17:54 4D 13.8KV OCB fdr #4 T/SO. 18:12 Blocked and closed 4D fdr #4. OK then released block. Not chcked yet. | 1
| 2020-01-15 07:26 | January | 7:26 | Morning | Wednesday | Weekdays | 15 | 2020 | 2019-11-28 14:39 | 13.8KV 4D FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 5 | Checked and found: 4DSB/13.8OCB4 T/SO, Counter : 304 / 305, Relay Flag : NONE Patrolled the line found : Not Found Cause : Lightning | 1
97 | 2020-01-15 08:30 | January | 8:30 | Morning | Wednesday | Weekdays | 15 | 2020 | 2019-11-25 17:54 | 13.8KV 5B FEEDER #8 | Minas | PGT South | Rain and Lightning | Lightning Arrester | 74 | 5b 13.8KV OCB fdr #8 T/R 1X. Not checked yet. | 1
| 2020-01-15 14:52 | January | 14:52 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 2019-11-27 15:32 | 13.8KV 5B FEEDER #8 | Minas | PGT South | Rain and Lightning | Lightning Arrester | 74 | Checked and found: 5BSB/13.8OCB8 T/R, Counter : 40 / 41, Relay Flag : NONE Patrolled the line found : Broken LA Cause : Lightning Arrester | 1
98 | 2020-01-15 15:00 | January | 15:00 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 2019-11-25 17:54 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Pin Insulator | 21 | Pungut 13.8KV OCB fdr #2 T/R 1X. Not checked yet. | 1
| 2020-01-15 15:00 | January | 15:00 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 2019-11-27 10:54 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Pin Insulator | 21 | Checked and found PGT VCB fdr #2 T/R 1x, ctr: 433/434, R/F: 51N Patrolled the line and found broken pin insulator @1 o/p 49/BT/17 Cause : Pin Insulator | 1
99 | 2020-01-15 15:24 | January | 15:24 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 2019-11-25 19:02 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Rain and Lightning | Unidentified | 45 | Libo fdr #2 T/R 2x Libo fdr #1 dropped 76 A (80 / 4 A) Not Checked Yet | 1
| 2020-01-15 16:17 | January | 16:17 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 2019-11-28 08:52 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Rain and Lightning | Unidentified | 45 | Checked and found: LBOSB/13.8OCB2 T/R, Counter : 515 / 517, Relay Flag : 51 Patrolled the line found : No Findings Cause : Unidentified | 1
100 | 2020-01-15 16:17 | January | 16:17 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 2019-11-25 19:08 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Rain and Lightning | Pin Insulator | 13 | Libo fdr #1 T/R 1x Not Checked Yet | 1
| 2020-01-16 11:21 | January | 11:21 | Morning | Thursday | Weekdays | 16 | 2020 | 2019-11-28 08:47 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Rain and Lightning | Pin Insulator | 13 | Checked and found: LBOSB/13.8OCB1 T/R, Counter : 595 / 596, Relay Flag : 51N Patrolled the line found : Pin Flash Over Cause : Pin Insulator | 1
101 | 2020-01-16 14:57 | January | 14:57 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2019-11-25 19:16 | 13.8KV 4D FEEDER #5 | Minas | PGT South | Rain and Lightning | Lightning | 5 | 4D OCB fdr#5 T/R 1x. Not checked yet. | 1
| 2020-01-16 14:57 | January | 14:57 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2019-11-27 12:15 | 13.8KV 4D FEEDER #5 | Minas | PGT South | Rain and Lightning | Lightning | 5 | Checked and found: 4DSB/13.8OCB5 T/R, Counter : 373 / 374, Relay Flag : 51. Patrolled the line found : Nothing found Cause : Lightning | 1
102 | 2020-01-17 01:35 | January | 1:35 | Night | Friday | Weekdays | 17 | 2020 | 2019-11-25 19:42 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Rain and Lightning | Dead End Insulator | 158 | 6DN OCB fdr#2 T/R 1x. Not checked yet. | 1
| 2020-01-17 01:35 | January | 1:35 | Night | Friday | Weekdays | 17 | 2020 | 2019-11-27 15:52 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Rain and Lightning | Dead End Insulator | 158 | Checked and found: 6DNSB/13.8OCB2 T/R, Counter : 330 / 331, Relay Flag : 50. Patrolled the line found : Broken Dead End Cause : Dead End Insulator | 1
103 | 2020-01-17 01:35 | January | 1:35 | Night | Friday | Weekdays | 17 | 2020 | 2019-11-26 09:03 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Fair | Dead End Insulator | 0 | Duri Community fdr #3 T/R 1x Not Checked Yet | 1
| 2020-01-18 14:00 | January | 14:00 | Afternoon | Saturday | Weekends | 18 | 2020 | 2019-11-30 09:25 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Fair | Dead End Insulator | 0 | Checked and found DCM fdr #3 T/R 1x, ctr: 99 / 100, R/F: 51N Patrolled the line and found: / Dead end flash over on @3 o/p SN/03D / Broken dead end on @3 o/p 4/DD/56 / Broken Pin Support on @1 o/p 4/DD/56 / Dead end flash over on @1 o/p DK/14 Cause : Dead End Insulator | 1
104 | 2020-01-18 14:05 | January | 14:05 | Afternoon | Saturday | Weekends | 18 | 2020 | 2019-11-26 10:26 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 19 | 10:26 Manual Open RCL 6D/78 (6D fdr #2), closed at 11:05 to connect jumper o/p 6C/24 Cause: Planned Maintenance | 1
105 | 2020-01-18 14:30 | January | 14:30 | Afternoon | Saturday | Weekends | 18 | 2020 | 2019-11-26 18:06 | 13.8KV 4D FEEDER #2 | Minas | PGT South | Fair | Unidentified | 103 | 4D fdr#4 Load dropped 83A(96/13A) 20:30 It was reported no power at well 3D.76, 3D.78, 3d.87, 3D.88, 3D.89 21:30 Checked & found Recl 4D.203 T/LO Ctr: 156/160 Patrolled the Line, but found nothing 22:30 Block & Closed the Recloser above, but Failed 01:15 Repatrolled the Line, found @1 fuse B/O Burning at Well 3D.79 Block & Closed Recl 4D.204, then released the block Cause: Unidentified | 1
106 | 2020-01-19 04:55 | January | 4:55 | Morning | Sunday | Weekends | 19 | 2020 | 2019-11-27 06:34 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Fair | Unidentified | - | 06:34 CDuri ACB fdr#3 T/R 1x Not checked yet | 1
| 2020-01-19 04:55 | January | 4:55 | Morning | Sunday | Weekends | 19 | 2020 | 2019-11-29 14:05 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Fair | Unidentified | - | Checked and found: CDRSG/13.8ACB13 T/R, Counter : 214 / 215, Relay Flag : 50 Patrolled the line found : No Findings Cause : Unidentified | 1
107 | 2020-01-19 05:18 | January | 5:18 | Morning | Sunday | Weekends | 19 | 2020 | 2019-11-27 10:14 | 13.8KV DURI FIELD FEEDER #1 | Duri | PGT North | Fair | Emergency | 0 | 10:14 Manual Open RCL 01/04/39 (Df fdr #1), closed at 12:15 Landfill near the fallen pole (1 road) Cause: Emergency. | 1
108 | 2020-01-19 05:18 | January | 5:18 | Morning | Sunday | Weekends | 19 | 2020 | 2019-11-27 14:02 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 82 | 14:02 Manually open minas ACB#2 ( feeder#3) due to c/o Tx #7 at GS#2. 14:20 Manually open 8C OCB#4 due to c/o Tx # 7 at GS #2. 14:39 Manually blocked & closed 8C OCB#4 and then released the block. 14:56 Manually blocked & closed Minas ACB#2 ( feeder#3) and then released the block. Cause: Plain maintenance. | 1
109 | 2020-01-19 07:26 | January | 7:26 | Morning | Sunday | Weekends | 19 | 2020 | 2019-11-27 15:20 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Rain and Lightning | Lightning Arrester | 116 | 15:20 C.Duri 13.8KV ACB#13 (feeder#3) T/O R/f :50 @1,@2 & 51g. ( In block position due to repair guy wire). 15:28 Blocked & closed C.Duri ACB#13 ( feeder#3) but tripped again Counter:215/216. 16:44 Patrolled the line but found nothing. 16:45 Blocked and Closed C.Duri ACB#13 fdr#3 , but tripped again. 16:53 Manually Open LBS 03/08/08. 16:54 Blocked and Closed C.Duri ACB#13 fdr#3. ok. 18:10 Manually Closed LBS 03/08/08 . C.Duri 13.8Kv ACB#13 fdr#3 T/O. 18:12 Manually Open LBS 03/08/08. Blocked and Closed C.Duri ACB#13 fdr#3. ok. 18:48 Manually closed LBS 03/08/08 . C,Duri 13.8Kv ACB#13 FDR#3 T/O. 18:50 Manually open LBS 03/08/08 . 18:51 Blocked and Closed C,Duri ACB#13 fdr#3. ok. 19:10 Manually Closed LBS 03/08/08. C.Duri 13.8Kv ACB#13 fdr#3 T/O. 19:12 Manually open LBS 03/08/08. 19:14 Blocked and Closed C.Duri ACB#13 fdr#3. ok. Open Jumper to isolated broken LA o/p: 03/04/05. 20:32 Cloaed LBS 03/08/08, OK. Released blocked C. Duri feeder #3 Cause: Lightning arrester (Broken). | 1
110 | 2020-01-19 07:26 | January | 7:26 | Morning | Sunday | Weekends | 19 | 2020 | 2019-11-27 17:46 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Rain and Lightning | Lightning | 21 | Libo 13.8KV OCB fdr#2 T/R 1x. Libo feeder#1 load dropped 10A (80/70A). Not checked yet. | 1
| 2020-01-19 08:00 | January | 8:00 | Morning | Sunday | Weekends | 19 | 2020 | 2019-11-29 09:40 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Rain and Lightning | Lightning | 21 | Checked and found LIBO VCB fdr #2 T/R 1x, ctr: 517 / 518, R/F: 51N Patrolled the line and found: / Broken dead end insulator on @3 o/p 33/CC/31C / Broken pin support insulator on @3 o/p KW/161 Cause : Lightning | 1
111 | 2020-01-19 08:00 | January | 8:00 | Morning | Sunday | Weekends | 19 | 2020 | 2019-11-27 18:33 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Rain and Lightning | Unidentified | 29 | Petani 13.8KV OCB#1 T/R 1x. Petani fdr#2 load dropped 16A (57/41A). Not checked yet. | 1
| 2020-01-19 09:05 | January | 9:05 | Morning | Sunday | Weekends | 19 | 2020 | 2019-11-28 09:33 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Rain and Lightning | Unidentified | 29 | Checked and found PTN VCB fdr #1 T/R 1x, ctr: 144 / 145, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
112 | 2020-01-19 09:05 | January | 9:05 | Morning | Sunday | Weekends | 19 | 2020 | 2019-11-28 09:40 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 19 | 09:40 Manually open LBS 06/BS/02 Load: 7A (58/51A) due to replace buck arm o/p 44/BX/02, closed at 16:10 Cause: Planed Maintenance. | 1
113 | 2020-01-19 16:48 | January | 16:48 | Afternoon | Sunday | Weekends | 19 | 2020 | 2019-11-28 10:12 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 10:12 CDGT#4 offline and then S/D the unit. | 1
114 | 2020-01-19 16:48 | January | 16:48 | Afternoon | Sunday | Weekends | 19 | 2020 | 2019-11-28 16:15 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 16:15 S/U CDGT #4 and then online at 16:32. | 1
115 | 2020-01-19 17:02 | January | 17:02 | Afternoon | Sunday | Weekends | 19 | 2020 | 2019-11-29 10:15 | 13.8KV PETAPAHAN FEEDER #4 | Petko | PGT South | Fair | Planned Maintenance | 14 | 10:15 Manually Open Recloser 28/CW/01 d/s Petapahan fdr#4. Replaced Fuse at Landfill. 10:25 Manually Closed Recloser 28/CW/01 d/s Petapahan fdr#4. Cause: Planned Maintenance. | 1
116 | 2020-01-19 17:02 | January | 17:02 | Afternoon | Sunday | Weekends | 19 | 2020 | 2019-11-29 16:00 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 0 | Bangko fdr#4 Load dropped 81A (165/84A). Bangko GFPC T/O. Not checked yet. | 1
117 | 2020-01-19 17:02 | January | 17:02 | Afternoon | Sunday | Weekends | 19 | 2020 | 2019-11-29 17:05 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 26 | Pinang OCB feeder#1 T/R 1x. Not checked yet. | 1
118 | 2020-01-19 18:06 | January | 18:06 | Afternoon | Sunday | Weekends | 19 | 2020 | 2019-11-29 18:43 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Rain and Lightning | Pin Insulator | 14 | Libo OCB feeder#1 T/R 1x. Not checked yet. | 1
| 2020-01-19 18:06 | January | 18:06 | Afternoon | Sunday | Weekends | 19 | 2020 | 2019-02-12 00:43 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Rain and Lightning | Pin Insulator | 14 | Checked and found: LBOSB/13.8OCB1 T/R, Counter : 596 / 597, Relay Flag : 51N. Patrolled the found : Pin insulator pecah 35 % Cause : Pin Insulator | 1
119 | 2020-01-19 19:00 | January | 19:00 | Night | Sunday | Weekends | 19 | 2020 | 2019-11-30 23:59 | CPI POWER SYSTEM |  |  |  | Normal Condition | - | CPI POWER SYSTEM ON NORMAL CONDITION | 1
1 | 2020-01-19 19:00 | January | 19:00 | Night | Sunday | Weekends | 19 | 2020 | 2019-01-12 07:20 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 56 | Sintong VCB feeder #2 T/R 1x. Not checked yet. | 1
2 | 2020-01-20 10:40 | January | 10:40 | Morning | Monday | Weekdays | 20 | 2020 | 2019-01-12 08:50 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 08:50 S/U MGT #7 and then on line at: 09:14. | 1
3 | 2020-01-20 10:40 | January | 10:40 | Morning | Monday | Weekdays | 20 | 2020 | 2019-01-12 12:01 | 13.8KV NORTH DURI FEEDER #10 | Duri | PGT North | Rain and Lightning | Equipment Failure | 8 | 12:01 N.Duri VCB feeder #10 T/O. 15:17 Checked & found N.Duri VCB feeder #10 T/SO. R/F:51@1 Counter:25-26. And spring in discharge position. 15:30 Manually blocked & closed N.Duri VCB feeder #10 and then released the block. Cause:Equipment. | 1
4 | 2020-01-20 14:00 | January | 14:00 | Afternoon | Monday | Weekdays | 20 | 2020 | 2019-01-12 13:38 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 39 | Batang VCB feeder #3 T/R 1x. Not checked yet. | 1
| 2020-01-20 17:00 | January | 17:00 | Afternoon | Monday | Weekdays | 20 | 2020 | 2019-03-12 16:12 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 39 | Checked And Found - BTGSB OCB3 Fdr # 3 T/R 2x, Ctr 385-387, R/F 50, @1,2,3, - RCL GFPC Fdr # 3 T/R 1x, Ctr 977-978, R/F 50N Patrolled The Line But Found Nothing Cause: Unidentified | 1
5 | 2020-01-21 09:55 | January | 9:55 | Morning | Tuesday | Weekdays | 21 | 2020 | 2019-01-12 15:45 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 129 | 15:45 Manually Open Recloser 21-V-01 d/s Nella VCB feeder #1. Due to Replace @1 Broken Dead end insulator o/p 22-V-73. Replaced @1 Broken Dead end insulator o/p 22-V-10. 16:44 Manually blocked & closed Recloser 21-V-01, and then release the block. Cause: Planned Maintenance. | 1
6 | 2020-01-21 18:52 | January | 18:52 | Afternoon | Tuesday | Weekdays | 21 | 2020 | 2019-02-12 11:30 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Lightning Arrester | 0 | C.Duri VCB feeder #16 T/R 1x. Not checked yet. | 1
| 2020-01-21 18:52 | January | 18:52 | Afternoon | Tuesday | Weekdays | 21 | 2020 | 2019-05-12 11:05 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Lightning Arrester | 0 | Checked And Found CDRSG ACB28 Fdr # 16 T/R 1x, Ctr 365-366, R/F 51N Patrolled The Line And Found La Broken @2 On Pole 09-M7-05 Cause: Lightning Arrester | 1
7 | 2020-01-22 05:31 | January | 5:31 | Morning | Wednesday | Weekdays | 22 | 2020 | 2019-02-12 22:23 | 13.8KV ROKAN FEEDER #3 | Bangko-Balam | PGT North | Fair | Dead End Insulator | - | Rokan 13.8KV VCB fdr#3 T/R 1x. Not checked yet. | 1
| 2020-01-22 05:31 | January | 5:31 | Morning | Wednesday | Weekdays | 22 | 2020 | 2019-05-12 11:12 | 13.8KV ROKAN FEEDER #3 | Bangko-Balam | PGT North | Fair | Dead End Insulator | - | Checked And Found RKNSB VCB3 Fdr # 3 T/R 1x, Ctr 627-628, R/F 51N Patrolled The Line And Found Dead End Sompel (Temuan Lama) @3 On Pole Rs-Rt-09 Cause: Dead End Insulator | 1
8 | 2020-01-22 09:12 | January | 9:12 | Morning | Wednesday | Weekdays | 22 | 2020 | 2019-03-12 06:23 | 115KV ROKAN - KETIGUL | Bangko-Balam | PGT North | Fair | Unidentified | - | 06:23 Line 115 kV ROKAN - KETIGUL Tripped 115 kV GCB #11 RKN T/R 1x 115 kV GCB #1 KTGL T/R 1x 115 KV GCB #2 KTGL T/SO, manual closed at 06:49 PMT fdr #2 T/O PMT fdr #1 load dropped 127 A (201 - 74 A) RGU fdr #1 load dropped 49 A (49 - 0 A) RGU fdr #2 load dropped 188 A (188 - 0 A) PTN fdr #1 load dropped 193 A (224 - 31 A) PTN fdr #2 load dropped 51 A (57 - 6 A) RKN fdr #2 load dropped 23 A (23 - 0 A) RKN fdr #3 load dropped 38 A (38 - 0 A) BLM fdr #1 load dropped 11 A (147 - 136 A) BLM fdr #4 load dropped 30 A (194 - 164 A) NLA fdr #1 load dropped 20 A (208 - 198 A) NLA fdr #2 load dropped 9 A (72 - 63 A) NLA GFPC T/R 1x NLA RCL for Cap Bank T/O, closed at 06:43 MGL fdr #1 load dropped 16 A (178 - 162 A) Cause: Not Checked Yet | 1
| 2020-01-22 09:12 | January | 9:12 | Morning | Wednesday | Weekdays | 22 | 2020 | 2019-05-12 11:28 | 115KV ROKAN - KETIGUL | Bangko-Balam | PGT North | Fair | Unidentified | - | Checked And Found - GCB11 RKN T/R 1x, Ctr 33-34, R/F 21 - GCB1 KTGL T/R 1x, Ctr 199-200, R/F 21 - GCB2 KTGL T/R 1x, Ctr 175-176, R/F 21 Patrolled The Line But Found Nothing @1,3 Cause: Unidentified | 1
9 | 2020-01-22 09:15 | January | 9:15 | Morning | Wednesday | Weekdays | 22 | 2020 | 2019-03-12 06:23 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Fair | Under investigation | 203 | 06:23 Pematang OCB feeder #2 T/O. 07:02 Checked and found Pematang OCB feeder #2 T/O by Relay 81. R/F: 81 Counter: 50-551. 08:29 Manually blocked and closed Pematang OCB feeder #2 --> OK. and then released the block. Cause: Under investigation. | 1
10 | 2020-01-22 09:16 | January | 9:16 | Morning | Wednesday | Weekdays | 22 | 2020 | 2019-03-12 10:35 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 16 | 10:35 Manually opened Recloser: 27-AL-21 D/S Menggala feeder #2. Due to Replace @3 broken dead end insulator on pole 27-AM-12. Replace @2 broken pin insulator on pole 27-AM-12. 10:23 Manually blocked and closed Recloser: 27-AL-21 --> OK. and then released the block. Cause: Planned maintenance. | 1
11 | 2020-01-23 10:30 | January | 10:30 | Morning | Thursday | Weekdays | 23 | 2020 | 2019-03-12 22:59 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Fair | Animal | 8 | 22:59 Bangko fdr #3 T/R 1x Bangko fdr #4 T/R 1x Not Checked Yet | 1
| 2020-01-23 14:16 | January | 14:16 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2019-07-12 13:44 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Fair | Animal | 8 | Checked and found Bangko 13.8KV OCB fdr #4 T/R 1X ctr:75-76 R/F: None. Patrolled the line and found dead Monkey at @1 near Transformer at Bangko #04. Cause: Animal (Monkey). | 1
12 | 2020-01-23 14:16 | January | 14:16 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2019-04-12 10:20 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Planned Maintenance | 91 | 10:20 Opened LBS 37-AQ-08 ( C.Duri fdr#1). Replaced 150Kva Tx with the same size at well Puncak#03. 11:35 Closed LBS 37-AQ-08. Cause: Plan Maintenance. | 1
13 | 2020-01-23 14:16 | January | 14:16 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2019-04-12 11:28 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 34 | 11:28 Manually opened 4D fdr#3. Repaired Hot Spot Jumper o/p 3D-257. 13:37 Blocked & closed 4D fdr#3, then release the block. Cause: Plan Maintenance. | 1
14 | 2020-01-23 20:05 | January | 20:05 | Night | Thursday | Weekdays | 23 | 2020 | 2019-05-12 12:36 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 12:36 S/U NDC #2 on line the unit at 14:47 ( Running test ). 18:05 Offline NDC#2 the S/D for maintenance . | 1
15 | 2020-01-23 22:05 | January | 22:05 | Night | Thursday | Weekdays | 23 | 2020 | 2019-05-12 14:20 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Fair | Planned Maintenance | 32 | 14:20 Manually Opened Recl. 7D-150 (Minas fdr#4). Replaced 550Kva Tx with the same size at well 8D-22. 14:35 Blocked & closed Recl. 7D-150, then release the block. Cause: Plan Maintenance. | 1
16 | 2020-01-24 08:26 | January | 8:26 | Morning | Friday | Weekdays | 24 | 2020 | 2019-05-12 15:03 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 2 | 15:03 Manually Opened LBS. 15-Z-16 (So.Balam fdr#1). Tie in Reactive well and install 150Kva Tx at well Antara#03. 15:30 Closed LBS 15-Z-16. Cause: Plan Maintenance. | 1
17 | 2020-01-25 06:46 | January | 6:46 | Morning | Saturday | Weekends | 25 | 2020 | 2019-06-12 06:55 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Fair | Unidentified | - | Duri Community ACB feeder #2 T/R 1X. Not Checked yet. | 1
| 2020-01-25 06:46 | January | 6:46 | Morning | Saturday | Weekends | 25 | 2020 | 2019-07-12 07:16 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Fair | Unidentified | - | Checked And Found DCS ACB30 Fdr #2 T/R 1x, Ctr 112 - 113, R/F 51G Patrolled The Line But Found Nothing Cause: Unidentified | 1
18 | 2020-01-25 09:10 | January | 9:10 | Morning | Saturday | Weekends | 25 | 2020 | 2019-06-12 07:29 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Animal | 21 | Ketigul VCB feeder#1 T/R 1x. Not checked yet. | 1
| 2020-01-25 17:39 | January | 17:39 | Afternoon | Saturday | Weekends | 25 | 2020 | 2019-09-12 10:29 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Animal | 21 | Checked And Found PKTGL VCB1Fdr # 1 T/R 1x, Ctr 222-223, R/F 51N Patrolled The Line And Found Monkey Dead On Pole Tilan 26 Cause: Animal | 1
19 | 2020-01-25 17:39 | January | 17:39 | Afternoon | Saturday | Weekends | 25 | 2020 | 2019-06-12 09:41 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Planned Maintenance | 12 | 09:41 Manually Opened Recl. 07-U1-19 (D.Field fdr#2). Repaired Hot spot. 10:51 Blocked & closed Recl. 07-U1-19, then release the block. Cause: Plan Maintenance. | 1
20 | 2020-01-26 08:22 | January | 8:22 | Morning | Sunday | Weekends | 26 | 2020 | 2019-06-12 10:40 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 165 | 10:20 Manually Opened Recl 6D-200 (6DN fdr#2). Replaced Broken Recl. 5D-112. 12:25 Blocked & closed Recl. 6D-200, then release the block. Cause: Plan Maintenance. | 1
21 | 2020-01-26 08:22 | January | 8:22 | Morning | Sunday | Weekends | 26 | 2020 | 2019-06-12 11:58 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 11:58 S/U NDC#2, then on line the unit at 12:50. (Running Test & Fine Tuning 10-100MW). | 1
22 | 2020-01-26 22:22 | January | 22:22 | Night | Sunday | Weekends | 26 | 2020 | 2019-06-12 16:09 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Rain | Recloser | 159 | 16:09 It was reported no power at 06-S1-02 (D.Field fdr#2). Duri Field fdr#2 Load dropped 80A (150-70A). 16:15 It was reported Fire at 06-S1-02. 16:31 Checked & found Fire at Recl. & Control Recl. o/p 06-S1-02. Recl. 07-U3-21 T/LO Ctr:15-18. Isolated & Bypass Recl. 06-S1-02. 18:00 Blocked & closed Recl. 07-U3-21, then release the block. Cause: Recloser. | 1
23 | 2020-01-26 22:22 | January | 22:22 | Night | Sunday | Weekends | 26 | 2020 | 2019-06-12 20:00 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 20:00 MGT #7 Offline and then S/D the unit for Standby. | 1
24 | 2020-01-26 22:22 | January | 22:22 | Night | Sunday | Weekends | 26 | 2020 | 2019-06-12 20:05 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 20:05 MGT #11 Offline and then S/D the unit for standby. | 1
25 | 2020-01-26 22:22 | January | 22:22 | Night | Sunday | Weekends | 26 | 2020 | 2019-06-12 23:30 | NORTH DURI POWER PLANT | Duri | PGT North | Fair | Under investigation | 146 | 23:30 NDC #2 TRIP Frequency : 59.33 Hz Load shedding level #3. by alarm Blade path spread high. LS level Feeder. Load. 2016 LS Trip time Close time. 1 Beruk #1 BOB well 59.7 23:30 01:27 4D F5 Area 5 01:37 Pusaka F1 Doral field 01:27 4D F4 Area 5 01:41 3D F6 Area 5 00:46 5B f7 Area 6 01:44 2 5B F5 Area 6 59.5 00:42 Zamrud F1 Zamrud field 01:27. 4B F4 Area 6 01:48 8D F3 Area 2 03:26 5B F4 Area 4 01:45 8D F1 Area 2 01:08 4B F1 Area 6 01:06 3 4D F6 Area 5 59.3 No Trip Minas F3 Area 1 No trip Pusaka F2 BOB 01:27 Zamrud F2 BOB 01:27 Zamrud F4 BOB 01:27 3D F3 Area 5 01:50 4B F6 Area 6 No Trip 8C F1 Area 2 00:53 3D F2 Area 5 01:03 4D F3 Area 5 01:02 4D F2 Area 5 01:00 5B F1 Area 4 00:42 5B F3 Area 5 Transfer to MSU #1 feeder #1 Suram F1 BOB 00:40 Suram F2 Lindai , Suram GS No Trip Batang F1 Batang field No Trip 8D F10 Area 2 No Trip 3D F5 Area 5 00:33 00:35 S/U NDC #2 but failed (2x). 00:36 S/U MGT #7 and then Online the unit at 01:10. 01:20 S/U NDC #2 and then Online the unit at 01:49. 03:12 NDC #2 TRIP Frequency : 59.75 Hz. by alarm Blade path spread high. 03:33 S/U NDC #2 and then Online the unit at 03:58. Cause: Under investigation. | 1
| 2020-01-26 22:53 | January | 22:53 | Night | Sunday | Weekends | 26 | 2020 | 2019-06-12 23:30 | NORTH DURI POWER PLANT | Duri | PGT North | Fair | Under investigation | 146 | Production Loss: 1. 8C feeder #1 = 30 Bbls / 25 wells ( GS #1 + GS #2 ) 2. 8D feeder #1 = 17 Bbls / 19 wells 3. 8D feeder #3 = 7 Bbls / 16 wells. 4. 5B feeder #1 = 66 Bbls / 24 wells 5. 5B feeder #4 = 39 Bbls / 16 wells. 6. 5B feeder #5 = 7 Bbls / 4 wells. 7. 5B feeder #7 = 55 Bbls / 4 wells. 8. 4B feeder #1 = 42 Bbls / 19 wells. 9. 4B feeder #2 = 2 Bbls / 13 wells. 10. 4B feeder #4 = 29 Bbls / 5 wells. 11. 4D feeder #2 = 26 Bbls / 21 wells. 12. 4D feeder #5 = 10 Bbls / 13 wells. 13. 3D feeder #2 = 27 Bbls / 18 wells. 14. 3D feeder #3 = 37 Bbls / 16 wells. 15. 3D feeder #4 = 57 Bbls / 35 wells. TOTAL = 451 Bbls / 248 Wells. | 1
26 | 2020-01-26 22:53 | January | 22:53 | Night | Sunday | Weekends | 26 | 2020 | 2019-07-12 08:15 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 08:15 S/U NDC#2 the online then unit 08:45. | 1
27 | 2020-01-26 22:56 | January | 22:56 | Night | Sunday | Weekends | 26 | 2020 | 2019-08-12 09:54 | 13.8KV 4B FEEDER #6 | Minas | PGT South | Lightning | Lightning | 15 | Checked And Found 4BSB OCB6Fdr # 6 T/R 1x, Ctr 195-196, R/F 50N Patrolled The Line But Found Nothing Cause: Lightning | 1
28 | 2020-01-26 22:56 | January | 22:56 | Night | Sunday | Weekends | 26 | 2020 | 2019-07-12 18:18 | NORTH DURI POWER PLANT | Duri | PGT North | Fair |  | - | 18:18 NDC#2 T/O by alarm (None) Freq 59:78. LS level Feeder. Load. 2016 LS Trip time Close time. 1 Beruk #1 BOB well 59.7 18:18 18:26 4D F5 Area 5 18:26 Pusaka F1 Doral field 18:26 4D F4 Area 5 18:26 3D F6 Area 5 18:22 5B F7 Area 6 18:25 5B F8 Area 6 18:24 Cause: Under investigation. Production loss: 1. 4D feeder #4 = 0 Bbls / 0 wells. 2. 4D feeder #5 = 10 Bbls / 13 wells. 3. 3D feeder #6 = 0 Bbls / 0 wells. 4. 4D feeder #4 = 0 Bbls / 0 wells. 5. 4D feeder #4 = 0 Bbls / 0 wells. --------------------------------------- + Grand total = 10 Bbls / 13 wells. | 1
29 | 2020-01-27 00:44 | January | 0:44 | Night | Monday | Weekdays | 27 | 2020 | 2019-07-12 19:52 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 19:52 ND CT #2 S/U, then On Line at 20:37, for Running test after T/O. Cause : under investigate | 1
30 | 2020-01-27 00:44 | January | 0:44 | Night | Monday | Weekdays | 27 | 2020 | 2019-08-12 08:30 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 08:30 Off Line then S/D for Stand by due to NDC CT#2 Run test to Base load.. | 1
31 | 2020-01-27 01:34 | January | 1:34 | Night | Monday | Weekdays | 27 | 2020 | 2019-08-12 09:55 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 09:55 MGT #8 Off Line , the S/D for Stand by, due to NDC CT#2 declared Normal also be run on Base Load. | 1
32 | 2020-01-27 01:34 | January | 1:34 | Night | Monday | Weekdays | 27 | 2020 | 2019-08-12 10:20 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Fair | Planned Maintenance | 12 | 10:20 Blocked Recl 36 CU 29 (CKB fdr#5) Open HLC to Replace Broken Deadend insulator on T/Op Well KB#404 & KB#456, also Replaced Broken LA o/p 34 CR 11 13:52 Back to normal. | 1
33 | 2020-01-27 01:34 | January | 1:34 | Night | Monday | Weekdays | 27 | 2020 | 2019-09-12 06:35 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Fair | Unidentified | 14 | 8C VCB feeder #6 T/R 1x 8C feeder #5 load dropped 198A (225-27A). 8C feeder #4 load dropped 213A (243-30A). Not checked yet. | 1
| 2020-01-27 06:08 | January | 6:08 | Morning | Monday | Weekdays | 27 | 2020 | 2019-10-12 08:07 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Fair | Unidentified | 14 | Checked and found 8C fdr #6 T/R 1x, ctr: 634 - 635, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
34 | 2020-01-27 10:37 | January | 10:37 | Morning | Monday | Weekdays | 27 | 2020 | 2019-10-12 06:43 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | 0 | N.Duri VCB feeder#1 T/R 1x. Not checked yet. | 1
| 2020-01-27 11:54 | January | 11:54 | Morning | Monday | Weekdays | 27 | 2020 | 13-12-2019 09:01 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | 0 | Checked And Found NDR VCB1 Fdr #1 T/R 2x, Ctr 332 - 334, R/F 51N Patrolled The Line And Found La Putus @3 O/P 12-F11-22 Cause: Lightning Arrester | 1
35 | 2020-01-27 11:54 | January | 11:54 | Morning | Monday | Weekdays | 27 | 2020 | 2019-10-12 07:48 | 13.8KV 8D FEEDER #11 | Minas | PGT South | Cloudy | Lightning | 64 | 8D VCB fdr #11 T/R 1x. Not checked yet | 1
| 2020-01-27 11:56 | January | 11:56 | Morning | Monday | Weekdays | 27 | 2020 | 13-12-2019 16:40 | 13.8KV 8D FEEDER #11 | Minas | PGT South | Cloudy | Lightning | 64 | Checked And Found 8D OCB11 Fdr #11 T/R 1x, Ctr 99927 - 99928, R/F 50N Patrolled The Line And Found No Found @1 Cause: Lightning | 1
36 | 2020-01-27 17:55 | January | 17:55 | Afternoon | Monday | Weekdays | 27 | 2020 | 2019-10-12 13:00 | 230KV NORTH DURI SWITCH YARD | Duri | PGT North | Fair | Planned Maintenance | - | PROGRAM SHUT OFF 230 KV LINE #1 LINE #2 NDURI - KBJ to Facilitate Tie In New 230 KV Tower 08:20 MGT #6 S/U, then Online at 08:42 08:47 MGT #8 S/U, then Online at 09:02 09:15 MGT #11 S/U,then Online at 09:38 10:22 NDC CT #2 Offline, then S/D for S/B 10:37 CGT #2 Offline, then S/D for S/B 11:00 Reduce Load at Field Operation South 10MW and BOB 12MW 13:00 Perform OP & SP Shut down 230KV Line #1,#2 NDuri-KBJ - Nduri, Isolate Line #1,#2 and Ring Back GCB#11,#13,#23,#25 - KBJ, Isolate Line #1,#2 and Kept Open GCB#91,#92,#93,#94 16:00 MGT#2 S/U, then Online at 16:25 to maintain Voltage system Cause: Planned Maintenance (PT HKI TOL high way). | 1
37 | 2020-01-27 17:55 | January | 17:55 | Afternoon | Monday | Weekdays | 27 | 2020 | 2019-10-12 23:50 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | Sintong feeder #1 load dropped 37A (90-53A). Sintong GFPC T/R 1x. Not checked yet. | 1
38 | 2020-01-27 18:12 | January | 18:12 | Afternoon | Monday | Weekdays | 27 | 2020 | 2019-10-12 23:56 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Recloser | - | 23:56 Sintong OCB feeder #1 T/R 1x. Sintong GFPC T/R 1x. 01:05 Sintong feeder #1 still dropped 50A (90-40A) 01:59 Checked and found Recloser: 25-AD-26 T/SO Counter: 130-131. Patrolled the line found nothing (IC 2 category). 02:44 Manually blocked and closed Recloser: 25-AD-06 but failed. 03:52 Manually opened Sintong OCB feeder #1. due to closed bypass of Recloser: 25-AD-26. 03:59 Manually blocked and closed Sintong OCB feeder #1 --> Success. and then released the block. Cause: Recloser. | 1
39 | 2020-01-27 18:12 | January | 18:12 | Afternoon | Monday | Weekdays | 27 | 2020 | 2019-10-12 23:56 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | Sintong feeder #2 load dropped 153A (249-96A). Not checked yet. | 1
40 | 2020-01-27 19:19 | January | 19:19 | Night | Monday | Weekdays | 27 | 2020 | 2019-11-12 09:54 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Fair | Tree | 113 | 09:54 PMT VCB fdr #1 T/SO 09:57 Call TDO crew to check the problem 10:50 Checked and found PMT VCB fdr #1 T/LO, ctr: 184-188, R/F: 51N Patrolled the line and found fallen trees at location PMT #25 Execute/cut the fallen tree. 11:18 Blocked and Close PMT VCB fdr #1 (manually due to RTU failed), OK. Cause: Tree | 1
41 | 2020-01-28 09:49 | January | 9:49 | Morning | Tuesday | Weekdays | 28 | 2020 | 2019-11-12 09:59 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Fair | Emergency | - | 09:59 Manual Open PMT VCB fdr #2 to maintain level tank (over flow) at PMT GS Request by Febry. Cause: Emergency | 1
42 | 2020-01-28 09:49 | January | 9:49 | Morning | Tuesday | Weekdays | 28 | 2020 | 2019-11-12 10:07 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Emergency | 0 | 10:07 Manual Open RGU VCB fdr #2 to maintain level tank (over flow) at PMT GS Request by Febry. Cause: Emergency | 1
43 | 2020-01-28 11:28 | January | 11:28 | Morning | Tuesday | Weekdays | 28 | 2020 | 2019-11-12 13:09 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Cloudy | Lightning Arrester | 0 | CD ACB fdr #16 T/R 1x, ctr: 366 - 367, R/F: 51N Not Patrolled Yet | 1
| 2020-01-28 11:28 | January | 11:28 | Morning | Tuesday | Weekdays | 28 | 2020 | 13-12-2019 16:47 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Cloudy | Lightning Arrester | 0 | Checked And Found CDR ACB28 Fdr #16 T/R 1x, Ctr 366 - 367, R/F 51N Patrolled The Line And Found La Pecah @2 O/P 09-M7-05 Cause: Lightning Arrester | 1
44 | 2020-01-29 07:49 | January | 7:49 | Morning | Wednesday | Weekdays | 29 | 2020 | 2019-11-12 16:31 | SINTONG SUBSTATION | Bangko-Balam | PGT North | Cloudy | Unidentified | 854 | 16:31 Sintong -Menggala 115KV line OCB #23 T/SO. Menggala fdr #1 dropped 152A (176-24A). Menggala fdr #12dropped 161A (164-3A). Ketigul fdr #1 dropped 105A (116-11A). Ketigul fdr #2 dropped 82A (84-2A). Ketigul fdr #3 dropped 44A (44-0A). 16:46 Menggala C/S T/O (No power to Menggala Substation). 16:59 Manual Closed Sintong 115KV OCB #23. OK. 17:24 Checked and found Sintong -Menggala 115KV line OCB #23 T/SO ctr:369-370 R/F: 67N. | 1
45 | 2020-01-29 08:03 | January | 8:03 | Morning | Wednesday | Weekdays | 29 | 2020 | 2019-11-12 16:59 | MENGGALA SUBSTATION | Bangko-Balam | PGT North | Cloudy | Powerline - Jumper | 528 | 16:59 Ketigul - Menggala 115KV Line T/O Ketigul 115KV GCB #1 T/SO. Ketigul 115KV GCB #3 T/SO. Menggala 115Kv GCB#29 T/SO 18:03 Checked & found MGL-KTG L90 R/F: 87L, 67N 20:00 Checked & found KTG GCB#1, Broken LA 22:02 Man. Open Rokan GCB#11, to Isolate LA at KTG GCB#1 Man. Open KTG GCB #2 22:30 Man. Open KTG VCB fdr#1#2#3 23:00 Isolated Broken L.A at KTG GCB#1 23:30 Man. Closed Rokan GCB#11 but Fail Found Broken @2 Jumper at GCB#11 toward KTG side DEC 12.2019 01:00 Open Isolation Switch KTG GCB#2 toward Rokan side 01:05 Man. Closed MGL GCB#29 01:15 Man. Closed KTG GCB#3 (Bus Voltage 13.6KV, VR +16) 01:20 Man Block & Closed KTG VCB#3, #2, #3 then released the Block Cause: Lightning | 1
| 2020-01-29 08:03 | January | 8:03 | Morning | Wednesday | Weekdays | 29 | 2020 | 2019-12-12 10:22 | MENGGALA SUBSTATION | Bangko-Balam | PGT North | Cloudy | Powerline - Jumper | 528 | 10:22 Manual Open 115 kV GCB #12 ROKAN SS (Rokan SS off during this job) Manual Open 115 kV Line Switch on pole PPR-44, closed at 16:15 repair broken jumper @2 at 115 kV GCB #11 RKN SS repair stuck isolation switch of 115 kV GCB #12 RKN SS 16:15 Manual Close 115 kV GCB #12 RKN SS, but failed 16:20 Manual Close 115 kV GCB #1 KETIGUL SS, OK 16:23 Manual Close 115 kV GCB #11 RKN SS, OK (restore load of ROKAN Subst) 16:44 Manual Close 115 kV GCB #12 ROKAN SS, OK 16:45 Manual Close 115 kV GCB #2 of KETIGUL SS, OK 115 kV line ROKAN - KETIGUL back to Normal Cause: Broken Jumper | 1
46 | 2020-01-29 15:30 | January | 15:30 | Afternoon | Wednesday | Weekdays | 29 | 2020 | 2019-12-12 10:21 | ROKAN SUBSTATION | Bangko-Balam | PGT North | Fair | Planned Maintenance | 225 | 10:21 Manual Open RKN fdr #2, closed at 16:47 Manual Open RKN fdr #3, closed at 16:46 Manual Open RKN fdr #4, closed at 16:43 10:22 Manual Open RKN 115 kV GCB #12, closed at 16:44 10:32 Manual Open 115 kV Line Switch on 4 pole PPR-44, closed at 16:15 Purpose: - Repair broken jumper @2 on 115 kV GCB #11 RKN SS - Repair stuck isolation switch on GCB #12 RKN SS 16:20 Manual Close 115 kV GCB #1 of KETIGUL SS, OK 16:23 Manual Close 115 kV GCB #11 of RKN SS, OK 16:45 Manual Close 115 kV GCB #2 of KETIGUL SS, OK (115 kV Line ROKAN - KETIGUL back to Normal) Cause: Planned Maintenance | 1
47 | 2020-01-29 17:52 | January | 17:52 | Afternoon | Wednesday | Weekdays | 29 | 2020 | 2019-12-12 15:01 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Fair | Others | - | 15:21 Manual Open RCL 6D -298 (6D fdr #2) (load decrease from 165 to 64 A) Support RIG BMS-06 activities at 6D-82 (estimate for 3 days) | 1
48 | 2020-01-29 17:52 | January | 17:52 | Afternoon | Wednesday | Weekdays | 29 | 2020 | 2019-12-12 19:22 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 |  |  | Fair | Lightning Arrester | 11 | MSU #2 (Bekasap fdr#2) Load dropped 168A(256-88A) Not checked yet | 1
| 2020-01-29 19:17 | January | 19:17 | Night | Wednesday | Weekdays | 29 | 2020 | 14-12-2019 08:11 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 |  |  | Fair | Lightning Arrester | 11 | Checked and found RCL 37-BD-40 T/R 1x, ctr: 1222-1223, R/F: None Patrolled the line and found : - broken LA @1 at BKS #21 - flash over dead end @1, @3 o/p 39-BD-01 Cause : Lightning Arrester | 1
49 | 2020-01-29 19:17 | January | 19:17 | Night | Wednesday | Weekdays | 29 | 2020 | 2019-12-13 05:52 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Fair | Unidentified | 0 | C.Duri ACB fdr#14 T/R 1x, counter: 203 / 204, R/F: 51P @1, @2 Not checked yet. | 1
| 2020-01-30 06:56 | January | 6:56 | Morning | Thursday | Weekdays | 30 | 2020 | 2019-12-14 08:19 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Fair | Unidentified | 0 | Patrolled the line and found broken conductor wire on @2 o/p 06/Q1/23 Cause : Unidentified | 1
50 | 2020-01-31 19:56 | January | 19:56 | Night | Friday | Weekdays | 31 | 2020 | 2019-12-14 09:12 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Lightning | 15 | KETIGUL feeder #2 T/R 1x Not Checked Yet | 1
| 2020-02-13 02:12 | February | 2:12 | Night | Thursday | Weekdays | 13 | 2020 | 2019-12-16 06:42 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Lightning | 15 | Checked and found KTGL VCB fdr #2 T/R 2x, ctr: 360 / 362, R/F: 51N Patrolled the line and found broken deadend insulator @1, @3 on TOP PGR #47 Cause : Lightning | 1
51 | 2020-02-13 02:12 | February | 2:12 | Night | Thursday | Weekdays | 13 | 2020 | 2019-12-15 23:59 | CPI POWER SYSTEM |  |  |  | Normal Condition | - | Normal System Condition. | 1
52 | 2020-02-13 04:21 | February | 4:21 | Morning | Thursday | Weekdays | 13 | 2020 | 2019-12-16 11:33 | 13.8KV ROKAN FEEDER #4 | Bangko-Balam | PGT North | Cloudy | Tree | 0 | ROKAN VCB feeder #4 T/R 1x Not Checked Yet | 1
| 2020-02-13 04:21 | February | 4:21 | Morning | Thursday | Weekdays | 13 | 2020 | 2019-12-20 09:29 | 13.8KV ROKAN FEEDER #4 | Bangko-Balam | PGT North | Cloudy | Tree | 0 | Checked And Found RKNSB VCB4 Fdr # 4 T/R 2x, Ctr 776/778, R/F 51N Patrolled The Line And Found Sawit Menyentuh Line On Pole Rs/Rt/01 Cause: Tree | 1
53 | 2020-02-13 07:28 | February | 7:28 | Morning | Thursday | Weekdays | 13 | 2020 | 2019-12-16 14:04 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Cloudy | Lightning | 47 | BKO VCB fdr #4 T/R 2x Not Checked Yet | 1
| 2020-02-13 08:28 | February | 8:28 | Morning | Thursday | Weekdays | 13 | 2020 | 2019-12-19 08:12 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Cloudy | Lightning | 47 | Checked And Found BKOSB OCB4 Fdr # 4 T/R 2x, Ctr 76/78, R/F 51N Patrolled The Line And Found Broken La @2 On Pole 25 Ac 39 Cause: Lightning | 1
54 | 2020-02-13 14:52 | February | 14:52 | Afternoon | Thursday | Weekdays | 13 | 2020 | 2019-12-16 14:56 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Tree | 14 | ROKAN VCB feeder #2 T/R 2x Not Checked Yet | 1
| 2020-02-13 14:52 | February | 14:52 | Afternoon | Thursday | Weekdays | 13 | 2020 | 2019-12-20 09:32 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Tree | 14 | Checked And Found RKNSB VCB2 Fdr # 2 T/R 3x, Ctr 1312/1315, R/F 51N Patrolled The Line And Found Pohon Tinggi Menyentuh Line On / Phase @2,3, Pole 31/Av/10 / Phase @2,3, Pole 31/Av/15 / Phase @2,3, Pole 30/Av/19 Cause: Tree | 1
55 | 2020-02-13 14:54 | February | 14:54 | Afternoon | Thursday | Weekdays | 13 | 2020 | 2019-12-16 15:08 | 44KV PEMATANG MAIN / RANGAU LINE | Bekasap | PGT North | Rain and Lightning | Tree | 33 | 44 kV GCB PMT Main feeder #2 (line to RANGAU) Not Checked Yet | 1
| 2020-02-14 07:57 | February | 7:57 | Morning | Friday | Weekdays | 14 | 2020 | 2019-12-20 15:05 | 44KV PEMATANG MAIN / RANGAU LINE | Bekasap | PGT North | Rain and Lightning | Tree | 33 | Checked And Found PMTMSB/44OCB2 Fdr #2 T/R 11111x, Ctr 40006/51117, R/F 50N Patrolled The Line And Found Pohon Akasia Menyentuh Line On Pole Rgu/14 Cause: Tree | 1
56 | 2020-02-14 15:32 | February | 15:32 | Afternoon | Friday | Weekdays | 14 | 2020 | 2019-12-17 09:47 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 67 | 09:47 Manual Open RCL 16/Z/25 (So Balam fdr #1), closed at 10:31 for MTCE team close HLC to tie in line for BLM #90 Cause: Planned Outage for Construction | 1
57 | 2020-02-14 16:10 | February | 16:10 | Afternoon | Friday | Weekdays | 14 | 2020 | 2019-12-17 13:06 | KETIGUL SUBSTATION | Bangko-Balam | PGT North | Heavy Rain | Lightning | 28 | 13:06 115 kV line Rokan / Ketigul T/SO, freq reach to 60.14 Hz GCB #11 RKN T/SO, closed at 13:26 GCB #1 KTGL T/SO, closed at 13:26 GCB #2 KTGL T/SO, closed at 13:27 GCB #43 CD T/R 1x, R/F: 67N, 50P @2 GCB #45 CD no TRIP Indication PMT fdr #1 load dropped 188 A (212 / 24 A) PMT fdr #2 load dropped 99 A (103 / 4 A) RGU fdr #1 load dropped 39 A (70 / 31 A) RGU fdr #2 load dropped 137 A (173 / 36 A) PTN fdr #1 load dropped 230 A (247 / 17 A) PTN fdr #2 load dropped 60 A (64 / 4 A) RKN fdr #2 load dropped 22 A (23 / 1 A) RKN fdr #3 load dropped 24 A (29 / 5 A) RKN fdr #4 load dropped 8 A (12 / 4 A) KTG fdr #1 load dropped 32 A (107 / 75 A) KTG fdr #2 load dropped 26 A (89 / 63 A) KTG fdr #3 load dropped 19 A (44 / 25 A) BLM fdr #4 load dropped 6 A (179 / 173 A) NLA fdr #1 load dropped 40 A (215 / 175 A) NLA fdr #2 load dropped 10 A (76 / 66 A) BKO fdr #1 load dropped 34 A (187 / 153 A) BKO fdr #3 load dropped 17 A (242 / 225 A) BKO fdr #4 load dropped 10 A (170 / 160 A) MGL fdr #1 load dropped 34 A (187 / 153 A) MGL fdr #2 load dropped 143 A (164 / 21 A) 13:26 RCL cap bank of Nella SS tripped, closed at 13:52 RCL cap bank of Sintong SS tripped, closed at 13:55 14:52 Checked and found at Ketigul SS (Joko Susilo) GCB #1 KTG operate 2x, ctr: 203 / 205, R/F: 87L @2; 21G/Z1 GCB #2 KTG operate 1x, ctr: 177 / 178 Patrolled the line from KTGL SS and found: / Broken 115 kV LA @2 at ex temp Gulamo SS 15:17 Checked and found at Rokan SS (Mukhlis) GCB #11 RKN operate 2x, ctr: 35 / 37, R/F at D60: 21G/Z1, 67N; R/F at L90: 21G/Z2, 67N, 87L Cause: Not Patrolled Yet | 1
| 2020-02-14 16:10 | February | 16:10 | Afternoon | Friday | Weekdays | 14 | 2020 | 2019-12-18 15:13 | KETIGUL SUBSTATION | Bangko-Balam | PGT North | Heavy Rain | Lightning | 28 | Checked And Found / KTGL GCB1 Operate 2x, Ctr 203/205, R/F 21 / KTGL GCB2 Operate 1x, Ctr 177/178, R/F 87 Patrolled The Line And Found Broken La @2 On Pole Ex Gulamo Substation / RKNSB GCB11 Operate 2x, Ctr 35/37, R/F 87 Patrolled The Line And Found Broken La @2 On Pole Rknsb Gcb11 Cause: Lightning | 1
58 | 2020-02-15 07:36 | February | 7:36 | Morning | Saturday | Weekends | 15 | 2020 | 2019-12-17 15:18 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Cloudy | Pin Insulator | 15 | 8C fdr #4 T/R 1x Not Checked Yet | 1
| 2020-02-15 10:42 | February | 10:42 | Morning | Saturday | Weekends | 15 | 2020 | 2019-12-19 15:17 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Cloudy | Pin Insulator | 15 | Checked And Found 8CSB VCB4 Fdr # 4 T/R 1x, Ctr 629/630, R/F 51N Patrolled The Line And Found Broken Pin Insulator On Phase @2 Pole 8D/59 Cause: Pin Insulator | 1
59 | 2020-02-15 10:42 | February | 10:42 | Morning | Saturday | Weekends | 15 | 2020 | 2019-12-17 22:19 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Unidentified | 15 | Darling VCB fdr#3 T/R 1x Not checked yet | 1
| 2020-02-15 10:50 | February | 10:50 | Morning | Saturday | Weekends | 15 | 2020 | 2019-12-20 09:37 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Unidentified | 15 | Checked And Found DRLG3 VCB3 Fdr # 3 T/R 1x, Ctr 264/265, R/F 51N Patrolled The Line But Found Nothing On Phase @0,2 Cause: Unidentified | 1
60 | 2020-02-15 10:50 | February | 10:50 | Morning | Saturday | Weekends | 15 | 2020 | 2019-12-18 08:37 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Animal | 0 | N.Duri VCB feeder #2 T/R 1X. Not checked yet. | 1
| 2020-02-15 12:08 | February | 12:08 | Afternoon | Saturday | Weekends | 15 | 2020 | 2019-12-21 11:10 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Animal | 0 | Checked And Found NDRSB VCB2 Fdr #2 T/R 1x, Ctr 285/286, R/F 51N Patrolled The Line And Found Monkey Dead At Fco On Phase @2 Pole 13 G2 40 Cause: Animal | 1
61 | 2020-02-15 12:08 | February | 12:08 | Afternoon | Saturday | Weekends | 15 | 2020 | 2019-12-18 16:40 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 14 | Nella 13.8 KV GFPC T/R 1X. Nella VCB feeder#1 load dropped 115A (211/96A). Not checked yet. | 1
62 | 2020-02-15 12:13 | February | 12:13 | Afternoon | Saturday | Weekends | 15 | 2020 | 2019-12-18 18:02 | 13.8KV NORTH DURI FEEDER #11 | Duri | PGT North | Fair | Unidentified | 0 | N Duri.VCB Feeder#11 T/R 1x Not checked yet. | 1
| 2020-02-15 12:13 | February | 12:13 | Afternoon | Saturday | Weekends | 15 | 2020 | 2019-12-21 11:12 | 13.8KV NORTH DURI FEEDER #11 | Duri | PGT North | Fair | Unidentified | 0 | Checked And Found NDRSB VCB11 Fdr #11 T/R 1x, Ctr 194/195, R/F 51N Patrolled The Line But Found Nothing On Cause: Unidentified | 1
63 | 2020-02-15 12:24 | February | 12:24 | Afternoon | Saturday | Weekends | 15 | 2020 | 2019-12-18 21:26 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Pin Insulator | 76 | PETANI feeder #1 T/R 1x PETANI feeder #2 load dropped 14 A (63 / 49 A) Not Checked Yet | 1
| 2020-02-15 12:24 | February | 12:24 | Afternoon | Saturday | Weekends | 15 | 2020 | 2019-12-20 09:41 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Pin Insulator | 76 | Checked And Found PTNSB OCB1 Fdr # 1 T/R 1x, Ctr 145/146, R/F 51N Patrolled The Line And Found Pin Flash Over On Phase @1 Pole Petani #20 Cause: Pin Insulator | 1
64 | 2020-02-15 17:01 | February | 17:01 | Afternoon | Saturday | Weekends | 15 | 2020 | 2019-12-19 09:40 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Fair | Planned Maintenance | 0 | 09:40 Manual Open LBS 34/CA/04, closed at 12:44 to cut dead trees near 36/BT/13/14 Cause: Planned Maintenance | 1
65 | 2020-02-15 17:47 | February | 17:47 | Afternoon | Saturday | Weekends | 15 | 2020 | 2019-12-20 16:30 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 16:30 MGT #10 Off line and then S/D unit for standby. | 1
66 | 2020-02-15 17:47 | February | 17:47 | Afternoon | Saturday | Weekends | 15 | 2020 | 2019-12-20 16:33 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 16:32 S/U NDC#2 and then Online the unit at 17:26. | 1
67 | 2020-02-15 18:20 | February | 18:20 | Afternoon | Saturday | Weekends | 15 | 2020 | 2019-12-20 17:45 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 17:45 MGT#6 Off line and then S/D the unit for standby. | 1
68 | 2020-02-16 10:25 | February | 10:25 | Morning | Sunday | Weekends | 16 | 2020 | 2019-12-20 18:45 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 18:45 MGT #3 offline and then S/D for standby | 1
69 | 2020-02-17 08:19 | February | 8:19 | Morning | Monday | Weekdays | 17 | 2020 | 2019-12-20 19:40 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 19:40 MGT #2 offline and then S/D for standby | 1
70 | 2020-02-17 08:19 | February | 8:19 | Morning | Monday | Weekdays | 17 | 2020 | 2019-12-20 20:51 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 20:51 MGT #4 offline and then S/D for standby | 1
71 | 2020-02-18 14:04 | February | 14:04 | Afternoon | Tuesday | Weekdays | 18 | 2020 | 2019-12-20 21:48 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 21:48 MGT #1 offline and then S/D for standby | 1
72 | 2020-02-19 08:58 | February | 8:58 | Morning | Wednesday | Weekdays | 19 | 2020 | 2019-12-21 06:35 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Fair | Pin Insulator | - | Duri Community VCB feeder #2 T/R 1x Not Checked Yet | 1
| 2020-02-19 08:58 | February | 8:58 | Morning | Wednesday | Weekdays | 19 | 2020 | 2019-12-24 08:59 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Fair | Pin Insulator | - | Checked And Found DCSG ACB30 Fdr #30 T/R 1x, Ctr 111/134, R/F 51N Patrolled The Line And Found Pin Sompel Di Bagian Bawah On Phase @2,3 Pole 2F/16A Cause: Pin Insulator | 1
73 | 2020-02-19 09:01 | February | 9:01 | Morning | Wednesday | Weekdays | 19 | 2020 | 2019-12-21 07:05 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Lightning | 67 | NKBS OCB feeder #2 T/R 1x. NKBS GFPC T/R 1x. NKBS feeder #3 load dropped 67A (93/26A). NKBS feeder #4 load dropped 175A (192/17A). NKBS feeder #5 load dropped 143A (176/33A). CKBS feeder #1 load dropped 13A (223/210A). CKBS feeder #2 load dropped 214A (259/45A). PTP feeder #6 load dropped 22A (65/43A). Not checked yet. | 1
| 2020-02-19 09:04 | February | 9:04 | Morning | Wednesday | Weekdays | 19 | 2020 | 2019-12-23 07:31 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Lightning | 67 | Checked And Found NKBKSB OCB2 Fdr #2 T/R 2x, Ctr 99929/99931, R/F 51 Patrolled The Line But Found Nothing On Phase @2,3 Cause: Lightning | 1
74 | 2020-02-19 10:56 | February | 10:56 | Morning | Wednesday | Weekdays | 19 | 2020 | 2019-12-21 21:57 | 115KV CENTRAL DURI / BATANG LINE | Duri | PGT North | Rain | Over voltage | 261 | 21:57 115 kV Line CD / STG Tripped, freq. reach to 60.49 Hz / CD GCB #31 T/R 2x, / CD GCB #33 T/R 3x / STG GCB #25 T/SO, manual closed at 22:16, OK. / BATANG SS is temporary down > Batang feeder #1 dropped 32 A (32 / 0 A) > Batang feeder #2 dropped 51 A (51 / 0 A) > Batang feeder #3 dropped 70 A (70 / 0 A) / PNG fdr #1 load dropped 62 A (92 / 30 A) / NLA fdr #1 load dropped 119 A (211 / 92 A) / NLA fdr #2 load dropped 53 A (76 / 23 A) / BKO fdr #1 load dropped 127 A (154 / 27 A) / BKO fdr #2 load dropped 233 A (252 / 19 A) / BKO fdr #3 load dropped 92 A (225 / 133 A) / BKO fdr #4 load dropped 90 A (176 / 86 A) / STG fdr #1 load dropped 58 A (91 / 33 A) / STG fdr #1 load dropped 164 A (242 / 78 A) / BLM fdr #1 load dropped 126 A (142/ 16 A) / BLM fdr #3 load dropped 99 A (100 / 1 A) / BLM fdr #4 load dropped 153 A (182/ 29 A) / MGL fdr #1 load dropped 88 A (185 / 97 A) / MGL fdr #2 load dropped 133 A (160 / 27 A) / KTG fdr #1 load dropped 65 A (97 / 32 A) / KTG fdr #2 load dropped 29 A (89 / 60 A) / KTG fdr #3 load dropped 31 A (44 / 13 A) / BKS fdr #2 load dropped 71 A (262 / 191 A) / BKS fdr #3 load dropped 66 A (184 / 118 A) / BKS fdr #5 load dropped 118 A (327 / 209 A) / BKS fdr #6 load dropped 33 A (76 / 43 A) / PMT fdr #1 load dropped 170 A (203 / 33 A) / PMT fdr #2 load dropped 82 A (106 / 69 A) / RGU fdr #1 load dropped 10 A (58 / 48 A) / RGU fdr #2 load dropped 82 A (151 / 69 A) / PTN fdr #1 load dropped 161 A (234 / 73 A) / PTN fdr #2 load dropped 43 A (63 / 20 A) / LBO fdr #1 load dropped 8 A (66 / 58 A) / PGT fdr #1 load dropped 6 A (72 / 66 A) / PGT fdr #2 load dropped 13 A (60 / 47 A) / DRL fdr #4 load dropped 49 A (63 / 14 A) / DRL fdr #7 load dropped 47 A (104 / 57 A) Checked and found at Central Duri: / GCB #31 CD operate 2x, ctr: 47 / 49, R/F: 50N, 67N, 21P/Z2, 21G/Z2, 87L / GCB #33 CD operate 3x, ctr: 654 / 657, R/F: 21P/Z1, 21G/Z1 / GCB #25 STG operate 1x, ctr: 320 / 321, R/F: 87L Cause: Under Investigation | 1
| 2020-02-19 10:56 | February | 10:56 | Morning | Wednesday | Weekdays | 19 | 2020 | 2019-12-27 09:27 | 115KV CENTRAL DURI / BATANG LINE | Duri | PGT North | Rain | Over voltage | 261 | Checked And Found / CDRSY/115OCB31 T/LO , Ctr 49/53, R/F 87 / CDRSY/115OCB33 T/LO , Ctr 657/664, R/F 21 Patrolled The Line And Found Broken La On Phase @2,3, Pole Structure Cd Sy Cause: Over voltage | 1
75 | 2020-02-20 06:59 | February | 6:59 | Morning | Thursday | Weekdays | 20 | 2020 | 2019-12-21 23:49 | CENTRAL DURI SWITCH YARD | Duri | PGT North | Fair | Over voltage | - | 23:49 C Duri 115 KV OCB #11 TRIP 115 KV line Incoming Tx #1 C Duri S. Y C Duri 115 KV OCB #13 TRIP. C Duri ACB #14 ( Breaker secondary Tx #1 to Bus #1 CDGT ). C Duri 115 kV GCB #45 TRIP, manual closed at 01:13. 00:21 C Duri 115KV GCB #43 Trip C Duri 115KV GCB #41 Trip C Duri 115KV OCB #63 Trip C Duri 115KV OCB #23 Trip, manual closed at 00:56 C Duri 115KV OCB #21 Trip C Duri 115KV GCB #15 Trip, manual closed at 01:05. C Duri 115KV GCB #10 Trip C Duri 115KV GCB #11 Trip Duri 115KV OCB #32 Trip Duri 115KV OCB #30 Trip Checked and found: *GCB #15 Close, GCB #13 Open, GCB #11 Open TXP/1 Central Duri Shutdown Relay Flag TX#1 : Current, Phase A/B, Netral Ground Relay Flag Line Duri/2 : 87L, 21G. GCB #10 Open. GCB #25 Close, GCB #23 Open, GCB #21 Open 115 kV CD Line 1 – DRB still energize from DRB (GCB #22/ #24 Close) GCB #45 Open, GCB #43 Open, GCB #41 Open. GCB #65 Close, GCB #63 Open. 00:22 5B 13.8KV OCB Fdr#4 Trip Close at.01:44. 5B 13.8KV OCB Fdr#5 Trip Close at.01:44. 00:56 Sintong 115KV OCB #22 Trip Close at 01:20. Batang 115KV OCB #1 Trip Close at 01:18. 00:58 Bangko 115KV Circuit switcher Trip 01:16 Manually Open Sintong 13.8KV VCB Fdr#1 Manually Open Sintong 13.8KV VCB Fdr#2 01:17 Sintong 115KV OCB #21 Trip Sintong 115KV OCB #23 Trip 01:19 Manually Open Menggala 13.8KV OCB Fdr#1. Manually Open Menggala 13.8KV OCB Fdr#2. 01:24 Manually Open Menggala 115KV Circuit switcher. 01:20 Manually Open Nella 115KV GCB#27 Manually Open Ketigul 13.8KV VCB Fdr#2 Manually Open Ketigul 13.8KV VCB Fdr#3 01:26 Manually Close Rokan 115KV GCB#12 (but failed to closed) 01:29 Sintong 115KV OCB#25 Trip 01:29 C Duri 115KV OCB#31 T/R C Duri 115KV OCB#33 T/R. Continued to 02:22 //> | 1
| 2020-02-20 06:59 | February | 6:59 | Morning | Thursday | Weekdays | 20 | 2020 | 2019-12-22 02:22 | CENTRAL DURI SWITCH YARD | Duri | PGT North | Fair | Over voltage | - | 02:22 Manually Open C Duri 115KV ACB#15 Checked and found: @1 LA Broken near 115 KV OCB #13 at C Duri S.Yard. ( 115 KV line to Line #2 and to TX #1 ). @1 LA Broken near 115 KV OCB #43 at C Duri S.Yard. ( 115 KV line to Pematang ). 02:53 IT netwok down and restore at 03:40. 03:37 Manually Close Sintong 115KV ACB#25. 03:37 Manually Close Sintong 115KV ACB#23. 03:37 Manually Close Sintong 115KV ACB#23. 03:39 Manually Close Rokan 115KV ACB#12. 03:41 Manually Open Ketigul Feeder#1. 03:42 Manually Open Ketigul Feeder#2. 03:42 Manually Open Ketigul Feeder#3. 03:43 Manually Close Ketigul 115KV GCB#3. 03:44 Manually Close Ketigul 115KV GCB#2. 03:45 Manually Close Ketigul 13.8KV VCB Fdr#1. 03:46 Manually Close Ketigul 13.8KV VCB Fdr#2. 03:51 Manually Close Ketigul 13.8KV VCB Fdr#3. 03:48 115KV C.Duri / Batang ACB#31 T/R. 03:48 115KV C.Duri / Batang ACB#33 T/R. 03:48 115KV C.Duri / Batang ACB#1 T/O. 04:15 Manually Close Menggala 115KV Circuit switcher 04:16 Manually Close Menggala 13.8KV OCB Fdr#1. 04:17 Manually Close Menggala 13.8KV OCB Fdr#2. 04:20 Offline CDGT #2 ( due to supply power to TX #1 Trip open). 04:28 Manually Close C Duri 13.8KV ACB# 19 ( Tie Bus ). 04:34 Manually Close Sintong 115KV ACB#21 04:35 Manually Close Sintong 13.8KV VCB Fdr#2. 04:35 Manually Close Sintong 13.8KV VCB Fdr#1. 04:44 CDGT #3 Trip by alarm Exhaust High Spread Trip. 04:50 Manually Close Bangko 115KV Circuit switcher (but failed to closed) 05:20 Manually Close Bangko 115KV Circuit switcher //> OK 05:30 Manually Close Bangko 13.8KV VCB Fdr#3. 05:30 Manually Close Bangko 13.8KV VCB Fdr#4. 05:40 Manually Open Bangko 13.8KV VCB Fdr#4. 05:42 Manually Close Bangko 13.8KV VCB Fdr#4. 05:56 Manually Close Bangko 13.8KV VCB Fdr#2 05:23 Manually Close Nella 115KV Circuit switcher (OK) Continued to 07: 23 //> | 1
| 2020-02-20 10:30 | February | 10:30 | Morning | Thursday | Weekdays | 20 | 2020 | 2019-12-22 07:23 | CENTRAL DURI SWITCH YARD | Duri | PGT North | Fair | Over voltage | - | 07:23 Manually Block & Closed Sintong OCB feeder #1 //> OK. and then released the block. 07:52 Manually Block & Closed Bangko OCB feeder #1 //> OK. and then released the block. 07:54 Manually Block & Closed Nella OCB feeder #1 //> OK. and then released the block. 07:56 Manually Block & Closed Nella OCB feeder #2 //> OK. and then released the block. 08:22 Manually Block & Closed Menggala OCB feeder #2 //> OK. and then released the block. 08:23 Manually Block & Closed Menggala OCB feeder #1 //> OK. and then released the block. Patrolled Result 115KV Sintong / Batang Line. ~@1 Broken dead end Insulator o/p STG #87. ~Rubber tree near power line o/p STG #63. ~Pruning is done. 09:20 Bangko Voltage Regulator Checked & found VR: Raise 3 Bus voltage :13.6KV Closed Recloser for Cap Bank Bus voltage :13.8 KV VR:Netral 11:00 Open both side isolation switch of 115KV C.Duri S Yard OCB#13. Open both side isolation switch of 115KV Duri Ring Bus OCB#30. Open both side isolation switch of 115KV Duri Ring Bus OCB#32. * Due to Dismantle @1,2,3 broken 115KV L.A. 10:32 Closed both side isolation switch of 115Kv OCB#13 10:41 Closed both side isolation switch of 115Kv OCB#30 10:41 Closed both side isolation switch of 115Kv OCB#32. 11:14 Manually open S Balam VCB feeder #1. due to Bus Voltage 12.3 KV. 12:56 Manually closed 115KV Duri Ring Bus OCB#30 //> OK. 12:57 Manually closed 115KV Duri Ring Bus OCB#30 //> OK. 13:03 Manually closed 115KV C.Duri S Yard GCB#15 //> OK. 13:03 Manually closed 115KV C.Duri S Yard OCB#13 //> OK. 13:04 Manually closed 115KV C.Duri S Yard OCB#11 //> OK. 13:08 Manually closed 115KV C.Duri S Yard GCB#10 //> OK. 13:09 Manually closed 115KV C.Duri S Yard OCB#21 //> OK. 13:09 Manually closed 115KV C.Duri S Yard GCB#43 //> OK. 13:10 Manually closed 115KV C.Duri S Yard GCB#41 //> OK. 13:11 Manually closed 115KV C.Duri S Yard OCB#63 //> OK. 15:09 Manually block & closed 115Kv Batang OCB#1 //> but trip again. *115Kv C.Duri GCB#45 T/R 1x *115Kv C.Duri GCB#43 T/R 1x Batang substation no powe at same time. / Batang OCB Feeder#1. / Batang OCB Feeder#2. / Batang OCB Feeder#3. 16:05 S/U CDGT #3 and then Online the unit at 16:22. 16:15 Manually closed Recloser for Cap Bank at Sintong substation . Bus Voltage: 13.2 t0 13.7 KV. 16:41 Manually closed Recloser for Cap Bank at Nella substation . Bus Voltage: 13.2 t0 13.6 KV. 16:41 Manually closed Recloser for Cap Bank at Bangko substation . Bus Voltage :13.2 to 13.7 KV Voltage regulator: Raise – 16. Continue Patrolled 115 KV Batang / Sintong Line. / Suspected L.A near Batang substation . / Suspected @1 L.A On pole Sintong #26. 17:01 S/U CDGT #5 and then Online the unit at 17:18. 18:18 Dismantle @1,2,3 L.A on pole Sintong #26. 18:25 CDGT #3 TRip by alarm Exhaust Spread High Trip. 18:43 Manually block & closed 115Kv OCB#1 at Batang //> OK. 18:44 Manually block & closed 115Kv OCB#25 at Sintong //> OK. ( 115 KV Batang / Sintong Line back to Normal ). Cause: Under Investigation. | 1
| 2020-02-20 11:16 | February | 11:16 | Morning | Thursday | Weekdays | 20 | 2020 | 2019-12-27 09:36 | CENTRAL DURI SWITCH YARD | Duri | PGT North | Fair | Over voltage | - | Checked And Found / CDRSY/115GCB15 T/SO, Ctr 196/196, R/F 87 / CDRSY/115OCB11 T/SO, Ctr 23/24, R/F 51N / CDRSY/115OCB13 T/SO, Ctr 27/29, R/F 21AG / DRIRB/115OCB30 T/SO, Ctr 100/101, R/F 87 / DRIRB/115OCB32 T/SO , Ctr 40/41, R/F 21AG Patrolled The Line And Found Broken LA On Phase @1 Pole Structure Cd Sy Cause: Over voltage | 1
76 | 2020-02-20 13:58 | February | 13:58 | Afternoon | Thursday | Weekdays | 20 | 2020 | 2019-12-21 23:49 | SOUTH BALAM SUBSTATION | Bangko-Balam | PGT North | Fair | Voltage regulator failure | 451 | 23:49:01 South Balam 115 KV Circuit Switcher TRIP. No power at Balam Substation. / S Balam VCB feeder #1. / S Balam VCB feeder #2. / S Balam VCB feeder #3. / S Balam VCB feeder #4. 01:26:00 Manually open S Balam 13.8KV VCB Fdr#1. Manually open S Balam 13.8KV VCB Fdr#2. Manually open S Balam 13.8KV VCB Fdr#3. Manually open S Balam 13.8KV VCB Fdr#4. 06:37 Manually Close S Balam 115KV Circuit switcher //> OK. 06:42 Manually Open S Balam 115KV Circuit switcher. Due to unbalance on Voltage Regulator and then Bypass it. 06:48 Manually Close S Balam 115KV Circuit switcher //> OK. 06:52 Manually Blocked & Close Balam 13.8KV VCB Fdr#3 //> OK. 06:53 Manually Blocked & Close Balam 13.8KV VCB Fdr#2 //> OK. 06:54 Manually Blocked & Close Balam 13.8KV VCB Fdr#1 //> OK. 06:54 Manually Blocked & Close Balam 13.8KV VCB Fdr#4 //> OK. 11:14 Manually open S Balam 13.8KV VCB Fdr#1. due to maintain voltage on Bus. ( Bus voltage: 12.3 KV ). 18:54 Manually Blocked & Close Balam 13.8KV VCB Fdr#1 //> OK. Bus voltage: 13.1 KV. (After closed 115 KV Batang / Sintong Line). Cause: Voltage Regulator. | 1
77 | 2020-02-20 13:58 | February | 13:58 | Afternoon | Thursday | Weekdays | 20 | 2020 | 2019-12-22 00:57 | ROKAN SUBSTATION | Bangko-Balam | PGT North | Fair | Unidentified | 36 | 00:57 115 KV Rokan Circuit Switcher Trip. / Relay Flag : PNCT Diff. / Relay Flag : 51. 01:20 Manually Open Rokan 13.8KV VCB Fdr#2. Manually Open Rokan 13.8KV VCB Fdr#3. Manually Open Rokan 13.8KV VCB Fdr#4. 04:00 Manually Close 115KV Rokan Circuit swicher //> OK. 04:01 Manually Blocked & Close Rokan 13.8KV VCB Fdr#2. 04:02 Manually Blocked & Close Rokan 13.8KV VCB Fdr#3. 04:02 Manually Blocked & Close Rokan 13.8KV VCB Fdr#4. Cause: Not patrolled yet. | 1
| 2020-02-20 14:15 | February | 14:15 | Afternoon | Thursday | Weekdays | 20 | 2020 | 2019-12-27 09:24 | ROKAN SUBSTATION | Bangko-Balam | PGT North | Fair | Unidentified | 36 | Checked And Found RKNSB/115CS T/O, Ctr 224/225, R/F 87 Patrolled The Line But Found Nothing Cause: Unidentified | 1
78 | 2020-02-20 14:15 | February | 14:15 | Afternoon | Thursday | Weekdays | 20 | 2020 | 2019-12-22 08:54 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Lightning | 14 | Nella VCb feeder #1 T/R 1x. Nella GFPC T/R 1x. Not checked yet. | 1
| 2020-02-20 15:55 | February | 15:55 | Afternoon | Thursday | Weekdays | 20 | 2020 | 2019-12-29 08:10 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Lightning | 14 | Checked And Found NLASB VCB1 Fdr #1 T/R 2x, Ctr 567/569, R/F 51N Patrolled The Line And Found: / Pin Flash Over On Phase @1 Pole 20 T 05 / Dead End Broken 5% On Phase @2 Pole 20 T 18 Cause: Lightning | 1
79 | 2020-02-21 11:56 | February | 11:56 | Morning | Friday | Weekdays | 21 | 2020 | 2019-12-22 16:05 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 16:05 S/U CDGT #3 and then online at : 16:22. | 1
80 | 2020-02-21 11:56 | February | 11:56 | Morning | Friday | Weekdays | 21 | 2020 | 2019-12-22 17:01 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 17:01 S/U CDGT #5 and then online at : 17:18. | 1
81 | 2020-02-21 14:02 | February | 14:02 | Afternoon | Friday | Weekdays | 21 | 2020 | 2019-12-22 17:24 | 13.8KV NORTH DURI FEEDER #6 | Duri | PGT North | Heavy Rain | Lightning Arrester | - | N Duri VCB feeder #6 T/R 1x. Not checked yet. | 1
| 2020-02-22 06:38 | February | 6:38 | Morning | Saturday | Weekends | 22 | 2020 | 2019-12-27 08:15 | 13.8KV NORTH DURI FEEDER #6 | Duri | PGT North | Heavy Rain | Lightning Arrester | - | Checked And Found NDRSB VCB6 Fdr #6 T/R 1x, Ctr 314/315, R/F 51N Patrolled The Line And Found Jumper La Putus On Phase @2 Pole 12/F11/04 Cause: Lightning Arrester | 1
82 | 2020-02-22 11:40 | February | 11:40 | Morning | Saturday | Weekends | 22 | 2020 | 2019-12-22 18:25 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 18:25 CDGT #3 Trip by Alarm Exhaust Hight Spread trip. | 1
83 | 2020-02-22 12:40 | February | 12:40 | Afternoon | Saturday | Weekends | 22 | 2020 | 2019-12-22 20:26 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 20:26 Started Up CGT #2 and On Line to the system at 20:47 | 1
84 | 2020-02-23 06:30 | February | 6:30 | Morning | Sunday | Weekends | 23 | 2020 | 2019-12-23 10:56 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 10:56 S/U CDGT #3 and then on line at:11:14. | 1
85 | 2020-02-23 06:30 | February | 6:30 | Morning | Sunday | Weekends | 23 | 2020 | / | MINAS POWER PLANT | Minas | PGT South |  |  | - | / | 1
86 | 2020-02-23 10:27 | February | 10:27 | Morning | Sunday | Weekends | 23 | 2020 | 2019-12-23 23:59 | CPI POWER SYSTEM |  |  |  | Normal Condition | - | Normal System Condition. | 1
87 | 2020-02-24 01:07 | February | 1:07 | Night | Monday | Weekdays | 24 | 2020 | 2019-12-24 06:33 | 13.8KV BATANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Others | 0 | Batang 13.8KV OCB fdr #1 T/R 1X. Batang GFPC T/R 1X. Not checked yet. | 1
| 2020-02-24 01:07 | February | 1:07 | Night | Monday | Weekdays | 24 | 2020 | 2019-12-27 16:14 | 13.8KV BATANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Others | 0 | Checked And Found BTGSB OCB1 T/O , Ctr 163/171, Patrolled The Line And Found Flash Over Pin Ins At Batang 02 On Phase @3 Pole None Cause: Others | 1
88 | 2020-02-24 09:06 | February | 9:06 | Morning | Monday | Weekdays | 24 | 2020 | 2019-12-24 09:08 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 759 | 09:08 Menggala OCB feeder #1 Load Dropped 77A (184/103A). Menggala OCB feeder #2 Load Dropped 133A (163/30A). Not Checked yet. JDE Number = 123 | 1
| 2020-02-24 13:59 | February | 13:59 | Afternoon | Monday | Weekdays | 24 | 2020 | 2019-12-29 08:43 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 759 | Checked and found: MGLSB/13.8OCB2 T/R, Counter : 557 / 559, Relay Flag : 51N. Patrol led the line found : Unidentified Phase : 0 Cause : Unidentified | 1
89 | 2020-02-24 13:59 | February | 13:59 | Afternoon | Monday | Weekdays | 24 | 2020 | 2019-12-24 09:32 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Lightning | 106 | S.Balam VCB feeder #4 T/R 1x. Not checked yet. | 1
| 2020-02-25 09:43 | February | 9:43 | Morning | Tuesday | Weekdays | 25 | 2020 | 2019-12-29 08:36 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Lightning | 106 | Checked And Found SBLM VCB4 Fdr #4 T/R 1x, Ctr 373/374, R/F 51N Patrolled The Line And Found Broken Pin Support Near Balam# 67 Dan Balam#37 On Phase @3 Cause: Lightning | 1
90 | 2020-02-25 09:45 | February | 9:45 | Morning | Tuesday | Weekdays | 25 | 2020 | 2019-12-24 10:09 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Cloudy | Pin Insulator | 73 | Libo OCB feeder #1 T/R 1x. Libo feeder #2 Load Dropped 18A (63/45A). Not checked yet. | 1
| 2020-02-25 15:02 | February | 15:02 | Afternoon | Tuesday | Weekdays | 25 | 2020 | 2019-12-26 07:27 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Cloudy | Pin Insulator | 73 | Checked And Found LBOSB OCB1 Fdr #1 T/R 1x, Ctr 597/598, R/F 51N Patrolled The Line And Found Flash Over Dead End On Phase @1 Pole 36 Cc 19A Cause: Pin Insulator | 1
91 | 2020-02-26 06:37 | February | 6:37 | Morning | Wednesday | Weekdays | 26 | 2020 | 2019-12-24 12:31 | 13.8KV BATANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Lightning | 0 | Batang OCB feeder #1 T/R 1x. Not cecked yet. | 1
| 2020-02-26 06:37 | February | 6:37 | Morning | Wednesday | Weekdays | 26 | 2020 | 2019-12-29 07:14 | 13.8KV BATANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Lightning | 0 | Checked And Found BTGSB OCB1 T/O, Ctr 163/171, Patrolled The Line But Found Nothing Cause: Lightning | 1
92 | 2020-02-26 11:35 | February | 11:35 | Morning | Wednesday | Weekdays | 26 | 2020 | 2019-12-25 08:34 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Fair | Pin Insulator | 0 | Duri Community ACB Fdr#1 T/R 1x Not checked yet | 1
| 2020-02-26 13:40 | February | 13:40 | Afternoon | Wednesday | Weekdays | 26 | 2020 | 2019-12-27 16:50 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Fair | Pin Insulator | 0 | Checked And Found DCSG ACB30 Fdr #2 T/R 1x, Ctr 111/145, R/F 51 Patrolled The Line And Found Broken Pin (Temuan Lama) On Phase @2,3 Pole 2F 16A Cause: Pin Insulator | 1
93 | 2020-02-26 13:47 | February | 13:47 | Afternoon | Wednesday | Weekdays | 26 | 2020 | 2019-12-25 09:06 | 13.8KV BATANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Lightning | - | 09:06 Batang OCB fdr#1 T/O (Supply power to PHE). Batang Ground fault alarm Checked & found Batang OCB fdr#1 Ctr: 163/171, R/F: None PHE teams Perform Patrolled the Line, but found nothing 13:00 Manual Block & Closed Batang OCB fdr#1, but Tripped again 13:45 Opened Isolation Switches Batang OCB fdrf#1 14:00 Manual Block & Closed Batang OCB fdr#1, Wait for 30 minutes, OK 14:30 Opened Back Batang OCB fdr#1, Closed back Isolation Switches. 20:45 Manually open Line Switch on pole 39/AH/51. 20:51 Manually blocked and closed Batang VCB feeder #1 //> OK. and then released the block. Continued patrolled tomorrow morning. DEC 26 2019 11:30 Manually Opened Batang VCB fdr#1 PHE team Open Line Switch O/P 39.AH.51 Replaced Flash Over Pin Insulator O/P Btg 71 Repaired Guywire O/P BTG 02 12:00 Closed Lines Switch O/P 39.AH.51 Manually Block & Closed Batang VCB fdr#1 13:13 Batang VCB fdr#1 & GFPC T/O PHE team Open Back Lines Switch to Troubleshoot 14:00 Manually Block & Closed Back Batang VCB fdr#1 Source: PHE team, continued troubleshoot DEC 27 2019 09:00 Open Fuse All Transformers under Batang VCB fdr#1 Closed Line Switch O/P 39.AH.51 17:00 Manually Block & Closed Batang VCB fdr#1, then released the Block Cause : Broken LA. (PHE Team) | 1
| 2020-02-26 15:29 | February | 15:29 | Afternoon | Wednesday | Weekdays | 26 | 2020 | 2019-12-29 07:15 | 13.8KV BATANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Lightning | - | Checked And Found BTGSB OCB1 T/O, Ctr 163/171, Patrolled The Line But Found Nothing Cause: Lightning | 1
94 | 2020-02-26 16:13 | February | 16:13 | Afternoon | Wednesday | Weekdays | 26 | 2020 | 2019-12-25 09:10 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Unidentified | 9 | 09:10 It was reported NO Power O/P 07.U1.17 (D.field Fdr#2) Checked & found Recl. 07.U1.19 T/O, Ctr: 10:10 Block & Closed the Recloser, then Released the Block. Cause: Unidentified | 1
95 | 2020-02-26 16:13 | February | 16:13 | Afternoon | Wednesday | Weekdays | 26 | 2020 | 2019-12-25 14:15 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Unidentified | 134 | 14:15 It was reported no Power o/p 03/01/26 (Cduri fdr#7) Checked & found Recl 03.01.39 T/O, Ctr: 188/189, R/F: None Also Found Recloser Unplug, No Batteries Installed, B/O control Card 18:05 Decided Transfer Load to CD fdr#6, by Closed LBS 03.01.02 Cause: Unidentified | 1
96 | 2020-02-26 16:15 | February | 16:15 | Afternoon | Wednesday | Weekdays | 26 | 2020 | 2019-12-26 06:10 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Equipment Failure | 152 | 06:10 Ketigul VCB feeder #2 T/O, 08:00 Checked & found KTG VCB fdr#2 T/LO, Ctr: 562/564, R/F: 51 @B 08:48 Manually BLock & Closed KTG VCB fdr#2, then released the Block Cause: Not Patrolled yet | 1
| 2020-02-26 17:50 | February | 17:50 | Afternoon | Wednesday | Weekdays | 26 | 2020 | 2019-12-27 16:10 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Equipment Failure | 152 | Checked And Found PKTGL VCB2 T/O , Ctr 224/226, R/F 51N Patrolled The Line And Found Broken Pt Of Cap Bank On Phase @1,2,3, Pole 32 Ak 43 Cause: Equipment Failure | 1
97 | 2020-02-27 17:43 | February | 17:43 | Afternoon | Thursday | Weekdays | 27 | 2020 | 2019-12-26 14:08 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 126 | Menggala VCB fdr#2 T/R 1x Menggala Fdr#1 Load dropped 95A (183/88A) Not checked yet | 1
| 2020-02-27 19:04 | February | 19:04 | Night | Thursday | Weekdays | 27 | 2020 | 2019-12-31 08:17 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 126 | Checked And Found MGLSB OCB2 Fdr #2 T/R 1x, Ctr 557/558, R/F 51N Patrolled The Line And Found Unidentified Cause: Unidentified | 1
98 | 2020-02-27 19:50 | February | 19:50 | Night | Thursday | Weekdays | 27 | 2020 | 2019-12-26 20:35 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Capasitor Bank | 140 | 20:35 Ketigul VCB feeder #1 T/O. 22:50 Checked and found Ketigul VCB feeder #1 T/SO. Counter: 224/226 R/F: 51 @1,2,3 and 51N. 23:52 Patrolled the line found burnt out fuse of a Potential Transformer for Cap bank on pole 42/AK/43. Isolate Cap Bank from line. 02:24 Manually block and closed Ketigul VCB feeder #1 //> OK. and then released the block. Cause: Potential transformer for Capacitor Bank. Production loss : 140 Bbls / 20 wells //> Up to 24:00. | 1
99 | 2020-02-27 19:53 | February | 19:53 | Night | Thursday | Weekdays | 27 | 2020 | 2019-12-27 04:48 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 04:48 CDGT #5 Trip by alarm Generator Electrical Trouble. | 1
100 | 2020-02-27 20:09 | February | 20:09 | Night | Thursday | Weekdays | 27 | 2020 | 2019-12-27 06:04 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Lightning Arrester | 0 | N Duri VCB feeder #2 T/R 1x. Not checked yet. | 1
| 2020-02-28 06:34 | February | 6:34 | Morning | Friday | Weekdays | 28 | 2020 | 2019-12-27 10:53 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Lightning Arrester | 0 | Checked And Found NDRSB VCB2 Fdr #2 T/R 1x, Ctr 286/287, R/F 51N Patrolled The Line And Found LA Putus Di Phese 2 On Phase @2 Pole Nf 07 F2 Cause: Lightning Arrester | 1
101 | 2020-02-28 11:35 | February | 11:35 | Morning | Friday | Weekdays | 28 | 2020 | 2019-12-27 11:13 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 24 | 11:13 Sintong Fdr#2 Load dropped 21A (225/204A) Sintong Fdr#2 Ground fault Alarm It was reported No Power at Genting Field 15:00 Checked & found Recl 29.Z.13A T/O, Ctr: 214/316, R/F: N.A Patrolled the Line, but found nothing Manually Block & Closed the Recloser, then released the block Cause: Unidentified | 1
102 | 2020-02-29 09:00 | February | 9:00 | Morning | Saturday | Weekends | 29 | 2020 | 2019-12-27 11:31 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Unidentified | 66 | NKB VCB fdr#2 T/R 1x Not checked yet | 1
| 2020-03-13 05:32 | March | 5:32 | Morning | Friday | Weekdays | 13 | 2020 | 2019-12-30 16:49 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Unidentified | 66 | Checked And Found NKBKSB OCB2 Fdr#2 T/R 1x Ctr:99931/99932 R/F:51N Patrolled The Line But Found Nothing. Cause: Unidentified | 1
103 | 2020-03-13 05:32 | March | 5:32 | Morning | Friday | Weekdays | 13 | 2020 | 2019-12-28 23:59 | CPI POWER SYSTEM |  |  |  | Normal Condition | - | Normal System Condition. | 1
104 | 2020-03-13 18:28 | March | 18:28 | Afternoon | Friday | Weekdays | 13 | 2020 | 2019-12-29 17:31 | 115KV KOTABATAK / PETAPAHAN LINE | Petko | PGT South | Fair | Under investigation | 2599 | 17:31 115Kv Line CKBS/Petapahan GCB#1 T/SO. No Power at Petapahan Subst & Suram Subst. 18:00 Checked All 115Kv Breakers & Line Switch Closed. 19:09 Checked and found CKBS 115 KV GCB#1 T/SO. and status spring Discharge Counter: 44/45. 19:30 Manually Open CKBS VCB feeder#6 (due to maintain level Tank). 19:35 Manually blocked and closed CKBS 115 KV GCB #1 , but failed. 21:45 Manually Open New Petapahan 115 KV GCB#5. 21:47 Manually Open New Petapahan 115 KV GCB#4. 23:25 Manually Block & Closed CKBS VCB feeder#6. 23:36 Manually Open NKBS 115 KV OCB #1. for Bypass CKBS 115 KV GCB #1. 23:41 Manually Block & Closed 115 KV OCB #1 //> OK. and then released the block. CKB Substation was energized. 23:47 Manually Closed 115 KV GCB #4 //> OK. (from DSC failed). 23:47 Manually Closed 115 KV GCB #5 //> OK. (from DSC failed). Petapahan Substation was energized. Cause: Under investigation. Production loss: CKB SUBSTATION. 1. CKBS VCB feeder #1 : 58 Bbls / 55 wells. + 88 Bbls 2. CKBS VCB feeder #2 : 28 Bbls / 64 wells. + 42 Bbls 3. CKBS VCB feeder #5 : 44 Bbls / 44 wells. + 66 Bbls. 4. CKBS VCB feeder #6 : 294 Bbls / 41 wells. +39 Bbls. PETAPAHAN SUBSTATION. 1. PTP VCB feeder #3 : 957 Bbls / 58 wells. +116 Bbls. 2. PTP VCB feeder #4 :1767 Bbls / 48 wells. + 98 Bbls. 3. PTP VCB feeder #6 : 309 Bbls / 9 wells. + 25 Bbls. 4. PTP VCB feeder #8 : 210 Bbls / 8 wells. + 36 Bbls. SURAM SUBSTATION. 1. Suram OCB feeder #2 : 17 Bbls / 3 wells. + 2 Bbls. /////////////////////////////////////////////// + Grand total : 3684 Bbls / 330 wells. + 512 Bbls. 4196 Bbls / 330 Wells. JDE Number = 12345 | 1
| 2020-03-13 18:28 | March | 18:28 | Afternoon | Friday | Weekdays | 13 | 2020 | 2019-12-30 08:50 | 115KV KOTABATAK / PETAPAHAN LINE | Petko | PGT South | Fair | Under investigation | 2599 | 02:00 It Was reported no Power at KBGS Area#2 Facility, 3 Unit WIPs, 6MVATX 06:57 Manually Opened CKB fdr#6, then Closed at 13:15. 07:06 Manually Opened CKB fdr#5, then closed at 14:33. (Requested KB GS for Maintain Level Tank). 08:50 Checked & found Recl. KB GS T/O Ctr:1010/1718. Blocked & Closed the Recl. then release the block. Cause: Recloser. | 1
105 | 2020-03-14 05:00 | March | 5:00 | Morning | Saturday | Weekends | 14 | 2020 | 2019-12-30 02:00 | 13.8KV NEW KOTABATAK FEEDER #4 | Petko | PGT South | Fair | Recloser | 1026 | 02:00 It Was reported no Power at KBGS Area#2 Facility, 3 Unit WIPs, 6MVATX 06:57 Manually Opened CKB fdr#6, then Closed at 13:15. 07:06 Manually Opened CKB fdr#5, then closed at 14:33. (Requested KB GS for Maintain Level Tank). 08:50 Checked & found Recl. KB GS T/O Ctr:1010/1718. Blocked & Closed the Recl. then release the block. Cause: Recloser. CKB SUBSTATION. 1. CKBS VCB feeder #5 : 488 Bbls / 40 wells. 2. CKBS VCB feeder #6 : 674 Bbls / 44 wells. __________________________________________ + Grand Total : 1162 Bbls / 84 wells | 1
106 | 2020-03-14 05:00 | March | 5:00 | Morning | Saturday | Weekends | 14 | 2020 | 2019-12-30 17:35 | KETIGUL SUBSTATION | Bangko-Balam | PGT North | Cloudy | Under investigation | 495 | 17:35 KETIGUL 115KV GCB#2 & GCB#3 T/O No Power to Ketigul Substation: 1. Ketigul VCB feeder#1. 2. Ketigul VCB feeder#2. Status Bypass. 3. Ketigul VCB feeder#3. 20:10 Checked and found: 1. Ketigul 115 KV GCB #2 T/O Counter: 178/180. 2. Ketigul 115 KV GCB #3 T/O Counter: 168/170. 3. @1 broken Bypass fuse on Ketigul VCB feeder #2. 4. Burnt out cable of NGR (Neutral Ground Resistant). 5. R/F Tx : Phase A,B to Ground. 20:11 Manually open Ketigul VCB feeder#1 Ketigul VCB feeder#2. Status Bypass. 20:14 Manually open Ketigul VCB feeder#3. (from DSC failed). Open @1,2,3 Bypass fuse. Patrolled the line found 21:37 Manually closed 115 KV GCB #3 //> OK. Monitor performance TX. 21:47 Manually closed 115 KV GCB #2. //> OK. Transfer Load Ketigul VCB feeder#2 to Ketigul VCB feeder#3 , by closed LBS: 34/AN/04. 22:10 Manually block and closed Ketigul VCB feeder#1//>OK. and then released the block. 22:12 Manually block and closed Ketigul VCB feeder#3 //>OK. and then released the block. Ketigul Substation back to Normal. Cause: Under Investigation. Production loss: Ketigul Substation. 1. Ketigul VCB feeder #1 : 216 Bbls / 20 wells. 2. Ketigul VCB feeder #2 : 258 Bbls / 21 wells. 3. Ketigul VCB feeder #3 : 37 Bbls / 2 wells. /////////////////////////////////////////////// + Grand total : 511 Bbls / 43 wells. | 1
107 | 2020-03-14 06:52 | March | 6:52 | Morning | Saturday | Weekends | 14 | 2020 | 2019-12-30 18:00 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 18:00 S/U CDGT #5 and then Online the unit at 18:22. | 1
108 | 2020-03-14 09:20 | March | 9:20 | Morning | Saturday | Weekends | 14 | 2020 | 2019-12-31 18:51 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Fair | Recloser | 37 | 18:51 Bangko feeder #1 load dropped 51A (156/105A). 20:21 It was reported no power at wells Bangko # 197,297,179,325 and Bangko #61. 21:13 Checked and found Recloser: 23/X/08 T/SO Counter: 413/414. 21:16 Manually blocked and closed Recloser: 23/X/08 //> but failed. 22:17 Manually opened Bangko OCB feeder #1, due to bypass Recloser: 23/X/08. 22:28 Manually blocked and closed Bangko OCB feeder #1 //> OK. and then released the block. Cause: Recloser. | 1
1 | 2020-03-15 09:30 | March | 9:30 | Morning | Sunday | Weekends | 15 | 2020 | 2020-01-01 12:59 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Tree | 33 | 12:59 Sintong GFPC T/R 1x, T/ R again on 13:41 and 14:12 ( total T/R 3x) Sintong fdr #2 T/R 1x, T/ R again on 13:41 and 14:12 (total T/R 3x) Not Checked Yet | 1
| 2020-03-15 14:41 | March | 14:41 | Afternoon | Sunday | Weekends | 15 | 2020 | 2020-06-01 07:36 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Tree | 33 | Checked and found STG VCB fdr #2 T/R 3x, Counter : 507 - 510, R/F : 51N Patrolled the line and found - palm tree touch the power line on @1 o/p 26 AE 08 - broken LA at @2 on pole 27-AF-61 Cause : Tree | 1
2 | 2020-03-15 14:41 | March | 14:41 | Afternoon | Sunday | Weekends | 15 | 2020 | 2020-01-01 13:41 | 13.8KV BATANG FEEDER #2 | Bangko-Balam | PGT North | Fair | Emergency | - | 13:41 Manual Open Batang VCB fdr #2, closed at 14:24 MTCE team cutting jumper on TOP 34-AD-06 to isolate locations RB due to water flooding (request by customer) Cause: Emergency | 1
3 | 2020-03-15 16:46 | March | 16:46 | Afternoon | Sunday | Weekends | 15 | 2020 | 2020-02-01 10:54 | 13.8KV NORTH DURI FEEDER #6 | Duri | PGT North | Fair | Planned Maintenance | 16 | 10:54 Manual Open RCL 12-F11-06 (ND fdr #6) MTCE team to c/o TX on pole 12-F11-08 (112.5 kVA) Cause: Planned Maintenance | 1
4 | 2020-03-15 21:35 | March | 21:35 | Night | Sunday | Weekends | 15 | 2020 | 2020-02-01 12:32 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Cloudy | Dead End Insulator | 32 | 3D VCB fdr #2 T/R 1x Not Checked Yet | 1
| 2020-03-15 21:35 | March | 21:35 | Night | Sunday | Weekends | 15 | 2020 | 2020-07-01 21:31 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Cloudy | Dead End Insulator | 32 | Checked And Found 3DSB OCB2 Fdr #2 T/R 1x, Ctr 358-359, R/F 50N Patrolled The Line On 03-Jan-2020 And Found Broken Dead End Insulator On Phase @3 Pole 2F-01 Cause: Dead End Insulator | 1
5 | 2020-03-16 08:45 | March | 8:45 | Morning | Monday | Weekdays | 16 | 2020 | 2020-02-01 13:32 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | CGT#3 Trip by Alarm Loss of Exhaust Thermocouple. | 1
6 | 2020-03-16 08:45 | March | 8:45 | Morning | Monday | Weekdays | 16 | 2020 | 2020-02-01 20:00 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Fair | Emergency | - | 20:00 Manually Open Minas ACB fdr#4, Field Mns Area2 to Maintain Level tank Mns GS#2 23:09 Manually Open & Closed back the Feeder Cause: Emergency | 1
7 | 2020-03-16 10:05 | March | 10:05 | Morning | Monday | Weekdays | 16 | 2020 | 2020-02-01 21:03 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 21:03 S/U CGT#3, then on line the unit at 21:18. | 1
8 | 2020-03-16 13:12 | March | 13:12 | Afternoon | Monday | Weekdays | 16 | 2020 | 2020-03-01 06:52 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Fair | Unidentified | 0 | C.Duri ACB fdr#3 T/R1x Ctr: Not patrolled yet. | 1
| 2020-03-16 13:12 | March | 13:12 | Afternoon | Monday | Weekdays | 16 | 2020 | 2020-04-01 11:52 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Fair | Unidentified | 0 | Checked And Found CDRSG ACB13 Fdr #13 T/R 1x, Ctr 221-222, Patrolled The Line But Found Nothing Cause: Unidentified | 1
9 | 2020-03-16 15:05 | March | 15:05 | Afternoon | Monday | Weekdays | 16 | 2020 | 2020-03-01 13:02 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Fair | Unidentified | 0 | Duri Community fdr #3 T/R 1x Not Checked Yet | 1
| 2020-03-17 09:59 | March | 9:59 | Morning | Tuesday | Weekdays | 17 | 2020 | 2020-07-01 11:04 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Fair | Unidentified | 0 | Checked And Found DCSG ACB26 Fdr #3 T/R 1x, Ctr 100-101, R/F 51 Patrolled The Line But Found Nothing On Phase @1,2,3, Cause: Unidentified | 1
10 | 2020-03-17 14:25 | March | 14:25 | Afternoon | Tuesday | Weekdays | 17 | 2020 | 2020-04-01 23:59 | CPI POWER SYSTEM |  |  |  | Normal Condition | - | Normal System Condition. | 1
11 | 2020-03-18 08:15 | March | 8:15 | Morning | Wednesday | Weekdays | 18 | 2020 | 2020-05-01 01:39 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Fair | Unidentified | 5 | Ketigul VCB fdr#3 T/R 1x Not checked yet | 1
| 2020-03-18 09:27 | March | 9:27 | Morning | Wednesday | Weekdays | 18 | 2020 | 2020-08-01 16:30 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Fair | Unidentified | 5 | Checked And Found KTGL VCB Fdr #3 T/R 2x, Ctr 227-229, R/F 51N Patrolled The Line On 08-Jan-2020 But Found Nothing Cause: Unidentified | 1
12 | 2020-03-19 09:50 | March | 9:50 | Morning | Thursday | Weekdays | 19 | 2020 | 2020-05-01 06:21 | 13.8KV 8D FEEDER #11 | Minas | PGT South | Fair | Unidentified | 0 | 8D OCB fdr#11 T/R 1x. Not checked yet. | 1
| 2020-03-19 10:25 | March | 10:25 | Morning | Thursday | Weekdays | 19 | 2020 | 2020-09-01 15:44 | 13.8KV 8D FEEDER #11 | Minas | PGT South | Fair | Unidentified | 0 | Checked and found 8D VCB fdr #11 T/R 1x, ctr: 99928 - 99929, R/F: 51N Patrolled the line but found nothing. Cause : Unidentified | 1
13 | 2020-03-19 10:27 | March | 10:27 | Morning | Thursday | Weekdays | 19 | 2020 | 2020-06-01 05:59 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Fair | Unidentified | 0 | C.Duri ACB fdr#3 T/R 1x Ctr:221-222 R/F:51@3. Not patrolled yet. | 1
| 2020-03-19 17:02 | March | 17:02 | Afternoon | Thursday | Weekdays | 19 | 2020 | 2020-09-01 09:24 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found: CDRSG-13.8ACB13 T/R, Counter : 221 - 222, Relay Flag : 51N Patrolled the line found : Unidentified Phase : 0 Cause : Unidentified | 1
14 | 2020-03-20 10:51 | March | 10:51 | Morning | Friday | Weekdays | 20 | 2020 | 2020-06-01 10:02 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Planned Maintenance | 34 | 10:02 Manual Open LBS 07-S8-20 (DF fdr #2), closed at 10:11 (to open bypass switch of RCL 06-S1-02 (DF fdr #2) MTCE team to replace transformer on pole 06-S1-11. 11:24 Manual Close LBS 06-S1-19 (load transferred to DF fdr #4) Cause: Planned Maintenance | 1
15 | 2020-03-20 18:20 | March | 18:20 | Afternoon | Friday | Weekdays | 20 | 2020 | 2020-06-01 10:54 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Fair | Planned Maintenance | 0 | 10:54 Manual open 8C fdr #4, closed at 13:17 (MTCE team to replace b/o insulator o/p 8D-59) Cause: Planned Maintenance | 1
16 | 2020-03-20 18:20 | March | 18:20 | Afternoon | Friday | Weekdays | 20 | 2020 | 2020-06-01 14:30 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Cloudy | Unidentified | 60 | 14:30 It was reported no power on Road 07-U1-XX d/s: DF fdr #2. !5:50 Checked and found Recl: 07-U1-19 T/SO ctr:71-72. Patrolled the line but found nothing. 15:55 Blocked and closed the Recl. OK then released the block. Cause: Unidentified. | 1
17 | 2020-03-20 23:31 | March | 23:31 | Night | Friday | Weekdays | 20 | 2020 | 2020-06-01 14:40 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Cloudy | Animal | 78 | 14:40 Petani 13.8KV OCB fdr #1 T/R 1X. 14:47 Petani 13.8KV OCB fdr #1 T/R again. 14:49 Petani 13.8KV OCB fdr #1 T/R again. Not checked yet. | 1
| 2020-03-21 07:06 | March | 7:06 | Morning | Saturday | Weekends | 21 | 2020 | 2020-10-01 14:21 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Cloudy | Animal | 78 | Checked and found: PTNSB-13.8OCB1 T/R, Counter : 153 - 154, Relay Flag : 51N Patrolled the line found : Burung hantu mati di dekat meja trafo Phase : 3 Cause : Animal | 1
18 | 2020-03-21 07:06 | March | 7:06 | Morning | Saturday | Weekends | 21 | 2020 | 2020-06-01 15:29 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 0 | C. Duri 13.8KV ACB fdr #16 T/R 1X. Not checked yet. | 1
| 2020-03-21 07:24 | March | 7:24 | Morning | Saturday | Weekends | 21 | 2020 | 2020-09-01 09:25 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found: CDRSG-13.8ACB28 T/R, Counter : 367 - 368, Relay Flag : 51N. Patrolled the line found : Nothing Found Phase : 0 Cause : Unidentified | 1
19 | 2020-03-21 07:24 | March | 7:24 | Morning | Saturday | Weekends | 21 | 2020 | 2020-06-01 17:05 | 13.8KV DURI COMMUNITY FEEDER #5 | Duri | PGT North | Fair | Unidentified | 0 | Duri Comm. 13.8KV ACB fdr #5 T/R 1X. Not checked yet. | 1
| 2020-03-21 12:05 | March | 12:05 | Afternoon | Saturday | Weekends | 21 | 2020 | 2020-11-01 10:26 | 13.8KV DURI COMMUNITY FEEDER #5 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found DCM VCB fdr #5 T/R 1x, ctr: 122-123, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
20 | 2020-03-21 12:05 | March | 12:05 | Afternoon | Saturday | Weekends | 21 | 2020 | 2020-06-01 17:19 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain | Unidentified | 27 | C. Duri 13.8KV ACB fdr #1 T/R 1x ctr:269-270 R/F: 51G, 51N. Not patrolled yet. | 1
| 2020-03-22 06:55 | March | 6:55 | Morning | Sunday | Weekends | 22 | 2020 | 2020-09-01 09:28 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain | Unidentified | 27 | Checked and found: CDRSG-13.8ACB11 T/R, Counter : 269 - 270, Relay Flag : 51N. Patrolled the line found : Nothing Found Phase : 0 Cause : Unidentified | 1
21 | 2020-03-22 10:16 | March | 10:16 | Morning | Sunday | Weekends | 22 | 2020 | 2020-07-01 06:32 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Animal | 77 | Petani fdr#1 T/R 1x. Not checked yet. | 1
| 2020-03-22 12:28 | March | 12:28 | Afternoon | Sunday | Weekends | 22 | 2020 | 2020-10-01 14:20 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Animal | 77 | Checked and found: PTNSB-13.8OCB1 T/R, Counter : 153 - 154, Relay Flag : 51N Patrolled the line found: Burung hantu mati di dekat meja trafo Phase : 3 Cause : Animal | 1
22 | 2020-03-22 12:28 | March | 12:28 | Afternoon | Sunday | Weekends | 22 | 2020 | 2020-07-01 06:49 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Tree | 12 | Rokan fdr#2 T/R 1x. Not checked yet. | 1
| 2020-03-22 12:30 | March | 12:30 | Afternoon | Sunday | Weekends | 22 | 2020 | 2020-10-01 14:25 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Tree | 12 | Checked and found: RKNSB-13.8VCB2 T/R, Counter : 1316 - 1317, Relay Flag : 51N Patrolled the line found : Pohon sukun menyentuh line Phase : 0 Cause : Tree | 1
23 | 2020-03-22 12:30 | March | 12:30 | Afternoon | Sunday | Weekends | 22 | 2020 | 2020-07-01 06:51 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Fair | Lightning | 0 | 8D fdr#5 T/R 1x. Not checked yet. | 1
| 2020-03-22 14:22 | March | 14:22 | Afternoon | Sunday | Weekends | 22 | 2020 | 2020-10-01 11:43 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Fair | Lightning | 0 | Checked and found: 8DSB-13.8OCB5 T/R, Counter : 566 - 566, Relay Flag : 50N Patrolled the line found : Not Found Phase : 0 Cause : Lightning | 1
24 | 2020-03-22 14:22 | March | 14:22 | Afternoon | Sunday | Weekends | 22 | 2020 | 2020-07-01 09:29 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Fair | Planned Maintenance | 421 | 09:29 Manual Open 8C feeder #3, closed at 12:50 09:30 Manual Open 8C feeder #4, closed at 12:38 09:31 Manual Open Minas feeder #3, closed at 13:10 (MTCE team to repair broken LBS o/p 8D-198) Cause: Planned Maintenance | 1
25 | 2020-03-22 15:34 | March | 15:34 | Afternoon | Sunday | Weekends | 22 | 2020 | 2020-07-01 10:01 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Fair | Planned Maintenance | 28 | 10:01 Manual Open RCL 03-2-02 (CD fdr #6), closed at 11:02 MTCE team to repair broken guy wire o/p 03-2-25 11:19 The RCL 03-2-02 failed to re-closed, load transferred to CD fdr #8 by close LBS 03-2-41. Cause: Planned Maintenance | 1
26 | 2020-03-22 15:34 | March | 15:34 | Afternoon | Sunday | Weekends | 22 | 2020 | 2020-07-01 16:40 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Animal | 96 | 16:40 So BLM VCB fdr #4 T/O (on block position for HPS #09 at BLM #297) 16:50 Got contact with HPS #09 crew and reported they are OK. 16:51 Call TL Ops (Soski) and get permitting to manually close So BLM fdr #4 16:52 Manually close VCB So BLM fdr #4, OK. Stayed on block position. Cause: Not Checked Yet | 1
27 | 2020-03-22 17:51 | March | 17:51 | Afternoon | Sunday | Weekends | 22 | 2020 | 2020-08-01 09:08 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Lightning Arrester | 25 | Ketigul VCB feeder #2 T/R 1 x. Not checked yet. | 1
| 2020-03-22 17:58 | March | 17:58 | Afternoon | Sunday | Weekends | 22 | 2020 | 2020-09-01 10:12 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Lightning Arrester | 25 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 369 - 370, Relay Flag : 51N. Patrolled the line found: LA putus Phase : 2 Cause : Lightning Arrester | 1
28 | 2020-03-22 23:51 | March | 23:51 | Night | Sunday | Weekends | 22 | 2020 | 2020-09-01 16:13 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 28 | Ketigul VCB feeder #2 T/R 1x. Not checked yet. | 1
| 2020-03-22 23:51 | March | 23:51 | Night | Sunday | Weekends | 22 | 2020 | 2020-10-01 14:31 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 28 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 370 - 371, Relay Flag : 51N. Patrolled the line found : No Findings Phase : 0 Cause : Unidentified | 1
29 | 2020-03-22 23:53 | March | 23:53 | Night | Sunday | Weekends | 22 | 2020 | 2020-11-01 01:23 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Rain | Unidentified | 88 | 01:23 Minas ACB fdr #3 T/LO, ctr: 80166 - 80168, R/F: 51P @1 @2 Patrolled the line but found nothing 02:33 Block and manually close Minas ACB fdr #3, OK then release the block. Cause: Unidentified | 1
30 | 2020-03-22 23:53 | March | 23:53 | Night | Sunday | Weekends | 22 | 2020 | 2020-11-01 01:34 | 13.8KV 8C FEEDER #2 | Minas | PGT South | Rain | Circuit Breaker | 60 | 01:34 8C VCB fdr #2 T/SO. 01:52 Blocked and manually close VCB 8C fdr #3 (after got approval by TL Ops South (Priambudi) but failed. 02:52 Checked and found 8C VCB fdr #2 T/SO, ctr: 530 - 532, R/F: 51P @2 @3. Patrolled the line but found nothing. 04:15 Manually close VCB 8C fdr #2 9by DSC), but still failed 04:40 Manually close by local but failed too. 05:05 Transfer load of 8C fdr #2 to 8C fdr #1 by close LBS 9D-49 Continue tomorrow, need troubleshoot by MTCE team. Cause: Circuit Breaker | 1
31 | 2020-03-23 00:19 | March | 0:19 | Night | Monday | Weekdays | 23 | 2020 | 2020-11-01 08:55 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Cloudy | Dead End Insulator | 30 | Rangau OCB feeder#2 T/R 1x. Not checked yet. | 1
| 2020-03-23 00:19 | March | 0:19 | Night | Monday | Weekdays | 23 | 2020 | 14-01-2020 11:37 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Cloudy | Dead End Insulator | 30 | Checked and found: RGUSB-13.8OCB2 T/R, Counter : 347 - 348, Relay Flag : 51. Patrolled the line found : Dead end pecah Phase : 3 Cause : Dead End Insulator | 1
32 | 2020-03-23 00:40 | March | 0:40 | Night | Monday | Weekdays | 23 | 2020 | 2020-11-01 18:03 | 13.8KV 6D FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | 28 | 6D138KV OCB FEEDER#1 T/R 1x. Not checked yet. | 1
| 2020-03-23 00:40 | March | 0:40 | Night | Monday | Weekdays | 23 | 2020 | 13-01-2020 21:06 | 13.8KV 6D FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | 28 | Checked and found 6D VCB fdr #1 T/R 1x, ctr: 372 - 373, R/F: 51P @1 Patrolled the line but found nothing Cause : Lightning | 1
33 | 2020-03-23 00:41 | March | 0:41 | Night | Monday | Weekdays | 23 | 2020 | 2020-12-01 01:13 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Cloudy | Unidentified | 18 | Libo feeder #1 T/R 1x Not Checked Yet | 1
| 2020-03-23 00:41 | March | 0:41 | Night | Monday | Weekdays | 23 | 2020 | 14-01-2020 09:00 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Cloudy | Unidentified | 18 | Checked and found Libo OCB feeder #1 T/R 1x. R/F: 51N Counter: 598-599. Patrolled the line found nothing. Cause: Unidentified. | 1
34 | 2020-03-23 00:43 | March | 0:43 | Night | Monday | Weekdays | 23 | 2020 | 2020-12-01 16:45 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 73 | 16:45 C.Duri feeder #1 load dropped 61A (146A - 79A). 17:46 Checked and found Recloser 39- AV-36 T/O (on blocked). 18:09 Blocked and Closed the Recloser above , OK.Still on block due to RIG BKU #02 Couse: Not patrolled yet. | 1
| 2020-03-23 00:43 | March | 0:43 | Night | Monday | Weekdays | 23 | 2020 | 13-01-2020 08:16 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 73 | Checked and found: 5441-R.39AV36 T/O, Counter : 296 - 296, Relay Flag : 51N Patrolled the line found : Nothing Found Phase : 0 Cause : Unidentified | 1
35 | 2020-03-23 01:15 | March | 1:15 | Night | Monday | Weekdays | 23 | 2020 | 2020-01-13 18:05 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | C.Duri ACB feeder#1 T/R 1x. R/F 51G , 51N 51 @1. Not checked yet. | 1
| 2020-03-23 01:15 | March | 1:15 | Night | Monday | Weekdays | 23 | 2020 | 2020-01-16 09:00 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found C Duri ACB #11 (feeder #1) T/R 1x. R/F: 51@1 , 51G and 51N Counter: 270/271. Patrolled the line found nothing. Cause: Unidentified. | 1
36 | 2020-03-23 01:15 | March | 1:15 | Night | Monday | Weekdays | 23 | 2020 | 2020-01-14 06:35 | 13.8KV DURI FIELD FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Duri Field VCB fdr #1 T/R 1x Not Patrolled Yet | 1
| 2020-03-23 01:15 | March | 1:15 | Night | Monday | Weekdays | 23 | 2020 | 2020-01-17 09:00 | 13.8KV DURI FIELD FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Checked And Found DFSG ACB41 Fdr #1 T/R 1x, Ctr 726/727, R/F 51 Patrolled The Line On 17/Jan/2020 And Found Phase Time Overcurrent On Phase @1 Cause: Unidentified | 1
37 | 2020-03-23 06:54 | March | 6:54 | Morning | Monday | Weekdays | 23 | 2020 | 2020-01-14 06:51 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Pin Insulator | 33 | PTN VCB feeder #2 T/R 1x PTN feeder #1 load dropped 51 A (226 / 175 A) //> WIP trip 1 unit Not Checked Yet | 1
| 2020-03-23 06:54 | March | 6:54 | Morning | Monday | Weekdays | 23 | 2020 | 2020-01-17 09:29 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Pin Insulator | 33 | Checked and found: PTNSB/13.8OCB2 T/R, Counter : 323 / 324, Relay Flag : 51N Patrolled the line found: Pin pecah di bagian bawah Phase : 1 Cause : Pin Insulator | 1
38 | 2020-03-23 06:54 | March | 6:54 | Morning | Monday | Weekdays | 23 | 2020 | 2020-01-14 07:09 | 13.8KV 8D FEEDER #2 | Minas | PGT South | Fair | Lightning | 0 | 8D OCB feeder#2 T/R 1x Not Checked Yet. | 1
| 2020-03-23 09:51 | March | 9:51 | Morning | Monday | Weekdays | 23 | 2020 | 2020-01-15 12:12 | 13.8KV 8D FEEDER #2 | Minas | PGT South | Fair | Lightning | 0 | Checked and found: 8DSB/13.8OCB2 T/R, Counter : 289 / 290, Relay Flag : 51N Patrolled the line found : Not found Phase : 0 Cause : Lightning | 1
39 | 2020-03-24 10:40 | March | 10:40 | Morning | Tuesday | Weekdays | 24 | 2020 | 2020-01-14 09:35 | 13.8KV NELLA GFPC | Bangko-Balam | PGT North | Cloudy | Lightning | 1 | Nella GFPC T/R 1x. Nella feeder #1 load dropped 102A (199/97A). Not checked yet. | 1
| 2020-03-24 15:39 | March | 15:39 | Afternoon | Tuesday | Weekdays | 24 | 2020 | 2020-01-21 07:18 | 13.8KV NELLA GFPC | Bangko-Balam | PGT North | Cloudy | Lightning | 1 | Checked And Found 13.8KVNEL_GFPC T/R 2x, Ctr 1111/2931, R/F 51N Patrolled The Line On 20/Jan/2020 And Found Broken Dead End 40% On Phase @1,3, Pole 21 U 47 Dekat Bko #131 Cause: Lightning | 1
40 | 2020-03-24 15:39 | March | 15:39 | Afternoon | Tuesday | Weekdays | 24 | 2020 | 2020-01-14 10:20 | 13.8KV BEKASAP FEEDER #2 | Bekasap | PGT North | Fair | Unidentified | 95 | 10:20 It was reported no power at Jambon Field , Bekasap #168 , Bekasap #105. Bekasap feeder #2 (MSU/2 feeder#2) dropped 30A (259/229A). !1:30 Checked and found Recl: 38/BD/39 T/SO ,(Display blank). Patrolled the line but found nothing. 11:32 Manually closed the Recl. OK , then released the block. Cause: Unidentified. | 1
41 | 2020-03-25 06:56 | March | 6:56 | Morning | Wednesday | Weekdays | 25 | 2020 | 2020-01-14 10:56 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 13 | 10:56 It was reported no power at Perkebunan field. 12:51 Checked and found Recl: 29/Z/13A T/O, D/S Sintong fdr#2. ctr:218/219. Patrolled the line but found nothing. Manually Closed Recloser 29/Z/13A. Ok. Cause: Unidentified. 13:00 Sintong VCB feeder #2 Load dropped 168A (242/74A). 18:00 Checked and found Recloser 29/Z/13A T/SO (Control failure). Blocked and Closed the Recloser 29/Z/13A. OK. Unplug ( cotrol failure). Patrolled the line but found nothing . Couse: Unidentified. | 1
42 | 2020-03-25 06:56 | March | 6:56 | Morning | Wednesday | Weekdays | 25 | 2020 | 2020-01-14 14:41 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Fair | Lightning Arrester | 63 | 3D OCB Feeder #2 T/R 1x. 3D Feeder #3 Load Dropped 20A (90/70A). 3D Feeder #4 Load Dropped 12A (165/153A). Not checked yet. | 1
| 2020-03-25 07:18 | March | 7:18 | Morning | Wednesday | Weekdays | 25 | 2020 | 2020-01-17 08:35 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Fair | Lightning Arrester | 63 | Checked and found: 3DSB/13.8OCB2 T/R, Counter : 359 / 360, Relay Flag : 51 Patrolled the line found : Broken LA Phase : 2 Cause : Lightning Arrester | 1
43 | 2020-03-25 07:18 | March | 7:18 | Morning | Wednesday | Weekdays | 25 | 2020 | 2020-01-15 07:26 | DARLING SUBSTATION | Duri | PGT North | Fair | Under investigation | 900 | 07:26 It was reported No Power at CGS#5 and CCS#6. 08:45 Checked & found 115Kv GCB#1 T/O Ctr:200/201. 115Kv GCB#3 T/O Ctr:111/112. (Darling Subst. Tx/2 No Power). Checked Tx/2 & VR Normal Condition. 09:30 Manually Open Darling VCB fdr#6, the closed at 09:51. Manually Open Darling VCB fdr#7, the closed at 09:52. Manually Open Darling VCB fdr#8, the closed at 09:53. 09:45 Closed 115Kv Darling GCB#1. 09:47 Closed 115Kv Darling GCB#3. Cause: Under Investigation. Production loss 8 SE :350 Bbls / 179 wells. 8 SW : 278 Bbls / 151 wells. ////////////////////////////////////////////////// + Grand total : 628 Bbls / 330 wells. | 1
44 | 2020-03-25 07:59 | March | 7:59 | Morning | Wednesday | Weekdays | 25 | 2020 | 2020-01-15 08:30 | 13.8KV DARLING VCB FEEDER #8 | Duri | PGT North | Fair | Recloser / Control Recloser | - | C Duri ACB #12 (feeder #2) transfer to Darling VCB feeder #8. 08:30 It was reported no power on pole 08/L7/17 D/S Darling feeder #8. Checked and found Recloser: 08/M1/38 T/O No indication on display. Patrolled the line found nothing. 12:08 Manually block and closed Recloser: 08/M1/38 //> OK. and then released the block. Cause: Suspect control Recloser. | 1
45 | 2020-03-25 07:59 | March | 7:59 | Morning | Wednesday | Weekdays | 25 | 2020 | 2020-01-15 14:52 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 14:52 S/U MGT#7, then on line the unit at 15:13. | 1
46 | 2020-03-25 08:06 | March | 8:06 | Morning | Wednesday | Weekdays | 25 | 2020 | 2020-01-15 15:00 | 13.8KV DARLING VCB FEEDER #8 | Duri | PGT North | Fair | Unidentified | 105 | 15:00 It was reported No Power o/p 08/M5_17. 17:15 Checked & found Recl. 05/M3/02 T/LO Ctr:97/101. Patrolled the line but found nothing. 18:38 Blocked & closed Recl 05/M5/02, then release the blocked. Cause: Unidentified. | 1
| 2020-03-25 14:30 | March | 14:30 | Afternoon | Wednesday | Weekdays | 25 | 2020 | 2020-01-17 15:33 | 13.8KV DARLING VCB FEEDER #8 | Duri | PGT North | Fair | Unidentified | 105 | Checked and found : Rec 08/M3/38 T/O, Counter : 157 / 158, Relay Flag : NONE Patrolled the line foung : No Findings Phase : 0 Cause : Unidentified | 1
47 | 2020-03-25 14:56 | March | 14:56 | Afternoon | Wednesday | Weekdays | 25 | 2020 | 2020-01-15 15:24 | MINAS POWER PLANT | Minas | PGT South |  |  | - | Off line MGT#8, then S/D the unit for S/B. | 1
48 | 2020-03-26 15:43 | March | 15:43 | Afternoon | Thursday | Weekdays | 26 | 2020 | 2020-01-15 16:17 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 16 | N.Duri VCB fdr#1 T/R 1x. Not checked yet. | 1
| 2020-03-26 19:30 | March | 19:30 | Night | Thursday | Weekdays | 26 | 2020 | 2020-01-17 09:00 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 16 | Checked and found N Duri VCB feeder #1 T/R 1x. R/F: 51@2 Counter: 336/337. Patrolled the line found nothing. Cause: Unidentified. | 1
49 | 2020-03-27 11:02 | March | 11:02 | Morning | Friday | Weekdays | 27 | 2020 | 2020-01-16 11:21 | 13.8KV BATANG FEEDER #2 | Bangko-Balam | PGT North | Fair | Construction Job | 0 | 11:21 Manually Opened Batang VCB fdr#2. to Tie In Some Wells ;Rbs #014, #015, #028, #041,# 042, #053, #059 due to will Start after flooding condition. 12:02 Block & Closed Batang VCB fdr#2, then released the block Cause: Construction job. | 1
50 | 2020-03-27 18:34 | March | 18:34 | Afternoon | Friday | Weekdays | 27 | 2020 | 2020-01-16 14:57 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Tree | 0 | Menggala feeder #1 load dropped 129A (203/ 74A) Not checked yet. | 1
| 2020-03-27 18:34 | March | 18:34 | Afternoon | Friday | Weekdays | 27 | 2020 | 2020-01-21 07:24 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Tree | 0 | Checked And Found gfpc 1 Fdr #1 T/R 2x, Ctr 128/130, R/F 51N Patrolled The Line On 20/Jan/2020 And Found Sawit On Phase @1 Pole 22 Ai 01 Cause: Tree | 1
51 | 2020-03-28 14:47 | March | 14:47 | Afternoon | Saturday | Weekends | 28 | 2020 | 2020-01-17 01:35 | 13.8KV 6DN FEEDER #6 | Minas | PGT South | Fair | Unidentified | 370 | 01:35 6DN OCB feeder #6 T/O 04:46 Checked and found 6DN OCB feeder #1 T/LO. R/F: 51 @2,@3 and 50 @2,@3 Counter: 190/194. Patrolled the line found nothing. 05:59 Manually blocked and closed 6DN OCB feeder #6 //> OK. and then released the block. Cause: Unidentified. | 1
52 | 2020-03-28 14:47 | March | 14:47 | Afternoon | Saturday | Weekends | 28 | 2020 | 2020-01-17 01:35 | 13.8KV 6DN FEEDER #5 | Minas | PGT South | Fair | Normal Condition | 0 | 6DN feeder #5 load dropped 50A (50/0A). Not checked yet. | 1
| 2020-03-28 15:22 | March | 15:22 | Afternoon | Saturday | Weekends | 28 | 2020 | 2020-01-22 08:18 | 13.8KV 6DN FEEDER #5 | Minas | PGT South | Fair | Normal Condition | 0 | Checked and found: 6DNSB/13.8OCB5 None, Counter : / , Relay Flag : NONE Patrolled the line found : normal Phase : 0 Cause : Normal Condition | 1
53 | 2020-03-28 15:22 | March | 15:22 | Afternoon | Saturday | Weekends | 28 | 2020 | 2020-01-18 14:00 | 13.8KV PETAPAHAN FEEDER #8 | Petko | PGT South | Fair | Emergency | 0 | 14:00 Manually Opened Petapahan Vcb fdr#8 to Open HLC o/p toward Well PTH#02 for RIG activity 14:10 Manually Closed Back Petapahan Vcb fdr#8 the HLC stay Open til end Rig activity Cause: Emergency | 1
54 | 2020-03-28 15:56 | March | 15:56 | Afternoon | Saturday | Weekends | 28 | 2020 | 2020-01-18 14:05 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Dumai | PGT North | Fair | Planned Maintenance | 0 | 14:05 Manually opened Dumai 4160V feeder #4 for , 1. Cut high trees on pole H 57/58. 2. Cut High Trees On Pole H 58 – H 59. 3. Cut High Trees On Pole H 18 34. 4. Replace broken fuse link on pole H70/03 Mendut complex. 5. Repair cable for lighting at Perimeter CPS. 15:30 Manually blocked and closed Dumai 4160V feeder #4. Cause: Planned maintenance. | 1
55 | 2020-03-28 15:56 | March | 15:56 | Afternoon | Saturday | Weekends | 28 | 2020 | 2020-01-18 14:30 | 13.8KV 4D FEEDER #4 | Minas | PGT South | Fair | Emergency | 0 | 14:30 Manually Opened Recloser 4D.51A (4D fdr#4) for rig activity BSM#11 at Well 4C.52R Cause: Emergency | 1
56 | 2020-03-29 09:20 | March | 9:20 | Morning | Sunday | Weekends | 29 | 2020 | 2020-01-19 04:55 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Heavy Rain | Lightning | 30 | Ketigul VCB feeder #1 T/R 1x. Not checked yet. | 1
| 2020-03-29 15:09 | March | 15:09 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-19 16:09 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Heavy Rain | Lightning | 30 | Checked And Found PKTGL VCB2 Fdr #2 T/R 1x, Ctr 371/372, R/F 51 Patrolled The Line On 19/Jan/2020 And Found Lightning Arrester Pecah 2 On Phase @2,3, Pole 29 Al 09 Cause: Lightning | 1
57 | 2020-03-29 16:28 | March | 16:28 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-19 05:18 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Animal | 98 | Petani OCB feeder #2 T/R 1x. Not checked yet. | 1
| 2020-03-29 16:28 | March | 16:28 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-19 16:07 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Animal | 98 | Checked And Found PTNSB OCB2 Fdr #2 T/R 1x, Ctr 324/325, R/F 51 Patrolled The Line On 19/Jan/2020 And Found Musang Di Terminal Pole Sisi Primary Jumper On Phase @2 Pole Ptn 52 Cause: Animal | 1
58 | 2020-03-29 16:28 | March | 16:28 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-19 07:26 | 44KV PEMATANG MAIN / PETANI LINE | Bekasap | PGT North | Fair | Unidentified | 80 | 44KV line Pematang Main ////>Petani OCB#1 T/R 1x. Not checked yet. | 1
| 2020-03-29 17:52 | March | 17:52 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-22 13:24 | 44KV PEMATANG MAIN / PETANI LINE | Bekasap | PGT North | Fair | Unidentified | 80 | Checked And Found PMT Main 44 kV GCB Fdr #1 T/R 1x, Ctr: 197/198, R/F: 50N Patrolled the line but found nothing. Cause: Unidentified | 1
59 | 2020-03-29 17:52 | March | 17:52 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-19 08:00 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | 190 | 08:00 C.Duri fdr#1 load dropped 66A (146/80A). Checked and found Recloser: 39/AV/36 T/SO (in blocked position) Due to RIG BKU #02 activity at location Puncak #04 , R/F: 51 @3 and 51N. Patrolled the line found @3 broken Lightning Arrester on Terminal pole , location Kulin #55. 10:10 Manually blocked and closed Recloser: 39/AV/36 and still in block position. Cause: Broken Lightning Arrester. | 1
| 2020-03-29 18:03 | March | 18:03 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-19 16:03 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | 190 | Checked And Found 5441/R.39AV36 T/SO, Ctr 296/297, R/F 51 Patrolled The Line On 19/Jan/2020 And Found La Broken On Teriminal Pole D On Phase @3 Pole Kulin 55 Cause: Unidentified (L/A) | 1
60 | 2020-03-29 18:03 | March | 18:03 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-19 09:05 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Animal | 12 | 09:05 Petani fdr#2 T/R 1x. Checked and found Petani fdr#2 T/R 1x. R/F: 51@2 and 51N Counter:325/326. Patrolled the line found Animal (chivet) on terminal pole Petani #52. Cause: Animal (chivet). | 1
| 2020-03-29 18:05 | March | 18:05 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-19 16:05 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Animal | 12 | Checked And Found PTNSB OCB2 Fdr #2 T/R 1x, Ctr 325/326, R/F 51 Patrolled The Line On 19/Jan/2020 And Found Musang Di Terminal Pole On Phase @2 Pole Ptn 52 Cause: Animal | 1
61 | 2020-03-29 18:05 | March | 18:05 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-19 16:48 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Fair | Animal | 35 | Bangko 13.8KV OCB feeder#4 T/R 1x. Bangko GFPC T/SO. Not checked yet. | 1
| 2020-03-29 18:18 | March | 18:18 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-21 07:31 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Fair | Animal | 35 | Checked And Found / BKOSB OCB4 Fdr #4 T/R 1x, Ctr 80/81, R/F 50N / GFPC T/R 2x, Ctr 238/240, R/F 51N Patrolled The Line On 20/Jan/2020 And Found Burung Elang Di Atas Trafo On Phase @2,3, Pole 23 Y 12 Cause: Animal | 1
62 | 2020-03-29 18:18 | March | 18:18 | Afternoon | Sunday | Weekends | 29 | 2020 | 2020-01-19 17:02 | 13.8KV NORTH DURI FEEDER #5 | Duri | PGT North | Fair | Suspension Insulator | 71 | N.Duri 13.8KV VCB feeder#5 T/R 1x. Not checked yet. | 1
| 2020-03-30 03:41 | March | 3:41 | Night | Monday | Weekdays | 30 | 2020 | 2020-01-21 16:41 | 13.8KV NORTH DURI FEEDER #5 | Duri | PGT North | Fair | Suspension Insulator | 71 | Checked and found: NDRSB/13.8VCB5 T/R, Counter : 137 / 138, Relay Flag : 51N Patrolled the line found : Suspension insulator pecah Phase : 2 Operated Device : NDRSB/13.8VCB5 T/R Counter : 137 / 138 Relay Flag : 51N Finding Patrol : Bushing recloser terbakar Phase : 1, 2, 3, Pole : 12/E11/02 Cause : Suspension Insulator | 1
63 | 2020-03-30 03:41 | March | 3:41 | Night | Monday | Weekdays | 30 | 2020 | 2020-01-19 17:02 | NORTH DURI SUBSTATION | Duri | PGT North | Fair | Under investigation | 1082 | 17:02 N.Duri 115KV C/S 13 T/O. No power at 13.8KV Bus#2 and bus#3. at that time also no power at feeder#4,5,6,7,8, and #9,10,11. (Note. TX#12 & VR is in isolate due to Service, and Close Bus Tie#8/9 Bus#2/#3) 18:00 Checked & found NDuri C/S TX#13 T/O, Ctr:...…. R/F: 51N 13.8KV Nd vcvb fdr#5 T/R 1x, Ctr: 136/137, R/F: 51N Checked & found TX#13 Normal .. 18:40 Opened Tie LBS 8/9. 18:46 Closed Isolation Switcht Load Side VR Tx/12. 18:48 Closed N.Duri VCB fdr#4. 18:49 Closed N.Duri VCB fdr#5 18:50 Closed N.Duri VCB fdr#6. 18:50 Closed N.Duri VCB fdr#7. 18:51 Closed N.Duri VCB fdr#8. 18:52 Closed C/S Tx/13. 18:53 Closed N.Duri VCB fdr#9. 18:54 Closed N.Duri VCB fdr#10. 18:54 Closed N.Duri VCB fdr#11. Cause: Under investigation. Production loss : 1. 10 SE : 189 Bbls / 190 wells (Facility Degassing 10SE shutdown). 2. 10 SC : 56 Bbls / 152 wells (Facility Degassing 10SC shutdown). ////////////////////////////////// + Total : 245 Bbls / 342 wells. 20:00 Checked and found Recloser 12/F7//03 T/SO D/S N.Duri feeder #6. counter : 88/89. LBS 12F/F7/49 Open. 22:18 Manually block & closed Recloser 12/F7/03 /////>Ok. and release the block. 22:57 Checked and found AWT Tes Station off (area#12). 23:00 Manually block & closed Recloser 12/E11/02 /////>Ok.and then release the block. R/F:51@3/51N. Counter:267/268. Cause: Not Patrolled yet. Production loss: 768 Bbls / 575 wells. | 1
64 | 2020-03-30 03:48 | March | 3:48 | Night | Monday | Weekdays | 30 | 2020 | 2020-01-19 18:06 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 32 | Nella 13.8KV VCB feeder#2 T/R 1x. Nella GFPC T/R. Not checked yet. | 1
| 2020-03-30 03:48 | March | 3:48 | Night | Monday | Weekdays | 30 | 2020 | 2020-01-21 07:26 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 32 | Checked And Found NLASB VCB2 Fdr #2 T/R 2x, Ctr 353/355, R/F 51N Patrolled The Line On 20/Jan/2020 But Found Nothing Cause: Unidentified | 1
65 | 2020-03-30 03:48 | March | 3:48 | Night | Monday | Weekdays | 30 | 2020 | 2020-01-19 19:00 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Fair | Unidentified | 13 | Ketigul VCB fdr#3 T/R 1x Not checked yet | 1
| 2020-03-30 14:45 | March | 14:45 | Afternoon | Monday | Weekdays | 30 | 2020 | 2020-01-20 18:29 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Fair | Unidentified | 13 | Checked And Found PKTGL VCB3 Fdr #3 T/R 1x, Ctr 231/232, R/F 51N dan 51 Patrolled The Line On 20/Jan/2020 But Found Nothing On Phase @3 Cause: Unidentified | 1
66 | 2020-03-30 15:59 | March | 15:59 | Afternoon | Monday | Weekdays | 30 | 2020 | 2020-01-20 10:40 | 13.8KV CENTRAL DURI FEEDER #8 | Duri | PGT North | Fair | Dead End Insulator | 0 | C.Duri ACB fdr#8 T/R 1x Ctr:48/49 R/F:51@2@3. Not patrolled yet. | 1
| 2020-03-30 15:59 | March | 15:59 | Afternoon | Monday | Weekdays | 30 | 2020 | 2020-01-22 13:56 | 13.8KV CENTRAL DURI FEEDER #8 | Duri | PGT North | Fair | Dead End Insulator | 0 | Checked And Found CDRSG ACB32 8 Fdr #8 T/R 1x, Ctr 439/440, R/F 51 Patrolled The Line On 21/Jan/2020 And Found Dead End Flash Over On Phase @3 Pole 03/1/40 Cause: Dead End Insulator | 1
67 | 2020-03-31 10:01 | March | 10:01 | Morning | Tuesday | Weekdays | 31 | 2020 | 2020-01-20 14:00 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:00 S/U CGT#3, then On Line the unit at 1534. | 1
68 | 2020-03-31 16:04 | March | 16:04 | Afternoon | Tuesday | Weekdays | 31 | 2020 | 2020-01-20 17:00 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | Off Line CGT#5, then S/D the unit for S/B. | 1
69 | 2020-03-31 21:34 | March | 21:34 | Night | Tuesday | Weekdays | 31 | 2020 | 2020-01-21 09:55 | 13.8KV PUNGUT FEEDER #1 | Bekasap | PGT North | Fair | Planned Maintenance | 71 | 09:55 Manually Opened Recl 45BP.09 (Pungut Fdr#1) to Opened Jumper for TOL project 14:40 Block & Closed The Recloser then released the block Cause: Planned maintenance (TOL Project) | 1
70 | 2020-03-31 21:34 | March | 21:34 | Night | Tuesday | Weekdays | 31 | 2020 | 2020-01-21 18:52 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 39 | 18:52 CDuri Fdr#1 Load dropped 67A (71/4A) 20:12 Checked and found Recloser: 39/AV/36 T/SO (in blocked position) Due to RIG BKU #02 activity at location Puncak #04 , R/F: 51 @3 and 51N. 10:10 Manually blocked and closed Recloser: 39/AV/36 /////> Ok. and still in block position. ( RIG BKU #02 activity ). Cause: Not Patrolled yet. | 1
| 2020-04-13 06:27 | April | 6:27 | Morning | Monday | Weekdays | 13 | 2020 | 2020-01-27 17:38 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 39 | Checked and found: 5441/R.39AV36 T/R, Counter : 297 / 298, Relay Flag : NONE Patrolled the line found: Unidentified Phase : 0 Cause : Unidentified | 1
71 | 2020-04-13 06:27 | April | 6:27 | Morning | Monday | Weekdays | 13 | 2020 | 2020-01-22 05:31 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Lightning Arrester | - | 5B OCB feeder #7 T/R 1x. Not checked yet. | 1
| 2020-04-13 13:45 | April | 13:45 | Afternoon | Monday | Weekdays | 13 | 2020 | 2020-01-23 11:30 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Lightning Arrester | - | Checked And Found 5BSB OCB7 Fdr #7 T/R 0x, Ctr 498/498, R/F 51N Patrolled The Line On 22/Jan/2020 And Found Broken La On Phase @2 Pole 4C/45 Cause: Lightning Arrester | 1
72 | 2020-04-13 14:50 | April | 14:50 | Afternoon | Monday | Weekdays | 13 | 2020 | 2020-01-22 09:12 | 13.8KV NEW KOTABATAK FEEDER #4 | Petko | PGT South | Fair | Others | 63 | 09:12 NKB fdr #4 load dropped 76 A (141 / 64 A) 09:42 Reported no power for some unit pumps at KBGS Call TDO Crew to checked the problem. 10:15 Manual Open CKB fdr #6 (to maintain level tank at KBGS 10:16 Manual Open OKB fdr #2 (currently d/s NKB fdr #2) (to maintain level tank) 11:15 Checked and found RCL for 6MVA TX at KBGS (for area 1 and 2) T/LO counter: 1018 / 1019, caused: unidentified 11:31 Blocked and close the RCL, OK then release the block. Cause: Unidentified | 1
| 2020-04-13 14:50 | April | 14:50 | Afternoon | Monday | Weekdays | 13 | 2020 | 2020-01-23 10:59 | 13.8KV NEW KOTABATAK FEEDER #4 | Petko | PGT South | Fair | Others | 63 | Checked And Found 5443/RCL T/O T/O , Ctr 1010/1819, R/F 51 Patrolled The Line On 22/Jan/2020 But Found Nothing Cause: Others | 1
73 | 2020-04-13 19:41 | April | 19:41 | Night | Monday | Weekdays | 13 | 2020 | 2020-01-22 09:15 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Petko | PGT South | Fair | Emergency | 0 | 09:15 Manually Open CKB fdr #6, closed at 12:24 (to maintain level tank at KBGS) Cause: Emergency | 1
74 | 2020-04-13 21:10 | April | 21:10 | Night | Monday | Weekdays | 13 | 2020 | 2020-01-22 09:16 | 13.8KV KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Emergency | 0 | 09:16 Manually Open OKB fdr #2 (currently d/s NKB fdr #2) , closed at 11:45 (to maintain level tank at KBGS) Cause: Emergency | 1
75 | 2020-04-13 21:10 | April | 21:10 | Night | Monday | Weekdays | 13 | 2020 | 2020-01-23 10:30 | SOUTH BALAM SUBSTATION | Bangko-Balam | PGT North | Fair | Planned Maintenance | 2135 | 10:30 Manual Open South BLM fdr #1, closed at 15:10, ctr: 411 10:42 Manual Open South BLM fdr #2, closed at 15:03, ctr: 118 (not change) 10:46 Manual Open South BLM fdr #3, closed at 15:07, ctr: 174 10:35 Manual Open South BLM fdr #4, closed at 15:13, ctr: 376 10:48 Manual Open Sout BLM C/S, closed at 14:22, ctr: 180 (MTCE team to replaced VR unit of So. BLM Subst.) Cause: Planned Maintenance | 1
76 | 2020-04-14 05:20 | April | 5:20 | Morning | Tuesday | Weekdays | 14 | 2020 | 2020-01-23 14:16 | 13.8KV BANGKO FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 0 | 14:16 Bangko fdr #2 load dropped 204 A (240 / 36 A) Bangko fdr #1 load dropped 24 A (146 / 122 A) Bangko fdr #3 load dropped 179 A (202 / 23 A) Bangko fdr #4 load dropped 90 A (196 / 116 A) Cause: Not Checked Yet | 1
77 | 2020-04-14 05:20 | April | 5:20 | Morning | Tuesday | Weekdays | 14 | 2020 | 2020-01-23 14:16 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 0 | Nella fdr #1 load dropped 80 A (196 / 116 A) Cause: Not Checked Yet | 1
78 | 2020-04-14 07:22 | April | 7:22 | Morning | Tuesday | Weekdays | 14 | 2020 | 2020-01-23 14:16 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 0 | SINTONG fdr #2 load dropped 54 A (240 / 186 A) Cause: Not Checked Yet | 1
79 | 2020-04-14 08:30 | April | 8:30 | Morning | Tuesday | Weekdays | 14 | 2020 | 2020-01-23 20:05 | CENTRAL DURI POWER PLANT | Duri | PGT North |  | Under investigation | - | 20:05 CGT #3 Trip Off by alarm Loss of Flame Trip , Hydraulic Press Low 20:17 Closed Bus Tie Breaker Cause : Under Investigate | 1
80 | 2020-04-14 13:12 | April | 13:12 | Afternoon | Tuesday | Weekdays | 14 | 2020 | 2020-01-23 22:05 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 22:05 CGT #3 S/U, then On line at 22:30 to Restore Power due to CGT#3 Trip Off | 1
81 | 2020-04-15 14:33 | April | 14:33 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 2020-01-24 08:26 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Animal | 0 | MENGGALA fdr #2 T/R 1x MENGGALA GFPC T/R 1x Cause: Not Checked Yet | 1
82 | 2020-04-16 03:54 | April | 3:54 | Night | Thursday | Weekdays | 16 | 2020 | 2020-01-25 06:46 | 13.8KV NORTH DURI FEEDER #11 | Duri | PGT North | Fair | Tree | 31 | NDuri VCB fdr#11 T/R 1x Not checked yet | 1
| 2020-04-16 06:39 | April | 6:39 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-01-28 08:20 | 13.8KV NORTH DURI FEEDER #11 | Duri | PGT North | Fair | Tree | 31 | Checked and found: NDRSB/13.8VCB11 T/R, Counter : 196 / 197, Relay Flag : 51N Patrolled the line found : High tree Phase : 1 Cause : Tree | 1
83 | 2020-04-16 06:39 | April | 6:39 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-01-25 09:10 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 58 | 09:10 Manual Open RCL 44/BX/06 (PGT fdr #2), closed at ….. Relocate power line to support Toll Highway Project Location Impacted/Off : Asih #02; Gading #01, N. Asih #03, Ami #03 21:10 Manually Closed Recl 44 BX 06, after finished the Job Relocate Pole Cause: Planned Maintenance | 1
84 | 2020-04-16 06:41 | April | 6:41 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-01-25 17:39 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Lightning | 39 | KETIGUL feeder #2 T/R 1x KETIGUL feeder #1 dropped 27 A (114 / 87 A) Not Checked Yet | 1
| 2020-04-16 06:41 | April | 6:41 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-01-27 17:41 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Lightning | 39 | Checked and found : PKTGL/13.8VCB2 T/R, Counter : 372 / 373, Relay Flag : 51N Patrolled the line found : Broken LA Phase : 1 Cause : Lightning | 1
85 | 2020-04-16 06:42 | April | 6:42 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-01-26 08:22 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Fair | Lightning | 16 | 8D feeder #5 T/R 1x Not Checked Yet | 1
| 2020-04-16 06:42 | April | 6:42 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-01-29 15:41 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Fair | Lightning | 16 | Checked and found: 8D OCB fdr #5 T/R 1x, Ctr: 566 / 566 (ctr problem), R/F : 51N Patrolled the line but found nothing Cause : Lightning | 1
86 | 2020-04-16 13:38 | April | 13:38 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-01-26 22:22 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Rain and Lightning | Unidentified | 99 | C.Duri ACB fdr#5 T/R 1x. Not checked yet. | 1
| 2020-04-16 14:11 | April | 14:11 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-01-31 15:06 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Rain and Lightning | Unidentified | 99 | Checked and found ACB 22 CD fdr #5, ctr: 264 / 265, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
87 | 2020-04-16 14:11 | April | 14:11 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-01-26 22:22 | 115KV CENTRAL DURI / BATANG LINE | Duri | PGT North | Rain and Lightning | Unidentified | 153 | 115Kv Line C.Duri / Batang GCB#31 T/R 1x R/F: 51N, 51@1@3. 115Kv Line C.Duri / Batang GCB#31 T/O, then closed at 00:00. 115Kv Line Sintong / Batang GCB#25 T/R 1x. 5B 13.8Kv fdr#4 T/O R/F 81, then closed at 00:23. 5B 13.8Kv fdr#5 T/O R/F:81, then closed a t00:23. Pinang fdr#1 Load dropped 85A (10/25A). Nella fdr#1 Load dropped 114A (196/82A). Nella fdr#2 Load dropped 34A (70/36A). Bangko fdr#2 Load dropped 198A (250/52A)Pump Off. Bangko fdr#3 Load dropped 182A (200/18A)Pump Off. Bangko fdr#4 Load dropped 85A (170/85A0. Sintong fdr#2 Load dropped 91A (240/149A). S.Balam fdr#1 Load dropped 114A (150/36A). S.Balam fdr#2 Load dropped 78A (85/7A) Pump Off. S.Balam fdr#3 Load dropped 87A (100/13A) Pump Off. S.Balam fdr#4 Load dropped 146A (200/54A). Menggala fdr#1 Load dropped 88A (184/90A. Menggala fdr#2 Load dropped 114A (156/42A). Batang fdr#3 Load dropped 19A (69/50A). Ketigul fdr#1 Load dropped 15A (114/99A). Bekasap fdr#3 Load dropped 22A (254/232A). Bekasap fdr#5 Load dropped 117 A (248/131A) Pump Off. Pematang fdr#1 Load dropped 149A (198/49A). Pematang fdr#2 Load dropped 17A (105/88). Rangau fdr#2 Load dropped 43A (183/140A). Petani fdr#2 Load dropped 43A (228/185A). Not checked yet. | 1
| 2020-04-17 06:57 | April | 6:57 | Morning | Friday | Weekdays | 17 | 2020 | 2020-01-31 15:14 | 115KV CENTRAL DURI / BATANG LINE | Duri | PGT North | Rain and Lightning | Unidentified | 153 | Checked and found: / CDSY GCB #31 T/R 1x, counter: 63 / 64, R/F: 51N / CDSY GCB #33 T/R 1x, counter: 665 / 666, R/F: 21P / STG GCB #25 T/R 1x, counter: 324 / 325, R/F: 87L Patrolled the line but found nothing Cause : Unidentified | 1
88 | 2020-04-17 06:57 | April | 6:57 | Morning | Friday | Weekdays | 17 | 2020 | 2020-01-26 22:53 | 44KV PEMATANG MAIN / RANGAU LINE | Bekasap | PGT North | Rain and Lightning | Dead End Insulator | - | 44Kv Line Pematang Main / Rangau GCB#2 T/R 1x. Not checked yet. | 1
| 2020-04-17 08:26 | April | 8:26 | Morning | Friday | Weekdays | 17 | 2020 | 2020-01-30 17:30 | 44KV PEMATANG MAIN / RANGAU LINE | Bekasap | PGT North | Rain and Lightning | Dead End Insulator | - | Checked And Found PMT Main GCB fdr #2 T/R 1x, Ctr: 22102/22103, R/F: 50P @1 Patrolled The Line And Found Dead End Flash Over On Phase @1 Pole RGU #19 Cause: Dead End Insulator | 1
89 | 2020-04-17 08:26 | April | 8:26 | Morning | Friday | Weekdays | 17 | 2020 | 2020-01-26 22:56 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Pin Insulator | - | N.Duri VCB fdr#1 T/R 1x. Not checked yet. | 1
| 2020-04-17 10:27 | April | 10:27 | Morning | Friday | Weekdays | 17 | 2020 | 2020-01-30 17:20 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Pin Insulator | - | Checked And Found ND VCB Fdr #1 T/R 2x, Ctr: 337/339, R/F: 51N Patrolled The Line And Found Bypass Switch Insulator, broken 38 % On layer 1 Phase @1 Pole 12/E3/27 Cause: Pin Insulator | 1
90 | 2020-04-17 10:35 | April | 10:35 | Morning | Friday | Weekdays | 17 | 2020 | 2020-01-27 00:44 | 13.8KV 8D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 12 | 8D fdr#2 T/R 1x. Not checked yet. | 1
| 2020-04-17 10:36 | April | 10:36 | Morning | Friday | Weekdays | 17 | 2020 | 2020-01-30 08:27 | 13.8KV 8D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 12 | Checked and found: 8D OCB fdr #2 T/R, Ctr: 290 / 294, R/F : 51P Patrolled the line but found nothing Cause : Lightning | 1
91 | 2020-04-17 10:39 | April | 10:39 | Morning | Friday | Weekdays | 17 | 2020 | 2020-01-27 01:34 | 115KV KOTABATAK JUNCTION / 5B LINE | Petko | PGT South | Rain and Lightning | Lightning | 16 | 115Kv Line 5B/KBJ GCB#22 T/R. 115Kv Line 5B/KBJ GCB#24 T/R. 115Kv Line KBJ /5B GCB#21 & GCB#23 Not Operated. Not checked yet. | 1
| 2020-04-17 11:16 | April | 11:16 | Morning | Friday | Weekdays | 17 | 2020 | 2020-01-29 09:25 | 115KV KOTABATAK JUNCTION / 5B LINE | Petko | PGT South | Rain and Lightning | Lightning | 16 | Checked And Found / 115 kV OCB #24 KBJ T/R 1x Ctr 669/670 / 115 kV OCB #22 KBJ Not Operate, ctr: 663 / 663 / R/F 21BC Patrolled The Line But Found Nothing Cause: Lightning | 1
92 | 2020-04-17 14:40 | April | 14:40 | Afternoon | Friday | Weekdays | 17 | 2020 | 2020-01-27 01:34 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Heavy Rain | Pin Insulator | 365 | 01:34 4B fdr #1 load dropped 92 A (130 / 38 A) 4B fdr #2 load dropped 17 A (49 / 32 A) 4B fdr #3 load dropped 44 A (94 / 54 A ) 09:00 Checked and found RCL 4B/101 T/LO (last counter: 657) Patrolled the line and found broken insulator o/p 4A/09 15:04 Isolate power line by opening visual opening RCL 4B/101 Replaced the broken insulator by MTCE team 16:45 Manual block and close RCL 4B/101, OK. then release the block. Cause: Pin Insulator | 1
93 | 2020-04-17 17:50 | April | 17:50 | Afternoon | Friday | Weekdays | 17 | 2020 | 2020-01-27 06:08 | 4 DELTA SUBSTATION | Minas | PGT South | Rain and Lightning | Under investigation | 157 | 06:08 4D 115KV C/S TX#1 T/O. Effected 4D Fdr#1, #2, #3 No Power 08:35 Checked and found / C/S of TX/1 T/O but the visual open switch not fully open / VCB fdr #1m fdr #2m fdr #3 are OPEN / 86HR operate, no relay flag activated. suspected operated by bucholtz / found animal (lizard) at auxiliary contact on control box of C/S / station service tx on bus/1 found OFF 09:00 Isolate C/S by opened isolation switch of C/S 09:44 Transferred load of 4D fdr #1 to 3D fdr #6 by close LBS/A at GS/5 09:48 Transferred load of 4D fdr #2 to 4D fdr #5 by close LBS 3D/66 10:03 Transferred load of 4D fdr #3 to 3D fdr #3 by close LBS 4C/27 10:55 Close tie LBS for bus/1 and bus/2 of 4D SS (STA TX re/energize) Cause :Under Investigation | 1
94 | 2020-04-18 08:56 | April | 8:56 | Morning | Saturday | Weekends | 18 | 2020 | 2020-01-27 10:37 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Others | 3 | 10:37 Manually open LBS 15/Z/16A (Balam feeder #1), closed at 11:11 MTCE team to tre in reactive well at Antara#09. Well impacted/off Antara#06 & Antara#02. Cause: Project | 1
95 | 2020-04-18 09:20 | April | 9:20 | Morning | Saturday | Weekends | 18 | 2020 | 2020-01-27 11:54 | 13.8KV 8D FEEDER #1 | Minas | PGT South | Fair | Emergency | 0 | 11:54 Manually open 8D feeder#1, closed at 12:12 (to limiting fluida for GS/1 due to plan to S/D 8D feeder#7) Cause: Emergency | 1
96 | 2020-04-18 17:00 | April | 17:00 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-01-27 11:54 | 13.8KV 8D FEEDER #10 | Minas | PGT South | Fair | Emergency | 0 | 11:54 Manually open 8D feeder#10, closed at 2:12 (to limiting fluid for GS/1 due to plan to S/D 8D feeder#7) Cause: Emergency | 1
97 | 2020-04-18 17:00 | April | 17:00 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-01-27 11:56 | 13.8KV 8D FEEDER #7 | Minas | PGT South | Fair | Emergency | 5 | 11:56 Manually Open 8D feeder#7, closed at MTCE team To bypass and isolate recloser 8D/88A (Reported the recloser indicate and potentially to burned out) Cause: Emergency. | 1
98 | 2020-04-18 17:00 | April | 17:00 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-01-27 17:55 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Pin Insulator | 22 | CD fdr #1 (ACB #11) T/R 1x, ctr: 271/272, R/F: 51N, 51G Not Checked Yet | 1
| 2020-04-18 17:00 | April | 17:00 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-01-30 17:25 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Pin Insulator | 22 | Checked And Found CD ACB11 Fdr #1 T/R 1x, Ctr: 272/273, R/F :51N Patrolled The Line and Found Insulator Support for LBS 09/L5/01 broken 8 % On Phase @2 Cause: Pin Insulator | 1
99 | 2020-04-18 18:00 | April | 18:00 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-01-27 18:12 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 49 | 3D VCB fdr #4 T/R 1x Not Checked Yet | 1
| 2020-04-18 18:24 | April | 18:24 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-01-30 08:31 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 49 | Checked And Found 3D OCB Fdr #4 T/R 1x, Ctr: 94/95, R/F: 51N Patrolled The Line But Found Nothing Cause: Lightning | 1
100 | 2020-04-18 18:24 | April | 18:24 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-01-31 11:37 | 4.16KV NO RUMBAI FEEDER #2 | Rumbai | PGT South | Fair | Lightning Arrester | - | Checked and found: NRBSB/4.16VCB2 T/R, Counter : 363 / 364, Relay Flag : 51 Patrolled the line found: Broken LA Phase : 1 Cause : Lightning Arrester | 1
101 | 2020-04-18 18:35 | April | 18:35 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-01-28 09:49 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Pin Insulator | 26 | Central Duri 13.8 kV ACB#11 feeder #1 T/R 1x, ctr: 272 / 273, R/F: 51G, 51N. Not Checked Yet. | 1
| 2020-04-18 18:35 | April | 18:35 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-01-31 15:18 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Pin Insulator | 26 | Checked And Found CDRSG ACB11 1 Fdr #1 T/R 1x, Ctr 272/273, R/F 51N Patrolled The Line On 29/Jan/2020 And Found Insulator Support Blade Lbs 2 Pecah 8 % On Phase @2 Pole 09 L5 01 Cause: Pin Insulator | 1
102 | 2020-04-18 19:06 | April | 19:06 | Night | Saturday | Weekends | 18 | 2020 | 2020-01-28 11:28 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Cloudy | Unidentified | - | Duri Community VCB Fdr#3 T/R 1x Not checked yet | 1
| 2020-04-18 19:06 | April | 19:06 | Night | Saturday | Weekends | 18 | 2020 | 2020-01-28 11:28 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Cloudy | Unidentified | - | Checked And Found DCSG ACB26 Fdr #3 T/R 1x, Ctr 101/102, R/F 51 Patrolled The Line On 29/Jan/2020 But Found Nothing Cause: Unidentified | 1
103 | 2020-04-18 19:37 | April | 19:37 | Night | Saturday | Weekends | 18 | 2020 | 2020-01-29 07:49 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 54 | Sintong VCB feeder#2 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. | 1
104 | 2020-04-18 19:37 | April | 19:37 | Night | Saturday | Weekends | 18 | 2020 | 2020-01-29 08:03 | 13.8KV MBL SUBSTATION 1 DURI FEEDER #1 | Duri | PGT North | Heavy Rain | Dead End Insulator | 25 | MSU#1 VCB feeder#1 T/R 1x (Carry load 5B feeder#2 & 3). MSU#1 feeder#2 load dropped 125A (181/56A) (Carry load 5B#6). Not checked yet. | 1
| 2020-04-18 20:14 | April | 20:14 | Night | Saturday | Weekends | 18 | 2020 | 2020-04-02 13:45 | 13.8KV MBL SUBSTATION 1 DURI FEEDER #1 | Duri | PGT North | Heavy Rain | Dead End Insulator | 25 | Checked and found : MBL1IDR/13.8VCB1 T/R, Counter : 416 / 417, Relay Flag : 51. Patrolled the line found : Broken Dead End Insulator Phase : 2, 3, Cause : Dead End Insulator | 1
105 | 2020-04-18 20:14 | April | 20:14 | Night | Saturday | Weekends | 18 | 2020 | 2020-01-29 15:30 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 15:30 C Duri ACB #45 (Breaker for station service) Trip. C Duri ACB #46 (Gen Breaker CDGT #4) Trip. Checked and found Transformer for Station Service Leakage. 15:49 Closed C Duri ACB #46 //> OK CDGT #4 back to Normal. Cause: Transformer for Station Service Leakage. | 1
106 | 2020-04-18 20:57 | April | 20:57 | Night | Saturday | Weekends | 18 | 2020 | 2020-01-29 17:52 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Tree | 77 | 17:52 C Duri feeder #1 load dropped 68A (70/2A) 19:20 Checked and found RCL 39/AV/36 T/O (on block position) counter: 198 / 199, R/F: None 19:28 Manually close RCL 39/AV/36, OK. Not Patrolled Yet | 1
| 2020-04-18 20:57 | April | 20:57 | Night | Saturday | Weekends | 18 | 2020 | 2020-01-31 15:21 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Tree | 77 | Patrolled the line and found high palm trees under power line near pole 36/AU/36 Cause : Tree | 1
107 | 2020-04-19 02:13 | April | 2:13 | Night | Sunday | Weekends | 19 | 2020 | 2020-01-29 19:17 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Pin Insulator | 29 | PETANI feeder #1 T/R 1x Not Checked Yet | 1
| 2020-04-19 06:07 | April | 6:07 | Morning | Sunday | Weekends | 19 | 2020 | 2020-03-02 11:15 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Pin Insulator | 29 | Checked and found PTN OCB fdr #1 T/R, 1x Ctr: 154 / 155, R/F : 51N Patrolled the line and found Pin Insulator @3 Flash Over o/p 34/AZ/30 Cause : Pin Insulator | 1
108 | 2020-04-19 06:44 | April | 6:44 | Morning | Sunday | Weekends | 19 | 2020 | 2020-01-30 06:56 | ROKAN SUBSTATION | Bangko-Balam | PGT North | Fair | Animal | 80 | 06:56 ROKAN Substation C/S TRIP. ROKAN fdr #2 T/R 1X , Relay flag:51@1. counter: 1317/ 1318. ROKAN fdr #2, fdr #3, fdr #4 no power / So BLM fdr #1 dropped 10 A (153 / 143 A) / So BLM fdr #4 dropped 64 A (200 / 136 A) / NLA fdr #1 dropped 16 A (198 / 182 A) / NLA fdr #2 dropped 9 A (70 / 61 A) / BKO fdr #1 dropped 9 A (159 / 150 A) / BKO fdr #2 dropped 7 A (251 / 144 A) / BKO fdr #4 dropped 66 A (173 / 107 A) / MGL fdr #1 dropped 20 A (183 / 163 A) / MGL fdr #2 dropped 9 A (155 / 146 A) / STG fdr #1 dropped 8 A (87 / 79 A) / PTN fdr #1 dropped 6 A (226 / 220 A) / PTN fdr #2 dropped 7 A (71 /64 A) / PMT fdr #1 dropped 56 A (194 / 138 A) / PMT fdr #2 dropped 9 A (104 / 95 A) / KTG fdr #1 dropped 8 A (117 / 109 A) / KTG fdr #3 dropped 11 A (44/ 33 A) Not Checked Yet 08:18 Checked and found Rokan 115KV Circuit Switcher T/O. Patrolled the line and found the Monkey dead in VR. R/F: D60 , 51T. 09:50 Manually Open Rokan feeder #2. Manually Open Rokan feeder #3. Manually Open Rokan feeder #4. 09:56 Manually Closed & block Rokan feeder #2 /////>Ok. Counter:1319. 09:58 Manually Closed & block Rokan feeder #3 /////>Ok. Counter:631. 09:59 Manually Closed & block Rokan feeder #4 /////>Ok. Counter:780. Cause: Animal (Monkey). | 1
109 | 2020-04-19 10:00 | April | 10:00 | Morning | Sunday | Weekends | 19 | 2020 | 2020-01-31 19:56 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Fair | Animal | 150 | 19:56 Bekasap feeder #3 Load dropped 38A (240/202A). 20:00 It was reported No power atAmpuh GS. 21:24 Checked and found Recl. 34/BI/18 T/LO ctr: 188/194 R/F: 51p@3. Patrolled the line but found nothing ( at Cucut and Hiu field). 22:50 Blocked and closed Recl: 34/BI/18, but tripped again. Continued to patrolled the line at Pukat field and found Dead Monkey at Buck Arm o/p: 32/BH/13. 00:53 Completed to remove the Dead Monkey. 00:56 Blocked and closed Recl: 34/BI/18, Ok then released the Block ctr: 195. Cause: Animal (Monkey). | 1
1 | 2020-04-19 13:15 | April | 13:15 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-01-02 12:37 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Fair | Powerline - Conductor | 719 | 12:37 ND feeder #7 T/LO 16:09 Checked and found ND VCB fdr #7 T/LO, ctr: 113 - 117, R/F: 51P @1 @2 Patrolled the line, found spark at guy wire at pole NF-06 and Broken Conductor O/P 10-K2-19 18:25 Block and close ND VCB fdr #7 but failed 18:36 Open both side isolation switch of ND VCB fdr #7 Function test the VCB by close command but failed again. Planned to transfer ND fdr #7 to ND fdr #8 via LBS 10-K6-14 18:52 Unplugged RCL 10-K6-02 and block ND VCB fr #8 18:57 Closed LBS 10-K6-14, suddenly ND fdr #8 T/O Reopened the LBS 10-K6-14 and then close again ND VCB fdr #8 21:22 Isolate broken conductor by cutting jumper on pole 10-K2-19 (power line OFF from 10-K2-19 to branch line 10-K4-16 to 10-K4-30) 21:27 transferred part line of ND fdr #7 to ND fdr #8 by close LBS 10-K6-14 but any spark at bypass switch of RCL 10-K2-18 21:29 Reopened LBS 10-K6-14 and then open bypass switch of RCL 10-K2-18 21:45 Transferred part line of ND fdr #7 to ND fdr #2 by close LBS 10-K2-33A 21:47 Transferred part load of ND fdr #7 to ND fdr #8 by close LBS 10-K6-14 Continue to repair the broken conductor tomorrow. Cause: Broken Conductor | 1
| 2020-04-19 13:30 | April | 13:30 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-02-02 09:57 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Fair | Powerline - Conductor | 719 | 09:57 Manually block and Closed N.Duri VCB feeder #7----->OK. then release the block. 09:59 Open LBS 10-K6-14. 10:17 Open LBS 10-K2-33A connect wire broken. 12:05 Closed LBS 10-K2-33A. Cause: Broken Conductor. Production loss: 1 Feb 20 -->> 383 Bbls / 158 Wells 2 Feb 20 -->> 182 Bbls --------------------------------------------- + Grand Total >> 565 Bbls / 158 Wells | 1
2 | 2020-04-19 13:30 | April | 13:30 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-01-02 18:39 | 13.8KV MENGGALA GFPC | Bangko-Balam | PGT North | Cloudy and Lightning | Lightning | - | Menggala OCB feeder #1 T/R 1x. Menggala GFPC T/R 1x. Not checked yet. | 1
3 | 2020-04-19 13:30 | April | 13:30 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-02-02 23:59 | CPI POWER SYSTEM |  |  | Fair | Normal Condition | - | CPI POWER SYSTEM NORMAL CONDITION | 1
4 | 2020-04-19 13:30 | April | 13:30 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-03-02 23:59 | CPI POWER SYSTEM |  |  | Fair | Normal Condition | - | CPI Power System Normal Condition | 1
5 | 2020-04-19 13:30 | April | 13:30 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-04-02 07:27 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | - | Duri Community ACB feeder#1 T/R 1x. Not checked yet. | 1
| 2020-04-19 13:30 | April | 13:30 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-08-02 08:49 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | - | Checked And Found DCSG ACB25 Fdr #1 T/R 1x, Ctr 140-141, R/F 51N Patrolled The Line On 05-Feb-2020 And Found La Broken On Phase @1 Pole 5Kt-06 Cause: Lightning Arrester | 1
6 | 2020-04-19 13:30 | April | 13:30 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-04-02 07:42 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Construction Job | 0 | Manually Open Ketigul VCB feeder #1. Due to Lifting and Dismantle and Install pipe 20" road crossing at Tilan Main road. Cause: Contruction job. | 1
7 | 2020-04-19 13:30 | April | 13:30 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-04-02 14:26 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | - | CD ACB-28 fdr #16 T/R 1x, R/F 51N Not Checked Yet | 1
| 2020-04-19 13:46 | April | 13:46 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-09-02 19:26 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | - | Checked and found: CDRSG-13.8ACB28 T/R, Counter : 272 - 273, Relay Flag : 51G. Patrolled the line found : Tidak ada temuan hasil patrol, patrolsudah dilakukan tgl 6 Feb 2020, Relay flag 51G dan 51N 51phase1. Phase : 1 Cause : Unidentified | 1
8 | 2020-04-19 14:03 | April | 14:03 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-04-02 14:26 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | - | North Duri VCB fdr #1 T/R 1x Not Checked Yet | 1
| 2020-04-19 14:03 | April | 14:03 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-08-02 08:59 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | - | Checked And Found NDRSB VCB1 Fdr #1 T/R 1x, Ctr 339-340, R/F 51 Patrolled The Line On 05-Feb-2020 And Found La Broken On Phase @1 Pole 12 E5 11 Cause: Lightning Arrester | 1
9 | 2020-04-19 14:05 | April | 14:05 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-04-02 14:30 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Lightning | 26 | KTGL VCB feeder #2 T/R 1x Not Checked Yet | 1
| 2020-04-19 14:34 | April | 14:34 | Afternoon | Sunday | Weekends | 19 | 2020 | 2020-05-02 18:26 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Lightning | 26 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 374 - 375, Relay Flag : 51 Patrol led the line found: LA Broken phase B and C dan sudah dilakukan penggantiannya di 3 phase hari ini Rabu 5 Feb 2020, RF 51Phase B dann 51 Phase c dan 51N Phase : 2, 3, Cause : Lighting | 1
10 | 2020-04-20 10:34 | April | 10:34 | Morning | Monday | Weekdays | 20 | 2020 | 2020-05-02 01:20 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Fair | Others | 0 | 8D VCB fdr #5 T/R 1x Not Checked Yet | 1
| 2020-04-20 10:34 | April | 10:34 | Morning | Monday | Weekdays | 20 | 2020 | 2020-07-02 14:55 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Fair | Others | 0 | Checked And Found 8DSB OCB5 Fdr #5 T/R 0x, Ctr 566-566, R/F 51N Patrolled The Line On 05-Feb-2020 But Found Nothing Cause: Others | 1
11 | 2020-04-20 10:53 | April | 10:53 | Morning | Monday | Weekdays | 20 | 2020 | 2020-05-02 10:22 | KETIGUL SUBSTATION | Bangko-Balam | PGT North | Fair | Planned Maintenance | 387 | 10:22 Manually Open Ketigul 115Kv GCB#2. then closed at 15:53. Manually Open Ketigul 115Kv GCB#3, then closed at 15:46. 10:25 Manually Open 13.8 Kv Ketigul fdr#3, then closed at 15:56. Manually Open 13.8 Kv Ketigul fdr#2, then closed at 15:54. For Replaced NGR and Repaired 28Mva Tx Leak at Ketigul Substation.. Cause: Plan Maintenance. Production loss Ketigul feeder #2 = 276 Bbls / 19 wells. Ketigul feeder #3 = 111 Bbls / 4 wells. ---------------------------------------------- + Grand total = 387 Bbls / 23 wells. | 1
12 | 2020-04-20 11:04 | April | 11:04 | Morning | Monday | Weekdays | 20 | 2020 | 2020-06-02 05:21 | NEW PETAPAHAN SUBSTATION | Petko | PGT South | Fair | Relay Failure | 979 | 05:21 Petapahan 115 KV GCB#3 T/O. Petapahan 115 KV GCB#5 T/O. Petapahan TX #2 DeEnergize Effected No Power at, Petapahan VCB fdr#6, #7, #8 05:26 Manually Opened PTH VCB fdr#4. 05:45 Checked & found PTH TX#2, R/F: 86 HR. 06:09 Manually Opened PTH VCB fdr#3. 06:15 Manually Opened PTH VCB fdr#6. then Closed at: 06:32. 06:16 Manually Opened PTH VCB fdr#8. then Closed at: 06:33. 06:18 Manually Opened PTH VCB fdr#7. then Closed at: 06:40. (WIP). 06:19 Manually Closed PTH GCB#3 06:19 Manually Closed PTH GCB#5 Cause:Under investigation. | 1
| 2020-04-20 14:45 | April | 14:45 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-06-02 15:49 | NEW PETAPAHAN SUBSTATION | Petko | PGT South | Fair | Relay Failure | 979 | Checked And Found PHNSB VCB6 T/O T/O , Ctr 382-383, R/F 86HR Patrolled The Line On 06-Feb-2020 And Found Relay Failure Cause: Relay Failure | 1
13 | 2020-04-20 14:45 | April | 14:45 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-06-02 16:23 | NEW PETAPAHAN SUBSTATION | Petko | PGT South | Fair | Relay Failure | 352 | 16:23 Petapahan 115 KV GCB#3 T/O. Petapahan 115 KV GCB#5 T/O. Petapahan TX #2 DeEnergize Effected No Power at Petapahan VCB fdr#6, #7, #8 16:27 Manually Opened PTH VCB fdr#4. then Closed at: 17:27. 16:27 Manually Opened PTH VCB fdr#3. then Closed at: 17:38. 16:30 Checked & found PTH TX#2, R/F: 86 HR. 16:37 Manually Opened PTH VCB fdr#6. then Closed at: 17:37. 16:38 Manually Opened PTH VCB fdr#8. then Closed at: 17:33. 16:45 Manually Opened PTH VCB fdr#7. then Closed at: 17:31. (WIP). 17:15 Manually Opened Disconnect VR Tx#2. 17:26 Manually Opened MOD Tx#2. 17:27 Manually Closed PTH GCB#3. 17:28 Manually Closed PTH GCB#5. 17:29 Manually Closed TIE breaker. Cause:Under investigation. | 1
| 2020-04-20 14:45 | April | 14:45 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-07-02 13:53 | NEW PETAPAHAN SUBSTATION | Petko | PGT South | Fair | Relay Failure | 352 | Checked And Found PHNSB VCB6 T/O , Ctr 383-384, R/F 86HR Patrolled The Line On 06-Feb-2020 And Found Relay Failure Cause: Relay Failure | 1
14 | 2020-04-20 16:45 | April | 16:45 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-06-02 18:55 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Dead End Insulator | 83 | Petani VCB fdr#1 T/R 1x. Not checked yet. | 1
| 2020-04-20 16:45 | April | 16:45 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-11-02 13:52 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Dead End Insulator | 83 | Checked and found: PTNSB-13.8OCB1 T/R, Counter : 155 - 156, Relay Flag : 51N Patrolled the line found : Dead end flash over Phase : 1 Cause : Dead End Insulator | 1
15 | 2020-04-21 16:43 | April | 16:43 | Afternoon | Tuesday | Weekdays | 21 | 2020 | 2020-06-02 19:28 | 13.8KV CENTRAL DURI FEEDER #15 | Duri | PGT North | Fair | Lightning Arrester | 0 | C Duri ACB #18 (feeder #15) T/R 1x. Not checked yet. | 1
| 2020-04-21 16:43 | April | 16:43 | Afternoon | Tuesday | Weekdays | 21 | 2020 | 2020-11-02 13:56 | 13.8KV CENTRAL DURI FEEDER #15 | Duri | PGT North | Fair | Lightning Arrester | 0 | Checked and found: CDRSG-13.8ACB18 T/R, Counter : 416 - 417, Relay Flag : 51N. Date Patrol : 10-FEB-2020 Patrolled the line found : Jumper LA putus Phase : 2 Cause : Lightning Arrester | 1
16 | 2020-04-21 17:02 | April | 17:02 | Afternoon | Tuesday | Weekdays | 21 | 2020 | 2020-07-02 23:59 | CPI POWER SYSTEM |  |  |  |  | - | CPI Power System Normal Condition. | 1
17 | 2020-04-21 17:02 | April | 17:02 | Afternoon | Tuesday | Weekdays | 21 | 2020 | 2020-08-02 03:08 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Dead End Insulator | 31 | Petani OCB feeder #2 T/R 1x. Petani feeder #1 load dropped 203A (229-26A). Not checked yet. | 1
| 2020-04-22 09:29 | April | 9:29 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-11-02 14:00 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Dead End Insulator | 31 | Checked and found: PTNSB-13.8OCB2 T/R, Counter : 326 - 328, Relay Flag : 50 Patrolled the line found : Dead end flash over Phase : 1 Operated Device : PTNSB-13.8OCB2 T/R Counter : 326 - 328 Relay Flag : 50 Finding Patrol : Pin pecah Phase : 2 Pole : 34-AZ-60 Cause : Dead End Insulator | 1
18 | 2020-04-22 09:29 | April | 9:29 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-08-02 08:42 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | 2 | S.Balam feeder #1 load dropped 100A (156-56A). S.Balam GFPC T/R 1x. Not checked yet. | 1
| 2020-04-22 11:05 | April | 11:05 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-09-02 07:31 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | 2 | Checked and found: 5440-R.16AA43 T/SO, Counter : 89 - 90, Relay Flag : 51N Patrolled the line found : not found Cause : Unidentified | 1
19 | 2020-04-22 12:25 | April | 12:25 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-08-02 09:00 | 13.8KV 6DN FEEDER #6 | Minas | PGT South | Fair | Planned Maintenance | 37 | 09:00 Transfer Part Load 6DN fdr#6 to Minas fdr#6 by Closed LBS 6E-08, and Opened Recloser 6E-64 Manually Opened 6DN VCB fdr#6, ( impact Some Wells Down ) to Conduct Vegetation Control at well 6D-19 12:00 Normalized back 6DN fdr#6 from Minas fdr#6 After Finished the Jobs Cause: Planned Maintenance | 1
20 | 2020-04-22 13:17 | April | 13:17 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-08-02 09:50 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | 148 | 09:50 It was reported no power at well SO.Balam#216,#071,#028,#303 (S.Balam feeder #4). 10:00 Check & found Recloser 17-AA-43 T/SO. Patrol the line but found nothing. Blocked & closed recloser 17-AA-43,then release the blocked. Cause: Unidentified. | 1
21 | 2020-04-22 13:17 | April | 13:17 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-08-02 10:55 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Fair | Animal | 135 | 10:55 It was reported no power at well Petani #82, #83, #118, #97 (Petani fdr#2). 12:00 Checked & found Recl. 32 AW 09 T/LO ctr:516-521. Patrolled the line & found Dead Monkey on Recl. 32 AW 09. Blocked & closed Recl. 32 AW 09, then release the block. Cause: Animal (Bird). | 1
22 | 2020-04-22 13:17 | April | 13:17 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-08-02 17:46 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Fair | Animal | 0 | 17:46 It was reported b/o fuse o/p 06-Q5-28 d/s C.Duri feeder #3. 18:45 Checked and found @3 b/o fuse to 500 KVA TX, and replaced the TX. 20:41 Blocked C.Duri feeder #14. 20:44 Due to closed for to 500 KVA TX for SMF area#6, ok. 20:46 Re Normallized block C.Duri feeder #14. Cause : Animal (Monkey). | 1
23 | 2020-04-22 13:17 | April | 13:17 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-09-02 10:00 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Planned Maintenance | 449 | 10:00 Manually Opened Recl. 39AV36 (C.Duri fdr#1). Repaired Cross Arm o/p 38AS09. Replaced Broken Recl. 38AS09. 15:17 Blocked & Closed Recl. 39AV36, then release the block. (Recl. 38AS09 Still By Pass by Control Recl. Trouble. Cause: Plan Maintenance. | 1
24 | 2020-04-22 13:27 | April | 13:27 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-09-02 17:34 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Fair | Others | 0 | CKBS Feeder #5 load dropped 156A (206-50A). Not checked yet. | 1
| 2020-04-22 13:27 | April | 13:27 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-11-02 16:56 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Fair | Others | 0 | Checked and found: 5442-RCL T/R, Counter : 328 - 329, Relay Flag : NONE Patrolled the line found : Not Found Cause : Others | 1
25 | 2020-04-22 13:30 | April | 13:30 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-10-02 09:17 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 266 | 09:17 Menggala VCB fdr#2 T/O (Blocked position). Patrolled the line but found noting. 11:00 Blocked & Closed Menggala VCB fdr#2, ok. Not checked yet. | 1
| 2020-04-22 13:30 | April | 13:30 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-12-02 09:17 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 266 | 15:30 Checked and found Menggala 13.8KV VCB fdr #2 T/O ctr: 560-561 R/F: 51N (On blocked for Project JOB) Patrolled the line but found nothing. Cause: Unidentified. | 1
26 | 2020-04-22 13:30 | April | 13:30 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-10-02 15:25 | 13.8KV 8C FEEDER #5 | Minas | PGT South | Fair | Planned Maintenance | 51 | 15:25 Manually Opened 8C OCB fdr#5. Replaced 1500 Kva Tx with the same size at GS#2. 16:05 Blocked & Closed 8C OCB fdr#5, then release the block. Cause: Plan Maintenance. | 1
27 | 2020-04-22 13:53 | April | 13:53 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-10-02 18:03 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Lightning | 116 | 18:03 Nella VCB fdr#2 T/O. Nella GFPC T/O. 18:20 Checked and found Nella OCB feeder#2 T/SO. R/F:51N,51@1 Counter:255-256. Patrolled the line found nothing. 20:04 Manually blocked and closed Nella OCB feeder #2.-->Ok. and then release the block. 20:09 Manually blocked and closed Nella GFPC.-->Ok. Counter:233-237. Cause: Suspect lightning. | 1
28 | 2020-04-22 13:53 | April | 13:53 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-11-02 15:53 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 145 | Nella VCB fdr#1 T/R 1x Not checked yet | 1
29 | 2020-04-22 14:09 | April | 14:09 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-12-02 07:28 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | CDGT-2 offline and then S/D for HCT workint to install PSV and tie in CDGF | 1
30 | 2020-04-22 14:09 | April | 14:09 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-12-02 07:39 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 07:39 MGT-6 S/U and then online at 08:10 (to accommodate CDGT-2 offline and shut down) | 1
31 | 2020-04-22 16:27 | April | 16:27 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-12-02 09:17 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Fair | Construction Job | - | 09:17 Manual Open VCB Libo fdr #1 (support toll road at Libo area) 18:06 Manual Closed the VCB after finished the Jobs Cause: Planned maintenance | 1
32 | 2020-04-22 16:27 | April | 16:27 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-12-02 09:17 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Fair | Construction Job | - | 09:17 Manual Open VCB Libo fdr #2 (support toll road at Libo area) 18:04 Manual Closed the VCB after finished the Jobs Cause : Planned maintenance | 1
33 | 2020-04-22 16:27 | April | 16:27 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-12-02 22:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Rain and Lightning | Dead End Insulator | - | Duri Community ACB fdr#1 T/R 1x Not checked yet | 1
| 2020-04-22 16:27 | April | 16:27 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 17-02-2020 17:41 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Rain and Lightning | Dead End Insulator | - | Checked and found: DCSG-13.8ACB25 T/R, Counter : 141 - 152, Relay Flag : 51N Patrolled the line found : Dead end flash over Cause : Dead End Insulator | 1
34 | 2020-04-22 16:27 | April | 16:27 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-02-13 02:12 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Rain and Lightning | Lightning | 79 | 02:12 NKBS fdr#2 Load Dropped 89A (220/131A). 06:12 NKBS fdr#2 T/R 1x. Not checked yet. | 1
| 2020-04-22 16:35 | April | 16:35 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-02-13 15:27 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Rain and Lightning | Lightning | 79 | Checked and found: NKBKSB/13.8OCB2 T/R, Counter : 99933 / 99934, Relay Flag : 50N. Patrolled the line found : Not Found Cause : Lightning | 1
35 | 2020-04-22 16:35 | April | 16:35 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-02-13 04:21 | 13.8KV NORTH DURI FEEDER #11 | Duri | PGT North | Rain and Lightning | Others | 0 | 04:21 N.Duri nVCB fdr#11 T/O (Blocked Position). 04:26 Blocked & closed N.Duri VCB fdr#11. Not checked yet. | 1
| 2020-04-23 13:51 | April | 13:51 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-02-17 17:30 | 13.8KV NORTH DURI FEEDER #11 | Duri | PGT North | Rain and Lightning | Others | 0 | Checked and found: NDRSB/13.8VCB11 T/R, Counter : 197 / 198, Relay Flag : 51N. Patrolled the line found : Isolator by pass ada bekas terbakar di phase 1 dan di tanah ada di temukan pecahan isolator Cause : Others | 1
36 | 2020-04-23 13:51 | April | 13:51 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-02-13 07:28 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Fair | Transformer Failure | 0 | 07:28 Duri Community feeder #1 T/R 1x ctr:...…….R/F:51p@2 15:18 Duri Community feeder #1 tripped again. 15:31 Duri Community feeder #1 tripped again. 15:35 Duri Community feeder #1 tripped again. 16:05 Duri Community feeder #1 tripped again. 16:35 Duri Community feeder #1 tripped again. 16:38 Checked and found Duri Comm. fdr #1 T/R ctr:......R/F:51P@2. 16:40 Duri Community feeder #1 tripped again. 16:42 Duri Community feeder #1 T/LO ctr:......R/F:...…… 17:34 open isolation switch for under ground cable O/P: N/N (back of PGT Maintenance Shop) 17:35 Blocked and closed Duri Comm. fdr #1, OK 17:36 Manuall Open Duri Comm. fdr #1. Closed isolation switch for under ground cable O/P: N/N (back of PGT Maintenance Shop) 17:46 Patrolled the line and found all@ b/o fuse for 150KVA TX/8 beside Bowling Alley. Isolated 150KVA TX/8 near Bowling Alaley. !8:28 Blocked and closed Duri Comm. fdr #1, OK then released the block. 18:38 Closed LBS near Mass hall to transfer TX/6, 6 and 7 to Duri Comm fdr #2. Cause: Transforner failure. | 1
37 | 2020-04-23 14:16 | April | 14:16 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-02-13 08:28 | 115KV KOTABATAK JUNCTION / LIBO LINE | Petko | PGT South | Fair | Construction Job | 0 | (Switching to Shutted Down power 115KV KBJ/Libo) 08:28 Manuall Open Libo VCB fdr #1, /////>Closed at 17:50. 08:29 Manuall Open Libo VCB fdr #2, /////>Closed at 17:48. 08:31 Manual Open 115KB KBJ/Libo GCB #53, /////>Closed at 08:52. 08:31 Manual Open 115KB KBJ/Libo GCB #53, /////>Closed at 08:54. (Switching to Nomalized power 115KV KBJ/Libo) 17:21 Manual Open 115KB KBJ/Libo GCB #53, /////>Closed at 17:40. 17:23 Manual Open 115KB KBJ/Libo GCB #53, /////>Closed at 17:42. Cause: Project (TOL Road). | 1
38 | 2020-04-23 14:16 | April | 14:16 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-02-13 14:52 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Transformer Failure | 0 | 14:52 Duri Community feeder #1 T/R 1x 15:18 DCM fdr #1 T/R again 1x Not Checked Yet | 1
| 2020-04-23 14:18 | April | 14:18 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-02-17 17:36 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Transformer Failure | 0 | Checked and found D.Comunitu ACB25 Fdr#1 T/LO Ctr:141/152 R/F: 51. Patrolled the line & found Trafo 8 bowling Failure Replace 150Kva Tx with the same size at Duri Bowling. Cause : Transformer Failure. | 1
39 | 2020-04-23 14:18 | April | 14:18 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-02-13 14:54 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Animal | 102 | South BALAM feeder #1 T/R 1x Not Checked Yet | 1
40 | 2020-04-23 14:18 | April | 14:18 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-02-14 07:57 | 115KV KOTABATAK JUNCTION / LIBO LINE | Petko | PGT South | Fair | Construction Job | 323 | 07:57 Switching to shut down 115KV KBJ/LIBO line. Manual Open 13.8KV LIBO VCB fdr #2,////>Closed at 17:50. 07:59 Manual Open 13.8KV LIBO VCB fdr #1,////>Closed at 17:52. 08:02 Manual Open 115KV KBJ/LIBO GCV # 53, /////>Closed at 08:24. 08:04 Manual Open 115KV KBJ/LIBO GCV # 55, /////>Closed at 08:26. 17:19 Manual Open 115KV KBJ/LIBO GCV # 53, /////>Closed at 17:41. 17:21 Manual Open 115KV KBJ/LIBO GCV # 55, /////>Closed at 17:43. Cause: Project (TOL Road). | 1
41 | 2020-04-23 14:18 | April | 14:18 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-02-14 15:32 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 15:32 CGT #4 Tripped Off by alarm "Lube Oil Brg. Header Temp. High due to loss off 480V Supply. 17:29 Started UP CGT #4 and On line to the system at 17:47 to restored load after trip. | 1
42 | 2020-04-23 14:56 | April | 14:56 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-02-14 16:10 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Cloudy | Broken Fuse Holder | 2 | DF feeder #4 T/R 1x Not Checked Yet | 1
| 2020-04-23 14:56 | April | 14:56 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-02-17 17:08 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Cloudy | Broken Fuse Holder | 2 | Checked and found: DFSG/13.8ACB51 T/R, Counter : 576 / 577, Relay Flag : 50. Patrolled the line found : Fuse Holder broken Phase : 2 Cause : Broken Fuse Holder | 1
43 | 2020-04-24 13:58 | April | 13:58 | Afternoon | Friday | Weekdays | 24 | 2020 | 2020-02-15 07:36 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 19 | 07:36 Nella fdr 1 T/R 1x, Recloser Capacitor Bank Trip, manual closed at 07:54 13:38 Field verification completed by OPS PGT, all RCL on normal condition as well checker information, any locations still OFF. Not Checked Yet | 1
44 | 2020-04-24 13:58 | April | 13:58 | Afternoon | Friday | Weekdays | 24 | 2020 | 2020-02-15 10:42 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | 10:42 Darling feeder #3 T/R 1x Darling feeder #4 dropped 11 A (20 / 9 A) Darling feeder #8 dropped 17 A (32 / 15 A) Not Checked Yet | 1
| 2020-04-24 17:29 | April | 17:29 | Afternoon | Friday | Weekdays | 24 | 2020 | 2020-02-17 17:00 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | Checked and found: DRLG3/13.8VCB3 T/R, Counter : 265 / 266, Relay Flag : 51N. Patrolled the line found : No Findings Cause : Unidentified | 1
45 | 2020-04-24 17:29 | April | 17:29 | Afternoon | Friday | Weekdays | 24 | 2020 | 2020-02-15 10:50 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Lightning | 361 | 10:50 MSU/2 feeder #2 (BKS Main SS) load dropped 213 A (256 / 38 A) 12:27 Reported no power at some location at BEKASAP Area (well BKS #53, #86,. #113, #114, #118, #119 12:45 Checked and found RCL 37/BD/12 T/O (on block position) Counter: 1224 / 1225, R/F: None 12:48 Manual Close RCL 37/BD/12, OK then release the block. Not Patrolled Yet | 1
| 2020-04-24 17:30 | April | 17:30 | Afternoon | Friday | Weekdays | 24 | 2020 | 2020-02-18 11:11 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Lightning | 361 | Checked and found RCL 37/BD/12 T/O (on block) , Counter: 1224 / 1225, R/F : NONE. Patrolled the line but found nothing Cause : Lightning | 1
46 | 2020-04-24 17:30 | April | 17:30 | Afternoon | Friday | Weekdays | 24 | 2020 | 2020-02-15 12:08 | 13.8KV MINAS FEEDER #2 | Minas | PGT South | Rain and Lightning | Others | 26 | Minas ACB/13 (feeder #2) T/R 1x, ctr: 81 / 82, R/F: 51P @3 Not Patrolled Yet | 1
| 2020-04-24 23:17 | April | 23:17 | Night | Friday | Weekdays | 24 | 2020 | 2020-02-16 13:27 | 13.8KV MINAS FEEDER #2 | Minas | PGT South | Rain and Lightning | Others | 26 | Checked and found MNS fdr #2 T/R 1x, ctr: 81 / 82, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
47 | 2020-04-25 23:59 | April | 23:59 | Night | Saturday | Weekends | 25 | 2020 | 2020-02-15 12:13 | 13.8KV 4D FEEDER #5 | Minas | PGT South | Rain and Lightning | Dead End Insulator | 72 | 12:13 4D fdr #5 T/R 1x 4D Fdr 2 Dropped 94 A (137/43 A) 4D Fdr 4 Dropped 17 A (70/53 A) 4D Fdr 6 Dropped 133 A (135/2 A) Not Checked Yet | 1
| 2020-04-26 03:28 | April | 3:28 | Night | Sunday | Weekends | 26 | 2020 | 2020-02-16 17:55 | 13.8KV 4D FEEDER #5 | Minas | PGT South | Rain and Lightning | Dead End Insulator | 72 | Checked and found 4D fdr #5 T/R 1x, ctr: 376 / 377, R/F: 51P @1 @2 Patrolled the line and found broken dead end insulator @1 and @2 o/p 4D/27 Cause : Dead End Insulator | 1
48 | 2020-04-26 03:28 | April | 3:28 | Night | Sunday | Weekends | 26 | 2020 | 2020-02-15 12:24 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Rain and Lightning | Pin Insulator | 9 | 6DN fdr #2 T/R 1x, counter: 331/332, R/F: 51P @1 @2 6DN Fdr #1 Load dropped 119 A (159/40 A) 6DN Fdr #3 Load dropped 125 A (189/64 A) Not Checked Yet | 1
| 2020-04-26 22:27 | April | 22:27 | Night | Sunday | Weekends | 26 | 2020 | 2020-02-16 13:50 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Rain and Lightning | Pin Insulator | 9 | Checked and found 6DN fdr #2 T/R 1x, ctr: 331/332, R/F: 51P @2 Patrolled the line and found broken pin insulator @2 on NN pole Cause : Pin Insulator | 1
49 | 2020-04-27 05:10 | April | 5:10 | Morning | Monday | Weekdays | 27 | 2020 | 2020-02-15 17:01 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | CDGT #3 S/U and then online at 17:20 | 1
50 | 2020-04-27 09:30 | April | 9:30 | Morning | Monday | Weekdays | 27 | 2020 | 2020-02-15 17:47 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Tree | 550 | 17:47 MENGGALA fdr #2 T/LO MENGGALA GFPC T/R 1x 17:51 Informed to TDO Crew 18:17 Reported by Pager GS that found broken insulator on pole 28AL04 & 28AL03 19:45 Checked & found @1 broken insulator on pole 28AL04 & 28AL03 Fall Down Tree Between pole 28AL04 & 28AL05. 19:53 Opened LBS o/p 27AL03, then closed at 21:45. 21:48 Blocked & closed Menggala fdr#2, then release the block. Cause: Tree. | 1
| 2020-04-27 09:30 | April | 9:30 | Morning | Monday | Weekdays | 27 | 2020 | 2020-02-16 17:47 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Tree | 550 | checked and founded Menggala fdr 2 T/LO ctr :561/565 R/F 51N. also founded GFPC T/R 1x ctr 134/135 Patrolled power line and founded : 1. Fallen trees on power line between pole 28 AL 04 and 05 2. broken pin on pole 28 AL 03 @fasa 1 and 28 AL 04 @fasa 1. | 1
51 | 2020-04-27 09:38 | April | 9:38 | Morning | Monday | Weekdays | 27 | 2020 | 2020-02-15 18:20 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Cloudy | Lightning Arrester | 48 | 18:20 It was reported no power o/p 07/U1/19 (D.Field fdr#2). 19:24 Checked & found Recl: 07/U1/19 T/LO Ctr:72/77. Patrolled the line & found @1@2@3 Broken LA o/p 07/U1/10, then Isolated. 21:45 Blocked & closed Recl. 07/U1/19, then release the block. Cause: Lightning Arrester. | 1
52 | 2020-04-27 16:07 | April | 16:07 | Afternoon | Monday | Weekdays | 27 | 2020 | 2020-02-16 10:25 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 82 | 10:25 Manual Open RCL 29/AA/07 (BLM fdr #4), closed at 12:41 to completing primary jumpers TX for reactive well SE/BLM #05. Cause: Planned Maintenance | 1
53 | 2020-04-27 20:25 | April | 20:25 | Night | Monday | Weekdays | 27 | 2020 | 2020-02-17 08:19 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Unidentified | 0 | Rangau Fdr#2 Load dropped 83A(128/45A) Not checked yet | 1
| 2020-04-27 20:25 | April | 20:25 | Night | Monday | Weekdays | 27 | 2020 | 2020-02-19 09:34 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Unidentified | 0 | Checked and found RCL 23/BD/01 T/R 1x, Ctr 420/421, R/F/: None Patrolled the line On 18/Feb/2020 but found nothing Cause: Unidentified | 1
54 | 2020-04-27 22:24 | April | 22:24 | Night | Monday | Weekdays | 27 | 2020 | 2020-02-18 14:04 | 13.8KV 8C FEEDER #3 | Minas | PGT South | Heavy Rain | Others | 47 | 14:04 8C fdr #3 load dropped 90 A (121 / 31 A) 16:51 Reported no power for location 8D/43; 8D/45 and around 17:20 Checked and found RCL 8D/18A T/LO, ctr: 195 / 199, R/F: NONE Patrolled the line and found palm tree touch the conductor near pole 8D/46A 17:51 Execute/cut the palm tree, finished at 19:00 19:18 Block and closed RCL 8D/18A, OK then release the Block. Cause: Tree | 1
55 | 2020-04-27 22:24 | April | 22:24 | Night | Monday | Weekdays | 27 | 2020 | 2020-02-19 08:58 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Pin Insulator | 15 | Rokan 13.8 KV VCB feeder #2 T/R 1X. Not Checked yet. | 1
| 2020-04-28 08:45 | April | 8:45 | Morning | Tuesday | Weekdays | 28 | 2020 | 2020-02-20 16:48 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Pin Insulator | 15 | Checked and found: RKNSB/13.8VCB2 T/R, Counter : 1319 / 1320, Relay Flag : 51 Patrolled the line found : Pin pecah di bagian bawah Cause : Pin Insulator | 1
56 | 2020-04-28 10:05 | April | 10:05 | Morning | Tuesday | Weekdays | 28 | 2020 | 2020-02-19 09:01 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 0 | 09:01 Manual Open LBS 45/BZ/05 (Pungut fdr #2), closed at 15:52. for due to Tol Project (Asih,Gading field were off). Cause: Planned maintenance. | 1
57 | 2020-04-28 10:33 | April | 10:33 | Morning | Tuesday | Weekdays | 28 | 2020 | 2020-02-19 09:04 | 13.8KV PETAPAHAN FEEDER #4 | Petko | PGT South | Fair | Planned Maintenance | 40 | 09:04 Manual Open Recloser 38/CW/01 (Petapahan fdr #4), closed at 11:35. for Replaced Dead end at o/p 27/CV/14. Cause: Planned maintenance. | 1
58 | 2020-04-28 12:12 | April | 12:12 | Afternoon | Tuesday | Weekdays | 28 | 2020 | 2020-02-19 10:56 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Transformer Failure | 73 | 10:56 Menggala OCB fdr #1 Load dropped 58A (184/126A). 11:17 It was reported No Power at Meso GS. 12:29 Checked and Recloser 19/AO/01 T/LO (Menggala fdr#1) Ctr:500/504. Patrolled the line found @1 B/O fuse for 750 KVA TX. 15:32 Manually blocked & closed Recloser 19 / AO / 01 /////> Ok. and then release the block. Cause: TX failure ( TX low megger). | 1
| 2020-04-28 12:37 | April | 12:37 | Afternoon | Tuesday | Weekdays | 28 | 2020 | 2020-02-21 10:56 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Transformer Failure | 73 | Replace 750Kva with the same size aboive at So. Menggala GS. Cause: Transformer Failure. | 1
59 | 2020-04-29 08:12 | April | 8:12 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-02-20 06:59 | 13.8KV NORTH DURI FEEDER #8 | Duri | PGT North | Fair | Tree | 0 | North Duri fdr #8 T/R 1x Not Checked Yet | 1
| 2020-04-29 08:12 | April | 8:12 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-02-23 11:43 | 13.8KV NORTH DURI FEEDER #8 | Duri | PGT North | Fair | Tree | 0 | Checked and found ND VCB feeder #8 T/R 1x, Ctr 101/102, R/F: 51P @1 Patrolled the line and found high trees closed to power line near pole 10/K2A/23 Cause: Tree | 1
60 | 2020-04-29 09:29 | April | 9:29 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-02-20 10:30 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 10:30 S/U MGT #1 and then Online the unit at 10:57. | 1
61 | 2020-04-29 21:54 | April | 21:54 | Night | Wednesday | Weekdays | 29 | 2020 | 2020-02-20 11:16 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 11:16 MGT #4 S/U and then Online the unit at 11:39 | 1
62 | 2020-04-29 21:54 | April | 21:54 | Night | Wednesday | Weekdays | 29 | 2020 | 2020-02-20 13:58 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Normal Condition | 28 | Ketigul feeder #2 load dropped 82A (84/2A). Not checked yet. | 1
| 2020-04-30 00:44 | April | 0:44 | Night | Thursday | Weekdays | 30 | 2020 | 2020-02-26 14:24 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Normal Condition | 28 | Checked and found: PKTGL/13.8VCB2 None, Counter : 375 / 375, Relay Flag : NONE. Patrolled the line found : No Findings Cause : Normal Condition | 1
63 | 2020-04-30 00:44 | April | 0:44 | Night | Thursday | Weekdays | 30 | 2020 | 2020-02-20 14:15 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 14:15 Offline MGT #1 and then S/D the unit for Standby. | 1
64 | 2020-04-30 10:26 | April | 10:26 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-02-20 14:15 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:15 S/U CDGT #4 and then Online the unit at 14:36. | 1
65 | 2020-04-30 10:26 | April | 10:26 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-02-20 15:55 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 15:55 Offline CDGT #1 and then S/D the unit for Standby. | 1
66 | 2020-04-30 10:26 | April | 10:26 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-02-21 11:56 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain | Lightning | 32 | 3D OCB feeder #2 T/R 1X. Not checked yet. | 1
| 2020-04-30 11:25 | April | 11:25 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-02-23 16:27 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain | Lightning | 32 | Checked and found 3D OCB feeder #2 T/R 9x, Ctr: 360/369, R/F: 51N Patrolled the line but found nothing Cause: Lightning | 1
67 | 2020-04-30 11:25 | April | 11:25 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-02-21 14:02 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 7 | 14:02 Manually open Recloser 19/AO/01 D/S Menggala #1. Replaced 750 KVA TX. 14:52 Manually blocked & closed Recloser 19/AO/01/////>Ok. and then release the block. ( TX still off). Cause: Planned maintenance. | 1
68 | 2020-04-30 16:22 | April | 16:22 | Afternoon | Thursday | Weekdays | 30 | 2020 | 2020-02-22 06:38 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 06:38 CDGT #3 Emergency Offline and Shutdown due to hydraulic oil leak. | 1
69 | 2020-04-30 16:22 | April | 16:22 | Afternoon | Thursday | Weekdays | 30 | 2020 | 2020-02-22 11:40 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 11:40 S/U CDGT #3 and then online the system at 11:52. | 1
70 | 2020-04-30 17:56 | April | 17:56 | Afternoon | Thursday | Weekdays | 30 | 2020 | 2020-02-22 12:40 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Fair | Tree | 135 | 12:40 ND fdr #7 T/O, (reported no power on pole 10/L1/16) 13:20 Checked and found ND VCB fdr #7 T/LO, Counter: 119 / 123, R/F: 51N, 51P @1 @2. Patrolled the line and found fallen tree touch to power line o/p 10/K6/02. Execute the fallen tree and finished at 17:10. 17:17 Blocked and Close ND VCB fdr #7, OK. then release the block. Caused: Tree | 1
71 | 2020-04-30 17:56 | April | 17:56 | Afternoon | Thursday | Weekdays | 30 | 2020 | 2020-02-23 06:30 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | - | 06:30 So BALAM feeder #4 load dropped 17 A (200 / 183 A) Not Checked Yet | 1
| 2020-04-30 23:05 | April | 23:05 | Night | Thursday | Weekdays | 30 | 2020 | 2020-02-28 07:32 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | - | Checked and found: SBLM/13.8VCB4 None, Counter : 376 / 376, Relay Flag : NONE. Patrolled the line found : NONE Cause : Unidentified | 1
72 | 2020-04-30 23:05 | April | 23:05 | Night | Thursday | Weekdays | 30 | 2020 | 2020-02-23 10:27 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Dumai | PGT North | Fair | Planned Maintenance | - | 10:27 Manually open Recloser: H 33/07 D/S Dumai feeder #4. Due to Repair Hot Spot on LBS: H/55. Cut danger trees. 14:44 Manually blocked and closed Recloser: H 33/07 //> Ok Cause: Plan maintenance. | 1
73 | 2020-05-13 00:05 | May | 0:05 | Night | Wednesday | Weekdays | 13 | 2020 | 2020-02-24 01:07 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Cloudy | Unidentified | 78 | 01:07 8D feeder #5 T/SO 01:48 Checked and found 8D VCB fdr #5 T/O, ctr: 566 (problem not change) R/F: 81 (under frequency) 01:49 Block and Close 8D fdr #5. OK then release the block 04:10 8D feeder #5 T/SO again 04:52 Checked and found 8D VCB fdr #5 T/O, ctr: 566 (problem not change) R/F: 81 (under frequency) 04:53 Block and Close 8D fdr #5. OK then release the block Cause: Unidentified (frequency) | 1
| 2020-05-13 00:05 | May | 0:05 | Night | Wednesday | Weekdays | 13 | 2020 | 2020-02-25 13:47 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Cloudy | Unidentified | 78 | Checked and found 8D OCB fdr #5 T/SO, Counter : 566 / 566, Relay Flag : 81 Patrolled the line found nothing. Cause : Unidentified | 1
74 | 2020-05-13 00:11 | May | 0:11 | Night | Wednesday | Weekdays | 13 | 2020 | 2020-02-24 09:06 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Construction Job | - | 09:06 Manually open LBS 15/Z/16 D/S S.Balam feeder #1. Due to tie in new well at Antara #11. 12:12 Manually Closed LBS 15/Z/16. Cause : Construction Job. | 1
75 | 2020-05-13 00:11 | May | 0:11 | Night | Wednesday | Weekdays | 13 | 2020 | 2020-02-24 13:59 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Broken Fuse Cut Out | 0 | C.Duri ACB #12 (feeder #2 ) T/R 1x. R/F 51N , 51 @1,@2 Counter :399/400. Not checked yet. | 1
| 2020-05-13 18:35 | May | 18:35 | Afternoon | Wednesday | Weekdays | 13 | 2020 | 2020-02-26 14:18 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Broken Fuse Cut Out | 0 | Checked and found: CDRSG/13.8ACB12 T/R, Counter : 399 / 400, Relay Flag : 51N. Patrolled the line found : Broken FCO for PT Recloser 40/BA/02 Cause : Broken Fuse Cut Out | 1
76 | 2020-05-13 18:35 | May | 18:35 | Afternoon | Wednesday | Weekdays | 13 | 2020 | 2020-02-25 09:43 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 09:43 S/U MGT #3 and then Online the unit at 10:05. | 1
77 | 2020-05-14 16:57 | May | 16:57 | Afternoon | Thursday | Weekdays | 14 | 2020 | 2020-02-25 09:45 | 13.8KV 4D FEEDER #5 | Minas | PGT South | Fair | Planned Maintenance | 3 | 09:45 Manual Open 4D OCB fdr #5, closed at 16:22 MTCE team to replace insulator @1 on pole 4D/12 Cause: Planned Maintenance | 1
78 | 2020-05-14 16:57 | May | 16:57 | Afternoon | Thursday | Weekdays | 14 | 2020 | 2020-02-25 15:02 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 15:02 S/U MGT #2 and then Online the unit at 15:48. | 1
79 | 2020-05-14 17:25 | May | 17:25 | Afternoon | Thursday | Weekdays | 14 | 2020 | 2020-02-26 06:37 | 13.8KV DARLING VCB FEEDER #6 | Duri | PGT North | Fair | Static Wire | 110 | 06:37 Darling fdr #6 T/SO (2x trip) CGS COC Area 5 Closed Tie Breaker Not Checked Yet | 1
| 2020-05-15 06:07 | May | 6:07 | Morning | Friday | Weekdays | 15 | 2020 | 2020-02-26 14:12 | 13.8KV DARLING VCB FEEDER #6 | Duri | PGT North | Fair | Static Wire | 110 | 07:30 Checked and found Darling VCB fdr#6 T/LO, Ctr: 230/230, R/F:51N. Patrolled the line found, Broken Static Wire Phase @1 O/p 05/M7/18 08:55 Isolated the Static Wire O/p LBS 05/N7/20N to 05/M7/24 (No power 1 road) Manually Block & Closed Darling VCB fdr#6, then released the Block 12:35 Closed LBS 05/N7/20N After finished Repair the Broken Static Cause : Broken Static Wire (Counter not Change) | 1
80 | 2020-05-15 06:07 | May | 6:07 | Morning | Friday | Weekdays | 15 | 2020 | 2020-02-26 11:35 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 16 | 11:35 So Balam Fdr#1 Load dropped 90A(153/63A) 12:50 Checked & found Recl 16.Z.25 T/O, Ctr: 62/63 Patrolled the Line, but found nothing 13:45 Block & Closed the Recloser, then released the Block Cause: Unidentified | 1
81 | 2020-05-15 14:07 | May | 14:07 | Afternoon | Friday | Weekdays | 15 | 2020 | 2020-02-26 13:40 | CENTRAL DURI POWER PLANT | Duri | PGT North | Fair |  | - | 13:40 CDGT #1 S/U, then On Line at 14:24 to Backed Up NDC CT#3 Shut Down | 1
82 | 2020-05-15 16:05 | May | 16:05 | Afternoon | Friday | Weekdays | 15 | 2020 | 2020-02-26 13:47 | MINAS POWER PLANT | Minas | PGT South | Fair |  | - | 13:47 MGT #6 S/U, then On Line at 14:17 to Backed Up NDC CT#3 Shut down | 1
83 | 2020-05-15 16:26 | May | 16:26 | Afternoon | Friday | Weekdays | 15 | 2020 | 2020-02-26 15:29 | NORTH DURI POWER PLANT | Duri | PGT North | Fair |  | - | 15:29 NDC CT #3 Off Line, then S/D for Maintenance. | 1
84 | 2020-05-15 17:25 | May | 17:25 | Afternoon | Friday | Weekdays | 15 | 2020 | 2020-02-26 16:13 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Fair | Tree | 49 | Batang VCB fdr#3 T/R 1x Not checked yet | 1
| 2020-05-15 19:13 | May | 19:13 | Night | Friday | Weekdays | 15 | 2020 | 2020-02-29 18:26 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Fair | Tree | 49 | Checked and found: BTGSB/13.8OCB3 T/R, Counter : 387 / 388, Relay Flag : 51 Patrolled the line found : Relay Flag 51 N, 51 Phase B dan 51 phase C, Pohon sawit sudah menyentuh line dan sudah gosong dekat Pemburu 20. Cause : Tree | 1
85 | 2020-05-16 06:01 | May | 6:01 | Morning | Saturday | Weekends | 16 | 2020 | 2020-02-26 16:15 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 97 | 16:15 Sintong VCB fdr#1 T/O in Block Position (PT KRS Lifting Job) Got Inform from PT KRS Its Normal conditions Patrolled the Line, but found nothing 17:33 Manually Closed the VCB in Block Position Cause: Unidentified | 1
86 | 2020-05-16 06:01 | May | 6:01 | Morning | Saturday | Weekends | 16 | 2020 | 2020-02-26 17:50 | MINAS POWER PLANT | Minas | PGT South | Fair |  | - | 17:50 MGT #1 S/U, then On Line at 18:28 to Backed up NDC CT#3 Shut down | 1
87 | 2020-05-16 06:24 | May | 6:24 | Morning | Saturday | Weekends | 16 | 2020 | 2020-02-27 17:43 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 17:43 S/U NDC#3, then on line the unit at 18:10. | 1
88 | 2020-05-16 06:24 | May | 6:24 | Morning | Saturday | Weekends | 16 | 2020 | 2020-02-27 19:04 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 19:04 Offline MGT #2 , and then S/D the unit for Standby. | 1
89 | 2020-05-16 12:00 | May | 12:00 | Afternoon | Saturday | Weekends | 16 | 2020 | 2020-02-27 19:50 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 19:50 Offline MGT #1 , and then S/D the unit for Standby. | 1
90 | 2020-05-16 12:00 | May | 12:00 | Afternoon | Saturday | Weekends | 16 | 2020 | 2020-02-27 19:53 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 19:53 Offline CDGT #1 , and then S/D the unit for Standby. | 1
91 | 2020-05-16 21:44 | May | 21:44 | Night | Saturday | Weekends | 16 | 2020 | 2020-02-27 20:09 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 20:09 Offline MGT #11 , and then S/D the unit for Standby. | 1
92 | 2020-05-16 21:44 | May | 21:44 | Night | Saturday | Weekends | 16 | 2020 | 2020-02-28 06:34 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Guy Wire | 127 | 06:34 Sintong VCB feeder #2 T/R. Sintong GFPC T/R 1x. 07:30 Checked & found Recl. 28/AF/17 T/O (Block position) Ctr:461/462. Patrolled the line & found Broken guy wire on T/P STG#21. 08:40 Blocked & Closed Recl. 28/AF/17. Cause: Broken Guy Wire. | 1
93 | 2020-05-17 05:55 | May | 5:55 | Morning | Sunday | Weekends | 17 | 2020 | 2020-02-28 11:35 | 13.8KV PETAPAHAN FEEDER #6 | Petko | PGT South | Fair | Unidentified | 91 | 11:35 Petapahan fdr#6 T/O (blocked position). 12:30 Checked and found Petapahan fdr#6 T/O ctr : 384 / 385. r/f : 51@2 Patrol the line but found nothing. 12:35 Blocked & closed Petapahan fdr#6. the release the block. Couse : Unidentified. | 1
94 | 2020-05-17 05:55 | May | 5:55 | Morning | Sunday | Weekends | 17 | 2020 | 2020-02-29 09:00 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 11 | 09:00 Manually Opened Recl. 2F/11 (3D fdr#2). Trimming Danger Trees D/S Recl. 2F/11. 14:30 Blocked & Closed Recl. 2F/11, then Release the block. Cause: Plan Maintenance. | 1
1 | 2020-05-17 11:23 | May | 11:23 | Morning | Sunday | Weekends | 17 | 2020 | 2020-01-03 12:33 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 423 | 12:33 Nella VCB fdr#1 T/O (Block Position). 14:00 Checked & found Nella VCB fdr#1 T/O Ctr:571-572 R/F:51@1. Patrolled the line but found nothing. 14:14 Blocked & Closed Nella VCB fdr#1, then release the block. Cause: Un identified. JDE Number = 123456 | 1
2 | 2020-05-17 11:23 | May | 11:23 | Morning | Sunday | Weekends | 17 | 2020 | 2020-02-03 09:20 | MINAS POWER PLANT | Minas | PGT South |  |  | - | MGT#5 Off line then S/D the Unit for S/B. | 1
3 | 2020-05-17 12:04 | May | 12:04 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-02-03 10:00 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Fair | Planned Maintenance | 132 | 10:00 Manually Opened 3D fdr#4. Repaired Cross Arm o/p 3D-216. 16:15 Blocked & closed 3D fdr#4, then release the block. Cause: Plan Maintenance. | 1
4 | 2020-05-17 12:04 | May | 12:04 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-02-03 14:15 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 30 | Nella VCB feeder #2 T/R ix. Nella GFPC T/R 1x. Not checked yet. | 1
| 2020-05-17 12:11 | May | 12:11 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-03-03 07:18 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 30 | Checked and found: NLASB-13.8VCB2 T/O, Counter : 571 - 572, Relay Flag : 51N. Patrolled the line found : none Cause : Unidentified | 1
5 | 2020-05-17 13:51 | May | 13:51 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-02-03 16:16 | MINAS POWER PLANT | Minas | PGT South |  |  | - | MGT#4 Trip by Alarm Exhaust Thermocouple Trouble. | 1
6 | 2020-05-17 13:51 | May | 13:51 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-03-03 09:44 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 30 | Nella VCB fdr#2 T/R 1x. Not checked yet. | 1
7 | 2020-05-17 16:04 | May | 16:04 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-03-03 10:54 | 13.8KV CENTRAL DURI FEEDER #15 | Duri | PGT North | Fair | Pin Insulator | 0 | C.Duri ACB fdr#15 T/R 1x Ctr:417-418 R/F:51@1@2. Not patrolled yet. | 1
| 2020-05-17 16:04 | May | 16:04 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-09-03 08:38 | 13.8KV CENTRAL DURI FEEDER #15 | Duri | PGT North | Fair | Pin Insulator | 0 | Checked and found: CD ACB #18 (fdr #15) T/R 1x, Ctr : 417 - 418, R/F: 51N. Patrolled the line found broken pin @3 o/p 06-Q5-19 Cause : Pin Insulator | 1
8 | 2020-05-17 18:29 | May | 18:29 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-03-03 15:05 | NEW PETAPAHAN SUBSTATION | Petko | PGT South |  | Planned Maintenance | 70 | 15:05 Perform S/P Reenergized Petapahan TX#2 after troubleshoot 86HR 15:28 Manually Opened PTH VCB fdr#6, Closed at 16:03 15:28 Manually Opened PTH VCB fdr#8, Closed at 16:08 Cause: Planned Maintenance. Production loss: 1. Petapahan VCB feeder #6 = 47 Bbls / 9 wells. 2. Petapahan VCB feeder #8 = 28 Bbls / 8 wells. ------------------------------------------------------ + Grand total = 75 Bbls / 17 wells. | 1
9 | 2020-05-17 18:29 | May | 18:29 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-04-03 08:40 | 13.8KV 8C FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 0 | 08:40 Manuall Open 13.8KV 6C fdr #3. TOL Road project. Cause: Project | 1
10 | 2020-05-18 07:31 | May | 7:31 | Morning | Monday | Weekdays | 18 | 2020 | 2020-04-03 09:00 | 13.8KV 8C FEEDER #5 | Minas | PGT South | Fair | Planned Maintenance | 0 | 09:00 Manuall Open LBS 8D-247 D/S 8C fdr #5. TOL Road project. Cause: Project. | 1
11 | 2020-05-18 07:31 | May | 7:31 | Morning | Monday | Weekdays | 18 | 2020 | 2020-04-03 09:05 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 34 | 09:05 Manuall Open LBS 7D-117 D/S Minas fdr #3. TOL Road project. Cause: Project. | 1
12 | 2020-05-18 07:31 | May | 7:31 | Morning | Monday | Weekdays | 18 | 2020 | 2020-04-03 12:36 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Fair | Powerline - Conductor | 22 | 12:36 It was reported broken contactor at well 3A-65. 13:45 Checked & found @2 broken contactor ground 3A-12. 14:06 Open LBS 3A-22 (9well off during repair broken conductor). 18:40 Closed LBS 3A-22. Cause: Conductor. | 1
13 | 2020-05-18 10:00 | May | 10:00 | Morning | Monday | Weekdays | 18 | 2020 | 2020-04-03 15:48 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 143 | 15:48 C.Duri feeder #1 load dropped 59A (172-113A). It was reported no Power at Puncak GS. 17:45 Checked and found Recl. 38-AF-09 T/SO ctr:336-336. Patrolled the line but found nothing. 18:35 Blocked & Closed Recl. 38AS09, then release the block. Cause: Unidentified. | 1
14 | 2020-05-18 10:39 | May | 10:39 | Morning | Monday | Weekdays | 18 | 2020 | 2020-05-03 02:18 | 13.8KV MINAS FEEDER #2 | Minas | PGT South | Fair | Lightning | 63 | 02:18 Minas ACB fdr#2 T/LO, Ctr: 82-84, R/F: 50 @123, 51N Minas Fdr#1 Load dropped 166A (166-0A) Minas Fdr#3 Load dropped 182A (250-68) Minas Fdr#4 Load dropped 137A (172-35A) Minas Fdr#6 Load dropped 71A (121-50A) 07:30 Patrolled the line (Minas fdr #2) but found nothing Cause: Unidentified | 1
| 2020-05-18 14:46 | May | 14:46 | Afternoon | Monday | Weekdays | 18 | 2020 | 2020-05-03 07:30 | 13.8KV MINAS FEEDER #2 | Minas | PGT South | Fair | Lightning | 63 | Checked and found: MNSSG-13.8ACB13 T/LO, Counter : 82 - 84, Relay Flag : 51N. Patrolled the line found : None Cause : Lightning | 1
15 | 2020-05-18 16:07 | May | 16:07 | Afternoon | Monday | Weekdays | 18 | 2020 | 2020-05-03 06:13 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 69 | 6DN fdr#2 Load dropped 184A (254-70A). Not checked yet. | 1
| 2020-05-19 06:02 | May | 6:02 | Morning | Tuesday | Weekdays | 19 | 2020 | 13-03-2020 17:31 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 69 | Checked and found 6DN OCB feeder #2 T/R 1x. Counter: 21-22 R/F: 51N. Patrolled the line found nothing. Cause: Suspect Lightning. | 1
16 | 2020-05-20 01:22 | May | 1:22 | Night | Wednesday | Weekdays | 20 | 2020 | 2020-05-03 06:15 | 13.8KV 4D FEEDER #5 | Minas | PGT South | Rain and Lightning | Lightning | 0 | 4D fdr#5 T/R 1x. Not checked yet. | 1
| 2020-05-20 01:22 | May | 1:22 | Night | Wednesday | Weekdays | 20 | 2020 | 2020-09-03 16:29 | 13.8KV 4D FEEDER #5 | Minas | PGT South | Rain and Lightning | Lightning | 0 | Checked and found: 4DSB-13.8OCB5 T/R, Counter : 378 - 379, Relay Flag : 51 Patrolled the line found : Not found Cause : Lightning | 1
17 | 2020-05-20 05:59 | May | 5:59 | Morning | Wednesday | Weekdays | 20 | 2020 | 2020-05-03 08:14 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Cloudy | Under investigation | 0 | 08:14 DCM VCB fdr #2 T/SO (1x operate) 08:16 Checked and found DCM VCB fdr #2 operated 2x, ctr: 115 - 117, R/F: 51N Patrolled the line and found fault at U/G cable for TX of Bowling Alley Isolate the cable and 150 kVA TX-8 for Bowling Alley 09:19 Blocked and manual close DCM VCB fdr #2, OK then release the block. Cause: Under Investigation | 1
18 | 2020-05-20 10:35 | May | 10:35 | Morning | Wednesday | Weekdays | 20 | 2020 | 2020-05-03 08:14 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Lightning | 0 | DCM feeder #1 T/R 1x Not Checked Yet | 1
| 2020-05-20 10:39 | May | 10:39 | Morning | Wednesday | Weekdays | 20 | 2020 | 2020-06-03 09:01 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Lightning | 0 | Checked and found DCM fdr #1 T/R 1x, ctr: 152 - 153, R/F: 51N Patrolled the line and found died animal (squirrel) o/p KT-54 Cause : Animal | 1
19 | 2020-05-20 10:40 | May | 10:40 | Morning | Wednesday | Weekdays | 20 | 2020 | 2020-05-03 10:10 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 52 | Nella feeder #1 load dropped 110A (202-92A). Not checked yet. | 1
20 | 2020-05-20 18:41 | May | 18:41 | Afternoon | Wednesday | Weekdays | 20 | 2020 | 2020-05-03 10:41 | 13.8KV PUNGUT FEEDER #1 | Bekasap | PGT North | Fair | Planned Maintenance | 26 | 10:41 Manual Open RCL 45-BP-09 (PGT fdr #1), closed at 12:06 MTCE team to c/o TX and LA at PGT #01 Caused: Planned Maintenance | 1
21 | 2020-05-20 18:41 | May | 18:41 | Afternoon | Wednesday | Weekdays | 20 | 2020 | 2020-05-03 12:53 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Cloudy | Lightning | 74 | Minas ACB #2 feeder #3 T/O. Not checked yet. | 1
| 2020-05-21 06:26 | May | 6:26 | Morning | Thursday | Weekdays | 21 | 2020 | 2020-10-03 08:27 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Cloudy | Lightning | 74 | Checked and found: MNSSG-13.8ACB02 T/O, Counter : 8168 - 8169, Relay Flag : 51N. Patrolled the line found : Not found Cause : Lightning | 1
22 | 2020-05-21 06:26 | May | 6:26 | Morning | Thursday | Weekdays | 21 | 2020 | 2020-05-03 18:20 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Rain and Lightning | Unidentified | 235 | 18:20 PMT fdr #1 T/R 1x PMT fdr #2 load dropped 52 A (111 - 59 A) 19:00 It was reported Unbalance Votage at Tx-A Pematang GS. 19:30 Manually Opened Rangau fdr#2, then Closed at 21:08. 20:46 Manually Opened Pematang fdr#2, then closed at 21:28. 20:58 Checked & found Recl. Tx-A at Pematang T/O. 21:00 Blocked & closed Recl. Tx-A at Pematang. Not Checked Yet | 1
| 2020-05-21 07:41 | May | 7:41 | Morning | Thursday | Weekdays | 21 | 2020 | 2020-09-03 09:01 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Rain and Lightning | Unidentified | 235 | Checked and found PMT OCB fdr #1 T/R 1x, Ctr: 188 - 189, R/F: 51N Date Patrol : 06-MAR-2020 Patrolled the line but found nothing Cause : Unidentified | 1
23 | 2020-05-21 22:26 | May | 22:26 | Night | Thursday | Weekdays | 21 | 2020 | 2020-05-03 18:29 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Cloudy | Normal Condition | 40 | 18:29 Batang fdr #3 load droope 46 A (69 - 23 A) Batang GFPC T/R 2x Not Checked Yet 18:37 Batang fdr #3 T/R 2x Batang GFPC T/R 3x Not Checked Yet | 1
| 2020-05-21 22:26 | May | 22:26 | Night | Thursday | Weekdays | 21 | 2020 | 2020-09-03 09:05 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Cloudy | Normal Condition | 40 | Checked and found: 5441-R.36-AL-13 None, Counter : 170 - 170, Relay Flag : NONE. Patrolled the line found : No Findings Cause : Normal Condition | 1
24 | 2020-05-22 06:13 | May | 6:13 | Morning | Friday | Weekdays | 22 | 2020 | 2020-06-03 03:51 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | 251 | 03:51 So. Balam VCB fdr#4 T/R 1x. So. Balam GFPC T/R 1x. 10:33 So Balam fdr #4 T/R 1x Not checked yet. | 1
25 | 2020-05-22 06:13 | May | 6:13 | Morning | Friday | Weekdays | 22 | 2020 | 2020-06-03 07:55 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Animal | 0 | 07:55 Duri Community VCB fdr #1 T/R 1x 09:01 Checked and found DCM VCB fdr #1 T/R 1x, ctr: 153 - 154, R/F: 51N Patrolled the line and found dead animal (squirrel) o/p KT-54 Cause: Animal | 1
| 2020-05-22 06:14 | May | 6:14 | Morning | Friday | Weekdays | 22 | 2020 | 2020-06-03 09:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Animal | 0 | Checked and found: DCSG-13.8ACB25 T/R, Counter : 152 - 154, Relay Flag : 51N. Patrolled the line found : Tupai mati Cause : Animal | 1
26 | 2020-05-22 06:14 | May | 6:14 | Morning | Friday | Weekdays | 22 | 2020 | 2020-06-03 11:40 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 0 | 11:40 Manual Open RCL 5B-93 (4B fdr #2) MTCE team to change out TX at loc 5B-12 Caused: Planned Maintenance | 1
27 | 2020-05-22 06:14 | May | 6:14 | Morning | Friday | Weekdays | 22 | 2020 | 2020-06-03 16:43 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Animal | 30 | Ketigul VCB fdr #2 T/R 1x Not Checked Yet | 1
| 2020-05-22 06:14 | May | 6:14 | Morning | Friday | Weekdays | 22 | 2020 | 2020-10-03 16:40 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Animal | 30 | Checked and found KTGL fdr #2 T/R 1x, ctr: 376 - 377, R/F: 51N Patrolled the line and found: - Died animal (monkey) at PGT #30 - Broken LA at @3 on pole 29-AM-02 Caused: Animal | 1
28 | 2020-05-22 06:54 | May | 6:54 | Morning | Friday | Weekdays | 22 | 2020 | 2020-07-03 06:28 | 13.8KV DARLING VCB FEEDER #4 | Duri | PGT North | Fair | Unidentified | 114 | Darling VCB fdr#4 T/R 1x. Not checked yet. | 1
| 2020-05-22 11:09 | May | 11:09 | Morning | Friday | Weekdays | 22 | 2020 | 2020-10-03 16:44 | 13.8KV DARLING VCB FEEDER #4 | Duri | PGT North | Fair | Unidentified | 114 | Checked and found Darling fdr #4 T/R 1x, ctr: 149 - 150, R/F: 51P @1 Patrolled the line but found nothing Cause : Unidentified | 1
29 | 2020-05-22 15:13 | May | 15:13 | Afternoon | Friday | Weekdays | 22 | 2020 | 2020-07-03 09:17 | IT MINI SUBSTATION | Duri | PGT North | Fair | Planned Maintenance | 0 | 09:17 Manual Open 4.16 kV RCL of Mini IT Substation MTCE team to execute high trees at Duri Camp Cause: Planned Maintenance | 1
30 | 2020-05-22 15:13 | May | 15:13 | Afternoon | Friday | Weekdays | 22 | 2020 | 2020-07-03 10:11 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 422 | 10:11 Manual Open VCB Nella fdr #1, closed at 12:09 MTCE team to change out broken dead end o/p 21-U-47 at @1 @3 and change out broken pin support at @2 o/p 20-T-17. Cause: Planned Maintenance | 1
31 | 2020-05-23 09:05 | May | 9:05 | Morning | Saturday | Weekends | 23 | 2020 | 2020-07-03 11:04 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Dead End Insulator | 0 | Duri Field feeder #2 T/R 1x Not Checked Yet | 1
| 2020-05-23 14:54 | May | 14:54 | Afternoon | Saturday | Weekends | 23 | 2020 | 2020-12-03 08:40 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Dead End Insulator | 0 | Checked and found: DFSG ACB-42 T/R 1x, Ctr : 1033 - 1034, R/F : 50. Patrolled the line and found broken dead end @2 o/p 07-V3-23 Cause : Dead End Insulator | 1
32 | 2020-05-23 15:48 | May | 15:48 | Afternoon | Saturday | Weekends | 23 | 2020 | 2020-07-03 15:42 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Cloudy | Others | 8 | 3D VCB fdr #2 T/R 1x Not Checked Yet | 1
| 2020-05-24 15:51 | May | 15:51 | Afternoon | Sunday | Weekends | 24 | 2020 | 2020-10-03 13:18 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Cloudy | Others | 8 | Checked and found 3D OCB fdr #2 T/R 1x, Ctr : 369 - 370, R/F : 50P @2 Patrolled the line but found nothing Cause : Others | 1
33 | 2020-05-24 15:51 | May | 15:51 | Afternoon | Sunday | Weekends | 24 | 2020 | 2020-08-03 06:35 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | 0 | C.Duri fdr#1 Load dropped 77A (173-96A). Not checked yet. | 1
| 2020-05-25 06:09 | May | 6:09 | Morning | Monday | Weekdays | 25 | 2020 | 2020-10-03 16:47 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | 0 | Checked and found RCl 41-AW-62 T/R 1x, ctr: 333 - 334, R/F: None Patrolled the line and found broken conductor at @1 o/p 40-AU-07 Cause : Unidentified (suspect conductor) | 1
34 | 2020-05-25 06:09 | May | 6:09 | Morning | Monday | Weekdays | 25 | 2020 | 2020-09-03 13:32 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 0 | ND VCB fdr #2 T/R 1x Not Checked Yet | 1
| 2020-05-25 14:44 | May | 14:44 | Afternoon | Monday | Weekdays | 25 | 2020 | 13-03-2020 14:27 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found: ND VCB fdr #2 T/R 1x, Ctr : 287 - 288, R/F : 51P Patrolled the line but found nothing Cause : Unidentified | 1
35 | 2020-05-25 14:44 | May | 14:44 | Afternoon | Monday | Weekdays | 25 | 2020 | 2020-10-03 11:43 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Fair | Planned Maintenance | 58 | 11:43 Manual Open RCL 7D-150 (MNS fdr #4), closed at 12:31 MTCE team to install TX at 8D-11 (reactive well) Planned Maintenance | 1
36 | 2020-05-25 14:50 | May | 14:50 | Afternoon | Monday | Weekdays | 25 | 2020 | 2020-11-03 00:55 | 13.8KV 4B FEEDER #5 | Minas | PGT South | Rain and Lightning | Lightning | 0 | 4B VCB fdr#5 T/R 1x Not checked yet | 1
| 2020-05-25 14:50 | May | 14:50 | Afternoon | Monday | Weekdays | 25 | 2020 | 13-03-2020 14:01 | 13.8KV 4B FEEDER #5 | Minas | PGT South | Rain and Lightning | Lightning | 0 | Date Checked and found: 4B OCB fdr #5 T/R 1x, Ctr : 175 - 176, R/F : 51N. Patrolled the line but found nothing Cause : Lightning | 1
37 | 2020-05-25 18:46 | May | 18:46 | Afternoon | Monday | Weekdays | 25 | 2020 | 2020-11-03 01:03 | 13.8KV 6D FEEDER #4 | Minas | PGT South | Rain and Lightning | Pin Insulator | 4 | 01:03 6D OCB fdr#4 T/O (WIP) 6D fdr#1 Load dropped 58A (167-109A) 6D fdr#2 Load dropped 79A (176-97A) 6D fdr#5 Load dropped 56A (73-17A) 6D fdr#6 Load dropped 125A (186-61A) (WIP) 01:20 Block & Closed 6D OCB fdr#4 (Requested by TDO South) Cause: Not checked yet | 1
| 2020-05-25 18:46 | May | 18:46 | Afternoon | Monday | Weekdays | 25 | 2020 | 13-03-2020 13:56 | 13.8KV 6D FEEDER #4 | Minas | PGT South | Rain and Lightning | Pin Insulator | 4 | Checked and found: 6D OCB fdr #4 T/LO, Counter : 575 - 576, R/F : 50P @2 Patrolled the line and found broken pin insulator @2 o/p 5C-122 Cause : Pin Insulator | 1
38 | 2020-05-25 19:05 | May | 19:05 | Night | Monday | Weekdays | 25 | 2020 | 2020-11-03 01:31 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Rain and Lightning | Pin Insulator | 287 | 01:31 6DN fdr#1 Load dropped 11A (235-124A) 16:00 It was reported no power D/S Rec 5E-05 D/S 6DN#1 17:14 Checked and found Recloser 5E-05 T/LO, counter 285-294 patrolled powerline found broken dead end o/p 5E-29 @3, 5E-32 @3, and palm trees o/p 4E-94E, 17:58 Manually blocked and closed recloser 5E-05--> ok caused by broken dead end. | 1
| 2020-05-25 19:05 | May | 19:05 | Night | Monday | Weekdays | 25 | 2020 | 13-03-2020 08:18 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Rain and Lightning | Pin Insulator | 287 | Checked and found: 5442-R.5E05 T/LO, Counter : 285 - 294, Relay Flag : 50P @3 Patrolled the line and found broken pin insulator @3 o/p 5D-35 Cause : Pin Insulator | 1
39 | 2020-05-26 10:28 | May | 10:28 | Morning | Tuesday | Weekdays | 26 | 2020 | 2020-11-03 01:49 | 13.8KV 6DN FEEDER #6 | Minas | PGT South | Rain and Lightning | Unidentified | 77 | 6DN OCB fdr#6 T/R 1x Not checked yet | 1
| 2020-05-26 10:45 | May | 10:45 | Morning | Tuesday | Weekdays | 26 | 2020 | 13-03-2020 13:39 | 13.8KV 6DN FEEDER #6 | Minas | PGT South | Rain and Lightning | Unidentified | 77 | Checked and found: 6DN OCB fdr #6 T/R 3x, Counter : 196 - 199, R/F : 51P Patrolled the line but found nothing Cause : Unidentified | 1
40 | 2020-05-26 15:34 | May | 15:34 | Afternoon | Tuesday | Weekdays | 26 | 2020 | 2020-11-03 03:17 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | 0 | Bangko Fdr#4 Load dropped 42A (174-132A) not checked yet | 1
| 2020-05-26 15:34 | May | 15:34 | Afternoon | Tuesday | Weekdays | 26 | 2020 | 15-03-2020 10:19 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | 0 | Checked And Found Patrolled The Line On 15-Mar-2020 But Found Nothing Cause: Unidentified | 1
41 | 2020-05-26 18:29 | May | 18:29 | Afternoon | Tuesday | Weekdays | 26 | 2020 | 2020-11-03 06:20 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 0 | CD ACB fdr#16 T/R 1x, Ctr: 369-370, R/F: 51 @1,2 & 51N Not checked yet | 1
| 2020-05-26 18:57 | May | 18:57 | Afternoon | Tuesday | Weekdays | 26 | 2020 | 13-03-2020 14:34 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found: CD ACB-28 fdr #16 T/R 1x, Ctr : 369 - 370, R/F : 51N. Patrolled the line but found nothing Cause : Unidentified | 1
42 | 2020-05-26 18:57 | May | 18:57 | Afternoon | Tuesday | Weekdays | 26 | 2020 | 2020-11-03 15:34 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning Arrester | 53 | 15:34 3D OCB feeder #2 T/O (in blocked position , RIG ACS #15 at well 3D-49) 15:52 Checked and found 3D OCB feeder #2 T/O. Counter: 370-371 R/F: 51@3. Patrolled the line found @1 and @3 broken Lightning Arrester , on pole 3E-34. 17:00 Blocked and closed 3D OCB feeder #2 --> OK. and then still in blocked position (RIG ACS #15) Cause: Broken Lightning Arrester. | 1
43 | 2020-05-26 19:14 | May | 19:14 | Night | Tuesday | Weekdays | 26 | 2020 | 2020-12-03 06:12 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Pin Insulator | 0 | 06:12 DF VCB fdr #4 T/O (on block for RIG APS #3519 at 6R-83A) 06:16 Got communication with Rig APS #3519 Clerk (Mr. Andi) and conformed no incident at Rig Location (on rig down progress) 06:20 Call TDO Crew (night shift crew) to manual close the VCB DF fdr #4 06:22 Manual Close VCB DF fdr #4 (still on block), OK and then release the block Cause: Not Checked Yet | 1
| 2020-05-26 19:14 | May | 19:14 | Night | Tuesday | Weekdays | 26 | 2020 | 13-03-2020 14:40 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Pin Insulator | 0 | Check and found: DFSG ACB-51 T/O, Counter : 577 - 578, Relay Flag : 51P Patrolled the line and found broken pin insulator @ 2 o/p 06-S1-13 Cause : Pin Insulator | 1
44 | 2020-05-27 05:57 | May | 5:57 | Morning | Wednesday | Weekdays | 27 | 2020 | 2020-12-03 06:46 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Lightning Arrester | 739 | 06:46 South Balam fdr #4 T/R 1x. 07:19 South Balam fdr #4 T/R 1x. 07:53 South Balam fdr #4 T/R 1x. Not Checked Yet. | 1
| 2020-05-27 05:57 | May | 5:57 | Morning | Wednesday | Weekdays | 27 | 2020 | 2020-12-03 16:30 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Lightning Arrester | 739 | Checked and found: SBLM-13.8VCB4 T/R, Counter : 376 - 378, Relay Flag : 51N Patrolled the line found @1 Broken Pin Support Insulator. Cause : Broken Pin Insulator. | 1
| 2020-05-27 10:00 | May | 10:00 | Morning | Wednesday | Weekdays | 27 | 2020 | 13-03-2020 00:35 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Lightning Arrester | 739 | 00:35 South BALAM fdr #4 T/R 1x, GFPC on block for RIG GBT #06 @ BLM #203 03:55 South BALAM feeder #4 T/R again 1x 04:29 South BALAM feeder #4 T/R again 1x 05:00 South BALAM feeder #4 T/R again 1x 05:30 T/R again 1x 06:11 Call TDO Crew to check the problem. 07:30 Checked and found So Balam VCB feeder #4 T/R 1x. Counter: 378-379 R/F: 51@1. 08:09 Patrolled the line found @1 broken Lightning Arrester and , @1 broken Pin Insulator on Terminal pole Balam #56 09:04 So Balam VCB feeder #4 T/R 1x again. 09:17 Blocked So Balam VCB feeder #4. Due to Open and close Hot line Clamp on Terminal pole Balam #56 and replacing broken Lightning Arrester and broken Pin Insulator. 10:05 Re normalized blocked So Balam VCB feeder #4. Cause: Broken Lightning Arrester. | 1
45 | 2020-05-27 11:27 | May | 11:27 | Morning | Wednesday | Weekdays | 27 | 2020 | 2020-12-03 11:08 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Planned Maintenance | 0 | 10:42 Transfer part load N Duri feeder #2 to N Duri feeder #11. (298-53A). 11:08 Manually open N Duri feeder #2 due to repair hot spot on pole NC-03. 12:00 Manually blocked and closed N Duri feeder #2 --> OK and then released the block. 12:17 Normalized load N Duri feeder #2 from N Duri feeder #11. Cause: Planned maintenance. | 1
46 | 2020-05-27 11:27 | May | 11:27 | Morning | Wednesday | Weekdays | 27 | 2020 | 16-03-2020 07:46 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Lightning | Unidentified | 40 | Checked and found: BTG VCB fdr #3 T/R 1x, Ctr: 392 - 393, R/F : 50 Patrolled the line but found nothing Cause : Unidentified | 1
47 | 2020-05-27 14:03 | May | 14:03 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-12-03 13:46 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Dead End Insulator | 26 | C Duri feeder #1 load dropped 50A (170-120A). Not checked yet. | 1
| 2020-05-27 16:33 | May | 16:33 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 16-03-2020 07:46 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Dead End Insulator | 26 | Checked and found: 5441-R.41-AW-62 T/R, Counter : 334 - 335, Relay Flag : NONE. Patrolled the line found : Dead end sompel di layer 2 dan 3 Cause : Dead End Insulator | 1
48 | 2020-05-27 16:33 | May | 16:33 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-12-03 14:38 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain and Lightning | Dead End Insulator | 114 | Bekasap ACB feeder #3 T/R 1x. Not checked yet. | 1
| 2020-05-27 17:02 | May | 17:02 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 16-03-2020 14:20 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain and Lightning | Dead End Insulator | 114 | Checked and found: BKS fdr #3 T/R 1x, Ctr: 99591 - 99592, R/F: 51P @1 Patrolled the line and found - flash over Dead end @1 o/p 37-BE-12 - broken LA @2 at PMT Bow #14 Cause : Dead End Insulator | 1
49 | 2020-05-27 17:02 | May | 17:02 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-12-03 14:39 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Cloudy | Tree | 150 | 14:39 PUNGUT OCB feeder #2 T/O. PUNGUT feeder #1 load dropped 29A (68-39AA). 16:19 Checked and found Pungut OCB feeder #2 T/LO . Counter: 334-337 R/F: 51N. Patrolled the line found fallen tree touches the powerline and @1,@2 broken Fuse Cut Out at well Piala #02. 17:55 Manually blocked and closed Pungut OCB feeder #2, and then released the block. Cause: Tree. | 1
50 | 2020-05-27 17:03 | May | 17:03 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-12-03 15:42 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 28 | Ketigul feeder #1 T/R 1x Not Checked Yet | 1
| 2020-05-27 17:03 | May | 17:03 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 16-03-2020 14:22 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 28 | Checked and found: KTGL fdr #1 T/R, 1x Counter: 228 - 229, R/F : 51N. Patrolled the line but found nothing Cause : Unidentified | 1
51 | 2020-05-27 17:45 | May | 17:45 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-03-13 05:32 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Heavy Rain | Unidentified | 445 | 05:32 Menggala feeder #2 dropped 68 A (156 / 88 A) Menggala feeder #1 dripped (6 A (173 / 167 A) Menggala GFPC T/R 1x Not Checked Yet | 1
| 2020-05-27 18:48 | May | 18:48 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-03-16 08:46 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Heavy Rain | Unidentified | 445 | Checked and found: 13.8KVMGL_GFPC T/R, Counter : 135 / 136, Relay Flag : 51N Patrolled the line found : Broken dead end 25% layer 1 Cause : Unidentified | 1
52 | 2020-05-27 18:48 | May | 18:48 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-03-13 18:28 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Unidentified | 22 | 18:28 Ketigul VCB feeder #2 T/R x. 20:00 Ketigul VCB fdr #2 T/R again 1x Not checked yet. | 1
| 2020-05-28 07:31 | May | 7:31 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-03-18 16:53 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Unidentified | 22 | Checked and found: PKTGL/13.8VCB2 T/R, Counter : 377 / 379, Relay Flag : 51N. Patrolled the line found : No Findings Cause : Unidentified | 1
53 | 2020-05-28 10:09 | May | 10:09 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-03-14 05:00 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | 233 | 05:00 South BALAM fdr #4 T/R 1x 08:17 South BALAM fdr #4 T/R 1x Checked and found So Balam VCB feeder #4 T/R 1x. Counter: 380/382 R/F: 51@1. Cause : Not Patrolled Yet | 1
| 2020-05-28 10:25 | May | 10:25 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-03-15 10:23 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | 233 | Checked And Found SBLM VCB4 Fdr #4 T/R 2x, Ctr 380/382, R/F 50N Patrolled The Line On 14/Mar/2020 But Found Nothing Cause: Unidentified | 1
54 | 2020-05-28 10:47 | May | 10:47 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-03-14 06:52 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Fair | Unidentified | 337 | 06:52 CKBS VCB fdr #5 T/R 1x 10:57 Check and found CKBS VCB fdr #5 T/R 1x. R/F 51N, counter : 177/178 Checked Recloser D/S CKBS VCB fdr #5 Normal. Cause : Unidentified | 1
55 | 2020-05-28 10:58 | May | 10:58 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-03-14 09:20 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 14 | 09:20 Manually open Recl. 2F/11 D/S 3D#2 Due to PT. BKP Team cut high trees. 15:44 Manually blocked and closed Recl. 2F/11 //> OK. And then released the block. Cause : Planned Maintenance | 1
56 | 2020-05-28 10:58 | May | 10:58 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-03-15 09:30 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Fair | Planned Maintenance | 4 | 09:30 Open fuse for pole sleeveing on pole 06/R1/16 and 17. 3 wells OFF during this job (wells 7Q/75A , 76A , 15A). Close fuse for energized weels above. Cause: Planned maintenance. | 1
57 | 2020-05-28 11:15 | May | 11:15 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-03-15 14:41 | 115KV CENTRAL DURI / BATANG LINE | Duri | PGT North | Cloudy | Suspension Insulator | 39 | 14:41 115 kV Line CD / STG Tripped. / CD OCB #31 T/R 1x, / CD OCB #33 T/R 1x / STG GCB #25 T/O, manual closed at 14:44, OK. Respectively load dropped at any feeders. *BATANG (No power at Batang Substation). /Batang feeder #1 /Batang feeder #2 /Batang feeder #3 *SINTONG. /Sintong feeder #1 load dropped 31A (91/60A). /Sintong feeder #2 load dropped 25A (186/161A). *MENGGALA. /Menggala feeder #1 load dropped 32A (174/142A). /Menggala feeder #2 load dropped 20A (161/141A). *BANGKO. /Bangko feeder #1 load dropped 36A (147/101A). /Bangko feeder #2 load dropped 33A (244/211A). /Bangko feeder #3 load dropped 7A (206/199A). /Bangko feeder #4 load dropped 18A (173/155A). *NELLA. /Nella feeder #1 load dropped 34A (206/172A). /Nella feeder #2 load dropped 14A (75/61A). *BALAM. /Balam feeder #1 load dropped 34A (150/116A). /Balam feeder #4 load dropped 37A (217/180A). *PINANG. /Pinang feeder #1 load dropped 18A (105/87A). Cause : Not Checked Yet | 1
| 2020-05-29 01:13 | May | 1:13 | Night | Friday | Weekdays | 29 | 2020 | 2020-03-18 17:06 | 115KV CENTRAL DURI / BATANG LINE | Duri | PGT North | Cloudy | Suspension Insulator | 39 | Checked and found: GCB/31 T/R, Counter : 64 / 65, Relay Flag : 50N. Patrolled the line found : Suspension broken Phase : 1 Pole : BTG/89 Date Patrol : 17/MAR/2020 Operated Device : GCB/33 T/R Counter : 666 / 667 Relay Flag : 21 Finding Patrol : Suspension broken Phase : 1 Pole : BTG/89 Cause : Suspension Insulator | 1
58 | 2020-05-29 06:03 | May | 6:03 | Morning | Friday | Weekdays | 29 | 2020 | 2020-03-15 16:46 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Lightning | Secondary Cable | 0 | 16:46 Duri Commy ACB#30 feeder #2 T/O. 17:16 Checked & found Duri Commy ACB #30 (feeder #2) T/LO. Counter: 111/179 R/F : 51N. Patrolled the line found spark on primary Cable of Tx #8 at Bowling. 17:28 Manually blocked & Closed Duri Commy ACB #30 (feeder #2)//>OK. and then released the block. Cause: Primary Cable. | 1
59 | 2020-05-29 11:30 | May | 11:30 | Morning | Friday | Weekdays | 29 | 2020 | 2020-03-15 21:35 | 115KV MINAS / 8D LINE | Minas | PGT South | Rain and Lightning | Under investigation | 148 | 21:35 Appeared Alarm "System High Frequency" (60.90Hz) 21:36 Minas GT RTU failed for 11 second MGT#3 tripped Off. Manually open NDC CT #1 Gen. Breaker due to Over Freq. (60.90 Hz) / 6DN fdr #1 load dropped 126 A (207 / 82 A) / 6DN fdr #2 load dropped 101 A (243 / 142 A) / 6DN fdr #4 load dropped 215 A (220 / 5 A) / 6DN fdr #5 load dropped 16 A (38 / 22 A) / 6DN fdr #6 load dropped 40 A (191 / 151 A) / 4D fdr #2 load dropped 60 A (143 / 83 A) / 4D fdr #3 load dropped 11 A (74 / 63 A) / 3D fdr #3 load dropped 32 A (74 / 42 A) / 3D fdr #5 load dropped 14 A (125 / 111 A) / 3D fdr #7 load dropped 79 A (122 / 43 A) / 3D fdr #8 load dropped 104 A (210 / 106 A) / 8D fdr #1 load dropped 135 A (135 / 0 A) / 8D fdr #2 load dropped 109 A (109 / 0 A) / 8D fdr #3 load dropped 91 A (91 / 0 A) / 8D fdr #5 load dropped 164 A (164 / 0 A) / 8D fdr #6 load dropped 337 A (337 / 0 A) / 8D fdr #7 load dropped 197 A (197 / 0 A) / 8D fdr #8 load dropped 186 A (186 / 0 A) / 8D fdr #9 load dropped 111 A (111 / 0 A) / 8D fdr #10 load dropped 116 A (116 / 0 A) / 8D fdr #11 load dropped 144 A (144 / 0 A) / 8C fdr #1 load dropped 69 A (173 / 104 A) / 8C fdr #2 load dropped 20 A (70 / 50 A) / 8C fdr #3 load dropped 92 A (200 / 108 A) //> WIP GS #1 / 8C fdr #4 load dropped 142 A (232 / 90 A) //> WIP GS #2 / 8C fdr #6 load dropped 118 A (207 / 89 A) / MINAS fdr #1 load dropped 27 A (170 / 143 A) / MINAS fdr #2 load dropped 43 A (113 / 70 A) / MINAS fdr #3 load dropped 33 A (144 / 111 A) / MINAS fdr #4 load dropped 65 A (170 / 105 A) / MINAS fdr #6 load dropped 25 A (118 / 93 A) / 4B fdr #1 load dropped 105 A (200 / 95 A) / 4B fdr #2 load dropped 30 A (54 / 24 A) / 4B fdr #1 load dropped 10 A (41 / 31 A) / 5B fdr #2 load dropped 30 A (153 / 120 A) / 5B fdr #6 load dropped 121 A (123 / 2 A) / 5B fdr #8 load dropped 46 A (197 / 151 A) / 6D fdr #3 load dropped 41 A (86 / 45 A) / 6D fdr #6 load dropped 246 A (246 / 0 A) / 6D fdr #2 load dropped 33 A (153 / 120 A) / 6D fdr #4 load dropped 83 A (83 / 0 A) / 6D fdr #5 load dropped 91 A (91 / 0 A) / NKB fdr #2 load dropped 82 A (236 / 154 A) / NKB fdr #3 load dropped 10 A (88 / 78 A) / NKB fdr #3 load dropped 60 A (165 / 105 A) / NKB fdr #5 load dropped 120 A (153 / 32 A) / CKB fdr #1 load dropped 30 A (201 / 171 A) / CKB fdr #4 load dropped 99 A (261 / 62 A) / CKB fdr #5 load dropped 109 A (220 / 111 A) / CKB fdr #6 load dropped 60 A (194 / 134 A) / PTP fdr #1 load dropped 16 A (76 / 60 A) / PTP fdr #7 load dropped 10 A (72 / 62 A) / S. BLM fdr #1 load dropped 6 A (149 / 143 A) / S. BLM fdr #3 load dropped 10 A (136 / 126 A) / S. BLM fdr #4 load dropped 10 A (210 / 200 A) / NELLA fdr #1 load dropped 148 A (211 / 6 A) / NELLA fdr #2 load dropped 6 A (76 / 70 A) / BKO fdr #1 load dropped 115 A (147 / 32 A) / BKO fdr #2 load dropped 210 A (242 / 32 A) //> BKO GS / BKO fdr #3 load dropped 9 A (211 / 202 A) //> BKO GS / BKO fdr #4 load dropped 7 A (174 / 167 A) Load shedding level/1: 21:45 3D fdr #6 T/LO at freq 59.73 Hz, manual closed at 22:19 21:55 5B fdr #8 T/LO, checked by crew ctr: 43/44, R/F: 81, closed at 23:18 5B fdr #7 T/LO, checked by crew ctr: 49/50, R/F: 81, closed at 23:19 22:32 Manual Open 6D fdr #5 (Req by Azandi / GS #4), closed at 23:34 to maintain level tank at GS #4 | 1
| 2020-05-29 11:30 | May | 11:30 | Morning | Friday | Weekdays | 29 | 2020 | 2020-03-16 07:00 | 115KV MINAS / 8D LINE | Minas | PGT South | Rain and Lightning | Under investigation | 148 | Checked and found: 21:33:47 115 kV Minas 6DN L90 relay indicated that : 2 Phasa/Ground fault . Occurred 115 kV Minas/8D Trip, 115 kV GCB #83 MSY T/R 1x, counter: 418 / 419 115 kV GCB #85 MSY T/R 1x, counter: 204 / 205 21:34:02 Transformer 1,2,3 energize at 8D, based on relay L90 115 kV Minas/ 6DN and XHQ data. Cause: Under Investigation | 1
60 | 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-03-16 08:45 | 13.8KV S. BALAM FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 0 | 08:45 S. Balam VCB Feeder 2 T/R 1 x. 08:48 S. Balam VCB Feeder 2 T/R 1 x. 08:50 S. Balam VCB Feeder 2 T/R 1 x. Not checked yet. | 1
| 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-03-17 13:54 | 13.8KV S. BALAM FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 0 | Checked and found: SBLM VCB fdr #2 T/R 2x, Ctr: 118 / 120, R/F : 50N Patrolled the line but found nothing Cause : Unidentified | 1
61 | 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-03-16 10:05 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 10:05 CDGT #1 Trip by alarm Loss of Flame Trip. Status: Stand by. | 1
62 | 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-03-16 13:12 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 39 | 6D OCB feeder #2 T/R 1x. 6D feeder #3 load dropped 100A (114/14A) //> WIP 6DN feeder #4 load dropped 137A ( 223/86A) //> WIP Not checked yet. | 1
| 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-03-19 17:16 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 39 | Checked and found: 6DSB/13.8OCB2 T/R, Counter : 259 / 260, Relay Flag : 50 Patrolled the line found : Not Found Cause : Lightning | 1
63 | 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-03-16 15:05 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Cloudy | Recloser | 0 | 15:05 It was reported no power at DCSS Facility D/S CD feeder#14. 16:35 Checked and found Recloser 06/JY/02 T/O (Control Form 3). Counter : 850/851. 16:40 Manually closed Recloser 06/JY/02 but Failed. 18:37 Manually opened CD ACB #27 (feeder #14). Closed ByPass of Recloser 06/JY/02. 18:45 Manually blocked and closed CD ACB #27 (feeder #14) //> OK. Cause : Control Recloser. | 1
64 | 2020-05-31 02:51 | May | 2:51 | Night | Sunday | Weekends | 31 | 2020 | 2020-03-17 09:59 | 13.8KV BEKASAP FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | - | 09:59 Block Recloser 37/BD/12 D/S Bekasap feeder #2. Open fuse due to install secondary protector, 2 wells were off ( Bekasap #81 & #87 ). 11:30 Close fuse Bekasap #87. 15:30 Close fuse Bekasap #82. 15:39 Normalized Block Recloser 37/BD/12. Cause : Planned Maintenance | 1
65 | 2020-05-31 02:51 | May | 2:51 | Night | Sunday | Weekends | 31 | 2020 | 2020-03-17 14:25 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:25 S/U CDGT#1, then on line the unit at 14:48. | 1
66 | 2020-05-31 02:55 | May | 2:55 | Night | Sunday | Weekends | 31 | 2020 | 2020-03-18 08:15 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | Off line CGT#3, then S/D the unit for S/B. | 1
67 | 2020-05-31 02:55 | May | 2:55 | Night | Sunday | Weekends | 31 | 2020 | 2020-03-18 09:27 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 52 | 09:27 Manually Open Recl. 5E/05 (6DN fdr#1). Replaced Broken Dead End & Pin Insulator . (14 wells Off during the job). 12:44 Blocked & Closed Recl. 5E/05, then release the block. Cause: Planned Maintenance. | 1
68 | 2020-05-31 02:55 | May | 2:55 | Night | Sunday | Weekends | 31 | 2020 | 2020-03-19 09:50 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 09:50 S/U MGT#11, then on line the unit at 10:16. | 1
69 | 2020-05-31 02:55 | May | 2:55 | Night | Sunday | Weekends | 31 | 2020 | 2020-03-19 10:25 | MINAS POWER PLANT | Minas | PGT South |  |  | - | Off line MGT#9, then S/D the unit for S/B. | 1
70 | 2020-05-31 11:41 | May | 11:41 | Morning | Sunday | Weekends | 31 | 2020 | 2020-03-19 10:27 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Fair | Planned Maintenance | 59 | 10:27 Manually Opened LBS 06/R1/21 (C.Duri fdr#14). Repaired Corrosion Pole 06/R1/14 & 06/R1/16. 16:09 Closed LBS 06/R1/21. Cause: Planned Maintenance. | 1
71 | 2020-05-31 12:30 | May | 12:30 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-19 17:02 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 0 | 17:02 Manually Opened Minas fdr#1. Replaced @1 Broken HLC o/p M5B4. 17:21 Blocked & closed Minas fdr#1, then release the block. Cause: Planned Maintenance. | 1
72 | 2020-05-31 12:53 | May | 12:53 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-20 10:51 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Fair | Guy Wire | 226 | 10:51 It was reported no power 13 wells D/S 4B fdr#1. 11:30 Checked & found Recl. 4B/101 T/LO ctr:657/662. Patrolled the line & found Broken Guy Line o/p K4B/12. 16:50 Opened 115Kv Line KBJ/4B GCB#33, then closed at 17:13. 16:52 Opened 115Kv Line KBJ/4B GCB#35, then closed at 17:11. 16:50 Opened 115Kv Line 4B/KBJ GCB#33, then closed at 17:13. Isolated Broken Guy Line. 17:18 Blocked & Closed Recl. $b/101, then release the block. Cause: Broken Guy Line. | 1
73 | 2020-05-31 13:20 | May | 13:20 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-20 18:20 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified (Fuse) | 26 | C.Duri fdr#1 Load dropped 57A (171/114A). Not checked yet. | 1
| 2020-05-31 15:16 | May | 15:16 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-23 14:07 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified (Fuse) | 26 | Checked And Found 5441/R.39AV36 Fdr #1 T/R 2x, Ctr 300/302, Patrolled The Line On 22/Mar/2020 And Found Fuse Putus On Phase @2 Pole Kulin #90 Cause: Unidentified (Fuse) | 1
74 | 2020-05-31 16:33 | May | 16:33 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-20 23:31 | 13.8KV PETAPAHAN FEEDER #8 | Petko | PGT South | Rain and Lightning | Unidentified (Fuse) | 23 | 23:31 It was reported @1 burnt fuse of 300 Kva transformer. supply power for : / Shipping Pump , Lighting and control room at Petapahan GS. 01:36 Manually opened Petapahan VCB feeder #8. for replacing burnt out fuse above with same size. 01:38 Manually blocked and closed Petapahan VCB feeder #8 //> OK. and then released the block. Cause: Burnt out fuse. | 1
75 | 2020-05-31 16:41 | May | 16:41 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-21 07:06 | 44KV MINAS / RUMBAI LINE | Minas | PGT South | Lightning | Lightning | 0 | 44Kv Line MNS/RBI ACB#21 T/R 1x. Not checked yet. | 1
| 2020-05-31 16:46 | May | 16:46 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-27 13:01 | 44KV MINAS / RUMBAI LINE | Minas | PGT South | Lightning | Lightning | 0 | Checked and found: Minas ACB # 21 T/R, Counter : 92 / 93, Relay Flag : 51 Patrolled the line found: : None Phase : 1, 2, Cause : Lightning | 1
76 | 2020-05-31 17:24 | May | 17:24 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-21 07:24 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Animal | 31 | 07:24 Ketigul VCB fdr#2 T/R 1x. 08:25 Ketigul VCB fdr#2 T/R 1x again. 09:21 Ketigul VCB fdr#2 T/R 1x again. Not checked yet. | 1
| 2020-05-31 18:21 | May | 18:21 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-22 09:54 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Animal | 31 | Checked And Found PKTGL VCB2 Fdr #2 T/R 3x, Ctr 379/382, R/F 51N Patrolled The Line On 21/Mar/2020 And Found Animal On Pole Pagar # 30 Cause: Animal | 1
77 | 2020-05-31 18:21 | May | 18:21 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-21 12:05 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Lightning | 0 | N.Duri VCB fdr#1 T/R 1x. Not checked yet. | 1
| 2020-05-31 20:15 | May | 20:15 | Night | Sunday | Weekends | 31 | 2020 | 2020-03-26 17:21 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Lightning | 0 | Checked And Found NDRSB VCB1 Fdr #1 T/R 1x, Ctr 340/341, R/F 51N Patrolled The Line On 22/Mar/2020 And Found Broken L/A On Phase @1,2,3, Pole 12F22 And 12G213 Cause: Lightning | 1
78 | 2020-06-13 01:41 | June | 1:41 | Night | Saturday | Weekends | 13 | 2020 | 2020-03-22 06:55 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Fair | Unidentified | 0 | Darling VCB feeder #7 T/R 1x. Not checked yet. | 1
79 | 2020-06-13 08:43 | June | 8:43 | Morning | Saturday | Weekends | 13 | 2020 | 2020-03-22 10:16 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 25 | 10:16 Manually Opened LBS 3A/22 (4B fdr#1). Repaired Broken Guy Line o/p K4B/12. 13:18 Closed LBS 3A/22. Cause: Planned maintenance. Production Loss: 0. 14:24 Manually Opened LBS 3B/22 (4B fdr#1). Replaced @1@2@3 Broken Pin Insulator o/p 3B/26. 15:24 Closed LBS 3B/22. Cause: Planned Maintenance. Production Loss: 25 Bbls / 8 wells. | 1
80 | 2020-06-13 08:43 | June | 8:43 | Morning | Saturday | Weekends | 13 | 2020 | 2020-03-22 12:28 | 5 BRAVO SUBSTATION | Minas | PGT South | Rain and Lightning | Lightning | 236 | 12:28 115Kv 5B GCB#23 T/O. 115Kv 5B GCB#24 T/O. 12:40 Manually open 5B fdr#1, then closed at 13:50. Manually open 5B fdr#2, then closed at 13:51. Manually open 5B fdr#3, then closed at 13:51. Manually open 5B fdr#6, then closed at 13:48. 12:31 Manually Opened 6DN fdr#1, then Closed at 13:05. Manually opened 6D fdr#5, then closed at 13:23. 13:40 Checked 115Kv 5B Tx/1 Normal Condition, an R.F 51G. Checked 5B fdr#6 T/R Ctr:269/270 R/F 51N. Checked 115Kv GCB#23 T/O, then closed at 13:45. Checked 115Kv GCB#23 T/O, then closed at 13:47. Cause: Lightning. Production Loss : / 5B feeder #1 = GS #6 : 20 Bbls / 12 Wells GS #4 : 33 Bbls / 11 Wells / 5B feeder #2 = GS #4 :105 Bbls / 27 Wells / 5B feeder #3 = GS #4 : 22 Bbls / 6 Wells / 5B feeder #6 = GS #4 : 0 Bbls / 0 Wells / 6D feeder #5 = GS #4 : 33 Bbls / 11 Wells / 6DN feeder #1 = GS #4 : 26 Bbls / 13 Wells ///////////////////////////////////// + Grand Total : 239 Bbls / 80 Wells. | 1
| 2020-06-13 10:53 | June | 10:53 | Morning | Saturday | Weekends | 13 | 2020 | 2020-03-26 17:22 | 5 BRAVO SUBSTATION | Minas | PGT South | Rain and Lightning | Lightning | 236 | Checked And Found / 5BSB/115OCB23 T/R 1x, Ctr 176/177, R/F 51G / 5BSB/115OCB24 T/R 1x, Ctr 672/673, R/F 51G Patrolled The Line On 22/Mar/2020 But Found Nothing Cause: Lightning | 1
81 | 2020-06-14 05:29 | June | 5:29 | Morning | Sunday | Weekends | 14 | 2020 | 2020-03-22 12:30 | 13.8KV 8D FEEDER #10 | Minas | PGT South | Rain and Lightning | Lightning | 37 | 8D feeder #10 T/R 1x. Not checked yet. | 1
| 2020-06-14 05:29 | June | 5:29 | Morning | Sunday | Weekends | 14 | 2020 | 2020-03-24 07:24 | 13.8KV 8D FEEDER #10 | Minas | PGT South | Rain and Lightning | Lightning | 37 | Checked and found: 8DSB/13.8OCB10 T/R, Counter : 274 / 275, Relay Flag : 51. Patrolled the line found : Not found Phase : 1, 3, Cause : Lightning | 1
82 | 2020-06-14 11:15 | June | 11:15 | Morning | Sunday | Weekends | 14 | 2020 | 2020-03-22 14:22 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 134 | 14:22 Sintong feeder #2 load dropped 163A (224/61A). Sintong GFPC T/R. 15:28 Checked & found Recloser 28/AF/02 T/O Counter: 1551/1552 Patrolled the line but found nothing. 16:23 Blocked & closed Recloser 28/AF/02 the relisted the block. Cause: unidentified. | 1
| 2020-06-14 15:02 | June | 15:02 | Afternoon | Sunday | Weekends | 14 | 2020 | 2020-03-24 07:22 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 134 | Checked and found: 5440/R.28AF02 T/O, Counter : 1551 / 1552, Relay Flag : 51TN. Patrolled the line found : None Phase : 1, 2, 3, Cause : Unidentified | 1
83 | 2020-06-15 07:21 | June | 7:21 | Morning | Monday | Weekdays | 15 | 2020 | 2020-03-22 15:34 | 13.8KV NORTH DURI FEEDER #5 | Duri | PGT North | Fair | Lightning Arrester | 0 | N.Duri feeder #5 T/R 1x. Not checked yet. | 1
| 2020-06-15 07:21 | June | 7:21 | Morning | Monday | Weekdays | 15 | 2020 | 2020-03-24 09:54 | 13.8KV NORTH DURI FEEDER #5 | Duri | PGT North | Fair | Lightning Arrester | 0 | Checked and found: NDRSB/13.8VCB5 T/R, Counter : 159 / 159, Relay Flag : 51N. Patrolled the line found : LA pecah Phase : 3 Cause : Lightning Arrester | 1
84 | 2020-06-15 07:57 | June | 7:57 | Morning | Monday | Weekdays | 15 | 2020 | 2020-03-22 17:51 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 27 | Nella VCB fdr#2 T/R 1x. Nella GFPC T/R 1x. Not checked yet. | 1
85 | 2020-06-15 09:47 | June | 9:47 | Morning | Monday | Weekdays | 15 | 2020 | 2020-03-22 17:58 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 147 | 17:58 Nella VCB fdr#1 T/R 2x. Nella GFPC T/R 2x. 18:10 Nella VCB fdr#1 T/R 1x again. Nella GFPC T/R 1x again. Not checked yet. | 1
86 | 2020-06-15 09:47 | June | 9:47 | Morning | Monday | Weekdays | 15 | 2020 | 2020-03-22 23:51 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Rain and Lightning | Pin Insulator | 0 | 4B feeder #2 Load dropped 35A (53/18A). Not checked yet. | 1
| 2020-06-15 10:00 | June | 10:00 | Morning | Monday | Weekdays | 15 | 2020 | 2020-03-25 15:37 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Rain and Lightning | Pin Insulator | 0 | Checked and found RCL 5B/93 T/R 4x, Counter: 216 / 220, R/F: None Patrolled the line and found broken pin insulator @2 o/p 5B/41 Cause : Pin Insulator | 1
87 | 2020-06-15 12:04 | June | 12:04 | Afternoon | Monday | Weekdays | 15 | 2020 | 2020-03-22 23:53 | 13.8KV 4B FEEDER #6 | Minas | PGT South | Rain and Lightning | Others | 22 | 4B OCB feeder #6 T/R 1x. Not checked yet. | 1
| 2020-06-15 14:46 | June | 14:46 | Afternoon | Monday | Weekdays | 15 | 2020 | 2020-03-25 09:36 | 13.8KV 4B FEEDER #6 | Minas | PGT South | Rain and Lightning | Others | 22 | Checked and found 4B fdr #6 T/R 1x, Counter: 196 / 197, R/F: 51P Patrolled the line but found nothing Cause : Others | 1
88 | 2020-06-16 10:46 | June | 10:46 | Morning | Tuesday | Weekdays | 16 | 2020 | 2020-03-23 00:19 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 22 | 5B feeder #2 Load dropped 127A (153/26A). Not checked yet. | 1
| 2020-06-16 14:52 | June | 14:52 | Afternoon | Tuesday | Weekdays | 16 | 2020 | 2020-03-25 16:22 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 22 | Checked and found RCL 5C/07 T/R 1x, Counter: 196 / 197, R/F: None Patrolled the line but found nothing Cause : Lightning | 1
89 | 2020-06-16 15:43 | June | 15:43 | Afternoon | Tuesday | Weekdays | 16 | 2020 | 2020-03-23 00:40 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Rain and Lightning | Dead End Insulator | 25 | 5B OCB feeder #7 T/R 1x. Not checked yet. | 1
| 2020-06-16 15:43 | June | 15:43 | Afternoon | Tuesday | Weekdays | 16 | 2020 | 2020-03-24 14:21 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Rain and Lightning | Dead End Insulator | 25 | Checked and found: 5BSB/13.8OCB7 T/R,Counter : 498 / 498, Relay Flag : 51N. Patrolled the line found : Broken Dead end Insulator Ø1 Phase : 1 Cause : Dead End Insulator | 1
90 | 2020-06-16 19:37 | June | 19:37 | Night | Tuesday | Weekdays | 16 | 2020 | 2020-03-23 00:41 | 13.8KV 6D FEEDER #6 | Minas | PGT South | Rain and Lightning | Others | 0 | 6D feeder #6 load dropped 120A (178/58A). Not checked yet. | 1
| 2020-06-16 20:13 | June | 20:13 | Night | Tuesday | Weekdays | 16 | 2020 | 2020-03-26 17:13 | 13.8KV 6D FEEDER #6 | Minas | PGT South | Rain and Lightning | Others | 0 | Checked And Found 6DSB OCB6 Fdr #6 T/R 0x, Ctr 611/611, Patrolled The Line On 24/Mar/2020 But Found Nothing Cause: Others | 1
91 | 2020-06-17 06:08 | June | 6:08 | Morning | Wednesday | Weekdays | 17 | 2020 | 2020-03-23 00:43 | 13.8KV 6D FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 58 | 6D OCB feeder #4 T/R 1x. Not checked yet. | 1
| 2020-06-17 06:08 | June | 6:08 | Morning | Wednesday | Weekdays | 17 | 2020 | 2020-03-23 17:25 | 13.8KV 6D FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 58 | Checked and found: 6DSB/13.8OCB4 T/R, Counter : 576 / 577, Relay Flag : 51. Patrolled the line found : Flas over Dead end insulator Phase : 1 Cause : Lightning | 1
92 | 2020-06-17 09:55 | June | 9:55 | Morning | Wednesday | Weekdays | 17 | 2020 | 2020-03-23 01:15 | 13.8KV 6D FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | 9 | 6D feeder #1 load dropped 76A (172/96A). Not checked yet. | 1
| 2020-06-17 15:50 | June | 15:50 | Afternoon | Wednesday | Weekdays | 17 | 2020 | 2020-03-25 09:32 | 13.8KV 6D FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | 9 | Checked and found all protection equipment in Normal Condition. Patrolled the line d/s RCL 5C/42 (counter: 166) but found nothing. Cause : Lightning | 1
93 | 2020-06-17 15:50 | June | 15:50 | Afternoon | Wednesday | Weekdays | 17 | 2020 | 2020-03-23 01:15 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 18 | 6D feeder #2 load dropped 147A (172/25A). Not checked yet. | 1
| 2020-06-17 16:05 | June | 16:05 | Afternoon | Wednesday | Weekdays | 17 | 2020 | 2020-03-25 15:24 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 18 | Checked and found RCL 6D/298 T/R 1x, counter: 88 / 89, R/F: None Patrolled the line but found nothing Cause : Lightning | 1
94 | 2020-06-17 16:05 | June | 16:05 | Afternoon | Wednesday | Weekdays | 17 | 2020 | 2020-03-23 06:54 | 44KV MINAS / RUMBAI LINE | Minas | PGT South | Cloudy | Lightning | 0 | Minas ACB #21 (44KV Line Minas/Rumbai) T/R 1x. Checked and found Minas ACB #21 (44KV Line Minas/Rumbai) T/R 1x. Counter: 92/93 R/F: 51@1,@2. Not patrolled yet. | 1
| 2020-06-18 06:44 | June | 6:44 | Morning | Thursday | Weekdays | 18 | 2020 | 2020-03-24 13:43 | 44KV MINAS / RUMBAI LINE | Minas | PGT South | Cloudy | Lightning | 0 | Checked and found: Device : ACB # 21 T/R, Counter : 92 / 93 , Relay Flag : 51. Patrolled the line found : • Flash Over Dead end Insulator Ø1 Phase : 1, 2, Cause : Lightning | 1
| 2020-06-18 06:44 | June | 6:44 | Morning | Thursday | Weekdays | 18 | 2020 | 2020-03-26 15:04 | 44KV MINAS / RUMBAI LINE | Minas | PGT South | Cloudy | Lightning | 0 | Checked And Found ACB # 21 T/R 1x, Ctr 92/93, R/F 51 Patrolled The Line On 23/Mar/2020 And Found Flash Over Dead End Insulator Ø1 On Phase @1,2, Pole Mr N1 Cause: Lightning | 1
95 | 2020-06-18 15:01 | June | 15:01 | Afternoon | Thursday | Weekdays | 18 | 2020 | 2020-03-23 09:51 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 1081 | 09:51 Manually Opened Sintong VCB fdr#2. Repaired Corrosion Cross Arm o/p 27AF22 & 27AF15. 16:23 Blocked & closed Sintong VCB fdr#2, then release the block. Cause: Plan Maintenance. | 1
96 | 2020-06-18 16:20 | June | 16:20 | Afternoon | Thursday | Weekdays | 18 | 2020 | 2020-03-24 10:40 | SURAM SUBSTATION | Petko | PGT South | Fair | Planned Maintenance | 0 | 10:40 Manually Opened Suram VCB fdr#2 to Dismantled 500 KVATX due to not active yet 16:05 Manually Closed the VCB after finished the Jobs Cause: Planned Maintenance | 1
97 | 2020-06-18 16:20 | June | 16:20 | Afternoon | Thursday | Weekdays | 18 | 2020 | 2020-03-24 15:39 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Rain and Lightning | Pin Insulator | 41 | 6DN feeder #1 load dropped 196A (204/8A). Not checked yet. | 1
| 2020-06-19 09:00 | June | 9:00 | Morning | Friday | Weekdays | 19 | 2020 | 2020-03-27 13:59 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Rain and Lightning | Pin Insulator | 41 | Checked and found: 5442/R.36DN32 T/R, Counter : 238 / 239, Relay Flag : NONE Patrolled the line found : Broken Pin Insulator Phase : 1 Cause : Pin Insulator | 1
98 | 2020-06-19 09:00 | June | 9:00 | Morning | Friday | Weekdays | 19 | 2020 | 2020-03-25 06:56 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | CD fdr #1 load dropped 56 A (174 / 118 A) Not Checked Yet | 1
| 2020-06-19 16:09 | June | 16:09 | Afternoon | Friday | Weekdays | 19 | 2020 | 2020-03-27 14:09 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found: 5441/R.41/AW/62 T/R, Counter : 336 / 337, Relay Flag : NONE Patrolled the line found : No Findings Phase : 2 Cause : Unidentified | 1
99 | 2020-06-19 16:09 | June | 16:09 | Afternoon | Friday | Weekdays | 19 | 2020 | 2020-03-25 07:18 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 83 | KETIGUL feeder #2 T/R 1x Not Checked Yet | 1
| 2020-06-19 19:36 | June | 19:36 | Night | Friday | Weekdays | 19 | 2020 | 2020-03-26 16:55 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 83 | Checked And Found PKTGL VCB2 Fdr #2 T/R 1x, Ctr 382/383, R/F 51N Patrolled The Line On 26/Mar/2020 But Found Nothing Cause: Unidentified | 1
100 | 2020-06-19 19:36 | June | 19:36 | Night | Friday | Weekdays | 19 | 2020 | 2020-03-25 07:59 | 13.8KV MINAS FEEDER #2 | Minas | PGT South | Fair | Lightning | 9 | MINAS ACB feeder #2 T/R 1x, R/F: 51N, counter: 84 / 85 Not Patrolled Yet | 1
| 2020-06-20 04:54 | June | 4:54 | Morning | Saturday | Weekends | 20 | 2020 | 2020-03-28 09:57 | 13.8KV MINAS FEEDER #2 | Minas | PGT South | Fair | Lightning | 9 | Checked And Found ACB # 21 Fdr #1 T/R 1x, Ctr 92/93, R/F 51 Patrolled The Line On 23/Mar/2020 And Found Flash Over Dead End Insulator Ø1 On Phase @1,2, Pole Mr N1 Cause: Lightning | 1
101 | 2020-06-20 10:50 | June | 10:50 | Morning | Saturday | Weekends | 20 | 2020 | 2020-03-25 08:06 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 92 | 08:06 CD feeder #2 load dropped 120 A (215 / 95 A) 08:33 Reported no power at road 08:M1/xx (loc. 6/M1/12) 09:00 Checked and found RCL 08/M1/38 T/O (on block position f for PT WKS clean up canals) 09:03 Manual Close RCl 08/M1/38, OK then release the block. Not Patrolled Yet | 1
102 | 2020-06-20 11:45 | June | 11:45 | Morning | Saturday | Weekends | 20 | 2020 | 2020-03-25 14:30 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:30 CDGT #3 S/U and then online at 14:47 | 1
103 | 2020-06-20 17:10 | June | 17:10 | Afternoon | Saturday | Weekends | 20 | 2020 | 2020-03-25 14:56 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:56 CDGT #4 Offline and then S/D at 14:57 (for replace pin tube radiator of CDGT #4) | 1
104 | 2020-06-21 17:34 | June | 17:34 | Afternoon | Sunday | Weekends | 21 | 2020 | 2020-03-26 15:43 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 91 | So Balam fdr #1 T/R 1x Not Checked Yet | 1
105 | 2020-06-21 18:33 | June | 18:33 | Afternoon | Sunday | Weekends | 21 | 2020 | 2020-03-26 19:30 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 28 | 19:30 It was reported no power at Meno GS (Menggala fdr#1) Checked & found @2 B/O fuse and Dead Monkey at 300KVATX of Meno GS 22:05 Manually Opened Recl 19AN04 Crew Remove Dead Monkey and Replaced B/O fuse 22:25 Manually Closed the Recloser after finished replaced B/O fuse Cause: Animal (Monkey) | 1
106 | 2020-06-21 18:33 | June | 18:33 | Afternoon | Sunday | Weekends | 21 | 2020 | 2020-03-27 11:02 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Fair | Others | 9 | 11:02 Manual Open LBS 9D/96 (8C fdr #1), closed at 11:15 to support SPS change out TX unit due to REDA motor sized up at location 9D/11A. Cause: Other (sized up pump) | 1
107 | 2020-06-21 19:14 | June | 19:14 | Night | Sunday | Weekends | 21 | 2020 | 2020-03-27 18:34 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Drizzle | Lightning | 16 | LIBO VCB feeder #1 T/R 2x Not Checked Yet | 1
| 2020-06-21 19:14 | June | 19:14 | Night | Sunday | Weekends | 21 | 2020 | 2020-03-29 07:31 | 13.8KV LIBO FEEDER #1 | Libo | PGT South | Drizzle | Lightning | 16 | Checked and found: LBOSB/13.8OCB1 T/R, Counter : 602 / 604, Relay Flag : 51N Patrolled the line found : none Phase : 2 Cause : Lightning | 1
108 | 2020-06-22 11:25 | June | 11:25 | Morning | Monday | Weekdays | 22 | 2020 | 2020-03-28 14:47 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Duri | PGT North | Heavy Rain | Pin Insulator | 187 | MSU/2 feeder #2 (BKS Main fdr #2) load dropped 164 A (254 / 90 A) Not Checked Yet | 1
| 2020-06-22 20:43 | June | 20:43 | Night | Monday | Weekdays | 22 | 2020 | 2020-03-30 16:16 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Duri | PGT North | Heavy Rain | Pin Insulator | 187 | Checked and found: RCL 37/BD/12 T/R, Counter : 125 / 127, Relay Flag : NONE Patrolled the found : Pin flash over Phase : 1 Cause : Pin Insulator | 1
109 | 2020-06-22 20:43 | June | 20:43 | Night | Monday | Weekdays | 22 | 2020 | 2020-03-28 15:22 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Cloudy | Unidentified | 46 | NKBS VCB feeder #2 T/R 1x NKBS GFPC T/R 1x Not Checked Yet | 1
| 2020-06-23 06:20 | June | 6:20 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-03-30 15:22 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Cloudy | Unidentified | 46 | Checked And Found NKBKSB OCB2 Fdr #2 T/R 1x, Ctr 99934/99935, R/F 50N Patrolled The Line On 30/Mar/2020 But Found Nothing Cause: Unidentified | 1
110 | 2020-06-23 06:20 | June | 6:20 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-03-28 15:56 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Rain | Unidentified | 0 | CD feeder #2 load dropped 53 A (206 / 153 A) Not Checked Yet | 1
| 2020-06-23 06:41 | June | 6:41 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-03-30 16:04 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Rain | Unidentified | 0 | Checked and found: 5441/R.08/M1/38 T/R, Counter : 197 / 198, Relay Flag : NONE Patrolled the line found: : No Findings Cause : Unidentified | 1
111 | 2020-06-23 06:41 | June | 6:41 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-03-29 09:20 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 39 | 09:20 Manual Open Recl. 6D/298, ////>and closed at 10:18. Replaced 3pcs Broken FCO o/p 6D/81. Cause: Plan Maintenance. | 1
112 | 2020-06-23 08:12 | June | 8:12 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-03-29 15:09 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 57 | Menggala 13.8KV OCB fdr #2 T/R 1X. Menggala fdr #1 Load dropped 38A (174/138A). Not checked yet. | 1
113 | 2020-06-23 10:00 | June | 10:00 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-03-29 16:28 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain and Lightning | Lightning Arrester | 27 | Bekasap Main fdr #3 load dropped 94A (264/170A). Not checked yet. | 1
| 2020-06-23 10:10 | June | 10:10 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-03-30 16:54 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain and Lightning | Lightning Arrester | 27 | Checked and found: 5440/R.34BI18 T/R, Counter : 196 / 197, Relay Flag : NONE Patrolled the line found : LA putus Cause : Lightning Arrester | 1
| 2020-06-23 10:19 | June | 10:19 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-03-04 12:12 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain and Lightning | Lightning Arrester | 27 | Checked And Found 5440/R.34BI18 Fdr #18 Ctr 196/197, Patrolled The Line On 30/Mar/2020 And Found La Putus On Phase @2 Pole Ampuh #24 Cause: Lightning Arrester | 1
114 | 2020-06-23 10:45 | June | 10:45 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-03-29 17:52 | 13.8KV 3D FEEDER #3 | Minas | PGT South | Rain and Lightning | Others | 126 | 3D fdr #3 T/R 2X Ctr:496/498 R/F:51@1@3. Not patrolled yet. | 1
| 2020-06-23 10:45 | June | 10:45 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-03-31 12:43 | 13.8KV 3D FEEDER #3 | Minas | PGT South | Rain and Lightning | Others | 126 | Checked and found: 3DSB/13.8OCB3 T/R, Counter : 496 / 498, Relay Flag : 51 Patrolled the line found : Not Found Phase : 1, 2, 3, Cause : Others | 1
115 | 2020-06-23 16:52 | June | 16:52 | Afternoon | Tuesday | Weekdays | 23 | 2020 | 2020-03-29 18:03 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain and Lightning | Unidentified | 183 | 18:03 3D fdr #4 T/R 2X. 18:20 Manual Open 3D fdr #3 To maintenance Tank level at GS #5. Not checked yet. | 1
| 2020-06-24 07:11 | June | 7:11 | Morning | Wednesday | Weekdays | 24 | 2020 | 2020-01-04 13:20 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain and Lightning | Unidentified | 183 | Checked and found: 3DSB/13.8OCB4 T/R, Counter : 96 / 98, Relay Flag : 50 Patrolled the line found : Not Found Phase : 2 Cause : Unidentified | 1
116 | 2020-06-24 07:11 | June | 7:11 | Morning | Wednesday | Weekdays | 24 | 2020 | 2020-03-29 18:05 | 13.8KV 3D FEEDER #7 | Minas | PGT South | Rain and Lightning | Tree | 25 | 18:05 3D fdr #7 T/R 2X. 18:09 3D OCB fdr#7 T/LO GS#5 Requested to S/D some Fdrs to Maintain Tank Level. 18:20 Manually Opened 3D OCB fdr#4, Closed at 20:58 18:26 Manually Opened 3D OCB fdr#3, Closed at 21:00 18:27 Manually Opened 4D OCB fdr#2, Closed at 20:31 18:28 Manually Opened 34 OCB fdr#3, Closed at 21:00 Patrolled the Line found, Fall down Tree, touch the Lines, Near Well 3D/25 Transfer Part Load 3D fdr#7 to 3D fdr#5, for Cutting and Remove the Trees 20:10 Opened LBS 3D/128, (3D fdr#7 20:23 Closed LBS 3D/144, (3D fdr#5) Cause: Tree | 1
| 2020-06-24 12:27 | June | 12:27 | Afternoon | Wednesday | Weekdays | 24 | 2020 | 2020-03-30 14:32 | 13.8KV 3D FEEDER #7 | Minas | PGT South | Rain and Lightning | Tree | 25 | Checked And Found 3DSB OCB7 Fdr #7 T/LO , Ctr 234/238, R/F 50 Patrolled The Line On 29/Mar/2020 And Found Fallen Tree Near Loc.3D/25 On Phase @1,2,3, Cause: Tree | 1
117 | 2020-06-24 12:27 | June | 12:27 | Afternoon | Wednesday | Weekdays | 24 | 2020 | 2020-03-29 18:18 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Pin Insulator | 142 | 18:08 3D OCB fdr#2 T/R 1x 18:18 3D OCB fdr#2 T/LO Patrolled the Line, but found nothing 21:56 Opened LBS 3E/64 to split troubleshoot 21:57 Block & Closed 3D fdr#2. To be continued tomorrow. | 1
| 2020-06-25 06:43 | June | 6:43 | Morning | Thursday | Weekdays | 25 | 2020 | 2020-03-30 14:26 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Pin Insulator | 142 | 12:14 Checked And Found 3DSB OCB2 Fdr #2 T/LO , Ctr 371/376, R/F 50N. Patrolled The Line On 29/Mar/2020 And Found Broken Pin Insulator Ø1 On Pole 4E/21R Blocked 3D frd #2. Closed LBS 3E/64. 12:22 Blocked and closed Recl 2F/11. OK tnen released the block. Cause: Pin Insulator | 1
118 | 2020-06-25 11:03 | June | 11:03 | Morning | Thursday | Weekdays | 25 | 2020 | 2020-03-30 03:41 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Dumai | PGT North | Rain and Lightning | Unidentified | 0 | Dumai 4160V ACB#22 fdr#4 T/R 1x. Not checked yet. | 1
| 2020-06-25 20:53 | June | 20:53 | Night | Thursday | Weekdays | 25 | 2020 | 2020-03-30 10:01 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Dumai | PGT North | Rain and Lightning | Unidentified | 0 | Checked and found: DMISB/4.16ACB22 T/R, Counter : 294 / 296, Relay Flag : 50 Patrolled the line found : No Findings Phase : 1, 3, Cause : Unidentified | 1
119 | 2020-06-25 20:53 | June | 20:53 | Night | Thursday | Weekdays | 25 | 2020 | 2020-03-30 03:48 | 13.8KV 3D FEEDER #6 | Minas | PGT South | Rain and Lightning | Others | 0 | 3D OCB fdr@6 T/R 1x Ctr:304/307 R/F:51N, 51@2. 3D Tx/2 GFPC T/R 1x. Not patrolled yet. | 1
| 2020-06-26 06:26 | June | 6:26 | Morning | Friday | Weekdays | 26 | 2020 | 2020-03-31 12:35 | 13.8KV 3D FEEDER #6 | Minas | PGT South | Rain and Lightning | Others | 0 | Checked and found: 3DSB/13.8OCB6 T/R, Counter : 304 / 307, Relay Flag : 51N Patrolled the line found: Not Found cause : others | 1
120 | 2020-06-26 06:26 | June | 6:26 | Morning | Friday | Weekdays | 26 | 2020 | 2020-03-30 03:48 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 474 | 04:48 3D OCB fdr#4 T/LO. 06:00 Checked & found 3D OCB fdr#4 T/LO Ctr;96/114 R/F:51@1@2@3. Patrolled the line to Recl 2D/14, but found nothing. 06:32 Manually Opened Recl 2D/14. 06:33 Blocked & closed #d OCB fdr#4. 06:43 Manually Opened Recl 2D/44. 06:45 Blocked & closed Recl 2D/14, then release the block. Continued to patrolled the line from Recl 2D/44 and found 25% @1 broken Dead End o/p 1D/11 . 07:42 Blocked & closed Recl 2D44 ,OK then release the block. Cause: Lightning. | 1
121 | 2020-06-26 10:00 | June | 10:00 | Morning | Friday | Weekdays | 26 | 2020 | 2020-03-30 14:45 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Fair | Planned Maintenance | 6 | 14:45 Manual Open Recl. 38/BE/10, and Closed at 14:52. Isolated broken Static wire at aman #10. Cause: Plan Maintenance. | 1
122 | 2020-06-27 10:14 | June | 10:14 | Morning | Saturday | Weekends | 27 | 2020 | 2020-03-30 15:59 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Unidentified | 27 | Ketigul 13.8KV fdr #1 T/R 1X. No checked yet. | 1
| 2020-06-28 06:35 | June | 6:35 | Morning | Sunday | Weekends | 28 | 2020 | 2020-03-31 11:37 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Unidentified | 27 | Checked and found: PKTGL/13.8VCB1 T/R, Counter : 229 / 230, Relay Flag : 51N Patrolled the line found : No Findings Phase : 0, 2, Cause : Unidentified | 1
123 | 2020-06-28 11:00 | June | 11:00 | Morning | Sunday | Weekends | 28 | 2020 | 2020-03-31 10:01 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 39 | 10:01 Manually open LBS 5D/57 D/S 6DN feeder #2. Replaced Tx at well 6D/11A. 10:44 Manually closed LBS 5D/57. Cause: Planned Maintenance. | 1
124 | 2020-06-29 09:29 | June | 9:29 | Morning | Monday | Weekdays | 29 | 2020 | 2020-03-31 16:04 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Cloudy | Under investigation | 219 | 16:04 Bekasap 13.8KV ACB feeder #6 T/SO. (suspected T/LO due to alarm indicated more twice trip) 17:00 Checked and found Bekasap fdr #3 T/SO R/F:..... ctr:384/385. Patrolled the line and found @3 broken Pin Insulator o/p: 38/BE/02. Rack Out Bekasap ACB fdr #6. Replaced @3 broken Pin Insulator o/p: 38/BE/02. Rack In Bekasap ACB fdr #6. 18:36 Blocked and closed Bekasap ACB fdr #6, Ok than released the block. Cause: Under investigation. | 1
125 | 2020-06-29 13:45 | June | 13:45 | Afternoon | Monday | Weekdays | 29 | 2020 | 2020-06-03 08:25 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Fair | Planned Maintenance | 37 | Checked and found: 5442/R.6E23A M/O, Counter : 542 / 543, Relay Flag : NONE. Patrolled the line found : MTCE team to cut high trees near location 6F/21, Planned Maintenance Cause : Planned Maintenance | 1
| 2020-06-29 14:11 | June | 14:11 | Afternoon | Monday | Weekdays | 29 | 2020 | 2020-03-31 21:34 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Fair | Planned Maintenance | 37 | 21:34 Minas ACB fdr#6 T/R 1x Ctr: 200/201 R/F:51N. 21:50 It was reported no power at Cermai & Dahlia. 22:15 Checked & found Recl 7E/67A T/O CXtr:90/91. 22:18 Blocked & closed Recl. 7E67A, then release the block. Not patrolled yet. | 1
1 | 2020-06-30 07:34 | June | 7:34 | Morning | Tuesday | Weekdays | 30 | 2020 | 2020-01-04 06:54 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Fair | Tree | 421 | 06:54 Central Duri fdr #9 T/R 1x 08:28 Reported no power at road 04-01-xx 08:43 Checked and found RCL 04-01-02 T/O (block for PT KRS repair bridge) Patrolled the line and found high trees at 4 spot (pole 04-01-04/16/19/22) Continue to executed the trees. 15:15 Manually Close RCL 04-01-02, OK (leave on block position) Cause: Tree | 1
2 | 2020-06-30 07:34 | June | 7:34 | Morning | Tuesday | Weekdays | 30 | 2020 | 2020-01-04 16:38 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Lightning | Lightning | 0 | Sintong fdr #2 load dropped 183 A (228 - 45 A) Sintong fdr #1 load dropped 12 A (93 - 81 A) Not Checked Yet | 1
| 2020-06-30 10:42 | June | 10:42 | Morning | Tuesday | Weekdays | 30 | 2020 | 2020-02-04 17:06 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Lightning | Lightning | 0 | Checked and found RCL 28-AF-17 T/R 1x, Counter: 462 - 463, R/F: 51N Patrolled the line and found Pin Support Flash Over at @3 o/p 27-AG-03 Cause : Lightning | 1
3 | 2020-06-30 11:03 | June | 11:03 | Morning | Tuesday | Weekdays | 30 | 2020 | 2020-01-04 16:41 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Rain and Lightning | Tree | - | 16:41 VCB-30 DCM fdr #2 T/LO (operate 2x) 16:48 Informed to TDO crew 17:10 Visually check Bowling TX, condition normal. 17:15 Continue to patrolled the line and found fallen trees near Water Reservoir Seulawah 17:43 Rack Out VCB fdr #2 at Duri Community SG Reported VCB T/LO, R/F: 51P @2, Counter: 119 - 121 Execute the fallen trees, finished at 18:10 18:11 Rack in VCB-30 DCM fdr #2 18:13 Blocked and manually close VCB-30 DCM fdr #2, OK then release the block. Cause: Tree | 1
4 | 2020-06-30 17:12 | June | 17:12 | Afternoon | Tuesday | Weekdays | 30 | 2020 | 2020-01-04 17:25 | 13.8KV BANGKO FEEDER #3 | Bangko-Balam | PGT North | Lightning | Lightning | - | 17:25 BKO feeder #3 T/R 1x BKO feeder #2 load dropped 160 A (239 - 79 A) BKO feeder #4 load dropped 51 A (141 - 90 A) Not Checked Yet | 1
| 2020-06-30 22:30 | June | 22:30 | Night | Tuesday | Weekdays | 30 | 2020 | 2020-02-04 11:30 | 13.8KV BANGKO FEEDER #3 | Bangko-Balam | PGT North | Lightning | Lightning | - | Checked and found VCB BKO feeder #3 T/R 1x, ctr: 99963-99964, R/F: 51N Patrolled the line and found broken LA @1 o/p 22-Z-17 Cause : Lightning | 1
5 | 2020-07-13 04:22 | July | 4:22 | Morning | Monday | Weekdays | 13 | 2020 | 2020-02-04 09:40 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Fair | Planned Maintenance | 63 | 09:40 Manual Open RCL 6E-23A (MNS fdr #6), closed at 11:29 MTCE team to cut high trees near location 6F-21 Planned Maintenance | 1
6 | 2020-07-13 04:22 | July | 4:22 | Morning | Monday | Weekdays | 13 | 2020 | 2020-02-04 15:51 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Dead End Insulator | 43 | 15:51 BKO VCB feeder #4 T/R 1x BKO feeder #1 load dropped 100 A (152 - 52 A) BKO feeder #2 load dropped 224 A (245 - 21 A) BKO feeder #3 load dropped 165 A (223 - 58 A) Not Checked yet Production loss: -->Bangko fdr #1 : 105 Bbls, 61 Wells. -->Bangko fdr #4 : 53 Bbls, 30 Wells. ------------------------------------------+ Total : 159 Bbls, 90 Wells. | 1
| 2020-07-13 07:02 | July | 7:02 | Morning | Monday | Weekdays | 13 | 2020 | 2020-05-04 10:15 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Dead End Insulator | 43 | Checked and found Bangko OCB feeder #4 T/R 1x. Counter: 81-82 R/F: 51N. Patrolled the line found @1 flash over dead end insulator towards Bangko #274. Cause: Dead end insulator. | 1
7 | 2020-07-13 07:02 | July | 7:02 | Morning | Monday | Weekdays | 13 | 2020 | 2020-02-04 16:20 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Lightning | Lightning | 42 | 16:20 Sintong VCB fdr #2 T/R 1x Sintong feeder #1 load dropped 21 A (93 - 72 A) Not Checked Yet | 1
| 2020-07-13 08:48 | July | 8:48 | Morning | Monday | Weekdays | 13 | 2020 | 2020-05-04 10:23 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Lightning | Lightning | 42 | Checked and found Sintong OCB feeder #2 T/R 1x. Counter: 513-514 R/F: 51N. Patrolled the line found @3 flash over Fuse Cut Out on pole NN. Cause: Suspected Lightning (Fuse Cut Out). | 1
8 | 2020-07-13 15:30 | July | 15:30 | Afternoon | Monday | Weekdays | 13 | 2020 | 2020-02-04 17:53 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | - | CD ACB fdr #1 load dropped 20 A (165 - 145 A) Not Checked Yet | 1
| 2020-07-13 15:30 | July | 15:30 | Afternoon | Monday | Weekdays | 13 | 2020 | 2020-03-04 15:03 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | - | Checked And Found 5441-R.09-L7-01 Fdr #1 T/R 1 x, Ctr 251-252, Patrolled The Line On 03-Apr-2020 But Found Nothing Cause: Unidentified | 1
9 | 2020-07-14 10:31 | July | 10:31 | Morning | Tuesday | Weekdays | 14 | 2020 | 2020-02-04 22:45 | 13.8KV 3D TX-2 GFPC | Minas | PGT South | Heavy Rain | Lightning | - | 22:45 3D GFPC T/R 1X. No load droped. Not checked yet. | 1
| 2020-07-14 10:35 | July | 10:35 | Morning | Tuesday | Weekdays | 14 | 2020 | 2020-06-04 09:28 | 13.8KV 3D TX-2 GFPC | Minas | PGT South | Heavy Rain | Lightning | - | Checked and found: 13.8KV3D2_GFPC T/R, Counter : 642 - 643, Relay Flag : NONE. Patrolled the line found : Not Found Cause : Lightning | 1
10 | 2020-07-15 16:55 | July | 16:55 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 2020-02-04 23:17 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Rain and Lightning | Static Wire | 1199 | 23:17 Minas 13.8KV ACB fdr #4 T/LO R/F:50@1, 50N ctr:9-11. 23:40 Checked and found Broken Static wire 2 spen from minas Swy. 00:15 Open Recl. 7D-150 and Closed LBS 8D-151 (de feed from 8D fdr #7). Will be continued tomorrow. | 1
| 2020-07-15 16:55 | July | 16:55 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 2020-03-04 17:58 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Rain and Lightning | Static Wire | 1199 | 13:39 Manually Open ACB Minas fdr #3, closed at 17:17 Manually Open ACB Minas fdr #4, closed at 17:19 Repair the broken static at 8 pole structure Minas, finished at 17:00 17:21 Blocked and Close ACB Minas fdr #4 17:34 Close RCL 7D-150, OK (parallel Minas fdr #4 with 8D fdr #7) 17:37 Open LBS 8D-151, OK (Minas fdr #4 and 8D fdr #7 back to Normal) Cause: Static Wire | 1
11 | 2020-07-16 06:48 | July | 6:48 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-03-04 09:31 | 13.8KV MINAS FEEDER #2 | Minas | PGT South | Drizzle | Lightning | 0 | Minas ACB-13 feeder #2 T/R 1x, ctr: 85 - 86, R/F: 51N Not Checked Yet | 1
| 2020-07-16 06:48 | July | 6:48 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-06-04 08:30 | 13.8KV MINAS FEEDER #2 | Minas | PGT South | Drizzle | Lightning | 0 | checked and found: MNSSG-13.8ACB13 T/R, Counter : 85 - 86, Relay Flag : 51N Patrolled the line found : Not Found Cause : Lightning | 1
12 | 2020-07-16 09:59 | July | 9:59 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-03-04 09:37 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Cloudy | Unidentified | 61 | 09:37 NKBS VCB fdr #2 T/R 1x 10:12 Informed to TDO crew and KBGS that load still minus about 200A 10:46 Crew reported 2 unit RCL d/s NKBS fdr #2 on NORMAL condition - RCL 38-CW-08, counter: 123 (no event) - RCL 38-CX-25, counter : 342 (no event) 14:49 Checked and found NKB OCB Fdr #2 T/R 1 x, Ctr 99935-99936, R/F: 50N Patrolled the line On 03-Apr-2020 but found nothing Cause: Unidentified. | 1
13 | 2020-07-16 09:59 | July | 9:59 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-03-04 09:53 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Recloser | 1 | 09:53 SINTONG feeder #2 load dropped 160 A (262-102 A) -- BENAR GS Reported RCL 28-AF-02 T/R 1x Not Patrolled Yet | 1
| 2020-07-16 12:13 | July | 12:13 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-04-04 14:56 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Recloser | 1 | Checked and found STG fdr #2 T/R 1x, ctr: 1552 - 1553, R/F: 51N Patrolled the line and found problem at Control recloser 28-AF-02 Cause : Recloser | 1
14 | 2020-07-16 13:51 | July | 13:51 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-03-04 13:39 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 179 | 13:39 Manual Open Minas ACB fdr #3, closed at 17:17 Manual Open Minas ACB fdr #5 (no load), closed at 17:19 MTCE team to repair broken static wire at 8 pole structure Minas Planned Maintenance | 1
15 | 2020-07-16 13:51 | July | 13:51 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-04-04 06:44 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 24 | Ketigul VCB feeder #1 T/R 1x. Not checked yet. | 1
| 2020-07-16 14:16 | July | 14:16 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-06-04 07:16 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 24 | Checked and found: PKTGL-13.8VCB1 T/R, Counter : 230 - 231, Relay Flag : 51N. Patrolled the line found : No Finding Cause : Unidentified | 1
16 | 2020-07-16 14:16 | July | 14:16 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-04-04 09:46 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Planned Maintenance | 111 | 09:10 Transfer part load of CD feeder #2 to Darling feeder #8 by: - Close LBS 08-M6-01 and Open RCL 08-M3-38 - Close LBS 08-M2-01 and Open RCL 08-M1-38 09:46 Manual Open C Duri ACB #12 (feeder #2) Purpose for mtce team working d/s of CD fdr #2 to dismantle RCL 40-BA-02 and close the bypass switch. 13:45 Manually blocked and closed C Duri ACB #12 (feeder #2) --> OK, and then released the block. Cause: Planned Maintenance. | 1
17 | 2020-07-16 15:49 | July | 15:49 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-04-04 14:46 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Cloudy | Pin Insulator | 43 | 8C VCB feeder #4 T/R 1x ---> WIP GS-2 Not Checked Yet | 1
| 2020-07-16 15:49 | July | 15:49 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-07-04 17:05 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Cloudy | Pin Insulator | 43 | Checked and found 8C VCB fdr #4 T/R 1x, ctr: 632 - 633, R/F: 51P @3 Patrolled the line and found broken pin insulator @3 o/p M8C-18 Cause : Pin Insulator | 1
18 | 2020-07-16 17:29 | July | 17:29 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-04-04 14:56 | 115KV ROKAN - KETIGUL | Bangko-Balam | PGT North | Heavy Rain | Unidentified | 554 | 14:56 115 kV Line Rokan - Ketigul T/SO, frequency rise to 60.20 Hz - 115 kV GCB #43 CD T/R 1x - 115 kV GCB #1 KTGL T/SO, closed at 15:00, R/F: None, ctr: 205-207 - 115 kV GCB #2 KTGL T/SO, R/F: 67N, ctr: 181 - 182, closed at 17:48 - 115 kV GCB #11 RKN T/SO, R/F: 87L, 21GZ1, ctr: 37 - 39, closed at 17:24 - PINANG fdr#1 dropped 23 A (105 - 82 A) - NELLA fdr #1 dropped 62 A (203 - 141 A) - NELLA fdr #2 dropped 19 A (66 - 47 A) - BANGKO fdr #1 dropped 32 A (157 - 125 A) - BANGKO fdr #4 dropped 15 A (167 - 152 A) - SINTONG fdr #1 dropped 18 A (96 - 78 A) - SINTONG fdr #2 dropped 45 A (256 - 211 A) - S. BALAM fdr #1 dropped 19 A (146 - 127 A) - S. BALAM fdr #3 dropped 33 A (136 - 103 A) - S. BALAM fdr #4 dropped 31 A (172 - 141 A) - MENGGALA fdr #1 dropped 35 A (195 - 160 A) - MENGGALA fdr #2 dropped 14 A (167 - 153 A) - KETIGUL fdr #1 dropped 51 A (111 - 160 A) - KETIGUL fdr #2 dropped 34 A (81 - 47 A) - PEMATANG fdr #1 dropped 181 A (207 - 26 A) - PEMATANG fdr #2 dropped 102 A (111 - 9 A) - RANGAU fdr #1 dropped 53 A (58 - 5 A) - RANGAU fdr #2 dropped 154 A (154 - 0 A) - PETANI fdr #1 dropped 228 A (237 - 9 A) - PETANI fdr #2 dropped 65A (67 - 2 A) - ROKAN fdr #2 dropped 34 A (81 - 47 A) - ROKAN fdr #4 dropped 11 A (15 - 4 A) 16:20 Checked ROKAN Substation and found - GCB #11 T/SO, spring discharge, ctr: 37 - 39, R/F: 87L, 21GZ1 17:20 Closing spring back to charge after troubleshoot (support by mtce) 17:24 Manual Close 115 kV GCB #11 RKN (by DSC), OK. 17:37 Checked KETIGUL Substation and found - GCB #1 CLOSE (by DSC on 15:00), R/F: None, ctr: 205 - 207 - GCB #2 T/O, R/F: 67N, ctr: 181 - 182 17:48 Manually close 115 kV GCB #2 KTGL (by DSC) OK. Production Loss: * Petani fdr #1 : 24 Bbls, 2 Wells. * Petani fdr #2 : 2 Bbls, 2 Wells. --------------------------------------+ TOTAL Loss : 26 Bbls, 4 Wells. | 1
| 2020-07-16 17:29 | July | 17:29 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-08-04 07:55 | 115KV ROKAN - KETIGUL | Bangko-Balam | PGT North | Heavy Rain | Unidentified | 554 | Checked and found: 115 kV GCB#43 Central Duri Trip 1x Counter : 125 - 126, R/F 67N; 50P @2 115 kV GCB#45 Central Duri Trip 1x Counter : 158 – 159, R/F 67N; 50P @2 115 kV GCB #1 KTGL T/SO, closed at 15:00, R/F: None, counter: 205-207 115 kV GCB #2 KTGL T/SO, R/F: 67N, counter: 181 - 182, 115 kV GCB #11 RKN T/SO, R/F: 87L, 21GZ1, counter: 37 - 39 Patrolled the power line but found nothing. Cause: Unidentified. | 1
19 | 2020-07-16 19:04 | July | 19:04 | Night | Thursday | Weekdays | 16 | 2020 | 2020-04-04 15:00 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | 140 | 15:00 Minas fdr #1 T/LO, ctr: 91 - 93, R/F: 50P @1 @2 Minas fdr #2 dropped 42 A (117 - 75 A) Minas fdr #3 dropped 75 A (135 - 60 A) Minas fdr #4 dropped 75 A (132 - 57 A) Minas fdr #6 dropped 13 A (38 - 25 A) 15:47 Patrolled Minas fdr #1 and found broken pin @1 and @3 o/p 7E-43 (Rain) 16:32 Shut down housing Minas feeder to replace the broken pin finished at 17:15 17:18 Manual close Minas fdr #1, OK Cause: Lightning | 1
20 | 2020-07-17 01:25 | July | 1:25 | Night | Friday | Weekdays | 17 | 2020 | 2020-04-04 15:52 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain | Lightning | 455 | 15:52 MGL VCB fdr #1 T/R 1x, Bus voltage rise to 16.4 kV (MGL substation) Bus Voltage at all Substation (BANGKO, BALAM, NELLA, PINANG, SINTONG, MENGGALA) also high, and then impact to load dropped at feeders: - MENGGALA ropped 104 A (256 - 152 A) - PINANG dropped 83 A (105 - 22 A) - NELLA #1 dropped 164 A (203 - 39 A) - NELLA #2 dropped 52 A (66 - 14 A) - BANGKO fdr #1 dropped 21 A (157 - 136 A) - BANGKO fdr #2 dropped 131 A (246 - 115 A) - BANGKO fdr #3 dropped 59 A (240 - 181 A) - BANGKO fdr #4 dropped 71 A (167 - 96 A) - SINTONG fdr #2 dropped 104 A (256 - 152 A) - S. BALAM fdr #1 dropped 120 A (146 - 26 A) - S. BALAM fdr #2 dropped 90 A (96 - 6 A) - S. BALAM fdr #3 dropped 130 A (136 - 6 A) - S. BALAM fdr #4 dropped 111 A (172 - 61 A) - KETIGUL fdr #1 dropped 51 A (111 - 60 A) - KETIGUL fdr #1 dropped 34 A (81 - 47 A) - KETIGUL fdr #1 dropped 6 A (42 - 36 A) 17:34 Checked and found RCL 19-AN-04 T/SO, ctr: 822-823 Block and close the recloser, OK. then release the block. 17:48 Checked and found RCL 19-AO-01 T/SO, ctr: 522-825 Block and close the recloser, OK. then release the block. Cause: Not Patrolled Yet | 1
| 2020-07-17 01:30 | July | 1:30 | Night | Friday | Weekdays | 17 | 2020 | 2020-06-04 09:09 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain | Lightning | 455 | Checked and found Recl. 19AN04 T/SO Ctr:822-823 R/F:51N. Recl. 19AO01 T/R 2x Ctr:522-525 R/F:51N. Patrol led the line found but found nothing. Cause : Lightning | 1
21 | 2020-07-17 01:30 | July | 1:30 | Night | Friday | Weekdays | 17 | 2020 | 2020-04-04 15:52 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Rain | Over voltage | 19 | 15:52 S. Balam fdr #1 Load dropped 108A (130-22A). S. Balam fdr #2 Load dropped 99A (166-67A). Not Checked yet. | 1
| 2020-07-17 01:30 | July | 1:30 | Night | Friday | Weekdays | 17 | 2020 | 2020-05-04 01:44 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Rain | Over voltage | 19 | 01:44 It was reported no Power around S. Balam #21 and S. Balam # 180. 02:58 Checked and found Recl. 16-Z-41 T/O, ctr:320-322. Blocked and closed the Recloser but tripped again. Continued the line but found nothing. will be continued this morning. 08:00 Re-patrol the power line but found nothing 08:50 Block SGF and manual Close RCL 16-Z-41, OK, ctr: 3204 Cause: Unidentified (Sensitive Ground Fault) | 1
22 | 2020-07-17 01:30 | July | 1:30 | Night | Friday | Weekdays | 17 | 2020 | 2020-05-04 09:56 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Transformer Failure | - | 09:56 It was reported broken fuse @ JURONG #37. Checked and found Tx Failure. Cause: TX failure (need to be replaced). | 1
| 2020-07-17 01:44 | July | 1:44 | Night | Friday | Weekdays | 17 | 2020 | 2020-07-04 09:56 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Transformer Failure | - | 11:00 Replaced 300Kva Tx at Jorong #37. Cause : TX failure | 1
23 | 2020-07-17 01:44 | July | 1:44 | Night | Friday | Weekdays | 17 | 2020 | 2020-05-04 10:20 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Fair | Planned Maintenance | 0 | 10:20 Manual Open DCM VCB fdr #2, after transferred partial load to DCM fdr #1 11:09 Manual Close DCM VCB fdr #2, ctr: 121 - 122 Purpose for maintenance to repair broken jumper on pole 2F-17 Cause: Planned Maintenance | 1
24 | 2020-07-17 18:39 | July | 18:39 | Afternoon | Friday | Weekdays | 17 | 2020 | 2020-05-04 10:43 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | 339 | 10:43 CD feeder #1 load dropped 53 A (142 - 89 A) 12:51 Reported no power at Kulin field and Puncak GS 14:24 Checked and found RCL 38-AS-09 T/SO, ctr: 443 - 444, R/F: 51P @3 Patrolled the power line but found nothing 15-17 Block and manual close RCL 38-AS-09, OK. then release the block Cause: Unidentified | 1
25 | 2020-07-17 18:39 | July | 18:39 | Afternoon | Friday | Weekdays | 17 | 2020 | 2020-05-04 12:20 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Transformer Failure | - | 12:20 It was reported B/O fuse for TX at Meso #04 Checked and found b/o fuse 2 pcs at MESO #04. TTR tested and Megger the TX and found TX failure. Cause: TX Failure (need to replace). | 1
| 2020-07-18 08:14 | July | 8:14 | Morning | Saturday | Weekends | 18 | 2020 | 2020-06-04 14:00 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Transformer Failure | - | Change out 500 KVA TX at MESO #04 Cause: Transformer Failure | 1
26 | 2020-07-18 08:14 | July | 8:14 | Morning | Saturday | Weekends | 18 | 2020 | 2020-05-04 18:10 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Cloudy | Unidentified | 0 | Central Duri ACB-28 feeder #16 T/R 1x, ctr: 370 - 371 R/F: 51N Not Patrolled Yet | 1
| 2020-07-18 13:09 | July | 13:09 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-06-04 16:18 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Cloudy | Unidentified | 0 | Checked and found ACB-28 CD fdr #16 T/R 1x, ctr: 370-371, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
27 | 2020-07-18 13:09 | July | 13:09 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-05-04 18:11 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Fair | Unidentified | - | 18:11 C. Duri fdr #5 load dropped 11A (85-74A). 20:10 It was reported No Power around 03-06-25A. 20:57 Checked and found Recl. 03-06-03 T/LO ctr:170-174. Patrolled the line but found nothing. 22:12 Blocked and closed Recl. 03-06-03, Ok then released the block. 02:00 It was reported No Power around 03-06-25A. 02:17 Checked and found Recl. 03-06-03 T/O ctr:174-175 (On blocked). Closed Recl. 03-06-03, Ok then released the block Cause: Unidentified. | 1
28 | 2020-07-18 13:18 | July | 13:18 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-06-04 06:02 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 0 | 06:02 C. Duri 13.8KV ACB fdr #16 T/R 3x F/R:51 @1, @2 ctr:371-374. 16:20 Patrolled the line but found nothing Cause: Unidentified | 1
| 2020-07-18 13:18 | July | 13:18 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-06-04 16:20 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found: CDRSG-13.8ACB28 T/R, Counter : 371 - 374, Relay Flag : 51 Patrolled the line found : No Finding Phase : 1, 2, Cause : Unidentified | 1
29 | 2020-07-18 13:23 | July | 13:23 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-06-04 08:00 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | 31 | 08:00 ACB-11 CD feeder #1 T/R 1x, ctr: 273 - 274, R/F: 51N, 51G 16:13 Patrolled the line but found nothing Cause: Unidentified | 1
| 2020-07-18 13:24 | July | 13:24 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-06-04 16:13 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | 31 | Checked and found: CDRSG-13.8ACB11 T/R, Counter : 273 - 274, Relay Flag : 51N Patrolled the line found : No Finding Cause : Unidentified | 1
30 | 2020-07-18 13:24 | July | 13:24 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-06-04 14:38 | 13.8KV 4B FEEDER #6 | Minas | PGT South | Fair | Planned Maintenance | 6 | 14:38 Manual Open LBS 4B-150 D/S 4B feeder #6. MTCE team to cut high trees near location 4B-24/13/16/35. 15:32 Manually closed LBS 4B-150. Cause: Planned Maintenance. | 1
31 | 2020-07-18 13:28 | July | 13:28 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-06-04 15:15 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Lightning | 32 | Nella VCB fdr #2 T/R 1x Not Checked Yet | 1
| 2020-07-18 17:30 | July | 17:30 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-04 14:17 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Lightning | 32 | Checked and found: NELLA VCB fdr #2 T/R 1x, ctr : 359 - 360, R/F : 51N Patrolled the line and found broken Pin insulator 10% on @2 and 5% on @3 Cause : Lightning | 1
32 | 2020-07-18 17:30 | July | 17:30 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-06-04 15:17 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 0 | Menggala feeder #2 load dropped 156 (165 - 9 A) Not Checked Yet | 1
| 2020-07-18 18:44 | July | 18:44 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-08-04 10:23 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 0 | Checked and found Menggala GFPC T/R 1x Ctr:137 -140 R/F:NONE Patrolled the line found but found nothing. Cause : Unidentified. | 1
33 | 2020-07-18 19:44 | July | 19:44 | Night | Saturday | Weekends | 18 | 2020 | 2020-06-04 15:46 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Cloudy and Lightning | Lightning | 42 | 14:46 BEKASAP VCB fdr #6 T/SO 16:40 Checked and found VCB BKS fdr #6 T/SO, ctr: 385 - 386, R/F: 51N, 50N Not Patrolled Yet | 1
34 | 2020-07-19 06:21 | July | 6:21 | Morning | Sunday | Weekends | 19 | 2020 | 2020-06-04 15:46 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Duri | PGT North | Cloudy and Lightning | Lightning | 102 | 15:46 BKS fdr #2 (MSU fdr #2) load dropped 188 A (254 - 66 A) Not Checked Yet | 1
35 | 2020-07-19 06:21 | July | 6:21 | Morning | Sunday | Weekends | 19 | 2020 | 2020-06-04 15:46 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Cloudy and Lightning | Lightning | 64 | 15:46 BKS Main VCB fdr #3 T/R 1x BKS Main feeder #5 load dropped 243 A (245 - 2 A) 16:39 Checked and found BKS VCB fdr #3 T/R 1x, ctr: 99592 - 99593, R/F 51P @2 Not Patrolled Yet | 1
36 | 2020-07-19 10:53 | July | 10:53 | Morning | Sunday | Weekends | 19 | 2020 | 2020-06-04 17:10 | 13.8KV 8D FEEDER #6 | Minas | PGT South | Rain and Lightning | Lightning | 0 | 17:10 8D fdr #6 T/R 1x 8D fdr #7 load dropped 186 A (210 - 24 A) -- pumps 8D fdr #8 load dropped 184 A (188 - 4 A) -- pumps Not Checked Yet | 1
| 2020-07-20 06:28 | July | 6:28 | Morning | Monday | Weekdays | 20 | 2020 | 2020-07-04 17:18 | 13.8KV 8D FEEDER #6 | Minas | PGT South | Rain and Lightning | Lightning | 0 | Checked and found 8D VCB fdr #6 T/R 1x, R/F: 50P @3, ctr: 2065 - 2066 Patrolled the line and found flash over pin insulator @3 o/p 8D-307 Cause : Lightning | 1
37 | 2020-07-20 15:37 | July | 15:37 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-06-04 17:12 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Rain and Lightning | Pin Insulator | 37 | 8C VCB fdr #1 T/R 2x 8C fdr #3 load dropped 132 A (197 - 65 A) Not Checked Yet | 1
| 2020-07-20 16:10 | July | 16:10 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-09-04 08:12 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Rain and Lightning | Pin Insulator | 37 | Checked & found 8C OCB fdr#1 T/R 2x Ctr:696-698 R/F:51@3. Patrolled the line & found @3 Broken Pin Insulator o/p 9D-13. Cause : Pin Insulator. | 1
38 | 2020-07-20 16:10 | July | 16:10 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-06-04 17:21 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Rain and Lightning | Others | 0 | 17:21 8D fdr #5 load dropped 44 A (170 - 126 A) Not Checked Yet | 1
| 2020-07-21 17:38 | July | 17:38 | Afternoon | Tuesday | Weekdays | 21 | 2020 | 2020-09-04 07:52 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Rain and Lightning | Others | 0 | Checked and found Recl. GS1 T/R 1x Ctr:113-114 R/F:NONE Patrolled the line found BJU Pump at GS-1 Trip. Cause : Others. | 1
39 | 2020-07-22 00:43 | July | 0:43 | Night | Wednesday | Weekdays | 22 | 2020 | 2020-06-04 17:21 | 13.8KV 8D FEEDER #11 | Minas | PGT South | Rain and Lightning | Lightning | 45 | 8D fdr #11 T/R 1 X Not checked yet. | 1
| 2020-07-22 00:43 | July | 0:43 | Night | Wednesday | Weekdays | 22 | 2020 | 2020-08-04 08:05 | 13.8KV 8D FEEDER #11 | Minas | PGT South | Rain and Lightning | Lightning | 45 | Checked and found: 8D OCB11 T/R 1x, Counter : 99929 - 99930, Relay Flag : 51N Patrolled the line but found nothing Cause : Lightning | 1
40 | 2020-07-22 05:25 | July | 5:25 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-04 06:52 | 13.8KV DURI FIELD FEEDER #3 | Duri | PGT North | Fair | Animal | 0 | Duri Field fdr #3 T/R 1X. Not checked yet. | 1
| 2020-07-22 05:25 | July | 5:25 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-08-04 07:13 | 13.8KV DURI FIELD FEEDER #3 | Duri | PGT North | Fair | Animal | 0 | Checked and found DF ACB-52 T/R 1x, Counter : 283 - 284, Relay Flag : 51N Patrolled the line and found dead squirrel behind TDO Shop. Cause : Animal | 1
41 | 2020-07-22 05:44 | July | 5:44 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-04 10:06 | 44KV PEMATANG MAIN - RANGAU LINE | Bekasap | PGT North | Fair | Others | 286 | 10:06 Manual Open 13.8 kV VCB fdr #1 RANGAU Subst., closed at 15:22 Currently Rangau fdr #1 also supplied for Rangau fdr #2. 10:08 Manual Open 44 kV GCB #2 PMT Main (line to RANGAU), closed at 15:19 Purposed to support production team job to: - change out block valve discharge booster pump - change out bypass valve Rangau DS Cause: Others (other team request) Production Loss: Rangau fdr #1 : 26 Bbls, 4 Wells. Rangau fdr #2 : 260 Bbls, 17 Wells. ------------------------------------------+ TOTAL : 286 Bbls, 21 Wells. | 1
42 | 2020-07-22 05:44 | July | 5:44 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-04 10:07 | 13.8KV 8D FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 59 | 10:07 Manual Open VCB 8D fdr #1, closed at 11:05 (MTCE team to c/o broken pin insulator o/p 8E-133) Cause: Planned Maintenance | 1
43 | 2020-07-22 06:15 | July | 6:15 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-04 14:58 | 13.8KV 8D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 37 | 14:58 Manually Open 8D VCB fdr #2, closed at 15:30 (MTCE team to cut high trees near location 8E-45N) Cause: Planned Maintenance | 1
44 | 2020-07-22 06:15 | July | 6:15 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-08-04 08:35 | 13.8KV RANGAU FEEDER #1 | Bekasap | PGT North | Fair | Unidentified | 0 | Rangau fdr #1 (currently also supplied Rangau fdr #2) load dropped 145 A (223 - 78 A) Not Checked Yet | 1
| 2020-07-22 06:15 | July | 6:15 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-09-04 16:21 | 13.8KV RANGAU FEEDER #1 | Bekasap | PGT North | Fair | Unidentified | 0 | Checked and found RCL 23-BD-01 T/R 5x, Ctr: 425 - 430, R/F: None Patrolled the line but found nothing Cause : Unidentified | 1
45 | 2020-07-22 06:15 | July | 6:15 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-08-04 16:26 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Cloudy | Broken Fuse Cut Out | 18 | 8D OCB feeder#5 T/R 1x. Not checked yet. | 1
| 2020-07-22 07:39 | July | 7:39 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-12-04 08:27 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Cloudy | Broken Fuse Cut Out | 18 | Checked and found 8D OCB fdr:#5 T/R 1x Ctr:314-315 R/F:50@2,@3. Patrolled the line found @2@3 broken fuse cut out o/p 8E-07. Cause: Broken Fuse Cut Out. | 1
46 | 2020-07-22 07:39 | July | 7:39 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-08-04 17:37 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 53 | Menggala VCB fdr#2 T/R 1x. Menggala GFPC T/R 1x. Not checked yet. | 1
| 2020-07-22 11:33 | July | 11:33 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-09-04 12:48 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 53 | Checked and found MGL VCB fdr #1 T/R 1x, Counter : 566 - 567, R/F : 51N GFPC of MGL Subst. T/R 1x, Counter : 140 - 141 Patrolled the line found but found nothing Cause : Unidentified | 1
47 | 2020-07-22 12:47 | July | 12:47 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-10-04 11:05 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Dead End Insulator | - | Checked and found DCM VCB feeder #1, ctr: 154-155, R/F: 51N Patrolled the line and found broken dead end on @1 o/p KT-54 Cause : Dead End Insulator | 1
48 | 2020-07-22 14:49 | July | 14:49 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-09-04 13:50 | 13.8KV PUNGUT FEEDER #1 | Bekasap | PGT North | Cloudy | Planned Maintenance | 60 | 13:50 Manual open Recl 45 BP 09 D/S Pungut Fdr#1 Install New L/A o/p 44 DN 01 Requested By Team TOPI. 15:50 Block and Closed Recl 45 BP 09 and then release the Block. Cause: Planned Maintenance. | 1
49 | 2020-07-22 15:12 | July | 15:12 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-09-04 14:21 | 13.8KV 8D FEEDER #10 | Minas | PGT South | Cloudy | Planned Maintenance | 0 | 14:21 Manually open LBS 7E-54 D/S 8D Fdr# 10. Due to repair Hot spot at Recl 63-23A by Mtce Team. 15:27 Manually closed LBS 7E-54. Cause: Planned Maintenance. | 1
50 | 2020-07-22 15:12 | July | 15:12 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-10-04 09:42 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Fair | Planned Maintenance | 0 | 09:42 Manual open LBS 7E-40A D/S Minas Fdr # 6 to Repair Hot Spot at LBS 7E-67 A. 10:37 Close LBS 7E-40A. Cause: Planned maintenance. | 1
51 | 2020-07-22 15:13 | July | 15:13 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-10-04 10:05 | 13.8KV 8D FEEDER #10 | Minas | PGT South | Fair | Planned Maintenance | 0 | 10:05 Manual open LBS 7E-86 D/S 8D feeder #10. to Repair Hot Spot. Recl 6E-23A. 10:50 Close LBS. Cause: Planned maintenance. | 1
52 | 2020-07-22 15:13 | July | 15:13 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-10-04 16:35 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 20 | 16:35 Manual Open Recl 29 Y 21 D/S Bangko feeder #1 Due to repair Hot Spot on Take of pole Bangko # 161. 16:55 Block and Closed Recl 29 Y 21.and then released the block. Cause: Planned maintenance. | 1
53 | 2020-07-22 15:13 | July | 15:13 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-11-04 07:22 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Lightning | 174 | C.Duri ACB fdr#2 T/R 1x Ctr:401-402 R/F :51@1@2. Not patrolled yet. | 1
| 2020-07-22 15:13 | July | 15:13 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-12-04 12:03 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Lightning | 174 | Checked and found C.Duri ACB fdr#2 T/R 1x Ctr:402-403 R/F:51@1. Patrolled the line found @1 Broken LA o/p 10 3 H. @3 Broken Pin Insulator o/p SCC 20 Cause : Lightning. | 1
54 | 2020-07-22 15:26 | July | 15:26 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-11-04 07:53 | DARLING SUBSTATION | Duri | PGT North | Fair | Under investigation | 163 | 07:53 115Kv Darling GCB#1 T/O. 115Kv Darling GCB#3 T/O. Darling fdr#6, fdr#7, fdr#8 no power. 08:40 Checked & found 115Kv Darling GCB#1 T/O Ctr:201-202 R/F:51G. 115Kv Darling GCB#3 T/O Ctr:112-113. 08:44 Opened Darling fdr#6, then Closed at 09:00. Opened Darling fdr#7, then Closed at 09:00. Opened Darling fdr#8, then Closed at 09:00. 08:50 Closed 115Kv Darling GCB#1. Closed 115Kv Darling GCB#3. Cause: Under investigation 09:31 115Kv Darling GCB#1 T/O. 115Kv Darling GCB#3 T/O. Darling fdr#6, fdr#7, fdr#8 no power. 09:50 Manually Opened N.Duri fdr#7, then closed at 11:35. Manually Opened N.Duri fdr#8, then closed at 11:30. 09:55 Checked & found 115Kv Darling GCB#1 T/O Ctr:202-203 R/F:51G.. 115Kv Darling GCB#3 T/O Ctr:113-114. 10:00 Opened Darling fdr#6, then Closed at 11:10. Opened Darling fdr#7, then Closed at 11:12. Opened Darling fdr#8, then Closed at 11:13. 10:57 Closed 115Kv Darling GCB#1. 10:58 Closed 115Kv Darling GCB#3. Cause: Under investigation. | 1
55 | 2020-07-22 15:26 | July | 15:26 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-11-04 08:14 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | 131 | So.Balam VCB feeder#4 T/R 1x. So.Balam GFPC T/R 1x. Not checked yet. | 1
| 2020-07-23 06:34 | July | 6:34 | Morning | Thursday | Weekdays | 23 | 2020 | 14-04-2020 07:23 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | 131 | Checked and found SBLM VCB fdr #4 T/R 1x, Ctr : 385 - 385, R/F : 51N Patrolled the line found but found nothing Cause : Unidentified | 1
56 | 2020-07-23 08:30 | July | 8:30 | Morning | Thursday | Weekdays | 23 | 2020 | 2020-11-04 09:00 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 29 | 09:00 Manually open 6DN OCB feeder #2. due to replace broken pin insulator near location 5E-91. 12:26 Manually blocked and closed 6DN OCB feeder #2, and then released the block. Cause : Planned Maintenance. | 1
57 | 2020-07-23 11:16 | July | 11:16 | Morning | Thursday | Weekdays | 23 | 2020 | 2020-11-04 12:05 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Fair | Planned Maintenance | 72 | 12:05 Open LBS 04-01-01 d/s C.Duri feeder #9. Repair curation pole 04-0-13. 14:31 Closed LBS 04-01-01. Cause: Plain maintenance. | 1
58 | 2020-07-23 13:04 | July | 13:04 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-11-04 14:28 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 14:28 S/U MGT#8, then on line the unit at 15:04. (Running Test) | 1
59 | 2020-07-23 16:19 | July | 16:19 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-12-04 09:39 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Lightning | 74 | Sintong VCB feeder#2 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. | 1
| 2020-07-23 16:19 | July | 16:19 | Afternoon | Thursday | Weekdays | 23 | 2020 | 16-04-2020 14:50 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Lightning | 74 | Checked and found: VCB Sintong Feeder 2 T/R 1X counter: 514-515, R/F : 51N, Sintong GFPC T/R 4X counter: 1226-1230 R/F : 51N, Patrolled and found broken pin insulator on pole 29 AD 07 on phase 3 on Benar main line and normal operation. | 1
60 | 2020-07-23 16:19 | July | 16:19 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-12-04 14:30 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Lightning | Lightning | 49 | Bangko OCB feeder#4 T/R 1x. Bangko GFPC T/R 1x. Not checked yet. | 1
| 2020-07-23 16:27 | July | 16:27 | Afternoon | Thursday | Weekdays | 23 | 2020 | 14-04-2020 07:22 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Lightning | Lightning | 49 | Checked and found BKO OCB fdr #4 T/R, Counter : 82 - 83, Relay Flag : 51N Patrolled the line found : Broken Pin 5% @1 o/p 24-Z-31 Cause : Lightning | 1
61 | 2020-07-23 16:27 | July | 16:27 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-12-04 15:29 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Lightning | 4 | S.Balam fdr #1 load dropped 100A (155-55A). Not checked yet. | 1
| 2020-07-23 17:04 | July | 17:04 | Afternoon | Thursday | Weekdays | 23 | 2020 | 14-04-2020 07:35 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Lightning | 4 | Checked and found: 16-Z-25 T/R 1x, Counter : 101 - 102, Relay Flag : NONE Patrolled the line but found nothing Cause : Lightning | 1
62 | 2020-07-23 17:04 | July | 17:04 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-04-13 06:27 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | - | Sintong feeder #1 load dropped 43 A (102 / 59 A) Sintong GFPC T/R 1x Not Checked Yet | 1
| 2020-07-23 17:10 | July | 17:10 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-04-14 12:48 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | - | Checked and found RCL 25/AD/26 T/R 1x, Counter : 161 / 162, Relay Flag : 51N Patrolled the line and found Broken Fuse Cap bank at STG Subst Cause : Unidentified | 1
63 | 2020-07-23 17:10 | July | 17:10 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-04-13 13:45 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 16 | 13:45 Manually opened Recl. 6D/50 (6DN fdr#2). Replaced Broken FCO on TOP well 6D/56. (6wells Off during the job). 14:33 Blocked & closed Recl 6D/50, then release the block. Cause: Plan Maintenance. | 1
64 | 2020-07-24 06:12 | July | 6:12 | Morning | Friday | Weekdays | 24 | 2020 | 2020-04-13 14:50 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Planned Maintenance | 15 | 14:50 Manually Opened LBS /6/S1/19 (D.Field fdr#4). Replaced 112,5Kva Tx with the same size o/p 06/S1/05. 16:00 Closed LBS 06/S1/19. Cause: Plan Maintenance. | 1
| 2020-07-24 10:38 | July | 10:38 | Morning | Friday | Weekdays | 24 | 2020 | 2020-04-13 14:50 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Unidentified | 5 | 14:50 It was reported No power on road 07/T3. 15:00 Checked & found Recl. 07/T3/02 T/SO Ctr:259/260. Patrolled the line but found nothing. 15:25 Blocked & closed Recl. 07/T3/02, then release the block. Cause: Unidentified. | 1
65 | 2020-07-24 18:06 | July | 18:06 | Afternoon | Friday | Weekdays | 24 | 2020 | 2020-04-13 19:41 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Powerline / Jumper | 1219 | 19:41 CD fdr #16 (currently also supply CD fdr #1) dropped 184 A (148 / 64 A) 19:44 Reported no power at Puncak GS and Kulin area. 21:10 Checked RCL 09/M1/16, position unplug and recloser close 21:25 Checked RCL 09/M4/01, position unplug and recloser close 21:45 Checked RCL 41/AW/62, 39/AV/36 and 38/AS/09, position Normal (close) Crew continue to patrol the power line 23:56 Crew patrol found broken jumper phase @2 at RCL 09/M1/16 waiting MTCE team to close the bypass switch of the recloser 09/M1/16 01:43 Re/plug and manual open RCL 09/M4/01 (for MTCE team working at RCL 09/M1/16 (close bypass switch) 02:05 Block and close RCL 09/M4/01, OK and then unplug again. Continue tomorrow to repair jumper of the recloser 09/M1/16 Cause: Jumper (broken) Production Loss: 8SE 68 wells , Oil loss : 185.8 Bbl 8S 71 wells , Oil loss : 218.6 Bbl 9NE 83 wells , Oil loss : 221.0 Bbl KULIN 60 wells , Oil loss : 286.7 Bbl PUNCAK 18 wells , Oil loss : 132.0 Bbl ____________________________________ Total 300 wells , Oil loss : 1044.1 Bbl | 1
66 | 2020-07-24 18:06 | July | 18:06 | Afternoon | Friday | Weekdays | 24 | 2020 | 2020-04-13 21:10 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Fair | Lightning | 36 | 8C VCB feeder #1 T/R 1x Not Checked Yet | 1
| 2020-07-25 17:07 | July | 17:07 | Afternoon | Saturday | Weekends | 25 | 2020 | 2020-04-16 08:56 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Fair | Lightning | 36 | Checked and found: 8CSB/13.8VCB1 T/R, Counter : 698 / 700, Relay Flag : 51 Patrolled the line found : Not Found Phase : 1, 2, Cause : Lightning | 1
67 | 2020-07-25 17:07 | July | 17:07 | Afternoon | Saturday | Weekends | 25 | 2020 | 2020-04-14 05:20 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | Duri Community VCB fdr #2 T/R 1x Not Checked Yet | 1
| 2020-07-26 09:08 | July | 9:08 | Morning | Sunday | Weekends | 26 | 2020 | 2020-04-19 19:20 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | Checked & found Duri Community ACB fdr#2 T/R 1x Ctr:112/223 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. | 1
68 | 2020-07-27 06:20 | July | 6:20 | Morning | Monday | Weekdays | 27 | 2020 | 2020-04-14 07:22 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 57 | Menggala VCB feeder #2 T/R 1x Not Checked Yet | 1
69 | 2020-07-27 06:20 | July | 6:20 | Morning | Monday | Weekdays | 27 | 2020 | 2020-04-14 08:30 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Fair | Lightning Arrester | 81 | 04:34 C.Duri fdr#5 Load dropped 16A (82/66A). 08:30 It was reported no power at road 03/06 D/S C Duri feeder #5. 09:48 Checked & found Rec; 03/6/03 T/LO Ctr:188/193 R/F:51N. Patrolled the line & found @2 Broken LA o/p 03/6/16B, then isolated. 12:02 Blocked & closed Recl. 03/06/03, then release the block. Cause: Lightning Arrester. | 1
70 | 2020-07-27 06:49 | July | 6:49 | Morning | Monday | Weekdays | 27 | 2020 | 2020-04-14 13:12 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Fair | Tree | 0 | 13:12 Darling VCB fdr#7 T/LO 14:10 Checked & found Darling VCB fdr#7 T/LO Ctr:184/188 R/F:51@1@2. Patrolled the line but found nothing. 14:16 Blocked & closed Darling fdr#7, but failed. Patrolled the line & found Fall Down trees near CGS#5, then icolated. 16:40 Blocked & closed Darling VCB fdr#7, then release the block. Cause: Tree. | 1
71 | 2020-07-27 06:49 | July | 6:49 | Morning | Monday | Weekdays | 27 | 2020 | 2020-04-15 14:33 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Cloudy | Recloser / Control Recloser | 34 | 14:40 C.Duri Fdr # 9 load Dropped 10 A ( 169 / 159A ) 15:45 Checked and found Recl 04/05/02 T/SO Ctr:182/182. Block and closed Recl. 04/05/02, but Fail. 16:53 Blocked & Closed Recl 04/05/02 ( Jumper Control ) Ok unplug The Recl ( Control Failure ) Cause : Control Rec Failure. | 1
72 | 2020-07-27 09:45 | July | 9:45 | Morning | Monday | Weekdays | 27 | 2020 | 2020-04-16 03:54 | NORTH DURI SUBSTATION | Duri | PGT North | Fair | Under investigation | 453 | 03:54 N.Duri 115Kv C/S Tx/12 T/O. 05:15 Checked & found N.Duri 115Kv C/S Tx/12 T/O Ctr:222/223 R/F: Bocholt. Opened N.Duri VCB fdr#4, then closed at 06:33. Opened N.Duri VCB fdr#5, then closed at 06:36. Opened N.Duri VCB fdr#6, then closed at 06:40. Opened N.Duri VCB fdr#7, then closed at 06:41. Opened N.Duri VCB fdr#8, then closed at 06:42. 06:15 Closed N.Duri 115Kv C/S Tx/12. Cause: Under Investigation. | 1
73 | 2020-07-27 14:32 | July | 14:32 | Afternoon | Monday | Weekdays | 27 | 2020 | 2020-04-16 06:39 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Animal | 0 | C.Duri ACB #33 (feeder#7) T/R 1x Ctr:565/566 R/F:51@1. Not patrolled yet. | 1
| 2020-07-28 08:22 | July | 8:22 | Morning | Tuesday | Weekdays | 28 | 2020 | 2020-04-19 18:32 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Animal | 0 | Checked And Found CDRSG ACB33 Fdr #7 Ctr 565/566, R/F 51 Patrolled The Line On 17/Apr/2020 And Found Tupai Mati On Phase @1 Pole 03/5/27 Cause: Animal | 1
74 | 2020-07-29 09:26 | July | 9:26 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-04-16 06:41 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | 0 | Duri Community ACB #25 (feeder#1) T/R 1x. Not checked yet. | 1
| 2020-07-29 10:30 | July | 10:30 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-04-19 19:41 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | 0 | Checked & found Duri Community T/R 1x Ctr:155/156 R/F:51N. Patrolled the line & found @2 Broken LA o/p 3DF6A. Cause : Lightning Arrester. | 1
75 | 2020-07-29 11:06 | July | 11:06 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-04-16 06:42 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | - | Menggala fdr#1 Load dropped 106A (189/83A). Not checked yet. | 1
| 2020-07-29 12:35 | July | 12:35 | Afternoon | Wednesday | Weekdays | 29 | 2020 | 2020-04-16 14:25 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | - | Checked and found: 5440/R.19AN04 T/R, Counter : 823 / 824, Relay Flag : 51N Patrolled the line found : Monkey Dead on FCO Terminal pole Meno#15 Cause : Animal | 1
76 | 2020-07-29 12:35 | July | 12:35 | Afternoon | Wednesday | Weekdays | 29 | 2020 | 2020-04-16 13:38 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain | Lightning | 0 | 13:38 Sintong Fdr # 2 load drop 49 A ( 251/102 A ) Not Checked Yet. | 1
77 | 2020-07-29 14:59 | July | 14:59 | Afternoon | Wednesday | Weekdays | 29 | 2020 | 2020-04-16 14:11 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Rain | Lightning | 0 | 14:11 Bangko Fdr # 4 Load drop 151 A ( 167 / 16 A ) Not Checked Yet. | 1
78 | 2020-07-30 09:15 | July | 9:15 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-04-16 14:11 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Rain | Lightning | 0 | 14:11:01 Bangko Fdr # 4 Load drop 84A ( 202/118A ) Not Checked Yet. | 1
79 | 2020-07-30 10:57 | July | 10:57 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-04-17 06:57 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Fair | Animal | 0 | 06:57 N.Duri Fdr#7 T/R 2X Not Checked Yet. | 1
| 2020-07-31 08:25 | July | 8:25 | Morning | Friday | Weekdays | 31 | 2020 | 2020-04-19 18:32 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Fair | Animal | 0 | Checked And Found NDRSB VCB7 Fdr #7 Ctr 137/140, R/F 51 Patrolled The Line On 17/Apr/2020 And Found Tupai Mati On Phase @1,2, Pole 10 L1 17 Cause: Animal | 1
80 | 2020-07-31 08:25 | July | 8:25 | Morning | Friday | Weekdays | 31 | 2020 | 2020-04-17 08:26 | 13.8KV 8D FEEDER #6 | Minas | PGT South | Fair | Unidentified | 0 | 8D fdr #6 T/R 1X. Not checked yet. | 1
| 2020-07-31 08:49 | July | 8:49 | Morning | Friday | Weekdays | 31 | 2020 | 2020-04-20 07:25 | 13.8KV 8D FEEDER #6 | Minas | PGT South | Fair | Unidentified | 0 | Checked and found 8C OCB feeder #6 T/R 1x. Counter: 2066/2067 R/F : 51N. Patrolled the line found nothing. Cause: Unidentified. | 1
81 | 2020-07-31 20:56 | July | 20:56 | Night | Friday | Weekdays | 31 | 2020 | 2020-04-17 10:27 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Fair | Emergency | 0 | 10:27 Manuall Open Nella fdr #2. (Req, from TL FON Bangko due to 24" production line leakage). 12:35 Blocked & closed Nella fdr#2, then release the block. Cause: Emergency. | 1
82 | 2020-07-31 20:56 | July | 20:56 | Night | Friday | Weekdays | 31 | 2020 | 2020-04-17 10:35 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 10:35 S/U CGT#4, then on line the uit at 10:53. 10:50 Opened Tie Breaker ACB #39. | 1
83 | 2020-08-13 11:09 | August | 11:09 | Morning | Thursday | Weekdays | 13 | 2020 | 2020-04-17 10:36 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Fair | Planned Maintenance | 0 | 10:36 Manuall Open Recl. 2D/33 (3D fdr #4.) Cut high trees under Recl. 2D/33. 16:06 Blocked & closed Recl 2D/33, then release the block. Cause: Plan Maintenance | 1
84 | 2020-08-13 17:28 | August | 17:28 | Afternoon | Thursday | Weekdays | 13 | 2020 | 2020-04-17 10:39 | 13.8KV 8D FEEDER #11 | Minas | PGT South | Fair | Planned Maintenance | 49 | 10:39 Manually Opened 8D fdr #11. Replaced 300Kva Tx with the same size at well 8E/64. 11:04 Blocked & closed 8D fdr#11, then release the block. Cause: Plan maintenance. | 1
85 | 2020-08-13 17:28 | August | 17:28 | Afternoon | Thursday | Weekdays | 13 | 2020 | 2020-04-17 11:16 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | Off line CGT#5, then S/D the unit for S/B. | 1
86 | 2020-08-13 22:14 | August | 22:14 | Night | Thursday | Weekdays | 13 | 2020 | 2020-04-17 14:40 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | CGT#3 Trip By Alarm Exhaust Thermocouple Trip. | 1
87 | 2020-08-13 22:14 | August | 22:14 | Night | Thursday | Weekdays | 13 | 2020 | 2020-04-17 17:50 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | S/U CGT#5, then on line the unit at 18:02. | 1
88 | 2020-08-14 06:12 | August | 6:12 | Morning | Friday | Weekdays | 14 | 2020 | 2020-04-18 08:56 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Planned Maintenance | 89 | 08:56 Manually open Recl 08/M3/38 Repair Hot Spot on pole 10 3H | 1
89 | 2020-08-14 06:12 | August | 6:12 | Morning | Friday | Weekdays | 14 | 2020 | 2020-04-18 09:20 | MINAS POWER PLANT | Minas | PGT South | Fair |  | - | 09:20 Start Up MGT # 4 and then online the unit at 09:35. | 1
90 | 2020-08-14 07:18 | August | 7:18 | Morning | Friday | Weekdays | 14 | 2020 | 2020-04-18 17:00 | 13.8KV 6D FEEDER #1 | Minas | PGT South | Rain and Lightning | Unidentified | 26 | 17:00 6D Fdr #1 Load Drop 127 A ( 164/37A) Not Checked yet. | 1
| 2020-08-14 07:18 | August | 7:18 | Morning | Friday | Weekdays | 14 | 2020 | 2020-04-21 11:56 | 13.8KV 6D FEEDER #1 | Minas | PGT South | Rain and Lightning | Unidentified | 26 | Checked and found: 5442/R.5C42 None, Counter : 166 / 166, Relay Flag : NONE Patrolled the line found : Not Found Cause : Unidentified | 1
91 | 2020-08-14 07:37 | August | 7:37 | Morning | Friday | Weekdays | 14 | 2020 | 2020-04-18 17:00 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 0 | 17:00:01 6D Fdr # 2 Load drop 142 A ( 170/ 28A ) Not Checked yet. | 1
| 2020-08-14 11:43 | August | 11:43 | Morning | Friday | Weekdays | 14 | 2020 | 2020-04-22 08:11 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 0 | Checked and found: 5442/R.6D78A T/R, Counter : 237 / 240, Relay Flag : NONE. Patrolled the line found : Not Found Cause : Lightning | 1
92 | 2020-08-14 11:43 | August | 11:43 | Morning | Friday | Weekdays | 14 | 2020 | 2020-04-18 18:00 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 28 | 18:00 Nella Fdr# 2 T/R 1X Nella fdr#1 Load dropped 121A (210/79A). 18:20 Nella Fdr# 2 T/R 2X again Not checked yet. | 1
93 | 2020-08-14 13:18 | August | 13:18 | Afternoon | Friday | Weekdays | 14 | 2020 | 2020-04-18 18:24 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain and Lightning | Lightning | 31 | Bekasap 13.8Kv ACB fdr #3 T/R 1x. Bekasap feeder #5 load dropped 242A (248/6A). Bekasap feeder #6 load dropped 32A (77/45A). Not checked yet. | 1
| 2020-08-14 13:18 | August | 13:18 | Afternoon | Friday | Weekdays | 14 | 2020 | 2020-04-19 18:54 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain and Lightning | Lightning | 31 | Checked & found Bekasap fdr#3 T/R 1x CTr;99593/99594 R/F:51@2. Patrolled the line & found @2 Flashed Over LA o/p 37BE67, Cause : Lightning. | 1
94 | 2020-08-15 17:09 | August | 17:09 | Afternoon | Saturday | Weekends | 15 | 2020 | 2020-04-18 18:35 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Heavy Rain | Animal | 27 | Ketigul fdr #2 T/R 1X. Not checked yet. | 1
| 2020-08-15 17:09 | August | 17:09 | Afternoon | Saturday | Weekends | 15 | 2020 | 2020-04-21 07:04 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Heavy Rain | Animal | 27 | Checked and found: PKTGL/13.8VCB2 T/R, Counter : 383 / 384, Relay Flag : 51 Patrolled the line found : Ditemukan Ada Monyet mati dekat Well Pad Cause : Animal | 1
95 | 2020-08-15 17:09 | August | 17:09 | Afternoon | Saturday | Weekends | 15 | 2020 | 2020-04-18 19:06 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Rain and Lightning | Pin Insulator | 34 | 19:06 Pematang 13.8Kv OCB fdr #1 T/R 1x. Pematang feeder #2 load dropped 70A (108/70A). 19:24 Pematang 13.8Kv OCB fdr #1 T/R 1x again. Not checked yet. | 1
| 2020-08-15 17:09 | August | 17:09 | Afternoon | Saturday | Weekends | 15 | 2020 | 2020-04-19 19:06 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Rain and Lightning | Pin Insulator | 34 | Checked & found Pematang VCB fdr#1 T/R 3x Ctr:189/192 R/F:51@2. Patrolled the line & found @2 Broken Pin Supported o/p 35BC22. Cause : Pin Insulator. | 1
96 | 2020-08-16 12:21 | August | 12:21 | Afternoon | Sunday | Weekends | 16 | 2020 | 2020-04-18 19:37 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Rain and Lightning | Lightning | 62 | Bekasap VCB fdr#6 T/R 1x. Not checked yet. | 1
| 2020-08-16 12:21 | August | 12:21 | Afternoon | Sunday | Weekends | 16 | 2020 | 2020-04-19 19:37 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Rain and Lightning | Lightning | 62 | Checked & found Bekasap VCB fdr#6 T/R 1x Ctr:386/387 F/F:51@1@2. Patrolled the line & found @1@2 Flashed LA o/p 37BE67. Cause : Lightning | 1
97 | 2020-08-17 04:37 | August | 4:37 | Morning | Monday | Weekdays | 17 | 2020 | 2020-04-18 20:14 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Rain and Lightning | Lightning | 61 | NKB fdr#2 T/R 1x. NKB GFPC T/R 1x. Not checked yet. | 1
| 2020-08-17 04:37 | August | 4:37 | Morning | Monday | Weekdays | 17 | 2020 | 2020-04-21 07:29 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Rain and Lightning | Lightning | 61 | Checked and found: NKBKSB/13.8OCB2 T/R, Counter : 99936 / 99938, Relay Flag : 50N. Patrolled the line found : NOT FOUND Cause : Lightning | 1
98 | 2020-08-17 07:55 | August | 7:55 | Morning | Monday | Weekdays | 17 | 2020 | 2020-04-18 20:57 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Tree | 67 | Pematang VCB fdr#2 T/R 2x. Not checked yet. | 1
| 2020-08-17 14:58 | August | 14:58 | Afternoon | Monday | Weekdays | 17 | 2020 | 2020-04-19 20:57 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Tree | 67 | Checked And Found PMTSB OCB2 Fdr #2 T/R 3 x, Ctr 554/557, R/F 51 Patrolled The Line On 19/Apr/2020 And Found Temuan Pohon Sawit Phase B Dan C Terdekat Jalan Besar Simpang Rangau Ke Pematang On Phase @2,3, Pole 34 Bc 92 Cause: Tree | 1
99 | 2020-08-17 17:45 | August | 17:45 | Afternoon | Monday | Weekdays | 17 | 2020 | 2020-04-19 02:13 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Petko | PGT South | Rain and Lightning | Emergency | 0 | 02:13 Manually opened CKBS gfr#6. Requested KB GS to maintained Tank Level. 12:05 Block & closed CKBS fdr#6, then release the block. Cause: Emergency | 1
100 | 2020-08-17 17:45 | August | 17:45 | Afternoon | Monday | Weekdays | 17 | 2020 | 2020-04-19 06:07 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Rain and Lightning | Emergency | 0 | 06:07 Manually Opened CKBS fdr#5. Requested KB GS for Maintained Tank Level. 09:29 Blocked & closed CKBS fdr#5, then release the block. Cause: Emergency. | 1
101 | 2020-08-17 18:36 | August | 18:36 | Afternoon | Monday | Weekdays | 17 | 2020 | 2020-04-19 06:44 | 13.8KV CENTRAL DURI FEEDER #8 | Duri | PGT North | Fair | Recloser / Control Recloser | 16 | 06:44 C.Duri fdr#8 Load dropped 39A (229/190A). 07:30 It was reported No Power at Css/4. 09:14 Checked & found Recl. 04/06/40 T/SO Ctr:153/154 R/F:51@1@2@3. Patrolled the line & found Dead Monkey o/p 04/06/15. 09:46 Closed Recl. 04/06/40 and Unplug Cable Control . Cause: Control Recloser. | 1
102 | 2020-08-17 18:36 | August | 18:36 | Afternoon | Monday | Weekdays | 17 | 2020 | 2020-04-19 10:00 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 69 | 10:00 Manually open 6DN feeder #1. Replaced broken dead end insulator o/p 36/DN/38 & 5D/14. 11:12 Closed 6DN feeder #1. Cause: Plain maintenance. | 1
103 | 2020-08-18 06:22 | August | 6:22 | Morning | Tuesday | Weekdays | 18 | 2020 | 2020-04-19 13:15 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 0 | Bangko feeder #4 load dropped 119A (193/74A). Not checked yet. | 1
104 | 2020-08-18 06:22 | August | 6:22 | Morning | Tuesday | Weekdays | 18 | 2020 | 2020-04-19 13:30 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | C.Duri 13.8Kv ACB#28 (fdr#16) T/R 1x. R/f 51N @1,2 Counter :574/575. Not checked yet. | 1
| 2020-08-18 07:00 | August | 7:00 | Morning | Tuesday | Weekdays | 18 | 2020 | 2020-04-21 07:48 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | Checked and found: CDRSG/13.8ACB28 T/R, Counter : 574 / 575, Relay Flag : 51N. Patrolled the line found : No Finding Cause : Unidentified | 1
105 | 2020-08-18 07:27 | August | 7:27 | Morning | Tuesday | Weekdays | 18 | 2020 | 2020-04-19 13:30 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Rain and Lightning | Lightning | 0 | C.Duri 13.8Kv ACB#33 (fdr#7) T/R 1x. R/f others Counter:566/567. C.Duri feeder #5 load dropped 16A (78/62A). C.Duri feeder #8 load dropped 15A (229/214A). C.Duri feeder #9 load dropped 38A (178/140A). Not checked yet. | 1
| 2020-08-18 14:52 | August | 14:52 | Afternoon | Tuesday | Weekdays | 18 | 2020 | 2020-04-21 07:15 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Rain and Lightning | Lightning | 0 | Checked and found: CDRSG/13.8ACB33 T/R, Counter : 566 / 567, Relay Flag : 51N. Patrolled the line found : LA Broken Cause : Lightning | 1
106 | 2020-08-19 10:00 | August | 10:00 | Morning | Wednesday | Weekdays | 19 | 2020 | 2020-04-19 13:30 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | C.Duri feeder #1 load dropped 100A (140/40A). Checked and found C. Duri fdr #1 T/R 1X R/F: 51G, 51@1 &@2 ctr:287/288. Not checked yet. | 1
| 2020-08-19 13:28 | August | 13:28 | Afternoon | Wednesday | Weekdays | 19 | 2020 | 2020-04-22 15:00 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Unidentified | 0 | Checked and found: CDRSG/13.8ACB11 T/R, Counter : 287 / 288, Relay Flag : 51 Patrolled the line found : No Findings Cause : Unidentified | 1
107 | 2020-08-19 13:48 | August | 13:48 | Afternoon | Wednesday | Weekdays | 19 | 2020 | 2020-04-19 13:30 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Lightning Arrester | 0 | C.Duri feeder #2 load dropped 82A (199/117A). Checked and found C. Duri fdr #2 T/R 1X R/F: 51N, 51G ctr: 403/404. Not checked yet. | 1
| 2020-08-19 13:48 | August | 13:48 | Afternoon | Wednesday | Weekdays | 19 | 2020 | 2020-04-22 15:00 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Rain and Lightning | Lightning Arrester | 0 | Checked and found: 5441/R.08/M3/38 T/R, Counter : 159 / 160, Relay Flag : NONE. Patrolled the line found : LA Broken Operated Device : CDRSG/13.8ACB12 T/R Counter : 403 / 404 Relay Flag : 51N Finding Patrol : LA Broken Phase : 1 Pole : SAA 14 Patrol by : Edi dan Ade Input by : SIHN Cause : Lightning Arrester | 1
108 | 2020-08-19 14:33 | August | 14:33 | Afternoon | Wednesday | Weekdays | 19 | 2020 | 2020-04-19 13:46 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 40 | Menggala feeder #2 load dropped 150A (156/6A). Menggala feeder #1 load dropped 14A (176/162A). Menggala GFPC T/R 1x. Not checked yet. | 1
109 | 2020-08-19 14:33 | August | 14:33 | Afternoon | Wednesday | Weekdays | 19 | 2020 | 2020-04-19 14:03 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 25 | 14:03 Pinang 13.8Kv OCB fdr#1 T/R. 14:05 Pinang 13.8Kv OCB fdr#1 T/R. (Again). 14:09 Pinang 13.8Kv OCB fdr#1 T/R. (Again). 14:13 Pinang 13.8Kv OCB fdr#1 T/R. (Again). Not checked yet. | 1
| 2020-08-20 06:45 | August | 6:45 | Morning | Thursday | Weekdays | 20 | 2020 | 2020-04-21 14:32 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 25 | Checked and found: PNGSB/13.8OCB1 T/R 4x Ctr:458/462 R/F: 51N Patrolled the line & found @2 Broken Pin Insulator o/p 11D12. @1@2 Broken Dead End Insulator o/p 12F2. @2 Broken Jumper on TOP Pinang#37. Cause: Lightning. | 1
110 | 2020-08-20 08:59 | August | 8:59 | Morning | Thursday | Weekdays | 20 | 2020 | 2020-04-19 14:05 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 0 | S.Balam feeder #4 load dropped 40A (209/199A). Not checked yet. | 1
111 | 2020-08-20 08:59 | August | 8:59 | Morning | Thursday | Weekdays | 20 | 2020 | 2020-04-19 14:34 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Fair | Planned Maintenance | 7 | 14:34 Manually open 8C OCB feeder #4. Due to replaced broken dead and insulator o/p M8C/18. 14:56 Manually block and closed 8C OCB feeder #4, and then released the block. Cause: Planned maintenance. | 1
112 | 2020-08-21 06:56 | August | 6:56 | Morning | Friday | Weekdays | 21 | 2020 | 2020-04-20 10:34 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Tree | 0 | CKBS VCB feeder#1 T/R 1x. Not checked yet. | 1
| 2020-08-21 06:56 | August | 6:56 | Morning | Friday | Weekdays | 21 | 2020 | 2020-04-22 14:46 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Tree | 0 | Checked and found: CKBSSB/13.8VCB1 T/R, Counter : 247 / 249, Relay Flag : 51. Patrolled the line found : High Palm Trees Cause : Tree | 1
113 | 2020-08-21 09:34 | August | 9:34 | Morning | Friday | Weekdays | 21 | 2020 | 2020-04-20 10:53 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 0 | 10:53 Manually opened 8C OCB feeder #1. Due to replace broken Dead End Insulator on pole 9D/13 11:57 Manually blocked an closed 8C OCB feeder #1, and then released the block. Cause : Planned Maintenance. | 1
114 | 2020-08-22 06:49 | August | 6:49 | Morning | Saturday | Weekends | 22 | 2020 | 2020-04-20 11:04 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Fair | Planned Maintenance | 58 | 11:04 Manually opened Pematang OCB feeder #1. 11:05 Manually opened Rangau OCB feeder#2. 11:14 Manually opened Pematang OCB feeder #2. Due to replace @2 broken Pin Insulator on pole 35/BJ/22. 11:21 Manually blocked and closed Pematang OCB feeder #1 //> OK and then released the block. 11:45 Manually blocked and closed Rangau OCB feeder #2 //> OK and then released the block. 11:47 Manually blocked and closed Pematang OCB feeder #2 //> OK and then released the block. Cause : Planned maintenance. | 1
115 | 2020-08-22 12:44 | August | 12:44 | Afternoon | Saturday | Weekends | 22 | 2020 | 2020-04-20 14:45 | KETIGUL SUBSTATION | Bangko-Balam | PGT North | Fair | Unidentified (L/A) | 305 | 14:45 115KV Ketigul GCB #1 T/RC 1X. 14:45 115KV Ketigul GCB #2 T/SO. 14:45 115KV Rokan GCB #11 T/SO. Pinang fdr #1 load dropped 9A (102/93A). Nella fdr #1 load dropped 37A (212/175A). Nella fdr #2 load dropped 8A (59/51A). Bangko fdr #1 Load dropped 20A (163/143A). Bangko fdr #4 Load dropped 34A (198/164A). Sintong fdr #2 load dropped 17A (240/223A). S. Balam fdr #1 load dropped 26A (154/128A). S. Balam fdr #3 load dropped 34A (140/106A). S. Balam fdr #4 load dropped 27A (214/187A). Menggala fdr #1 load dropped 59A (189/130A). Menggala fdr #2 load dropped 39A (154/115A). Batang fdr #2 load dropped 12A (46/34A). Ketigul fdr #1 load dropped 48A (126/78A). Ketigul fdr #2 load dropped 18A (73/55A). Ketigul fdr #3 load dropped 8A (43/35A). Bekasap fdr #5 load dropped 19A (248/229A). Pematang fdr #1 load dropped 167A (197/30A). Pematang fdr #2 load dropped 93A (106/13A). Rangau fdr #1 load dropped 42A (61/19A). Rangau fdr #2 load dropped 141A (145/4A). Petani fdr #1 load dropped 229A (238/9A). Petani fdr #2 load dropped 65A (67/2A). Rokan fdr #2 load dropped 23A (23/0A). Rokan fdr #4 load dropped 15A (18/3A). 16:16 Checked and found 115 kV Rokan GCB # 11 T/SO R/F 87L , 21G. 16:36 Checked and Found 115 kV Ketigul GCB # 1 T/R R/F 87L , 21G Counter 207 / 208. Checked and Found 115 kV Ketigul GCB # 2 T/SO R/F 87L , 21G Counter 182 / 183. 16:45 Function test Rokan GCB # 11 but fail. 19:50 Closed 115Kv GCB #11 at Rokan. 20:11 Closed 115Kv GCb #2 at Ketigul. Cause: Under Investigation. | 1
| 2020-08-22 17:00 | August | 17:00 | Afternoon | Saturday | Weekends | 22 | 2020 | 2020-04-21 13:55 | KETIGUL SUBSTATION | Bangko-Balam | PGT North | Fair | Unidentified (L/A) | 305 | Patrolled the line but found nothing. Cause : Unidentified (L/A) | 1
| 2020-08-22 17:00 | August | 17:00 | Afternoon | Saturday | Weekends | 22 | 2020 | 2020-03-05 00:58 | KETIGUL SUBSTATION | Bangko-Balam | PGT North | Fair | Unidentified (L/A) | 305 | Checked And Found: / KTGL/115GCB1 Fdr #1 T/R 1 x, Ctr 207/208, R/F 87 / KTGL/115GCB2 Fdr #2 T/SO Ctr 182/183, R/F 87 / RKN/115GCB11 Fdr #11 Ctr 39/39, R/F 87 Patrolled The Line On 20/Apr/2020 And Found Record R/F 87L , 21G Dan 51N, Tidak Ada Temuan Baru Dilapangan Kondisinya Hujan Dan Petir. Kondisi Breaker Open, Counter Tidak Berubah. Cause: Unidentified (L/A) | 1
116 | 2020-08-22 17:01 | August | 17:01 | Afternoon | Saturday | Weekends | 22 | 2020 | 2020-04-20 16:45 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 0 | N.Duri VCB feeder#2 T/R 1X. Not Checked yet. | 1
| 2020-08-23 08:09 | August | 8:09 | Morning | Sunday | Weekends | 23 | 2020 | 2020-04-24 07:11 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found: NDR VCB fdr #2 T/R 1x, Counter : 289 / 290, R/F: 51P @1 Patrolled the line but found nothing Cause : Unidentified | 1
117 | 2020-08-23 08:09 | August | 8:09 | Morning | Sunday | Weekends | 23 | 2020 | 2020-04-21 16:43 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Rain | Dead End Insulator | 35 | Pematang OCB feeder#1 T/R 1x Not checked yet. | 1
| 2020-08-23 16:02 | August | 16:02 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-24 16:52 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Rain | Dead End Insulator | 35 | Checked and found: PMTSB/13.8OCB1 T/R, Counter : 193 / 194, Relay Flag : 51N Patrolled the line found : Dead End Pecah Cause : Dead End Insulator | 1
118 | 2020-08-23 16:02 | August | 16:02 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-21 17:02 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Dead End Insulator | 62 | Pematang OCB feeder#2 T/R 1x Not checked yet. | 1
| 2020-08-23 16:18 | August | 16:18 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-24 17:08 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Dead End Insulator | 62 | Checked and found Pematang OCB feeder #2 T/R 4x. Counter: 582/562 R/F: 51N. Patrolled the line found @3 flash oer Dead end Insulator on pole 34/BB/26. Cause: Dead End Insulator. | 1
119 | 2020-08-23 16:18 | August | 16:18 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-22 09:29 | 13.8KV NORTH DURI FEEDER #5 | Duri | PGT North | Cloudy | Dead End Insulator | 0 | ND VCB fdr #5 T/R 1x Not Checked Yet | 1
| 2020-08-23 16:23 | August | 16:23 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-23 13:46 | 13.8KV NORTH DURI FEEDER #5 | Duri | PGT North | Cloudy | Dead End Insulator | 0 | Checked and found: NDRSB/13.8VCB5 T/R, Counter : 159 / 159, Relay Flag : 51N. Patrolled the line found : Broken Dead End layer 1 Cause : Dead End Insulator | 1
120 | 2020-08-23 16:23 | August | 16:23 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-22 11:05 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 13 | 11:05 Manual Open RCL 36DN/32A, closed at 13:46 MTCE team to c/o broken dead end o/p 5D/14 Cause: Planned Maintenance | 1
121 | 2020-08-23 16:29 | August | 16:29 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-22 12:25 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Fair | Planned Maintenance | 51 | 12:25 Manual Open RCL 23/W/02 (Libo fdr #2) MTCE team to dismantle conductor o/p 21/BU/16 (hazard hunt) Cause: Planned Maintenance | 1
122 | 2020-08-23 16:49 | August | 16:49 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-22 13:17 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 319 | 13:17 BKO VCB fdr #4 T/O (on block for PT KRS) 13:31 Manual Close (as per TL TDO order), OK then release the block. 14:58 Reported still no power at BNR GS (from BKO fdr #4) 16:33 Checked and found RCL 25/Z/07 T/SO, ctr: 240 / 241) 16:44 Block and manual close RCL 25/Z/07, OK, then release the block. Cause: Not Patrolled Yet | 1
| 2020-08-23 16:49 | August | 16:49 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-25 09:41 | 13.8KV BANGKO FEEDER #4 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 319 | Checked and found VCB BKO fdr #4 T/R 1x, ctr: 83 / 84, R/F: 51N Patrolled the line and found broken pin insulator phase 1 o/p 24/Y/31 Cause : Lightning | 1
123 | 2020-08-23 16:52 | August | 16:52 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-22 13:17 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 900 | 13:17 BKO VCB fdr #1 T/SO 13:33 Blocked and manual close BKO VCB fdr #1 (as per TL TDO order) 17:30 the load still dropped 65 A 17:54 checked and found RCL 23/X/08 T/So, ctr: 425 / 426 18:03 Block and close RCL 23/X/08, Ok then release the block Cause: Not Patrolled Yet | 1
| 2020-08-23 16:52 | August | 16:52 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-23 17:17 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 900 | Checked and found BKO VCB fdr #1 T/SO, Counter : 87 / 88, Relay Flag : 51N Patrolled the line and found RCL 23/X/08 T/SO Counter : 425 / 426 Patrolled the line d/s of RCL but found nothing Cause : Lightning | 1
124 | 2020-08-23 17:04 | August | 17:04 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-22 13:27 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 132 | 13:27 Nella VCB fdr #2 T/SO Nella fdr #1 load dropped 99 A (207 / 108 A) 14:55 Checked and found VCB Nella fdr #2 T/SO, ctr: 364 / 365, R/F: 51P @1 and @3, closing spring at discharge position 15:00 Troubleshoot and manual crank the closing spring of VCB Nella fdr #2 15:13 Block and manual close VCB Nella fdr #2, Ok then release the block. the closing spring back to normal after close. Cause: Not Patrolled Yet | 1
| 2020-08-23 17:04 | August | 17:04 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-23 14:46 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 132 | Checked and found NLA VCB fdr #2 T/SO, Counter : 364 / 365, Relay Flag : 51N Patrolled the line but found nothing, Closing Spring of VCB Status Discharge Cause : Lightning | 1
125 | 2020-08-23 17:27 | August | 17:27 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-22 13:30 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 42 | Ketigul VCB fdr #1 T/R 1x Ketigul fdr #2 load dropped 71 A (252 / 181 A) Ketigul fdr #3 load dropped 35 A (43 / 8 A) Not Checked Yet | 1
| 2020-08-23 17:27 | August | 17:27 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-24 08:41 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 42 | Checked and found KTGL VCB fdr #1 T/R 1x, ctr: 231 / 232, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
| 2020-08-23 17:51 | August | 17:51 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-04-24 08:41 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 42 | Checked and found: PKTGL/13.8VCB1 T/R, Counter : 231 / 232, Relay Flag : 51. Patrolled the line found: : No Findings Cause : Unidentified | 1
126 | 2020-08-24 02:13 | August | 2:13 | Night | Monday | Weekdays | 24 | 2020 | 2020-04-22 13:53 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Transformer Failure | 104 | South Balam VCB fdr #1 T/R 1x South Balam VCB fdr #2 load dropped 67 A (104 / 37 A) South Balam VCB fdr #3 load dropped 100 A (101 / 1 A) South Balam VCB fdr #4 load dropped 143 A (209 / 66 A) Not Checked Yet | 1
| 2020-08-24 02:13 | August | 2:13 | Night | Monday | Weekdays | 24 | 2020 | 2020-04-25 09:36 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Transformer Failure | 104 | Checked and found S. BALAMA VCB fdr #1 T/R 1x, ctr: 413 / 414, R/F: 51N Patrolled the line and found transformer failure at So Balam #364 Cause : Transformer Failure | 1
127 | 2020-08-24 07:38 | August | 7:38 | Morning | Monday | Weekdays | 24 | 2020 | 2020-04-22 14:09 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Rain and Lightning | Lightning | 0 | 14:09 Central Duri feeder #5 load dropped 35 A (80 / 45 A) 14:44 checked and found RCL 03/4/16 T/O (on block for PT WKS) 14:46 Manually close RCL 03/4/16 (CD fdr #5) Not Patrolled Yet | 1
| 2020-08-24 07:38 | August | 7:38 | Morning | Monday | Weekdays | 24 | 2020 | 2020-04-24 16:47 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Rain and Lightning | Lightning | 0 | Checked and found Recloserl : 03/04/16 T/R 1x. Counter: 236/237 R/F: Patrolled the line nothing found. Cause: Suspected Lightning. | 1
128 | 2020-08-24 21:18 | August | 21:18 | Night | Monday | Weekdays | 24 | 2020 | 2020-04-22 16:27 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 9 | 3D VCB fdr #2 T/R 1x Not Checked Yet | 1
| 2020-08-25 09:03 | August | 9:03 | Morning | Tuesday | Weekdays | 25 | 2020 | 2020-04-25 06:31 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 9 | Checked and found 3D OCB feeder #2 T/R 2x. Counter: 377/379 R/F: 50 @2,@3. Patrolled the line nothing found. Cause: Suspected Lightning. | 1
129 | 2020-08-25 09:03 | August | 9:03 | Morning | Tuesday | Weekdays | 25 | 2020 | 2020-04-22 16:27 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Cloudy | Unidentified | 9 | 16:27 reported no power at road 07/T5/xx (DF fdr #2) DF feeder #2 load dropped 8 A (153 / 145 A) 18:01 Checked and found RCL 07/T5/19 T/SO, ctr: 542 / 543 and closing fuse was b/o 18:03 replace the b/o fuse, but the RCL suddenly Close and then T/R 1x, last counter 544 Cause: not patrolled yet | 1
| 2020-08-25 13:50 | August | 13:50 | Afternoon | Tuesday | Weekdays | 25 | 2020 | 2020-04-23 07:11 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Cloudy | Unidentified | 9 | Checked and found: 5441/R.07/T5/19 T/SO, Counter : 542 / 544, Relay Flag : NONE. Patrolled the line found : Tidak Ada Temuan Setelah Patrol di power line, ganti Fuse Closing Control(karena Temuannya Putus) Cause : Unidentified | 1
| 2020-08-25 13:50 | August | 13:50 | Afternoon | Tuesday | Weekdays | 25 | 2020 | 2020-04-23 07:11 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Cloudy | Unidentified | 9 | Checked and found: 5441/R.07/T5/19 T/SO, Counter : 542 / 544, Relay Flag : NONE. Patrolled the line found : Tidak Ada Temuan Setelah Patrol di power line, ganti Fuse Closing Control(karena Temuannya Putus) Cause : Unidentified | 1
130 | 2020-08-25 14:54 | August | 14:54 | Afternoon | Tuesday | Weekdays | 25 | 2020 | 2020-04-22 16:35 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Rain and Lightning | Lightning | 11 | 4D VCB fdr #3 T/R 1x 4D fdr #2 load dropped 131 A (167 / 36 A) 4D fdr #1 load dropped 122 A (126 / 4 A) Not Checked Yet | 1
| 2020-08-25 22:32 | August | 22:32 | Night | Tuesday | Weekdays | 25 | 2020 | 2020-04-25 06:39 | 13.8KV 4D FEEDER #3 | Minas | PGT South | Rain and Lightning | Lightning | 11 | Checked and found 4D OCB feeder #3 T/R 1x. Counter: 298/299 R/F: 51N. Patrolled the line nothing found. Cause: Suspected lightning. | 1
131 | 2020-08-25 23:30 | August | 23:30 | Night | Tuesday | Weekdays | 25 | 2020 | 2020-04-23 13:51 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Heavy Rain | Unidentified | 57 | 13:51 Ketigul VCB fdr #3 T/R 1x Ketigul feeder #2 load dropped 20 A (73 / 53 A) Not Checked Yet | 1
| 2020-08-26 10:00 | August | 10:00 | Morning | Wednesday | Weekdays | 26 | 2020 | 2020-04-24 06:29 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Heavy Rain | Unidentified | 57 | Checked and found Ketigul VCB feeder #3 T/R 1x. Counter : 233/234 R/F: 51N. Patrolled the line but found nothing Cause: Unidentified. | 1
132 | 2020-08-27 09:40 | August | 9:40 | Morning | Thursday | Weekdays | 27 | 2020 | 2020-04-23 14:16 | 13.8KV 4B FEEDER #6 | Minas | PGT South | Rain and Lightning | Lightning | 32 | 14:16 4B VCB feeder #6 T/SO (1x operate) 4B feeder #3 load dropped 61 A (117 / 56 A) // WIP GS/6 4B feeder #4 load dropped 118 A (122 / 4 A) // WIP GS/6 4B feeder #5 load dropped 128 A (137 / 9 A) // WIP GS/6 15:27 Checked and found 4B VCB fdr #6 T/SO, ctr: 197 / 198, R/F: 51P @1 @3, 50P @2 15:41 Block and manual close 4B VCB fdr #6, OK then release the block. Cause: Not Patrolled Yet | 1
| 2020-08-27 10:07 | August | 10:07 | Morning | Thursday | Weekdays | 27 | 2020 | 2020-04-25 17:26 | 13.8KV 4B FEEDER #6 | Minas | PGT South | Rain and Lightning | Lightning | 32 | Checked and found 4B fdr #6 T/SO, ctr: 197 / 198, R/F: 51P @1 #3 and 50P @2 Patrolled the line but found nothing Cause : Lightning | 1
133 | 2020-08-28 10:21 | August | 10:21 | Morning | Friday | Weekdays | 28 | 2020 | 2020-04-23 14:18 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Rain and Lightning | Dead End Insulator | 33 | 4B feeder #1 load dropped 127 A (210 / 73 A) 4B feeder #2 load dropped 10 A (53 / 43 A) Not Checked Yet | 1
| 2020-08-29 09:56 | August | 9:56 | Morning | Saturday | Weekends | 29 | 2020 | 2020-04-25 17:50 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Rain and Lightning | Dead End Insulator | 33 | Checked and found RCL 4B/101 T/R 1x, ctr: 663 / 664, R/F: None Patrolled the line and found broken dead end @2 o/p 3B/15 Cause : Dead End Insulator | 1
134 | 2020-08-29 15:59 | August | 15:59 | Afternoon | Saturday | Weekends | 29 | 2020 | 2020-04-23 14:18 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain | Lightning Arrester | 17 | 14:18 Ketigul VCB fdr #1 T/R 1x 15:00 Reported no power at Tilan Field 17:00 Checked and found RCL 32/AK/16 T/So, ctr: 154 (not change), R/F: None Try to close the RCL but failed (alarm indicator illuminate and fail to reset) Waiting another crew from to for troubleshoot. 18:51 Block Ketigul feeder #1, release at 18:56 18:55 Close RCL 32/AK/16 (by direct trigger), OK and then unplug cable control Not Patrolled Yet | 1
| 2020-08-29 17:18 | August | 17:18 | Afternoon | Saturday | Weekends | 29 | 2020 | 2020-04-24 16:48 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Rain | Lightning Arrester | 17 | Patrolled the line found @1,@2 & @3 broken Lightning Arrester, on pole 31/AN/39A. Cause: Lightning Arrester. | 1
135 | 2020-08-29 17:18 | August | 17:18 | Afternoon | Saturday | Weekends | 29 | 2020 | 2020-04-23 14:56 | 13.8KV 8D FEEDER #10 | Minas | PGT South | Heavy Rain | Lightning | 38 | 8D VCB feeder #10 T/R 1x 8D feeder #11 load dropped 33 A (138 / 95 A) Not Checked Yet | 1
| 2020-08-29 17:58 | August | 17:58 | Afternoon | Saturday | Weekends | 29 | 2020 | 2020-04-27 08:00 | 13.8KV 8D FEEDER #10 | Minas | PGT South | Heavy Rain | Lightning | 38 | Checked and found 8D OCB fdr #10 T/R 1x, ctr: 291/292, R/F: 50P @2 Patrolled the line and found flash over pin insulator @2 o/p MB/13 Cause : Lightning | 1
136 | 2020-08-29 17:58 | August | 17:58 | Afternoon | Saturday | Weekends | 29 | 2020 | 2020-04-24 13:58 | 13.8KV CENTRAL DURI FEEDER #8 | Duri | PGT North | Fair | Powerline / Jumper | 96 | 13:58 It was reported there is unbalance Voltage D/S C.Duri Fdr#8 ( On Road 03/02 and 04/02 ) Checked by electrician on loc 5Q/36B ( 482/478/400 ) 19:20 Patrolled the line and found @3 broken jumper on pole SDD 06. Part load C Duri feeder #8 transfer to C Duri feeder #9 by Opened and Closed : 19:52 Shutoff Recl 04/05/32 and Closed LBS 04/05/25A (C.Duri fdr #9). 20:07 Shutoff Recl 04/02/22 and Closed LBS 04/02/02 (C.Duri fdr #9). 21:26 Shutoff Recl 04/04/22 and Closed LBS 04/04/02 (C.Duri fdr #9). 22:00 Manual open CD # 8. Part load C Duri feeder #8 transfer to C Duri feeder #7 by Closed : 22:08 Closed LBS 03/03/44 (C.Duri fdr #7). Cause: Broken jumper. | 1
| 2020-08-30 01:27 | August | 1:27 | Night | Sunday | Weekends | 30 | 2020 | 2020-04-26 15:27 | 13.8KV CENTRAL DURI FEEDER #8 | Duri | PGT North | Fair | Powerline / Jumper | 96 | Checked And Found CDRSG ACB32 Fdr #32 Ctr 480/480, Patrolled The Line On 26/Apr/2020 And Found Unbalance Load At Phase 3 Conductor Jumper On Pole Sdd 06 Cause: Jumper | 1
137 | 2020-08-30 17:16 | August | 17:16 | Afternoon | Sunday | Weekends | 30 | 2020 | 2020-04-24 17:29 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Tree | 67 | PMT OCB fdr #2 T/R 1x (reclose after 6 minutes) Rangau feeder #2 load dropped 43 A (148 / 105 A) Not Checked Yet | 1
| 2020-08-30 17:16 | August | 17:16 | Afternoon | Sunday | Weekends | 30 | 2020 | 2020-04-26 14:18 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Tree | 67 | Checked and found Pematang OCB fdr #2 T/R 1x. R/F: 51 Counter: 562/563. Patrolled the line and found high tree near pole 34 BC 50 near to PEMATANG 48. Cause : Tree | 1
138 | 2020-08-30 17:47 | August | 17:47 | Afternoon | Sunday | Weekends | 30 | 2020 | 2020-04-24 17:30 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Cloudy | Unidentified | 99 | Petani feeder #1 load dropped 114 A (238 / 124) Not Checked Yet | 1
| 2020-08-31 14:20 | August | 14:20 | Afternoon | Monday | Weekdays | 31 | 2020 | 2020-04-26 13:56 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Cloudy | Unidentified | 99 | Patrolled the line and found nothing. Cause : Unidentified | 1
139 | 2020-08-31 15:00 | August | 15:00 | Afternoon | Monday | Weekdays | 31 | 2020 | 2020-04-24 23:17 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Unidentified | 27 | 23:17 Rangau Fdr# 2 Load drop 134A ( 148 /14A) 01:22 Checked and found Recl 23BD01 T/O ( On Block ) 01:25 Blocked and Closed the Recl / Ok , then release block Not Patrol yet. | 1
140 | 2020-04-25 23:59 | April | 23:59 | Night | Saturday | Weekends | 25 | 2020 | 2020-04-25 23:59 | CPI POWER SYSTEM |  |  |  |  | - | 23:59 CPI Power system Normal. | 1
141 | 2020-04-26 03:28 | April | 3:28 | Night | Sunday | Weekends | 26 | 2020 | 2020-04-26 03:28 | 13.8KV NORTH DURI / DUMAI FEEDER | Duri | PGT North | Rain and Lightning | Tree | - | 03:28 North Duri VCB # 14 T/O. 05:56 Manuall Open N.Duri 44KV GCV #1, Checked and found N. Duri VCB #14 T/O, ctr:167/168 R/F: 51 @1, @3. Transferred to GENSET HCT: 06:00 Manual Open 4160 VCB #1 and rack out 06:05 Manual Open 4160 VCB #2 and rack out 06:07 Manual Open 4160 VCB #13 fdr #2 06:08 Manual Open 4160 VCB #12 fdr #1 06:09 Manual Open 4160 VCB #22 fdr #4 06:10 Manual Open 4160 VCB #23 fdr #5 06:37 Closed ALCO #7 for independent 06:45 Closed VCB #13 fdr #2 to CPS 06:46 Closed VCB #10 Tie Breaker 06:47 Closed VCB #23 fdr #5 Industrial Area 06:48 Closed VCB #22 fdr #4 Housing Area. Normalize 44 kV Line to Dumai and Dumai Substation 07:03 Manual Closed 13.8 VCB #14 North Duri (TX/14 North Duri energized) 07:45 Manual Open VCB #22 fdr #4, closed at 07:58, ctr: 298 07:46 Manual Open VCB #23 fdr #5, closed at 07:59, ctr: 310 07:47 Manual Open VCB #10, tie breaker 07:48 Manual Open VCB #13 fdr #2, closed at 07:57, ctr: 163 07:49 Manual Open VCB #11 (at HCT CPS) 07:54 Manual Close VCB #1, Incoming breaker from TX/1 07:56 Manual Close VCB #2, Incoming breaker from TX/2 08:00 Manual Close VCB #12 fdr #1, ctr: 319 08:02 Manual Close VCB #24 fdr #6, ctr: 021 Cause: Not Patrolled Yet | 1
| 2020-04-26 03:28 | April | 3:28 | Night | Sunday | Weekends | 26 | 2020 | 2020-04-26 09:07 | 13.8KV NORTH DURI / DUMAI FEEDER | Duri | PGT North | Rain and Lightning | Tree | - | Checked And Found NDRSB VCB14 Ctr 167/168, R/F 51 Patrolled The Line On 26/Apr/2020 And Found Fallen Tree On Phase @1,3, Pole Dd 259 Cause: Tree | 1
142 | 2020-04-26 22:27 | April | 22:27 | Night | Sunday | Weekends | 26 | 2020 | 2020-04-26 22:27 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Fair | Others | 0 | 22:27 Minas fdr #4 load dropped 23a (152/129A). 02:39 It was reported Vadnalism at wells: 8D/14, 8D/15, 8D/25 & 8D/13N. Caused: Vandalism. | 1
143 | 2020-04-27 05:10 | April | 5:10 | Morning | Monday | Weekdays | 27 | 2020 | 2020-04-27 05:10 | 4.16KV EAST RUMBAI FEEDER #1 | Rumbai | PGT South | Rain and Lightning | Lightning | 0 | 05:10 East Rumbai feeder #1 T/R 1X. 13:21 Checked and found VCB East RBI fdr #1 T/R 1x Counter: 581 / 582, R/F: 51P Patrolled the line but found nothing Cause: Suspect Lightning. | 1
144 | 2020-04-27 09:30 | April | 9:30 | Morning | Monday | Weekdays | 27 | 2020 | 2020-04-27 09:30 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Cloudy | Animal | 114 | CKB VCB feeder #5 T/R 1x. Not checked yet. | 1
| 2020-04-27 09:30 | April | 9:30 | Morning | Monday | Weekdays | 27 | 2020 | 2020-04-30 08:24 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Cloudy | Animal | 114 | Checked And Found CKBS VCB5 Fdr #5 Ctr 179/180, R/F 51 Patrolled the line and found dead Owl at location KB/01. Cause: Animal. | 1
145 | 2020-04-27 09:38 | April | 9:38 | Morning | Monday | Weekdays | 27 | 2020 | 2020-04-27 09:38 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 40 | 09:38 Switching to shut down Sintong feeder #1, (with Operating Procedure). 09:52 Manually opened Sintong VCB feeder #1. Due to repaired LBS: 26/AE/06. 10:02 Manually blocked and closed Sintong VCB feeder #1, and then released the block. Cause: Planned maintenance. | 1
146 | 2020-04-27 16:07 | April | 16:07 | Afternoon | Monday | Weekdays | 27 | 2020 | 2020-04-27 16:07 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 16:07 MGT #10 S/U and then online at 17:00 for taking some data at TXP/10 | 1
147 | 2020-04-27 20:25 | April | 20:25 | Night | Monday | Weekdays | 27 | 2020 | 2020-04-27 20:25 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Cloudy | Tree | 120 | 20:25 Duri Field ACB #51 (feeder#4) T/LO. inform from security broken tree at pole 07/V5/03 Found Recloser 07/V5/02 T/LO 22:00 Block and Closed DF #4 then release block. 22:33 Block and Closed Recl 07/V5/02 then release block. Cause : Tree. | 1
| 2020-04-27 20:25 | April | 20:25 | Night | Monday | Weekdays | 27 | 2020 | 2020-04-29 10:04 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Cloudy | Tree | 120 | Checked and found D Field ACB/51 (feeder#4) T/LO. Counter : 578 / 582 R/F: 50P @1 @2 The outage caused by fallen tree near pole 07/V5/03 Cause : Tree. | 1
148 | 2020-04-27 22:24 | April | 22:24 | Night | Monday | Weekdays | 27 | 2020 | 2020-04-27 22:24 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Fair | Tree | - | 22:24 N.Duri 44 kV GCB # 1 T/R 1X 22:33 Trip reclosed again just alarm Not Checked Yet. | 1
| 2020-04-27 22:24 | April | 22:24 | Night | Monday | Weekdays | 27 | 2020 | 2020-04-30 16:14 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Fair | Tree | - | Checked And Found 44KV GCB#1 (44 KV Duri Dumai Line). Counter: 151/152 R/F: 51 @2. Patrolled the line found tree touch powerline in @2 on pole DD/301 Cause: Tree. | 1
149 | 2020-04-28 08:45 | April | 8:45 | Morning | Tuesday | Weekdays | 28 | 2020 | 2020-04-28 08:45 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 08:45 CDGT #2 offline and then Shut Down at 08:47 (to S/D TXP/2 CDSY for PM service) | 1
150 | 2020-04-28 10:05 | April | 10:05 | Morning | Tuesday | Weekdays | 28 | 2020 | 2020-04-28 10:05 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 10 | 10:05 Manually Opened Recloser: 5B/93 D/S 4B feeder# 2. Due to replaced @ 2 broken dead end insulator on pole NN by Mtce team. 11:58 Manually blocked and closed Recloser: 5B/93 and then released the block. Cause: Planned Maintenance. | 1
151 | 2020-04-28 10:33 | April | 10:33 | Morning | Tuesday | Weekdays | 28 | 2020 | 2020-04-28 10:33 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Fair | Planned Maintenance | 28 | 10:33 Manually Opened Recloser: 03/4/16 D/S C Duri feeder #5. Due to change out 112.5 Kva Transformer failure on pole 03/04/24. 12:18 Manually bocked and closed Recloser: 03/4/16, and then released the block. Counter recloser: 237 / 238. Cause: Planned Maintenance. | 1
152 | 2020-04-28 12:12 | April | 12:12 | Afternoon | Tuesday | Weekdays | 28 | 2020 | 2020-04-28 12:12 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 12:12 MGT #5 Trip by Exhaust Temperature High 12:13 MGT #4 Open Generator Breaker by Over Excitation 12:18 MGT #4 back to Online 13:19 S/U MGT #3 and then Online at 13:22 13:38 CDGT #3 tripped Informed by CDGT that gas quality was bad 14:25 S/U CDGT #3 and then online at 14:37 Cause: Exhaust Temperature High | 1
153 | 2020-04-28 12:37 | April | 12:37 | Afternoon | Tuesday | Weekdays | 28 | 2020 | 2020-04-28 12:37 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Fair | Emergency | 186 | 12:37 Manual Open Pematang OCB fdr #2 PMT GS requested to maintain level tank due to WIP problem 14:12 Manually blocked and closed Pematang OCB feeder #2, OK, then release the block. Cause: Emergency. | 1
154 | 2020-04-29 08:12 | April | 8:12 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-04-29 08:12 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Tree | - | N.Duri VCB feeder #1 T/R 1x. Not checked yet. | 1
| 2020-04-29 08:12 | April | 8:12 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-01-05 14:43 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Tree | - | Checked and found N DuriVCB1feedr #1 T/R 1 x, Counter: 341/342, R/F : 51@3 Patrolled the line found Sengon tree branches touch the jumper transformer in @3 on pole 12/E5/16. (pole mounted transformer). Cause: Tree. | 1
155 | 2020-04-29 09:29 | April | 9:29 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-04-29 09:29 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Fair | Tree | 24 | 09:29 Batang VCB fdr#3 T/O (Blocked Position). 09:44 Blocked & closed Batang VCB fdr#3. 14:14 Checked and found Batang VCB fdr #3 operate 1x. Counter: 393 / 394, R/F: 51N Patrolled the line and found palm trees touch the power line o/p 36/AL/10 Cause: PalmTree. | 1
156 | 2020-04-29 21:54 | April | 21:54 | Night | Wednesday | Weekdays | 29 | 2020 | 2020-04-29 21:54 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Cloudy and Lightning | Unidentified | - | C Duri ACB/23 (feeder #6) T/R 1x, Counter: 521/522 R/F: 50P @1 @3 Not Patrolled Yet. | 1
| 2020-04-29 21:54 | April | 21:54 | Night | Wednesday | Weekdays | 29 | 2020 | 2020-01-05 14:35 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Cloudy and Lightning | Unidentified | - | Checked and found C Duri ACB #23 (feeder # 6 ). Counter: 521/522 R/F :50@1,@3 Patrolled the line nothing found. Cause: Unidentified. | 1
157 | 2020-04-30 00:44 | April | 0:44 | Night | Thursday | Weekdays | 30 | 2020 | 2020-04-30 00:44 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Rain and Lightning | Lightning Arrester | - | 00:44 Duri Field ACB/51 (feeder #4) T/R 1x. 16:19 Checked and found Duri field ACB/51 (feeder #4) T/R 1x. Counter: 582/583 R/F : 51N. Patrolled the line found @1 Broken Lightning Arrester on pole 07/U2/01. Cause: Lightning Arrester. | 1
158 | 2020-04-30 00:44 | April | 0:44 | Night | Thursday | Weekdays | 30 | 2020 | 2020-04-30 00:44 | 13.8KV DURI COMMUNITY FEEDER #5 | Duri | PGT North | Rain and Lightning | Transformer Failure | 0 | 00:44 Duri Community VCB/33 feeder #5 T/R 1x Not Checked Yet 16:22 Checked And Found DCSG ACB33 Fdr #5 Ctr 112/234, R/F 51N Patrolled The Line & Found Trafo Failure At Lpt On Phase @1 Cause: Transformer Failure | 1
159 | 2020-04-30 10:26 | April | 10:26 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-04-30 10:26 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Cloudy | Tree | 102 | CKBS VCB feeder #5 T/R 1x. Not checked yet. | 1
| 2020-04-30 10:26 | April | 10:26 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-01-05 15:12 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Cloudy | Tree | 102 | Checked and found CKBS VCB5 feeder #5 T/R 1x. Counter: 180/181 R/F 51N. Patrolled the line found danger tree near powerline beetwen poles 36/CU/26 to 27. Cause: Tree. | 1
160 | 2020-04-30 10:26 | April | 10:26 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-04-30 10:26 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 11 | 10:26 Manually Opened Recloser: 36/DN/3A (D/S 6DN feeder#1). Repaired Broken LBS on pole36/DN/27. (6 well Off During the job). 11:53 Blocked & closed Recloser: 36DN32A, and then release the block. Cause: Planned Maintenance. | 1
161 | 2020-04-30 11:25 | April | 11:25 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-04-30 11:25 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Unidentified | 61 | NKBS OCB feeder #2 T/R 1x. Not checked yet. | 1
| 2020-04-30 11:25 | April | 11:25 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-01-05 14:59 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Unidentified | 61 | Checked and found NKBS OCB Feeder #2 T/R 1x. Counter :99938/99939 R/F : 51N. Patrolled the line nothing found. Cause: Unidentified. | 1
162 | 2020-04-30 16:22 | April | 16:22 | Afternoon | Thursday | Weekdays | 30 | 2020 | 2020-04-30 16:22 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 40 | Sintong VCB feeder#1 T/R 1x. Not checked yet. | 1
| 2020-04-30 16:22 | April | 16:22 | Afternoon | Thursday | Weekdays | 30 | 2020 | 2020-03-05 09:43 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 40 | Checked and found intong OCB feeder #1 T/R 1x,. Counter : 426/427 R/F : 51 @1,@3 Patrolled the line nothing found. Cause: Unidentified. | 1
163 | 2020-04-30 17:56 | April | 17:56 | Afternoon | Thursday | Weekdays | 30 | 2020 | 2020-04-30 17:56 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 61 | So.Balam VCB feeder#1 T/R 2x. So.Balam GFPC T/R 1x. Not checked yet. | 1
| 2020-04-30 17:56 | April | 17:56 | Afternoon | Thursday | Weekdays | 30 | 2020 | 2020-02-05 08:39 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 61 | Checked and found So.Balam VCB Fdr#1 T/R 1x Ctr:414/415 R/F: 51N Patrolled the line but nothing found. Cause : Unidentified. | 1
164 | 2020-04-30 23:05 | April | 23:05 | Night | Thursday | Weekdays | 30 | 2020 | 2020-04-30 23:05 | 13.8KV 5B FEEDER #3 | Minas | PGT South | Rain and Lightning | Tree | 51 | 5B fdr#3 Load dropped 45A (85/40A). Not checked yet. | 1
| 2020-04-30 23:05 | April | 23:05 | Night | Thursday | Weekdays | 30 | 2020 | 2020-01-05 11:00 | 13.8KV 5B FEEDER #3 | Minas | PGT South | Rain and Lightning | Tree | 51 | 11:00 It was reported no power D/S 5B FDR#3. 12:40 Checked & found Recl. 4D/65 T/LO ctr:80/98. Patrolled the line & found Danger Sawit D/S Recl. 4D/65. Blocked & closed Recl. 4D/65, then release the block. Cause: Tree. | 1
1 | 2020-01-05 09:57 | January | 9:57 | Morning | Sunday | Weekends | 5 | 2020 | 2020-01-05 09:57 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Cloudy | Emergency | - | 09:57 Manually Opened Pematang fdr#2 (Req. Pematang GS). Multilin control Trouble. 16:36 Manually blocked & closed Pematang fdr#2, then release the block. Cause: Emergency. | 1
2 | 2020-01-05 10:49 | January | 10:49 | Morning | Sunday | Weekends | 5 | 2020 | 2020-01-05 10:49 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Cloudy | Tree | 102 | 10:49 CKBS fdr#5 T/R 1x. 15:26 Checked and found CKBS VCB5 feeder #5 T/R 1x. Counter : 181-182 R/F: 51N. Patrolled the line found danger palm tree between poles 36-CU-26 to 27. Cause: Tree. | 1
3 | 2020-01-05 13:49 | January | 13:49 | Afternoon | Sunday | Weekends | 5 | 2020 | 2020-01-05 13:49 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 15 | Pinang OCB feeder#1 T/R 1x. Not checked yet. | 1
| 2020-01-05 13:49 | January | 13:49 | Afternoon | Sunday | Weekends | 5 | 2020 | 2020-03-05 09:45 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 15 | Checked and found Pinang OCB feeder #1 T/R 1 x. Counter: 462-463 R/F : 51@2 Patrolled the line nothing found. Cause: Suspect Lightning. | 1
4 | 2020-02-05 11:12 | February | 11:12 | Morning | Wednesday | Weekdays | 5 | 2020 | 2020-02-05 11:12 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Planned Maintenance | 50 | 11:12 Switching to for repaired Jumper o/p SDDB-06. Manually Opened LBS 04-08-29 (C.Duri fdr#7). 13:19 Closed LBS 04-08-29. (Postponed due to damage in the bucket truck, will continue tomorrow). Cause: Planned Maintenance. | 1
5 | 2020-02-05 16:44 | February | 16:44 | Afternoon | Wednesday | Weekdays | 5 | 2020 | 2020-02-05 16:44 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Lightning | 0 | C.Duri ACB #28 (feeder#16) T/R 2x Counter:375-377 R/F:51@1@2. Not patrolled yet. | 1
| 2020-02-05 16:44 | February | 16:44 | Afternoon | Wednesday | Weekdays | 5 | 2020 | 2020-03-05 15:25 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Lightning | 0 | Checked And Found CD ACB Feeder #16 T/R 1 x, Ctr 462-463, R/F: 51P Patrolled The Line On 02-May-2020 But Found Nothing Cause: Lightning | 1
6 | 2020-03-05 08:12 | March | 8:12 | Morning | Thursday | Weekdays | 5 | 2020 | 2020-03-05 08:12 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 0 | Nella feeder#1 Load dropped 117A (214-97A). Not checked yet. | 1
| 2020-03-05 08:12 | March | 8:12 | Morning | Thursday | Weekdays | 5 | 2020 | 2020-04-05 12:16 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 0 | Checked and found Recloser:16-Z-01 T/R 1x. Counter: 114-115 R/F: 51N Patrolled the line and found on @1 dead monkey on pole 21-W-09. Cause: Animal. | 1
7 | 2020-03-05 08:34 | March | 8:34 | Morning | Thursday | Weekdays | 5 | 2020 | 2020-03-05 08:34 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Planned Maintenance | 67 | 08:34 Manually Opened LBS 04-08-29 (D/S C.Duri feeder#7). due to repaired Broken Jumper o/p SDDB-06. 11:20 Switching to Normalized Load C.Duri feeder#7, fdr#8, Fdr#9. (C.Duri fdr#8 Back to Normal). Cause: Planned Maintenance. | 1
8 | 2020-03-05 09:21 | March | 9:21 | Morning | Thursday | Weekdays | 5 | 2020 | 2020-03-05 09:21 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Fair | Animal | 181 | CKBS VCB feeder#5 T/R 1x. Not checked yet. | 1
| 2020-03-05 09:21 | March | 9:21 | Morning | Thursday | Weekdays | 5 | 2020 | 2020-05-05 07:14 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Fair | Animal | 181 | Checked and found: CKBS VCB feeder #5 T/R 1x. Counter : 182 - 183, Relay Flag : 51N. Patrolled the line found dead monkey on Recloser:36-CU-29. Causing @1,2,3 cover bushings to burn. Cause : Animal. | 1
9 | 2020-03-05 11:48 | March | 11:48 | Morning | Thursday | Weekdays | 5 | 2020 | 2020-03-05 11:48 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Unidentified | 66 | NKBS OCB feeder#2 T/R 1x. Not checked yet. | 1
| 2020-03-05 11:48 | March | 11:48 | Morning | Thursday | Weekdays | 5 | 2020 | 2020-05-05 16:29 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Unidentified | 66 | Checked and found NKBS OCB feeder #2 T/R 1x, ctr: 99939 - 99940, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
10 | 2020-03-05 15:04 | March | 15:04 | Afternoon | Thursday | Weekdays | 5 | 2020 | 2020-03-05 15:04 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | C.Duri feeder#1 Load dropped 82A (155-73A). Not checked yet. | 1
| 2020-03-05 15:04 | March | 15:04 | Afternoon | Thursday | Weekdays | 5 | 2020 | 2020-05-05 07:05 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found Recloser:41-AW-62 T/R 2x. Counter : 337 - 339, Relay Flag : NONE. Patrolled the line nothing found. Cause : Unidentified. | 1
11 | 2020-04-05 06:16 | April | 6:16 | Morning | Sunday | Weekends | 5 | 2020 | 2020-04-05 06:16 | 13.8KV CENTRAL DURI FEEDER #8 | Duri | PGT North | Cloudy | Unidentified | 0 | 06:16 CD ACB #32 (feeder#8) T/R 1x, Counter: 481-482, R/F: 51N 17:18 Checked C Duri ACB #32 (feeder #8) T/R 1x. Counter: 481-482 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. | 1
12 | 2020-04-05 09:40 | April | 9:40 | Morning | Sunday | Weekends | 5 | 2020 | 2020-04-05 09:40 | 13.8KV 8D FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 9 | 09:40 Manually Opened Recloser: 8D-30 (D/S 8D feeder#3). Due to replacement @3 broken dead end insulator, on Terminal pole well: 9D-01. 10:23 Manually blocked & closed 8D-30, and then release the block. Cause: Planned Maintenance. | 1
13 | 2020-04-05 16:43 | April | 16:43 | Afternoon | Sunday | Weekends | 5 | 2020 | 2020-04-05 16:43 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 34 | C.Duri feeder#1 Load dropped 53A (145-93A). Not checked yet. | 1
| 2020-04-05 16:43 | April | 16:43 | Afternoon | Sunday | Weekends | 5 | 2020 | 2020-05-05 15:28 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 34 | Checked and found Recloser:41-AW-62 T/R 1x. Counter: 339 - 340 R/F: None Patrolled the line but nothing found. Cause : Unidentified. | 1
14 | 2020-05-05 23:59 | May | 23:59 | Night | Tuesday | Weekdays | 5 | 2020 | 2020-05-05 23:59 | CPI POWER SYSTEM |  |  |  |  | - | CPI Power System on Normal Condition | 1
15 | 2020-06-05 01:55 | June | 1:55 | Night | Friday | Weekdays | 5 | 2020 | 2020-06-05 01:55 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Tree | 21 | 01:55 It was reported no power on road 07-V5-xx (DF fdr #4) (no load dropped appear d/s of DF fdr #4) 03:15 Checked and found RCL 07-V5-02 T/LO, ctr: 168-175 patrolled the line and found fallen tree near pole 07-V5-03 Continue tomorrow to execute the tree (after coordinate with MTCE team) 06:08 The fallen tree completely executed 06:10 Manual close the RCL 07-V5-02, OK. Cause: Tree | 1
16 | 2020-06-05 07:47 | June | 7:47 | Morning | Friday | Weekdays | 5 | 2020 | 2020-06-05 07:47 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Recloser - Control Recloser | 229 | 07:47 Bangko feeder #1 load dropped 57A (158-101A). 09:27 Checked & found recloser 23-X-08 T/SO and also found control recloser ----> Blank. 10:15 Block Bangko feeder#1. Closed recloser 23-X-08 , Oke and realized block Bangko feeder #1. Cause : Control recloser failure. | 1
17 | 2020-06-05 14:21 | June | 14:21 | Afternoon | Friday | Weekdays | 5 | 2020 | 2020-06-05 14:21 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Fair | Unidentified | 0 | 14:21 Darling feeder #7 T/O (Block position RIG BN#11) 14:26 Block Closed Darling feeder #7. | 1
| 2020-06-05 14:21 | June | 14:21 | Afternoon | Friday | Weekdays | 5 | 2020 | 2020-12-05 07:25 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found: DRLG7-13.8VCB7 T/O, Counter : 189 - 190, Relay Flag : 51 Patrolled the line found : No Finding Cause : Unidentified | 1
18 | 2020-06-05 18:25 | June | 18:25 | Afternoon | Friday | Weekdays | 5 | 2020 | 2020-06-05 18:25 | ROKAN SUBSTATION | Bangko-Balam | PGT North | Cloudy | Animal | 74 | 18:25 115Kv Rokan C/S T/O. Pinang feeder #1 load dropped 17A (106-89A). S.Balam feeder #1 load dropped 19A (157-138A). S.Balam feeder #2 load dropped 65A (103-38A), Pump Off. S.Balam feeder #3 load dropped 131A (132-1A), Pump Off. S.Balam feeder #4 load dropped 90A (212-122A). Nella feeder #1 load dropped 115A (215-100A). Nella feeder #2 load dropped 17A (70-53A). Bangko feeder #1 load dropped 37A (158-121A). Bangko feeder #2 load dropped 103A (238-135A), Pump Off. Bangko feeder #3 load dropped 15A (220-205A), Pump Off. Bangko feeder #4 load dropped 124A (193-69A). Menggala feeder #1 load dropped 143A (188-45A). Menggala feeder #2 load dropped 180A (210-21A). Sintong feeder #1 load dropped 43A (99-56A). Sintong feeder #2 load dropped 151A (188-37A). Pematang feeder #1 load dropped 155A (192-37A). Pematang feeder #2 load dropped 8A (111-103A). Rangau feeder #1 load dropped 13A (55-42A). Rangau feeder #2 load dropped 41A (158-117A) . Petani feeder #1 load dropped 9A (223-224A). Petani feeder #2 load dropped 12A (71-59A). Ketigul feeder #1 load dropped 15A (107-92A). Ketigul feeder #2 load dropped 37A (76-39A). Ketigul feeder #3 load dropped 11A (44-33A). 20:15 Checked & found 115Kv Rokan C/S T/O Ctr:227 R/F:51@1@2. Dead Monkey on Rokan VR. Checked Rokan Power Tx Normal Condition. 20:16 Opened Rokan fdr#2, then closed at 20:21. Opened Rokan fdr#3, then closed at 20:22. Opened Rokan fdr#2, then closed at 20:22. 20:20 Closed 115Kv Rokan C/S. Cause: Animal (Monkey). | 1
19 | 2020-06-05 20:34 | June | 20:34 | Night | Friday | Weekdays | 5 | 2020 | 2020-06-05 20:34 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Unidentified | 10 | 20:34 D.Field fdr#2 Load dropped 76A (148-72A). 21:15 It was reported no power at Road 07-U3. 22:00 Checked & found Recl. 07-U3-23 T/SO Ctr:18-19. Patrolled the line but found nothing. 22:03 Blocked & closed Recl. 07-U3-23, the release the block. Cause: Unidentified. | 1
20 | 2020-07-05 07:03 | July | 7:03 | Morning | Sunday | Weekends | 5 | 2020 | 2020-07-05 07:03 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 0 | C.Duri ACB #28 (feeder #16) T/R 1x. R/F : 51N,51@1 &@2 Counter: 577-578. Not patrolled yet. | 1
| 2020-07-05 07:03 | July | 7:03 | Morning | Sunday | Weekends | 5 | 2020 | 13-05-2020 18:07 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 0 | Patrolled the line nothing found. Cause: Unidentified. | 1
21 | 2020-07-05 18:59 | July | 18:59 | Afternoon | Sunday | Weekends | 5 | 2020 | 2020-07-05 18:59 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 9 | Batang feeder#3 Load dropped 45A (78-33A). Batang GFPC T/R 2x. Not checked yet. | 1
| 2020-07-05 18:59 | July | 18:59 | Afternoon | Sunday | Weekends | 5 | 2020 | 13-05-2020 07:15 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 9 | Checked Down stream Batang feeder #3 and found: - All Recloser counters have not changed (Normal). - And Batang GFPC T/R 5x Counter: 1011-1016. Patrolled the line nothing found. Cause: Suspected Lightning. | 1
22 | 2020-08-05 23:44 | August | 23:44 | Night | Wednesday | Weekdays | 5 | 2020 | 2020-08-05 23:44 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Cloudy | Unidentified | 53 | NKBS feeder#2 T/R 1x. Not checked yet. | 1
| 2020-08-05 23:44 | August | 23:44 | Night | Wednesday | Weekdays | 5 | 2020 | 2020-12-05 06:51 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Cloudy | Unidentified | 53 | Checked and found NKBS OCB feeder #2 T/R 1x. Counter: 99940-99941 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. | 1
23 | 2020-08-05 23:44 | August | 23:44 | Night | Wednesday | Weekdays | 5 | 2020 | 2020-08-05 23:44 | 13.8KV NEW KOTABATAK FEEDER #3 | Petko | PGT South | Cloudy | Unidentified | 44 | NKBS feeder#3 T/R 1x. Not checked yet. | 1
| 2020-08-05 23:44 | August | 23:44 | Night | Wednesday | Weekdays | 5 | 2020 | 2020-12-05 06:57 | 13.8KV NEW KOTABATAK FEEDER #3 | Petko | PGT South | Cloudy | Unidentified | 44 | Checked and found NKBS OCB feeder #23 T/R 1x. Counter: 324-325 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. | 1
24 | 2020-09-05 14:02 | September | 14:02 | Afternoon | Saturday | Weekends | 5 | 2020 | 2020-09-05 14:02 | CENTRAL DURI POWER PLANT | Duri | PGT North | Fair | Under investigation | - | CGT#3 Trip by Alarm Exhaust temperature high Trip Cause: Under investigation | 1
25 | 2020-09-05 17:54 | September | 17:54 | Afternoon | Saturday | Weekends | 5 | 2020 | 2020-09-05 17:54 | MINAS POWER PLANT | Minas | PGT South | Fair |  | - | 17:54 S/U MGT#7, then on line the unit at 18:16. | 1
26 | 2020-10-05 23:30 | October | 23:30 | Night | Monday | Weekdays | 5 | 2020 | 2020-10-05 23:30 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Unidentified | 25 | 23:30 Darling VCB fdr#7 T/SO. 23:43 Blocked & closed Darling VCB fdr#7, then release the block. Not checked yet. | 1
| 2020-10-05 23:30 | October | 23:30 | Night | Monday | Weekdays | 5 | 2020 | 13-05-2020 07:49 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Unidentified | 25 | Checked and found Darling VCB feeder #3 T/SO. Counter: 267-268 R/F: 51@2. Patrolled the line nothing foud. Cause: Unidentified. | 1
27 | 2020-11-05 07:10 | November | 7:10 | Morning | Thursday | Weekdays | 5 | 2020 | 2020-11-05 07:10 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Unidentified | 0 | 07:10 C.Duri Fdr# 7 load drop 51A ( 147 - 96A ) Not Checked yet. | 1
| 2020-11-05 07:10 | November | 7:10 | Morning | Thursday | Weekdays | 5 | 2020 | 13-05-2020 07:31 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found Recloser: 03-03-42 T/R 1x. Counter: 240-241. Patrolled the line nothing found. Cause: Unidentified. | 1
28 | 2020-11-05 11:30 | November | 11:30 | Morning | Thursday | Weekdays | 5 | 2020 | 2020-11-05 11:30 | 115KV CENTRAL DURI - ROKAN LINE | Duri | PGT North | Fair | Under investigation | 1479 | 11:30 115KV C. Duri -Rokan GCB #43 T/O, ----->and Closed at 14:31. 115KV C. Duri -Rokan GCB #45 T/O, ----->and Closed at 14:12. 115KV Rokan GCB #12 T/O, ----->and Closed at 14:15. (On block due to RIG APS-3516 at Petani 02) No Power To Pematng SUB, Rangau SUB and Petani SUB. Rokan fdr #2 Load dropped 11A (22-11A). Ketigul fdr #1 load dropped 23A (121-97A). Ketigul fdr #2 load dropped 10A (75-65A). Pinang fdr #1 load dropped 12A (156-134A) S. Balam fdr #1 load dropped 22A (156-134A). S. Balam fdr #4 load dropped 40A (208-170A). Nella fdr #1 load dropped 15A (214-199A). Bangko fdr #1 load dropped 20A (164-144A). Bangko fdr #4 load dropped 8A (190-182A). Menggala fdr #2 load dropped 38A (201-170A). Sintong fdr #2 load dropped 20A (1897-177A). 11:50 Manual Open Rokan fdr #2. -----> Closed at 15:03. 12:53 Manual Open Pematang fdr #1, ----->and Closed at 14:20. Manual Open Pematang fdr #2, ----->and Closed at 14:44. 12:54 Manual Open Rangau fdr #1, ----->and Closed at 14:20. Manual Open Rangau fdr #1, ----->and Closed at 14:22. Manual Open Petani fdr #1, ----->and Closed at 14:28. Manual Open Petani fdr #2, ----->and Closed at 14:48. 13:00 Checked and found 115KV C. Duri GCB #43 T/O (On blocked). Checked and found 115KV C. Duri GCB #45 T/O (On blocked). R/F : 51 @1, @2, 51G, 51N, 21G, 67N and 87L. 13:50 Checked at Pamatang main, but found nothing Abnormal. Patrolled the line but found nothing. 13:59 Manual Open 44KV Pematang Main OCB #1, ----->and Closed at 14:18 13:59 Manual Open 44KV Pematang Main OCB #2, ----->and Closed at 14:18 14:00 Manual Open 44KV Pematang Main OCB #3, ----->and Closed at 14:18. 14:00 Manual Open Pematang Main C/S, ----->and Closed at 14:17. Cause: Under investigation. Prod Loss Pematang GS : 627 Bbls 47 Wells. Petani GS : 648 Bbls 52 Wells. Rokan fdr#2 : 85 Bbls 6 Wells. Rangau GS : 172 Bbls 20 Wells. ----------------------------------------- Total Prod Loss : 1532 Bbls 125 Wells. JDE Number = 123 | 1
29 | 2020-11-05 14:36 | November | 14:36 | Afternoon | Thursday | Weekdays | 5 | 2020 | 2020-11-05 14:36 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Unidentified | 159 | 14:36 Darling 13.8KV fdr #3 T/SO. 16:03 Checked and found Darling fdr #3 T/SO R/F:51N, 51@1, @2. Patrolled the line but found nothing. 16:04 Blocked and closed Darling fdr #3, but tripped again. Checked and found R/F:51N. Patrolled the line but found nothing. 17:25 Function test Darling fdr #3. Ok. 17:37 Open LBS 05-N7-20N, ----->Closed at Blocked and closed Darling fdr #3. Ok. 17:45 Open LBS 05-N3-24, ----->Closed at 17:48 Open LBS 05-N5-22, ----->Closed at 17:50 Closed LBS 05-N7-20N but Darling fdr #3 tripped again. 18:10 Blocked & Closed Darling VCB fdr#1, then release the block. 18:53 Blocked & closed Darling VCB fdr#5, then release the block. Opened Bypass Ex VR ( 3 span aftrer Recl. 05-M7-24). Closed LBS 05-N7-20N. 18:47 Blocked & closed Darling VCB fdr#3, then release the block. Cause: Unidentified. | 1
30 | 2020-12-05 02:36 | December | 2:36 | Night | Saturday | Weekends | 5 | 2020 | 2020-12-05 02:36 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Animal | 88 | 02:36 Darling VCB feeder#3 T/SO. 02:40 Blocked & closed Darling VCB feeder#3, but failed. 03:30 Checked & found Darling VCB fdr#3 T/LO Ctr; 270-277 R/F:51@2. 04:44 Patrolled the line & found Dead Monkey o/p 05-Ni-08. Opened Bypass Recl. 05-N1-24. 06:35 Blocked & closed Darling VCB fdr#3, but failed. | 1
31 | 2020-12-05 07:00 | December | 7:00 | Morning | Saturday | Weekends | 5 | 2020 | 2020-12-05 07:00 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 112 | 07:00 N. Duri fdr #2 load dropped 41A (239-198A). 09:55 It was reported No power at 10-J8-05. 11:10 Checked and found Recl. 10-J8-16A T/SO ctr: 67-68. Patrolled the line but found nothing. 11:18 Blocked and closed the Recl. Ok than released the block. Cause: Unidentified. | 1
32 | 2020-12-05 09:06 | December | 9:06 | Morning | Saturday | Weekends | 5 | 2020 | 2020-12-05 09:06 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 09:06 Started Up MGT #9 and On Line to the system at 09:35. (To back Up power prior Series S/D NDC CT #1, #2, #3 and 230 KV Line S/D). | 1
33 | 2020-12-05 10:46 | December | 10:46 | Morning | Saturday | Weekends | 5 | 2020 | 2020-12-05 10:46 | MINAS POWER PLANT | Minas | PGT South |  |  | - | at 10:46 S/U MGT #5 and then Online the unit at 11:12. | 1
34 | 2020-12-05 11:16 | December | 11:16 | Morning | Saturday | Weekends | 5 | 2020 | 2020-12-05 11:16 | MINAS POWER PLANT | Minas | PGT South |  |  | - | at 11:16 S/U MGT #1 and then Online the unit at 11:42. | 1
35 | 2020-12-05 11:38 | December | 11:38 | Morning | Saturday | Weekends | 5 | 2020 | 2020-12-05 11:38 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Planned Maintenance | - | 11:38 Manually opened LBS:06-S1-19 D/S D.Field Fdr#2 Due to replace transformer on pole: 06-S1-05 12:05 ManuallyClosed LBS:06-S1-19 --> OK. Cause: Planned maintenance. | 1
36 | 2020-12-05 14:28 | December | 14:28 | Afternoon | Saturday | Weekends | 5 | 2020 | 2020-12-05 14:28 | MINAS POWER PLANT | Minas | PGT South |  |  | - | at 14:28 S/U MGT #10 and then Online the unit at 14:40. | 1
37 | 2020-12-05 15:31 | December | 15:31 | Afternoon | Saturday | Weekends | 5 | 2020 | 2020-12-05 15:31 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | - | C.Durir# feeder #1 load drop 56A ( 145-89A ) Not checked yet. | 1
| 2020-12-05 15:31 | December | 15:31 | Afternoon | Saturday | Weekends | 5 | 2020 | 15-05-2020 07:05 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | - | Checked and found Recloser: 41-AW-62 T/R 1x. Counter: 340-341 R/F: none. Patrolled the line nothing found. Cause: Unidentified. | 1
38 | 2020-12-05 16:20 | December | 16:20 | Afternoon | Saturday | Weekends | 5 | 2020 | 2020-12-05 16:20 | NORTH DURI POWER PLANT | Duri | PGT North | Fair |  | - | 16:20 NDC #1 off line and then Shut down. Lower from local KBJ Transformer #1 two steps ( -10 ) Lower from local KBJ Transformer #2 two steps ( -2 ) At DSC LTC KBJ Transformer #1 R:4 At DSC LTC KBJ Transformer #2 R:4. | 1
39 | 2020-12-05 22:24 | December | 22:24 | Night | Saturday | Weekends | 5 | 2020 | 2020-12-05 22:24 | 13.8KV 5B FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 0 | 5B OCB feeder#4 T/R 1x. Not checked yet. | 1
| 2020-12-05 22:24 | December | 22:24 | Night | Saturday | Weekends | 5 | 2020 | 15-05-2020 08:00 | 13.8KV 5B FEEDER #4 | Minas | PGT South | Rain and Lightning | Lightning | 0 | Checked and found: 5BSB-13.8OCB4 T/R, Counter : 712 - 713, Relay Flag : 51N Patrol led the line found: Flash Over Pin Insulator Ø1 Cause : Lightning | 1
40 | 2020-12-05 22:24 | December | 22:24 | Night | Saturday | Weekends | 5 | 2020 | 2020-12-05 22:24 | 4 BRAVO SUBSTATION | Minas | PGT South | Rain and Lightning | Lightning | 0 | 115Kv Line 5B-4B T/R 1x. - 5B 115 KV GCB#21 T/R 1x. - 5B 115 KC GCB#26 T/R 1x. - 4B 115 KV GCB#22 T/R 1x. Not checked yet. | 1
| 2020-12-05 22:24 | December | 22:24 | Night | Saturday | Weekends | 5 | 2020 | 14-05-2020 08:04 | 4 BRAVO SUBSTATION | Minas | PGT South | Rain and Lightning | Lightning | 0 | Checked and found : - 5B 115 KV OCB #21 T/R 1x Counter: 2846-2947 R/F: 21 AG. - 5B 115 KV OCB #26 T/R 1x Counter: 875-876 R/F: 21 AG. - 4B 115 kV OCB #22 T/R 1x, Counter: 315 - 316, R/F: 21AG, 87L Patrolled the line but found nothing Cause: Suspected Lightning. | 1
41 | 2020-12-05 22:24 | December | 22:24 | Night | Saturday | Weekends | 5 | 2020 | 2020-12-05 22:24 | 115KV DURI - PUNGUT LINE | Duri | PGT North | Rain and Lightning | Dead End Insulator | 40 | 22:24 115Kv DRB - Pungut Line T/O. -115Kv DRB OCB #21 T/O and then Manually closed at 22:31 -115Kv DRB OCB #29 T/O and then Manually closed at 22:31. -115Kv Pungut OCB #21 T/O and then Manually closed at 22:32. Not checked yet. | 1
| 2020-12-05 22:24 | December | 22:24 | Night | Saturday | Weekends | 5 | 2020 | 14-05-2020 07:42 | 115KV DURI - PUNGUT LINE | Duri | PGT North | Rain and Lightning | Dead End Insulator | 40 | Checked and found *115 kV GCB#21 T/O R/F: 87 counter: 256-257 *115 kV GCB#29 T/O R/F: 87 counter: 150-151 Patrolled the line and found - broken suspension insulator o/p DP-41 - broken dead end insulator o/p DP-45 - broken guy wire o/p DP-39 Cause : Suspension Insulator & Dead End insulator | 1
42 | 2020-12-05 22:24 | December | 22:24 | Night | Saturday | Weekends | 5 | 2020 | 2020-12-05 22:24 | 115KV PUNGUT - KOTABATAK JUNCTION LINE | Petko | PGT South | Rain and Lightning | Unidentified | - | 22:24 115KV KBJ - Pungut Line T/O. - 115 KV KBJ GCB #51 T/O and then Manually closed at 22:33. - 115 KV KBJ GCB #53 T/O and then Manually closed at 22:33. - 115 KV Pungut OCB #22 Normal. Not checked yet. | 1
| 2020-12-05 22:24 | December | 22:24 | Night | Saturday | Weekends | 5 | 2020 | 19-05-2020 08:08 | 115KV PUNGUT - KOTABATAK JUNCTION LINE | Petko | PGT South | Rain and Lightning | Unidentified | - | Checked and found: GCB 51 KBJ T/O, Counter : 255 - 256, R/F : 67N GCB 52 KBJ T/O, Counter : 255 - 256, R/F : 67N Patrolled the line but found nothing Patrol by : Nasrul Akhyar Input by : HNHE Cause : Unidentified | 1
43 | 2020-05-13 00:05 | May | 0:05 | Night | Wednesday | Weekdays | 13 | 2020 | 2020-05-13 00:05 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Rain and Lightning | Pin Insulator | 74 | Petani OCB feeder#1 T/R 1x. Not checked yet. | 1
| 2020-05-13 00:05 | May | 0:05 | Night | Wednesday | Weekdays | 13 | 2020 | 2020-05-15 06:47 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Rain and Lightning | Pin Insulator | 74 | Checked and found Petani OCB feeder #1 T/R 1x. Counter: 157/158 R/F: 51@1. Patrolled the line found @1 broken pin insulator on pole 33/AY/14. Cause: Pin Insulator. | 1
44 | 2020-05-13 00:11 | May | 0:11 | Night | Wednesday | Weekdays | 13 | 2020 | 2020-05-13 00:11 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 |  |  | Rain and Lightning | Lightning Arrester | 63 | MSU feeder#2 (BKS feeder#2) Load dropped 210A (262/52A). Not checked yet. | 1
| 2020-05-13 00:11 | May | 0:11 | Night | Wednesday | Weekdays | 13 | 2020 | 2020-05-15 06:53 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 |  |  | Rain and Lightning | Lightning Arrester | 63 | Checked and found Recloser: 37/BD/12 T/R 2x ( D/S MSU feeder #2). Counter: 1468/1470 R/F: none. Patrolled the line found: 1. @1 broken dead end insulator on pole 37/BD/32. 2. @3 broken pin insulator on pole 37/BD/109. 3. @3 broken Lightning Arrester on terminal pole well Bekasap #37. Cause: Lightning Arrester. | 1
45 | 2020-05-13 18:35 | May | 18:35 | Afternoon | Wednesday | Weekdays | 13 | 2020 | 2020-05-13 18:35 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Pin Insulator | 14 | Rokan VCB fdr #2 T/R 1x Not Checked Yet | 1
| 2020-05-13 18:35 | May | 18:35 | Afternoon | Wednesday | Weekdays | 13 | 2020 | 2020-05-20 09:07 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Pin Insulator | 14 | Check and found Rokan VCB feeder #2 T/R 2x. Counter: 1322/1324 R/F: 51@3. Patrolled the line found @3 broken pin insulator on pole 28/AV/02. Cause: Pin insulator. | 1
46 | 2020-05-14 16:57 | May | 16:57 | Afternoon | Thursday | Weekdays | 14 | 2020 | 2020-05-14 16:57 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Fair | Pin Insulator | - | DCM VCB fdr #3 T/R 1x Not Checked Yet | 1
| 2020-05-14 16:57 | May | 16:57 | Afternoon | Thursday | Weekdays | 14 | 2020 | 2020-05-18 10:12 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Fair | Pin Insulator | - | Checked and found DCM VCB fdr #3 T/R 1x, counter: 103 / 105, R/F: 51N Patrolled the line and found Broken Pin Insulator @1, o/p 4/DD/56 Cause : Pin Insulator | 1
47 | 2020-05-14 17:25 | May | 17:25 | Afternoon | Thursday | Weekdays | 14 | 2020 | 2020-05-14 17:25 | NORTH DURI POWER PLANT | Duri | PGT North | Fair |  | - | 17:25 NDC CT/3 Offline and shut down for Offline wash | 1
48 | 2020-05-15 06:07 | May | 6:07 | Morning | Friday | Weekdays | 15 | 2020 | 2020-05-15 06:07 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Fair | Dead End Insulator | - | Ketigul VCB feeder # 3 T/R 1x. Ketigul feeder # 2 Load drop 12A ( 75/63A ) Ketigul feeder # 1 Load drop 25A ( 121/96A ) Not Checked yet. | 1
| 2020-05-15 06:07 | May | 6:07 | Morning | Friday | Weekdays | 15 | 2020 | 2020-05-20 07:15 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Fair | Dead End Insulator | - | Checked and found KTGL VCB fdr #3 T/R 1x, ctr: 234/235, R/F: 51N Patrolled the line and found Dead End Flash @1 o/p 21/AR/14 and @3 o/p 31/AP/0/9 Cause : Dead End Insulator | 1
49 | 2020-05-15 14:07 | May | 14:07 | Afternoon | Friday | Weekdays | 15 | 2020 | 2020-05-15 14:07 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 14:07 MGT #2 S/U and then Online at 14:31 | 1
50 | 2020-05-15 16:05 | May | 16:05 | Afternoon | Friday | Weekdays | 15 | 2020 | 2020-05-15 16:05 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 16:05 NDC CT/3 S/U and then online at 16:31 after maintenance activities at TXP/3 NDC and OLW at CT/3 | 1
51 | 2020-05-15 16:26 | May | 16:26 | Afternoon | Friday | Weekdays | 15 | 2020 | 2020-05-15 16:26 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 16:26 MGT #3 S/U and then Online at 16:44 | 1
52 | 2020-05-15 17:25 | May | 17:25 | Afternoon | Friday | Weekdays | 15 | 2020 | 2020-05-15 17:25 | 13.8KV MENGGALA GFPC | Bangko-Balam | PGT North | Cloudy | Unidentified | - | Menggala GFPC T/R 1x Not checked yet | 1
53 | 2020-05-15 19:13 | May | 19:13 | Night | Friday | Weekdays | 15 | 2020 | 2020-05-15 19:13 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 19:13 NDC CT/2 Offline and shutdown for Offline wash | 1
54 | 2020-05-16 06:01 | May | 6:01 | Morning | Saturday | Weekends | 16 | 2020 | 2020-05-16 06:01 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Fair | Dead End Insulator | - | C.Duri ACB #13 (feeder#3) T/R 1x. Not Checked yet. | 1
| 2020-05-16 06:01 | May | 6:01 | Morning | Saturday | Weekends | 16 | 2020 | 2020-05-21 10:25 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Fair | Dead End Insulator | - | Checked and found CDRSG/13.8ACB13 T/R 1x R/F 51P @1 Counter 230 / 231. Patrolled the line and found flash deadend insulator on pole 03/08/01. Cause : Deadend Insulator | 1
55 | 2020-05-16 06:24 | May | 6:24 | Morning | Saturday | Weekends | 16 | 2020 | 2020-05-16 06:24 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Tree | - | C.Duri ACB #33 (feeder#7) T/R 1x. Not Checked yet. | 1
| 2020-05-16 06:24 | May | 6:24 | Morning | Saturday | Weekends | 16 | 2020 | 2020-05-21 10:03 | 13.8KV CENTRAL DURI FEEDER #7 | Duri | PGT North | Fair | Tree | - | Checked and found CDRSG/13.8ACB33 T/R 1x R/F 51P @2, @3; Ctr: 568 /569. Patrolled the line and found high tree near pole 03/05/25A. Cause : Tree | 1
56 | 2020-05-16 12:00 | May | 12:00 | Afternoon | Saturday | Weekends | 16 | 2020 | 2020-05-16 12:00 | KOTABATAK JUNCTION SW STA | Petko | PGT South | Fair | Under investigation | 9492 | 12:00 Frequency System Critically High, reach 61.08 Hz (under investigation) NDC/1 Auto Open Gen Breaker due by frequency high MGT #1, #2, #3, #10 Auto Open Gen Breaker MGT #6, #7 Manual Open Gen Breaker CDGT #4 Auto Open Gen Breaker 115 kV OCB #21 6D T/SO 115 kV OCB #1 NKBS T/R 1x KBJ and SURAM RTU failed 12:14 NDC #3 Gen Breaker Trip by High Frequency 230 kV GCB #33 ND and GCB #35 ND T/O System load shedding level 9 (frequency down to 58.58 Hz) 3D fdr #2 T/O, closed at 16:25 3D fdr #3 T/O, closed at 16:27 3D fdr #4 T/O, closed at 16:27 3D fdr #5 T/O, closed at 15:43 3D fdr #6 T/O, closed at 15:42 3D fdr #7 T/O, closed at 15:42 3D fdr #8 T/O, closed at 15:30 4B fdr #1 T/O, closed at 16:29 4B fdr #4 T/O, closed at 15:49 4B fdr #5 T/O, closed at 15:49 4B fdr #6 T/O, closed at 16:34 4D fdr #1 T/O, closed at 15:43 4D fdr #2 T/O, closed at 16:28 4D fdr #2 T/O, closed at 16:28 5B fdr #1 T/O, closed at 16:34 5B fdr #2 T/O, closed at 16:35 5B fdr #3 T/O, closed at 16:31 5B fdr #4 T/O, closed at 16:35 5B fdr #5 T/O, closed at 16:36 5B fdr #7 T/O, closed at 17:19 6D fdr #1 T/O, closed at 16:04 6D fdr #2 T/O, closed at 19:13 6D fdr #3 T/O, closed at 16:02 6D fdr #4 T/O, closed at 16:05 6D fdr #5 T/O, closed at 19:05 6D fdr #6 T/O, closed at 19:13 6DN fdr #1 T/O, closed at 19:23 6DN fdr #2 T/O, closed at 18:45 6DN fdr #3 T/O, closed at 16:02 6DN fdr #4 T/O, closed at 16:02 6DN fdr #5 T/O, closed at 19:35 6DN fdr #6 T/O, closed at 19:35 8C fdr #1 T/O, closed at 16:21 8C fdr #2 T/O, closed at 16:22 8C fdr #3 T/O, closed at 16:22 8C fdr #4 T/O, closed at 15:47 (locally) 8C fdr #5 T/O, closed at 14:28 8D fdr #1 T/O, closed at 16:09 8D fdr #2 T/O, closed at 16:09 8D fdr #3 T/O, closed at 16:22 8D fdr #5 T/O, closed at 16:50 8D fdr #6 T/O, closed at 13:25 8D fdr #7 T/O, closed at 13:26 8D fdr #8 T/O, closed at 13:26 8D fdr #9 T/O, closed at 13:27 8D fdr #10 T/O, closed at 15:46 8D fdr #11 T/O, closed at 16:10 MNS fdr #4 T/O, closed at 16:24 MNS fdr #5 T/O, closed at 15:49 SRM fdr #1 T/O, closed at 14:42 (locally) CKB fdr #1 T/O, closed at 15:15 (locally) CKB fdr #5 T/O, closed at 13:27 CKB fdr #6 T/O, closed at 13:27 PTP fdr #3 T/O, closed at 15:25 PTP fdr #4 T/O, closed at 15:26 PTP fdr #6 T/O, closed at 16:37 BKS fdr #3 T/O, closed at 15:02 BKS fdr #5 T/O, closed at 14:19 BKS fdr #6 T/O, closed at 16:00 PTN fdr #2 T/O, closed at 16:26 RKN fdr #2 T/O, closed at 16:24 RKN fdr #3 T/O, closed at 16:20 RKN fdr #4 T/O, closed at 16:55 PGT fdr #1 T/O, closed at 16:27 PGT fdr #2 T/O, closed at 16:27 LBO fdr #1 T/O, closed at 16:26 (locally) LBO fdr #2 T/O, closed at 16:27 (locally) PNG fdr #1 T/O, closed at 13:39 BLM fdr #1 T/O, closed at 14:45 NLA fdr #1 T/O, closed at 13:49 MGL fdr #1 T/O, closed at 13:45 MGL fdr #2 T/O, closed at 13:46 STG fdr #1 T/O, closed at 13:49 STG fdr #2 T/O, closed at 13:50 BTG fdr #2 T/O, closed at 14:35 CD fdr #16 T/O, closed at 14:43 ND fdr #7 T/O, closed at 14:57 ND fdr #9 T/O, closed at 14:57 ND fdr #11 T/O, closed at 14:57 Cause: Under Investigation Continue to next page ..…… JDE Number = 0 | 1
| 2020-05-16 12:00 | May | 12:00 | Afternoon | Saturday | Weekends | 16 | 2020 | 2020-05-16 12:21 | KOTABATAK JUNCTION SW STA | Petko | PGT South | Fair | Under investigation | 9492 | continued from May 16, at 12:00... 12:20 Put to Online MGT #6, OK 12:21 Man Open 6DN fdr #2 (R/ Mira GS 3) – Maintain level tank 12:23 Put to Online MGT #7, OK 12:27 Put to Online MGT #1, OK 12:29 Put to Online MGT #2, OK 12:30 Put to Online MGT #3, OK 12:32 Man Open 8D fdr #7 (R/ Warik GS 2) – Maintain level tank 12:40 Man Open MNS fdr #1 (R/ Mira GS 3) – Maintain level tank, closed at 16:24 Man Open MNS fdr #2 (R/ Mira GS 3) – Maintain level tank, closed at 15:51 12:54 Man Open MNS fdr #6 (R/Mira GS 3) – Maintain level tank, closed at 16:52 Man Open 6D fdr #6 (R/ Mira – GS 3) – Maintain level tank, closed 19:13 12:56 Man Open CD fdr #7 – decrease load bus 4 to online CGT/4, close at 13:22 13:12 Man Open CD fdr #9 – decrease load bus 4 to online CGT/4, close at 13:22 13:20 CGT #4 back to online 12:45 Begin load restoration at North Area 13:57 S/U CGT #2 14:30 Man Open CD fdr #2 / decrease load bus 1 to online CGT/2, close at 14:38 14:35 CGT #2 put to Online, OK 14:36 NDC #3 put to Online, OK 15:11 MGT #10 put to Online, OK 15:25 Begin load restoration in South Area 16:07 NDC/1 back to Online 16:55 Close last feeder North Area (complete North Area restoration) 17:30 HRSG NDC 1 startup process then continue with HRSG NDC 3 18:06 NDC HRSG/1 Online 19:23 Close last feeder South Area, complete restoration Production loss record: / South Area Total 5708 Bbls / 633 Wells / North Area Total 3577 Bbls / 422 Wells / HO Area Total 1535 Bbls / 1069 Wells /////////////////////////////////////////////////////// + / Grand Total 10820 Bbls / 2124 Wells Cause: Under Investigation | 1
57 | 2020-05-16 21:44 | May | 21:44 | Night | Saturday | Weekends | 16 | 2020 | 2020-05-16 21:44 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Fair | Emergency | - | 21:44 Manually opened 8C VCB feeder# 1. Manually closed at 12:03 (17/May/2020). 21:44 Manually opened 8C VCB feeder# 2. Manually closed at 11:39 (17/May/2020). 21:45 Manually opened 8C VCB feeder# 3, Manually closed at 00:16 (17/May/2020). 21:45 Manually opened 8D OCB feeder# 1. Manually closed at 13:04 (17/May/2020). 21:45 Manually opened 8D OCB feeder# 2, Manually closed at 05:38 (17/May/2020). 21:50 Manually opened 8D OCB feeder# 11 22:05 Manually opened 8D OCB feeder# 5, Manually closed at 05:39 (17/May/2020). 22:10 Manually opened 8D OCB feeder# 10, Manually closed at 06:00 (17/May/2020). 22:16 Manually opened Minas ACB #1 (Minas feeder #4). Manually closed at 11:37 (17/May/2020). 22:21 Manually opened Minas ACB #13 (Minas feeder #2), Manually closed at 22:54. 23:55 Manually opened 8D OCB feeder #3. Manually closed at 13:35 (17/May/2020). Due to 30" main line water pipe leaks /broken. (Request from GS#1). Cause: Emergency. | 1
| 2020-05-16 21:44 | May | 21:44 | Night | Saturday | Weekends | 16 | 2020 | 2020-05-17 08:29 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Fair | Emergency | - | 08:29 Manually Opened 8D OCB feeder #2. Manually closed at 15:15 Manually Opened 8D OCB feeder #5. Manually closed at 14:43. Manual Open 8D OCB feeder #10. Manually closed at 11:37 Manual Close Minas fdr #4 11:39 Manual Close 8C fdr #2 12:03 Manual Close 8C fdr #1 13:04 Manual Close 8D fdr #1 13:35 Manual Close 8D fdr #3 (request by GS/1 (Faisal) related to emergency case at Field Area/1) 30" main line water pipe leaks /broken. Cause: Emergency | 1
58 | 2020-05-17 05:55 | May | 5:55 | Morning | Sunday | Weekends | 17 | 2020 | 2020-05-17 05:55 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Fair | Unidentified | - | 8C VCB Fdr # 6 T/R 1X Not Checked yet. | 1
| 2020-05-17 05:55 | May | 5:55 | Morning | Sunday | Weekends | 17 | 2020 | 2020-05-19 14:13 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Fair | Unidentified | - | Checked and found 8C VCB fdr #6 T/R 1x, ctr: 635/636, R/F: 51N Patrolled the line but found nothing. Cause : Unidentified | 1
59 | 2020-05-17 11:23 | May | 11:23 | Morning | Sunday | Weekends | 17 | 2020 | 2020-05-17 11:23 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Normal Condition | - | Menggala GFPC T/R 1x Menggala feeder #2 load dropped 185A (208/23A). Not checked yet. | 1
| 2020-05-17 11:23 | May | 11:23 | Morning | Sunday | Weekends | 17 | 2020 | 2020-05-19 11:23 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Normal Condition | - | Checked and found Menggala Feeder 2 T/R 1X counter: 569/570, R/F : 81 (under Frequency), caused by outage on May 16th Patrolled and found nothing. Cause: Normal Operation | 1
60 | 2020-05-17 12:04 | May | 12:04 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-05-17 12:04 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Normal Condition | 7 | S.Balam feeder #1 load dropped 97A (151/54A). S.Balam feeder #2 load dropped 66A (70/4A). S.Balam feeder #3 load dropped 133A (133/0A). S.Balam feeder #4 load dropped 18A (217/199A). Not checked yet. | 1
| 2020-05-17 12:04 | May | 12:04 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-05-18 12:04 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Normal Condition | 7 | Checked and found So Balam Feeder 1 T/R 1X counter: 415/416, R/F : 81 (under Frequency), caused by outage on May 16th. patrolled and found nothing. Cause: Normal Operation | 1
61 | 2020-05-17 12:11 | May | 12:11 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-05-17 12:11 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 43 | Menggala OCB feeder #1 T/R 1x. Menggala feeder #2 load dropped 176A (208/32A). Menggala GFPC T/R 1x. 16:04 Checked and found Menggala OCB feeder#1 T/R 1x. Counter: 286/287 R/F: 51@3. Patrolled the line nothing found. Cause: Suspected Lightning. | 1
62 | 2020-05-17 13:51 | May | 13:51 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-05-17 13:51 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Cloudy | Unidentified | - | Batang GFPC T/R 1x Not Checked Yet | 1
| 2020-05-17 13:51 | May | 13:51 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-05-25 16:15 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Cloudy | Unidentified | - | Checked and found RCL GFPC of Batang SS on normal condition, counter: 1023 Cause: Unidentified | 1
63 | 2020-05-17 16:04 | May | 16:04 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-05-17 16:04 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Heavy Rain | Unidentified | - | 16:04 Reported no power at location 6E/6F and around Gelatik and complex 16:34 Checked and found RCL 7E/67A T/SO, ctr: 94 / 96 16:36 Manual Close RCL 7E/67A, Ok Cause: Not Patrolled Yet | 1
| 2020-05-17 16:04 | May | 16:04 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-05-19 14:25 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Heavy Rain | Unidentified | - | Patrolled the line on May 18th, but found nothing Cause: Unidentified | 1
64 | 2020-05-17 18:29 | May | 18:29 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-05-20 07:13 | 13.8KV RANGAU FEEDER #1 | Bekasap | PGT North | Rain | Unidentified | - | Checked and found VCB RGU fdr #1 T/R 1x, ctr: 40 / 41, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
| 2020-05-17 18:29 | May | 18:29 | Afternoon | Sunday | Weekends | 17 | 2020 | 2020-05-20 07:13 | 13.8KV RANGAU FEEDER #1 | Bekasap | PGT North | Rain | Unidentified | - | Checked and found VCB RGU fdr #1 T/R 1x, ctr: 40 / 41, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
65 | 2020-05-18 07:31 | May | 7:31 | Morning | Monday | Weekdays | 18 | 2020 | 2020-05-18 07:31 | 44KV PEMATANG MAIN / PETANI LINE | Bekasap | PGT North | Fair | Unidentified | 109 | 07:31 44 kV PMT Main GCB #1 (line to PTN) T/R 1x / Petani Substation is down / Petani fdr #1 and Petani fdr #2 no power Not Checked Yet | 1
| 2020-05-18 07:31 | May | 7:31 | Morning | Monday | Weekdays | 18 | 2020 | 2020-05-21 08:12 | 44KV PEMATANG MAIN / PETANI LINE | Bekasap | PGT North | Fair | Unidentified | 109 | Checked and found: PMT Main GCB #1 T/R 1x, Counter : 198 / 200, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
66 | 2020-05-18 07:31 | May | 7:31 | Morning | Monday | Weekdays | 18 | 2020 | 2020-05-18 07:31 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Fair | Follow Another Outage | - | 07:31 PMT fdr #1 load dropped 113 A (197 / 84 A) PMT fdr #2 load dropped 9 A (108 / 99 A) RGU fdr #2 load dropped 21 A (147 / 126 A) Cause: Follow Another Outage (PMM GCB #1 to PTN SS T/R 1x) | 1
67 | 2020-05-18 10:00 | May | 10:00 | Morning | Monday | Weekdays | 18 | 2020 | 2020-05-18 10:00 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Tree | 179 | 10:00 CD ACB fdr #2 T/O (on block for PT WKS clean up canals) Counter: 405 / 406, R/F: 50P @1 @2 Calls PT WKS at field and reported Normal/OK 10:49 Patrolled the line and found fallen tree at pole 40/BA/35 Remove the fallen tree and finished at 11:09 11:11 Manually Close CD ACB fdr #2, OK CD ACB fdr #2 leave on Block position for PT WKS. Cause: Tree | 1
68 | 2020-05-18 10:39 | May | 10:39 | Morning | Monday | Weekdays | 18 | 2020 | 2020-05-18 10:39 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 7 | 10:39 Manually Open RCL 36/DN/32A, closed at 11:11 (MTCE team to repair broken insulator o/p 4E/34 and 5D/156) Impact 14 wells OFF at area 3 Cause: Planned Maintenance | 1
69 | 2020-05-18 14:46 | May | 14:46 | Afternoon | Monday | Weekdays | 18 | 2020 | 2020-05-18 14:46 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 9 | 14:46 Manual Open RCL 5E/83, closed at 15:35 (Maintenance team to replace broken insulator o/p 5E/18) Cause: Planned Maintenance | 1
70 | 2020-05-18 16:07 | May | 16:07 | Afternoon | Monday | Weekdays | 18 | 2020 | 2020-05-18 16:07 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Planned Maintenance | - | 16:07 It was reported broken Jumper Recl. 40/BA/02. 16:58 Manually opened C Duri ACB #12 (feeder #2). Due to repair bypass jumpers on pole 40/BA/02. 17:12 Manually blocked and closed C Duri ACB #12 (feeder #2). and then released the block. Cause: Planned maintenance. \ | 1
71 | 2020-05-19 06:02 | May | 6:02 | Morning | Tuesday | Weekdays | 19 | 2020 | 2020-05-19 06:02 | ROKAN SUBSTATION | Bangko-Balam | PGT North | Fair | Animal | 246 | 06:02 115 kV C/S Rokan Substation T/O. Rokan TXP is Down. Rokan fdr #2, fdr #3 and fdr #4 no power. RTU failed for Rokan, Ketigul and Petani Substation. 06:03 Bekasap Bus and line over voltage, reach to 15.01 kV. Bekasap fdr #3 load drop 25A ( 273/248A). Bekasap fdr #1 load drop 134A ( 188/54A). Pematang fdr #1 load drop 162A ( 200/38A). Rangau fdr #2 load drop 49 A ( 151/102A). Rangau fdr #2 load drop 49A ( 151/102A). Menggala and S. Balam Bus and line over voltage, reach to 14.72 kV S.Balam fdr #1 load drop 51A ( 151/100A). S.Balam fdr #3 load drop 106A ( 141/35A). S.Balam fdr #4 load drop 111A ( 210/209A). Manggala fdr #1 load drop 134A ( 188/54A). Manggala fdr #2 load drop 137A ( 155/18A). Bangko /Nella Bus and line over voltage, reach to 15.83 kV. Bangko fdr #1 load drop 139A ( 171/32A). Bangko fdr #2 load drop 102A ( 252/180A). Bangko fdr #3 load drop 130A ( 195/65A). Nella fdr #1 load drop 123A ( 211/88A). Nella fdr #2 load drop 45A ( 70/25A). Sintong fdr #1 load drop 96A ( 103/6A). Sintong fdr #2 load drop 213A ( 251/38A). Pinang fdr #1 load drop 42A ( 107/65A ). 09:17 Checked and found: / C/S for TXP Rokan T/O, visual blades of C/S still close (spring discharge). / 13.8 kV VCB fdr #2, fdr #3 and fdr #4 are close. / All Relays are OFF (no power). / TX visual condition is Normal, status OK. / Died animal (monkey) on TX base surface. 09:20 Reset Contactor K2 on rectifier of Rokan SS. / DC power has been transferred to battery system / Relays , RTU and IT equipment back to online / Check Relay Flag at T60 Relay but found no indication/no R/F / Manual Open VCB fdr #2. / Manual Open VCB fdr #3. / Manual Open VCB fdr #4. 09:30 Manual Crank visual isolation blades of C/S Rokan SS, OK (spring charge). 09:35 Manually Close C/S Rokan SS, OK (TXP Rokan has been energized). 09:37 Manually Close VCB Rokan fdr #2, OK. 09:38 Manually Close VCB Rokan fdr #3, OK. Manually Close VCB Rokan fdr #4, OK. 09:39 Rokan Substation back to Normal. Cause: Animal (monkey). Production Loss: Bangko fdr #1 : 22 Bbls / 40 wells. Bangko fdr #2 : 16 Bbls / 31 wells. Nella fdr #1 : 18 Bbls / 31 wells. Nella fdr #2 l : 2 Bbls / 11 wells. Rokan Sub. : 88 Bbls / 7 Wells. /////////////////////////////////////////+ Total Loss : 144 Bbls / 120 Wells. | 1
72 | 2020-05-20 01:22 | May | 1:22 | Night | Wednesday | Weekdays | 20 | 2020 | 2020-05-20 01:22 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 36 | Ketigul 13.8Kv VCB #2 T/R 1x. Ketigul feeder #1 load dropped 14A (111/251A). Not checked yet. | 1
| 2020-05-20 01:22 | May | 1:22 | Night | Wednesday | Weekdays | 20 | 2020 | 2020-05-22 08:52 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 36 | Checked and found: PKTGL/13.8VCB2 None, Counter : 384 / 384, Relay Flag : NONE. Patrolled the line found : Tidak ada temuan dilapangan setelah patrol dilakukan Cause : Unidentified | 1
73 | 2020-05-20 05:59 | May | 5:59 | Morning | Wednesday | Weekdays | 20 | 2020 | 2020-05-20 05:59 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Fair | Animal | 47 | 05:59 N.Duri VCB feeder #7 T/LO. 07:39 Checked & found, N.Duri VCB fdr#7 T/LO. R/F: 51 @A & @B, Counter: 140/145. Patrolled The line and found, a death squirell hanging on @2, on bypass Recloser. 10/L1/17. (The Recloser status on Bypass position) 08:04 Blocked and closed N.Duri VCB feeder#7, then released the block. (The power back to normal). Cause: Animal (squirrel). | 1
74 | 2020-05-20 10:35 | May | 10:35 | Morning | Wednesday | Weekdays | 20 | 2020 | 2020-05-20 10:35 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Planned Maintenance | - | 10:35 Manual Open Rokan 13.8KV VCB fdr #2 for PM service. ( Load transfer to Rokan fdr #4). Cause: Plan Maintenance. | 1
75 | 2020-05-20 10:39 | May | 10:39 | Morning | Wednesday | Weekdays | 20 | 2020 | 2020-05-20 10:39 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Fair | Planned Maintenance | 37 | 10:39 Manual Open LBS: 04/01/01. Changed over 112.5Kva TX op: 04/02/02. 11:52 Closed LBS: 04/01/01. Cause: Plan Maintenance. | 1
76 | 2020-05-20 10:40 | May | 10:40 | Morning | Wednesday | Weekdays | 20 | 2020 | 2020-05-20 10:40 | 13.8KV CENTRAL DURI FEEDER #4 | Duri | PGT North | Fair | Tree | 72 | 10:40 C. Duri fdr #4 T/LO ctr:528/532 R/F: 50@3, 51@1, @2. Patrolled the line and found the Tree touched power line between o/p 09/Q7/01 and 09/Q7/2. 11:28 Blocked and closed C. Duri fdr #4. Ok than released the block. Cause: Tree. | 1
77 | 2020-05-20 18:41 | May | 18:41 | Afternoon | Wednesday | Weekdays | 20 | 2020 | 2020-05-20 18:41 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Dead End Insulator | 31 | Ketigul fdr #2 T/R 1X. Not checked yet. | 1
| 2020-05-20 18:41 | May | 18:41 | Afternoon | Wednesday | Weekdays | 20 | 2020 | 2020-05-22 08:49 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Dead End Insulator | 31 | Checked and found: PKTGL/13.8VCB2 T/R, Counter : 384 / 385, Relay Flag : 51. Patrolled the line found : R/F 51 Phase B deadend Flash Over Cause : Dead End Insulator | 1
78 | 2020-05-21 06:26 | May | 6:26 | Morning | Thursday | Weekdays | 21 | 2020 | 2020-05-21 06:26 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Fair | Unidentified | - | Batang GFPC T/R 1x (fault indication d/s Batang VCB fdr #3) No load dropped at any feeders Not Checked Yet | 1
| 2020-05-21 06:26 | May | 6:26 | Morning | Thursday | Weekdays | 21 | 2020 | 2020-05-25 16:14 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Fair | Unidentified | - | Checked and found RCL GFPC of Batang SS on normal condition, counter: 1023 Cause: Unidentified | 1
79 | 2020-05-21 07:41 | May | 7:41 | Morning | Thursday | Weekdays | 21 | 2020 | 2020-05-21 07:41 | ROKAN SUBSTATION | Bangko-Balam | PGT North | Fair | Under investigation | 32 | 07:41 Rokan 115KV C/S T/O ctr: 228/229 R/F: 51N, 51@3. (No power to Rokan Substation, Rokan fdr # and Rokan fdr #4). Petani fdr #1 load dropped 45A (240/195A). Bangko fdr #4 load dropped 50A (195/145A). 09:08 Checked and found Rokan 115KV C/S T/O ctr: 228/229 R/F: 51N, 51@3. Also Checked Rokan transforme, found Normal condition. 09:10 Manual Open Rokan VCB fdr #3, Closed at 09:27. 09:11 Manual Open Rokan VCB fdr #3, Closed at 09:29. 09:17 Closed 115KV Rokan C/S, OK. Cause: Under Investigation. | 1
80 | 2020-05-21 22:26 | May | 22:26 | Night | Thursday | Weekdays | 21 | 2020 | 2020-05-21 22:26 | 13.8KV MINAS FEEDER #5 | Minas | PGT South | Fair | Unidentified | - | Minas ACB/26 fdr #5 T/R 1x, counter: 97/98, R/F: 51N Not Patrolled Yet | 1
| 2020-05-21 22:26 | May | 22:26 | Night | Thursday | Weekdays | 21 | 2020 | 2020-05-22 15:30 | 13.8KV MINAS FEEDER #5 | Minas | PGT South | Fair | Unidentified | - | Patrolled the line but found nothing Cause: Unidentified | 1
81 | 2020-05-22 06:13 | May | 6:13 | Morning | Friday | Weekdays | 22 | 2020 | 2020-05-22 06:13 | 13.8KV DARLING VCB FEEDER #6 | Duri | PGT North | Fair | Broken Fuse Cut Out | 0 | Darling VCB fdr #6 T/SO Darling feeder #3 load dropped 50 A (146 / 96 A) Darling GFPC T/O Not Checked Yet | 1
| 2020-05-22 06:13 | May | 6:13 | Morning | Friday | Weekdays | 22 | 2020 | 2020-05-23 16:00 | 13.8KV DARLING VCB FEEDER #6 | Duri | PGT North | Fair | Broken Fuse Cut Out | 0 | Checked and found DRL VCB fdr #6 T/SO, ctr: 1444/1445, R/F: 51N Patrolled the power line and found broken F/CO near CGS/5 gate @1 @2 Cause : Broken Fuse Cut Out | 1
82 | 2020-05-22 06:14 | May | 6:14 | Morning | Friday | Weekdays | 22 | 2020 | 2020-05-22 06:14 | 13.8KV DARLING VCB FEEDER #8 | Duri | PGT North | Fair | Normal Condition | 0 | Darling feeder #8 load dropped 15 A (29 / 14 A) // 51% Not Checked Yet | 1
| 2020-05-22 06:14 | May | 6:14 | Morning | Friday | Weekdays | 22 | 2020 | 2020-05-25 10:37 | 13.8KV DARLING VCB FEEDER #8 | Duri | PGT North | Fair | Normal Condition | 0 | Checked and found all protection device on normal condition. Cause: Normal Operation | 1
83 | 2020-05-22 06:14 | May | 6:14 | Morning | Friday | Weekdays | 22 | 2020 | 2020-05-22 06:14 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Normal Condition | 68 | Darling fdr #3 load dropped 50 A (146 / 96 A) Not Checked Yet | 1
| 2020-05-22 06:14 | May | 6:14 | Morning | Friday | Weekdays | 22 | 2020 | 2020-05-25 10:27 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Normal Condition | 68 | Checked and found all protection devices on normal condition. Cause: Normal Operation | 1
84 | 2020-05-22 06:54 | May | 6:54 | Morning | Friday | Weekdays | 22 | 2020 | 2020-05-22 06:54 | 13.8KV CENTRAL DURI FEEDER #14 | Duri | PGT North | Fair | Animal | 68 | 06:54 C. Duri fdr #14 load dropped 36A (2230187A). 07:75 It was reported no power at 05/P3/14. 10:55 Checked and found Recloser 05/P3/02 T/O (On blocked PT WKS clean Canal). Patrolled the line and found Dead Monkey at %00KVA TX at SST/5. 11:00 Blocked and Closed the Recloser. OK. Cause: Animal (Monkey). | 1
85 | 2020-05-22 11:09 | May | 11:09 | Morning | Friday | Weekdays | 22 | 2020 | 2020-05-22 11:09 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Fair | Planned Maintenance | 211 | 11:09 Manual Open C. Duri fdr #9 to repair Jumper o/p: SDD/06. 13:13 Closed C. Duri fdr #9. Cause: Plan Maintenance. | 1
86 | 2020-05-22 15:13 | May | 15:13 | Afternoon | Friday | Weekdays | 22 | 2020 | 2020-05-22 15:13 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 58 | Menggala 13.8KV VCB fdr#2 T/R 1x. Menggala feeder #1 load dropped 129A (189/160A). Not checked yet. | 1
| 2020-05-22 15:13 | May | 15:13 | Afternoon | Friday | Weekdays | 22 | 2020 | 2020-05-27 07:17 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 58 | Checked and found: MGLSB/13.8OCB2 T/R, Counter : 570 / 571, Relay Flag : 51N Patrolled the line found : Broken Pin Insulator 80 % Cause : Lightning | 1
87 | 2020-05-23 09:05 | May | 9:05 | Morning | Saturday | Weekends | 23 | 2020 | 2020-05-23 09:05 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 09:05 S/U NDC #2 the unit then on line 09:40. | 1
88 | 2020-05-23 14:54 | May | 14:54 | Afternoon | Saturday | Weekends | 23 | 2020 | 2020-05-23 14:54 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 14:54 Off line & S/D MGT #10. | 1
89 | 2020-05-23 15:48 | May | 15:48 | Afternoon | Saturday | Weekends | 23 | 2020 | 2020-05-23 15:48 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 15:48 Off line & S/D MGT #9. | 1
90 | 2020-05-24 15:51 | May | 15:51 | Afternoon | Sunday | Weekends | 24 | 2020 | 2020-05-24 15:51 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Tree | 0 | NKBS OCB feeder #1 T/R 1x. NKBS GFPC T/R 1x. Not checked yet. | 1
| 2020-05-24 15:51 | May | 15:51 | Afternoon | Sunday | Weekends | 24 | 2020 | 2020-05-25 15:51 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Tree | 0 | Checked and found NKBS OCB feeder #1 T/R 1x, Counter: 277/278 R/F: 51@1 & @2. Patrolled the line and found palm tree touching the power line between poles 27/CV/52 to 27/CV/53. Cause : Tree. | 1
91 | 2020-05-25 06:09 | May | 6:09 | Morning | Monday | Weekdays | 25 | 2020 | 2020-05-25 06:09 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Lightning Arrester | 0 | CD ACB/28 feeder #16 T/R 1x, counter: 379/380, R/F: 51N Not Checked Yet | 1
| 2020-05-25 06:09 | May | 6:09 | Morning | Monday | Weekdays | 25 | 2020 | 2020-05-25 10:28 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Lightning Arrester | 0 | Checked and found CDRSG/13.8ACB28 T/R 1x R/F: 51N Counter: 379/380. Patrolled the line and found broken Lightning Arrester on pole 09/M7/05 @2. Cause : Lightning Arrester | 1
92 | 2020-05-25 14:44 | May | 14:44 | Afternoon | Monday | Weekdays | 25 | 2020 | 2020-05-25 14:44 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:44 CDGT #3 Trip. 15:19 S/U CDGT #3 the online then unit 15:33. | 1
| 2020-05-25 14:44 | May | 14:44 | Afternoon | Monday | Weekdays | 25 | 2020 | 2020-05-25 14:44 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:44:01 CDGT #5 Trip. 15:00 S/U CDGT #5 the online then unit 15:15. | 1
93 | 2020-05-25 14:50 | May | 14:50 | Afternoon | Monday | Weekdays | 25 | 2020 | 2020-05-25 14:50 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Pin Insulator | 54 | Sintong 13.8Kv VCB #2 T/R. Sintong feeder #1 load drooped 49A (100/51A) Not checked yet. | 1
| 2020-05-25 14:50 | May | 14:50 | Afternoon | Monday | Weekdays | 25 | 2020 | 2020-05-27 07:37 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Pin Insulator | 54 | Checked and found Sintong OCB feeder #2 T/R 3x. Counter : 516 / 519 Relay Flag : 51N Patrolled the line found @1 broken Pin Insulator towards well Sintong #30. Cause : Pin insulator. | 1
94 | 2020-05-25 18:46 | May | 18:46 | Afternoon | Monday | Weekdays | 25 | 2020 | 2020-05-25 18:46 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Unidentified | 60 | Ketigul VCB #2 T/R 2x. Ketigul feeder #1 load dropped 107A (128/21A). Ketigul feeder #3 load dropped 41A (42/1A). Not checked yet. | 1
| 2020-05-25 18:46 | May | 18:46 | Afternoon | Monday | Weekdays | 25 | 2020 | 2020-05-26 17:22 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Unidentified | 60 | Checked and found KTGL VCB fdr #2 T/R 3x, counter: 386/389, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
95 | 2020-05-25 19:05 | May | 19:05 | Night | Monday | Weekdays | 25 | 2020 | 2020-05-25 19:05 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Pin Insulator | 0 | Sintong 13.8 kV VCB #2 T/R 1x. Not checked yet. | 1
| 2020-05-25 19:05 | May | 19:05 | Night | Monday | Weekdays | 25 | 2020 | 2020-05-27 07:25 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Pin Insulator | 0 | Checked and found Sintong OCB feeder #2 T/R 3x. Counter : 516 / 519 Relay Flag : 51N Patrolled the line found @1 broken Pin Insulator towards well Sintong #30. Cause : Pin insulator. | 1
96 | 2020-05-26 10:28 | May | 10:28 | Morning | Tuesday | Weekdays | 26 | 2020 | 2020-05-26 10:28 | 13.8KV NORTH DURI FEEDER #11 | Duri | PGT North | Fair | Tree | 91 | 10:28 N.Duri feeder #11 load dropped 17A (67/50A). 11:28 It was reported no power o/p 13/E11/10 D/S N.Duri feeder #11. 12:00 Checked & found recloser 13/F3/49 T/So. R/f 51 @1 Ctr:78/79. 12:02 Blocked and Closed recloser 13/F3/49 OK. Cause: Tree (suspected). | 1
97 | 2020-05-26 10:45 | May | 10:45 | Morning | Tuesday | Weekdays | 26 | 2020 | 2020-05-26 10:45 | 13.8KV 8C FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 23 | 10:45 Manually open 8C OCB feeder #2. Due to: 1. C/O @1 broken dead end insulator on Terminal polle well #8DC/14. 2. C/O @2 broken Pin insulator on pole 9D/176. 3. C/O @3 broken Pin insulator on pole 9D/51. 12:00 Manually blocked and Closed 8C OCB feeder #2, and then released the block. Cause: Planned maintenance. | 1
98 | 2020-05-26 15:34 | May | 15:34 | Afternoon | Tuesday | Weekdays | 26 | 2020 | 2020-05-26 15:34 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain | Lightning | 49 | 3D 13.8Kv OCB #4 T/R 1x. 3D feeder #2 load dropped 45A (193/148A). 3D feeder #3 load dropped 27A (84/57A). Not checked yet. | 1
| 2020-05-26 15:34 | May | 15:34 | Afternoon | Tuesday | Weekdays | 26 | 2020 | 2020-01-06 14:21 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Rain | Lightning | 49 | Checked and found 3D OCB feeder #4 T/R 2x. Counter: 112/180 R/F:50@2,@3. Patrolled the line nothing found. Cause : Unidentified. | 1
99 | 2020-05-26 18:29 | May | 18:29 | Afternoon | Tuesday | Weekdays | 26 | 2020 | 2020-05-26 18:29 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Rain | Emergency | 0 | 18:29 Manually open Pamatang feeder #2 due to High level tank. (WIP Problem). | 1
100 | 2020-05-26 18:57 | May | 18:57 | Afternoon | Tuesday | Weekdays | 26 | 2020 | 2020-05-26 18:57 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Rain | Lightning | 0 | Minas ACB#14 (feeder #1) T/R 1x. Not patrolled yet. | 1
| 2020-05-26 18:57 | May | 18:57 | Afternoon | Tuesday | Weekdays | 26 | 2020 | 2020-01-06 14:28 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Rain | Lightning | 0 | Checked and found Minas ACB #14 (feeder #1) T/R 1x. Counter: 94/95 R/F: 51@1. Patrolled the line nothing found. Cause : Suspected Lightning. | 1
101 | 2020-05-26 19:14 | May | 19:14 | Night | Tuesday | Weekdays | 26 | 2020 | 2020-05-26 19:14 | 13.8KV 5B FEEDER #1 | Minas | PGT South | Rain | Lightning | 26 | 5B OCB feeder #1 T/R 1x. Not checked yet. | 1
| 2020-05-26 19:14 | May | 19:14 | Night | Tuesday | Weekdays | 26 | 2020 | 2020-01-06 14:19 | 13.8KV 5B FEEDER #1 | Minas | PGT South | Rain | Lightning | 26 | Checked and found 5B OCB feeder #1 T/R 3x. Counter: 276/279 R/F: 51@1,@2. Patrolled the line nothing found. Cause: Suspected lightning. | 1
102 | 2020-05-27 05:57 | May | 5:57 | Morning | Wednesday | Weekdays | 27 | 2020 | 2020-05-27 05:57 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Fair | Tree | 0 | Central Duri ACB feeder #6 T/R 1x ctr: 522/523 R/F:51N, 51G Not Patrolled Yet | 1
| 2020-05-27 05:57 | May | 5:57 | Morning | Wednesday | Weekdays | 27 | 2020 | 2020-05-27 10:55 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Fair | Tree | 0 | Checked and found ACB CD fdr #6 T/R 1x, Counter : 522 / 523, R/F : 51N, 51G Patrolled the line found high trees and broken Pin Insulator @1 o/p 01/01/30 Cause : Tree | 1
103 | 2020-05-27 10:00 | May | 10:00 | Morning | Wednesday | Weekdays | 27 | 2020 | 2020-05-27 10:00 | 13.8KV 5B FEEDER #5 | Minas | PGT South | Fair | Planned Maintenance | 6 | 10:00 Manually opened 5B fdr# 5 To Replace Dead end and Pin insulator. 12:23 Blocked & closed 5B fdr#5, then release the block. Cause: Plan Maintenance. | 1
104 | 2020-05-27 11:27 | May | 11:27 | Morning | Wednesday | Weekdays | 27 | 2020 | 2020-05-27 11:27 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | C.Duri Fdr# 1 load drop 52 A ( 146 / 94 A ) Not checked yet. | 1
| 2020-05-27 11:27 | May | 11:27 | Morning | Wednesday | Weekdays | 27 | 2020 | 2020-01-06 14:37 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found Recloser: 41/AW/62 T/R 3x. Counter: 341/344 R/F: None. Patrolled the line nothing found. Cause: Unidentified. | 1
105 | 2020-05-27 14:03 | May | 14:03 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-05-27 14:03 | 13.8KV 5B FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 25 | 14:03 Manually opened 5B fdr# 1 Cut high palm trees 15:00 Blocked & closed 5B fdr#1, then release the block. Cause: Plan Maintenance. | 1
106 | 2020-05-27 16:33 | May | 16:33 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-05-27 16:33 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Rain and Lightning | Unidentified (Fuse) | 78 | Petani fdr# 1 T/R 1X Not checked yet. | 1
| 2020-05-27 16:33 | May | 16:33 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-01-06 14:43 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Rain and Lightning | Unidentified (Fuse) | 78 | Checked and found Petani OCB feeder #1 T/R 1x. Counter: 158/159 R/F: 51N. Patrolled the line found @1,@2 and @3 broken fuse on pole 33/AY/98. Cause : Broken Fuse. | 1
107 | 2020-05-27 17:02 | May | 17:02 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-05-27 17:02 | 13.8KV BATANG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | Batang fdr#2 T/R 1x. Batang GFPC T/R 1x. Not checked yet. | 1
| 2020-05-27 17:02 | May | 17:02 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-05-28 15:37 | 13.8KV BATANG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | Checked and found BTG VCB feeder #2 T/R 3x, Counter : 198 / 201, R/F : 51N Patrolled the line found: / Broken LA @2 at R. BAIS #22, / Broken Pin Insulator @1 o/p 35/AE/18 near RB #07, / Broken Pin Insulator @1 o/p 35 AE 02 / Broken LA @2 o/p 35/AF/29 Cause : Lightning Arrester | 1
108 | 2020-05-27 17:03 | May | 17:03 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-05-27 17:03 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Tree | 75 | 17:03 Batang fdr#3 T/r 1x. Batang GFPC T/R 1x. 17:08 Batang fdr#3 T/r 1x. Batang GFPC T/R 1x. 17:21 Batang fdr#3 T/r 1x. Batang GFPC T/R 1x. Not checked yet. | 1
| 2020-05-27 17:03 | May | 17:03 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-05-28 15:30 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain and Lightning | Tree | 75 | Checked and found BTG VCB feeder #3 T/R 3x, Counter: 394 / 397, R/F: 51P Patrolled the line found palm trees touch the power line and had burned marks. Cause : Tree | 1
109 | 2020-05-27 17:45 | May | 17:45 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-05-27 17:45 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 27 | Nella fdr#2 T/R 1x. Not checked yet. | 1
110 | 2020-05-27 18:48 | May | 18:48 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-05-27 18:48 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Dumai | PGT North | Rain and Lightning | Lightning | - | Dumai 4160kV VCB # 22 (feeder #4) T/R 1x. Not checked yet. | 1
| 2020-05-27 18:48 | May | 18:48 | Afternoon | Wednesday | Weekdays | 27 | 2020 | 2020-01-06 14:51 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Dumai | PGT North | Rain and Lightning | Lightning | - | Checked and found Dumai 4160kV VCB # 22 (feeder #4) T/R 1x. Counter: 298/299 R/F: 50@2. Patrolled the line nothing found. Cause: Suspected Lightning. | 1
111 | 2020-05-28 07:31 | May | 7:31 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-05-28 07:31 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Animal | 59 | 07:31 Manggala Fdr# 2 T/R 2 X Not Checked yet. | 1
112 | 2020-05-28 10:09 | May | 10:09 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-05-28 10:09 | 13.8KV PETAPAHAN FEEDER #6 | Petko | PGT South | Fair | Planned Maintenance | 43 | 10:09 Manually opened Petapahan fdr # 6 Repair broken jumper o/p 31 CZ 05 and replace broken L/A at terminal Pole Petapahan # 25. 11:08 Blocked and closed Petapahan Fdr # 6 then release block. Cause : Plan Maintenance. | 1
113 | 2020-05-28 10:25 | May | 10:25 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-05-28 10:25 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 30 | 10:25 Manually opened Recl 23 BD 01. Replace broken Fuse and install secondary protection o/p 22BD09. 10:40 Blocked and Closed recl 23BD01, then release the block. cause: Plan maintenance. | 1
114 | 2020-05-28 10:47 | May | 10:47 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-05-28 10:47 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Fair | Planned Maintenance | 45 | 10:47 Manually opened Recl 7D/150 Open Hot Line clamp for LTC wells. 11:40 Blocked and Closed Recl then release Block Plan maintenance. | 1
115 | 2020-05-28 10:58 | May | 10:58 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-05-28 10:58 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Fair | Lightning Arrester | 0 | Darling VCB Fdr# 7 T/R 1X Not checked yet. | 1
| 2020-05-28 10:58 | May | 10:58 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-01-06 14:59 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Fair | Lightning Arrester | 0 | Checked and found Darling VCB feeder #7 T/R 1x. Counter: 190/191 R/F: 51@1,@2 and @3. Patrolled the line found @1,@2,@3 broken Lightning Arrester on pole SA/01, behind CSS Area #6. Cause : Lightning Arrester. | 1
116 | 2020-05-28 11:15 | May | 11:15 | Morning | Thursday | Weekdays | 28 | 2020 | 2020-05-28 11:15 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Fair | Planned Maintenance | 120 | 11:15 Manually open Recl 23 BW 02 D/S Libo Fdr# 2, Open HLC O/P 23 BW 14 Dismantle LTC wells. 14:10 Blocked and Closed Recl 23 BW 02 then release Block. Plan Maintenance. | 1
117 | 2020-05-29 01:13 | May | 1:13 | Night | Friday | Weekdays | 29 | 2020 | 2020-05-29 01:13 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 27 | Nella fdr #2 T/R 1X. Prod loss: 30 BBLS /19 Well. Nella fdr #1 load dropped 113A (194/81A) Prod loss: 27BBLS/15 Well. Not checked yet. | 1
118 | 2020-05-29 06:03 | May | 6:03 | Morning | Friday | Weekdays | 29 | 2020 | 2020-05-29 06:03 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Rain | Lightning | 0 | 06:03 Menggala fdr #2 load dropped 11A (151/140A). 15:00 Patrolled the line but found nothing. Cause: Unidentified. | 1
119 | 2020-05-29 11:30 | May | 11:30 | Morning | Friday | Weekdays | 29 | 2020 | 2020-05-29 11:30 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Fair | Lightning | 46 | 11:30 Minas Fdr # 6 T/R 1X Ctr:202/203 R/F: 51@2@3. 12:50 Checked and found Recl 7E/67A T/SO Ctr:96/97. 12:52 Blocked and Closed Recl 7E/67A, then release block. 17:00 Patrolled the line but found nothing. Cause: Unidentified. | 1
| 2020-05-29 11:30 | May | 11:30 | Morning | Friday | Weekdays | 29 | 2020 | 2020-05-29 14:10 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Fair | Lightning | 46 | Checked and found: MNSSG/13.8ACB18 T/R, Counter : 202 / 203, Relay Flag : 51 Date Patrol : 29/MAY/2020 Patrolled the line : Not Found Cause : Lightning | 1
120 | 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-05-30 20:25 | 13.8KV 5B FEEDER #4 | Minas | PGT South | Rain and Lightning | Load Shedding | 12 | 20:25 5B 13.8Kv OCB fdr #4 T/SO. 22:07 Checked & found 5B feeder #4 T/LO Ctr :714 / 715 R/F: 81. 22:14 Blocked & Closed 5B feeder #4 //>OK. Cause : Load Shedding | 1
| 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-05-06 13:25 | 13.8KV 5B FEEDER #4 | Minas | PGT South | Rain and Lightning | Load Shedding | 12 | Checked and found: 5BSB/13.8OCB4 T/SO, Counter : 714 / 715, Relay Flag : 81. Patrolled the line found: No Patrol Cause : Load Shedding | 1
121 | 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-05-30 20:25 | 13.8KV 5B FEEDER #5 | Minas | PGT South | Rain and Lightning | Load Shedding | 2 | 20:25 5B 13.8Kv OCB fdr #5 T/SO. 22:07 Checked & found 5B feeder #5 T/LO Ctr: 340 / 341 R/F: 81. 22:14 Blocked & Closed 5B feeder #5 //>OK. Cause : Control failure. | 1
| 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-05-06 13:26 | 13.8KV 5B FEEDER #5 | Minas | PGT South | Rain and Lightning | Load Shedding | 2 | Checked and found: 5BSB/13.8OCB5 T/SO, Counter : 340 / 341, Relay Flag : 81 Patrolled the line found : No Patrol Cause : Load Shedding | 1
122 | 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-05-30 20:25 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Rain and Lightning | Unidentified | 13 | 5B 13.8Kv OCB fdr #7 T/R 1x. Not checked yet. | 1
| 2020-05-30 20:25 | May | 20:25 | Night | Saturday | Weekends | 30 | 2020 | 2020-05-06 13:25 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Rain and Lightning | Unidentified | 13 | Checked and found OCB fdr #7 T/R 1x, ctr: 499 / 500, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
123 | 2020-05-31 02:51 | May | 2:51 | Night | Sunday | Weekends | 31 | 2020 | 2020-05-31 02:51 | 13.8KV 3D FEEDER #8 | Minas | PGT South | Fair | Others | 0 | 3D fdr #8 Load dropped 165A (2375/110A). Not checked yet. | 1
| 2020-05-31 02:51 | May | 2:51 | Night | Sunday | Weekends | 31 | 2020 | 2020-03-06 13:40 | 13.8KV 3D FEEDER #8 | Minas | PGT South | Fair | Others | 0 | Checked and found protection devices on Normal Condition Suspect HPS pump OFF Cause : Others | 1
124 | 2020-05-31 02:55 | May | 2:55 | Night | Sunday | Weekends | 31 | 2020 | 2020-05-31 02:55 | 13.8KV 3D FEEDER #5 | Minas | PGT South | Fair | Others | 0 | 3D fdr #5 Load Dropped 102A (104/2A)////WIP. Not checked yet. | 1
| 2020-05-31 02:55 | May | 2:55 | Night | Sunday | Weekends | 31 | 2020 | 2020-03-06 13:55 | 13.8KV 3D FEEDER #5 | Minas | PGT South | Fair | Others | 0 | Checked and found protection devices on Normal Condition Suspect HPS pump OFF at GS/5 Cause : Others | 1
125 | 2020-05-31 02:55 | May | 2:55 | Night | Sunday | Weekends | 31 | 2020 | 2020-05-31 02:55 | 13.8KV 3D FEEDER #6 | Minas | PGT South | Fair | Others | 0 | 3D fdr #6 Load Dropped 125A(126/1A)////WIP. Not checked yet. | 1
| 2020-05-31 02:55 | May | 2:55 | Night | Sunday | Weekends | 31 | 2020 | 2020-03-06 13:55 | 13.8KV 3D FEEDER #6 | Minas | PGT South | Fair | Others | 0 | Checked and found protection devices on Normal Condition Suspect HPS pump OFF at GS/5 Cause : Others | 1
126 | 2020-05-31 11:41 | May | 11:41 | Morning | Sunday | Weekends | 31 | 2020 | 2020-05-31 11:41 | NORTH DURI POWER PLANT | Duri | PGT North | Fair | Under investigation | 357 | 11:41 NDC#2 Trip, Load Shedding Level#4, Freq: 59,65. N.Duri 230Kv GCB#21 T/O, then closed at 14:35. N.Duri 230Kv GCB#23 T/O, then closed at 14:35. 3D fdr#2 T/O, then Closed at 13:01. 3D fdr#3 T/O, then Closed at 13:09. 3D fdr#5 T/O, then Closed at 11:56. 3D fdr#6 T/O, then Closed at 11:55. 4D fdr#2 T/O, then Closed at 13:00. 4D fdr#3 T/O, then Closed at 13:00. 4B fdr#1 T/O, then Closed at 12:26. 4B fdr#4 T/O, then Closed at 11:47. 4B fdr#5 T/O, then Closed at 11:48. 4B fdr#6 T/O, then Closed at 13:08. 5B fdr#8 T/O, then Closed at 12:53. 5B fdr#7 T/O, then Closed at 13:28. 5B fdr#6 T/R 1x 5B fdr#5 T/O, then Closed at 12:26. 5B fdr#4 T/O, then Closed at 12:25. 5B fdr#3 T/O, then Closed at 13:00. 5B fdr#1 T/O, then Closed at 12:59. 8D fdr#1 T/O, then Closed at 13:24. 8D fdr#3 T/O, then Closed at 13:26. 8D fdr#10 T/O, then Closed at 12:17. 8C fdr#1 T/O, then Closed at 13:02. Suram fdr#1 T/O, then closed at 12:17. BOB Zamrud T/O, Closed 13:11. 12:30 S/U MGT#8 then O/L the unit at 12:55. 12:53 S/U CGT#2, then O/L the unit at 13:11. 13:20 S/U MGT#9, then O/L the unit at 13:39. 15:16 S/U NDC CT #2, then O/L the unit at 16:15. 16:41 Off Line CGT#2, then S/D the unit for S/B. 16:46 NDC#2 Trip again on load 22MW. 3D fdr#6 T/O, then closed at 17:46. 5B gfr#7 T/O, then closed at 17:51. 5B fdr#8 T/O, then closed at 18:22. 17:20 S/U MGT #10 then O/L the unit at 17:41. 20:15 S/U NDC CT #2 then O/L the Unit at 20:42. Cause: Under Investigation. Production Loss: GS #5/////>3D fdr #2 : 39 Bbls / 19 Wells. 3D fdr #3 : 28 Bbls / 17 Wells. 4D fdr #2 : 10 Bbls / 24 Wells. 4D fdr #3 : 8 Bbls / 11 Wells. GS #3/////>3D fdr #2 : 19 Bbls / 8 Wells. 5B fdr #1 : 34 bbls / 10 Wells. 5B fdr #3 : 12 bbls / 4 Wells. GS #1&2/////////////> : 282 Bbls / 69 Wells. GS # 6 /////////////> : 121 Bbls / 65 Wells. //////////////////////////////////////////////////+ TOTAL : 553 Bbls / 227 Wells. | 1
127 | 2020-05-31 12:30 | May | 12:30 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-05-31 12:30 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 12:30 S/U MGT #8 and then Online the unit at 12:55. | 1
128 | 2020-05-31 12:53 | May | 12:53 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-05-31 12:53 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 12:53 S/U CDGT #2 and then Online the unit at 13:11. | 1
129 | 2020-05-31 13:20 | May | 13:20 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-05-31 13:20 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 13:20 S/U MGT #9 and then Online the unit at 13:39. | 1
130 | 2020-05-31 15:16 | May | 15:16 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-05-31 15:16 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 15:16 S/U NDC #2 and then Online the unit at 16:15. | 1
131 | 2020-05-31 16:33 | May | 16:33 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-05-31 16:33 | MINAS POWER PLANT | Minas | PGT South |  |  | - | MGT#6 Trip by Alarm Generator Diff. Trip. | 1
132 | 2020-05-31 16:41 | May | 16:41 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-05-31 16:41 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | Off Line CGT#2, then S/D the unit for S/B. | 1
133 | 2020-05-31 16:46 | May | 16:46 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-05-31 16:46 | NORTH DURI POWER PLANT | Duri | PGT North | Fair | Under investigation | - | 16:46 NDC#2 Trip again at 22MW. 3D fdr#6 T/O, then closed at 17:46. 5B gfr#7 T/O, then closed at 17:51. 5B fdr#8 T/O, then closed at 18:22. Cause: Under Investigation. | 1
134 | 2020-05-31 17:24 | May | 17:24 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-05-31 17:24 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 17:24 S/U MGT#10, then on line the unit at 17:41. | 1
135 | 2020-05-31 18:21 | May | 18:21 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-05-31 18:21 | ROKAN SUBSTATION | Bangko-Balam | PGT North | Fair | Powerline / Jumper | 127 | 18:21 115Kv Rokan C/S T/O. 20:10 Checked and found Rokan C/S T/O ctr:...…...R/F: 51N. Checked TX condition, Normal. 21:05 Closed Rokan C/S but tripped again. 02:13 Found @1, @3 broken BUS Jumper. 02:20 Unplug Recl. 32/AW/09. Blocked Petani fdr #2. 02:53 Closed LBS: 32/AV/11, to Transfer load Rokan fdr #2 to Petani fdr #2. Isolated Rokan fdr #3 and Rokan fdr #4. 03:02 Closed LBS: RT/01 to transfer load Rokan fdr #4 to Petani fdr #2. (for Rokan fdr #3 will be Closed 4160V Tie breaker at Rokan WTP). Cause: Broken Jumper. Production Loss until 24:00: 127 Bbls / 6 Wells. | 1
| 2020-05-31 18:21 | May | 18:21 | Afternoon | Sunday | Weekends | 31 | 2020 | 2020-03-06 07:00 | ROKAN SUBSTATION | Bangko-Balam | PGT North | Fair | Powerline / Jumper | 127 | Checked and found: RKNSB/115CS T/O, Counter : 230 / 231, Relay Flag : 51 Patrolled the line found : Relay Flag 51N, 51 Phase A ditemukan Jumper dari cable 13.8kV untuk PT metering di BUS terbakar (Putus di phase A dan C) sehingga sudah di isolate Cause : Jumper | 1
136 | 2020-05-31 20:15 | May | 20:15 | Night | Sunday | Weekends | 31 | 2020 | 2020-05-31 20:15 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 20:15 S/U NDC #2 and then Online the unit at 20:42. | 1
1 | 2020-01-06 03:54 | January | 3:54 | Night | Monday | Weekdays | 6 | 2020 | 2020-01-06 03:54 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Rain and Lightning | Pin Insulator | - | C.Duri 13.8 kV ACB # 41 ( CD # 9 ) T/R 1X Not checked yet. | 1
| 2020-01-06 03:54 | January | 3:54 | Night | Monday | Weekdays | 6 | 2020 | 2020-02-06 18:29 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Rain and Lightning | Pin Insulator | - | Checked and found: CDRSG-13.8ACB41 T/R, Counter : 409 - 410, Relay Flag : 51 Patrolled the line found : Temuan hasil patrol dijumpai pin type insulator kondisinya pecah sekitar 80% di Area 04 Road 07 (04 07 22) di Phase 1 dan Broken LA di phase 2 di Pole 04 07 24(relay Flag Time over current 1/ 51Phase 1) Cause : Pin Insulator | 1
2 | 2020-01-06 07:47 | January | 7:47 | Morning | Monday | Weekdays | 6 | 2020 | 2020-01-06 07:47 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Lightning Arrester | 0 | NKBS 13.8 VCB #1 T/R 1x. Not checked yet. | 1
| 2020-01-06 07:47 | January | 7:47 | Morning | Monday | Weekdays | 6 | 2020 | 2020-02-06 14:08 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Lightning Arrester | 0 | Checked and found NKBS OCB feeder #1 T/R 1x. Counter: 278-279 R/F: 50@1. Patrolled the line found @1 broken lightning arrester at Terminal pole KB-173. Cause : Lightning Arrester. | 1
3 | 2020-01-06 08:23 | January | 8:23 | Morning | Monday | Weekdays | 6 | 2020 | 2020-01-06 08:23 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Unidentified | 77 | Petan 13.8Kv OCB #1 T/R 1x. Not checked yet. | 1
| 2020-01-06 08:23 | January | 8:23 | Morning | Monday | Weekdays | 6 | 2020 | 2020-03-06 15:17 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Unidentified | 77 | Checked and found PTN VCB fdr #1 T/R 1x, ctr: 159 - 160, R/F: 50P Patrolled the line but found nothing Cause : Unidentified | 1
4 | 2020-01-06 16:34 | January | 16:34 | Afternoon | Monday | Weekdays | 6 | 2020 | 2020-01-06 16:34 | 13.8KV DARLING VCB FEEDER #3 | Duri | PGT North | Fair | Others | 82 | 16:34 Darling 13.8Kv VCB #3 T/R 1x. Darling GFPC T/R. 17:00 Darling 13.8Kv VCB #3 T/SO Darling GFPC T/SO. 17:37 Checked & found Darling 13.8Kv VCB#3 T/SO Ctr:278-280 R/F:51@1,51G. Darling GFPC T/SO Ctr:370-372. Patrolled the line & found @1 Broken By Pass Recl. o/p 05-M7-24. 18:23 Dismantle @1@2@3 Broken By Pass Recl. o/p 05-M7-24. 18:38 Blocked & closed C.Duri ACB fdr#10, then release the block. 19:20 By Pass Darling TX-1 GFPC and Block. 19:24 Blocked Darling fdr #3, Ok then released the block. Cause: Broken By Pass Recloser. | 1
5 | 2020-01-06 16:46 | January | 16:46 | Afternoon | Monday | Weekdays | 6 | 2020 | 2020-01-06 16:46 | MINAS POWER PLANT | Minas | PGT South |  |  | - | Off Line MGT#10, them S/D the unit for S/B. | 1
6 | 2020-01-06 17:20 | January | 17:20 | Afternoon | Monday | Weekdays | 6 | 2020 | 2020-01-06 17:20 | MINAS POWER PLANT | Minas | PGT South |  |  | - | Off Line MGT#8, then S/D the unit for S/B. | 1
7 | 2020-02-06 06:14 | February | 6:14 | Morning | Thursday | Weekdays | 6 | 2020 | 2020-02-06 06:14 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain | Unidentified | - | C.Duri Fdr # 1 load drop 56 A ( 146 - 90A ) Not checked yet. | 1
| 2020-02-06 06:14 | February | 6:14 | Morning | Thursday | Weekdays | 6 | 2020 | 2020-05-06 07:08 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain | Unidentified | - | Checked and found RCL 41-AW-62 T/R 2x, ctr: 344-346, R/F: None Patrolled the line but found nothing Cause : Unidentified | 1
8 | 2020-02-06 10:30 | February | 10:30 | Morning | Thursday | Weekdays | 6 | 2020 | 2020-02-06 10:30 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 33 | 10:30 Manually open LBS 3A-22 (4B feeder #1). C/O broken FCO at T/P well 2A-33. 13:43 Manually Closed LBS 3A-22 (4B feeder #1) --->Ok. cause : Plan maintenance. | 1
9 | 2020-03-06 10:24 | March | 10:24 | Morning | Friday | Weekdays | 6 | 2020 | 2020-03-06 10:24 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Fair | Dead End Insulator | 35 | Pematang Fdr# 1 T/R 1X Pematang Fdr# 2 Load Dropped 30A ( 100-70 A) Not Checked yet. | 1
| 2020-03-06 10:24 | March | 10:24 | Morning | Friday | Weekdays | 6 | 2020 | 2020-05-06 07:32 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Fair | Dead End Insulator | 35 | Checked and found PMT OCB fdr #1 T/R 1x, R/F: 51N, ctr: 196 - 197 Patrolled the line and found broken dead end @3 on pole 34-BC-36 Cause : Dead End Insulator | 1
10 | 2020-04-06 07:10 | April | 7:10 | Morning | Monday | Weekdays | 6 | 2020 | 2020-04-06 07:10 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Unidentified | 209 | 07:10 BKO feeder #1 load dropped 60 A (166 - 106 A) 08:20 Checked and found RCL 23-X-08 T/SO Counter: 428 - 456, R/F: 51N, 51P @1 @2 Patrolled the line but found nothing. 10:17 Block and Close RCL 23-X-08, OK. then release block. Cause: Unidentified | 1
11 | 2020-04-06 08:28 | April | 8:28 | Morning | Monday | Weekdays | 6 | 2020 | 2020-04-06 08:28 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | Sintong fdr #1 load dropped 66 A (109 - 43 A) Not Checked Yet | 1
12 | 2020-04-06 08:28 | April | 8:28 | Morning | Monday | Weekdays | 6 | 2020 | 2020-04-06 08:28 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | Sintong fdr #2 load dropped 237 A (257 - 20 A) Not Checked Yet | 1
13 | 2020-04-06 09:25 | April | 9:25 | Morning | Monday | Weekdays | 6 | 2020 | 2020-04-06 09:25 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Cloudy | Dead End Insulator | - | DCM ACB #30 feeder #2 T/R 1x Not Checked Yet | 1
| 2020-04-06 09:25 | April | 9:25 | Morning | Monday | Weekdays | 6 | 2020 | 2020-07-06 13:14 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Cloudy | Dead End Insulator | - | Checked and found ACB-30 DCM feeder #2 T/R 1x, Counter: 123-124, R/F: 51N Patrolled the line and found flash over dead end @1 o/p 2F-14 Cause : Dead End Insulator | 1
14 | 2020-04-06 17:54 | April | 17:54 | Afternoon | Monday | Weekdays | 6 | 2020 | 2020-04-06 17:54 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | - | CD ACB feeder #16 T/R 1x, counter: 280 - 281, R/F: 51N Not Checked Yet | 1
| 2020-04-06 17:54 | April | 17:54 | Afternoon | Monday | Weekdays | 6 | 2020 | 2020-06-06 18:46 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | - | Checked and found ACB-28 CD feeder #16 T/R 1x, ctr: 380 - 381, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
15 | 2020-05-06 12:33 | May | 12:33 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-05-06 12:33 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Pin Insulator | 28 | CD fdr #1 load dropped 69 A (139 - 70 A) Not Checked Yet | 1
| 2020-05-06 12:33 | May | 12:33 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-07-06 13:13 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Pin Insulator | 28 | Checked and found RCL 41-AW-62 T/R 2x, Counter: 346 - 348, R/F: 51N Patrolled the line and found broken pin insulator @1 @3 o/p 40-AV-48 Cause : Pin Insulator | 1
16 | 2020-05-06 14:47 | May | 14:47 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-05-06 14:47 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Dead End Insulator | 0 | Duri Community VCB fdr #1 T/R 1x Not Checked Yet | 1
| 2020-05-06 14:47 | May | 14:47 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-06-06 18:45 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Dead End Insulator | 0 | Checked and found ACB-25 DCM feeder #1 T/R 1x, R/F: 51N, Counter: 156-157 Patrolled the line and found broken dead end insulator @3 o/p KT-45 Cause : Dead End Insulator | 1
17 | 2020-05-06 16:20 | May | 16:20 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-05-06 16:20 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Cloudy and Lightning | Lightning | 259 | 16:20 Minas ACB-1 fdr #4 T/LO, counter: 113 - 115, R/F: 50P @1 @2, 51P @2 #3 Minas feeder #2 load dropped 66 A (276 - 210 A) Minas feeder #6 load dropped 37 A (121 - 84 A) 16:24 TDO Crew patrol the power line (finished at 17:10) but found nothing Got approval from TL TDO to manual close the ACB on block position. 17:19 Block and manual close ACB-1 Minas fdr #4, OK but tripped again after a few second. 17:21 Re-patrolled the power line 18:10 Separate the power line by open RCL 7D-150 and RCL 7D-121 18:16 Manual Close ACB-1 MNS fdr #4 (on block), OK. Continue to patrol the power line d/s of RCL but found nothing 18:39 Block and Manual Close RCL 7D-150, OK then release the block. 19:40 Block and Manual Close RCL 7D-121, OK then release the block. Minas Feeder #4 back to Normal Cause: Lightning | 1
| 2020-05-06 16:20 | May | 16:20 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-06-06 08:54 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Cloudy and Lightning | Lightning | 259 | Checked and found: MNSSG-13.8ACB01 T/LO, Counter : 113 - 115, Relay Flag : 51. Patrolled the line found : Unidentified Cause : Lightning | 1
18 | 2020-05-06 16:21 | May | 16:21 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-05-06 16:21 | MINAS POWER PLANT | Minas | PGT South | Rain and Lightning | Others | - | Minas GT-5 Tripped by alarm Generator Differential Trip | 1
19 | 2020-05-06 16:48 | May | 16:48 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-05-06 16:48 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain | Tree | - | BKS feeder #3 load dropped 88 A (250 - 162 A) Not Checked Yet | 1
| 2020-05-06 16:48 | May | 16:48 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-07-06 18:16 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain | Tree | - | Checked and found Bekasap VCB feeder #3 T/R 1x R/F 51N Ctr:1185 - 1186. Patrolled the line and found high palm tree between pole 35-BI-11 - 35-BI-12 . Cause : Tree | 1
20 | 2020-05-06 16:55 | May | 16:55 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-05-06 16:55 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Rain | Lightning Arrester | 0 | CD ACB-12 feeder #2 T/R 1x, R/F: 51 @2, Ctr: 407 - 408 Not Checked Yet | 1
| 2020-05-06 16:55 | May | 16:55 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-07-06 13:15 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Rain | Lightning Arrester | 0 | Patrolled the line on Jun 6th and found: - Broken LA @3 o/p SAA-14 - Broken LA @1 o/p SAA-15B Cause : Lightning Arrester | 1
21 | 2020-05-06 18:35 | May | 18:35 | Afternoon | Wednesday | Weekdays | 6 | 2020 | 2020-05-06 18:35 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Heavy Rain | Lightning | 65 | 18:35 BKO feeder #1 load dropped 114 A (166 - 52 A) BKO feeder #4 load dropped 66 A (194 - 128 A) -- WIP Benar GS OFF Not Checked Yet | 1
22 | 2020-06-06 10:24 | June | 10:24 | Morning | Saturday | Weekends | 6 | 2020 | 2020-06-06 10:24 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 10:24 MGT-5 S/U and then Online at 11:00 | 1
23 | 2020-07-06 23:59 | July | 23:59 | Night | Monday | Weekdays | 6 | 2020 | 2020-07-06 23:59 | CPI POWER SYSTEM |  |  |  | Normal Condition | - | Normal System Condition. | 1
24 | 2020-08-06 06:57 | August | 6:57 | Morning | Thursday | Weekdays | 6 | 2020 | 2020-08-06 06:57 | 13.8KV NORTH DURI FEEDER #9 | Duri | PGT North | Fair | Tree | 0 | ND VCB fdr #9 T/R 1x Not Checked Yet | 1
| 2020-08-06 06:57 | August | 6:57 | Morning | Thursday | Weekdays | 6 | 2020 | 2020-09-06 06:25 | 13.8KV NORTH DURI FEEDER #9 | Duri | PGT North | Fair | Tree | 0 | Checked and found ND fdr #9 T/R 1x, Counter: 84 - 85, R/F: 51N, 51P @1 @2 Patrolled the line and found fallen tree and touch the line near 11-H3-03 Cause : Tree | 1
25 | 2020-08-06 09:05 | August | 9:05 | Morning | Thursday | Weekdays | 6 | 2020 | 2020-08-06 09:05 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Duri | PGT North | Fair | Emergency | - | 09:05 Manual Open MSU VCB fdr #2 (BKS fdr #2), closed at 12:46 FON BKS Central Request to repair 12" suction valve WIP-B of BKS EOR Cause: Emergency (other team request) | 1
26 | 2020-08-06 09:59 | August | 9:59 | Morning | Thursday | Weekdays | 6 | 2020 | 2020-08-06 09:59 | 13.8KV 6D FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 59 | 09:59 Manually Open RCL 5C-42 (6D fdr #1), closed at 12:15 MTCE team to c/o insulator on pole 6B-01, 6B-08 and 5C-94. Caused: Planned Maintenance | 1
27 | 2020-08-06 19:05 | August | 19:05 | Night | Thursday | Weekdays | 6 | 2020 | 2020-08-06 19:05 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Transformer Failure | 65 | NKBS fdr #2 T/R 1x Not Checked Yet | 1
| 2020-08-06 19:05 | August | 19:05 | Night | Thursday | Weekdays | 6 | 2020 | 2020-09-06 14:18 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Transformer Failure | 65 | Checked and found NKB OCKB fdr #2 T/R 1x, Ctr: 99941 - 99942, R/F: 50N Patrolled the line and found failure TX (low megger at KB #30) Cause : Transformer Failure | 1
28 | 2020-08-06 19:36 | August | 19:36 | Night | Thursday | Weekdays | 6 | 2020 | 2020-08-06 19:36 | 13.8KV DARLING VCB FEEDER #6 | Duri | PGT North | Fair | Broken Fuse Cut Out | - | Darling Fdr#6 T/R 1X Not checked yet. | 1
| 2020-08-06 19:36 | August | 19:36 | Night | Thursday | Weekdays | 6 | 2020 | 2020-09-06 11:20 | 13.8KV DARLING VCB FEEDER #6 | Duri | PGT North | Fair | Broken Fuse Cut Out | - | Checked and found DRL VCB fdr #6 T/R 1x, ctr: 1444 (not change), R/F: 51N Patrolled the line and found broken FCO @3 at CGS #5 (2500 kVA) Cause : Broken Fuse Cut Out | 1
29 | 2020-09-06 08:19 | September | 8:19 | Morning | Sunday | Weekends | 6 | 2020 | 2020-09-06 08:19 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Construction Job | - | 08:19 Manual open Ketigul Fdr # 1 for Shutdown Pager GS to repair Gas Line,Gas Boot V2 ,V3 , V5. 20:19 Blocked and closed Ketigul Fdr#1 then release block. | 1
30 | 2020-09-06 08:19 | September | 8:19 | Morning | Sunday | Weekends | 6 | 2020 | 2020-09-06 08:19 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Construction Job | - | 08:19 Manual open Ketigul Fdr # 2 for Shutdown Pager GS to repair Gas Line,Gas Boot V2 ,V3 , V5. 20:37 Blocked and closed Ketigul Fdr#2 then release block. | 1
31 | 2020-09-06 08:19 | September | 8:19 | Morning | Sunday | Weekends | 6 | 2020 | 2020-09-06 08:19 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Fair | Construction Job | - | 08:19 Manual open Ketigul Fdr # 3 for Shutdown Pager GS to repair Gas Line,Gas Boot V2 ,V3 , V5. 20:37 Blocked and closed Ketigul Fdr#3 then release block. | 1
32 | 2020-09-06 08:39 | September | 8:39 | Morning | Sunday | Weekends | 6 | 2020 | 2020-09-06 08:39 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 134 | 08:39 Menggala fdr #1 load dropped 105 A (174 - 69 A) 09:50 Checked and found RCL 19-AN-04 T/O (on block position for PT WKS) Counter: 824 - 825, R/F: 51P @2, 51N Patrolled the line and found died monkey at MENO #12. Cause: Animal (monkey) | 1
33 | 2020-09-06 09:40 | September | 9:40 | Morning | Sunday | Weekends | 6 | 2020 | 2020-09-06 09:40 | 13.8KV 8C FEEDER #3 | Minas | PGT South | Fair | Others | 0 | 09:40 Manually Open RCL 8D-18A (8C fdr #3) Purpose: repair pole construction for project toll road near Sp. Perawang. Cause: Other (project) | 1
34 | 2020-09-06 10:41 | September | 10:41 | Morning | Sunday | Weekends | 6 | 2020 | 2020-09-06 10:41 | 13.8KV CENTRAL KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Relay Failure | 0 | 10:41 CKB fdr #2 T/R 1x, NKB fdr #5 load dropped 22 A (175 - 153) conformed by substation MTCE team in substation, that the back up relay (UR F35) was failure that triggered CB to Trip, isolate Relay for temporary. Cause: Relay Failure | 1
35 | 2020-10-06 08:33 | October | 8:33 | Morning | Tuesday | Weekdays | 6 | 2020 | 2020-10-06 08:33 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 08:33 S/U CDGT #2 the online then unit 08:57. | 1
36 | 2020-10-06 09:10 | October | 9:10 | Morning | Tuesday | Weekdays | 6 | 2020 | 2020-10-06 09:10 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 09:10 Off line CDGT #3 the S/D 10:03. | 1
37 | 2020-10-06 09:29 | October | 9:29 | Morning | Tuesday | Weekdays | 6 | 2020 | 2020-10-06 09:29 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 19 | 09:29 Manually open recloser 9D-14A (8C feeder #1). Repair broken conductor o/p 9D-112 (7Well down during the job). 12:05 Manually closed recloser 9D-14A (8c feeder #1) OK. cause : Plain maintenance. | 1
38 | 2020-10-06 10:25 | October | 10:25 | Morning | Tuesday | Weekdays | 6 | 2020 | 2020-10-06 10:25 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Dead End Insulator | 0 | C.Duri 13.8Kv ACB #28 fdr#16 T/R. Ctr: 381-384 R/f :50 @1 & @2 Not checked yet. | 1
| 2020-10-06 10:25 | October | 10:25 | Morning | Tuesday | Weekdays | 6 | 2020 | 14-06-2020 08:03 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Dead End Insulator | 0 | Checked and found 13.8 kV VCB #28 T/R 3x R/F 51N @1 Counter: 381 - 384. Patrolled the line and found broken dead end insulator on pole 3H3. Cause : Dead end insulator | 1
39 | 2020-10-06 10:36 | October | 10:36 | Morning | Tuesday | Weekdays | 6 | 2020 | 2020-10-06 10:36 | 13.8KV NEW KOTABATAK FEEDER #4 | Petko | PGT South | Fair | Planned Maintenance | 6 | 10:36 Manually open NKBS feeder #4. C/O 300Kva Tx at well 174. 11:05 Manually Closed NKBS feeder #4. OK 11:03 Manually open CKBS feeder #6. 11:30 Manually Closed CKBS feeder #6. OK cause : plan maintenance. | 1
40 | 2020-10-06 14:10 | October | 14:10 | Afternoon | Tuesday | Weekdays | 6 | 2020 | 2020-10-06 14:10 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Petko | PGT South | Cloudy | Lightning | 49 | CKBS 13.8Kv VCB #6 T/R 1x. Not checked yet. | 1
| 2020-10-06 14:10 | October | 14:10 | Afternoon | Tuesday | Weekdays | 6 | 2020 | 2020-11-06 15:53 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Petko | PGT South | Cloudy | Lightning | 49 | Checked and found CKBSSB-13.8VCB6 T/R 1x Ctr:154-155 R/F:51N. Patrolled the line & found @2 Flashed pin insulator o/p 34-CU-26. Cause : Lightning | 1
41 | 2020-10-06 15:35 | October | 15:35 | Afternoon | Tuesday | Weekdays | 6 | 2020 | 2020-10-06 15:35 | 13.8KV DARLING VCB FEEDER #6 | Duri | PGT North | Fair | Planned Maintenance | 25 | 15:35 Manually Open LBS 05-M7-20N D/S Darling feeder #6. C/O FCO for 2500Kva Tx-B at CGS #5. Manually Closed LBS 05-M7-20N (Darling feeder #6) OK. Cause : Plain maintenance. | 1
42 | 2020-10-06 16:52 | October | 16:52 | Afternoon | Tuesday | Weekdays | 6 | 2020 | 2020-10-06 16:52 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Recloser - Control Recloser | 258 | 16:52 S. Balam feeder #1 load dropped 100A (160-62A). 18:02 Checked and found Recl. 16-Z-25 T/SO ctr:104-105. Patrolled the line but found nothing. 18:29 Blocked and closed the Recl. OK then released the block. 22:40 Reported no power at location BLM #173, #125 and some other location 23:27 Checked and found RCL 16-Z-88 T/SO, ctr: 47-48 23:30 Block and manual close RCL the recloser, OK then release the block. Cause: Control Recloser failure. | 1
43 | 2020-11-06 07:01 | November | 7:01 | Morning | Friday | Weekdays | 6 | 2020 | 2020-11-06 07:01 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Emergency | 0 | 07:01 Manual open VCB Ketigul fdr#1 07:02 Manual open VCB Ketigul fdr#2 07:04 Manual open VCB Ketigul fdr#3 07:16 Manual open VCB Menggala fdr #2 Shut down pager GS to repair gas line gas boot V2, V3 and scrubber V5 14:48 Manually Closed VCB Ketigul fdr #2 OK. 15:07 Manually Closed VCB Ketigul fdr #3 OK. 15:22 Closed LBS 31-AL-4A Transfer load Ketigul fdr #1 to Ketigul fdr #2. (Ketigul feeder #1 PM Service). 15:39 Manually Closed Menggala fdr #2 Ok Cause: Emergency (Other team Request). | 1
44 | 2020-11-06 08:34 | November | 8:34 | Morning | Friday | Weekdays | 6 | 2020 | 2020-11-06 08:34 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 08:34 S/U CDGT #3 the online then unit 08:59. | 1
45 | 2020-11-06 09:41 | November | 9:41 | Morning | Friday | Weekdays | 6 | 2020 | 2020-11-06 09:41 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 09:41 CDGT #4 off line the S/D 09:42. | 1
46 | 2020-11-06 09:43 | November | 9:43 | Morning | Friday | Weekdays | 6 | 2020 | 2020-11-06 09:43 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Fair | Planned Maintenance | 0 | 09:43 Manually open LBS 03-08-08 D/S C.Duri feeder #3. Repair broken cross aram o/p 03-08-04. 14:26 Manually closed LBS 03-08-08 (C.Duri feeder #3) OK. Cause: Plain maintenance. | 1
47 | 2020-11-06 10:10 | November | 10:10 | Morning | Friday | Weekdays | 6 | 2020 | 2020-11-06 10:10 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 10:10 S/U MGT #8 the online then unit 11:14. | 1
48 | 2020-11-06 10:38 | November | 10:38 | Morning | Friday | Weekdays | 6 | 2020 | 2020-11-06 10:38 | 13.8KV 5B FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 21 | 10:38 Manually open 5B feeder #1. Repair hot spot o/p 5B-59. 11:29 Manually Closed 5B feeder #1 OK. Cause : Plan maintenance. | 1
49 | 2020-11-06 14:15 | November | 14:15 | Afternoon | Friday | Weekdays | 6 | 2020 | 2020-11-06 14:15 | MINAS POWER PLANT | Minas | PGT South |  |  | - | Off line and S/D MGT #9 at 14:15 for S/B. | 1
50 | 2020-12-06 19:15 | December | 19:15 | Night | Sunday | Weekends | 6 | 2020 | 2020-12-06 19:15 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain | Dead End Insulator | 20 | 19:15 BATANG VCB feeder #3 T/O (block for Rig BKU #02) at Pemburu #02 Confirmed to rig AU #02, normal condition 19:28 After got permitting from TL TDO, Manual Close VCB BTG fdr #3, OK Cause: Not Checked Yet | 1
| 2020-12-06 19:15 | December | 19:15 | Night | Sunday | Weekends | 6 | 2020 | 16-06-2020 07:13 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Rain | Dead End Insulator | 20 | Checked and found: BTGSB-13.8OCB3 T/R, Counter : 397 - 398, Relay Flag : 51N. Patrolled the line found : Dead end pecah Cause : Dead End Insulator | 1
51 | 2020-12-06 22:49 | December | 22:49 | Night | Sunday | Weekends | 6 | 2020 | 2020-12-06 22:49 | 4.16KV EAST RUMBAI FEEDER #1 | Rumbai | PGT South | Heavy Rain | Unidentified | 0 | East RUMBAI VCB fdr #1 T/R 1x Not Checked Yet | 1
| 2020-12-06 22:49 | December | 22:49 | Night | Sunday | Weekends | 6 | 2020 | 17-06-2020 16:26 | 4.16KV EAST RUMBAI FEEDER #1 | Rumbai | PGT South | Heavy Rain | Unidentified | 0 | Checked and found: ERBSB-4.16VCB1 T/R, Counter : 582 - 583, Relay Flag : 51N Patrolled the line found : Not Found Cause : Unidentified | 1
52 | 2020-12-06 23:41 | December | 23:41 | Night | Sunday | Weekends | 6 | 2020 | 2020-12-06 23:41 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Heavy Rain | Dead End Insulator | 350 | 23:41 Minas ACB-1 feeder #4 T/R1x 23:56 Minas ACB-1 feeder #4 T/LO Informed to TDO Crew (Sartoni) 00:27 Isolate part line of Minas fdr #4 by open RCL 7D-121 00:29 Block and manual close ACB-4 Minas fdr #1, OK then release the block Patrol line continue tomorrow due to heavy rain at field Cause: Not Patrolled Yet | 1
| 2020-12-06 23:41 | December | 23:41 | Night | Sunday | Weekends | 6 | 2020 | 13-06-2020 01:06 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Heavy Rain | Dead End Insulator | 350 | 02:08 Minas fdr #4 T/R 1x again, R/F: 51N, 51G Minas tie breaker #8 and #16 also Trip Minas RTU failed 03:11 Manual Close ACB #16 tie breaker bus 1 and bus 3 MGT, OK Suddenly ACB-1 Minas fdr #4 T/O, 03:18 Manual Close ACB #8 bus 1-2 tie breaker MGT, OK Crew patrol the power line but found nothing 03:59 Block and manual close ACB-1 Minas fdr #4 but failed/trip again 04:20 Re-patrol the power line and found broken dead end @1 on 8 pole structure behind of MGT yard 08:25 Racked Out Minas 13.8KV ACB fdr #4. 08:51 Manual Open Minas 13.8KV ACB fdr #3. Replaced Broken Dead end O/P-8 beside MGT plan. 09:23 Closed Minas 13.8KV ACB fdr #3. 09:42 Closed Minas 13.8KV ACB fdr #4. 10:03 Blocked and closed Recl. 7D-121, Ok then released the block. Cause: Broken Dead End. | 1
53 | 2020-06-13 01:41 | June | 1:41 | Night | Saturday | Weekends | 13 | 2020 | 2020-06-13 01:41 | 115KV MINAS / LUKUT LINE | Minas | PGT South | Heavy Rain | Others | 0 | 01:41 115 kV Line MINAS / LUKUT dropped 11 MW (17 / 6 MW) Call BOB SCADA to ensure the problem, there is a problem at power line through to Zamrud Fields. 09:21 Close Zamrud Field feeder #1, #2 and #4 Req. by BOB SCADA (Gatot) Cause: Others | 1
54 | 2020-06-13 08:43 | June | 8:43 | Morning | Saturday | Weekends | 13 | 2020 | 2020-06-13 08:43 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Cloudy | Unidentified | 0 | Darling feeder #7 T/R 1x. Darling feeder #4 load dropped 80A (94/14A). Not checked yet. | 1
| 2020-06-13 08:43 | June | 8:43 | Morning | Saturday | Weekends | 13 | 2020 | 2020-06-15 07:51 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Cloudy | Unidentified | 0 | Checked and found: DRLG7/13.8VCB7 T/R, Counter : 191 / 192 Flag, Relay : NONE. Patrolled the line found : Unidentified Cause : Unidentified | 1
55 | 2020-06-13 10:53 | June | 10:53 | Morning | Saturday | Weekends | 13 | 2020 | 2020-06-13 10:53 | DURI COMMUNITY SW GEAR | Duri | PGT North | Cloudy | Under investigation | 0 | 10:53 Duri Community ACB #34 T/SO ctr:131/132 R/F: 50@1, @2. 11:30 Checked and found, H/@1, @2 Burnt Out Bushing for 100KVA TX. Transfer DC Power Supply from Duri Field: 126VDC / 4A. Under Investigation. | 1
56 | 2020-06-14 05:29 | June | 5:29 | Morning | Sunday | Weekends | 14 | 2020 | 2020-06-14 05:29 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Normal Condition | 0 | North Duri feeder #2 load dropped 33 A (236 / 203 A) Not Checked Yet | 1
| 2020-06-14 05:29 | June | 5:29 | Morning | Sunday | Weekends | 14 | 2020 | 2020-06-17 08:04 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Normal Condition | 0 | Checked and found: CDRSG/13.8ACB28 T/R, Counter : 384 / 385, Relay Flag : 50 Patrolled the line found : ditemukan monyet mati di bawah tiang 09/N4/10 Cause : Animal | 1
57 | 2020-06-14 11:15 | June | 11:15 | Morning | Sunday | Weekends | 14 | 2020 | 2020-06-14 11:15 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 1 | 11:15 Manual Open Recloser 7D/93 d/s Minas fedder #3. Cementing Scondary cable protection at well 7D/93N. Three well down during the JOB: 7D/93, 7D/91, 8C/16, 15. 11:41 Closed Recloser 7D/93. Plan Maintenance. | 1
58 | 2020-06-14 15:02 | June | 15:02 | Afternoon | Sunday | Weekends | 14 | 2020 | 2020-06-14 15:02 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Animal | 0 | C. Duri 13.8KV ACB #28 (feeder #16) T/R 1x. Counter: 384/385 R/F:50@1, @2. Not patrolled yet. | 1
59 | 2020-06-15 07:21 | June | 7:21 | Morning | Monday | Weekdays | 15 | 2020 | 2020-06-15 07:21 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Fair | Lightning | 33 | Minas 13.8KV fdr #1 T/R 1X ctr:105/106 R/F: 51N. Not checked yet. | 1
| 2020-06-15 07:21 | June | 7:21 | Morning | Monday | Weekdays | 15 | 2020 | 2020-06-18 15:03 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Fair | Lightning | 33 | Checked and found: MNSSG/13.8ACB14 T/R, Counter : 105 / 106, Relay Flag : 51N Patrolled the line found : Not Found Cause : Lightning | 1
60 | 2020-06-15 07:57 | June | 7:57 | Morning | Monday | Weekdays | 15 | 2020 | 2020-06-15 07:57 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Recloser / Control Recloser | 308 | 07:57 S. Balam fdr #1 load dropped 99A )158/59A). 09:30 Checked and found Recl. 16/Z/25 T/SO ctr:105/106. Patrolled the line but found nothing. 10:16 Blocked and closed the Recloser, Ok tne released block and Unplug. Cause:Control Recloser. | 1
61 | 2020-06-15 09:47 | June | 9:47 | Morning | Monday | Weekdays | 15 | 2020 | 2020-06-15 09:47 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Fair | Normal Condition | 20 | 09:47 Batang fdr #3 load dropped 69A (71/2A). Batang fdr #1 load dropped 322A (34/2A). | 1
| 2020-06-15 09:47 | June | 9:47 | Morning | Monday | Weekdays | 15 | 2020 | 2020-06-18 07:17 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Fair | Normal Condition | 20 | Checked and found: 5441/R.36/AL/13 None, Counter : 172 / 172, Relay Flag : NONE Patrol led the line found: Counter recloser tidak ada yang berubah, dan tidak ada indikasi trip Cause : Normal Condition | 1
62 | 2020-06-15 10:00 | June | 10:00 | Morning | Monday | Weekdays | 15 | 2020 | 2020-06-15 10:00 | 13.8KV BATANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Powerline / Conductor | 0 | 10:00 Batang fdr #3 T/LO ctr:178/182 R/F: @151. It wsa reported Broken Conductor o/p: 39/AH/66 at Batang #18 . Isolation broken Conductor o/p 39_AH/66. 11:16 Blocked and closed Batang fdr #1, Ok then released block. 16:19 Manual open 13.8 kv batang fdr#1(PHE Req ). 17:01 Blocked and closed Batang fdr #1, Ok then released block. Cause: Broken Conductor. | 1
63 | 2020-06-15 12:04 | June | 12:04 | Afternoon | Monday | Weekdays | 15 | 2020 | 2020-06-15 12:04 | 13.8KV LIBO FEEDER #2 | Libo | PGT South | Fair | Planned Maintenance | 10 | 12:04 Manual Open LBS: 33/DC/6B. Dismantled power line at well Se. Libo#14. 12:47 Closed LBS: 33/DC/6B. Cause: Plan Maintenance. | 1
64 | 2020-06-15 14:46 | June | 14:46 | Afternoon | Monday | Weekdays | 15 | 2020 | 2020-06-15 14:46 | BEKASAP MAIN SUBSTATION | Bekasap | PGT North | Fair | Emergency | 0 | 14:46 It was reported (by Bekasap GS) production line leak (PBB ) Bekasap GS . Manual Open Bekasap fdr #2 (MSY fdr #2), Closed at 16:17. 14:47 Manual Open Bekasap fdr #3, Closed at 15:55.. 14:59 Manual Open Bekasap fdr #6, Closed at 16:36. Cause: Emergency. | 1
65 | 2020-06-16 10:46 | June | 10:46 | Morning | Tuesday | Weekdays | 16 | 2020 | 2020-06-16 10:46 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Planned Maintenance | 33 | 10:46 Manually Open 5B OCB feeder #7. Repaired Hot Spot at HLC o/p 4C/118 (by using PDKB SOP). 15:28 Manually blocked and closed 5B OCB feeder #7, and then released the block. Cause: Planed maintenance. | 1
66 | 2020-06-16 14:52 | June | 14:52 | Afternoon | Tuesday | Weekdays | 16 | 2020 | 2020-06-16 14:52 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Recloser | 65 | S. Balam fdr #1 load dropped 101A (161/60A). Not checked yet. | 1
67 | 2020-06-16 15:43 | June | 15:43 | Afternoon | Tuesday | Weekdays | 16 | 2020 | 2020-06-16 15:43 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Cloudy | Lightning | 260 | 15:43 CKB 13.8 kv fdr#5 T/R. Cause : Not checked yet. | 1
| 2020-06-16 15:43 | June | 15:43 | Afternoon | Tuesday | Weekdays | 16 | 2020 | 2020-06-17 14:34 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Petko | PGT South | Cloudy | Lightning | 260 | Checked and found: CKBSSB/13.8VCB5 T/R, Counter : 184 / 185, Relay Flag : 51N Patrolled the line found : Flash Over Pin Insulator Cause : Lightning | 1
68 | 2020-06-16 19:37 | June | 19:37 | Night | Tuesday | Weekdays | 16 | 2020 | 2020-06-16 19:37 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 19:37 MGT #8 Trip, will check tomorrow. Cause: Not checked yet | 1
69 | 2020-06-16 20:13 | June | 20:13 | Night | Tuesday | Weekdays | 16 | 2020 | 2020-06-16 20:13 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 20:13 S/U MGT #9, then O/L at 20:37 | 1
70 | 2020-06-17 06:08 | June | 6:08 | Morning | Wednesday | Weekdays | 17 | 2020 | 2020-06-17 06:08 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 31 | Ketigul VCB feeder #2 T/R 1x. Not patrolled yet. | 1
| 2020-06-17 06:08 | June | 6:08 | Morning | Wednesday | Weekdays | 17 | 2020 | 2020-06-19 17:57 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Dead End Insulator | 31 | Checked and found Ketigul VCB feeder #2 T/R 3x. Counter : 391 / 394 Relay Flag : 51N Patrolled the found @1 flash over dead end insulator on pole 29/AN/31. Cause: Dead end insulator. | 1
71 | 2020-06-17 09:55 | June | 9:55 | Morning | Wednesday | Weekdays | 17 | 2020 | 2020-06-17 09:55 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Powerline / Jumper | 28 | 09:55 It Was Reported no power at 10/K6/36 11:10 Checked and found broken jumper at @2 o/p 10/K4/41 11:20 Manual open Recl 10/K4/41 14:30 Blocked N.Duri Fdr#1 to repair broken jumper 15:00 Blocked and closed Recl 10/K4/41,then release block. Cause : Broken jumper. | 1
72 | 2020-06-17 15:50 | June | 15:50 | Afternoon | Wednesday | Weekdays | 17 | 2020 | 2020-06-17 15:50 | 13.8KV 8D FEEDER #9 | Minas | PGT South | Rain and Lightning | Lightning | 0 | 8D Feeder # 9 T/R 1X Not checked yet. | 1
| 2020-06-17 15:50 | June | 15:50 | Afternoon | Wednesday | Weekdays | 17 | 2020 | 2020-06-18 15:14 | 13.8KV 8D FEEDER #9 | Minas | PGT South | Rain and Lightning | Lightning | 0 | Checked and found 8D OCB feeder #9 T/R 1x. Counter : 108 / 109 Relay Flag : 50@2,@3 Patrolled the line nothing found. Cause : Suspected Lightning. | 1
73 | 2020-06-17 16:05 | June | 16:05 | Afternoon | Wednesday | Weekdays | 17 | 2020 | 2020-06-17 16:05 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Rain and Lightning | Unidentified | 30 | 8C Feeder # 6 T/R 1X 8C Feeder # 5 Load drop 139 A ( 147 / 8A ) 8C Feeder # 4 Load drop 227 A ( 241 / 13A ) Not checked yet. | 1
| 2020-06-17 16:05 | June | 16:05 | Afternoon | Wednesday | Weekdays | 17 | 2020 | 2020-06-18 15:18 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Rain and Lightning | Unidentified | 30 | Checked and found 8C VCB feeder #6 T/R 1x. Counter : 636 / 637, Relay Flag : 51@2,@3 Patrolled the line found nothing found. Cause : Suspected Lightning. | 1
74 | 2020-06-18 06:44 | June | 6:44 | Morning | Thursday | Weekdays | 18 | 2020 | 2020-06-18 06:44 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Rain | Unidentified | 0 | C.Duri Fdr#16 T/R 1X CTRL:385/386 R/F:51@1@2. Not patrolled yet. | 1
| 2020-06-18 06:44 | June | 6:44 | Morning | Thursday | Weekdays | 18 | 2020 | 2020-06-19 17:59 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Rain | Unidentified | 0 | Checked and found: CDRSG/13.8ACB28 T/R, Counter : 385 / 386, Relay Flag : 51 Patrolled the line found : No Findings Phase : 1, 2, Cause : Unidentified | 1
75 | 2020-06-18 15:01 | June | 15:01 | Afternoon | Thursday | Weekdays | 18 | 2020 | 2020-06-18 15:01 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Planned Maintenance | 8 | 15:01 Manually open 5B Feeder # 7. Repair hot spot at Loc 4C/45 Planned maintenance. | 1
76 | 2020-06-18 16:20 | June | 16:20 | Afternoon | Thursday | Weekdays | 18 | 2020 | 2020-06-18 16:20 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Cloudy | Pin Insulator | 0 | C.Duri fdr#6 T/R 1X Ctr:523/524 R/F:51N, 51@2. Not patrolled yet. | 1
| 2020-06-18 16:20 | June | 16:20 | Afternoon | Thursday | Weekdays | 18 | 2020 | 2020-06-20 09:06 | 13.8KV CENTRAL DURI FEEDER #6 | Duri | PGT North | Cloudy | Pin Insulator | 0 | Checked and found Central Duri ACB #23 (feeder #6) T/R 1x. Counter : 523 / 524, Relay Flag : 51N , 51@2. Patrol led the line found @2 broken pin insulator on pole 01/01/30. Cause : Broken Pin Insulator. | 1
77 | 2020-06-19 09:00 | June | 9:00 | Morning | Friday | Weekdays | 19 | 2020 | 2020-06-19 09:00 | 13.8KV NEW KOTABATAK FEEDER #3 | Petko | PGT South | Fair | Broken Fuse Holder | 104 | NKBS VCB feeder # 3 T/R 1x. Not checked yet. | 1
| 2020-06-19 09:00 | June | 9:00 | Morning | Friday | Weekdays | 19 | 2020 | 2020-06-22 08:08 | 13.8KV NEW KOTABATAK FEEDER #3 | Petko | PGT South | Fair | Broken Fuse Holder | 104 | Checked and found NKBS VCB feeder #3 T/R 2x. Counter: 325/327 Relay Flag: 50@1,@2. Patrolled the line found @1 and @2 broken fuse holder at well KB #170. Cause: Broken fuse holder. | 1
78 | 2020-06-19 16:09 | June | 16:09 | Afternoon | Friday | Weekdays | 19 | 2020 | 2020-06-19 16:09 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Unidentified | 20 | CKBS feeder #1 load dropped 21A (282/261A). Not checked yet. | 1
| 2020-06-19 16:09 | June | 16:09 | Afternoon | Friday | Weekdays | 19 | 2020 | 2020-06-23 07:20 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Unidentified | 20 | Checked and found all reclosers : 38/CW/08 , 38/CX/25 and 40/CY/16, Normal operation. Cause: Unidentified. | 1
79 | 2020-06-19 19:36 | June | 19:36 | Night | Friday | Weekdays | 19 | 2020 | 2020-06-19 19:36 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Pin Insulator | 78 | 19:36 Petani 13.8KV OCB Feeder#1 T/R 1x Cause: Not Patrolled Yet. | 1
| 2020-06-19 19:36 | June | 19:36 | Night | Friday | Weekdays | 19 | 2020 | 2020-06-24 11:19 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Pin Insulator | 78 | Checked and found PTN fdr #1 T/R 1x, ctr: 160 / 161, R/F: 51N Patrolled the line and found: / broken pin insulator @1 o/p 34/AZ/14 / spark LA @2 o/p 33/AY/61 Cause : Pin Insulator | 1
80 | 2020-06-20 04:54 | June | 4:54 | Morning | Saturday | Weekends | 20 | 2020 | 2020-06-20 04:54 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Rain | Tree | 75 | 04:54 6DN feeder #1 load dropped 82A (159/77A). 6DN feeder #2 load dropped 10A (255/245A). 08:37 Checked & found recloser 5E/05 T/LO Counter :301. Patrol the line & found Dahan sawit at pole 4E/08. 09:30 Blocked & Closed recloser 5E/05 then release the block. Cause : Tree. | 1
81 | 2020-06-20 10:50 | June | 10:50 | Morning | Saturday | Weekends | 20 | 2020 | 2020-06-20 10:50 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 10:50 S/U MGT #8, then O/L at 11:27. | 1
82 | 2020-06-20 11:45 | June | 11:45 | Morning | Saturday | Weekends | 20 | 2020 | 2020-06-20 11:45 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 43 | 11:45 Blocked Pinang feeder #1. Open HLC on top Pinang #12 (5 well off during the job). 15:14 Blocked and closed Pinang feeder #1 Ok. Plan maintenance . | 1
83 | 2020-06-20 17:10 | June | 17:10 | Afternoon | Saturday | Weekends | 20 | 2020 | 2020-06-20 17:10 | MINAS POWER PLANT | Minas | PGT South |  |  | - | Off line MGT # 7,then shut down the unit for standby. | 1
84 | 2020-06-21 17:34 | June | 17:34 | Afternoon | Sunday | Weekends | 21 | 2020 | 2020-06-21 17:34 | 13.8KV NORTH DURI / DUMAI FEEDER | Duri | PGT North | Fair | Under investigation | - | 17:34 N.Duri 13.8Kv VCB #14 T/O. (44KV line to Dumai off). 18:35 Checked and found 13.8KV ND/Dumai VCB #14 T/O ctr:168/169. Also found 44KV ND GCB #1 T/R ctr:152/153 RF:51 @1, @2. Checked TX condition Normal. 19:49 Open and Rack Out 4160V Dumai OCB #01, /////>Closed at 21:50. 19:50 Open and Rack Out 4160V Dumai OCB #02, /////>Closed at 21:51. 20:17 Manual Open 4160V VCB #12 Dumai fdr #1, /////>Closed at 21:51. 20:17 Manual Open 4160V VCB #22 Dumai fdr #4, /////>Closed at 21:54. 20:17 Manual Open 4160V VCB #23 Dumai fdr #5, /////>Closed at 21:54. 20:58 Patrolled the line but found nothing. 21:12 Manual Open 44KV ND GCB #1, /////>Closed at 21:18. 21:13 Closed 13.8KV ND VCB #14 (ND to Dumai Line). 21:25 Manual Open 4160V VCB #12 Dumai fdr #2, /////>Closed at 21:52. Checked and found: Dumai 4160V VCB 12 feeder #1 T/R 3X ctr:319/322. Dumai 4160V VCB 13 feeder #2 T/R 1X ctr:163/164. Dumai 4160V VCB 22 feeder #4 T/R 2X ctr:299/301. Dumai 4160V VCB 23 feeder #5 T/R 2X ctr:310/312. Cause: Under Investigation. | 1
85 | 2020-06-21 18:33 | June | 18:33 | Afternoon | Sunday | Weekends | 21 | 2020 | 2020-06-21 18:33 | 13.8KV NORTH DURI FEEDER #5 | Duri | PGT North | Fair | Unidentified | 0 | N.Duri 13.8Kv VCB #5 T/R 1x. Not checked yet. | 1
| 2020-06-21 18:33 | June | 18:33 | Afternoon | Sunday | Weekends | 21 | 2020 | 2020-06-26 15:38 | 13.8KV NORTH DURI FEEDER #5 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found N Duri VCB feeder #5 T/R 1x. Counter: 158/159 Relay Flag: 51N. Patrolled the line nothing found. Cause: Unidentified. | 1
86 | 2020-06-21 19:14 | June | 19:14 | Night | Sunday | Weekends | 21 | 2020 | 2020-06-21 19:14 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain | Lightning | 205 | 19:14 Menggala fdr #1 load dropped 138A (180/42A). 22:00 Checked and found Recl. 19/AN/04 T/O (In block due to PT RDF JOB). Patrolled the line, but found nothing. 22:08 Blocked and closed Recl. 19/AN/04, OK. Cause: Suspected Lightning. | 1
87 | 2020-06-21 19:14 | June | 19:14 | Night | Sunday | Weekends | 21 | 2020 | 2020-06-21 19:14 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Rain | Lightning | 0 | 19:14 Menggala fdr #2 load dropped 126A (155/29A). Not checked yet. | 1
88 | 2020-06-22 11:25 | June | 11:25 | Morning | Monday | Weekdays | 22 | 2020 | 2020-06-22 11:25 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 34 | 11:25 Sintong feeder #1 T/R 1X R/F 50 @1 Counter : 428/429 Sintong feeder #2 load drop 210A ( 254/44A ) Not patrolled yet. | 1
89 | 2020-06-22 20:43 | June | 20:43 | Night | Monday | Weekdays | 22 | 2020 | 2020-06-22 20:43 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Heavy Rain | Lightning | 4 | 20:43 4B fdr #2 T/O (In Blocked RIG ACS #15 at well 3D/76) 4B fdr #1 load dropped 48A (136/88A). Comfirmed to RIG ACS #15 activity, Normal. 21:16 Blocked and closed 4B fdr #2, OK and keep in Blocked for RIG activity. 22:08 Checked and found 4B fdr #2 T/O ctr:292/293 R/F: 51 @2, @3. Not patrolled yet. | 1
| 2020-06-22 20:43 | June | 20:43 | Night | Monday | Weekdays | 22 | 2020 | 2020-06-24 13:20 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Heavy Rain | Lightning | 4 | Patrolled the line on 23 Jun 2020, but found nothing Cause: Lightning | 1
90 | 2020-06-23 06:20 | June | 6:20 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-06-23 06:20 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Fair | Others | - | 06:20 Duri Community fdr #2 T/E 1X. Not checked yet. | 1
| 2020-06-23 06:20 | June | 6:20 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-06-24 11:28 | 13.8KV DURI COMMUNITY FEEDER #2 | Duri | PGT North | Fair | Others | - | Checked and found DCM fdr #2 T/R 1x, ctr: 124 / 125, R/F: 51P @1 @2 Patrolled the line and found flash over insulator @1 @2 of LBS o/p 2F/15/14 Cause : Others (insulator) | 1
91 | 2020-06-23 06:41 | June | 6:41 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-06-23 06:41 | 13.8KV 8D FEEDER #3 | Minas | PGT South | Fair | Lightning | 12 | 8D fdr #3 T/R 1X. not checked yet. | 1
| 2020-06-23 06:41 | June | 6:41 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-06-24 13:22 | 13.8KV 8D FEEDER #3 | Minas | PGT South | Fair | Lightning | 12 | Checked and found 8D VCB fdr #3 T/R 1x, ctr: 276 / 277, R/F: 50N Patrolled the line but found nothing Cause : Lightning | 1
92 | 2020-06-23 08:12 | June | 8:12 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-06-23 08:12 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 63 | 08:12 C.Duri VCB fdr#16 T/LO Ctr:386/390 R/F:51@1@2. 08:45 Patrolled the line but found nothing. 10:00 Blocked & closed C.Duri VCB fdr#16, then release the block. Cause: Unidentified. | 1
93 | 2020-06-23 10:00 | June | 10:00 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-06-23 10:00 | MINAS POWER PLANT | Minas | PGT South | Fair |  | - | MGT # 2 Status standby. | 1
94 | 2020-06-23 10:10 | June | 10:10 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-06-23 10:10 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 244 | 10:10 Manually Opened Pematang VCB fdr#2. Replaced @2 Broken Dead End Insulator o/p 34/BC/90B. Replaced @2 Broken Dead End Insulator T/P Pematang #75. 12:02 Blocked & closed Pematang VCB fdr#2, then release the block. Cause: Plan Maintenance. | 1
95 | 2020-06-23 10:19 | June | 10:19 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-06-23 10:19 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Planned Maintenance | 24 | 10:19 Manually Opened 5B fdr#7. Replaced Broken Pin Insulator o/p . 4C / 106;108;117 and 103 Replaced Broken LA o/p .4C / 115;116 and 113 12:48 Blocked & closed 5B fdr#7, then release the block. Cause: Plan Maintenance. | 1
96 | 2020-06-23 10:45 | June | 10:45 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-06-23 10:45 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | C.Duri ACB #11 (feeder#1) T/R 1x. Counter:289/290 R/F:51@1@2. Not patrolled yet. | 1
| 2020-06-23 10:45 | June | 10:45 | Morning | Tuesday | Weekdays | 23 | 2020 | 2020-06-25 17:45 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found CD fdr #1 T/R 1x, ctr: 289 / 290, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
97 | 2020-06-23 16:52 | June | 16:52 | Afternoon | Tuesday | Weekdays | 23 | 2020 | 2020-06-23 16:52 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 138 | 16:52 S.Balam Feeder # 1 T/O R/F 51N counter 416/417 Patrol the line but found nothing 17:57 Block and closed S.Balam Feeder # 1 ( still Block position Rig activities ). Cause : Unidentified. | 1
98 | 2020-06-24 07:11 | June | 7:11 | Morning | Wednesday | Weekdays | 24 | 2020 | 2020-06-24 07:11 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Dead End Insulator | 0 | C Duri ACB #28 (feeder #16) T/R 1x. Not Checked Yet. | 1
| 2020-06-24 07:11 | June | 7:11 | Morning | Wednesday | Weekdays | 24 | 2020 | 2020-06-26 15:43 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Dead End Insulator | 0 | Checked and found C Duri ACB #28 (feeder #16) T/R 1x. Counter: 390/391 Relay Flag: 51@1. Patrolled the line found @1 Flash over dead end insulator on pole: 09/P6/05. Cause: Dead end insulator. | 1
99 | 2020-06-24 12:27 | June | 12:27 | Afternoon | Wednesday | Weekdays | 24 | 2020 | 2020-06-24 12:27 | 13.8KV NORTH DURI FEEDER #11 | Duri | PGT North | Fair | Dead End Insulator | 0 | ND VCB feeder #11 T/R 1x. Not Checked Yet. | 1
| 2020-06-24 12:27 | June | 12:27 | Afternoon | Wednesday | Weekdays | 24 | 2020 | 2020-06-26 16:36 | 13.8KV NORTH DURI FEEDER #11 | Duri | PGT North | Fair | Dead End Insulator | 0 | Checked and found N Duri VCB #11 T/R 1x. Counter: 200/201 Relay Flag: 51@3. Patrolled the line found @3 Flash over dead end insulator on pole NN, (the second pole of N Duri Substation). Cause: Dead end insulator. | 1
100 | 2020-06-25 06:43 | June | 6:43 | Morning | Thursday | Weekdays | 25 | 2020 | 2020-06-25 06:43 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Others | 316 | 06:43 Sintong feeder # 2 T/R 1X Sintong Feeder # 1 Load Drop 36A ( 108/74A ) 07:19 Reported unbalanced voltage at Benar GS 07:21 Informed there is spark/lose connection at RCL 28/AF/02 07:41 Manual Open VCB Sintong fdr #2 to minimize spark at the Recloser Checked and found broken solid blade phase 3 at RCL 28/AF/02 08:42 Open isolation switch of VCB Sintong fdr #2 Maintenance team to repair the broken solid blade 09:22 Change out/repair solid blade has finished 09:29 Close Isolation Switch of VCB Sintong fdr #2 09:30 Manual Close VCB Sintong fdr #2, success Cause: Other (broken solid blade) | 1
101 | 2020-06-25 11:03 | June | 11:03 | Morning | Thursday | Weekdays | 25 | 2020 | 2020-06-25 11:03 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Planned Maintenance | 26 | 11:03 Manual Open VCB 5B fdr #7, closed at 13:42 MTCE team to change out pin insulator to pin post d/s of 5B #7 Cause: Planned Maintenance | 1
102 | 2020-06-25 20:53 | June | 20:53 | Night | Thursday | Weekdays | 25 | 2020 | 2020-06-25 20:53 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Rain | Tree | 47 | 20:53 5B feeder #2 load dropped 168A (191/23A). 22:50 Checked & found Recloser 5C/07 T/R 10x Ctr: 197/207. Cause: Not patrolled yet. | 1
| 2020-06-25 20:53 | June | 20:53 | Night | Thursday | Weekdays | 25 | 2020 | 2020-06-26 16:46 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Rain | Tree | 47 | Checked and found Recloser: 5C/07 T/R 10x. Counter: 197/207 Relay Flag: None. Patrolled the line found branch of palm trees almost touches the powerline on pole 5D/18. Cause : Tree. | 1
103 | 2020-06-26 06:26 | June | 6:26 | Morning | Friday | Weekdays | 26 | 2020 | 2020-06-26 06:26 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Lightning Arrester | 13 | 06:26 C.Duri fdr#2 Load dropped 97A (211/147A). 07:15 Checked and found RCL 08/M1/38 T/O (on block for PT WKS) Counter: 200/201, R/F: None 07:22 Manual Close RCL 08/M1/38, OK (leave on block position) Not Patrolled yet. | 1
| 2020-06-26 06:26 | June | 6:26 | Morning | Friday | Weekdays | 26 | 2020 | 2020-06-30 06:53 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Lightning Arrester | 13 | Checked and found Recloser: 08/M3/38 T/R 1x and Recloser: 08/M1/38 T/R 1x.. Counter: 161/162 Relay Flag: None. Counter: 200/201 Relay Flag: None. Patrolled the line found: / @1,@2 broken Lightning Arrester on pole 08/M2/01 (LBS). / @3 burnt out fuse on pole 08/L7/07. Cause: Lightning Arrester. | 1
104 | 2020-06-26 10:00 | June | 10:00 | Morning | Friday | Weekdays | 26 | 2020 | 2020-06-26 10:00 | MINAS POWER PLANT | Minas | PGT South |  |  | - | Off Line MGT/9, then Shut Down the unit for Standby. | 1
105 | 2020-06-27 10:14 | June | 10:14 | Morning | Saturday | Weekends | 27 | 2020 | 2020-06-27 10:14 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 35 | 10:14 Manual Open LBS 3E/64, closed at 12:09 MTCE team to change out broken insulator o/p 3E/02 and 3E/13 Cause: Planned Maintenance | 1
106 | 2020-06-28 06:35 | June | 6:35 | Morning | Sunday | Weekends | 28 | 2020 | 2020-06-28 06:35 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Unidentified | 256 | 06:35 So.Balam fdr#4 T/O (Blocked Position for GBT #12) Checked and found VCB Balam fdr #4 T/O, ctr: 385 (not change), R/F: 51N 07:30 Patrolled the line but found nothing 07:41 Manual Close (on block) VCB Balam fdr #4, OK. Leave on block position. Cause: Unidentified. | 1
107 | 2020-06-28 11:00 | June | 11:00 | Morning | Sunday | Weekends | 28 | 2020 | 2020-06-28 11:00 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Fair | Emergency | 0 | 11:00 Manual Open VCB 3D fdr #4, closed at 11:52 Manual Open VCB 3D fdr #8, closed at 12:27 Emergency case at GS/5, short circuit at wash tank/4. Cause: Emergency | 1
108 | 2020-06-29 09:29 | June | 9:29 | Morning | Monday | Weekdays | 29 | 2020 | 2020-06-29 09:29 | 13.8KV 6D FEEDER #5 | Minas | PGT South | Fair | Planned Maintenance | 59 | 09:29 Manual Open VCB 6D fdr #5, closed at …… MTCE team to replace/change out insulator o/p ......... Cause: Planned Maintenance | 1
109 | 2020-06-29 13:45 | June | 13:45 | Afternoon | Monday | Weekdays | 29 | 2020 | 2020-06-29 13:45 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 13:45 MGT/7 S/U and then Online at 14:05 as replacement of CGT/4 that S/D for certification | 1
110 | 2020-06-29 14:11 | June | 14:11 | Afternoon | Monday | Weekdays | 29 | 2020 | 2020-06-29 14:11 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:11 CGT/4 Offline and then S/D at 14:13 (Prepared for HRSG certification) | 1
111 | 2020-06-30 07:34 | June | 7:34 | Morning | Tuesday | Weekdays | 30 | 2020 | 2020-06-30 07:34 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Cloudy | Unidentified | 72 | NKB fdr #2 T/R 1x (supply for OKB fdr #2) Not Checked Yet | 1
| 2020-06-30 07:34 | June | 7:34 | Morning | Tuesday | Weekdays | 30 | 2020 | 2020-01-07 16:20 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Cloudy | Unidentified | 72 | Checked and found NKB OCB fdr #2 T/R 1x, ctr: 99945 / 99946, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
112 | 2020-06-30 10:42 | June | 10:42 | Morning | Tuesday | Weekdays | 30 | 2020 | 2020-06-30 10:42 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Planned Maintenance | 108 | 10:42 Manual Open RCL 38/CX/25, closed at 15:07 For Maintenance team repair hot spot at KB #341 and c/o pin insulator Cause: Planned Maintenance | 1
113 | 2020-06-30 11:03 | June | 11:03 | Morning | Tuesday | Weekdays | 30 | 2020 | 2020-06-30 11:03 | 13.8KV MINAS FEEDER #4 | Minas | PGT South | Fair | Planned Maintenance | 72 | 11:03 Manual Open RCL 7D/150, closed at 13:06 MTCE team to completing installation for reactive well at 8D/32/33/42 Cause: Planned Maintenance | 1
114 | 2020-06-30 17:12 | June | 17:12 | Afternoon | Tuesday | Weekdays | 30 | 2020 | 2020-06-30 17:12 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Powerline / Conductor | 651 | 17:12 CD fdr #1 load dropped 67 A (144 / 77A) 17:29 Reported there is broken conductor (still live) near gate 126 / Kulin #32 17:38 Manual Open ACB CD fdr #1 18:00 Checked and reported @3 broken conductor 2 pole before line VR Kulin near Kulin #71, pole 40/AW/12. 18:23 Manual Open RCL 41/AW/62, then opened visually opening Recl. 41/AW/62. 19:22 Blocked & closed C.Duri fdr#1, then release the block. 22:15 Repaired @3 Broken Conductor o/p 41/AW/12. 22:34 Manually Open C.Duri fdr#1, then closed at 22:37. 22:36 Closed visual opening recl. 41/AW/62. 22:38 Blocked Recl 41/AW/62, then release the block. Cause: Conductor | 1
115 | 2020-06-30 22:30 | June | 22:30 | Night | Tuesday | Weekdays | 30 | 2020 | 2020-06-30 22:30 | 4.16KV MINAS IND FEEDER | Minas | PGT South | Fair | Unidentified | 0 | 22:30 It was reported no power at PGPA Office & Gate#1 Minas. 23:00 Checked & found 4160V Industrial Recl. T/O Ctr:691/692 R/F:50N. Patrolled the line but found nothing. 00:05 Blocked & Closed 4160V Industrial Recl., then release the block. Cause: Unidentified. | 1
1 | 2020-01-07 09:45 | January | 9:45 | Morning | Tuesday | Weekdays | 7 | 2020 | 2020-01-07 09:45 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 1105 | 09:45 Manually open Nella feeder #1. Repair Hot spot o/p 21-V-03 (77 well off durum the job). 11:10 Closed Nella VCB fdr #1 but failed. 13:51 Manual Open Nella VCB fdr #2, ----->Closed at 14:00. 13:56 Manual Open 115KV Nella C/S, ----->Closed at 13:59. 13:57 Closed By Pass Switch Nella VCB fdr #1, OK (due to Failed to Closed). Cause : plan maintenance. Production Loss: Nella fdr #1 : 1369 Bbls / 78 Wells. Nella fdr #2 : 40 Bbls / 18 Wells. -----------------------------------------_+ TOTAL : 1409 Bbls / 96 Wells. | 1
2 | 2020-01-07 12:09 | January | 12:09 | Afternoon | Tuesday | Weekdays | 7 | 2020 | 2020-01-07 12:09 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 12:09 S/U MGT #5 the online then unit 12:24. | 1
3 | 2020-01-07 21:00 | January | 21:00 | Night | Tuesday | Weekdays | 7 | 2020 | 2020-01-07 21:00 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 21:20 MGT-8 Offline and shut down at 21:22 for standby | 1
4 | 2020-02-07 03:41 | February | 3:41 | Night | Friday | Weekdays | 7 | 2020 | 2020-02-07 03:41 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Fair | Main breaker | 389 | 03:41 5B feeder #2 no load (zero) -- normal load 185 A No trip indication at DSC 06:15 Trip indication just appear at DSC 06:31 Checked and found 5B VCB fdr #2 T/SO (operate 1x) ctr:344-345 R/F:51N. 06:38 Block and close 5B VCB fdr #2 but failed Try to close the breaker locally, but trip again 06:59 Continue to patrol the power line till LBS 5C-01, OK. 07:31 Open LBS 5C-01. 07:35 Blocked and closed 5B fdr #2, OK (from Substation). 08:31 Manual Open 5B fdr #2 for function test. 10:00 Open Recl. 5C-07. Closed LBS 6D-332 D/S 6DN fdr #2 10:02 Open Recl. 6D-50 ( part load 6DN fdr #2 transfer to 6D fdr #6. (planning to transfer 5B fdr #2 to 6DN fdr #2) 10:46 Closed LBS 36DN-22 (load 5B fdr #2 transfer to 6DN fdr #1). Replaced 3 Set Broken Dead End o/p 4C-74. 14:49 Blocked and closed 5B fdr #2, Ok then released the block. 15:19 Closed LBS 5C-01. Cause: Breaker failure. | 1
5 | 2020-02-07 08:39 | February | 8:39 | Morning | Friday | Weekdays | 7 | 2020 | 2020-02-07 08:39 | 13.8KV 5B FEEDER #5 | Minas | PGT South | Fair | Unidentified | 3 | 5B 13.8Kv OCB #5 T/R 1x. Not checked yet. | 1
| 2020-02-07 08:39 | February | 8:39 | Morning | Friday | Weekdays | 7 | 2020 | 2020-09-07 07:56 | 13.8KV 5B FEEDER #5 | Minas | PGT South | Fair | Unidentified | 3 | Checked and found 5B OCB feeder #5 No equipment operating. Counter: 342-342 R/F: None. Cause: Unidentified. | 1
6 | 2020-02-07 15:35 | February | 15:35 | Afternoon | Friday | Weekdays | 7 | 2020 | 2020-02-07 15:35 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 16 | 15:35 Manual Open LBS 5C-20 (before defeed from 6DN fdr #1). Cutting high tree. 15:57 Closed recloser 5E-07 Ctr: 208 Cause: Plan Maintenance. | 1
7 | 2020-02-07 18:48 | February | 18:48 | Afternoon | Friday | Weekdays | 7 | 2020 | 2020-02-07 18:48 | 115KV NELLA SW. STA - PINANG LINE | Bangko-Balam | PGT North | Fair | Substation Failure (Tx SS) | 23256 | 18:48 Nella 115KV GCB 27 T/O. S. Balam fdr #1 load dropped 112A (171-59A). S. Balam fdr #2 load dropped 35A (106-71A). S. Balam fdr #4 load dropped 172A (216-44A). Nella fdr #2 load dropped 42A (61-19A). Bangko fdr #1 load dropped 110A (160-50A). Bangko fdr #2 load dropped 62A (240-178A). Bangko fdr #3 load dropped 11A (240-229A). Bangko fdr #4 load dropped 87A (187-100A). Sintong fdr #1 load dropped 53A (101-48A). Sintong fdr #2 load dropped 208A (246-38A). Menggala fdr #1 load dropped 128A (181-53A). Menggala fdr #2 load dropped 136A (166-30A). Ketigul fdr #1 load dropped 84A (115-31A). Ketigul fdr #2 load dropped 175A (194-19A). Ketigul fdr #3 load dropped 72A (79-7A). 20:15 Checked and found 115 kV GCB #27 Nella T/O, Counter: 239 - 240, R/F: 50P @1 @3, 21P Z2 Patrolled the power line through to Pinang SS 22:10 Checked and found at Pinang Substation Broken 13.8 KV bus insulator support, LA and dead end insulator at PNG SS HSGS Status : …… R/F: …… 22:50 Confirmed that no potential to congeal at Pinang GS and field Conformed by TL FON (Yaqub) Continue tomorrow to repair the broken parts at Pinang Substation Cause: Under Investigation | 1
| 2020-02-07 18:48 | February | 18:48 | Afternoon | Friday | Weekdays | 7 | 2020 | 2020-03-07 18:48 | 115KV NELLA SW. STA - PINANG LINE | Bangko-Balam | PGT North | Fair | Substation Failure (Tx SS) | 23256 | Maintenance team Started work at Pinanng Substation.: Removed Broken Bus support of LA. Trouble shoot relay protection. 15:17 Closed both isolation switch 115Kv Nella-->Pinang GCB #27. 15:30 Blocked & Closed GCB #27 (Failed from DSC). 15:35 Blocked & closed GCB #27 But tripped again R/F 50P @1 @3. 15:42 Open both isolation switch Nella-->Pinang GCB #27. 16:00 Checked & found Tx failure. Will be replaced tomorrow. | 1
| 2020-02-07 18:48 | February | 18:48 | Afternoon | Friday | Weekdays | 7 | 2020 | 2020-05-08 18:48 | 115KV NELLA SW. STA - PINANG LINE | Bangko-Balam | PGT North | Fair | Substation Failure (Tx SS) | 23256 | Replaced on July 11,2020. - 7 Mva to 10.5 MVA Power transformer. - Repaired Voltage regulator, Bus & isolator support. - Resetting Protection system. Energized on July 21,2020. Cause: Power transformer failure. | 1
8 | 2020-03-07 09:28 | March | 9:28 | Morning | Saturday | Weekends | 7 | 2020 | 2020-03-07 09:28 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Animal | 21 | Ketigul 13.8Kv VCB fdr#1 T/R 1x. Ketigul feeder #2 load dropped 22A (79-57A). Ketigul feeder #3 load dropped 18A (32-14A). Not checked yet. | 1
| 2020-03-07 09:28 | March | 9:28 | Morning | Saturday | Weekends | 7 | 2020 | 2020-04-07 06:04 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Fair | Animal | 21 | Checked and found KTGL VCB fdr #1 T/R 1x, ctr: 240 - 241, R/F: 51P @2 Patrolled the line and found died animal (monkey) near pole 20-AJ-13 and also found broken dead end on @1 and @2 Cause : Animal | 1
9 | 2020-03-07 09:29 | March | 9:29 | Morning | Saturday | Weekends | 7 | 2020 | 2020-03-07 09:29 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Recloser - Control Recloser | 32 | 09:29 Duri field feeder #2 load dropped 12A (161-144A). 14:23 it was reported no power on road 07-U1-xx D/S Duri Field feeder #2. 15:05 Checked & found recloser 07-U1-19 T/SO Ctr:272-273. Patrolled the line and found @1 b/o fuse of cap at 07-U1-15. 15:10 Blocked & closed recloser 07-U1-19 OK. Then normal the block. cause : Control Recloser. | 1
10 | 2020-03-07 09:34 | March | 9:34 | Morning | Saturday | Weekends | 7 | 2020 | 2020-03-07 09:34 | SOUTH BALAM SUBSTATION | Bangko-Balam | PGT North | Fair | Planned Maintenance | 1272 | 09:34 Manually open 13.8Kv So.Balam feeder #1, ---->Closed at12:26. 09:39 Manually open 13.8Kv So.Balam feeder #4, ---->Closed at12:27. 09:49 Manually open 13.8Kv So.Balam feeder #2, ---->Closed at12:04. 09:50 Manually open 13.8Kv So.Balam feeder #3, ---->Closed at12:05. 09:52 Manually open 115Kv So.Balam C/S, ---->Closed at12:01. (Repair Hot Spot at Terminal connection of VR) Cause : Plan maintenance. | 1
11 | 2020-04-07 07:24 | April | 7:24 | Morning | Tuesday | Weekdays | 7 | 2020 | 2020-04-07 07:24 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Cloudy | Unidentified | 0 | Batang 13.8KV GFPC T/R 1X. No load dropped. | 1
| 2020-04-07 07:24 | April | 7:24 | Morning | Tuesday | Weekdays | 7 | 2020 | 2020-07-07 09:02 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Cloudy | Unidentified | 0 | Checked and found Batang GFPC T/R 1x. Counter: 435-436 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. | 1
12 | 2020-04-07 08:21 | April | 8:21 | Morning | Tuesday | Weekdays | 7 | 2020 | 2020-04-07 08:21 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | 297 | 08:21 SO.Balam 13.8Kv VCB fdr#1 T/O. (On block RIG GBT #12). 09:15 Checked and found S. Balam fdr #1 T/O ctr:418-419 R/F: 51@1. patrolled the line but found nothing. 09:55 Blocked and closed So. Balam fdr #1, Ok then released the block. Cause: Unidentified. | 1
| 2020-04-07 08:21 | April | 8:21 | Morning | Tuesday | Weekdays | 7 | 2020 | 2020-04-07 11:56 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | 297 | Checked and found: SBLM-13.8VCB1 T/O, Counter : 418 - 419, Relay Flag : 51N Patrolled the line found : None Cause : Unidentified | 1
13 | 2020-04-07 18:10 | April | 18:10 | Afternoon | Tuesday | Weekdays | 7 | 2020 | 2020-04-07 18:10 | 44KV PEMATANG MAIN - PETANI LINE | Bekasap | PGT North | Drizzle | Animal | 27 | Pematang Main 44KV OCB #1 T/R 1X. (No power to Petani fdr #1 and Petani fdr #2). Rangau fdr #2 load dropped 28A (134-106A). Pematang fdr #1 load dropped 61A (209-148A). Pematang fdr #2 load dropped 22A (118-96A). Not checked yet. | 1
| 2020-04-07 18:10 | April | 18:10 | Afternoon | Tuesday | Weekdays | 7 | 2020 | 2020-07-07 09:37 | 44KV PEMATANG MAIN - PETANI LINE | Bekasap | PGT North | Drizzle | Animal | 27 | Checked and found Pematang 44 Kv OCB #1 T/R x. Counter: 200-201 Relay Flag: 51N. Patrolled the line nothing found , Checked in Control unit OCB found scorched lizard. Cause: Animal (Lizard). | 1
14 | 2020-05-07 23:59 | May | 23:59 | Night | Thursday | Weekdays | 7 | 2020 | 2020-05-07 23:59 | CPI POWER SYSTEM |  |  | Fair | Normal Condition | - | CPI Power System on Normal Condition | 1
15 | 2020-06-07 03:01 | June | 3:01 | Night | Sunday | Weekends | 7 | 2020 | 2020-06-07 03:01 | 13.8KV 3D TX-1 GFPC | Minas | PGT South | Fair | Unidentified | 0 | 3D GFPC TX-1 T/R 1x 3D feeder #4 load dropped 7 A (150 - 143 A) Not Checked Yet | 1
| 2020-06-07 03:01 | June | 3:01 | Night | Sunday | Weekends | 7 | 2020 | 2020-10-07 06:39 | 13.8KV 3D TX-1 GFPC | Minas | PGT South | Fair | Unidentified | 0 | Checked and found 3D GFPC TX #1 T/R 2x. Counter: 4271-4273 R/F: None. Patrolled the line found Recloser: 2D-14 T/R 2x [ D/S 3D feeder #4 ]. Counter: 40-42 R/F: None. Patrolled D/S Recloser 2D-14 nothing found. Cause: Unidentified. | 1
16 | 2020-06-07 08:27 | June | 8:27 | Morning | Sunday | Weekends | 7 | 2020 | 2020-06-07 08:27 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Fair | Powerline - Conductor | 83 | 08:27Minas 13.8Kv ACB fdr#6 T/LO ctr:203-205 R/F:50@1. Minas feeder #1 load dropped 126A (183-57A). Minas feeder #2 load dropped 37A (105-68A). Minas feeder #3 load dropped 131A (131-0A). Minas feeder #4load dropped 104A (149-45A). 09:45 Patrolled the line and found @1 & @2 twisted conductor O/P:...….around PT. PP office (EX triparta office) . -Racked out Minas feeder #6. -Repair twisted conductor. 10:29 Racked in Minas feeder #6. 10:29 Blocked & closed Minas feeder #6, Ok then released block. 10:50 Checked & found recloser 7E-67A T/LO Ctr:98-102. 10:53 Blocked & closed Recloser, Ok then released block. -Checked recloser 6E-23A,Ok (Normal). Cause : Conductor. | 1
17 | 2020-06-07 16:01 | June | 16:01 | Afternoon | Sunday | Weekends | 7 | 2020 | 2020-06-07 16:01 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Heavy Rain | Animal | 16 | 16:01 S. Balam fdr #4 load dropped 35A (215-180). (ground fault alarm appear on GFPC signal) 18:40 Checked and found RCL 16-AB-03 T/LO, ctr: 467 - 471 Patrolled the power line but found nothing. 19:10 Block and close RCL 16-AB-03, OK but trip again after a few second Re-patrol the line but still found nothing. 21:00 Block and close RCL 16-AB-03, OK but trip again. Continue patrol the power line and found animal (snake) fall down from power line near pole 17-AB-53. 21:22 Block and close the RCL, OK. then release the block. Last Counter RCL 16-AB-03 = 477) Cause: Animal (snake) | 1
18 | 2020-06-07 17:20 | June | 17:20 | Afternoon | Sunday | Weekends | 7 | 2020 | 2020-06-07 17:20 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Cloudy | Unidentified | - | Batang 13.8KV GFPC T/R 1X. No load dropped. | 1
| 2020-06-07 17:20 | June | 17:20 | Afternoon | Sunday | Weekends | 7 | 2020 | 2020-10-07 06:47 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Cloudy | Unidentified | - | Checked and found Batang GFPC T/R 3x. Counter: 435-438 Relay Flag : 50@1,@3. Patrolled the line nothing found. Cause: Unidentified. | 1
19 | 2020-07-07 07:45 | July | 7:45 | Morning | Tuesday | Weekdays | 7 | 2020 | 2020-07-07 07:45 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 0 | C. Duri fdr #2 Load dropped 100A (221-121A ). Not checked yet. | 1
| 2020-07-07 07:45 | July | 7:45 | Morning | Tuesday | Weekdays | 7 | 2020 | 2020-11-07 14:40 | 13.8KV CENTRAL DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found: 5441-R.08-M1-38 T/R, Counter : 201 - 202, Relay Flag : NONE Patrolled the line found : No Findings Cause : Unidentified | 1
20 | 2020-07-07 11:14 | July | 11:14 | Morning | Tuesday | Weekdays | 7 | 2020 | 2020-07-07 11:14 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 171 | 11:14 It was reported wells off under Nella fdr #1. Checked and found Nella fdr #1 loads dropped 55A (210-155A). No alarm at DSC due to load be set on Manual (High reading). 12:30 Checked and found Recl. 22-V-01 T/SO ctr: 254 (Not change). Patrolled the line but found nothing. 12:59 Blocked and closed the Recloser, Ok then released block. Cause: Unidentified. | 1
21 | 2020-07-07 13:42 | July | 13:42 | Afternoon | Tuesday | Weekdays | 7 | 2020 | 2020-07-07 13:42 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Fair | Planned Maintenance | 4 | 13:42 Manual Open Recloser 07-T3-02 D/S DF fdr #2. C/O @1 broken Pin insulator o/p: 07-T3-18. 14:47 Closed Recloser 07-T3-02. Plan maintenance. | 1
22 | 2020-07-07 14:27 | July | 14:27 | Afternoon | Tuesday | Weekdays | 7 | 2020 | 2020-07-07 14:27 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Pin Insulator | 106 | 14:27 SO. Balam fdr #4 load dropped 52A (213-161A). 15:00 It was reported no power under Recl. 16-AB-03. 16:00 Checked and found Recl. 16-AB-03 T/LO ctr:477-481. Patrolled the line and found @3 broken Pin insulator o/p:17-AB-53. Isolated @3 broken Pin insulator o/p:17-AB-53. 17:40 Blocked and closed Recloser 16-AB-03, Ok then released block. Cause: Broken Pin Insulator. (@3 broken Pin insulator o/p:17-AB-53 NOT REPLACED YET). | 1
| 2020-07-07 14:27 | July | 14:27 | Afternoon | Tuesday | Weekdays | 7 | 2020 | 2020-08-07 07:15 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Pin Insulator | 106 | Checked and found: 5440-R.16AB03 T/LO, Counter : 477 - 481, Relay Flag : 51N. Patrol led the line found : Broken pin support insulator, Jumper short Cause : Pin Insulator | 1
23 | 2020-07-07 16:33 | July | 16:33 | Afternoon | Tuesday | Weekdays | 7 | 2020 | 2020-07-07 16:33 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Heavy Rain | Lightning | 0 | Ground fault alarm from Sintong fdr $2. Sintong fdr #2 dropped 185A (248-63A). Sintong fdr #1 dropped 11A (101-90A). Not checked yet. | 1
24 | 2020-08-07 07:43 | August | 7:43 | Morning | Friday | Weekdays | 7 | 2020 | 2020-08-07 07:43 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Recloser - Control Recloser | 92 | 07:43 Nella feeder #1 load dropped 70A (210-140A). 09:30 Checked & Found recloser 21-V-01 T/SO Ctr: 254. Blocked & Closed recloser 21-V-01 unplug control recloser. Cause : Control recloser. | 1
25 | 2020-09-07 17:20 | September | 17:20 | Afternoon | Monday | Weekdays | 7 | 2020 | 2020-09-07 17:20 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 131 | 17:20 Ketigul VCB fdr#2 T/O (Block Position). 18:45 Checked & Found Ketigul VCB fdr#2 T/O Ctr:394-395 R/F:50N. Patrolled the line but found nothing. 19:29 Blocked and closed Ketigul fdr #2, Ok. Cause: Unidentified. | 1
26 | 2020-10-07 10:40 | October | 10:40 | Morning | Wednesday | Weekdays | 7 | 2020 | 2020-10-07 10:40 | 13.8KV 4D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 10 | 10:40 Manually open LBS 3D-66 (4D feeder #2). Replaced broken pin insulator o/p 4D-147 & 3E-18. 11:46 Manually Closed LBS 3D-66 Ok. Cause: Plain maintenance. | 1
27 | 2020-10-07 15:57 | October | 15:57 | Afternoon | Wednesday | Weekdays | 7 | 2020 | 2020-10-07 15:57 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Cloudy | Unidentified | 0 | N.Duri 13.8Kv OCB fdr#7 T/R 1x. Not checked yet. | 1
| 2020-10-07 15:57 | October | 15:57 | Afternoon | Wednesday | Weekdays | 7 | 2020 | 2020-12-07 14:28 | 13.8KV NORTH DURI FEEDER #7 | Duri | PGT North | Cloudy | Unidentified | 0 | Checked and found: NDRSB-13.8VCB7 T/R, Counter : 145 - 146, Relay Flag : 51N. Patrolled the line found : Relay Flag 51N dan 51phase 1 dan2 , tidak ada temuan setelah dipatrol Cause : Unidentified | 1
28 | 2020-11-07 04:30 | November | 4:30 | Morning | Saturday | Weekends | 7 | 2020 | 2020-11-07 04:30 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 172 | 04:30 Nella 13.8KV VCB fdr #2 T/SO. (Nella fdr #2 load dropped 67A (67-0A), and breaker status still Close) Nella fdr #1 Load dropped 26A (211-185A). 06:00 Checked and found Nella fdr #2 T/SO ctr: 374-375 R/F:51@2, @3. Patrolled the line, but found nothing. 06:47 Blocked and closed Nella fdr #2, but failed (from Substation). (Can not be closed from DSC due to Status still Close). Function test the breaker, OK (found spring breaker not Re-Charge). 07:04 Blocked and closed Nella fdr#2, Ok then released the block. Last counter: 376. Cause: Breaker (failure). | 1
29 | 2020-12-07 07:09 | December | 7:09 | Morning | Monday | Weekdays | 7 | 2020 | 2020-12-07 07:09 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Unidentified | 69 | Petani OCB feeder #1 T/R 1x. Not Checked yet. | 1
| 2020-12-07 07:09 | December | 7:09 | Morning | Monday | Weekdays | 7 | 2020 | 14-07-2020 13:25 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Fair | Unidentified | 69 | Checked and found: PTNSB-13.8OCB1 T/R, Counter : 161 - 162, Relay Flag : 50N Patrolled the line found : No Findings Cause : Unidentified | 1
30 | 2020-12-07 14:58 | December | 14:58 | Afternoon | Monday | Weekdays | 7 | 2020 | 2020-12-07 14:58 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Dumai | PGT North | Heavy Rain | Tree | 0 | 14:58 Dumai 4160V ACB#22 fdr#4 T/LO. 15:13 Checked & found Dumai 4160V ACB#22 fdr#4 T/LO Ctr:307-309 R/F:51@1@3, 51N. Patrolled the line but found nothing. 16:18 Blocked & closed Dumai 4160V ACB#22 fdr#4, but failed. 16:37 Patrolled again & found Trees fault to Line at Mendud. 17:00 Opened LBS H5-7 for isolated line. 17:34 Blocked & closed Dumai 4160V ACB#22 fdr#4, then release the block. Cause: Tree. | 1
31 | 2020-12-07 18:29 | December | 18:29 | Afternoon | Monday | Weekdays | 7 | 2020 | 2020-12-07 18:29 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Pin Insulator | 30 | Ketigul VCB feeder #2 T/R 1x. Not checked yet. | 1
| 2020-12-07 18:29 | December | 18:29 | Afternoon | Monday | Weekdays | 7 | 2020 | 14-07-2020 13:28 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Pin Insulator | 30 | Checked and found Ketigul VCB feeder #2 T/R 2x. Counter : 395 - 397 Relay Flag : 51N Patrolled the line found @1 flash over Pin insulator on pole towards well Pagar #15. Cause : Pin Insulator. | 1
32 | 2020-07-13 04:22 | July | 4:22 | Morning | Monday | Weekdays | 13 | 2020 | 2020-07-13 04:22 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Rain | Lightning | 51 | 5B feeder #2 Load dropped 145A (154/9A). Not checked yet. | 1
| 2020-07-13 04:22 | July | 4:22 | Morning | Monday | Weekdays | 13 | 2020 | 17/07/2020 11:05 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Rain | Lightning | 51 | Checked and found Recloser: 5C/07 T/R 4x ( Down stream 5B feeder #2). Counter: 208 / 212 R/F: None Patrolled the line but nothing found. Cause : Suspect Lightning. | 1
33 | 2020-07-13 07:02 | July | 7:02 | Morning | Monday | Weekdays | 13 | 2020 | 2020-07-13 07:02 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Rain | Pin Insulator | 30 | Ketigul Feeder #2 T/R 1X Not checked yet. | 1
| 2020-07-13 07:02 | July | 7:02 | Morning | Monday | Weekdays | 13 | 2020 | 2020-07-14 13:30 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Rain | Pin Insulator | 30 | Checked and found Ketigul VCB feeder #2 T/R 2x. Counter : 395 / 397, Relay Flag : 51N Patrolled the line found @1 flash over pin insulator on pole towards well Pagar #15. Cause : Pin Insulator. | 1
34 | 2020-07-13 08:48 | July | 8:48 | Morning | Monday | Weekdays | 13 | 2020 | 2020-07-13 08:48 | 13.8KV NEW KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Transformer Failure | 0 | 08:48 New Kotabatak Feeder # 1 T/R 1X Checked and found NKBS OCB feeder #1 T/R 1x. Counter: 279/280 Relay Flag: 51@1. Patrolled the line found @3 broken bushing transformer at KB/338. Cause : Transformer Failure. | 1
35 | 2020-07-13 15:30 | July | 15:30 | Afternoon | Monday | Weekdays | 13 | 2020 | 2020-07-13 15:30 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Cloudy | Others | 0 | North Duri Feeder #1 T/R 1X Not Checked yet. | 1
| 2020-07-13 15:30 | July | 15:30 | Afternoon | Monday | Weekdays | 13 | 2020 | 17/07/2020 16:44 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Cloudy | Others | 0 | Checked and found ND VCB fdr #1 T/R 2x, ctr: 343 / 345, R/F: 51N Patrolled the line and found broken insulator of bypass switch @3 o/p 12/E3/27 Cause : Others | 1
36 | 2020-07-14 10:31 | July | 10:31 | Morning | Tuesday | Weekdays | 14 | 2020 | 2020-07-14 10:31 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 191 | 10:31 Manggala Feeder#1 load drop 117A ( 180/87A) 12:13 Checked and found Recl 19 AN 04 T/O ( Block Position) ctr : 826/827 Patrolled the line but found nothing ( suspect Monkey ) 13:15 Blocked and closed Recl 19 AN 04. Couse : Animal | 1
37 | 2020-07-14 10:35 | July | 10:35 | Morning | Tuesday | Weekdays | 14 | 2020 | 2020-07-14 10:35 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 149 | 10:35 So. Balam Feeder #1 load drop 34A ( 172/138A ) 14:30 Checked and found Recloser 16Z41 T/So Ctr:3204/3205 Patrolled the line Found dead monkey on T/P So.Balam 52. 15:16 Blocked and Closed Recl 16Z41,then release the block. Couse : Animal. | 1
38 | 2020-07-15 16:55 | July | 16:55 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 2020-07-15 16:55 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Fair | Unidentified | - | Batang GFPC T/R 1x. Not checked yet. | 1
| 2020-07-15 16:55 | July | 16:55 | Afternoon | Wednesday | Weekdays | 15 | 2020 | 17/07/2020 16:40 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Fair | Unidentified | - | Checked and found BTG GFPC T/R 2x, ctr: 1036 / 1038, R/F: 50N Patrol the line but found nothing Cause : Unidentified | 1
39 | 2020-07-16 06:48 | July | 6:48 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-07-16 06:48 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Cloudy | Unidentified | 0 | 06:48 Rangau Feeder #2 Load drop 120A ( 129/9A ) 08:20 Checked and found RCL 23/BD/01 T/O (on block position) Counter: 435 / 436, R/F: None 08:35 Manual Close RCL 23/BD/01 (after got permit from TL OPS), OK Then release the block. Cause: Not Patrolled Yet | 1
| 2020-07-16 06:48 | July | 6:48 | Morning | Thursday | Weekdays | 16 | 2020 | 17/07/2020 07:26 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Cloudy | Unidentified | 0 | Checked and found RCL 23/BD/01 T/O (on block position), ctr: 435 / 436, R/F: 50P Patrol the line but found nothing Cause : Unidentified | 1
40 | 2020-07-16 09:59 | July | 9:59 | Morning | Thursday | Weekdays | 16 | 2020 | 2020-07-16 09:59 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | 15 | Sintong VCB feeder #1 T/R 1x Not Checked Yet | 1
| 2020-07-16 09:59 | July | 9:59 | Morning | Thursday | Weekdays | 16 | 2020 | 17/07/2020 09:59 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | 15 | Check and found Sintong Fdr#1 T/R 1X Ctr:429/430 R/F 51N Patrolled the line but found nothing Couse unidentified. | 1
41 | 2020-07-16 12:13 | July | 12:13 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-07-16 12:13 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Dumai | PGT North | Cloudy | Corrosion | 0 | 12:13 Dumai VCB/12 feeder #1 (also supply Dumai fdr #5) T/SO. (load Dumai fdr #5 transferred due to metering upgrade/installation job) 12:48 Checked and found VCB/12 Dumai fdr #1 operate 2x Counter: 328 / 330, R/F: 50 P @1, @2, @3 13:30 Patrolled the line and found broken pin insulator (corroded steel pin) @2 on pole W/29 14:15 Manual Open LBS W/91 to isolate source from genset WHARF Dumai 15:05 Manual Open LBS I/21 to separate line Dumai fdr #1 with Dumai fdr #5 15:08 Rack In VCB/23 Dumai fdr #5 Blocked and then manual close the VCB, OK, then release the block 15:20 Rack Out VCB/12 Dumai fdr #1 (MTCE team to replace broken pin insulator o/p W/29), complete at 16:38 16:42 Rack In VCB/12 Dumai fdr #1, manual close the VCB, OK. 17:13 Close LBS on pole W/91 to normalize line through to WHARF. Cause: Corroded (steel pin of insulator) | 1
42 | 2020-07-16 13:51 | July | 13:51 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-07-16 13:51 | 115KV CENTRAL DURI / ROKAN LINE | Duri | PGT North | Cloudy | Dead End Insulator | 103 | 13:51 115 kV line CD / RKN / KTGL T/R 1x, freq reach to 60.24 Hz / 115 kV GCB #43 CD T/R 1x / 115 kV GCB #45 CD T/R 1x / 115 kV GCB #11 ROKAN T/R 1x / 115 kV GCB #1 KETIGUL T/R 1x / 115 kV GCB #2 KETIGUL T/SO 1x, manual Close at 14:34 / Pematang fdr #1 dropped 182 A (206 / 24 A) / Pematang fdr #2 dropped 108 A (115 / 7 A) / Rangau fdr #1 dropped 27 A (51 / 24 A) / Rangau fdr #2 dropped 142 A (143 / 1 A) / Petani fdr #1 dropped 156 A (185 / 29 A) / Petani fdr #2 dropped 52 A (70 / 18 A) / Rokan fdr #2 dropped 6 A (16 / 10 A) / Rokan fdr #4 dropped 10 A (19 / 9 A) / Ketigul fdr #1 dropped 36 A (130 / 94 A) / Balam fdr #1 dropped 6 A (172 / 166 A) / Balam fdr #4 dropped 59 A (212 / 153 A) / Menggala fdr #1 dropped 42 A (180 / 138 A) / Menggala fdr #2 dropped 39 A (162 / 123 A) / Nella fdr #1 dropped 45 A (206 / 161 A) / Bangko fdr #1 dropped 9 A (161 / 152 A) / Bangko fdr #2 dropped 17 A (239 / 222 A) / Bangko fdr #3 dropped 10 A (219 / 209 A) / Sintong fdr #1 dropped 12 A (108 / 96 A) / Sintong fdr #2 dropped 229 A (247 / 18 A) / RCL for Cap Bank Sintong T/O, manual closed at 16:21 / RCL for Cap Bank Nella T/O, manual closed at 16:23 Cause: Not Checked Yet | 1
| 2020-07-16 13:51 | July | 13:51 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-07-21 07:21 | 115KV CENTRAL DURI / ROKAN LINE | Duri | PGT North | Cloudy | Dead End Insulator | 103 | Checked 115 KV Central Duri /Rokan Line and found: 1. 115 KV GCB #45 C Duri T/R 1x. Counter: 161/162 R/F: 50@2. Patrolled the line found @2 flash over Dead end insulator on pole PJR #21. 2. 115 KV GCB #43 C Duri T/R 1x. Counter: 129/130 R/F: 50@2. Patrolled the line found @2 flash over Dead end insulator on pole PJR #21. 3. 115 KV GCB #11 Rokan T/R 1x. Counter: 56 / 57 R/F: 50@2. Patrolled the line found @2 flash over Dead end insulator on pole PJR #21. 4. 115 KV GCB #12 Rokan Not operate. Cause : Dead End Insulator. | 1
43 | 2020-07-16 14:16 | July | 14:16 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-07-16 14:16 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Rain | Tree | 25 | Rangau fdr #2 T/R 1x Not Checked Yet | 1
| 2020-07-16 14:16 | July | 14:16 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-07-19 17:12 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Rain | Tree | 25 | Checked and found RGU VCB fdr #2 T/R 1x, Ctr: 366 / 367, R/F: 51P @3 Patrolled the line and found high trees near Pelita #01 Cause : Tree | 1
44 | 2020-07-16 15:49 | July | 15:49 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-07-16 15:49 | 13.8KV NEW KOTABATAK FEEDER #3 | Petko | PGT South | Rain and Lightning | Lightning | 45 | NKBS feeder #3 T/R 1x. NKBS feeder #1 load dropped 15 A (52/37A) NKBS feeder #2 load dropped 39 A (288/249A) Not Checked yet. | 1
| 2020-07-16 15:49 | July | 15:49 | Afternoon | Thursday | Weekdays | 16 | 2020 | 17/07/2020 13:49 | 13.8KV NEW KOTABATAK FEEDER #3 | Petko | PGT South | Rain and Lightning | Lightning | 45 | Checked and found NKB OCB fdr #3 T/R 1x, ctr: 327/328, R/F: 50N Patrolled the line but found nothing Cause : Lightning | 1
45 | 2020-07-16 17:29 | July | 17:29 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-07-16 17:29 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Tree | 0 | Rangau feeder #2 load dropped 130 A (143/130A) Not Checked yet. | 1
| 2020-07-16 17:29 | July | 17:29 | Afternoon | Thursday | Weekdays | 16 | 2020 | 2020-07-19 17:23 | 13.8KV RANGAU FEEDER #2 | Bekasap | PGT North | Fair | Tree | 0 | Checked and found RCL 23/BD/01 T/R 1x, ctr: 436 / 437, R/F: 51 Patrolled the line and found high palm trees near Jorang #40 (pole 19/BB/30) Cause : Tree | 1
46 | 2020-07-16 19:04 | July | 19:04 | Night | Thursday | Weekdays | 16 | 2020 | 2020-07-16 19:04 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 360 | 19:04 Ketigul Fdr#2 T/O ( Blocked for Rig BKU #2 at Pgr#07 ) 21:27 Patrol the line but found nothing Checked & found Ketigul fdr#2 T/O (Block Position) Ctr:297/298 R/F:51@1@3. 21:30 Blocked and closed Ketigul Fdr#2 Cause: Unidentified. | 1
47 | 2020-07-17 01:25 | July | 1:25 | Night | Friday | Weekdays | 17 | 2020 | 2020-07-17 01:25 | 13.8KV 6DN FEEDER #1 | Minas | PGT South | Rain and Lightning | Unidentified | 53 | 01:25 6DN fdr#1 T/R 1x. 6DN fdr#2 Load dropped 141A (203/64A). 6DN fdr#3 Load dropped 54A (124/70A). 05:15 6DN fdr#1 Still dropped 62A. 06:55 Checked & found Recl. 5E/83 T/SO Ctr:36 Not operated. Patrolled the line but found nothing. Block and close RCL 5E/83, OK then release the block. Cause: Unidentified. | 1
48 | 2020-07-17 01:30 | July | 1:30 | Night | Friday | Weekdays | 17 | 2020 | 2020-07-17 01:30 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Rain and Lightning | Tree | 0 | 5B fdr#2 Load dropped 78A (140/62A). Not checked yet. | 1
| 2020-07-17 01:30 | July | 1:30 | Night | Friday | Weekdays | 17 | 2020 | 2020-07-22 15:34 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Rain and Lightning | Tree | 0 | Checked and found Recloser 5442/R.5C07 T/R 4x R/F: / Counter: 212 / 216. Patrolled the line and found high palm oil touched powerline o/p 5C/18. Cause : Tree | 1
49 | 2020-07-17 01:30 | July | 1:30 | Night | Friday | Weekdays | 17 | 2020 | 2020-07-17 01:30 | 13.8KV 5B FEEDER #4 | Minas | PGT South | Rain and Lightning | Unidentified | 0 | 5B fdr#4 T/R 1x. Not checked yet. | 1
| 2020-07-17 01:30 | July | 1:30 | Night | Friday | Weekdays | 17 | 2020 | 2020-07-21 15:50 | 13.8KV 5B FEEDER #4 | Minas | PGT South | Rain and Lightning | Unidentified | 0 | Checked and Found: 5BSB/13.8OCB4 T/R, Counter : 716 / 717, Relay Flag : 51N Patrol led the line : Not Found Cause : Unidentified | 1
50 | 2020-07-17 01:44 | July | 1:44 | Night | Friday | Weekdays | 17 | 2020 | 2020-07-17 01:44 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 8 | 4B fdr#2 T/R 1x. Not checked yet. | 1
| 2020-07-17 01:44 | July | 1:44 | Night | Friday | Weekdays | 17 | 2020 | 2020-07-21 15:53 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Rain and Lightning | Lightning | 8 | Checked and found: 4BSB/13.8OCB2 T/R, Counter : 293 / 294, Relay Flag : 51 Patrolled the line found : Not Found Cause : Lightning | 1
51 | 2020-07-17 18:39 | July | 18:39 | Afternoon | Friday | Weekdays | 17 | 2020 | 2020-07-17 18:39 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Fair | Pin Insulator | 0 | Central Duri ACB #22 (feeder #5) T/R 1x,. Counter: 273 / 274 R/F: 51G, 51N Not Patrolled Yet. | 1
| 2020-07-17 18:39 | July | 18:39 | Afternoon | Friday | Weekdays | 17 | 2020 | 2020-07-21 13:10 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Fair | Pin Insulator | 0 | Central Duri ACB #22 (feeder #5) T/R 1x,. Counter: 273 / 274 R/F: 51G, 51N. Patrolled the line found @3 broken pin insulator on pole 03/07/12. Cause: Pin Insulator. | 1
52 | 2020-07-18 08:14 | July | 8:14 | Morning | Saturday | Weekends | 18 | 2020 | 2020-07-18 08:14 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Fair | Tree | 68 | Pematang feeder #2 T/R 1X Pematang feeder #1 load drop 170A ( 208/38A ) Not checked yet. | 1
| 2020-07-18 08:14 | July | 8:14 | Morning | Saturday | Weekends | 18 | 2020 | 2020-07-21 15:34 | 13.8KV PEMATANG FEEDER #2 | Bekasap | PGT North | Fair | Tree | 68 | Checked and found: PMTSB/13.8OCB2 T/R, Counter : 568 / 569, Relay Flag : 51N Patrolled the line : Pohon tinggi menyentuh line Cause : Tree | 1
53 | 2020-07-18 13:09 | July | 13:09 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-18 13:09 | 13.8KV 3D FEEDER #8 | Minas | PGT South | Cloudy and Lightning | Lightning | 21 | 13:09 3D VCB fdr #8 T/R 1x 3D fdr #7 load dropped 150 A (161 / 11 A) 3D fdr #6 load dropped 62 A (129 / 67 A) Not Checked Yet | 1
| 2020-07-18 13:09 | July | 13:09 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-21 10:56 | 13.8KV 3D FEEDER #8 | Minas | PGT South | Cloudy and Lightning | Lightning | 21 | Checked and found: 3DSB/13.8OCB8 T/R, Counter : 338 / 339, Relay Flag : 51 Patrolled the line : Not Found Cause : Lightning | 1
54 | 2020-07-18 13:18 | July | 13:18 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-18 13:18 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Rain and Lightning | Tree | 45 | 5B feeder #2 load dropped 129 A (147 / 18 A) Not Checked Yet | 1
| 2020-07-18 13:18 | July | 13:18 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-22 15:34 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Rain and Lightning | Tree | 45 | Checked and found Recloser 5442/R.5C07 T/R R/F: / Counter: 216 / 221. Patrolled the line and found high palm oil touched the powerline o/p 5C/18. Cause : Tree. | 1
55 | 2020-07-18 13:23 | July | 13:23 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-18 13:23 | 13.8KV 4D FEEDER #2 | Minas | PGT South | Cloudy and Lightning | Emergency | 35 | 13:23 Manual Open 4D VCB fdr #2 (also supply 4D fdr #5) (to maintain level tank at GS/5 (high) / MMI problem) Emergency | 1
56 | 2020-07-18 13:24 | July | 13:24 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-18 13:24 | 13.8KV 3D FEEDER #3 | Minas | PGT South | Cloudy and Lightning | Lightning | 39 | 13:24 3D VCB fdr #3 T/R 1x 3D fdr #2 load dropped 11 A (191 / 180 A) Not Checked Yet | 1
| 2020-07-18 13:24 | July | 13:24 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-21 10:52 | 13.8KV 3D FEEDER #3 | Minas | PGT South | Cloudy and Lightning | Lightning | 39 | Checked and found: 3DSB/13.8OCB3 T/R, Counter : 500 / 501, Relay Flag : 51 Patrolled the line found : Not Found Cause : Lightning | 1
57 | 2020-07-18 13:28 | July | 13:28 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-18 13:28 | 13.8KV 8C FEEDER #1 | Minas | PGT South | Rain and Lightning | Tree | 72 | 13:28 8C VCB feeder #1 load dropped 54 A (138 / 84 A) 16:42 Reported no power d/s RCL 9D/25 17:10 Checked and found RCL 9d/25 T/SO 17:13 Blocked and close the RCL but failed Patrol the power line and found fallen tree near loc. 9D/79 18:19 Manual Close RCL 9D/25. OK then release the block. (last counter: 124) Cause: Tree | 1
58 | 2020-07-18 17:30 | July | 17:30 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-18 17:30 | 13.8KV PETAPAHAN FEEDER #8 | Petko | PGT South | Fair | Powerline / Conductor | 220 | 17:30 PTP VCB fdr #8 T/R 1x, 17:30:01 115 kV GCB #3 Petapahan T/O. 115 kV GCB #5 Petapahan T/O. TXP #2 Petapahan Substation Shut Off. Petapahan feeder #6, feeder #7, and feeder #8 are no power 17:53 Checked and found: 115 kV GCB #3 PTP T/O, ctr: 199 / 200 115 kV GCB #3 PTP T/O, ctr: 90 / 91 TX R/F: 87T @2, 86T Operate 17:42 Manual Open PTP VCB fdr #4 Then closes at 20:22 17:55 Manual Open PTP VCB fdr #6 Then closes at 19:33 17:56 Manual Open PTP VCB fdr #7 Then closes at 18:29 Manual Open PTP VCB fdr #8 Then closes at 17:59 18:00 Manual Open PTP VCB fdr #3 Then closes at 20:18 18:23 Reset 86T switch Manual close 115 kV GCB #3 PTP, OK. TX energize, condition normal 18:26 Manual close 115 kV GCB #5 PTP, OK Cause: Other Production Loss : Fdr# 3 Loss 465 Bbls / 54 Wells Fdr# 4 Loss 406 Bbls / 44 Wells Fdr# 6 Loss 81 Bbls / 6 Wells Fdr# 8 Loss 150 Bbls / 9 Wells Total: 1102 Bbls / 113 Wells | 1
| 2020-07-18 17:30 | July | 17:30 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-20 08:16 | 13.8KV PETAPAHAN FEEDER #8 | Petko | PGT South | Fair | Powerline / Conductor | 220 | Checked and found: PHNSB/13.8VCB8 T/SO, Counter : 275 / 277, Relay Flag : 51 Patrolled the line found : Finding broken off conductor 1 O O/P 29 CY 16 Cause : Conductor | 1
59 | 2020-07-18 18:44 | July | 18:44 | Afternoon | Saturday | Weekends | 18 | 2020 | 2020-07-18 18:44 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Lightning | 42 | Sintong VCB fdr #1 T/R 1x Not Checked Yet | 1
60 | 2020-07-18 19:44 | July | 19:44 | Night | Saturday | Weekends | 18 | 2020 | 2020-07-18 19:44 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Cloudy | Others | 77 | 19:44 Minas Feeder #1 T/Lo R/F 51N 21:05 it was reported at Minas Km 33 Public truck Hit the power pole. Check and Patrolled the line found Pole 6D/19 Hit truck. Open LBS 6D/26A 21:28 Block and closed Minas Feeder #1. | 1
61 | 2020-07-19 06:21 | July | 6:21 | Morning | Sunday | Weekends | 19 | 2020 | 2020-07-19 06:21 | 13.8KV CENTRAL DURI FEEDER #4 | Duri | PGT North | Fair | Dead End Insulator | 0 | C.Duri feeder # 4 T/R 1X Not checked yet | 1
| 2020-07-19 06:21 | July | 6:21 | Morning | Sunday | Weekends | 19 | 2020 | 2020-07-21 15:34 | 13.8KV CENTRAL DURI FEEDER #4 | Duri | PGT North | Fair | Dead End Insulator | 0 | Checked and found: CDRSG/13.8ACB21 T/R, Counter : 532 / 533, Relay Flag : 51N Patrolled the line found : Dead end Flash Over Cause : Dead End Insulator | 1
62 | 2020-07-19 10:53 | July | 10:53 | Morning | Sunday | Weekends | 19 | 2020 | 2020-07-19 10:53 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Fair | Under investigation | - | 10:53 Pinang VCB fdr #1 T/O (on block position) 115 kV GCB #27 Nella also T/O 2 second after Pinang fdr #1 T/O. TXP Pinang was Shut Off 11:52 Checked and found at Nella substation / 115 kV GCB #27 T/LO, ctr: 255 / 256 / Display at relay Nella : T/60 Pinang Operate, TX Pinang L/O 16:30 Reported findings at Pinang SS / Pinang VCB fdr #1 T/O (on block), R/F: 81, ctr: / 86T switch Normal, 86HR switch Normal Continue investigation tomorrow. Cause: Under Investigation | 1
63 | 2020-07-20 06:28 | July | 6:28 | Morning | Monday | Weekdays | 20 | 2020 | 2020-07-20 06:28 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Unidentified | 136 | 06:28 DF fdr #2 load dropped 83 A (141 / 58 A) 08:57 Checked and found 07/U3/21 T/O (on block for RIG BMS #09), ctr: 19/20 Call Rig Crew and confirmed they are on Normal Condition (no incident) 09:24 Manual Close RCL 07/U3/21, OK then release the block. The rig have been remove to other location. Cause: Unidentified | 1
64 | 2020-07-20 15:37 | July | 15:37 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-07-20 15:37 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Animal | 482 | 15:37 So. BLM VCB fdr #4 T/O (on block for RIG GBT #09 at So BLM #207) Confirmed to RIG crew, they are OK but at location So. BLM #105. 16:00 Patrol the line but found nothing 16:40 Manual Close VCB So. BALAM fdr #4 but failed (trip again) 16:48 It was reported there is animal at conductor near SoBLM #193 Patrolled and found monkey touch to line @2 on TOP of SoBLM #193 17:23 Open Isolation Switch of VCB So. BLM fdr #4 MTCE team c/o broken pin support @2 and HLC @2 on TOP BLM #193 17:59 Manual Close VCB So. BLM fdr #4, OK then release the block Counter: 436 / 438, R/F: 51N, 51P @2 Cause: Animal (monkey) | 1
65 | 2020-07-20 16:10 | July | 16:10 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-07-20 16:10 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Unidentified | 108 | 16:10 DF fdr #2 load dropped again 77 A (141 / 64 A) 17:23 Checked and found RCL 07/U3/21 T/SO, ctr: 20/21, R/F: 51P @1, @2, @3 Patrolled the power line but found nothing 18:04 Block and close RCL 07/U3/21, OK then release the block. Cause: Unidentified | 1
| 2020-07-20 16:10 | July | 16:10 | Afternoon | Monday | Weekdays | 20 | 2020 | 2020-07-21 16:13 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Unidentified | 108 | Checked and found: 5441/R.07/V3/21 T/SO, Counter : 20 / 21, Relay Flag : 50N Patrolled the line found : 0 Cause : Unidentified | 1
66 | 2020-07-21 17:38 | July | 17:38 | Afternoon | Tuesday | Weekdays | 21 | 2020 | 2020-07-21 17:38 | 13.8KV BATANG FEEDER #2 | Bangko-Balam | PGT North | Drizzle | Powerline / Conductor | 56 | 17:38 Batang VCB fdr #2 T/LO. Batang GFPC T/R 8 x 18:12 Reported by operator Rantau Bais, they were found broken conductor near location Rantau Bais #07 (on pole 35/AD/02). 20:19 Checked & found Batang fdr#2 T/LO Ctr:201/205 R/F:51N. Opened Isolation Switch Batang VCB fdr#2 Cut Jumper o/p 35AD15 for Isolation Broken Conductor 21:03 Close Isolation Switch Batang VCB fdr#2. 21:12 Blocked & closed Batang GFPC. 21:13 Blocked & closed Batang VCB fdr#2, then release the block. Continued tomorrow. | 1
67 | 2020-07-22 00:43 | July | 0:43 | Night | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 00:43 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Animal | 118 | Nella Feeder #1 Load Drop 123A ( 216/93A ) Not checked yet. | 1
| 2020-07-22 00:43 | July | 0:43 | Night | Wednesday | Weekdays | 22 | 2020 | 2020-07-27 07:24 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Animal | 118 | Checked and found: NLASB/13.8VCB1 T/R, Counter : 653 / 654, Relay Flag : 51N. Patrol led the line found: Monyet tergantung di Tiang Cause : Animal | 1
68 | 2020-07-22 05:25 | July | 5:25 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 05:25 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 56 | Menggala feeder #1 load dropped 138A (180/42A). Not checked yet. | 1
| 2020-07-22 05:25 | July | 5:25 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-24 09:05 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 56 | Checked and found: 5440/R.19AN04 T/R, Counter : 648 / 649, Relay Flag : 51N Patrolled the line found : Suspension Sompel layer 2 Phase : 1 Pole : 19 AM 12 Date Patrol : 23/JUL/2020 Operated Device : 5440/R.19AO01 T/R Counter : 109 / 111 Relay Flag : 51N Finding Patrol : dead end Sompel Phase : 1, 2, Pole : 19 AO 04 Date Patrol : 23/JUL/2020 Operated Device : 5440/R.19AO01 T/R Counter : 109 / 111 Relay Flag : 51N Finding Patrol : dead end Sompel Phase : 1 Pole : 19 AO 14 Patrol by : BKP Cause : Lightning | 1
69 | 2020-07-22 05:44 | July | 5:44 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 05:44 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 0 | Sintong fdr#2 Load dropped 180A (243/63A). Not checked yet. | 1
| 2020-07-22 05:44 | July | 5:44 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-24 09:07 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 0 | Checked and found: 5440/R.29Y16 T/R, Counter : 111 / 112, Relay Flag : NONE. Patrolled the line found : Deadend sompel layer 1 Cause : Lightning | 1
70 | 2020-07-22 06:15 | July | 6:15 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 06:15 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 198 | Sintong 13.8Kv OCB fdr #1 T/O (On block Rig HPS #04 at Kerang #01). Not checked yet. | 1
| 2020-07-22 06:15 | July | 6:15 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 17:11 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 198 | Checked and found Sintong VCB feeder #1 T/O R/F: 51N Counter: 431 / 432. Patrolled the line but found nothing. Cause : Lightning | 1
71 | 2020-07-22 06:15 | July | 6:15 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 06:15 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 145 | Sintong feeder #2 load dropped 218A (243/25A). Not checked yet. | 1
| 2020-07-22 06:15 | July | 6:15 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-24 09:09 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 145 | Checked and found: 5440/R.29Y16 T/R, Counter : 111 / 112, Relay Flag : NONE. Patrolled the line found: : Deadend sompel layer 1 Cause : Lightning | 1
72 | 2020-07-22 07:39 | July | 7:39 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 07:39 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Fair | Lightning | 89 | 6DN fdr #2 T/R 1X. Not checked yet. | 1
| 2020-07-22 07:39 | July | 7:39 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-28 08:13 | 13.8KV 6DN FEEDER #2 | Minas | PGT South | Fair | Lightning | 89 | Checked and found: 6DN OCB fdr #2 T/R 1x, Counter : 335 / 336, R/F : 50P @3 Patrolled the line and found Flash over Dead end Insulator@3 o/p 5D/41 Cause : Lightning | 1
73 | 2020-07-22 11:33 | July | 11:33 | Morning | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 11:33 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Rain and Lightning | Unidentified | 118 | 11:33 6D fdr #2 load dropped 95A (268/173A). It was reported no power at well2 6C/79 and 6C/89. 13:15 Checked and found Recl. 6D/298 T/LO ctr:90/93. Patrolled the line but found nothing. 14:49 Blocked and closed 6D fdr #2, Ok then released the block. Cause: Unidentified. | 1
74 | 2020-07-22 12:47 | July | 12:47 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 12:47 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 265 | 12:47 S. Balam fdr #1 T/O on blocked RIG GBT #12 at well S. Balam/150. 13:30 Checked and found S. Balm fdr #1 T/O ctr:419/420 R/F:51N. Patrolled the line but found nothing. 14:09 Blocked and closed S. Balam fdr #1. OK Cause: Unidentified. | 1
75 | 2020-07-22 14:49 | July | 14:49 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 14:49 | 4.16KV DUMAI (HCT FEEDER) FEEDER #2 | Dumai | PGT North | Fair | Planned Maintenance | 0 | 14:49 Manual Open Dumai 4160V fdr #2. Repair Hotspot at Cap Bank C/02. 15:20 Closed Dumai fdr #2. Cause: Plan Maintenance. | 1
76 | 2020-07-22 15:12 | July | 15:12 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 15:12 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Rain and Lightning | Lightning | 61 | 5B fdr #7 T/R 1X. 5B fdr 2 load dropped 112A (158/46A). 5B fdr 4 load dropped 50A (51/1A). 5B fdr 5 load dropped 11A (12/1A). 5B fdr 8 load dropped 275A (288/13A)//>WIP. Not checked yet. | 1
| 2020-07-22 15:12 | July | 15:12 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-07-28 08:10 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Rain and Lightning | Lightning | 61 | Checked and found: 5BOCB fdr #7 T/R 1x, Counter : 503 / 504, Relay Flag : 51 Patrolled the line but found nothing Cause : Lightning | 1
77 | 2020-07-22 15:13 | July | 15:13 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 15:13 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Unidentified | 32 | 3D fdr #2 T/R 1X. 3D fdr #3 load dropped 42A (84/42A). 3D fdr #4 load dropped 70A (142/72A). 3D fdr #5 load dropped 53A (104/51A). 3D fdr #6 load dropped 61A (128/67A). 3D fdr #8 load dropped 9A (207/198A). Not checked yet. | 1
| 2020-07-22 15:13 | July | 15:13 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-07-28 08:33 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Unidentified | 32 | Checked and found: 3D OCB fdr #2 T/R 2x, Counter : 381 / 383, R/F : 51 Patrolled the line but found nothing Cause : Unidentified | 1
78 | 2020-07-22 15:13 | July | 15:13 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 15:13 | 13.8KV 4D FEEDER #1 | Minas | PGT South | Rain and Lightning | Others | 0 | 4D fdr #1 load dropped 69A (196/127A). Not cheked yet. | 1
| 2020-07-22 15:13 | July | 15:13 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-07-28 08:30 | 13.8KV 4D FEEDER #1 | Minas | PGT South | Rain and Lightning | Others | 0 | Checked and found 4D OCB fdr #1 Normal, Counter : 210 / 210, R/F : NONE. Not Patrolled the line, suspected HPS pump at GS/5 OFF. Cause : Others | 1
79 | 2020-07-22 15:26 | July | 15:26 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-07-22 15:26 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain | Animal | 281 | Nella fdr #1 T/R 1X. Not cheked yet. | 1
| 2020-07-22 15:26 | July | 15:26 | Afternoon | Wednesday | Weekdays | 22 | 2020 | 2020-07-24 08:57 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain | Animal | 281 | Checked and found: NLASB/13.8VCB1 T/R, Counter : 653 / 654, Relay Flag : 51N Patrolled the line found : Monkey dead Cause : Animal | 1
80 | 2020-07-23 06:34 | July | 6:34 | Morning | Thursday | Weekdays | 23 | 2020 | 2020-07-23 06:34 | 13.8KV CENTRAL DURI FEEDER #9 | Duri | PGT North | Fair | Animal | 470 | 06:34 CD ACB fdr #9 T/LO, ctr: 410 / 413, R/F: 51P @1 @2. 07:30 Patrolled the line and found broken Bushing at Recloser 04/02/01. Isolated Recloser and open its Visual opening. 09:18 Blocked and closed CD fdr #9, Ok then released block. Cause: Animal (Tupai). | 1
81 | 2020-07-23 08:30 | July | 8:30 | Morning | Thursday | Weekdays | 23 | 2020 | 2020-07-23 08:30 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Fair | Recloser / Control Recloser | 207 | 08:30 It was reported No power around wells 8C/56N. Checked at trending and found on 22 July 20: / at 11:22 8C fdr #6 load dropped 58A (163/105A)///>WIP and Field. /at 15:51 8C fdr #6 load dropped 69A (105/36A))///>WIP and Field. (the weather Rain and Lightning). 10:33 Checked and found Recl. 8C/94 T/SO ctr:68/69. Blocked and closed the recloser but failed. 12:17 closed LBS 8C/57, load transfer to 8C/ fdr #3. Cause: Recloser control failure. | 1
82 | 2020-07-23 11:16 | July | 11:16 | Morning | Thursday | Weekdays | 23 | 2020 | 2020-07-23 11:16 | 13.8KV DURI FIELD FEEDER #2 | Duri | PGT North | Fair | Under investigation | 405 | 11:16 DF fdr #2 load dropped 141A (153/12A). 11:18 It was reported no power around road 07/U5/30 and 06/S5/12. 12:45 Checked and found Recloser 07/U5/32 Close position. And then checked to DF Substation and found DF fdr #2 T/LO ctr:1035/1039 R/F: 50@1, 51@1. /Patrolled the line and found Bird nest at Bushing Recloser 07/U5/32, /And also found @1 broken Pin insulator o/p 07/T5/06. 15:21 Blocked and closed DF fdr #2, Ok then released block (from Substation). Cause: Under investigation. | 1
83 | 2020-07-23 13:04 | July | 13:04 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-07-23 13:04 | 13.8KV BATANG FEEDER #2 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 13 | 13:04 Manual Open Batang fdr #2. Repaired broken Conductor o/p 35/AE/15 at Rantau Bais/07. 13:53 Close Batang fdr #2. Cause: Plan Maintenance. | 1
84 | 2020-07-23 16:19 | July | 16:19 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-07-23 16:19 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Fair | Animal | 0 | 44KV GCB #1 Duri /Dumai line T/R 1X. Not checked yet. | 1
| 2020-07-23 16:19 | July | 16:19 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-07-24 17:10 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Fair | Animal | 0 | 17:10 44KV ND/Dumai line GCB #1 T/R 1X. Not chcked yet. | 1
| 2020-07-23 16:19 | July | 16:19 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-07-28 08:38 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Fair | Animal | 0 | Checked and found: 44KVNDGCB#44 T/R, Counter : 166 / 168, Relay Flag : 50 Patrolled the line found died animal (monkey) inside Dumai Substation Cause : Animal | 1
85 | 2020-07-23 16:27 | July | 16:27 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-07-23 16:27 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Cloudy | Unidentified | 12 | Bekasap VCB feeder #6 T/R 1x. Bekasap feeder #3 load dropped 42A (264/222A). Bekasap feeder #5 load dropped 15A (256/141A). Not checked yet. | 1
| 2020-07-23 16:27 | July | 16:27 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-07-30 07:35 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Cloudy | Unidentified | 12 | Checked and found Bekasap VCB feeder #6 T/R1x. Counter: 389/390 Relay Flag: 51@1,@2. Patrolled the line found nothing. Cause : Unidentified. | 1
86 | 2020-07-23 17:04 | July | 17:04 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-07-23 17:04 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain and Lightning | Dead End Insulator | 0 | Bekasap VCB feeder #3 T/R 1x. Not checked yet. | 1
| 2020-07-23 17:04 | July | 17:04 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-07-30 07:40 | 13.8KV BEKASAP FEEDER #3 | Bekasap | PGT North | Rain and Lightning | Dead End Insulator | 0 | Checked and found Bekasap VCB feeder #3 T/R 1x. Counter:99596/99597 Relay Flag: 51@1. Patrolled the line found @1 broken dead end insulator on pole 37/BD020. Cause: Dead end insulator. | 1
87 | 2020-07-23 17:10 | July | 17:10 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-07-23 17:10 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Pin Insulator | 30 | Petani OCB feeder #2 T/R 1x. Not checked yet. | 1
| 2020-07-23 17:10 | July | 17:10 | Afternoon | Thursday | Weekdays | 23 | 2020 | 2020-07-30 07:45 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Pin Insulator | 30 | Checked and found Petani OCB feeder#2 Counter: 330/331 Relay Flag: 50@1,@2. Patrolled the line found @1 broken pin insulator towards well Petani #14. Cause: Pin insulator. | 1
88 | 2020-07-24 06:12 | July | 6:12 | Morning | Friday | Weekdays | 24 | 2020 | 2020-07-24 06:12 | 13.8KV MINAS FEEDER #6 | Minas | PGT South | Fair | Lightning | 187 | 06:12 Minas ACB fdr #6 T/O (block for rig AU/08 at 7E/24) Counter: 205 / 206, R/F: 51N Call RIG AU/08 confirmed OK/Normal 06:47 Manual close ACB Minas fdr #6, OK. 10:46 It was reported no power under Minas fdr #6. 11:15 Checked and found Recloser 7E/67A T/SO ctr: 101/102. Block and closed Recl. 7E/67A, OK then released block. Patrolled line and found flash over dead end @2 o/p M6DN/6 near loc. 6E/93 Cause : Lightning | 1
89 | 2020-07-24 10:38 | July | 10:38 | Morning | Friday | Weekdays | 24 | 2020 | 2020-07-24 10:38 | NORTH DURI SUBSTATION | Duri | PGT North | Fair | Planned Maintenance | 0 | 10:23 Switching to normalized ND TX/13. 10:38 Manual Open ND fdr #9, /////>Closed at 10:45. 10:39 Manual Open ND fdr #10, /////>Closed at 10:44. 10:39 Manual Open ND fdr #11, /////>Closed at 10:43. 10:40 Manual Open LBS 9/8 (Separated BUS ND TX/12 and ND TX/13). Cause: Plan maintenance. | 1
90 | 2020-07-24 18:06 | July | 18:06 | Afternoon | Friday | Weekdays | 24 | 2020 | 2020-07-24 18:06 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Dead End Insulator | 33 | C.Duri fdr #1 load dropped 52A (141/89A). Not checked yet. | 1
| 2020-07-24 18:06 | July | 18:06 | Afternoon | Friday | Weekdays | 24 | 2020 | 2020-07-30 07:52 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Dead End Insulator | 33 | Checked and found Recloser: 41/AW/62 T/R 1x D/S C.Duri feeder #1. Counter: 352/353 Relay Flag: None. Patrolled the line found @2 flash over dead end insulator on pole 40/AV/18. Cause: Dead end insulator. | 1
91 | 2020-07-25 17:07 | July | 17:07 | Afternoon | Saturday | Weekends | 25 | 2020 | 2020-07-25 17:07 | MENGGALA SUBSTATION | Bangko-Balam | PGT North | Cloudy and Lightning | Lightning | 330 | 17:07 Menggal 115KV C/S T/O. Menggala 13.8KV OCB fdr #2 T/R 1X. 18:10 Checked and found Menggala 115KV C/S T/O, Ctr: 190/191, R/F: 51P @1. Also found Mengggala frd #2 T/R 1X, Counter: 575/576 R/F:51@1, 51P. 18:14 Open Menggala fdr #1, ////> Blocked and Closed at 18:28. 18:15 Open Menggala fdr #1, ////> Blocked and Closed at 18:35. 18:22 Closed 115KV Menggala C/S, OK. Cause: Not Patrolled. | 1
| 2020-07-25 17:07 | July | 17:07 | Afternoon | Saturday | Weekends | 25 | 2020 | 2020-07-27 18:14 | MENGGALA SUBSTATION | Bangko-Balam | PGT North | Cloudy and Lightning | Lightning | 330 | Patrolled the power line d/s of MGL feeder #2 and found broken pin support insulator at phase @1 and @2 o/p 26/AL/59 Cause : Lightning | 1
92 | 2020-07-26 09:08 | July | 9:08 | Morning | Sunday | Weekends | 26 | 2020 | 2020-07-26 09:08 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 30 | 09:08 Open LBS: 26/AE/06 d/s Sintong fdr #1. Replaced Broken Pin Insulator o/p: 26/AD/17 09:35 Closed LBS: 26/AE/06 . Plan Maintenance. | 1
93 | 2020-07-27 06:20 | July | 6:20 | Morning | Monday | Weekdays | 27 | 2020 | 2020-07-27 06:20 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Fair | Animal | 0 | 06:20 44 kV GCB #1 ND T/R 1x Dumai Substation No Power for a few second Not Checked Yet | 1
| 2020-07-27 06:20 | July | 6:20 | Morning | Monday | Weekdays | 27 | 2020 | 2020-07-28 08:43 | 44KV NORTH DURI / DUMAI LINE | Duri | PGT North | Fair | Animal | 0 | Checked and found: 44KV ND GCB #1 T/R 1x, Counter: 168 / 169, R/F : 51N Patrolled the line found and found died animal (monkey) at Dumai Substation Cause : Animal | 1
94 | 2020-07-27 06:49 | July | 6:49 | Morning | Monday | Weekdays | 27 | 2020 | 2020-07-27 06:49 | 13.8KV CENTRAL DURI FEEDER #10 | Duri | PGT North | Cloudy | Dead End Insulator | 0 | 06:49 CD ACB/42 feeder #10 T/R 1x, ctr: 379 / 380, R/F: 51N Not Checked Yet | 1
| 2020-07-27 06:49 | July | 6:49 | Morning | Monday | Weekdays | 27 | 2020 | 2020-07-30 08:00 | 13.8KV CENTRAL DURI FEEDER #10 | Duri | PGT North | Cloudy | Dead End Insulator | 0 | Checked and found C Duri ACB #42 (feeder #10) T/R 1x. Counter: 379/380 Relay Flag: 51N. Patrolled the line found @1 flash over dead end insulator on pole 05/M6/A6A. Cause : Dead End Insulator. | 1
95 | 2020-07-27 09:45 | July | 9:45 | Morning | Monday | Weekdays | 27 | 2020 | 2020-07-27 09:45 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Petko | PGT South | Fair | Planned Maintenance | 85 | 09:45 manual Open Recloser 36/CU/29 D/S CKBS fdr #6. Replaced @1 Broken Pin Insulator o/p: 36/CU/22. (12 wells down during the JOB). 11:10 Closed Recloser 36/CU/29, but failed (Control failure). 12:40 Closed CKBS fdr #5, OK (Load under Recl. 36/CU/29 de feed from CKBS fdr #5). Cause: Plan Maintenance. | 1
96 | 2020-07-27 14:32 | July | 14:32 | Afternoon | Monday | Weekdays | 27 | 2020 | 2020-07-27 14:32 | 13.8KV 3D FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 26 | 14:32 Manual Open 3D fdr #3. Tol Road project (Commisioning at 4C/24). 15:54 Closed 3D fdr #3. Project. | 1
97 | 2020-07-28 08:22 | July | 8:22 | Morning | Tuesday | Weekdays | 28 | 2020 | 2020-07-28 08:22 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Recloser / Control Recloser | 64 | 08:22 S. Balam feeder # 4 load dropped 9A (206/197A). 13:20 It was reported no power at well Balam/28, 216 and Balam/303. 14:22 Checked and found Recloser: 16/AA/43 T/SO Counter: 90/91. Patrolled the line but found nothing. 14:26 Blocked and closed Recloser: 16/AA/43, Ok then released block. Cause: Control Recloser. | 1
98 | 2020-07-29 09:26 | July | 9:26 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-07-29 09:26 | PEMATANG MAIN SUBSTATION | Bekasap | PGT North | Fair | Planned Maintenance | 1195 | S/D Pematang Main for Replaced 115Kv LA at Pematang Main Subst. 09:26 Manually opened Rokan VCB fdr#2, then closed at 13:55. 09:27 Manually opened Rangau VCB fdr#2, then closed at 13:52. 09:29 Manually opened Petani VCB fdr#2, then closed at 13:52. 09:30 Manually opened Pematang VCB fdr#2, then closed at 13:54. 09:31 Manually opened Rangau VCB fdr#1, then closed at 13:49. 09:31 Manually opened Petani VCB fdr#1, then closed at 13:13:45. 10:04 Manually opened Pematang VCB fdr#1, then closed at 13:13:48. 10:06 Manually opened 44Kv Pematang Main GCB#1, then closed at 13:43. 10:07 Manually opened 44Kv Pematang Main GCB#2, then closed at 13:43. 10:08 Manually opened 44Kv Pematang Main GCB#3, then closed at 13:13:44. 10:12 Manually opened 115Kv Pematang Main C/S, then closed at 13:40. Cause: Plan Maintenance. Production Loss: Rokan feeder #2 ///> 76 Bbls / 6 Wells. Rangau feeder #2 ///> 191 Bbls / 19 Wells. Petani feeder #2 ///> 227 Bbls / 21 Wells. Pematang feeder #2///> 425 Bbls / 28 Wells. Rokan feeder #1 ///> 7 Bbls / 3 Wells. Petani feeder #1 ///> 511 Bbls / 34 Wells. Pematang feeder #2///> 206 Bbls / 19 Wells. ////////////////////////////////////////////////////+ TOTAL: 1567 Bbls / 124 Wells. | 1
99 | 2020-07-29 10:30 | July | 10:30 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-07-29 10:30 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 7 | 10:30 Manually open 4B feeder #2. Repaired broken pin insulation. 11:13 Blocked & closed 4B feeder #2, The released the block. Cause : Maintenance job. | 1
100 | 2020-07-29 11:06 | July | 11:06 | Morning | Wednesday | Weekdays | 29 | 2020 | 2020-07-29 11:06 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 70 | Sintong 13.8Kv VCB fdr#2 T/R 1X. Not checked yet. | 1
101 | 2020-07-29 12:35 | July | 12:35 | Afternoon | Wednesday | Weekdays | 29 | 2020 | 2020-07-29 12:35 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Emergency | 0 | 12:35 Manually open NKBS feeder #2. Emergency pipe leak 14" at Kota Batak Area. 18:10 Blocked & closed NKBS feeder #2, Then released the block. 19:39 Manually open NKBS feeder #2. Emergency pipe leak 14" at Kota Batak Area (Continue). Cause: Emergency. | 1
| 2020-07-29 12:35 | July | 12:35 | Afternoon | Wednesday | Weekdays | 29 | 2020 | 2020-07-30 21:50 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Emergency | 0 | 21:50 Closed NKB feeder #2. | 1
102 | 2020-07-29 14:59 | July | 14:59 | Afternoon | Wednesday | Weekdays | 29 | 2020 | 2020-07-29 14:59 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 14:59 CGT#4 Trip by alarm Fire Detective. 15:08 Closed Tie Breaker ACB#39. | 1
103 | 2020-07-30 09:15 | July | 9:15 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-07-30 09:15 | 13.8KV 6DN FEEDER #5 | Minas | PGT South | Fair | Planned Maintenance | 168 | 09:15 Manually open LBS 6D/16 D/S 6DN feeder #5. Repair broken power pole 6D/19. Cause :Plain maintenance. | 1
104 | 2020-07-30 10:57 | July | 10:57 | Morning | Thursday | Weekdays | 30 | 2020 | 2020-07-30 10:57 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 327 | 10:37 Manaually open Manggala Feeder # 1. Repalace transformer for Sacfeeding #2 Manggala. 13:43 Block and closed manggala feeder #1. Plane maintenance. | 1
105 | 2020-07-31 08:25 | July | 8:25 | Morning | Friday | Weekdays | 31 | 2020 | 2020-07-31 08:25 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Cloudy | Unidentified | 0 | C.Duri 13.8Kv ACB #28 fdr# 16 T/R 1x. Not checked yet. | 1
| 2020-07-31 08:25 | July | 8:25 | Morning | Friday | Weekdays | 31 | 2020 | 2020-05-08 09:27 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Cloudy | Unidentified | 0 | Checked and found CDRSG/13.8ACB28 T/R 1x R/F: 51N Counter: 392/393. Patrolled the line and found nothing. Cause : Unidentified. | 1
106 | 2020-07-31 08:49 | July | 8:49 | Morning | Friday | Weekdays | 31 | 2020 | 2020-07-31 08:49 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 0 | 08:49 Sintong feeder #1 load dropped 43A (96/53A). 09:25 Checked & found recloser 25/AD/26 T/R 2x. Ctr: 1005/1007. 13:00 Patrolled the line but found nothing. Cause : unidentified. | 1
107 | 2020-07-31 20:56 | July | 20:56 | Night | Friday | Weekdays | 31 | 2020 | 2020-07-31 20:56 | 13.8KV PETAPAHAN FEEDER #4 | Petko | PGT South | Rain | Unidentified | 214 | 20:56 Petapahan Load dropped 23A (146/109A). 23:00 It was reported no Power at Topas wells. 23:43 Checked and found Recloser 28/CW/01 T/SO ctr:67/68. Blocked and closed Recloser 28/CW/01, Ok then released block. Not Patrolled yet. | 1
| 2020-07-31 20:56 | July | 20:56 | Night | Friday | Weekdays | 31 | 2020 | 2020-01-08 20:56 | 13.8KV PETAPAHAN FEEDER #4 | Petko | PGT South | Rain | Unidentified | 214 | Patrolled the line but found nothing. Cause : Unidentified. | 1
1 | 2020-01-08 10:34 | January | 10:34 | Morning | Wednesday | Weekdays | 8 | 2020 | 2020-01-08 10:34 | 13.8KV CENTRAL DURI FEEDER #5 | Duri | PGT North | Fair | Planned Maintenance | 0 | 10:34 Manually Opened Recl. 03-4-16 (C.Duri fdr#5). Repaired hot spot o/p for 2500Kva Tx at CGS#3. 11:08 Blocked & closed Recl. 03-4-16, then release the block. Cause: Maintenance Plan. | 1
2 | 2020-01-08 11:50 | January | 11:50 | Morning | Wednesday | Weekdays | 8 | 2020 | 2020-01-08 11:50 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 11:50 S/U MGT#1, then on line the unit at 12:24. | 1
3 | 2020-01-08 19:42 | January | 19:42 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-01-08 19:42 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Recloser - Control Recloser | 0 | Sintong feeder #1 load dropped 50A (102-52A). Not checked yet. | 1
4 | 2020-01-08 21:39 | January | 21:39 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-01-08 21:39 | 13.8KV MINAS FEEDER #1 | Minas | PGT South | Heavy Rain | Powerline - Jumper | 71 | 21:39 Minas ACB #14 fdr #1 T/Lo. Ctr : 108-110 R/f 50 @1,@2, @3. Patrolled & found @1 broken jumper o/p 6D-303. 23:01 Open LBS 6D-26A (12 wells will be down). 23:04 Blocked & closed Minas feeder #1, OK then released block. Cause : Jumper (Broken). | 1
5 | 2020-01-08 21:40 | January | 21:40 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-01-08 21:40 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 21:40 MGT #1 tripped Open Gen. Breaker by Exciter trouble And then S/D the unit for trouble shoot the problem. | 1
6 | 2020-02-08 08:05 | February | 8:05 | Morning | Saturday | Weekends | 8 | 2020 | 2020-02-08 08:05 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Animal | 179 | So.Balam fdr#4 Load dropped 69A (210-141A). So.Balam GFPC T/R 1x. Not checked yet. | 1
7 | 2020-02-08 08:39 | February | 8:39 | Morning | Saturday | Weekends | 8 | 2020 | 2020-02-08 08:39 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Recloser - Control Recloser | 0 | Sintong fdr#1 Load dropped 50A (102-52A). Not checked yet. | 1
8 | 2020-02-08 14:28 | February | 14:28 | Afternoon | Saturday | Weekends | 8 | 2020 | 2020-02-08 14:28 | 115KV CENTRAL DURI - BATANG LINE | Duri | PGT North | Fair | Others | 346 | 14:28 115Kv Line C.Duri-BTG OCB#31 T/LO Ctr:667-673 R/F:51@3. 115Kv Line C.Duri-BTG OCB#33 T/LO Ctr:65-69 R/F:86@1@3. 115Kv Line STG-BTG OCB#25 T/O Ctr:326-327. Batang fdr#1, fdr#2, fdr#3 no power. Pinang fdr#1 Load dropped 53A (101-48A). So.Balam fdr#1 Load dropped 56A (184-128A). So.Balam fdr#4 Load dropped 58A (210-152A). Nella fdr#1 Load dropped 44A (219-175A). Menggala fdr#1 Load dropped 32A (182-150A). Sintong fdr#2 Load dropped 64A (168-104A). Bangko fdr#1 Load dropped 42A (170-128A). Bangko fdr#4 Load dropped 67A (190-126A). Patrolled the line & found Fall Down Radio tower Beetween pole BTG#48-#49 at Kulim. Isolated Broken Radio Tower. 16:37 Closed 115Kv Line C.Duri-BTG OCB#31. 16:39 Closed 115Kv Line C.Duri-BTG OCB#33. 16:38 Closed 115Kv Line STG_BTG OCB#25. Cause: Other (Broken Radio Tower). | 1
9 | 2020-02-08 15:13 | February | 15:13 | Afternoon | Saturday | Weekends | 8 | 2020 | 2020-02-08 15:13 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 15:13 S/U MGT#5, then on line the unit at 15:28. | 1
10 | 2020-03-08 07:11 | March | 7:11 | Morning | Sunday | Weekends | 8 | 2020 | 2020-03-08 07:11 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | - | Duri Community ACB#25 fdr#1 T/R 1x. Not checked yet. | 1
| 2020-03-08 07:11 | March | 7:11 | Morning | Sunday | Weekends | 8 | 2020 | 2020-05-08 10:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Duri | PGT North | Cloudy | Unidentified | - | Checked and found DCSG-13.8ACB25 T/R 1x R/F: 51N Counter: 157-158. Patrolled the line and found nothing. Cause: Unidentified. | 1
11 | 2020-03-08 10:10 | March | 10:10 | Morning | Sunday | Weekends | 8 | 2020 | 2020-03-08 10:10 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Tree | 34 | 10:10 It was reported No power at 09-L5-18 (C.Duri fdr#16). 11:00 Checked & found Recl 09-L5-20 T/SO. Patrolled the line Danger Tree pole 09-L5-18. 15:00 Blocked & closed Recl.09-L5-20, then release the block. Cause: Tree. | 1
12 | 2020-03-08 14:07 | March | 14:07 | Afternoon | Sunday | Weekends | 8 | 2020 | 2020-03-08 14:07 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Fair | Planned Maintenance | 40 | 14:07 Manually opened Recl. 2D-14 (3D fdr#4). Dismantle conductor at well 1E-33 & 2D-33. 16:50 Block & closed Recl. 2D14, then release the block. Cause: Maintenance. | 1
13 | 2020-03-08 15:30 | March | 15:30 | Afternoon | Sunday | Weekends | 8 | 2020 | 2020-03-08 15:30 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 15:30 S/U MGT#8 Then on line the unit at 15:48. | 1
14 | 2020-03-08 16:50 | March | 16:50 | Afternoon | Sunday | Weekends | 8 | 2020 | 2020-03-08 16:50 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 16:50 S/U MGT#3, Then on line the unit at 17:07 | 1
15 | 2020-03-08 17:24 | March | 17:24 | Afternoon | Sunday | Weekends | 8 | 2020 | 2020-03-08 17:24 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 17:07 S/U MGT#9, Then on line the unit at 17:38. | 1
16 | 2020-03-08 17:45 | March | 17:45 | Afternoon | Sunday | Weekends | 8 | 2020 | 2020-03-08 17:45 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | Off Line NDC#2, then S/D the unit for Maintenance. | 1
17 | 2020-03-08 17:51 | March | 17:51 | Afternoon | Sunday | Weekends | 8 | 2020 | 2020-03-08 17:51 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 17:51 S/U MGT#3, Then on line the unit at 18:24. | 1
18 | 2020-04-08 00:40 | April | 0:40 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-04-08 00:40 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Heavy Rain | Lightning | 76 | 8C VCB feeder #6 T/R 1x. 8C feeder #4 load dropped 222A (302-80A). Not checked yet. | 1
| 2020-04-08 00:40 | April | 0:40 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-05-08 14:20 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Heavy Rain | Lightning | 76 | Checked and found 8CSB-13.8VCB6 T/R 5x R/F: 51 @1,2 Counter: 637 - 642. Patrolled the line and found nothing. Cause: Lightning. | 1
19 | 2020-04-08 01:23 | April | 1:23 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-04-08 01:23 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | 34 | 4B OCB feeder #1 T/R 1x. Not checked yet. | 1
| 2020-04-08 01:23 | April | 1:23 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-07-08 08:44 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Rain and Lightning | Lightning | 34 | Checked and found 13.8 kV 4B OCB #1 T/R 2x R/F: 51@1,2 Counter: 390-392. Patrolled the line and found Broken LA and PIN insulator on pole 4B-62 and Flash Over PIN insulator on pole 4B-99. Cause : Lightning | 1
20 | 2020-04-08 01:23 | April | 1:23 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-04-08 01:23 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Rain and Lightning | Others | 0 | 4B feeder #2 load dropped 40A (54-14A). Not checked yet. | 1
| 2020-04-08 01:23 | April | 1:23 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-07-08 08:37 | 13.8KV 4B FEEDER #2 | Minas | PGT South | Rain and Lightning | Others | 0 | Checked and found 13.8 kV 4B 0cb #2 normal condition. Then Checked Recloser 5B-93 and found normal condition. Suspect: HPS pump at GS #6 tripped. Cause: Others. | 1
21 | 2020-04-08 01:23 | April | 1:23 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-04-08 01:23 | 13.8KV 4B FEEDER #6 | Minas | PGT South | Rain and Lightning | Tree | 63 | 01:23 4B feeder #6 load dropped 71A (102-31A). 04:00 It was reported no power at wells in front NBS. 05:00 Checked and found Reclose 4B-148 T/SO ctr: 91-93. 05:06 Blocked and closer the recloser, but failed. Patrolled the line but found nothing. 06:00 Open LBS 4B-150, and then close REc. 4B-148 but tripped again. Continued to Patrolle and found Palm branch touch power line at LBS 4B-29. 06:43 Masnual Open 4B feeder #1, then removed Palm branch. 06:49 Closed 4B feeder #1. 06:53 Blocked and closed 4B feeder #6. Ok then released block. Cause: Tree. | 1
22 | 2020-04-08 01:58 | April | 1:58 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-04-08 01:58 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Heavy Rain | Suspension Insulator | 268 | 01:58 5B feeder #2 load dropped 112A (132-20A). 10:13 Checked and found Recloser 5C-07 T/LO Counter: 83-91 Patrolled the line found @2 broken suspension insulator , on pole NN towards cathodic # 5D-23. Blocked and closed the Recloser. Ok then released block. Cause: Broken suspension insulator . | 1
| 2020-04-08 01:58 | April | 1:58 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-10-08 08:12 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Heavy Rain | Suspension Insulator | 268 | On Aug 09,2020. Replaced broken suspension insulator on pole NN , towards Cathodic #5D-03. Cause: Broken Suspension insulator. | 1
23 | 2020-04-08 06:05 | April | 6:05 | Morning | Wednesday | Weekdays | 8 | 2020 | 2020-04-08 06:05 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Heavy Rain | Unidentified | 76 | 06:05 8C 13.8Kv VCB fdr #6 T/LO. 07:04 Manually Opened 8C fdr#3, then closed at 08:46. 07:04 Manually Opened 8D fdr#3, then closed at 08:18. 07:27 Manually opened Minas fdr#3, then closed at 09:01. 07:15 Checked & found 8C fdr#6 T/LO Ctr:637-642 R/F:51@1@2. Patrolled the line but found nothing. 08:07 Blocked & closed 8C VCB fdr#6, then release the block. Cause: Unidentified. Production loss: 8C feeder #3 and 8D fdr #3 : 95 bbls / 15 wells. Minas feeder # 3 : 58 Bbls / 26 wells. --------------------------------------------------------+ T O T A L : 153 Bbls / 41 wells. | 1
24 | 2020-04-08 06:07 | April | 6:07 | Morning | Wednesday | Weekdays | 8 | 2020 | 2020-04-08 06:07 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Heavy Rain | Normal Condition | 0 | 8D feeder #5 load dropped 40A (163-123A). Not checked yet. | 1
| 2020-04-08 06:07 | April | 6:07 | Morning | Wednesday | Weekdays | 8 | 2020 | 2020-07-08 08:21 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Heavy Rain | Normal Condition | 0 | Checked and found 13.8 kV 8D OCB #5 normal condition, Counter: 319-319. Patrolled the line and found nothing. Cause: Normal condition. | 1
25 | 2020-04-08 06:07 | April | 6:07 | Morning | Wednesday | Weekdays | 8 | 2020 | 2020-04-08 06:07 | 13.8KV 8D FEEDER #8 | Minas | PGT South | Heavy Rain | Others | 0 | 8D feeder #8 load dropped 70A (190-120A). Not checked yet. | 1
| 2020-04-08 06:07 | April | 6:07 | Morning | Wednesday | Weekdays | 8 | 2020 | 2020-07-08 08:17 | 13.8KV 8D FEEDER #8 | Minas | PGT South | Heavy Rain | Others | 0 | Checked and found 13.8 kV 8D OCB #8 normal condition, counter: 476-476. Suspect: HPS pump at GS #1 tripped. Cause: Others. | 1
26 | 2020-04-08 10:27 | April | 10:27 | Morning | Wednesday | Weekdays | 8 | 2020 | 2020-04-08 10:27 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Animal | 285 | 10:27 Ketigul Feeder#2 T/Lo 12:15 Checked and Found Ketigul Fdr# 2 T/R 3X Ctr: 398-401. Patroll the line found dead monkey o/p 29 AL 20 Pagar #17. 15:55 Block and closed Ketigul Fdr#2 then release the block. Couse : Animal. | 1
27 | 2020-04-08 12:28 | April | 12:28 | Afternoon | Wednesday | Weekdays | 8 | 2020 | 2020-04-08 12:28 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 95 | Sintong feeder # 2 T/R 1X Not checked yet. | 1
28 | 2020-05-08 10:27 | May | 10:27 | Morning | Friday | Weekdays | 8 | 2020 | 2020-05-08 10:27 | 13.8KV NEW KOTABATAK FEEDER #2 | Petko | PGT South | Fair | Planned Maintenance | 29 | 10:27 Switching to shutdown par of load CKBS Feeder #1 and NKBS Feeder #2 Replace broken dead end insulator o/p LBS 37-CX-11 @2 12:47 Re-energized load CKB F1 and NKB F2. Cause: Planned maintenance. | 1
29 | 2020-05-08 10:53 | May | 10:53 | Morning | Friday | Weekdays | 8 | 2020 | 2020-05-08 10:53 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 4 | 10:53 Central Duri ACB #28 ( feeder # 16) T/O in Block Position PT WKS Clean up cannal. Check to area PT WKS working normal condition 11:06 Manually blocked and closed C.Duri ACB #28 (feeder #16) and still in block position. Not checked yet. | 1
| 2020-05-08 10:53 | May | 10:53 | Morning | Friday | Weekdays | 8 | 2020 | 2020-09-08 08:17 | 13.8KV CENTRAL DURI FEEDER #16 | Duri | PGT North | Fair | Unidentified | 4 | Checked and found C Duri ACB #28 (feeder #16) T/R 1x. Counter : 393 - 394 Relay Flag : 50@1,@2. Patrolled the line nothing found. Cause : Unidentified. | 1
30 | 2020-05-08 20:00 | May | 20:00 | Night | Friday | Weekdays | 8 | 2020 | 2020-05-08 20:00 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 20:00 S/U NDC #2 then online the unit at 20:25. | 1
31 | 2020-06-08 07:07 | June | 7:07 | Morning | Monday | Weekdays | 8 | 2020 | 2020-06-08 07:07 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 07:07:01 S/D NDC #3 09:36 S/U NDC #3 then online the unit at 10:12. | 1
32 | 2020-06-08 07:08 | June | 7:08 | Morning | Monday | Weekdays | 8 | 2020 | 2020-06-08 07:08 | NORTH DURI SUBSTATION | Duri | PGT North | Fair | Lightning Arrester | 1316 | 07:08 North Duri 115kV GCB #1 T/O Closed at 8:30 Ctr: 115 North Duri 115kV GCB # 2 T/O Closed at 8:30 Ctr: 96 North Duri 115kV C/S # 11 Open Closed at 8:31 Ctr: 765 North Duri 115kV C/S # 12 Open Closed at 8:31 Ctr: 224 North Duri 115kV C/S # 13 Open Closed at 14:21 Ctr: 3566 08:00 Found out 115KV L/A after C/S TX13 was burn out, R/F 86B 08:27 Manual open 13.8 kV North Duri Fdr# 1 Block & Closed at 08:39 Ctr: 346 Manual open 13.8 kV North Duri Fdr# 2 Ctr: 291 Manual open 13.8 kV North Duri Fdr# 3 Ctr: 179 Manual open 13.8 kV North Duri Fdr# 4 Ctr: 206 Manual open 13.8 kV North Duri Fdr# 5 Ctr: 160 Manual open 13.8 kV North Duri Fdr# 6 Ctr: 32 Manual open 13.8 kV North Duri Fdr# 7 Ctr: 147 Manual open 13.8 kV North Duri Fdr# 8 Ctr: 120 Manual open 13.8 kV North Duri Fdr# 9 Ctr: 88 Manual open 13.8 kV North Duri Fdr# 10 Ctr: 54 Manual open 13.8 kV North Duri Fdr# 11 Ctr: 204 Manual open 44kV GCB#1 ND to Dumai Ctr: 170 09:16 Manual open 13.8 kV North Duri fdr# 6 as requested by CGS #10 11:26 Block and closed 13.8 kV North Duri fdr#6. 14:18 Manual open North Duri Fdr# 11 Closed at 14:24 14:19 Manual open North Duri Fdr# 10 Closed at 14:23 14:19 Manual open North Duri Fdr# 9 Closed at 14:22 Replace 3Pcs 115 kV L/A | 1
33 | 2020-06-08 10:15 | June | 10:15 | Morning | Monday | Weekdays | 8 | 2020 | 2020-06-08 10:15 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 10:15 Off line & S/D NDC #1 | 1
34 | 2020-06-08 10:25 | June | 10:25 | Morning | Monday | Weekdays | 8 | 2020 | 2020-06-08 10:25 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Planned Maintenance | 44 | 10:25 Open LBS 34 CT 58 D/S CKBS Fdr#5 Replace Broken P/Ins O/P 34CS06 and 35CT25. 11:34 Closed LBS 34CT58. Cause: Planned maintenance. | 1
35 | 2020-06-08 10:32 | June | 10:32 | Morning | Monday | Weekdays | 8 | 2020 | 2020-06-08 10:32 | 13.8KV 5B FEEDER #7 | Minas | PGT South | Fair | Planned Maintenance | 14 | 10:32 Manually opened 5B OCB feeder # 7. Replaced @2 broken pin insulator on pole 4C-13A. 11:39 Manually blocked and closed 5B OCB feeder#7 and then released the block. Cause: Planned maintenance. | 1
36 | 2020-06-08 12:08 | June | 12:08 | Afternoon | Monday | Weekdays | 8 | 2020 | 2020-06-08 12:08 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Emergency | - | Manually Opened Nella VCB fdf#1. Requested BKO GS by Pipe Leak. | 1
| 2020-06-08 12:08 | June | 12:08 | Afternoon | Monday | Weekdays | 8 | 2020 | 2020-07-08 03:02 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Emergency | - | Blocked & closed Nella VCB fd#1, then release the block. Cause: Emergency (Pipe Leak). | 1
37 | 2020-06-08 12:08 | June | 12:08 | Afternoon | Monday | Weekdays | 8 | 2020 | 2020-06-08 12:08 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Fair | Emergency | - | 12:08 Manual open Bangko fdr#1 requested by Operator Bangko EOR. Replace pipe leak water line. | 1
| 2020-06-08 12:08 | June | 12:08 | Afternoon | Monday | Weekdays | 8 | 2020 | 2020-07-08 02:55 | 13.8KV BANGKO FEEDER #1 | Bangko-Balam | PGT North | Fair | Emergency | - | Blocked & closed Bangko VCB fdr#1, then release the block. Cause: Emergency (Pipe Leak). | 1
38 | 2020-06-08 16:09 | June | 16:09 | Afternoon | Monday | Weekdays | 8 | 2020 | 2020-06-08 16:09 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 16:09 Off Line and S/D MGT #1. | 1
39 | 2020-06-08 16:12 | June | 16:12 | Afternoon | Monday | Weekdays | 8 | 2020 | 2020-06-08 16:12 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 69 | Sintong feeder #2 load drop 173 A ( 252-79A) Not Checked yet. | 1
| 2020-06-08 16:12 | June | 16:12 | Afternoon | Monday | Weekdays | 8 | 2020 | 2020-10-08 08:17 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 69 | Checked and found Recloser 28-AF-02 T/R 2x. Counter: 1556-1558 Relay Flag: None. Patrolled the line nothing found. Cause: Unidentified. | 1
40 | 2020-07-08 02:01 | July | 2:01 | Night | Wednesday | Weekdays | 8 | 2020 | 2020-07-08 02:01 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Theft | 626 | 02:01 C.Duri fdr#1 Load dropped 64A (136-72A). 03:20 Checked & found Recl. 41AW62 T/SO Ctr:353-354 R/F:51@3, 51N. 04:50 Patrolled the line & found @3 Broken Conductor o/p 39AV19. 07:50 Block and Closed Recl 41 AW 62. Couse : Theft (attempted theft). | 1
41 | 2020-08-08 03:38 | August | 3:38 | Night | Saturday | Weekends | 8 | 2020 | 2020-08-08 03:38 | 13.8KV PETAPAHAN FEEDER #8 | Petko | PGT South | Fair | Broken Fuse Cut Out | 396 | 03:38 It was reported Spark at Petapahan GS. 05:10 Chedked & found @1 Broken FCO for 500 Kva Tx at Petapahan GS. 05:15 Manually Open Petapahan fdr#6, then Closed at 06:15. 06:15 Manually open Petapahan fdr#3, then closed at 07:23. 06:48 Transfer part of load Fdr#8 to Pet Fdr#6 by closing LBS 30 CZ 04. 06:53 Shutoff Recl 30 CZ 23 , Normalized at 09:37. 07:15 Manually open Pet fdr#4 Req by Operator Petapahan GS 09:08 Manually open Pet Fdr#8 to replace broken Cutout. 09:23 Block and close Pet fdr#8. 09:39 Normalized load Pet fdr#8 by open LBS 30CZ04 from Pet fdr#6. | 1
42 | 2020-08-08 06:12 | August | 6:12 | Morning | Saturday | Weekends | 8 | 2020 | 2020-08-08 06:12 | 13.8KV SURAM FEEDER #1 | Petko | PGT South | Fair | Unidentified | 0 | Suram fdr#1 T/R 1x. Not checked yet. | 1
| 2020-08-08 06:12 | August | 6:12 | Morning | Saturday | Weekends | 8 | 2020 | 2020-08-08 06:12 | 13.8KV SURAM FEEDER #1 | Petko | PGT South | Fair | Unidentified | 0 | Checked and found SRMSB-13.8OCB1 T/R 1X R/F: 51N Counter : 152 - 153 Patrolled the line and found nothing Cause : Unidentified | 1
43 | 2020-08-08 08:51 | August | 8:51 | Morning | Saturday | Weekends | 8 | 2020 | 2020-08-08 08:51 | 13.8KV 6DN FEEDER #5 | Minas | PGT South | Fair | Planned Maintenance | 71 | 08:51 Manual open 6DN Feeder #5 Install flying tape o/p 6D-19A 11:06 Block and Close 6DN Feeder #5 , Ctr:266-267 Maintenance job. | 1
44 | 2020-08-08 16:39 | August | 16:39 | Afternoon | Saturday | Weekends | 8 | 2020 | 2020-08-08 16:39 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Fair | Unidentified | 0 | Darling Feeder #7 T/R 1X Not Checked yet. | 1
| 2020-08-08 16:39 | August | 16:39 | Afternoon | Saturday | Weekends | 8 | 2020 | 2020-11-08 09:59 | 13.8KV DARLING VCB FEEDER #7 | Duri | PGT North | Fair | Unidentified | 0 | Checked and found DRL VCB fdr #7 T/R 1x, ctr: 192 - 193, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
45 | 2020-09-08 10:36 | September | 10:36 | Morning | Tuesday | Weekdays | 8 | 2020 | 2020-09-08 10:36 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Fair | Unidentified | 8 | Ketigul feeder # 3 T/R 1X Not checked yet. | 1
| 2020-09-08 10:36 | September | 10:36 | Morning | Tuesday | Weekdays | 8 | 2020 | 2020-11-08 10:02 | 13.8KV KETIGUL FEEDER#3 | Bangko-Balam | PGT North | Fair | Unidentified | 8 | Checked and found KTGL VCB fdr #3 T/R 1x, ctr: 237 - 238, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
46 | 2020-09-08 11:30 | September | 11:30 | Morning | Tuesday | Weekdays | 8 | 2020 | 2020-09-08 11:30 | 13.8KV 5B FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 27 | 11:30 Manually open Recloser 5C-07 D/S 5B fdr#2 Replace sespention insulator o/p 5D-03 12:21 Closed Recloser 5C-07. Planned maintenance. | 1
47 | 2020-09-08 15:05 | September | 15:05 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-09-08 15:05 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Fair | Others | 21 | 8C Feeder # 4 T/R 1X Not checked yet. | 1
| 2020-09-08 15:05 | September | 15:05 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-11-08 17:39 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Fair | Others | 21 | Checked and found 8C VCB feeder #4 T/R 1x, ctr: 635 - 636, R/F: 50N Patrolled the line but found nothing Cause : Others | 1
48 | 2020-09-08 15:05 | September | 15:05 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-09-08 15:05 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Fair | Others | 33 | 8C Feeder # 6 T/R 1X Not checked yet. | 1
| 2020-09-08 15:05 | September | 15:05 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-11-08 17:48 | 13.8KV 8C FEEDER #6 | Minas | PGT South | Fair | Others | 33 | Checked and found 8C VCB feeder #6 T/R 1x, counter: 642-643, R/F: 50N Patrolled the line but found nothing Cause : Others | 1
49 | 2020-10-08 03:44 | October | 3:44 | Night | Thursday | Weekdays | 8 | 2020 | 2020-10-08 03:44 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Fair | Unidentified | 19 | 8D OCB fdr#5 T/R 1x. Not checked yet. | 1
| 2020-10-08 03:44 | October | 3:44 | Night | Thursday | Weekdays | 8 | 2020 | 2020-11-08 17:47 | 13.8KV 8D FEEDER #5 | Minas | PGT South | Fair | Unidentified | 19 | Checked and found 8D VCB fdr #5 T/R 1x, ctr: 319 - 320, R/F: 50N Patrolled the line but found nothing Cause : Others | 1
50 | 2020-10-08 16:00 | October | 16:00 | Afternoon | Thursday | Weekdays | 8 | 2020 | 2020-10-08 16:00 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 16:00 S/U NDC # 1 then on line at 16:28. | 1
51 | 2020-10-08 19:39 | October | 19:39 | Night | Thursday | Weekdays | 8 | 2020 | 2020-10-08 19:39 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | Off Line NDC#3, then S/D the unit for Maintenance. | 1
52 | 2020-11-08 09:50 | November | 9:50 | Morning | Sunday | Weekends | 8 | 2020 | 2020-11-08 09:50 | 13.8KV 4D FEEDER #4 | Minas | PGT South | Fair | Construction Job | 24 | 09:50 Manually open Recloser 4D-51A 12:15 Closed Recloser 4D-51A Cause: Construction job. | 1
53 | 2020-11-08 09:59 | November | 9:59 | Morning | Sunday | Weekends | 8 | 2020 | 2020-11-08 09:59 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Fair | Construction Job | 78 | 09:59 Manual open Recloser 34-BI-18, 13:31 Close Recloser 34 BI 18. Cause : Construction Job | 1
54 | 2020-12-08 07:01 | December | 7:01 | Morning | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 07:01 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Fair | Unidentified | 395 | 07:01 C.Duri feeder #1 load dropped 72A (145-73A). 09:00 Checked & found recloser 41-AW-62 T/O Ctr: 354-355. Patrolled the line but found nothing. 10:42 Blocked & closed the recloser 41-AW-62 OK. The released block. Cause : Unidentified. | 1
55 | 2020-12-08 15:30 | December | 15:30 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 15:30 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 15:30 NDC #3 the online then unit 15:57. GCB #33 Closed at 16:00. | 1
56 | 2020-12-08 15:59 | December | 15:59 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 15:59 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Cloudy | Tree | 43 | Batang 13.8Kv OCB fdr#3 T/R 3x. Not checked yet. | 1
| 2020-12-08 15:59 | December | 15:59 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 16-08-2020 15:21 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Cloudy | Tree | 43 | Checked and found BTGSB-13.8OCB3 T/R 3x R/F: 51@1,2 Counter: 398 - 401. Patrolled the line and found palm oil tree touched line near pole 36-AL-10. Cause : Tree. | 1
57 | 2020-12-08 16:10 | December | 16:10 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 16:10 | 13.8KV NORTH DURI FEEDER #10 | Duri | PGT North | Cloudy | Unidentified | 0 | N.Duri 13.8Kv VCB fdr#10 T/R. Not checked yet. | 1
| 2020-12-08 16:10 | December | 16:10 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 15-08-2020 15:16 | 13.8KV NORTH DURI FEEDER #10 | Duri | PGT North | Cloudy | Unidentified | 0 | Checked And Found NDRSB VCB10 Fdr #8 Ctr 54-54, Patrolled The Line On 15-Aug-2020 And Found Unidentified On Pole - Cause: Unidentified | 1
58 | 2020-12-08 16:15 | December | 16:15 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 16:15 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 16:15 S/D MGT#7, then offline the unit for S/B. | 1
59 | 2020-12-08 16:18 | December | 16:18 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 16:18 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Dumai | PGT North | Rain and Lightning | Tree | - | 16:18 Dumai 4.16Kv VCB #12 fdr #1 T/O 17:00 Checked & found Dumai 4.16Kv VCB #12 fdr #1 T/O Ctr :334-335 R/f 50 @1,@2,@3. Patrolle the line and found fallen tree touching power line at W-96 &W-97. Open LBS W-91 to isolated fallen tree. 17:40 Blocked & closed Dumai feeder #1, then released block. Cause: Tree. (The fallen tree not removed from power line yet). | 1
| 2020-12-08 16:18 | December | 16:18 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 13-08-2020 07:34 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Dumai | PGT North | Rain and Lightning | Tree | - | Checked And Found DMISB-4.16ACB12 Fdr #8 Ctr 334-335, R/F 50 Patrolled The Line On 12-Aug-2020 And Found Kayu Tinggi Bersandar Di Line Antara Pole W-96 Dan W-97 On Phase @1,2,3, Pole W-96 Cause: Tree | 1
60 | 2020-12-08 16:49 | December | 16:49 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 16:49 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 16:49 S/D MGT#4, then offline the unit for S/B. | 1
61 | 2020-12-08 17:30 | December | 17:30 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 17:30 | 13.8KV 3D FEEDER #5 | Minas | PGT South | Rain and Lightning | Unidentified | 0 | 3D OCB feeder #5 T/R 1x Not Checked Yet | 1
| 2020-12-08 17:30 | December | 17:30 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 15-08-2020 16:37 | 13.8KV 3D FEEDER #5 | Minas | PGT South | Rain and Lightning | Unidentified | 0 | Checked And Found 3D OCB Fdr #5 Ctr 119-120, R/F 51 Patrolled The Line On 15-Aug-2020 But Found Nothing Cause: Unidentified | 1
62 | 2020-12-08 17:30 | December | 17:30 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 17:30 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 17:30 S/D MGT#6, then offline the unit for S/B. 17:55 M/O Tie breaker #16 Minas. | 1
63 | 2020-12-08 17:42 | December | 17:42 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 17:42 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Tree | 45 | 3D 13.8Kv OCB fdr #2 T/R 1x. Not checked yet. | 1
| 2020-12-08 17:42 | December | 17:42 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 15-08-2020 16:40 | 13.8KV 3D FEEDER #2 | Minas | PGT South | Rain and Lightning | Tree | 45 | Checked And Found 3DSB OCB2 Fdr #8 Ctr 383-388, R/F 50 Patrolled The Line On 15-Aug-2020 And Found Dahan Sawit Tinggi On Phase @2 Pole 3E-13 Cause: Tree | 1
64 | 2020-12-08 18:00 | December | 18:00 | Afternoon | Tuesday | Weekdays | 8 | 2020 | 2020-12-08 18:00 | MINAS POWER PLANT | Minas | PGT South |  |  | - | 18:00 S/D MGT#5, then offline the unit for S/B. | 1
65 | 2020-08-13 11:09 | August | 11:09 | Morning | Thursday | Weekdays | 13 | 2020 | 2020-08-13 11:09 | 13.8KV 5B FEEDER #1 | Minas | PGT South | Fair | Planned Maintenance | 0 | 11:09 Manually open recloser 5B/06 d/s 5B feeder #1. Demolish at well 5B/53. 13:29 Closed recloser 5B/06 OK, Ctr:114. | 1
66 | 2020-08-13 17:28 | August | 17:28 | Afternoon | Thursday | Weekdays | 13 | 2020 | 2020-08-13 17:28 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Lightning | 0 | Menggala feeder #2 load dropped 6A (175/169A). Menggala GFPC T/R 1x. Not checked yet. | 1
| 2020-08-13 17:28 | August | 17:28 | Afternoon | Thursday | Weekdays | 13 | 2020 | 2020-08-17 17:56 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Lightning | 0 | Checked and found RCL 26/AK/24 T/R 1x, ctr: 265 / 266, R/F: 51N Patrolled the line and found broken pin insulator @1 o/p 29/AK/01 Cause : Lightning | 1
67 | 2020-08-13 22:14 | August | 22:14 | Night | Thursday | Weekdays | 13 | 2020 | 2020-08-13 22:14 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Heavy Rain | Lightning | 43 | BATANG VCB feeder #3 T/R 3x BATANG GFPC T/R 3x Not Checked Yet | 1
| 2020-08-13 22:14 | August | 22:14 | Night | Thursday | Weekdays | 13 | 2020 | 2020-08-17 22:14 | 13.8KV BATANG FEEDER #3 | Bangko-Balam | PGT North | Heavy Rain | Lightning | 43 | Checked and found Batang fdr #3 T/R 3X ctr:401/404 R/F: 51N. And also found Batang GFPC T/R 1X ctr:1049/1050. Patrolled the line and found @1,@2,@3 Broker LA o/p: 40/AZ/11. Cause: Lightning (broke LA). | 1
68 | 2020-08-14 06:12 | August | 6:12 | Morning | Friday | Weekdays | 14 | 2020 | 2020-08-14 06:12 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Animal | 31 | 06:12 Ketigul VCB fdr #2 T/ 1x Ketigul fdr #1 load dropped 50 A (123 / 73 A) Reported animal (monkey) touch the conductor at PGR #31 Not Checked Yet | 1
| 2020-08-14 06:12 | August | 6:12 | Morning | Friday | Weekdays | 14 | 2020 | 2020-08-16 15:24 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Cloudy | Animal | 31 | Checked and found PKTGL/13.8VCB2 T/R 1x R/F: 51@2 Counter: 401/402. Patrolled the line and found animal (monkey) on location Pagar #38. Cause: Animal. | 1
69 | 2020-08-14 07:18 | August | 7:18 | Morning | Friday | Weekdays | 14 | 2020 | 2020-08-14 07:18 | 13.8KV 5B FEEDER #3 | Minas | PGT South | Cloudy | Lightning | 2 | 5B 13.8Kv OCB fdr #3 T/R 1x. Not checked yet. | 1
| 2020-08-14 07:18 | August | 7:18 | Morning | Friday | Weekdays | 14 | 2020 | 2020-08-21 09:57 | 13.8KV 5B FEEDER #3 | Minas | PGT South | Cloudy | Lightning | 2 | Checked and found: 5BSB/13.8OCB3 T/R, Counter : 421 / 422, Relay Flag : 51N Patrol led the line found: Broken Dead end Insulator @1( Finding di input ke summary ORDC) Cause : Lightning | 1
70 | 2020-08-14 07:37 | August | 7:37 | Morning | Friday | Weekdays | 14 | 2020 | 2020-08-14 07:37 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Cloudy | Animal | 0 | 07:37 C.Duri feeder #1 load dropped 54A (145/91A). 09:40 Checked and found Recl. 41/AW/62 T/R 1X ctr:355/356 RF:51@1. Patrolled the line and found Dead monkey o/p 41/AW/63. Cause: Animal. | 1
71 | 2020-08-14 11:43 | August | 11:43 | Morning | Friday | Weekdays | 14 | 2020 | 2020-08-14 11:43 | 44KV MINAS / RUMBAI LINE | Minas | PGT South | Fair | Dead End Insulator | 0 | 11:43 Minas ACB #21 (Line 44 kV Minas to Rumbai) T/R 1x Not Checked Yet | 1
| 2020-08-14 11:43 | August | 11:43 | Morning | Friday | Weekdays | 14 | 2020 | 2020-08-15 11:43 | 44KV MINAS / RUMBAI LINE | Minas | PGT South | Fair | Dead End Insulator | 0 | Checked and found Minas ACB #21 T/R 1X ctr:93/94 R/F:51G. Patrolled the line and found @1, @2 Broken Dead End O/P: MR83. Cause: Dead End (broken). | 1
72 | 2020-08-14 13:18 | August | 13:18 | Afternoon | Friday | Weekdays | 14 | 2020 | 2020-08-14 13:18 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | 107 | South Balam VCB fdr #1 T/R 1x Not Checked Yet | 1
| 2020-08-14 13:18 | August | 13:18 | Afternoon | Friday | Weekdays | 14 | 2020 | 2020-08-17 17:59 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Cloudy | Unidentified | 107 | Checked and found So. BLM VCB fdr #1 T/R 1x, ctr: 420 / 421, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
73 | 2020-08-15 17:09 | August | 17:09 | Afternoon | Saturday | Weekends | 15 | 2020 | 2020-08-15 17:09 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Cloudy and Lightning | Unidentified | 80 | Petani 13.8Kv OCB fdr #1 T/R 1x. Not checked yet. | 1
| 2020-08-15 17:09 | August | 17:09 | Afternoon | Saturday | Weekends | 15 | 2020 | 2020-08-17 16:54 | 13.8KV PETANI FEEDER #1 | Bekasap | PGT North | Cloudy and Lightning | Unidentified | 80 | Checked and found PTN VCB fdr #1 T/R 1x, ctr: 163 / 164, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
74 | 2020-08-15 17:09 | August | 17:09 | Afternoon | Saturday | Weekends | 15 | 2020 | 2020-08-15 17:09 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Cloudy and Lightning | Lightning | 23 | Petani 13.8Kv OCB fdr #2 T/O (On block RIG APS #3516) Not checked yet. | 1
| 2020-08-15 17:09 | August | 17:09 | Afternoon | Saturday | Weekends | 15 | 2020 | 2020-08-17 16:54 | 13.8KV PETANI FEEDER #2 | Bekasap | PGT North | Cloudy and Lightning | Lightning | 23 | Checked and found PTN VCB fdr #2 T/O (on block for RIG at PTN #55 / Normal) Counter: 332 / 333, R/F: 51N and 50P @1 Patrolled the line and found broken LA @1 o/p 33/AY/06 Cause : Lightning | 1
75 | 2020-08-16 12:21 | August | 12:21 | Afternoon | Sunday | Weekends | 16 | 2020 | 2020-08-16 12:21 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Fair | Lightning | 33 | Pematang 13.8KV OCB fdr #1 T/R 1X. Not checked yet. | 1
| 2020-08-16 12:21 | August | 12:21 | Afternoon | Sunday | Weekends | 16 | 2020 | 2020-08-17 16:51 | 13.8KV PEMATANG FEEDER #1 | Bekasap | PGT North | Fair | Lightning | 33 | Checked and found PMT OCB fdr #1 T/R 1x, ctr: 198 / 199, R/F: 51N Patrolled the line and found flash over LA @1 o/p 35/BC/18D Cause : Lightning | 1
76 | 2020-08-17 04:37 | August | 4:37 | Morning | Monday | Weekdays | 17 | 2020 | 2020-08-17 04:37 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Fair | Tree | 32 | 04:37 4B VCB feeder #1 T/R 1x 4B feeder #2 load dropped 31 A (44 / 13 A) Not Checked Yet | 1
| 2020-08-17 04:37 | August | 4:37 | Morning | Monday | Weekdays | 17 | 2020 | 2020-08-21 10:07 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Fair | Tree | 32 | Checked and found: 4BSB/13.8OCB1 T/LO, Counter : 392 / 401, Relay Flag : 51N. Patrolled the line found : Not Found Operated Device : 5442/R.4B101 T/R Counter : 669 / 674 Relay Flag : NONE Finding Patrol : Dahan Sawit menyentuh Power Line Cause : Tree | 1
77 | 2020-08-17 07:55 | August | 7:55 | Morning | Monday | Weekdays | 17 | 2020 | 2020-08-17 07:55 | 13.8KV SINTONG FEEDER #1 | Bangko-Balam | PGT North | Fair | Animal | 44 | Sintong 13.8KV VCB fdr #1 T/R 1X. Not checked yet. | 1
78 | 2020-08-17 14:58 | August | 14:58 | Afternoon | Monday | Weekdays | 17 | 2020 | 2020-08-17 14:58 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Petko | PGT South | Fair | Emergency | 0 | 14:58 Manuall Open CKBS fdr #1 due to Water Injection Leak. Isolated Water Injection leakage. 15:40 Closed CKBS fdr #1. Cause: Emergency. | 1
79 | 2020-08-17 17:45 | August | 17:45 | Afternoon | Monday | Weekdays | 17 | 2020 | 2020-08-17 17:45 | 4.16KV SO RUMBAI FEEDER #3 | Rumbai | PGT South | Rain and Lightning | Lightning | 0 | 17:45 S. Rumbai 4160V fdr #3 T/R 1X. 18:04 S. Rumbai fdr #3 T/SO. | 1
| 2020-08-17 17:45 | August | 17:45 | Afternoon | Monday | Weekdays | 17 | 2020 | 2020-08-21 10:11 | 4.16KV SO RUMBAI FEEDER #3 | Rumbai | PGT South | Rain and Lightning | Lightning | 0 | Checked and found: 5443/4.16RCL3 T/R, Counter : 137 / 141, Relay Flag : NONE Patrolled the line found : Broken Pin Insulator @1 (Finding diinput ke summary ORDC untuk diplanningkan) Cause : Lightning | 1
80 | 2020-08-17 18:36 | August | 18:36 | Afternoon | Monday | Weekdays | 17 | 2020 | 2020-08-17 18:36 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Rain | Unidentified | 157 | 18:36 4B 13.8KV VCB fdr #1 T/LO 4B fdr #2 loads dropped 27A (39/12A). 23:53 Checked and found 4B VCB fdr #1 T/LO (operate 9x) Counter: 392 / 401, R/F: 51N, 51P @1, 2, 3, 50P @1, 2, 3 01:15 Finish to patrolled the power line but found nothing Other finding RCL 4B/101 Open but the control has down (suspect low batt) 01:24 Block and manual close VCB 4B fdr #1 but trip again (T/O) 4B fdr #2 dropped again 30 A (44 / 14 A) 01:38 Checked relay for 4B fdr #1 and found R/F: 50P @2, 3, counter: 401 / 402 Re/patrolled the power line but found nothing 02:19 Manual close 4B VCB fdr #1 (still on block), OK then release the block. 02:37 Block and Manual close RCL 4B/101, OK then release the block Recloser counter: 669 / 673 Prod Loss: 8/17 (18:36 / 00:00) ///// 170 Bbls / 21 Wells 8/18 (00:00 / 02:19) ///// Cause: Unidentified | 1
| 2020-08-17 18:36 | August | 18:36 | Afternoon | Monday | Weekdays | 17 | 2020 | 2020-08-18 08:10 | 13.8KV 4B FEEDER #1 | Minas | PGT South | Rain | Unidentified | 157 | Checked and found: 4BSB/13.8OCB1 T/LO, Counter : 392 / 401, Relay Flag : 51 Patrolled the line found : Not Found Cause : Unidentified | 1
81 | 2020-08-18 06:22 | August | 6:22 | Morning | Tuesday | Weekdays | 18 | 2020 | 2020-08-18 06:22 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Drizzle | Unidentified | 15 | 8C VCB fdr #4 T/R 1x Not Checked Yet | 1
| 2020-08-18 06:22 | August | 6:22 | Morning | Tuesday | Weekdays | 18 | 2020 | 2020-08-21 10:18 | 13.8KV 8C FEEDER #4 | Minas | PGT South | Drizzle | Unidentified | 15 | Checked and found: 8CSB/13.8VCB4 T/R, Counter : 636 / 637, Relay Flag : 51N. Patrol led the line found: Not Found Cause : Unidentified | 1
82 | 2020-08-18 07:00 | August | 7:00 | Morning | Tuesday | Weekdays | 18 | 2020 | 2020-08-18 07:00 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Fair | Unidentified | 65 | MGL VCB fdr #2 T/R 1x Not Checked Yet | 1
83 | 2020-08-18 07:27 | August | 7:27 | Morning | Tuesday | Weekdays | 18 | 2020 | 2020-08-18 07:27 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Animal | 359 | 07:27 Sintong fdr #2 load dropped 155A (232/77A). 07:48 It was reported no power at Benar GS. 08:30 Checked and found Recl. 28/AF/02 T/LO ctr:1558/1562. Patrolled the line but found nothing. 10:10 Blocked and closed Recl. 28/AF/02, but tripped again. Open Recl. 29/AY/16. Open Recl. 29/Z/13A. 11:26 Blocked and closed Recl. 28/AF/02, OK 11:30 Closed Recl. 29/Z/13A, but Recl. 28/AF/02 tripped again. Then Open Recl. 29/Z/13A. 11:32 Blocked and closed Recl. 28/AF/02, OK 11:36 Closed Recl. 29/AY/16, OK. Patrolled the line and found Dead Weasel O/P Denting /07 then removed it. 13:10 Blocked and closed Recloser 29/Z13A, k then released block. Cause: Animal (Weasel). | 1
84 | 2020-08-18 14:52 | August | 14:52 | Afternoon | Tuesday | Weekdays | 18 | 2020 | 2020-08-18 14:52 | 13.8KV NORTH DURI FEEDER #2 | Duri | PGT North | Fair | Unidentified | 479 | 14:52 North Duri feeder #2 dropped 163 A (213 / 50 A) 16:10 Checked and found RCL NC/04 T/O (block position for PT WKS c/u canals) Patrolled the power line but found nothing 16:53 Blocked and manual close RCL NC/04, OK. release the block Production Loss: => Area 10 NC & SC, well Off = 240 Wells, Oil loss = 200.1 Bbls => Area 13 SX well off = 100 Wells, oil loss = 286.9 Bbls => Total 340 Wells / 487 Bbls Cause: Unidentified | 1
85 | 2020-08-19 10:00 | August | 10:00 | Morning | Wednesday | Weekdays | 19 | 2020 | 2020-08-19 10:00 | CENTRAL DURI POWER PLANT | Duri | PGT North |  |  | - | 10:00 S/U CGT#4, them on line the unit at 10:23. 10:19 Opened Tie Breaker ACB#39. | 1
86 | 2020-08-19 13:28 | August | 13:28 | Afternoon | Wednesday | Weekdays | 19 | 2020 | 2020-08-19 13:28 | 13.8KV DURI FIELD FEEDER #4 | Duri | PGT North | Rain and Lightning | Capasitor Bank | 0 | 13:28 D.Field SW Gear 13.8KV VCB #51 T/R 2X. 15:41 Checked and found: D.Field fdr#4 T/R 3x Ctr:583/586 R/F:51 Patrolled the line found: Capasitor bank terbakar Cause : Capasitor Bank | 1
87 | 2020-08-19 13:48 | August | 13:48 | Afternoon | Wednesday | Weekdays | 19 | 2020 | 2020-08-19 13:48 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Rain and Lightning | Pin Insulator | 0 | C.Duri 13.8 KV ACB #13 ( CD F3 ) T/R 1X Ctr:231/232. Not checked yet. | 1
| 2020-08-19 13:48 | August | 13:48 | Afternoon | Wednesday | Weekdays | 19 | 2020 | 2020-08-21 08:38 | 13.8KV CENTRAL DURI FEEDER #3 | Duri | PGT North | Rain and Lightning | Pin Insulator | 0 | Checked and found: CDRSG/13.8ACB13 T/R, Counter : 231 / 232, Relay Flag : 51G. Patrolled the line found : Relay Glag 51 G temuan hasil patrol ditemukan pin broken bagian bawah di phase 1di tiang 1 TL 16 Phase : 1 Cause : Pin Insulator | 1
88 | 2020-08-19 14:33 | August | 14:33 | Afternoon | Wednesday | Weekdays | 19 | 2020 | 2020-08-19 14:33 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Pin Insulator | 10 | Rokan 13.8KV VCB #2 T/R 1X Not checked yet. | 1
| 2020-08-19 14:33 | August | 14:33 | Afternoon | Wednesday | Weekdays | 19 | 2020 | 2020-08-21 08:47 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Pin Insulator | 10 | Checked and found: RKNSB/13.8VCB2 T/R, Counter : 1344 / 1345, Relay Flag : 51 Patrolled the line found : Relay flag phase 1,2 dan 3 Broken pin insulator di Pole 29 AV 09, 29 AV 65, 28 AV 02 Cause : Pin Insulator | 1
89 | 2020-08-20 06:45 | August | 6:45 | Morning | Thursday | Weekdays | 20 | 2020 | 2020-08-20 06:45 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Fair | Unidentified | 127 | 04:45 Nella Fdr#1 Load drop 82A ( 227 / 145A ) 08:00 Checked and Found Recl 22 V 01 T/So ( Block position for Rig HPS #09 ) Patrolled the line but found nothing 08:41 Blocked and closed Recl 22 V 01, Ctr 6 / 7 Cause : Unidentified. | 1
90 | 2020-08-20 08:59 | August | 8:59 | Morning | Thursday | Weekdays | 20 | 2020 | 2020-08-20 08:59 | 4.16KV SO RUMBAI FEEDER #3 | Rumbai | PGT South | Fair | Lightning | 0 | So Rumbai Feeder # 3 T/R 1 X Not Checked yet. | 1
| 2020-08-20 08:59 | August | 8:59 | Morning | Thursday | Weekdays | 20 | 2020 | 2020-08-26 14:16 | 4.16KV SO RUMBAI FEEDER #3 | Rumbai | PGT South | Fair | Lightning | 0 | Checked and found RCL RBI fdr #3 T/R 1x, ctr: 141 / 142, R/F: 51N Patrolled the line and foundflash over dead end @1 o/p 3RF/8 Cause : Lightning | 1
91 | 2020-08-21 06:56 | August | 6:56 | Morning | Friday | Weekdays | 21 | 2020 | 2020-08-21 06:56 | 13.8KV DURI COMMUNITY FEEDER #5 | Duri | PGT North | Fair | Others | 0 | Duri Comm 13.8Kv ACB #33 fdr #5 T/R Not checked yet. | 1
| 2020-08-21 06:56 | August | 6:56 | Morning | Friday | Weekdays | 21 | 2020 | 2020-08-23 08:14 | 13.8KV DURI COMMUNITY FEEDER #5 | Duri | PGT North | Fair | Others | 0 | Checked and found: DCSG/13.8ACB33 T/R, Counter : 124 / 125, Relay Flag : 51. Patrol led the line found: relay Flag 51 N and 51 @B temuan bushing LBS di tiang 1 KT 41 di dempo bushingnya kondisinya flash Cause : Others | 1
92 | 2020-08-21 09:34 | August | 9:34 | Morning | Friday | Weekdays | 21 | 2020 | 2020-08-21 09:34 | 13.8KV 8C FEEDER #3 | Minas | PGT South | Fair | Planned Maintenance | 31 | 09:34 Manually open LBS 8C/57 D/S 8C/ F3 Cut Jumper o/p 8C/14 to install Safety Net ( Project Tol ) 10:00 Closed LBS. 15:30 Open LBS to install jumper o/p 8C/14 16:34 Closed LBS. Cause : Construction job. | 1
93 | 2020-08-22 06:49 | August | 6:49 | Morning | Saturday | Weekends | 22 | 2020 | 2020-08-22 06:49 | 13.8KV 3D FEEDER #4 | Minas | PGT South | Cloudy | Unidentified | 66 | 3D 13.8KV VCB fdr #4 T/LO. Ctr:112/215 R/F 50/51 @2 , @3 07:15 Patrol the line bud found nothing. 08:55 Blocked and closed 3D feeder #4 then released the block. Cause: unidentified. | 1
94 | 2020-08-22 12:44 | August | 12:44 | Afternoon | Saturday | Weekends | 22 | 2020 | 2020-08-22 12:44 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Fair | Planned Maintenance | - | 12:44 Manual open Recl 29/Z/13A D/S Sintong Fdr# 2 Replace @1@3 broken dead end insulator o/p 32/Z/02. 13:22 Blocked and Closed Recl 29/Z/13A,then release block. Cause: Planned Maintenance. | 1
95 | 2020-08-22 17:00 | August | 17:00 | Afternoon | Saturday | Weekends | 22 | 2020 | 2020-08-22 17:00 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Rain and Lightning | Unidentified | 35 | Minas feeder #3 T/R 1X Ctr:172/173 R/F:51N Not patrolled yet. | 1
| 2020-08-22 17:00 | August | 17:00 | Afternoon | Saturday | Weekends | 22 | 2020 | 2020-08-26 14:11 | 13.8KV MINAS FEEDER #3 | Minas | PGT South | Rain and Lightning | Unidentified | 35 | Checked and found MNS ACB fdr #3 T/R 1x, ctr: 172 / 173, R/F: 51N Patrolled the line and found high palm trees near pole 7D/68 Cause : Unidentified | 1
96 | 2020-08-22 17:01 | August | 17:01 | Afternoon | Saturday | Weekends | 22 | 2020 | 2020-08-22 17:01 | ROKAN SUBSTATION | Bangko-Balam | PGT North | Rain and Lightning | Animal | 360 | 17:01 115 Kv C/S Rokan T/O. Pinang feeder #1 load dropped 36A (101/65A) S.Balam feeder #1 load dropped 69A (177/108A) S.Balam feeder #3 load dropped 125A (125/0A) S.Balam feeder #4 load dropped 113A (214/101A) Nella feeder #1 load dropped 41A (227/186A) Bangko feeder #1 load dropped 128A (160/32A) Bangko feeder #2 load dropped 138A (248/110A) Bangko feeder #4 load dropped 108A (193/85A) Menggala feeder #1 load dropped 127A (187/60A) Menggala feeder #2 load dropped 148A (182/34A) Sintong feeder #1 load dropped 39A (99/60A) Sintong feeder #2 load dropped 160A (240/80A) Bekasap feeder #5 load dropped 79A (225/146A) Pematang feeder #1 load dropped 151A (204/53A) Pematang feeder #2 load dropped 19A (110/201A) Rangau feeder #2 load dropped 38A (146/108A) Ketigul feeder #1 load dropped 31A (120/89A) Ketigul feeder #2 load dropped 34A (88/54A). 17:57 Checked & found 115 Kv Rokan C/S T/O Ctr:244/245 R/F:51@1@2@3. @1@2@3 Broken 13.8Kv LA at Structure Rokan SS. Dead Monkey on Structure Rokan SS. 18:10 Manually Open Rokan fdr#2,/////>Closed at 20:07. Manually Open Rokan fdr#3,/////>Closed at 20:09. Manually Open Rokan fdr#4,,/////>Closed at 20:08. 19:20 Open Isolation switch of Rokan C/S. 19:40 Isolated broken LA at Structure Rokan SS. 19:43 Closed Isolation switch of Rokan C/S. 19:44 Closed 115KV Rokan C/S, failed. Open again Isolation switch of Rokan C/S. Fucntion test 115KV Rokan C/S, OK. 20:01 Closed Isolation switch of Rokan C/S. 20:02 Closed 115KV Rokan C/S, Ok. Cause : Animals (Monkey). | 1
97 | 2020-08-23 08:09 | August | 8:09 | Morning | Sunday | Weekends | 23 | 2020 | 2020-08-23 08:09 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | - | N.Duri 13.8Kv VCB fdr #1 T/R 1x. Not checked yet. | 1
| 2020-08-23 08:09 | August | 8:09 | Morning | Sunday | Weekends | 23 | 2020 | 2020-08-27 10:22 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Fair | Lightning Arrester | - | Checked and found ND VCB fdr #1 T/R 1x, ctr: 346 / 347, R/F: 51N Patrolled the line and found broken LA @1 o/p 12/F11/22 Cause : Lightning Arrester | 1
98 | 2020-08-23 16:02 | August | 16:02 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 16:02 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Rain and Lightning | Unidentified | 32 | Bekasap 13.8Kv ACB fdr #6 T/R 1x. Not checked yet. | 1
| 2020-08-23 16:02 | August | 16:02 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-26 16:40 | 13.8KV BEKASAP FEEDER #6 | Bekasap | PGT North | Rain and Lightning | Unidentified | 32 | Checked and found BKSM VCB fdr #6 T/R 1x, ctr: 410 / 411, R/F: 51P Patrolled the line but found nothing Cause : Unidentified | 1
99 | 2020-08-23 16:18 | August | 16:18 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 16:18 | 13.8KV BEKASAP FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Dead End Insulator | 71 | Bekasap feeder #6 load dropped 16A (254/89A). Not checked yet. | 1
| 2020-08-23 16:18 | August | 16:18 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-26 17:48 | 13.8KV BEKASAP FEEDER #2 | Bekasap | PGT North | Rain and Lightning | Dead End Insulator | 71 | Checked and found RCL 37/BD/12 T/R 3x, ctr: 1470/1473, R/F: 51N Patrolled the line and found: / broken dead end @1 o/p NN near BKS #09 / flash oven pin insulator @1 @3 o/p 37/BD/36 Cause : Dead End Insulator | 1
100 | 2020-08-23 16:23 | August | 16:23 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 16:23 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 480 | 16:23 Menggala 13.8Kv ACB fdr #2 T/LO. Manggala GFPC T/R 1X 20:04 Patroll the line and found broken p/ins at @1 o/p 28AJ07 20:05 Open LBS 28 AL 21 for replace broken p/ins 20:06 Block and closed Manggala Fdr #2,then release block 21:16 Block Manggal Fdr#2 21:17 Closed LBS 28 AL 21 and release block Cause : Broken P/Ins. | 1
101 | 2020-08-23 16:23 | August | 16:23 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 16:23 | 13.8KV MENGGALA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | Menggala feeder #1 load dropped 121A (187/66A). Not checked yet. | 1
102 | 2020-08-23 16:29 | August | 16:29 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 16:29 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | Sintong feeder #2 load dropped 206A (240/34A). Not checked yet. | 1
103 | 2020-08-23 16:49 | August | 16:49 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 16:49 | 44KV PEMATANG MAIN / RANGAU LINE | Bekasap | PGT North | Rain and Lightning | Lightning | 193 | 16:49 Pematang Main 44Kv line to Rangau OCB #2 T/R. Petani fdr #1 load dropped 175A (243/68A). Petani fdr #2 load dropped 58A (68/10A). Pematang fdr #1 load dropped 179A (213/34A). Pematang fdr #2 load dropped 105A (112/17A). 17:05 It was reported No power at WIP Pematang GS Manually open Pematang VCB fdr#2, then Closed at 18:25. 18:02 Manually open Rangau VCB fdr#2, then closed at 18:53. ( Maintained Tank Level ) 18:10 Checked & found Recl./A for Tx/A T/O Ctr:45/46, then closed at 18:12. Recl./B for Tx/B T/O Ctr:48/49, then closed at 18:12. Cause: Lightning | 1
| 2020-08-23 16:49 | August | 16:49 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-27 10:16 | 44KV PEMATANG MAIN / RANGAU LINE | Bekasap | PGT North | Rain and Lightning | Lightning | 193 | Checked and found PMT Main GCB #2 T/R 1x, ctr: 55106 / 66107, R/F: 51P Patrolled the line and found broken suspension insulator @2 o/p RGU #53 Cause : Lightning | 1
104 | 2020-08-23 16:52 | August | 16:52 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 16:52 | 13.8KV NELLA FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 113 | 16:52 Nella 13.8Kv OCB fdr#2 T/O. 18:28 Patrolled the line but found nothing. 18:38 Blocked & closed Nella Ok, the released the block. Cause: Lighting. | 1
105 | 2020-08-23 16:52 | August | 16:52 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 16:52 | 13.8KV NELLA FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | Nella feeder #1 load dropped 143A (227/84A). Not checked yet. | 1
106 | 2020-08-23 17:04 | August | 17:04 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 17:04 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Rain and Lightning | Unidentified | - | Duri comm 13.8Kv ACB #26 fdr #3 T/R 1x. Not checked yet. | 1
| 2020-08-23 17:04 | August | 17:04 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-25 22:21 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Rain and Lightning | Unidentified | - | Checked and found DCM ACB/26 fdr #3 T/R 1x, ctr: 107 (not change), R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
107 | 2020-08-23 17:27 | August | 17:27 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 17:27 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Unidentified | - | C.Duri feeder #1 load dropped 48A (148/100A). Not checked yet. | 1
| 2020-08-23 17:27 | August | 17:27 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-27 10:22 | 13.8KV CENTRAL DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Unidentified | - | Checked and found RCL 38/AS/09, ctr: 444 / 445, R/F: None Patrolled the line but found nothing Cause : Unidentified | 1
108 | 2020-08-23 17:51 | August | 17:51 | Afternoon | Sunday | Weekends | 23 | 2020 | 2020-08-23 17:51 | 13.8KV S. BALAM FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | - | S.Balam feeder #1 load dropped 100A (177/77A). Not checked yet. | 1
109 | 2020-08-24 02:13 | August | 2:13 | Night | Monday | Weekdays | 24 | 2020 | 2020-08-24 02:13 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Lightning Arrester | 0 | North Duri Feeder #1 T/R 1X Not checked yet. | 1
| 2020-08-24 02:13 | August | 2:13 | Night | Monday | Weekdays | 24 | 2020 | 2020-08-27 10:22 | 13.8KV NORTH DURI FEEDER #1 | Duri | PGT North | Rain and Lightning | Lightning Arrester | 0 | Checked and found ND VCB fdr #1 T/R 1x, ctr: 347 / 348, R/F 51N Patrolled the line and found LA broken @1 o/p 12/F11/22 Cause : Lightning Arrester | 1
110 | 2020-08-24 07:38 | August | 7:38 | Morning | Monday | Weekdays | 24 | 2020 | 2020-08-24 07:38 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Lightning Arrester | 0 | 07:38 Ketigul 13.8Kv VCB fdr #2 T/R 1x. 08:23 Ketigul 13.8Kv VCB fdr #2 T/R 1x. 17;30 Ketigul 13.8Kv VCB fdr #2 T/R 1x. Not checked yet. | 1
| 2020-08-24 07:38 | August | 7:38 | Morning | Monday | Weekdays | 24 | 2020 | 2020-08-26 16:38 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Lightning Arrester | 0 | Checked and found KTGL VCB fdr #2 T/R 3x, ctr: 402 / 405, R/F: 51N Patrolled the line and found broken LA @ LA @1 o/p 29/AL/07 | 1
111 | 2020-08-24 21:18 | August | 21:18 | Night | Monday | Weekdays | 24 | 2020 | 2020-08-24 21:18 | 13.8KV S. BALAM FEEDER #4 | Bangko-Balam | PGT North | Fair | Emergency | 0 | 21:18 It was reported Hot Spot o/p So. East Balam #02. 22:39 Open Recloser 19/AA/07. Open Fuse of TX at well So. East Balam #02. 22:45 Closed Recloser 19/AA/07. Cause: Emergency. | 1
112 | 2020-08-25 09:03 | August | 9:03 | Morning | Tuesday | Weekdays | 25 | 2020 | 2020-08-25 09:03 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Lightning Arrester | 31 | Ketigul VCB fdr#2 T/R 1x. Not checked yet. | 1
| 2020-08-25 09:03 | August | 9:03 | Morning | Tuesday | Weekdays | 25 | 2020 | 2020-08-26 16:20 | 13.8KV KETIGUL FEEDER#2 | Bangko-Balam | PGT North | Fair | Lightning Arrester | 31 | Checked and found KTGL VCB fdr #2 T/R 1x, ctr: 405 / 406, R/F: 51N Patrolled the line and found broken LA @3 o/p 29/AL/09 | 1
113 | 2020-08-25 13:50 | August | 13:50 | Afternoon | Tuesday | Weekdays | 25 | 2020 | 2020-08-25 10:21 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Rain and Lightning | Lightning | - | Checked and found: DCSG/13.8ACB26 T/LO, Counter : 107 / 113, Relay Flag : 51 Date Patrol : 25/AUG/2020 Patrol led the line found: Temuan Relay Flag 51phase 1, 51phase 2, 51 phase 3 dan 51N ditemukan pin broken ditiang 2DH 3,Talang 28 dan Broken LA ditiang I F 30 6, counter terakhir 113 samapai restorasi Cause : Lightning | 1
| 2020-08-25 13:50 | August | 13:50 | Afternoon | Tuesday | Weekdays | 25 | 2020 | 2020-08-25 13:50 | 13.8KV DURI COMMUNITY FEEDER #3 | Duri | PGT North | Rain and Lightning | Lightning | - | 13:50 Duri Community ACB fdr#3 T/LO. 14:21 Checked & found Duri Comm ACB fdr#3 T/O Ctr:107/110 R/F:51@1@2@3. Patrolled the line but found nothing. 16:00 Open LBS IF/27, then closed at 18:13. 16:20 Blocked & closed Duri Comm ACB fdr#3, but failed. Patrolled the line & found @1 Broken Pin Insulator o/p 2DH3. @1 Broken Pin Insulator near Talang#26. Opened LBS SN/01, then closed at 16:50. 16:27 Blocked & closed Duri Comm ACB fdr#3, ok. 16:34 Opened Recl. 4160V Mini Subst Sinabung. Closed 4160V LBS I/48 (Feed from fdr#2). 16:40 Opened LBS SD/01 at Dempo, 18:13 Closed LBS IF27, but Duri Comm fdr#3 T/O. open LBS Open/closed Fuse Transformer at SMP Cendana 18:34 Closed LBS IF 27 but DCM Fdr#3 T/O, open again 18:56 Open 13.8KV Recl mini suabstation ( singgalang ) 19:03 Bloked and Closed DCM Fdr#3 ok. 20:08 Isolated broken jumper L/A o/p IF 30 20:09 Closed LBS IF 27 ok Caused: Broken jumper L/A | 1
114 | 2020-08-25 14:54 | August | 14:54 | Afternoon | Tuesday | Weekdays | 25 | 2020 | 2020-08-25 14:54 | LIBO SUBSTATION | Libo | PGT South | Rain and Lightning | Unidentified | 98 | 14:54 115Kv Libo C/S T/O. 15:15 Checked & found 115Kv Libo C/S T/O Ctr:374/375 R/F:51N. 15:38 Opened Libo VCB fdr#1, then Closed at 15:41. Opened Libo VCB fdr#2, then closed at 15:41. 15:40 Closed 115Kv Libo C/S. Cause: Unidentified. | 1
115 | 2020-08-25 22:32 | August | 22:32 | Night | Tuesday | Weekdays | 25 | 2020 | 2020-08-25 22:32 | NORTH DURI POWER PLANT | Duri | PGT North | Fair | Load Shedding | 262 | 22:32 NDC #3 Trip Off by 86G Freq :59:29 Load shedding Level 4. Open 3D fdr #2//////> Closed at 00:35 Open 3D fdr #3//////> Closed at 00:30 Open 3D fdr #5//////> Closed at 22:50. Open 3D fdr #6//////> Closed at 22:50. Open 4D fdr #2//////> Closed at 00:28 Open 4B fdr #1//////> Closed at 00:10. Open 4B fdr #4//////> Closed at 22:47. Open 4B fdr #5//////> Closed at 22:49. Open 4B fdr #6//////> Closed at 00:15. Open 5B fdr #1//////> Closed at 00:08. Open 5B fdr #4//////> Closed at 00:17. Open 5B fdr #5//////> Closed at 00:16. Open 5B fdr #7//////> Closed at 00:34 Open 5B fdr #8//////> Closed at 00:25. Open 8C fdr #1//////> Closed at 23:42 Open 8D fdr #1//////> Closed at 00:01 Open 8D fdr #3//////> Closed at 23:44. Open 8D fdr #10/////> Closed at 00:02 Open Suram fdr #1//> Closed at 23:16. Manually open 5B fdr #2/////> Closed at 00:34. 23:30 S/U NDC #3 then online the unit at 00:01. 00:04 Closed 230KV ND GCB #33. Production lost: Minas Area 1 and 2 :331bbls / 87 Wells. | 1
116 | 2020-08-25 23:30 | August | 23:30 | Night | Tuesday | Weekdays | 25 | 2020 | 2020-08-25 23:30 | NORTH DURI POWER PLANT | Duri | PGT North |  |  | - | 23:30 S/U NDC #3 then online the unit at 24:01. | 1
117 | 2020-08-26 10:00 | August | 10:00 | Morning | Wednesday | Weekdays | 26 | 2020 | 2020-08-26 10:00 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 94 | 10:00 Manual Open RCL 46/BP/12 (PGT fdr #2) closed at 16:21 MTCE team to repair broken cross arm o/p 49/BM/01 and 48/BN/22 MTCE team to replace 29 pin insulators. 16:21 Blocked & closed Recl. 46/BP/12. then release the block. Planned Maintenance | 1
118 | 2020-08-27 09:40 | August | 9:40 | Morning | Thursday | Weekdays | 27 | 2020 | 2020-08-27 09:40 | 13.8KV 6D FEEDER #2 | Minas | PGT South | Fair | Planned Maintenance | 105 | 09:40 Manual Open RCL 6D/78A, closed at … MTCE team to cutting jumper on pole 6B/79A Planned Maintenance | 1
119 | 2020-08-27 10:07 | August | 10:07 | Morning | Thursday | Weekdays | 27 | 2020 | 2020-08-27 10:07 | 13.8KV ROKAN FEEDER #2 | Bangko-Balam | PGT North | Fair | Planned Maintenance | 52 | 10:07 Manual Open VCB RKN fdr #2 MTCE team jobs to: / replace broken insulator at Kopar Field (4 spots) / replace broken LA (1 spot) / repair cross arm o/p 30/AV/15 Planned Maintenance | 1
120 | 2020-08-28 10:21 | August | 10:21 | Morning | Friday | Weekdays | 28 | 2020 | 2020-08-28 10:21 | 13.8KV 6DN FEEDER #6 | Minas | PGT South | Fair | Planned Maintenance | 4 | 10:21 Manual open RCL 6E/64 d/s 6DN fdr #6 MTCE team to o/c jumper o/p 6E/23 to support ARO at loc 6E/24 Planned Maintenance | 1
121 | 2020-08-29 09:56 | August | 9:56 | Morning | Saturday | Weekends | 29 | 2020 | 2020-08-29 09:56 | 13.8KV PUNGUT FEEDER #2 | Bekasap | PGT North | Fair | Planned Maintenance | 24 | 09:56 Manual Open LBS 45/B5/05, closed at 14:05 MTCE team to c/o broken cross arm at 43/BY/03 Planned Maintenance | 1
122 | 2020-08-29 15:59 | August | 15:59 | Afternoon | Saturday | Weekends | 29 | 2020 | 2020-08-29 15:59 | 13.8KV PINANG FEEDER #1 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 26 | 15:59 Pinang VCB feeder #1 T/R 1x Not Checked Yet | 1
123 | 2020-08-29 17:18 | August | 17:18 | Afternoon | Saturday | Weekends | 29 | 2020 | 2020-08-29 17:18 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Cloudy | Dead End Insulator | 4 | 17:18 Ketigul VCB fdr #1 T/R 1x Ketigul feeder #3 load dropped 12 A (26 / 14 A) 17:31 Ketigul VCB fdr #1 T/R 1x again Ketigul feeder #2 load dropped 14 A (83 / 69A) Not Checked Yet | 1
| 2020-08-29 17:18 | August | 17:18 | Afternoon | Saturday | Weekends | 29 | 2020 | 2020-08-30 16:23 | 13.8KV KETIGUL FEEDER#1 | Bangko-Balam | PGT North | Cloudy | Dead End Insulator | 4 | Checked and found KTGL VCB fdr #1 T/R 2x, ct: 241 / 243, R/F: 51P @1 @2 @3 Patrolled the line and found broken dead end @1 @2 o/p 20/AJ/13 Cause : Dead End Insulator | 1
124 | 2020-08-29 17:58 | August | 17:58 | Afternoon | Saturday | Weekends | 29 | 2020 | 2020-08-29 17:58 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Rain | Unidentified | - | 17:58 Batang GFPC T/R 1x No feeder load dropped Not Checked Yet | 1
| 2020-08-29 17:58 | August | 17:58 | Afternoon | Saturday | Weekends | 29 | 2020 | 2020-08-30 16:30 | 13.8KV BATANG GFPC | Bangko-Balam | PGT North | Rain | Unidentified | - | Checked and found GFPC BTG T/R 1x, ctr: 1051 / 1052, R/F: 51N Patrolled the line but found nothing Cause : Unidentified | 1
125 | 2020-08-30 01:27 | August | 1:27 | Night | Sunday | Weekends | 30 | 2020 | 2020-08-30 01:27 | NORTH DURI POWER PLANT | Duri | PGT North | Fair | Under investigation | 1030 | 01:27 NDC#3 Trip by alarm Generator Lock Out Trip. Load shedding level#3, Freq. 59.30. 3D fdr#2 T/O, then Closed at 04:15. 3D fdr#3 T/O, then Closed at 04:21. 3D fdr#5 T/O, then Closed at 01:33. 3D fdr#6 T/O, then Closed at 01:33. 4B fdr#1 T/O, then Closed at 04:23. 4B fdr#4 T/O, then Closed at 01:30. 4B fdr#5 T/O, then Closed at 01:30. 4B fdr#6 T/O, then Closed at 04:19. 4D fdr#2 T/O, then Closed at 03:45. 4D fdr#3 T/O, then Closed at 03:50. 5B fdr#1 T/O, then Closed at 03:39. 5B fdr#3 T/O, then Closed at 03:42. 5B fdr#4 T/O, then Closed at 04:26. 5B fdr#5 T/O, then Closed at 04:27. 5B fdr#7 T/O, then Closed at 04:28. 5B fdr#8 T/O, then Closed at 02:10. 8C fdr#1 T/O, then Closed at 04:18. 8D fdr#1 T/O, then Closed at 04:24. 8D fdr#3 T/O, then Closed at 04:25. 8D fdr#10 T/O, then Closed at 01:58. Suram fdr#1 T/O, then Closed at 01:51. 01:45 Manually Open 5B fdr#2, then Closed at02:23. (Req. GS#4 for maniained Tank Level). 02:10 S/U NDC#3, then on line the unit at 04:10. 04:13 Closed 230Kv GCB#33. Cause: Under Investigation. Prod. Loss: GS#1 : 486 Bbls, 59 wells. GS#2 : 79 Bbls, 22 wells. GS#3 : 0 GS#4 : 169 Bbls, 49 wells. GS#5 : 233 Bbls, 71 wells. GS#6 : 234 Bbls, 69 wells. Total Prod> Loss : 1201 Bbls, 270 wells. | 1
126 | 2020-08-30 17:16 | August | 17:16 | Afternoon | Sunday | Weekends | 30 | 2020 | 2020-08-30 17:16 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Petko | PGT South | Fair | Emergency | 0 | 17:16 Manual Open VCB CKBS fdr #6 Emergency request from KBGS (INDRA) related to illegal tapping at KM 13250 Cause: Emergency | 1
| 2020-08-30 17:16 | August | 17:16 | Afternoon | Sunday | Weekends | 30 | 2020 | 2020-08-31 06:17 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Petko | PGT South | Fair | Emergency | 0 | Blocked & closed CKBS fdr#6, then release the block. | 1
127 | 2020-08-30 17:47 | August | 17:47 | Afternoon | Sunday | Weekends | 30 | 2020 | 2020-08-30 17:47 | 13.8KV SINTONG FEEDER #2 | Bangko-Balam | PGT North | Rain and Lightning | Lightning | 37 | 17:47 Sintong fdr #2 load dropped 130 A (233 / 103 A) Not Checked Yet | 1
128 | 2020-08-31 14:20 | August | 14:20 | Afternoon | Monday | Weekdays | 31 | 2020 | 2020-08-31 14:20 | 13.8KV 6DN FEEDER #6 | Minas | PGT South | Fair | Planned Maintenance | 24 | 14:20 Manual Open RCL 6E/64, closed at 16:30 MTCE team to connect jumper at 6E/23 for ARO project at 6E/24 Planned Maintenance | 1
129 | 2020-08-31 15:00 | August | 15:00 | Afternoon | Monday | Weekdays | 31 | 2020 | 31/08/2020 15:00 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 59 | 15:00 MGL VCB fdr #2 T/R 1x MGL GFPC T/R 1x MGL fdr #1 load dropped 28 A (184 / 156 A) Not Checked Yet | 1
| 2020-08-31 15:00 | August | 15:00 | Afternoon | Monday | Weekdays | 31 | 2020 | 2020-03-09 10:27 | 13.8KV MENGGALA FEEDER #2 | Bangko-Balam | PGT North | Cloudy | Unidentified | 59 | Checked and found Menggala VCB fdr #2 T/R 1x, ctr: 582 / 583, R/F: 51N Patrolled the line and found broken dead end insulator @1 near UBI #08 Cause : Unidentified | 1

## Sheet2
4:00
12:00
19:00