## SQL Results
No | TANGGAL | REPATROL | UNIT | WEATHER | CAUSE | LOSS | NVL(TO_CHAR(EVENT_STATUS.REMAR | NVL(TO_CHAR(JDE_NUMBER),'') | OutageCount | OutageHour | OutageTiming | OutageDay | OutageYear | OutageMonth
1 | 2015-01-01 15:43 | 2015-01-01 15:43 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 0 | 15:43 It was reported unbalance voltage for 112.5 Kva Tx o/p #08-L7-30. (C.Duri fdr #1) (4 wells were off). 17:20 Checked & found, @2 b/o 2.1SF fuse for 112.5 Kva Tx o/p #08-L7-30. Replaced the fuse above with the same size & energized the Tx. Couse: Animal. (Monkey) | 3001248 | 1 | 15:43 | Afternoon | Thursday | 2015 | 1
2 | 2015-01-01 18:06 | 2015-01-01 18:06 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Lightning | 30 | Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #1 load dropped 23A (190-173A). Ketigul fdr #3 load dropped 8A (16-8A). Not checked yet. | 3001248 | 1 | 18:06 | Afternoon | Thursday | 2015 | 1
3 | 2015-01-01 18:06 | 2015-03-01 13:06 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Lightning | 30 | Checked & found, Ketigul VCB fdr #2 T/R 1x (Ctr & R/F are not checked yet) (No acces to Ketigul Substation due to flood) Patrolled the line & found, broken @1 L/A o/p #31AN-06. Cause: Lightning. | 3001248 | 1 | 18:06 | Afternoon | Thursday | 2015 | 1
4 | 2015-02-01 06:22 | 2015-02-01 06:22 | NELLA SUBSTATION | Fair | Voltage regulator failure | 4985 | 06:22 115KV Bangko-Nella line load dropped 44A (124-80A). (Nella & Pinang Substation Scada failed at the time) 07:45 Checked & found, 115KV Nella C/S T/O, Ctr: 169-170 R/F: 87T (@1,@3) & 86T. Checked the TX & found: -Winding Temp. : 70-75 C. -Oil level : High. -Nitrogen Press : 4 Psi. -VR LTC position : L16. 07:52 Manual Opened 13.8KV Nella fdr #1 & Nella fdr #2 & Reset Relay 86T & 87T. 07:52 Closed 115KV Nella C/S, but T/O again. Ctr : 170-171 R/F: 87T (@1,@3) & 86T. Switching to transfer part load of Nella fdr #1 to Bangko Temporary fdr #1. 10:55 Open Recl. 22V-01. (Downstream of Nella fdr #1) Closed LBS #23W-01. (Bangko Temp. fdr #1, Load to 261A from 182A) 16:50 Blocked Bangko MSU-2 fdr #2. 16:50 Open LBS #24Y-01. (BKO #04, #291, #267, #274, #216, #273, #133 & #180 were off) (To connect Jumper o/p #24Y-06) 18:00 By passed Nella Voltage Regulator & Opened 2x 600Kvar Cap Bank at Nella Substation. 18:20 Closed 115KV Nella C/S, Ok. 19:15 Closed 2x 600Kvar Capacitor Banks, Ok. (Nella Bus Volatage 13.7KV) 19:18 Closed both isolation switches of 13.8Kv Nella VCB fdr #2. 19:20 Blocked & closed, 13.8Kv Nella VCB fdr #2, but failed. (from DSC) 19:22 Blocked & closed, 13.8Kv Nella VCB fdr #2, ok. (from local). Then released the block. 19:30 Checked load Nella fdr #2 & found, load 82A / Bus Voltage 13.4Kv. 19:35 Closed both isolation switches 13.8Kv Nella VCB fdr #1. 19:37 Blocked & closed, 13.8Kv Nella VCB fdr #1, Ok. Then released the block. 20:40 Closed Recl. 21V-01. 20:42 Closed LBS #24Y-01 (MSU-2 fdr #2), to energize 8 (Eigth) Wells. (After connected Jumper o/p #24Y-06 & Tested the Sequence rotation of Motor Pump, Ok) 20:57 Closed Recl. 22V-06 (Nella fdr #1), to energize some wells. (no Wells off any more) Checked Load Nella fdr #1. (156A & Bus Voltage 12.95Kv) Checked load Nella fdr #2. (86A) Cause: Voltage Regulator failure. | 3001248 | 1 | 6:22 | Morning | Sunday | 2015 | 2
5 | 2015-02-01 06:31 | 2015-02-01 06:31 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | No.Duri VCB fdr #1 T/R 1x. Not checked yet. | 3001248 | 1 | 6:31 | Morning | Sunday | 2015 | 2
6 | 2015-02-01 06:31 | 2015-06-01 08:31 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, No.Duri VCB fdr #1 T/R 1x Ctr: 258-259 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3001248 | 1 | 6:31 | Morning | Sunday | 2015 | 2
7 | 2015-02-01 07:00 | 2015-02-01 07:00 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Secondary Cable | 130 | 07:00 It was reported b/o fuses for Tx o/p #08-M5-03. 09:00 Checked & found, @1,@3 b/o 2.1SF fuses for 112.5Kva Tx o/p #08-M5-03. (Also found, broken scondary jumper of 112.5Kva Tx) 15:50 Replaced broken secondary cable and b/o fuse above with same size & energized the Tx. Cause: Broken Secondary Cable. | 3001248 | 1 | 7:00 | Morning | Sunday | 2015 | 2
8 | 2015-03-01 06:30 | 2015-03-01 06:30 | 13.8KV DURI FIELD FEEDER #4 | Fair | Guy Wire | 4 | 06:30 It was reported b/o fuses for Tx o/p #06-S3-05. 10:08 Checked & found, @1,@3 b/o 2.1SF fuses for 112.5Kva Tx o/p #06-S3-05. (Also found, broken guy wire & touching to secondary Tx cable) Blocked Recl. 06-S3-19, for dismantling guy wire above. Then replaced b/o fuse above with the same size & energized Tx. 11:08 Normalized block of Recl. 06-S3-19. Cause: Guy wire. | 3001248 | 1 | 6:30 | Morning | Sunday | 2015 | 3
9 | 2015-03-01 08:37 | 2015-03-01 08:37 | 13.8KV ROKAN FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3001248 | 1 | 8:37 | Morning | Sunday | 2015 | 3
10 | 2015-03-01 08:37 | 2015-06-01 13:20 | 13.8KV ROKAN FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 959-960. Patrolled the line & found, @1 broken Dead end Insulator o/p #20AV-22. Cause: Lightning. | 3001248 | 1 | 8:37 | Morning | Sunday | 2015 | 3
11 | 2015-03-01 13:00 | 2015-03-01 13:00 | 13.8KV PUNGUT FEEDER #2 | Fair | Animal | 7 | 13:00 It was reported that b/o fuse for Tx at Well Asih # 02. 14:00 Checked & found, @1,@3 b/o 3.5SF fuses for 150KVA Tx at Well Asih # 02. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal (Mice). | 3001248 | 1 | 13:00 | Afternoon | Sunday | 2015 | 3
12 | 2015-03-01 15:13 | 2015-03-01 15:13 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 0 | 15:13 It was reported that b/o fuse for Tx o/p #09-R8-01A. 15:48 Checked & found, @2 b/o 2.1SF fuse for 112.5KVA Tx o/p #09-R8-01A. Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Squirrel) | 3001248 | 1 | 15:13 | Afternoon | Sunday | 2015 | 3
13 | 2015-03-01 16:08 | 2015-03-01 16:08 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Sintong fdr #2 load dropped 7A (175-168A). Sintong GFPC T/R 1x. (Fault alarm on Sintong fdr #2) Not checked yet. | 3001248 | 1 | 16:08 | Afternoon | Sunday | 2015 | 3
14 | 2015-03-01 16:08 | 2015-06-01 13:50 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recl. 29AK-16 (Sintong fdr #2) T/R 1x Ctr: 194-195. Also found, Sintong GFPC T/R 1x Ctr: 706-707. Patrolled the line, but found nothing. Cause: Unidentified. | 3001248 | 1 | 16:08 | Afternoon | Sunday | 2015 | 3
15 | 2015-04-01 11:12 | 2015-04-01 11:12 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Transformer Failure | 0 | It was reported b/o fuse for Tx o/p #01-03-301. Not checked yet. | 3001248 | 1 | 11:12 | Morning | Wednesday | 2015 | 4
16 | 2015-04-01 11:12 | 2015-07-01 08:12 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Transformer Failure | 0 | Checked & found, @1,@3 b/o 2.1SF fuses for 112.5Kva Tx o/p #01-3-31. Tested the Tx & found, Low megger reading. Cause: Tx failure. (Low megger reading) (The Tx is not replaced yet, due to flooding) | 3001248 | 1 | 11:12 | Morning | Wednesday | 2015 | 4
17 | 2015-04-01 11:12 | 2015-01-17 10:10 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Transformer Failure | 0 | Replaced 112.5Kva Tx with the same size & energized the Tx o/p #01-3-03. Cause: Tx failure. | 3001248 | 1 | 11:12 | Morning | Wednesday | 2015 | 4
18 | 2015-05-01 23:59 | 2015-05-01 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system normal Condition. |  | 1 | 23:59 | Night | Friday | 2015 | 5
19 | 2015-06-01 16:21 | 2015-06-01 16:21 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 21 | Libo OCB fdr #2 T/R 1x. Libo fdr #1 load dropped 15A (84-69A). Not checked yet. | 3001248 | 1 | 16:21 | Afternoon | Monday | 2015 | 6
20 | 2015-06-01 16:21 | 2015-08-01 07:21 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 21 | Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 389-390 R/F: 51N. Patrolled the line & found: -@3 Flashed over Pin Insulator o/p #33CD-07. -@1 Flashed over Pin Insulator o/p #33CC-31. Cause: Lightning. | 3001248 | 1 | 16:21 | Afternoon | Monday | 2015 | 6
21 | 2015-06-01 17:35 | 2015-06-01 17:35 | 13.8KV CENTRAL DURI FEEDER #15 | Heavy Rain | Animal | 11 | It was reported b/o fuse for Tx o/p #06-R1-15. Not checked yet. | 3001248 | 1 | 17:35 | Afternoon | Monday | 2015 | 6
22 | 2015-06-01 17:35 | 2015-07-01 14:38 | 13.8KV CENTRAL DURI FEEDER #15 | Heavy Rain | Animal | 11 | 14:38 Checked & found, @3 b/o 2.1SF fuse for 112.5KVA Tx o/p #06-R1-15. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3001248 | 1 | 17:35 | Afternoon | Monday | 2015 | 6
23 | 2015-06-01 21:45 | 2015-06-01 21:45 | 13.8KV BEKASAP FEEDER #3 | Cloudy and Lightning | Lightning | 54 | Bekasap VCB fdr #3 T/R 1x. Not checked yet. | 3001248 | 1 | 21:45 | Night | Monday | 2015 | 6
24 | 2015-06-01 21:45 | 2015-07-01 13:45 | 13.8KV BEKASAP FEEDER #3 | Cloudy and Lightning | Lightning | 54 | Checked & found, Bekasap Main VCB fdr #3 T/R 1x Ctr: 577-578 R/F: 51N. Patrolled the line & found, @3 broken L/A o/p #37BE-30. Cause: Lightning. | 3001248 | 1 | 21:45 | Night | Monday | 2015 | 6
25 | 2015-06-01 22:12 | 2015-06-01 22:12 | 13.8KV BANGKO FEEDER #1 | Cloudy | Unidentified (Fuse) | 9 | 22:12 It was reported b/o fuse for Tx at Well Bangko #15. (Bangko fdr #1) 23:15 Check & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Bangko #15. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above the same size & energized the Tx. Cause: Unidentified (fuse). | 3001248 | 1 | 22:12 | Night | Monday | 2015 | 6
26 | 2015-07-01 01:36 | 2015-07-01 01:36 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain | Lightning | 0 | Duri Community VCB fdr #2 T/R 1x. Not checked yet. | 3001248 | 1 | 1:36 | Night | Wednesday | 2015 | 7
27 | 2015-07-01 01:36 | 2015-10-01 14:09 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain | Lightning | 0 | Checked & found, Duri Community VCB fdr #2 T/R 1x Ctr: 62-63 R/F: 51N. Patrolled the line, but found nothing. Cause: Lightning. | 3001248 | 1 | 1:36 | Night | Wednesday | 2015 | 7
28 | 2015-07-01 05:58 | 2015-07-01 05:58 | 13.8KV 6DN FEEDER #6 | Fair | Unidentified | 29 | 6DN fdr #6 Load dropped 144A (203-59A). Not checked yet. | 3001249 | 1 | 5:58 | Morning | Wednesday | 2015 | 7
29 | 2015-07-01 05:58 | 2015-09-01 16:20 | 13.8KV 6DN FEEDER #6 | Fair | Unidentified | 29 | Checked & found, Recl. 6E–64 (6DN fdr #6) T/R 1x Ctr: 23-24. Patrolled the line & found nothing. Cause: Unidentified. | 3001249 | 1 | 5:58 | Morning | Wednesday | 2015 | 7
30 | 2015-07-01 11:44 | 2015-07-01 11:44 | 13.8KV ROKAN FEEDER #2 | Fair | Pin Insulator | 2 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3001248 | 1 | 11:44 | Morning | Wednesday | 2015 | 7
31 | 2015-07-01 11:44 | 2015-10-01 14:15 | 13.8KV ROKAN FEEDER #2 | Fair | Pin Insulator | 2 | Checked & found , Rokan VCB fdr #2 T/R 1x Ctr: 960-961 R/F : 51@1,@2. Patrolled the line & found: -@1 Broken Pin Insulator o/p #31AV-17. -@2 Broken Pin Insulator o/p #31AV-01. Cause: Pin Insulator. | 3001248 | 1 | 11:44 | Morning | Wednesday | 2015 | 7
32 | 2015-07-01 12:58 | 2015-07-01 12:58 | MINAS POWER PLANT | Fair |  | - | MGT #5 T/O By Alarm: High vibration trip. Cause: Vibration. |  | 1 | 12:58 | Afternoon | Wednesday | 2015 | 7
33 | 2015-07-01 14:05 | 2015-07-01 14:05 | MINAS POWER PLANT |  |  | - | 14:05 S/U MGT #5 , then On Line at 14:55. |  | 1 | 14:05 | Afternoon | Wednesday | 2015 | 7
34 | 2015-07-01 22:41 | 2015-07-01 22:41 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 11 | Pungut OCB fdr #2 T/R 1x. Not checked yet. | 3001248 | 1 | 22:41 | Night | Wednesday | 2015 | 7
35 | 2015-07-01 22:41 | 2015-09-01 07:41 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 11 | Checked & found, Pungut OCB fdr #2 T/R 1x Ctr: 335-336 R/F: 51@1. Patrolled the line & found: -@1 Flashed over Pin Insulator o/p #DK-67. -@1 Flashed over Bypass Sw of Recl. 46BP-12. Cause: Lightning. | 3001248 | 1 | 22:41 | Night | Wednesday | 2015 | 7
36 | 2015-08-01 02:18 | 2015-08-01 02:18 | 13.8KV MINAS FEEDER #3 | Rain | Lightning | 269 | 02:18 Minas ACB fdr #3 T/LO. Ctr: 80076-80078 R/F: 51@1,@2. 02:34 Patrolled the line, but found nothing. 04:53 Blocked & closed Minas ACB fdr#3, Ok. Then release the block. Cause: Suspected by Lightning. (The line would be Re-Patrolled tomorrow) | 3001248 | 1 | 2:18 | Night | Saturday | 2015 | 8
37 | 2015-08-01 02:18 | 2015-09-01 16:18 | 13.8KV MINAS FEEDER #3 | Rain | Lightning | 269 | Re-Patrolled the line Minas fdr #3 & found: -@1 Broken Dead end Insulator o/p #8C-82. -@1 Broken Dead end Insulator o/p #8D-41. Cause: Lightning. | 3001248 | 1 | 2:18 | Night | Saturday | 2015 | 8
38 | 2015-08-01 02:19 | 2015-08-01 02:19 | MINAS POWER PLANT | Fair | Relay Failure | 0 | 02:19 MGT #1 Tripped By Alarm: Generator Diff. Lock out. 04:26 Checked & found, burnt out Relay-86. Cause: Relay failure. (Burnt out Relay-86) (MGT #1 Status - NSB) | 3001249 | 1 | 2:19 | Night | Saturday | 2015 | 8
39 | 2015-08-01 08:48 | 2015-08-01 08:48 | 13.8KV DURI FIELD FEEDER #2 | Rain | Unidentified | 11 | 08:48 Duri Field fdr #2 Load dropped 20A( 160-140). It was reported no Power near Pole #06-S5-11. (D.Field fdr #2) 09:26 Checked & found, Recl. 06-S5-02 (D.Field fdr #2) T/LO. Ctr: 416-426. Patrolled the line, but found nothing. 09:37 Blocked & Closed the Recl. 06-S5-02, Ok. Then Released the Block. Couse: Unidentified. | 3001248 | 1 | 8:48 | Morning | Saturday | 2015 | 8
40 | 2015-08-01 08:50 | 2015-08-01 08:50 | 13.8KV RANGAU FEEDER #2 | Cloudy | Lightning | 34 | Rangau VCB fdr #2 T/R 1x. Not checked yet. | 3001248 | 1 | 8:50 | Morning | Saturday | 2015 | 8
41 | 2015-08-01 08:50 | 2015-10-01 14:28 | 13.8KV RANGAU FEEDER #2 | Cloudy | Lightning | 34 | Checked & found, Rangau OCB fdr #2 T/R 1x Ctr: 300-301 R/F: Did not appear. Patrolled the line, but found nothing. Cuase: Suspected by lightning. | 3001248 | 1 | 8:50 | Morning | Saturday | 2015 | 8
42 | 2015-08-01 08:53 | 2015-08-01 08:53 | 13.8KV BANGKO FEEDER #2 | Fair | Unidentified | 1 | Bangko OCB fdr #2 T/R 1x. Bangko fdr #1 Load dropped 82A (268-196A). Not checked yet. | 3001248 | 1 | 8:53 | Morning | Saturday | 2015 | 8
43 | 2015-08-01 08:53 | 2015-10-01 07:53 | 13.8KV BANGKO FEEDER #2 | Fair | Unidentified | 1 | Checked & found, Bangko OCB fdr #2 T/R 1x Ctr: 99950-99951 R/F: 50@3 & 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3001248 | 1 | 8:53 | Morning | Saturday | 2015 | 8
44 | 2015-08-01 08:53 | 2015-08-01 08:53 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified (L/A) | 0 | Ketigul fdr #1 Load dropped 35A (167-132A). Not Checked yet. | 3001248 | 1 | 8:53 | Morning | Saturday | 2015 | 8
45 | 2015-08-01 08:53 | 2015-12-01 16:27 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified (L/A) | 0 | Patrolled the line & found, broken L/A o/p #33AJ-11. (at downstream of Ketigul Breaker VCB fdr #1) Ketigul VCB fdr #1 Ctr. & R/F are not checked yet. (Access to Ketigul Substation flooding) | 3001248 | 1 | 8:53 | Morning | Saturday | 2015 | 8
46 | 2015-08-01 16:11 | 2015-08-01 16:11 | 13.8KV PEMATANG FEEDER #1 | Cloudy | Planned Maintenance | 58 | 16:11 Manual Open Pematang OCB fdr #1. To bypass Recl. 37BC-14 (Pematang fdr #1). (Due to the Recloser tank was swelling & Oil leaks) 16:24 Blocked & Closed, Pematang OCB fdr #1, Ok. Then released the Block. Cause: Recloser problem. (The Recloser unit would be replaced tomorrow) | 123 | 1 | 16:11 | Afternoon | Saturday | 2015 | 8
47 | 2015-08-01 16:34 | 2015-08-01 16:34 | 13.8KV NORTH DURI FEEDER #7 | Rain and Lightning | Lightning | 0 | No.Duri VCB fdr #7 T/R 1x. Not checked yet. | 3001248 | 1 | 16:34 | Afternoon | Saturday | 2015 | 8
48 | 2015-08-01 16:34 | 13/01/2015 14:00 | 13.8KV NORTH DURI FEEDER #7 | Rain and Lightning | Lightning | 0 | Checked & found, No.Duri VCB fdr #7 T/R 1x Ctr: 183. (Not changed) R/F: 51@1 & 50N. Patrolled the line & found, @1 broken Dead end insulator o/p #10-J4-01. Cause: Lightning. | 3001248 | 1 | 16:34 | Afternoon | Saturday | 2015 | 8
49 | 2015-08-01 18:00 | 2015-08-01 18:00 | MINAS POWER PLANT |  |  | - | 18:00 Off line MGT #10, then S/D the Unit at 18:12. For S/B-Prior to troubleshooting high Vibration at BB-12. (Vibration 0.92"/sec) | 123 | 1 | 18:00 | Afternoon | Saturday | 2015 | 8
50 | 2015-08-01 18:20 | 2015-08-01 18:20 | MINAS POWER PLANT |  |  | - | 18:20 S/U MGT #6, then on line the unit at 18:55. |  | 1 | 18:20 | Afternoon | Saturday | 2015 | 8
51 | 2015-08-01 19:28 | 2015-08-01 19:28 | MINAS POWER PLANT | Drizzle | Main breaker | 138 | MGT #11 Tripped. By Alarm: Bearing Header Temp. High. Cause: No cooling System, 480V Main Breaker Station service trip when crank MGT-10. Ground fault relay flag at Main Breaker Station service (52M) of MGT-10 Remark: Currently, 480V Sta. service of MGT #11 is supplied from MGT #10. Frequency system dropped to 59.46Hz. (Load shedding level-1) 3D OCB fdr #5 T/O, then closed at 19:35. 4D OCB fdr #3 T/O, then closed at 19:36. 4D OCB fdr #5 T/O, then closed at 19:35. 5B OCB fdr #4 T/O, then closed at 19:36. 5B OCB fdr #5 T/O, then closed at 19:37. 20:23 S/U MGT #11, then on line the Unit at 21:00. | 3001249 | 1 | 19:28 | Night | Saturday | 2015 | 8
52 | 2015-09-01 15:25 | 2015-09-01 15:25 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 54 | 15:25 6D fdr #1 Load dropped 123A (334-211A). Not checked yet. | 3001249 | 1 | 15:25 | Afternoon | Tuesday | 2015 | 9
53 | 2015-09-01 15:25 | 2015-10-01 15:25 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 54 | Checked Recl. 5C-42 (6D fdr #1) & found, normal. (Counter did not change) Patrolled the line, but found nothing. Cause: Lightning. | 3001249 | 1 | 15:25 | Afternoon | Tuesday | 2015 | 9
54 | 2015-09-01 15:25 | 2015-09-01 15:25 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 13 | 15:25:01 6D fdr #2 Load dropped 150A (176-26A). Not checked yet. | 3001249 | 1 | 15:25 | Afternoon | Tuesday | 2015 | 9
55 | 2015-09-01 15:25 | 2015-10-01 15:25 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 13 | Checked 6D OCB fdr #2 & found, normal. (No R/F appeare & Ctr. did not change) Also checked Recl. 6D-78A & Recl. 6D-298 (6D fdr #2) & found, normal. (Ctr. did not change) Patrolled the line, but found nothing. Cause: Lightning. | 3001249 | 1 | 15:25 | Afternoon | Tuesday | 2015 | 9
56 | 2015-09-01 15:35 | 2015-09-01 15:35 | MINAS POWER PLANT |  |  | - | 15:35 S/U MGT #1, then on line the Unit at 19:00. |  | 1 | 15:35 | Afternoon | Tuesday | 2015 | 9
57 | 2015-09-01 18:58 | 2015-09-01 18:58 | DURI POWER PLANT |  |  | - | 18:58 S/U DGT #7, then on line the Unit at 19:00. |  | 1 | 18:58 | Afternoon | Tuesday | 2015 | 9
58 | 2015-09-01 19:33 | 2015-09-01 19:33 | MINAS POWER PLANT |  |  | - | Off Line MGT #11, then S/D the Unit for S/B. (Prior to checking the Heating Fuel nozzle set) |  | 1 | 19:33 | Night | Tuesday | 2015 | 9
59 | 2015-10-01 08:00 | 2015-10-01 08:00 | 13.8KV 8D FEEDER #11 | Fair | Low mega-ohm reading | 36 | 08:00 It was reported that b/o fuse for Tx at Well #7E-65E. 14:20 Checked & found, @1,@2 b/o 1.4SF fuses for 80Kva Tx at Well #7E-65E. Tested the Tx & found, Low megger reading. Cause: Tx low megger reading. (The Tx is not replaced yet) | 3001249 | 1 | 8:00 | Morning | Thursday | 2015 | 10
60 | 2015-10-01 08:00 | 13/01/2015 16:38 | 13.8KV 8D FEEDER #11 | Fair | Low mega-ohm reading | 36 | Replaced 80Kva Tx with 50Kva Tx & energized the Tx at Well #7E-65E. | 3001249 | 1 | 8:00 | Morning | Thursday | 2015 | 10
61 | 2015-10-01 21:59 | 2015-10-01 21:59 | 44KV MINAS - RUMBAI LINE | Fair | Unidentified | 0 | 21:59 Minas SWG ACB #21 (44KV Minas - Rumbai line) T/R 1x Ctr: 64-65 R/F: 51G (@1,@2). (At the time All Minas RTU & Libo RTU failed) The line is not Patrolled yet. | 3001249 | 1 | 21:59 | Night | Thursday | 2015 | 10
62 | 2015-10-01 21:59 | 13/01/2015 16:34 | 44KV MINAS - RUMBAI LINE | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3001249 | 1 | 21:59 | Night | Thursday | 2015 | 10
63 | 2015-11-01 07:50 | 2015-11-01 07:50 | 13.8KV 8D FEEDER #11 | Cloudy and Lightning | Lightning | 58 | 8D fdr #11 load dropped 141A (337-196A). Not checked yet. | 3001249 | 1 | 7:50 | Morning | Sunday | 2015 | 11
64 | 2015-11-01 07:50 | 15/01/2015 11:50 | 13.8KV 8D FEEDER #11 | Cloudy and Lightning | Lightning | 58 | Checked & found, Recl. 9E-02 (8D fdr #11) T/R 1x Ctr: 1052-1053. Patrolled the line, but found nothing. Cause: Lightning. | 3001249 | 1 | 7:50 | Morning | Sunday | 2015 | 11
65 | 2015-11-01 09:00 | 2015-11-01 09:00 | 13.8KV BEKASAP FEEDER #3 | Fair | Animal | 2 | 09:00 It was reported b/o fuses for Tx at Well Bekasap #49. Checked & found, @1,@2,@3 b/o 3.1SF fuse for 150Kva Tx at Well Bekasap #49. Performed TTR & Megger test & found, normal reading. 12:00 Replaced b/o fuses above with the same size & energized the Tx. Cause: Animal. (Monitor Lizard at Switchboard). | 3001248 | 1 | 9:00 | Morning | Sunday | 2015 | 11
66 | 2015-11-01 10:00 | 2015-11-01 10:00 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 0 | 10:00 It was reported b/o fuse for 112.5Kva Tx o/p #09-M1-12. Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #09-M1-12. Performed TTR & Megger test & found, normal reading. 16:00 Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Lizard at main breaker) | 3001248 | 1 | 10:00 | Morning | Sunday | 2015 | 11
67 | 2015-11-01 10:05 | 2015-11-01 10:05 | 13.8KV NELLA FEEDER #2 | Fair | Animal | 4 | 10:05 It was reported b/o fuses for Tx at Well Bangko #118. Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well Bangko #118. Tested the Tx & found, Normal reading. 11:05 Replaced b/o fuses above with the same size & energized the Tx. Cause: Animal. (wild cat) | 3001248 | 1 | 10:05 | Morning | Sunday | 2015 | 11
68 | 2015-11-01 15:48 | 2015-11-01 15:48 | 13.8KV 8D FEEDER #11 | Fair | Low mega-ohm reading | 0 | It was reported b/o fuse for Tx at Well #8E-74N. Checked & found, @1 b/o 14.0SF fuse for 550Kva Tx at Well #8E-74N. Performed Megger test & found, low Megger reading. Cause: Tx low megger Reading. (It will be replaced tomorrow) | 3001249 | 1 | 15:48 | Afternoon | Sunday | 2015 | 11
69 | 2015-11-01 15:48 | 2015-12-01 15:28 | 13.8KV 8D FEEDER #11 | Fair | Low mega-ohm reading | 0 | Replaced low-meg 550 Kva Tx with the same size at well 8E-74N. Cause: Low-Meg Reading Tx. | 3001249 | 1 | 15:48 | Afternoon | Sunday | 2015 | 11
70 | 2015-11-01 20:54 | 2015-11-01 20:54 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 77 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3001249 | 1 | 20:54 | Night | Sunday | 2015 | 11
71 | 2015-11-01 20:54 | 13/01/2015 07:54 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 77 | Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1242-1243 R/F: 51N. Patrolled the line & found, @3 broken Dead end Insulator o/p #38CX-14. Cause: Lightning. | 3001249 | 1 | 20:54 | Night | Sunday | 2015 | 11
72 | 2015-12-01 10:45 | 2015-12-01 10:45 | MINAS POWER PLANT |  |  | - | 10:45 S/U MGT #5, then online the Unit at 11:06. |  | 1 | 10:45 | Morning | Tuesday | 2015 | 12
73 | 2015-12-01 23:12 | 2015-12-01 23:12 | 13.8KV SINTONG GFPC | Fair | Unidentified | 0 | Sintong GFPC T/R 1x. Fault alarm on Sintong fdr #2. (No load dropped at any feeders) Not checked yet. | 3001248 | 1 | 23:12 | Night | Tuesday | 2015 | 12
74 | 2015-12-01 23:12 | 15/01/2015 16:12 | 13.8KV SINTONG GFPC | Fair | Unidentified | 0 | Checked & found, Sintong GFPC T/R 1x Ctr: 707-708. Patrolled Sintong fdr #2 line, but found nothing. Cause: Unidentified. | 3001248 | 1 | 23:12 | Night | Tuesday | 2015 | 12
75 | 2015-01-13 10:15 | 2015-01-13 10:15 | MINAS POWER PLANT |  |  | - | 10:15 S/U MGT #7, then online the Unit at 10:54. (Running on Test after Major Overhaul) |  | 1 | 10:15 | Morning | Tuesday | 2015 | 1
76 | 2015-01-13 10:15 | 2015-01-14 14:38 | MINAS POWER PLANT |  |  | - | 14:38 Offline MGT #7, then S/D the unit for S/B. (Prior to repair automazing air compressor). |  | 1 | 10:15 | Morning | Tuesday | 2015 | 1
77 | 2015-01-13 16:22 | 2015-01-13 16:22 | CENTRAL DURI POWER PLANT |  |  | - | 16:22 Offline CGT #4, then S/D the unit. 16:34 Closed AVB #39. (Tie breaker) 16:56 Re S/U CGT #4, then Online at 17:14. 17:11 Opened ACB #39. (Tie breaker) Cause: Loss of 480V Power Supply station service. |  | 1 | 16:22 | Afternoon | Tuesday | 2015 | 1
78 | 2015-01-14 10:12 | 2015-01-14 10:12 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 109 | 10:12-12:10 Manually open LBS #5B-67 to cut high danger trees between poles #5B-56 & #58. Cause: Maintenance job. | 123 | 1 | 10:12 | Morning | Wednesday | 2015 | 1
79 | 2015-01-14 10:22 | 2015-01-14 10:22 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 27 | Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #1 load dropped 35A (140-105A). Ketigul fdr #3 load dropped 7A (16-9A). Not checked yet. | 3001248 | 1 | 10:22 | Morning | Wednesday | 2015 | 1
80 | 2015-01-14 10:22 | 2015-01-20 13:22 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 27 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 147-148 R/F: 51N(@1). Patrolled the line & found, @1 broken L/A on TP of Well Pagar #14. Cause: Lightning. | 3001248 | 1 | 10:22 | Morning | Wednesday | 2015 | 1
81 | 2015-01-14 17:15 | 2015-01-14 17:15 | 13.8KV KETIGUL FEEDER#3 | Fair | Theft | 0 | It was reported Vandalism transformer at well Gulamo #3. (The well was off due to Zero Megg status since Jan 12, 2015) Cause: Thieft. | 3001248 | 1 | 17:15 | Afternoon | Wednesday | 2015 | 1
82 | 2015-01-14 17:40 | 2015-01-14 17:40 | CENTRAL DURI POWER PLANT |  |  | - | 17:40 S/U CGT #1, then online at 18:35. (Running on test after M/O) 18:34 Opened C.Duri ACB #19. (Tie Breaker) |  | 1 | 17:40 | Afternoon | Wednesday | 2015 | 1
83 | 2015-01-14 18:00 | 2015-01-14 18:00 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 34 | It was reported b/o fuses for Tx at Well Tilan #16. Not checked yet. | 3001248 | 1 | 18:00 | Afternoon | Wednesday | 2015 | 1
84 | 2015-01-14 18:00 | 2015-01-15 11:10 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 34 | Checked & found, @1,@2 b/o 14.0SF fuses for 500Kva Tx at Well Tilan #16. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with same size & energized the Tx. Cause: Animal. (Bird) | 3001248 | 1 | 18:00 | Afternoon | Wednesday | 2015 | 1
85 | 2015-01-14 22:43 | 2015-01-14 22:43 | 13.8KV 5B FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuses for Tx at Well #5B-85. Not checked yet. | 3001249 | 1 | 22:43 | Night | Wednesday | 2015 | 1
86 | 2015-01-14 22:43 | 2015-01-16 11:18 | 13.8KV 5B FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1 b/o 3.5SF fuse for 300Kva Tx at Well #5B-85. Performed TTR & Megger test & found, good reading. Replaced b/o fuse above wit the same size & energized Tx. Cause: Unindentified (fuse). | 3001249 | 1 | 22:43 | Night | Wednesday | 2015 | 1
87 | 2015-01-15 09:35 | 2015-01-15 09:35 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 09:35 It was reported b/o fuse for Tx o/p #03-01-35. Checked & found, @1 b/o 2.1SF fuse for 112.5Kva Tx o/p #03-01-35. 16:55 Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3001248 | 1 | 9:35 | Morning | Thursday | 2015 | 1
88 | 2015-01-15 09:40 | 2015-01-15 09:40 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 8 | 09:40-10:40 Blocked OKB fdr #2, to open HLC o/p #38CV-13. Replaced @3 broken Dead end insulator o/p #38CV-14. (Wells KB #46, #384, #446 were off during the job) Cause: Maintenance job. | 123 | 1 | 9:40 | Morning | Thursday | 2015 | 1
89 | 2015-01-15 15:15 | 2015-01-15 15:15 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | It was reported b/o fuse for Tx at Well Rantaubais #74. Not checked yet. | 3001248 | 1 | 15:15 | Afternoon | Thursday | 2015 | 1
90 | 2015-01-15 15:15 | 2015-01-16 11:55 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | Checked & found, @2 b/o 15K fuse for 180Kva Tx at Well Rantaubais #74. Perform TTR & megger test & found, normal. (good reading) Replaced b/o fuse above with the same size & Energized Tx. Cause: Animal. (Chicken) | 3001248 | 1 | 15:15 | Afternoon | Thursday | 2015 | 1
91 | 2015-01-15 23:19 | 2015-01-15 23:19 | ROKAN SUBSTATION | Fair | Guy Wire | 85 | 23:19 Petani, Rangau, Rokan & Ketigul Substation RTU Failed. 16-Jan-2015. 01:40 Checked & found: -Rokan 115kV C/S T/O. Ctr: 180-181 R/F: 51N. -Rokan VCB fdr #2 T/SO. Ctr: 743-744 R/F: 51N. -Rokan VCB fdr #4 T/SO. Ctr: 961-962 R/F: 51N & 51@2,@3. 01:45 Manual opened Rokan VCB fdr #3. 01:50 Closed 115KV Rokan C/S, Ok. Blocked & closed Rokan VCB fdr #3, Ok. Then released the Block. Ctr: 605-606. 02:00 Patrolled & found, broken Guy wire o/p #RS-RP-03 & the pole tilted. (D/S of Rokan fdr #4) (the Guy wire touching to Rokan fdr #2 & fdr #4 line) 03:30 Cut Jumper o/p #NN, to isolate the broken Guy wire above. 03:35 Blocked & closed Rokan VCB fdr #2, Ok. Then released the block. 16:00 Blocked & closed Rokan VCB fdr #4, Ok. Then released the block. (After repairing broken Guy wire above) Cause: Broken Guy wire. | 3001248 | 1 | 23:19 | Night | Thursday | 2015 | 1
92 | 2015-01-16 06:10 | 2015-01-16 06:10 | 13.8KV MENGGALA FEEDER #2 | Fair | Unidentified | 0 | Menggala fdr #2 load dropped 37A (87-50A). (Menggala GFPC in block position for Rig Job) Not patrolled yet. | 3001248 | 1 | 6:10 | Morning | Friday | 2015 | 1
93 | 2015-01-16 06:10 | 2015-01-18 09:31 | 13.8KV MENGGALA FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recl. 26AK-02 (Menggala fdr #2) T/R 1x Ctr: 145-146. (Menggala GFPc in block position for Rig Job) Patrolled the line, but found nothing. Cause: Unidentified. | 3001248 | 1 | 6:10 | Morning | Friday | 2015 | 1
94 | 2015-01-16 07:45 | 2015-01-16 07:45 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 07:45 It was reported b/o fuse for Tx o/p #04-07-07. 15:00 Checked & found, @1 b/o 2.1SF fuse for 112.5Kva Tx o/p #04-7-07. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3001248 | 1 | 7:45 | Morning | Friday | 2015 | 1
95 | 2015-01-16 07:50 | 2015-01-16 07:50 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Bangko fdr #4 load dropped 12A (139-127A). Bangko GFPC T/R 1x. (Ground fault alarm on Bangko fdr #4) Not checked yet. | 3001248 | 1 | 7:50 | Morning | Friday | 2015 | 1
96 | 2015-01-16 07:50 | 2015-01-18 15:00 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 2x Ctr: 49-51. Also found, Bangko GFPC T/R 1x Ctr: 438-439. Patrolled the line, but found nothing. Cause: Unidentified. | 3001248 | 1 | 7:50 | Morning | Friday | 2015 | 1
97 | 2015-01-16 08:55 | 2015-01-16 08:55 | CENTRAL DURI POWER PLANT | Fair | Others | - | 08:55 CGT #4 Generator Breaker Tripped. By Alarm: Cooling water pressure low. 09:03 Closed 13.8 KV ACB #39. (Tie breaker) 09:43 Opened 13.8 KV ACB #39. (Tie breaker) 09:47 Re-On Line CGT #4. Cause: Others. (One of two water cooling pump Trip) |  | 1 | 8:55 | Morning | Friday | 2015 | 1
98 | 2015-01-16 14:27 | 2015-01-16 14:27 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Main breaker | 0 | It was reported b/o fuse for Tx o/p #02-1-01. Checked & found, @1,@2,@3 b/o 2.1SF fuses for 112.5Kva Tx o/p #02-1-01. (Also found, broken Main Breaker & rusty panel box) Cause: Main Breaker. (Main breaker & panel box are not replaced yet, W/O Prod. MPU team) | 3001248 | 1 | 14:27 | Afternoon | Friday | 2015 | 1
99 | 2015-01-16 14:27 | 2015-01-21 14:27 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Main breaker | 0 | Replaced b/o fuse above with the same size & energized the Tx o/p #02-1-01. (After replacing broken Panel Box & Main Breaker by Electrician) | 3001248 | 1 | 14:27 | Afternoon | Friday | 2015 | 1
100 | 2015-01-16 15:46 | 2015-01-16 15:46 | 13.8KV 6D FEEDER #1 | Fair | Tree | 193 | 15:46 6D OCB fdr #1 T/LO. Ctr: 280-284 R/F: 51@2. 6D fdr #2 load dropped 36A (198-162A). 6D fdr #3 load dropped 11A (133-122A). Checked & found, fallen tree & hit to powerline at near Well #5C 59. (The Tree was cut by villagers) 16:53 Open LBS #5C-59, to isolate the tree above. 16:54 Blocked & closed, 6D OCB fdr #1, Ok. Then released the block. (After Clearing the fallen trees from powerline) 17:35 Re-Closed LBS #5C-59, to normalize 6D fdr #1 load. Cause: Tree. | 3001249 | 1 | 15:46 | Afternoon | Friday | 2015 | 1
101 | 2015-01-16 16:23 | 2015-01-16 16:23 | 13.8KV 6DN FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 16:23 It was reported b/o fuse for Tx at Well #5E-55. Checked & found, @1 b/o 14.0SF fuse for 550Kva Tx at Well #5E-55. Tested the Tx & found, normal. (good reading) 19:54 Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3001249 | 1 | 16:23 | Afternoon | Friday | 2015 | 1
102 | 2015-01-16 21:00 | 2015-01-16 21:00 | MINAS POWER PLANT |  |  | - | 21:00 S/U MGT #11, the on lin the Unit at 21:21. |  | 1 | 21:00 | Night | Friday | 2015 | 1
103 | 2015-01-16 22:00 | 2015-01-16 22:00 | DURI POWER PLANT |  |  | - | Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 22:00 | Night | Friday | 2015 | 1
104 | 2015-01-16 23:11 | 2015-01-16 23:11 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 3 | It was reported b/o fuse for Tx at Well Pagar #21. (Ketigul fdr #2) Not checked yet. | 3001248 | 1 | 23:11 | Night | Friday | 2015 | 1
105 | 2015-01-16 23:11 | 2015-01-17 11:43 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 3 | Checked & found, @2 b/o 7.8SF fuse for 300KVA Tx at Well #Pagar 21. Tested the Tx & found, normal. (good reading) Then replaced B/O fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3001248 | 1 | 23:11 | Night | Friday | 2015 | 1
106 | 2015-01-17 08:32 | 2015-01-17 08:32 | MINAS POWER PLANT | Fair |  | - | 08:32 Off line MGT #6, then S/D the unit for S/B. |  | 1 | 8:32 | Morning | Saturday | 2015 | 1
107 | 2015-01-18 07:32 | 2015-01-18 07:32 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | 07:32 It was reported fuse for Tx at Well Rantaubais #59. 12:40 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Rantaubais #59. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Rat) | 3001248 | 1 | 7:32 | Morning | Sunday | 2015 | 1
108 | 2015-01-18 08:52 | 2015-01-18 08:52 | 13.8KV BEKASAP FEEDER #6 | Fair | Pin Insulator | 79 | Bekasap fdr #6 Load dropped 57A (74-17A). Not checked yet. | 3001248 | 1 | 8:52 | Morning | Sunday | 2015 | 1
109 | 2015-01-18 08:52 | 2015-01-21 17:45 | 13.8KV BEKASAP FEEDER #6 | Fair | Pin Insulator | 79 | Checked & found, Recl. 38BE-10 (Bekasap fdr #6) T/R 1x Ctr: 73-74. Patrolled the line & found, @2 flashed over Pin Insulator o/p #38BF-07. Cause: Pin Insulator. | 3001248 | 1 | 8:52 | Morning | Sunday | 2015 | 1
110 | 2015-01-18 10:01 | 2015-01-18 10:01 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 14 | 10:00 It was reported b/o fuse for Tx o/p #07-V3-27. 14:30 Checked & found, @1, @2 b/o 2.1SF fuses for 112.5Kva Tx o/p #07-V3-27. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Squirrel) | 3001248 | 1 | 10:01 | Morning | Sunday | 2015 | 1
111 | 2015-01-18 14:18 | 2015-01-18 14:18 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Animal | 1 | 14:18 It was reported b/o fuse for Tx o/p #01-07-20. 14:30 Checked & found, @1, @2 b/o 2.1SF fuses for 112.5Kva Tx o/p #01-07-20. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Bird) | 3001248 | 1 | 14:18 | Afternoon | Sunday | 2015 | 1
112 | 2015-01-18 18:21 | 2015-01-18 18:21 | 13.8KV 8C FEEDER #4 | Fair | Unidentified | 19 | 8C VCB fdr #4 T/R 1x. Not checked yet. | 3001249 | 1 | 18:21 | Afternoon | Sunday | 2015 | 1
113 | 2015-01-18 18:21 | 2015-01-19 15:08 | 13.8KV 8C FEEDER #4 | Fair | Unidentified | 19 | Checked & found, 8C VCB fdr #4 T/R 1x Ctr: 568-569 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3001249 | 1 | 18:21 | Afternoon | Sunday | 2015 | 1
114 | 2015-01-19 15:39 | 2015-01-19 15:39 | MINAS POWER PLANT |  |  | - | S/U MGT #7, then Online the Unit at 16:00. (Running on test after M/O) |  | 1 | 15:39 | Afternoon | Monday | 2015 | 1
115 | 2015-01-19 16:15 | 2015-01-19 16:15 | 13.8KV MENGGALA FEEDER #2 | Cloudy | Unidentified | 53 | Menggala VCB fdr #2 T/R 1x. Not checked yet. | 3001248 | 1 | 16:15 | Afternoon | Monday | 2015 | 1
116 | 2015-01-20 16:30 | 2015-01-20 16:30 | MINAS POWER PLANT |  |  | - | Offline MGT #7, then S/D the unit for S/B. (Prior to replace fuel nozzle) |  | 1 | 16:30 | Afternoon | Tuesday | 2015 | 1
117 | 2015-01-20 19:08 | 2015-01-20 19:08 | 13.8KV 5B FEEDER #2 | Fair | Unidentified | 31 | 5B OCB fdr #2 T/R 1x. Not checked yet. | 3001249 | 1 | 19:08 | Night | Tuesday | 2015 | 1
118 | 2015-01-20 19:08 | 2015-01-26 15:08 | 13.8KV 5B FEEDER #2 | Fair | Unidentified | 31 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 325-326 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3001249 | 1 | 19:08 | Night | Tuesday | 2015 | 1
119 | 2015-01-21 03:41 | 2015-01-21 03:41 | 13.8KV 8C FEEDER #4 | Rain | Lightning | 0 | 8C VCB fdr #4 T/R 1x. 8C fdr #1 load dropped 45A (270-225A). 8C fdr #3 load dropped 7A (74-67A). Not checked yet. (See report, 22-Jan-2015 at 04:34) Checked & found, 8C VCB fdr #4 T/R 2x Ctr: 569-571 R/F: 51N. Patrolled the line & found, @1,@2 b/o L/As on TP of Well #8D-93. Cause: Lightning. | 3001248 | 1 | 3:41 | Night | Wednesday | 2015 | 1
120 | 2015-01-21 13:48 | 2015-01-21 13:48 | 13.8KV KOTABATAK FEEDER #2 | Fair | Human Failure | 72 | 13:48 OKB OCB fdr #2 T/O. (when PT SDI Troubleshoot for this fdr) 13:50 Blocked & closed OKB OCB fdr #2, Ok. Then release the block. Cause: Under investigation. 22-Feb-2015. the RCA for this incident had been done by Minas PSE team, and result of the investigation of this incident is Human factor. (Found the Document for this job had been completed) Cause: Human failure. | 3001249 | 1 | 13:48 | Afternoon | Wednesday | 2015 | 1
121 | 2015-01-21 14:25 | 2015-01-21 14:25 | 13.8KV NORTH DURI FEEDER #2 | Fair | Powerline - Conductor | 0 | It was reported b/o fuses for Tx o/p #13-G.51-17. Checked & found, @3 b/o 2.1SF fuse for 112.5Kva Tx o/p #13-G.51-17. (N.Duri fdr #2) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Under Ground Cable. | 3001248 | 1 | 14:25 | Afternoon | Wednesday | 2015 | 1
122 | 2015-01-21 15:59 | 2015-01-21 15:59 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Powerline - Hot Line Clamp | 6 | 15:59 It was reported b/o fuse for Tx o/p #08-M1-37A. 18:25 Checked & found, the fuses for 112.5Kva Tx o/p #08-M1-37A were normal. Also found, loss connection jumpers at HLC o/p #08-M1-37A. Then S/D the 112.5Kva Tx by Opening all fuses, to isolate it. Cause: HLC Loss connection. (it would be repaired tomorrow) | 3001248 | 1 | 15:59 | Afternoon | Wednesday | 2015 | 1
123 | 2015-01-21 15:59 | 2015-01-22 16:00 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Powerline - Hot Line Clamp | 6 | Replaced HLC above with the same size & energized the Tx o/p #08-M1-37A. | 3001248 | 1 | 15:59 | Afternoon | Wednesday | 2015 | 1
124 | 2015-01-21 22:33 | 2015-01-21 22:33 | 13.8KV KETIGUL FEEDER#1 | Fair | Pin Insulator | 2 | Ketigul fdr #1 load dropped 44A (162-118A). Not checked yet. | 3001248 | 1 | 22:33 | Night | Wednesday | 2015 | 1
125 | 2015-01-21 22:33 | 2015-01-23 15:37 | 13.8KV KETIGUL FEEDER#1 | Fair | Pin Insulator | 2 | Checked & found, Recl. 32AK-16 (Ketigul fdr #1) T/R 1x Ctr: 107-108. Patrolled the line & found, @2 broken Pin Insulator o/p #32AK-42. Cause: Lightning. | 3001248 | 1 | 22:33 | Night | Wednesday | 2015 | 1
126 | 2015-01-22 04:34 | 2015-01-22 04:34 | 13.8KV 8C FEEDER #4 | Rain | Lightning | 0 | 8C VCB fdr #4 T/R 1x Ctr: 571-572 R/F: 51N. Patrolled the line & found, @1,@2 broken L/As on TP of Well #8D-93. Cause: Lightning. (Also see report, 21-Jan-2015 at 03:41) | 3001248 | 1 | 4:34 | Morning | Thursday | 2015 | 1
127 | 2015-01-22 06:43 | 2015-01-22 06:43 | 4.16KV SO RUMBAI FEEDER #1 | Fair | Animal | 0 | 06:43 It was reported No power at Rumbai Enau Complex. (at House Enau #326). 10:05 Checked & found, @1,@2,@3 b/o 6K fuses for 75Kva Tx o/p #4LF-02. 11:30 Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Rat) | 3001249 | 1 | 6:43 | Morning | Thursday | 2015 | 1
128 | 2015-01-22 12:28 | 2015-01-22 12:28 | 13.8KV 8C FEEDER #2 | Fair | Low mega-ohm reading | 5 | 12:28 It was reported b/o fuse for Tx at Well #9D-16N. (8C fdr #2) 16:45 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well #9D-16N. Tested the Tx & found, Low Megger reading. Cause: Tx low megger reading. (The low megger Tx is not replaced yet) | 3001249 | 1 | 12:28 | Afternoon | Thursday | 2015 | 1
129 | 2015-01-22 12:28 | 2015-01-27 14:28 | 13.8KV 8C FEEDER #2 | Fair | Low mega-ohm reading | 5 | Replaced 150Kva Tx Low megger reading with the same size, and energized the Tx at Well #9D-16N. Cause: Tx low megger reading. | 3001249 | 1 | 12:28 | Afternoon | Thursday | 2015 | 1
130 | 2015-01-22 23:22 | 2015-01-22 23:22 | MINAS POWER PLANT | Fair |  | - | S/U MGT #6, then on line the Unit at 24:00. | 123 | 1 | 23:22 | Night | Thursday | 2015 | 1
131 | 2015-01-23 00:10 | 2015-01-23 00:10 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT #5, then S/D the Unit for S/B. (Prior to repairing AA Precooler leaks) | 123 | 1 | 0:10 | Night | Friday | 2015 | 1
132 | 2015-01-23 07:49 | 2015-01-23 07:49 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 30 | 07:49 Menggala VCB fdr #1 T/O. (In blocked Position for Rig Job) Menggala GFPC (did not operate). (In blocked posistion for Rig Job) 07:54 Blocked & closed, Menggala VCB fdr #1, Ok. Then released the block. 09:30 Checked & found, Menggala VCB fdr #1 T/O. Ctr: 297-298 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3001248 | 1 | 7:49 | Morning | Friday | 2015 | 1
133 | 2015-01-23 15:44 | 2015-01-23 15:44 | MINAS POWER PLANT |  |  | - | 15:44 S/U MGT#7, then on line the unit at 16:01. |  | 1 | 15:44 | Afternoon | Friday | 2015 | 1
134 | 2015-01-23 17:23 | 2015-01-23 17:23 | MINAS POWER PLANT |  |  | - | Off line MGT #6, then S/D the unit for S/B. |  | 1 | 17:23 | Afternoon | Friday | 2015 | 1
135 | 2015-01-23 17:56 | 2015-01-23 17:56 | 13.8KV KOTABATAK FEEDER #2 | Rain | Unidentified (Fuse) | 7 | 17:56 It was reported b/o fuse for Tx at Well KB #46. 19:30 Checked & found, @2 b/o 25K fuse for 550Kva Tx at Well KB #46. Megger & TTR tested the Tx & found, normal. (good reading) Replaced fuse above with same size & energized the Tx. Cause: Unidentified (fuse). | 3001249 | 1 | 17:56 | Afternoon | Friday | 2015 | 1
136 | 2015-01-24 14:21 | 2015-01-24 14:21 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 2 | 14:21 It was reported b/o fuse for Tx o/p #06-Q1-09. (D.Field fdr #2) 15:50 Checked & found, @1,@3 b/o 2.1SF fuses for 112.5Kva Tx o/p #06-Q1-09. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3001248 | 1 | 14:21 | Afternoon | Saturday | 2015 | 1
137 | 2015-01-24 17:41 | 2015-01-24 17:41 | 13.8KV 5B FEEDER #5 | Rain and Lightning | Lightning | 8 | 5B OCB fdr #5 T/R 1x. 5B OCB fdr #4 Load dropped 288A (317-29A). Not checked yet. | 3001249 | 1 | 17:41 | Afternoon | Saturday | 2015 | 1
138 | 2015-01-24 17:41 | 2015-01-26 15:41 | 13.8KV 5B FEEDER #5 | Rain and Lightning | Lightning | 8 | Checked & found, 5B OCB fdr #5 T/R 1x Ctr: 252-253 R/F: 51@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3001249 | 1 | 17:41 | Afternoon | Saturday | 2015 | 1
139 | 2015-01-25 12:13 | 2015-01-25 12:13 | CENTRAL DURI POWER PLANT |  |  | - | 12:13 S/U CGT #5, then online the Unit at 14:04. |  | 1 | 12:13 | Afternoon | Sunday | 2015 | 1
140 | 2015-01-25 15:01 | 2015-01-25 15:01 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 39 | Petani OCB fdr #2 T/R 1x. Not checked yet. | 3001248 | 1 | 15:01 | Afternoon | Sunday | 2015 | 1
141 | 2015-01-25 15:01 | 2015-01-27 13:28 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 39 | Checked & found, Petani OCB fdr #2 T/R 1x Ctr: 168-169 R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator o/p #33AY-04. Cause: Lightning. | 3001248 | 1 | 15:01 | Afternoon | Sunday | 2015 | 1
142 | 2015-01-25 15:25 | 2015-01-25 15:25 | MINAS POWER PLANT |  |  | - | 15:25 Offline MGT #5, then S/D the unit for S/B. |  | 1 | 15:25 | Afternoon | Sunday | 2015 | 1
143 | 2015-01-26 07:00 | 2015-01-26 07:00 | 13.8KV MINAS FEEDER #2 | Fair | Low mega-ohm reading | 11 | 07:00 It was reported b/o fuse for Tx at Well #7D-65E. Checked & found, @1 b/o 14.0SF fuse for 300Kva Tx at Well #7D-65E. Performed TTR / Megger test the Tx & found, Low megger reading. Cause: Low Megger raeding Tx. (The Low megger reading is not replaced yet / the road need to upgrade) | 3001248 | 1 | 7:00 | Morning | Monday | 2015 | 1
144 | 2015-01-26 07:00 | 2015-09-04 14:06 | 13.8KV MINAS FEEDER #2 | Fair | Low mega-ohm reading | 11 | Replaced 150 Kva Tx with 100 Kva Tx, then energized the Tx. Cause: Low Mega-Ohm Reading Tx. | 3001248 | 1 | 7:00 | Morning | Monday | 2015 | 1
145 | 2015-01-26 10:40 | 2015-01-26 10:40 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Broken Fuse Cut Out | 16 | 10:40 It was reported b/o fuse for Tx o/p #02-04-05. Checked & found, @1 b/o 2.1SF fuse for 112.5Kva Tx o/p #02-04-05. (C.Duri fdr #3) (Also found, @1,@3 broken FCOs o/p above) 15:10 Replaced b/o fuse & broken FCO above with the same size & energized the Tx. Cause: Broken FCO. | 3001248 | 1 | 10:40 | Morning | Monday | 2015 | 1
146 | 2015-01-27 02:09 | 2015-01-27 02:09 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 33 | Nella VCB fdr #2 T/R 1x. Not checked yet. | 3001248 | 1 | 2:09 | Night | Tuesday | 2015 | 1
147 | 2015-01-27 02:09 | 2015-01-28 17:17 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 33 | Checked & found, Nella VCB fdr #2 T/R 1x Ctr: 182-183 R/F: 51@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3001248 | 1 | 2:09 | Night | Tuesday | 2015 | 1
148 | 2015-01-27 08:05 | 2015-01-27 08:05 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Lightning | 0 | Menggala fdr #1 load dropped 102A (175-73A). Menggala GFPC T/R 1x. Not checked yet. | 3001248 | 1 | 8:05 | Morning | Tuesday | 2015 | 1
149 | 2015-01-27 08:05 | 2015-03-02 09:15 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Lightning | 0 | Checked & found, Recl. 19AN-04 (Menggala fdr #1) T/R 1x Ctr: 295-296. Also found, Menggala GFPC T/R 1x Ctr: 1084-1085. Patrolled & found, @3 broken Pin Insualtor o/p #19AK-09. Cause: Lightning. | 3001248 | 1 | 8:05 | Morning | Tuesday | 2015 | 1
150 | 2015-01-27 14:54 | 2015-01-27 14:54 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Animal | 59 | 14:54 It was reported b/o fuse for Tx at Well No.Menggala #26. Checked & found, @3 b/o 7.0SF fuse for 225Kva Tx at Well No.Menggala #26. Tested the Tx & found, normal. (good reading) 19:23 Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3001248 | 1 | 14:54 | Afternoon | Tuesday | 2015 | 1
151 | 2015-01-27 16:21 | 2015-01-27 16:21 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 0 | So.Bekasap fdr #1 load dropped 50A (155-105A). Not checked yet. | 3001248 | 1 | 16:21 | Afternoon | Tuesday | 2015 | 1
152 | 2015-01-27 16:21 | 2015-03-02 10:21 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 36BI-18 (So.Bekasap fdr #1) T/R 5x Ctr: 127-132. Patrolled the line & found, @1 broken Pin Insulator o/p #30BF-19. Cause: Lightning. | 3001248 | 1 | 16:21 | Afternoon | Tuesday | 2015 | 1
153 | 2015-01-27 16:27 | 2015-01-27 16:27 | CENTRAL DURI POWER PLANT |  |  | - | 16:27 Offline CGT #4, then S/D the Unit for S/B. (Prior to Major Overhaul) |  | 1 | 16:27 | Afternoon | Tuesday | 2015 | 1
154 | 2015-01-27 17:34 | 2015-01-27 17:34 | MINAS POWER PLANT |  |  | - | 17:34 S/U MGT #6, then online the Unit at 17:57. |  | 1 | 17:34 | Afternoon | Tuesday | 2015 | 1
155 | 2015-01-28 08:57 | 2015-01-28 08:57 | 13.8KV BEKASAP FEEDER #3 | Fair | Theft | 0 | 08:57 It was reported Vandalism 300Kva Tx at Well Bekasap #159. 16:20 Replaced broken 300Kva Tx with 100Kva Tx at Well Bekasap #159. Cause: Theft. | 3001248 | 1 | 8:57 | Morning | Wednesday | 2015 | 1
156 | 2015-01-28 11:21 | 2015-01-28 11:21 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Animal | 38 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3001248 | 1 | 11:21 | Morning | Wednesday | 2015 | 1
157 | 2015-01-28 11:21 | 2015-03-02 10:05 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Animal | 38 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 140-141 R/F: 51N. Patrolled the line & found, a Dead Monkey under Terminal pole of Well Tilan #21. Cause: Animal. (Monkey) | 3001248 | 1 | 11:21 | Morning | Wednesday | 2015 | 1
158 | 2015-01-28 15:27 | 2015-01-28 15:27 | 13.8KV SINTONG FEEDER #2 | Fair | Pin Insulator | 31 | Sintong fdr #2 load dropped 72A (171-99A). Sintong GFPC T/R 1x. Not checked yet. | 3001248 | 1 | 15:27 | Afternoon | Wednesday | 2015 | 1
159 | 2015-01-28 15:27 | 2015-01-30 07:27 | 13.8KV SINTONG FEEDER #2 | Fair | Pin Insulator | 31 | Checked & found, Recl. 19AN-04 (Sintong fdr #2) T/R 1x Ctr: 295-296. Also found, Sintong GFPC T/R 1x Ctr: 1084-1085. Patrolled the line & found, @3 broken Pin Insulator o/p #19AK-09. Cause: Pin Insulator. | 3001248 | 1 | 15:27 | Afternoon | Wednesday | 2015 | 1
160 | 2015-01-29 12:59 | 2015-01-29 12:59 | 13.8KV PEMATANG FEEDER #2 | Fair | Tree | 147 | 12:59 Pematang fdr #2 load dropped 25A (67-42A). Pematang fdr #1 load dropped 132A (163-31A). T/O WIP at Pematang GS. 16:15 Checked & found, Recl. 34BC-08 (Pematang fdr #2) T/LO. Ctr: 159-162. Patrolled & found, fall down Akasia tree & hit to power line, beetwen pole #34BC-09 and TP of Well Pematang #10. 17:45 Cut jumper o/p #34BC-09 to isolate the line. (Wells Pematang #10 & #44 were off) 18:11 Blocked & closed Recl. 38BD-08, Ok. Then released the block. Cause: Tree. | 3001248 | 1 | 12:59 | Afternoon | Thursday | 2015 | 1
161 | 2015-01-29 15:32 | 2015-01-29 15:32 | 3 DELTA SUBSTATION | Fair | Relay Failure | 252 | 15:32 115KV 3D C/S-Tx #1 T/O. By R/F: 51T(@1). 15:43 Man. Opened 3D OCB fdr #2. Man. Opened 3D OCB fdr #3. Man. Opened 3D OCB fdr #4. Man. Opened 3D OCB fdr #5. 16:01 Man. Closed 115KV 3D C/S-Tx #1, Ok. 16:02 Man. Closed 3D OCB fdr #2. Man. Closed 3D OCB fdr #3. Man. Closed 3D OCB fdr #4. Man. Closed 3D OCB fdr #5 17:06 115KV 3D C/S-Tx #1 T/O again. By R/F: 51T(@1). 17:14 Man. Opened 3D OCB fdr #2. Man. Opened 3D OCB fdr #3. Man. Opened 3D OCB fdr #4. Man. Opened 3D OCB fdr #5. 17:34 Man. Closed 115KV 3D C/S-Tx #1, Ok. (After disabled Relay 51T(@1)) 17:36 Man. Closed 3D OCB fdr #2. Man. Closed 3D OCB fdr #3. Man. Closed 3D OCB fdr #4. Man. Closed 3D OCB fdr #5. Cause: Relay failure. Production loss: 3D fdr #2 : 136 barrels / 37 wells. ( GS #5 & GS #4) 3D fdr #3 : 44 barrels / 23 wells. 3D fdr #4 : 115 barrels / 30 wells. ----------------------------------------------- + Total : 295 barrels / 90 wells. | 3001248 | 1 | 15:32 | Afternoon | Thursday | 2015 | 1
162 | 2015-01-29 19:28 | 2015-01-29 19:28 | 13.8KV RANGAU FEEDER #2 | Fair | Dead End Insulator | 182 | 19:28 Rangau fdr #2 load dropped 67A (72-5A). 22:13 Cheked & found, Recl. 23BD-01 (Rangau fdr #2) T/O. Ctr: 110-111. (In blocked position for Rig Job) Blocked & closed Recl. 23BD-01, Ok. (The Recloser is still in block for Rig Job) The line is not patrolled yet. | 3001248 | 1 | 19:28 | Night | Thursday | 2015 | 1
163 | 2015-01-29 19:28 | 2015-03-02 10:14 | 13.8KV RANGAU FEEDER #2 | Fair | Dead End Insulator | 182 | Patrolled the line & found, @1 broken Dead end Insulator o/p #23E-06. Cause: Dead end Insulator. | 3001248 | 1 | 19:28 | Night | Thursday | 2015 | 1
164 | 2015-01-30 12:05 | 2015-01-30 12:05 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 0 | Bangko GFPC T/R 1x. Ground Fault alarm at BKO fdr #1. (No load dropped at any feeders) Not checked yet. | 3001248 | 1 | 12:05 | Afternoon | Friday | 2015 | 1
165 | 2015-01-30 12:05 | 2015-03-02 16:27 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 24Y-21 (Bangko fdr #1) T/R 1x Ctr: 88-89. Also found, Bangko GFPC T/R 1x Ctr: 438-439. Patrolled the line, but found nothing. Cause: Lightning. | 3001248 | 1 | 12:05 | Afternoon | Friday | 2015 | 1
166 | 2015-01-30 13:20 | 2015-01-30 13:20 | 13.8KV 3D TX-2 GFPC | Fair | Unidentified | 0 | 3D GFPC-TX #2 T/R 1x. Ground fault alarm at 3D fdr #8. (No Load dropped at any feeders) Not checked yet. | 3001248 | 1 | 13:20 | Afternoon | Friday | 2015 | 1
167 | 2015-01-30 13:20 | 2015-09-02 09:00 | 13.8KV 3D TX-2 GFPC | Fair | Unidentified | 0 | Checked & found, 3D GFPC-TX #2 T/R 1x Ctr: 4043-4044. Patrolled 3D fdr #8 line, but found nothing. Cause: Unidentified. | 3001248 | 1 | 13:20 | Afternoon | Friday | 2015 | 1
168 | 2015-01-30 13:20 | 2015-01-30 13:20 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 52 | 13:20 Manual Open Recl. 34BC-08 (Pematang fdr #2). To cut high Palm Trees touching to Power line near Pole #34BC-09. 15:14 Blocked & Closed Recl. 34BC-08, Ok. Then released the block. Cause: Maintenance Job. | 123 | 1 | 13:20 | Afternoon | Friday | 2015 | 1
169 | 2015-01-30 18:20 | 2015-01-30 18:20 | 13.8KV BEKASAP MAIN GFPC | Fair | Unidentified | 0 | Bekasap GFPC-TX #C T/R 1x. Ground fault alarm at Bekasap fdr #1. (No Load dropped at any feeders) Not checked yet. | 3001248 | 1 | 18:20 | Afternoon | Friday | 2015 | 1
170 | 2015-01-30 18:20 | 2015-04-02 13:05 | 13.8KV BEKASAP MAIN GFPC | Fair | Unidentified | 0 | Checked & found, Bekasap GFPC T/R 1x Ctr: 321-322. Patrolled the line at downstream of Bekasap fdr #1, but found nothing. Cause: Unidentified. | 3001248 | 1 | 18:20 | Afternoon | Friday | 2015 | 1
171 | 2015-01-31 13:09 | 2015-01-31 13:09 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 43 | 13:09 Bangko OCB fdr #4 T/R 1x. Bangko GFPC T/R 1x. 13:28 Bangko OCB fdr #4 T/R 1x again. Bangko GFPC T/R 1x again. Not checked yet. | 3001248 | 1 | 13:09 | Afternoon | Saturday | 2015 | 1
172 | 2015-01-31 13:09 | 2015-01-02 16:48 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 43 | Checked & found, Bangko OCB fdr #4 T/R 2x Ctr: 99951-99953 R/F: 51@1,@2,@3. Also found, Bangko GFPC T/R 6x Ctr: 439-445. Patrolled the line & found, @3 broken conductor on TP of OBS Well Bangko #47. (Then dismantled it by cutting jumper on TOP of Well above) Cause: Lightning. | 3001248 | 1 | 13:09 | Afternoon | Saturday | 2015 | 1
173 | 2015-01-31 13:28 | 2015-01-31 13:28 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 10 | Bangko fdr #1 Load dropped 125A (236-87A). Bangko fdr #2 Load dropped 211A (236-25A). T/O WIP at Bangko EOR. Bangko fdr #3 Load dropped 146A (173-27A). T/O WIP at Bangko GS. Not checked yet. | 3001248 | 1 | 13:28 | Afternoon | Saturday | 2015 | 1
174 | 2015-01-31 13:28 | 2015-01-02 16:28 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 10 | Checked & found, Recl. 24Y-21 (Bangko fdr #1) T/R 1x Ctr: 88-89. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3001248 | 1 | 13:28 | Afternoon | Saturday | 2015 | 1
175 | 2015-01-02 11:09 | 2015-01-02 11:09 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 42 | Sintong feeder #2 Load dropped 96A (179-83A). Sintong GFPC T/R 1x. (Ground fault alarm at Sintong fdr #2) Not checked yet. | 3013629 | 1 | 11:09 | Morning | Friday | 2015 | 1
176 | 2015-01-02 11:09 | 2015-02-02 13:56 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 42 | Checked & found, Recl. 28AF-02 (Sintong fdr #2) T/R 1x Ctr: 242-243 R/F: 51@2. Also found, Sintong GFPC T/R 2x Ctr: 711-713. Patrolled the line & found, a Dead Monkey hung on the cross arm o/p #29AB-18. Cause: Animal. (Monkey) | 3013629 | 1 | 11:09 | Morning | Friday | 2015 | 1
177 | 2015-01-02 13:30 | 2015-01-02 13:30 | 13.8KV 6D FEEDER #1 | Fair | Tree | 100 | 13:30 Shutdown Wells #5B-97, #5B-98, #5B-98N, #5B-99, #6B-13 & #6B-14. (6D fdr #1) To cutting high Trees under power line near wells above. 16:00 Energized the Tx, Ok. (after clearing the above Trees) Cause: Trees. | 3013630 | 1 | 13:30 | Afternoon | Friday | 2015 | 1
178 | 2015-02-02 09:15 | 2015-02-02 09:15 | 13.8KV S. BALAM FEEDER #1 | Fair | Lightning Arrester | 50 | So.Balam VCB fdr #1 T/R 1x. So.Balam GFPC T/R 1x. (Ground fault alarm at So.Balam fdr #1) Not checked yet. | 3013629 | 1 | 9:15 | Morning | Monday | 2015 | 2
179 | 2015-02-02 09:15 | 2015-03-02 16:15 | 13.8KV S. BALAM FEEDER #1 | Fair | Lightning Arrester | 50 | Checked & found, So.Balam VCB fdr #1 T/R 1x Ctr: 334 (Did not change). R/F: 51N. Also found, So.Balam GFPC T/R 1x Ctr: 177-178. Patrolled the line & found, @2 broken L/A on TP of Well So.Balam #231. Cause: Lightning Arrester. | 3013629 | 1 | 9:15 | Morning | Monday | 2015 | 2
180 | 2015-02-02 09:40 | 2015-02-02 09:40 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 45 | 09:40 It was reported b/o fuse for Tx o/p #08-M5-A02. 18:30 Checked & found, @3 b/o 2.1SF fuse for 112.5Kva Tx o/p #08-M5-A02. Replaced the b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3013629 | 1 | 9:40 | Morning | Monday | 2015 | 2
181 | 2015-02-02 13:00 | 2015-02-02 13:00 | 13.8KV BATANG FEEDER #2 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx at Well Rantaubais #31. (Batang fdr #2) Not checked yet. | 3013629 | 1 | 13:00 | Afternoon | Monday | 2015 | 2
182 | 2015-02-02 13:00 | 2015-03-02 12:20 | 13.8KV BATANG FEEDER #2 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Rantaubais #31. Tested the Tx & found, normal. (Good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3013629 | 1 | 13:00 | Afternoon | Monday | 2015 | 2
183 | 2015-03-02 12:00 | 2015-03-02 12:00 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Animal | 21 | It was reported b/o fuse for Tx at Well Petapahan #07. (Petapahan fdr #1) Checked & found, @1,@2 b/o 2.5SF fuses for 130Kva Tx at Well Petapahan #07. Replaced b/o fuse above with same size & energized the Tx. Cause: Animal. (Monkey) | 3013630 | 1 | 12:00 | Afternoon | Monday | 2015 | 3
184 | 2015-03-02 12:05 | 2015-03-02 12:05 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Low mega-ohm reading | 1 | 12:05 It was reported b/o fuse for Tx at Well KB #265. (CKBS fdr #6) Checked & found, @1 b/o 1.0SF fuse for 50Kva Tx at Well KB #265. Perform TTR & Megger test the Tx & found, Low megger reading. 14:30 Replaced 50Kva Tx with 100Kva Tx & energized the Tx. Cause: Tx Low megger reading. | 3013630 | 1 | 12:05 | Afternoon | Monday | 2015 | 3
185 | 2015-03-02 15:30 | 2015-03-02 15:30 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 15:30 It was reported b/o fuse for Tx o/p #03-01-26. (C.Duri fdr #7) 17:00 Checked & found, @1, @2 b/o 2.1SF fuses for 112.5Kva Tx o/p #03-01-26. Replaced the b/o fuse with same size & energized the Tx. Cause: Unidentified (fuse). | 3013629 | 1 | 15:30 | Afternoon | Monday | 2015 | 3
186 | 2015-04-02 03:47 | 2015-04-02 03:47 | 13.8KV 4B FEEDER #2 | Fair | Unidentified | 144 | 4B OCB fdr #2 T/R 1x. 4B fdr #1 Load dropped 129A (305-176A). Not checked yet. | 3013630 | 1 | 3:47 | Night | Thursday | 2015 | 4
187 | 2015-04-02 03:47 | 2015-10-02 09:35 | 13.8KV 4B FEEDER #2 | Fair | Unidentified | 144 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 204-205 R/F: 51@2. Patrolled the line, but found nothing. Cause: Unidentified. Checked Recloser at downstream of 4B fdr #1 & found, normal. (Ctr. did not operate) Cause: Suspected some wells were off due to voltage dip when 4B OCB fdr #2 T/R. | 3013630 | 1 | 3:47 | Night | Thursday | 2015 | 4
188 | 2015-04-02 04:22 | 2015-04-02 04:22 | MINAS POWER PLANT |  |  | - | Emergency S/D MGT #7, Due to found: Fire at cooling water Pump-1. (480Volt Main Breaker MGT#7 Trip) Cause: Under investigation. |  | 1 | 4:22 | Morning | Thursday | 2015 | 4
189 | 2015-04-02 09:03 | 2015-04-02 09:03 | 13.8KV 4D FEEDER #5 | Fair | Unidentified | 30 | 09:03 4D fdr #5 load dropped 33A (160-127A). 09:45 It was reported that no power at LOSF & 7 wells were Off. 11:20 Checked & found, Recl. 4D-14A (4D fdr #5) T/SO. Ctr: 31-32. 11:30 Blocked & closed Recl. 4D-14A, Ok. Then released the block. The line is not patrolled yet. | 3013630 | 1 | 9:03 | Morning | Thursday | 2015 | 4
190 | 2015-04-02 09:03 | 2015-11-02 07:28 | 13.8KV 4D FEEDER #5 | Fair | Unidentified | 30 | Patrolled the line, but found nothing. Cause: Unidentified. | 3013630 | 1 | 9:03 | Morning | Thursday | 2015 | 4
191 | 2015-04-02 09:44 | 2015-04-02 09:44 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 09:44 C.Duri fdr #1 load dropped 48A (248-200A). 16:40 It was reported no Power at Well Kulim #16. 17:45 The Recl. 40AW-17 auto reclose when put the ladder at the recloser pole. (Suspected any loose connection part of the recloser control cards) Checked & found, Recl. 40AW-17 (C.Duri fdr #1) T/SO. Ctr: 562-564. Patrolled the line, but found nothing. Cause: Unidentified. | 3013629 | 1 | 9:44 | Morning | Thursday | 2015 | 4
192 | 2015-04-02 12:20 | 2015-04-02 12:20 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 101 | 12:20 Ketigul VCB fdr #2 T/O. (in block position for RIG ACS job at Pagar #01) Checked at the spot of RIG job & found, normal. 12:40 Blocked & closed, Ketigul VCB fdr #2, but failed. (from DSC) 13:30 Checked & found, Ketigul VCB fdr #2 T/SO. Ctr: 147-148 R/F: 51N. 13:50 Blocked & closed Ketigul VCB fdr #2 (from local), Ok. (The Breaker is still in Block for Rig Job at Pagar #01) The line is not patrolled yet. | 3013629 | 1 | 12:20 | Afternoon | Thursday | 2015 | 4
193 | 2015-04-02 12:20 | 2015-07-02 12:05 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 101 | Patrolled the line, but found nothing. Cause: Unidentified. | 3013629 | 1 | 12:20 | Afternoon | Thursday | 2015 | 4
194 | 2015-05-02 12:00 | 2015-05-02 12:00 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Broken Fuse Cut Out | 64 | 12:00 It was reported, no power for Tx o/p #08-M1-13. 21:28 Checked & found, @2 Broken FCO for 112.5Kva Tx & Tx tank leaks o/p #08-M1-13. Cause: Broken FCO. (It would be replaced tomorrow) | 3013629 | 1 | 12:00 | Afternoon | Saturday | 2015 | 5
195 | 2015-05-02 12:00 | 2015-06-02 11:00 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Broken Fuse Cut Out | 64 | Replaced @1,@2,@3 broken FCOs & Energized the Tx o/p #08-M1-13. Cause: Broken Fuse Cut Out. | 3013629 | 1 | 12:00 | Afternoon | Saturday | 2015 | 5
196 | 2015-05-02 17:41 | 2015-05-02 17:41 | CENTRAL DURI POWER PLANT | Fair |  | - | 17:41 CGT #2 Trip. By: DC ground. (when troubleshooting 88FC-3 vibration sensor of water cooling fan) Frequency system dropped to 59.72Hz. (No load shedding) 17:48 Closed ACB #19. (Tie Breaker) Cause: Under Investigation. 18:18 S/U CGT #2, then on line the Unit at 18:45. 18:32 Opened ACB #19. (Tie Breaker) |  | 1 | 17:41 | Afternoon | Saturday | 2015 | 5
197 | 2015-06-02 16:43 | 2015-06-02 16:43 | 13.8KV 4D FEEDER #5 | Fair | Recloser - Control Recloser | 49 | 16:43 4D fdr #5 Load dropped 33A (160-127A). 18:34 Checked & found, Recl. 4D-14A (4D fdr #5) T/SO. Ctr: 32-33. 20:45 Patrolled the line, but found nothing. 21:10 Then replaced Recloser Control. 21:25 Blocked & closed, the Recloser above, but failed to Close. 21:31 Open visual opening of Reloser above, then transfer Load under Recl. 4D-14A to 4D fdr #2. 21:50 By closing LBS #4D-240. Cause: Recloser control problem. | 3013630 | 1 | 16:43 | Afternoon | Tuesday | 2015 | 6
198 | 2015-07-02 07:06 | 2015-07-02 07:06 | 13.8KV MINAS FEEDER #5 | Fair | Unidentified | 8 | Minas ACB fdr #5 T/R 1x Ctr: 75-76 R/F: 51N. Not patrolled yet. | 3013630 | 1 | 7:06 | Morning | Thursday | 2015 | 7
199 | 2015-07-02 07:06 | 2015-10-02 15:41 | 13.8KV MINAS FEEDER #5 | Fair | Unidentified | 8 | Patrolled the line, but found nothing. Cause: Unidentifed. | 3013630 | 1 | 7:06 | Morning | Thursday | 2015 | 7
200 | 2015-07-02 08:00 | 2015-07-02 08:00 | 13.8KV 6D FEEDER #5 | Fair | Transformer Failure | 21 | 08:00 It was reported b/o fuse for Tx at Well #5D-64. 11:00 Checked & found, @1 b/o 3.1SF fuse for 150KVA Tx at Well #5D-64. Perform TTR, Megger test & found, Low megger reading. Cause : Tx failure. (The failure Tx is not Replaced yet) | 3013630 | 1 | 8:00 | Morning | Thursday | 2015 | 7
201 | 2015-07-02 10:47 | 2015-07-02 10:47 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 23 | Sintong fdr #2 load dropped 76A (175-99A). Sintong GFPC T/R 1x. Not checked yet. | 3013629 | 1 | 10:47 | Morning | Thursday | 2015 | 7
202 | 2015-07-02 10:47 | 2015-08-02 07:47 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 23 | Checked & found, Recl. 28AF-02 (Sintong fdr #2) T/R 1x Ctr: 243-244. Patrolled the line & found, a Dead Monkey under TP of Well Benar #07. Cause: Animal. (Monkey) | 3013629 | 1 | 10:47 | Morning | Thursday | 2015 | 7
203 | 2015-07-02 18:11 | 2015-07-02 18:11 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr #1 Load dropped 18A (218-200A) Not checked yet. | 3013629 | 1 | 18:11 | Afternoon | Thursday | 2015 | 7
204 | 2015-07-02 18:11 | 2015-11-02 09:13 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 41AW-17 (C.Duri fdr #1) T/R 1x Ctr: 564-565. Patrolled the line, but found nothing. Cause: Unidentified. | 3013629 | 1 | 18:11 | Afternoon | Thursday | 2015 | 7
205 | 2015-08-02 | 2015-08-02 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 19 | 00:00 It was reported b/o fuse for Tx at Well Puncak #35. 10:39 Checked & found, @1 b/o 3.1SF fuse for 150Kva Tx at Well Puncak #35. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Snake) | 3013629 | 1 | 0:00 | Night | Sunday | 2015 | 8
206 | 2015-08-02 16:02 | 2015-08-02 16:02 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 62 | Sintong OCB fdr #2 T/R 1x. Sintong GFPC did not operate. (In blocked position for Rig Job) Not checked yet. | 3013629 | 1 | 16:02 | Afternoon | Sunday | 2015 | 8
207 | 2015-08-02 16:02 | 2015-09-02 10:30 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 62 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 369-370 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3013629 | 1 | 16:02 | Afternoon | Sunday | 2015 | 8
208 | 2015-09-02 07:23 | 2015-09-02 07:23 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Broken Fuse Cut Out | 0 | C.Duri fdr #1 Load dropped 57A (244-192A). Not checked yet. | 3013629 | 1 | 7:23 | Morning | Wednesday | 2015 | 9
209 | 2015-09-02 07:23 | 2015-11-02 09:23 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Broken Fuse Cut Out | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 3x Ctr: 175-178. Patrolled the line & found, @1 broken FCO for Tx o/p #NN. (near Well Kulin #69) Cause: Broken FCO. | 3013629 | 1 | 7:23 | Morning | Wednesday | 2015 | 9
210 | 2015-09-02 07:58 | 2015-09-02 07:58 | 13.8KV S. BALAM GFPC | Cloudy and Lightning | Lightning | 0 | 07:58 So.Balam GFPC T/R 1x. Ground fault alarm on So.Balam fdr #4. No load dropped at any feeder. 14:15 Checked & found, So.Balam GFPC T/R 2x Ctr: 178-180 R/F: 51N. Patrolled So.Balam fdr #4 line, but found nothing. Cause: Unidentified. (Suspected by Lightning) | 3013629 | 1 | 7:58 | Morning | Wednesday | 2015 | 9
211 | 2015-10-02 23:59 | 2015-10-02 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI power system normal condition. |  | 1 | 23:59 | Night | Friday | 2015 | 10
212 | 2015-11-02 01:50 | 2015-11-02 01:50 | 13.8KV KOTABATAK FEEDER #2 | Fair | Switchboard Problem | 39 | 01:50 It was reported b/o fuse for Tx at Well KB #156. 10:00 Checked & found, @1 b/o 14.0SF fuse for 550Kva Tx at Well KB #156. Replaced b/o fuse above with the same size & energize the Tx. Cause: Switchboard problem. (Vacuum Contactor) | 3013630 | 1 | 1:50 | Night | Monday | 2015 | 11
213 | 2015-12-02 06:20 | 2015-12-02 06:20 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | 06:20 C.Duri ACB fdr #3 T/LO Ctr: 176-180 R/F: 51@1 & 51G. 06:41 Blocked & closed, C.Duri ACB fdr #3, Ok. Then released the block. Not patrolled yet. | 3013629 | 1 | 6:20 | Morning | Wednesday | 2015 | 12
214 | 2015-12-02 06:20 | 16/02/2015 16:31 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3013629 | 1 | 6:20 | Morning | Wednesday | 2015 | 12
215 | 2015-12-02 10:27 | 2015-12-02 10:27 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 33 | 10:27 Opened LBS #16Y-15B, to replace HLC with permanen jumper o/p #16Y-20. (10 Wells were off during the job done) 13:33 Closed LBS #16Y-15B & re-S/U all the wells. Cause: Maintenance Job. | 123 | 1 | 10:27 | Morning | Wednesday | 2015 | 12
216 | 2015-02-13 09:12 | 2015-02-13 09:12 | 13.8KV BEKASAP FEEDER #2 | Fair | Broken Fuse Holder | 17 | 09:12 It was reported b/o fuse for Tx at Well BKS #19. (BKS fdr #2) 11:00 Checked & found, @1,@3 b/o fuse Holder for 300Kva Tx at Well BKS #19. 14:00 Blocked Recl. 37BD-40 (Bekasap fdr #2). 15:50 Replaced b/o fuse Holder above with same size & then Energized the Tx. Then released the block. Cause: Broken Fuse Holder. | 3013629 | 1 | 9:12 | Morning | Friday | 2015 | 2
217 | 2015-02-13 09:45 | 2015-02-13 09:45 | 13.8KV ROKAN FEEDER #2 | Fair | Planned Maintenance | 0 | 09:45 Manual Open Rokan VCB fdr #2, then Opened Line Switch o/p #08-2-05. (Bekasap Production Team Replaced 16" Production Line at Kopar KM-28) 21:23 Closed Line Switches o/p #08-2-05 & closed Rokan VCB fdr #2. (after finishing to replace broken 16" Prod. line) Cause: Plant Maintenance. (For replacing 16" production line) | 123 | 1 | 9:45 | Morning | Friday | 2015 | 2
218 | 2015-02-13 13:23 | 2015-02-13 13:23 | 13.8KV DURI FIELD FEEDER #4 | Fair | Pin Insulator | 0 | Duri Field ACB fdr #4 T/R 1x Ctr: 433-434 R/F: 51@2. Duri Field fdr #1 Load dropped 35A (106-71A). Duri Field fdr #3 Load dropped 39A (158-115A). The line is not patrolled yet. | 3013629 | 1 | 13:23 | Afternoon | Friday | 2015 | 2
219 | 2015-02-13 13:23 | 2015-02-18 08:45 | 13.8KV DURI FIELD FEEDER #4 | Fair | Pin Insulator | 0 | Patrolled the line & found, @2 broken Pin Insulator o/p #07-V1-06. Cause: Pin Insulator. | 3013629 | 1 | 13:23 | Afternoon | Friday | 2015 | 2
220 | 2015-02-14 11:12 | 2015-02-14 11:12 | MINAS POWER PLANT | Fair | Equipment Failure | 44 | 11:12 MGT #9 T/O. By Alarm: Bearing Header Temp. high & Cooling Tower trouble. Cause: 26QT Control Error. (found Short Circuit of control cable for 26QT) Frequency system dropped to 59:57Hz. (Load sheddng level-1) 3D fdr #5 T/O, then Closed at 11:24 4D fdr #3 T/O, then Closed at 11:24 4D fdr #5 T/O, then Closed at 11:25 5B fdr #4 T/O, then Closed at 11:26 5B fdr #5 T/O, then Closed at 11:25 11:53 While waiting for S/U MGT #7, Frequency System drop to 59.82Hz. Asked Minas GS-6 to Shutdown WIP 1 unit at GS-6, and Re-S/U the WIP at 13:18. 12:41 Frequency system dropped again to 59.60Hz. 3D fdr #5 T/O, then Closed at 13:04. 12:20 S/U MGT #7, then on line at 13:04. MGT #9 Status-S/B. (Prior to trobleshooting) Prod. Loss, GS #5 (4D fdr #5 & 4D fdr #3)= 40 Bbls/ 40 Wells. GS #6 (5B fdr #4 & 5B fdr #5)= 40 Bbls/ 40 Wells. Total= 80 Bbls/ 80 Wells. | 3013630 | 1 | 11:12 | Morning | Saturday | 2015 | 2
221 | 2015-02-14 12:20 | 2015-02-14 12:20 | MINAS POWER PLANT |  |  | - | 12:20 S/U MGT #7, then the Unit on line at 13:04. |  | 1 | 12:20 | Afternoon | Saturday | 2015 | 2
222 | 2015-02-14 18:25 | 2015-02-14 18:25 | MINAS POWER PLANT | Fair |  | - | 18:25 S/U MGT #5, then on line the Unit at 18:41. | 123 | 1 | 18:25 | Afternoon | Saturday | 2015 | 2
223 | 2015-02-14 22:50 | 2015-02-14 22:50 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Theft | 0 | 22:50 It was reported spark at Tx jumper of Well KB #180. 00:34 Checked & found, @1, @2, @3 b/o 7.8SF fuses for 300Kva Tx at Well KB #180. (Suspected the Tx jumper was thrown by Outsider, using a piece of wire) Performed TTR & Megger and found, normal. (good reading) Replaced b/o fuses above with the same size, then energized the Tx. Cause: Theft. (also found lost of Reda cable of Well KB #180) | 3013630 | 1 | 22:50 | Night | Saturday | 2015 | 2
224 | 2015-02-15 00:35 | 2015-02-15 00:35 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Theft | 16 | 00:35 It was reported b/o fuse for Tx at Well KB #108. 01:17 Checked & found, @2, @3 b/o 3.5SF fuses for 150Kva Tx at Well KB #108. Also found, Tx primary jumper was thrown by Outsider, using a piece of wire. Performed TTR & Megger Test, found normal. (good reading) Replaced b/o fuses above with the same size, then energized the Tx. Cause: Theft. (also found lost of Reda cable of Well KB #108) | 3013630 | 1 | 0:35 | Night | Sunday | 2015 | 2
225 | 2015-02-15 07:32 | 2015-02-15 07:32 | 13.8KV 5B FEEDER #2 | Fair | Unidentified | 39 | 5B fdr #2 load dropped 71A (192-121A). 5B fdr #3 Load dropped 18A (119-101A). 5B fdr #1 Load dropped 26A (89-63A). 5B fdr #6 Load dropped 188A (190-2A). T/O 3 unit WIPs at GS-6. Not checked yet. | 3013630 | 1 | 7:32 | Morning | Sunday | 2015 | 2
226 | 2015-02-15 07:32 | 2015-02-16 15:01 | 13.8KV 5B FEEDER #2 | Fair | Unidentified | 39 | Checked & found, Recl. 5C-07 (5B fdr #2) T/R 1x Ctr: Not read. Patrolled the line, but found nothing. Cause: Unidentified. | 3013630 | 1 | 7:32 | Morning | Sunday | 2015 | 2
227 | 2015-02-15 13:21 | 2015-02-15 13:21 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Theft | 25 | It was reported b/o fuse for Tx at Well KB #196. (CKBS fdr #1) Checked & found, @2,@3 b/o 7.8SF fuses for 300Kva Tx at Well KB #196. Also found, Tx Primary jumper was thrown by Outsider, using a piece of wire. And also found, lost of Reda cable from junction box toward wellhead of well KB #196. Then replaced b/o fuse above with the same size, then Energiged the Tx. Cause: Theft. | 3013630 | 1 | 13:21 | Afternoon | Sunday | 2015 | 2
228 | 2015-02-16 14:00 | 2015-02-16 14:00 | 13.8KV BEKASAP FEEDER #3 | Fair | Animal | 41 | 14:00 It was reported b/o fuse for Tx at Well Bekasap #65. (BKS fdr #3) 15:00 Checked & found, @2,@3 b/o 7.0SF fuses for 225Kva Tx at Well Bekasap #65. Replaced b/o fuse above with same size & energized the Tx. Cause: Animal. (Squirrel) | 3013629 | 1 | 14:00 | Afternoon | Monday | 2015 | 2
229 | 2015-02-16 16:00 | 2015-02-16 16:00 | 13.8KV 8D FEEDER #7 | Fair | ESP Failure | 0 | 16:00 It was reported b/o fuse for Tx at Well #7E-91N. (8D fdr #7) 17:20 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well #7E-91N. Replaced b/o fuse above with same size & energized the Tx. Cause: ESP failure. (Reda HI Amps) | 3013630 | 1 | 16:00 | Afternoon | Monday | 2015 | 2
230 | 2015-02-16 21:18 | 2015-02-16 21:18 | 13.8KV BATANG FEEDER #3 | Fair | Animal | 57 | It was reported b/o fuse for Tx at well Pemburu #16 (Btg fdr #3). Not checked yet. | 3013629 | 1 | 21:18 | Night | Monday | 2015 | 2
231 | 2015-02-16 21:18 | 2015-02-17 01:00 | 13.8KV BATANG FEEDER #3 | Fair | Animal | 57 | Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Pemburu #16. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Squirrel) | 3013629 | 1 | 21:18 | Night | Monday | 2015 | 2
232 | 2015-02-17 08:08 | 2015-02-17 08:08 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified | 21 | CKBS VCB fdr #1 T/R 1x. Not checked yet. | 3013630 | 1 | 8:08 | Morning | Tuesday | 2015 | 2
233 | 2015-02-17 08:08 | 2015-02-18 13:08 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified | 21 | Checked & found, CKBS VCB fdr #1 T/R 1x Ctr: 173-174 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3013630 | 1 | 8:08 | Morning | Tuesday | 2015 | 2
234 | 2015-02-17 10:02 | 2015-02-17 10:02 | MINAS POWER PLANT |  |  | - | 10:02 S/U MGT #9, then on line the Unit at 10:30. |  | 1 | 10:02 | Morning | Tuesday | 2015 | 2
235 | 2015-02-17 14:43 | 2015-02-17 14:43 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 0 | OKB fdr #2 load dropped 185A (325-140A). Not checked yet. | 3013630 | 1 | 14:43 | Afternoon | Tuesday | 2015 | 2
236 | 2015-02-17 14:43 | 2015-02-18 07:39 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recl. 38CX-25 (OKB fdr #2) T/R 1x Ctr: 86-87. Patrolled the line, but found nothing. Cause: Unidentified. | 3013630 | 1 | 14:43 | Afternoon | Tuesday | 2015 | 2
237 | 2015-02-17 15:30 | 2015-02-17 15:30 | MINAS POWER PLANT |  |  | - | Off line MGT #6, then S/D the Unit for S/B. |  | 1 | 15:30 | Afternoon | Tuesday | 2015 | 2
238 | 2015-02-17 17:54 | 2015-02-17 17:54 | 13.8KV PETAPAHAN FEEDER #2 | Rain and Lightning | Lightning | 436 | Petapahan OCB fdr #2 T/R 1x. Petapahan fdr #1 load dropped 52A (80-28A). Not checked yet. | 3013630 | 1 | 17:54 | Afternoon | Tuesday | 2015 | 2
239 | 2015-02-17 17:54 | 2015-02-18 13:23 | 13.8KV PETAPAHAN FEEDER #2 | Rain and Lightning | Lightning | 436 | Checked & found, Petapahan OCB fdr #2 T/R 1x Ctr: 354-355 R/F: 51@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3013630 | 1 | 17:54 | Afternoon | Tuesday | 2015 | 2
240 | 2015-02-17 23:25 | 2015-02-17 23:25 | 13.8KV 6DN FEEDER #6 | Fair | Low mega-ohm reading | 0 | It was reported b/o fuse for Tx at Well #6E-23. (6DN fdr #6) Not checked yet. | 3013630 | 1 | 23:25 | Night | Tuesday | 2015 | 2
241 | 2015-02-17 23:25 | 2015-02-18 10:00 | 13.8KV 6DN FEEDER #6 | Fair | Low mega-ohm reading | 0 | 10:00 Checked & found, @1, @2 b/o 7.8SF fuses for 300Kva Tx at Well #6E-23. (6DN fdr #6) Tested TTR, Megger the Tx & found, Low Megger reading. 16:40 Replaced 300Kva Tx low megger with same size & energized the Tx. Cause: Low Megger reading Tx. | 3013630 | 1 | 23:25 | Night | Tuesday | 2015 | 2
242 | 2015-02-18 09:00 | 2015-02-18 09:00 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 09:00 It was reported that b/o fuses for Tx o/p #SD-03A. (D.C fdr #5) 10:00 Checked & found, @1, @2 b/o 7.8SF fuses for 300Kva Tx o/p #SD-03A. Replaced the b/o fuses with same size & energized the Tx. Caused: Unidentified (fuse). | 3013629 | 1 | 9:00 | Morning | Wednesday | 2015 | 2
243 | 2015-02-18 10:30 | 2015-02-18 10:30 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 43 | 10:30 It was reported b/o fuse for Tx at Well So.Balam #132. 11:50 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well So.Balam #132. Replaced the b/o fuse above with same size & energized the Tx. Cause: Animal. (Monkey) | 3013629 | 1 | 10:30 | Morning | Wednesday | 2015 | 2
244 | 2015-02-18 10:44 | 2015-02-18 10:44 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 121 | 10:44 C.Duri ACB fdr #1 T/LO. Ctr: 172-176 R/F: 51@1,@2 & 51G. Patrolled the line, but nothing found. 11:39 Blocked & closed C.Duri ACB fdr #1, Ok. the released the block. Cause: Suspected by Animal. (Monkey) | 3013629 | 1 | 10:44 | Morning | Wednesday | 2015 | 2
245 | 2015-02-18 16:01 | 2015-02-18 16:01 | 115KV NELLA SW. STA - PINANG LINE | Heavy Rain | Relay Failure | 404 | 16:01 115KV Nella GCB #27 (line to Pinang) T/O. 17:30 Checked & found, Nella GCB #27 (line to Pinang) T/SO. Ctr: 155-156 R/F: was Disabled. 18:11 Blocked & closed 115KV Nella GCB #27, Ok. Then released the block. 18:15 Blocked & closed 13.8KV Pinang VCB #1, Ok. Then released the block. 18:24 Manually Opened 115KV Nella GCB #27. (due to hissing sound at 13.8KV Pinang Breaker fdr #1) Then Bypassed 13.8KV Pinang Breaker fdr #1. 19:30 Blocked & closed 115KV Nella GCB #27, Ok. Then released the block. 19:31 It was reported that @2 b/o Bypass fuse of 13.8KV Pinang VCB fdr #1. Re-Open 115KV Nella GCB #27, to open Bypass switch of 13.8KV Pinang fdr #1. 20:08 Blocked & closed 115 KV GCB #27, Ok. Then blocked & closed 13.8KV Pinang VCB fdr #1. 20:10 115KV Nella GCB #27 T/O again. Patrolled Pinang fdr #1 line, but found nothing. 22:56 Blocked & closed 115KV Nella GCB #27, Ok. Then released the block. Adjusted Pinang Buss Voltage to 13.9KV from 14.4KV. (VR LTC position found on Raise-16, then lowered it to Raise-14) 23:09 Blocked & closed 13.8KV Pinang VCB fdr #1, Ok. Then released the block. Cause: Relay failure. (Relay for 115KV Nella - Pinang line failure) | 3013629 | 1 | 16:01 | Afternoon | Wednesday | 2015 | 2
246 | 2015-02-19 06:28 | 2015-02-19 06:28 | 13.8KV CENTRAL DURI FEEDER #9 | Heavy Rain | Animal | 25 | 06:28 C.Duri ACB fdr #1 load dropped 47A (148-101A). 09:08 Checked & found, Recl. 04-05-02 (C.Duri fdr #9) T/SO. Ctr: 162-163. (On block position) Patrolled the line, but nothing found. Blocked & closed Recl. 04-05-02, Ok. Then released the block. Cause: Suspected by Animal. (Monkey) | 301329 | 1 | 6:28 | Morning | Thursday | 2015 | 2
247 | 2015-02-19 06:43 | 2015-02-19 06:43 | 13.8KV KOTABATAK FEEDER #2 | Fair | Guy Wire | 150 | 06:43 OKB fdr #2 load dropped 176A (325-149A). 08:10 Checked & found, Recl. 38CW-08 (OKB fdr #2) T/LO. Ctr: 13-18. Patrolled the line & found, broken Guy wire & touching to power line o/p #38CX-38. 09:20 Blocked & closed Recl. 38CW-08, Ok. Then released the block. (After isolating the broken Guy wire above) Cause: Guy wire. | 3013630 | 1 | 6:43 | Morning | Thursday | 2015 | 2
248 | 2015-02-19 08:38 | 2015-02-19 08:38 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 0 | 08:38 It was reported b/o fuses for Tx o/p #05-M5-14. 10:00 Checked & foumd, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #05-M5-14. Replaced b/o fuse above with same size & energized the Tx. Cause: Animal. (Monkey) | 3013629 | 1 | 8:38 | Morning | Thursday | 2015 | 2
249 | 2015-02-19 12:45 | 2015-02-19 12:45 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Low mega-ohm reading | 11 | 12:45 It was reported b/o fuse for Tx o/p #04-7-02. (C.Duri fdr #9) 15:15 Checked & found, @1, @3 3.1SF fuses for 112.5Kva Tx o/p #04-7-02. Tested TTR, Megger the Tx & found Low Megger reading. Cause: Tx Low Megger. (The Tx is not replaced yet) | 3013629 | 1 | 12:45 | Afternoon | Thursday | 2015 | 2
250 | 2015-02-19 12:45 | 2015-02-20 16:22 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Low mega-ohm reading | 11 | Replaced Low megger 112.5Kva Tx with the same size & energized the Tx. Cause: Tx Low Megger reading. | 3013629 | 1 | 12:45 | Afternoon | Thursday | 2015 | 2
251 | 2015-02-20 15:40 | 2015-02-20 15:40 | MINAS POWER PLANT |  |  | - | 15:40 S/U MGT #6, then On line the Unit at 16:15. |  | 1 | 15:40 | Afternoon | Friday | 2015 | 2
252 | 2015-02-20 | 2015-02-21 02:59 | SURAM SUBSTATION | Fair | Animal | 9 | 02:59 It was reported no power at Kasikan field (reportedby Mr Gofar BOB). Suram RTU was Failed. 04:07 Checked & found, 115KV Suram Circuit Switcher T/O By R/F: 51G Ctr: 211-212. 04:23 Opened 13.8KV Suram OCB fdr #1. Opened 13.8KV Suram OCB fdr #2. 04:49 Closed 115KV Suram C/S ---> OK. 04:51 Blocked & Closed 13.8 KV OCB fdr #1, Ok. Then released the Block. 04:52 Blocked & Closed 13.8 KV OCB fdr #2, Ok. Then released the Block. 13:57 Re-Checked & found, @1 F/O Pin support Buss on Structure on the Suram OCB fdr #2. Cause: Suspected by Animal. (Bird) | 3013630 | 1 | 0:00 | Night | Friday | 2015 | 2
253 | 2015-02-21 08:06 | 2015-02-21 08:06 | 13.8KV KETIGUL FEEDER#1 | Fair | Lightning Arrester | 33 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3013629 | 1 | 8:06 | Morning | Saturday | 2015 | 2
254 | 2015-02-21 08:06 | 2015-02-24 15:29 | 13.8KV KETIGUL FEEDER#1 | Fair | Lightning Arrester | 33 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 141-142 R/F: 51N(@1). Patrolled the line & found, @1 broken L/A o/p #33AJ-11. Cause: Lightning Arrester. | 3013629 | 1 | 8:06 | Morning | Saturday | 2015 | 2
255 | 2015-02-22 13:25 | 2015-02-22 13:25 | 13.8KV SINTONG FEEDER #2 | Fair | Theft | 0 | 13:25 It was reported TX vandalism at Well Benar #34. (Sintong fdr #2) 14:30 Checked & found, Broken 225KVA TX at Well Benar #34. Not Replaced Yet. | 3013629 | 1 | 13:25 | Afternoon | Sunday | 2015 | 2
256 | 2015-02-22 13:25 | 2015-02-23 10:00 | 13.8KV SINTONG FEEDER #2 | Fair | Theft | 0 | Replaced 225Kva Tx with 300Kva Tx at Well Benar #34, then energized the Tx. Cause: Theft. | 3013629 | 1 | 13:25 | Afternoon | Sunday | 2015 | 2
257 | 2015-02-22 14:49 | 2015-02-22 14:49 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 41 | Bangko OCB fdr #4 T/R 1x. Ground fault alarm on Bangko fdr #4. Not checked yet. | 3013269 | 1 | 14:49 | Afternoon | Sunday | 2015 | 2
258 | 2015-02-22 14:49 | 2015-02-23 07:15 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 41 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99953-99954 R/F: 51@3. The line is not patrolled yet. | 3013269 | 1 | 14:49 | Afternoon | Sunday | 2015 | 2
259 | 2015-02-22 14:49 | 2015-02-25 14:49 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 41 | Patrolled Bangko fdr #4 line & found: -@3 Broken (45%) Pin Insulator o/p #24Z-12. -@1 Broken (60%) Pin Insulator o/p #25Y-18. -@1 Broken (30%) Pin Insulator o/p #25A-17A. -@3 Broken (10%) Pin Insulator o/p #24Z-31. Cause: Lightning. | 3013269 | 1 | 14:49 | Afternoon | Sunday | 2015 | 2
260 | 2015-02-23 01:01 | 2015-02-23 01:01 | 13.8KV BANGKO GFPC | Cloudy and Lightning | Lightning | 0 | 01:01 Bangko GFPC T/SO . Fault alarm on Bangko fdr #4. (No load dropped at any feeders) 07:15 Checked & found, Bangko GFPC T/SO. Ctr: 445-446 R/F: 50N. Then closed Bangko GFPC from DSC, Ok. Line Bangko fdr #4 is not patrolled yet. | 3013629 | 1 | 1:01 | Night | Monday | 2015 | 2
261 | 2015-02-23 01:01 | 2015-02-25 18:00 | 13.8KV BANGKO GFPC | Cloudy and Lightning | Lightning | 0 | Checked & found, Bangko GFPC T/SO. Ctr: 445-446. Patrolled Bangko fdr #4 line & found: -@3 Broken (45%) Pin Insulator o/p #24Z-12. -@1 Broken (60%) Pin Insulator o/p #25Y-18. -@1 Broken (30%) Pin Insulator o/p #25A-17A. -@3 Broken (10%) Pin Insulator o/p #24Z-31. Cause: Lightning. | 3013629 | 1 | 1:01 | Night | Monday | 2015 | 2
262 | 2015-02-23 12:25 | 2015-02-23 12:25 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 54 | Sintong OCB fdr #2 T/R 1x. Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #2) Not checked yet. | 3013629 | 1 | 12:25 | Afternoon | Monday | 2015 | 2
263 | 2015-02-23 12:25 | 2015-02-25 08:45 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 54 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 370-371 R/F: 51N. Also found, Sintong GFPC T/R 2x Ctr: 713-715 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3013629 | 1 | 12:25 | Afternoon | Monday | 2015 | 2
264 | 2015-02-23 13:59 | 2015-02-23 13:59 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Animal | 3 | 13:59 It was reported b/o fuse for Tx o/p #SC-4-T6. 15:00 Checked & found @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #SC-4-T6. Replaced the b/o fuse with same size & energized the Tx. Cause: Animal. (Monkey) | 3013629 | 1 | 13:59 | Afternoon | Monday | 2015 | 2
265 | 2015-02-23 17:41 | 2015-02-23 17:41 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 20 | 17:41 5B fdr #4 Load dropped 231A (331-100A). 17:50 5B fdr #4 Load dropped 119A (321-212A). (Prod loss 30 Bbls, 26 wells). Not checked yet. | 3013630 | 1 | 17:41 | Afternoon | Monday | 2015 | 2
266 | 2015-02-23 17:41 | 2015-02-26 17:41 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 20 | Checked & found, Recl. 4B-73 (5B fdr #4) T/R 2x Ctr: 23-25. Patrolled the line & found: -@2 Broken L/A o/p #3B-40F. -High Trees near poles #4B-77, #KN-28 & #4B-137. Cause: Lightning. | 3013630 | 1 | 17:41 | Afternoon | Monday | 2015 | 2
267 | 2015-02-23 17:43 | 2015-02-23 17:43 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 40 | 17:43 4B fdr #1 Load dropped 148A (345-197A). 21:24 Checked & found, Recl. 4B-101 (4B fdr #1) T/SO. Ctr: Did not changed. 21:50 Blocked & closed Recl. 4B-101, Ok. Then released the block. The line is not patrolled yet. | 3013630 | 1 | 17:43 | Afternoon | Monday | 2015 | 2
268 | 2015-02-23 17:43 | 2015-02-25 17:43 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 40 | Patrolled the line & found: -@1 broken L/A of LBS o/p #4B-150. -High Trees & touching power line between poles #4A-51 & #4A-53. Cause: Lightning. | 3013630 | 1 | 17:43 | Afternoon | Monday | 2015 | 2
269 | 2015-02-23 17:47 | 2015-02-23 17:47 | 13.8KV 3D FEEDER #5 | Rain and Lightning | Lightning | 67 | 3D OCB fdr #5 T/R 1x. 3D fdr #2 Load dropped 179A (244-65A). (Prod. loss = 55 Bbls / 26 Wells) 3D fdr #3 Load dropped 130A (168-38A). (Prod. loss = 46 Bbls / 32 Wells) Not checked yet. | 3013630 | 1 | 17:47 | Afternoon | Monday | 2015 | 2
270 | 2015-02-23 17:47 | 2015-02-25 17:47 | 13.8KV 3D FEEDER #5 | Rain and Lightning | Lightning | 67 | Checked & found, 3D OCB fdr #5 T/R 7x Ctr: 196-203 R/F: 51@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3013630 | 1 | 17:47 | Afternoon | Monday | 2015 | 2
271 | 2015-02-23 17:48 | 2015-02-23 17:48 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 41 | 3D OCB fdr #4 T/R 1x. Not checked yet. | 3013630 | 1 | 17:48 | Afternoon | Monday | 2015 | 2
272 | 2015-02-23 17:48 | 2015-02-25 17:48 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 41 | Checked & found, 3D OCB fdr #4 T/R 1x Ctr: 149-150 R/F: 51@1,@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3013630 | 1 | 17:48 | Afternoon | Monday | 2015 | 2
273 | 2015-02-23 17:50 | 2015-02-23 17:50 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 131 | 5B fdr #1 Load dropped 77A (100-23A). (Prod loss 30 Bbls, 15 wells). 5B fdr #3 Load dropped 120A (122-2A). (Prod loss 71 Bbls, 10 wells). 5B fdr #6 Load dropped 120A (189-69A). T/O WIP at GS-4. Not checked yet. | 3013630 | 1 | 17:50 | Afternoon | Monday | 2015 | 2
274 | 2015-02-23 17:50 | 2015-03-03 17:50 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 131 | Checked & found, Recl. 5B-06 (5B fdr #1) T/R 1x Ctr: not reported yet. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3013630 | 1 | 17:50 | Afternoon | Monday | 2015 | 2
275 | 2015-02-23 17:50 | 2015-02-23 17:50 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Tree | 3 | 4B fdr #2 Load dropped 80A (130-50A). (Prod loss 25Bbls, 21 wells). 4B fdr #3 Load dropped 130A (132-2A). (WIP). Not checked yet. | 3013630 | 1 | 17:50 | Afternoon | Monday | 2015 | 2
276 | 2015-02-23 17:50 | 2015-02-25 15:50 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Tree | 3 | Checked & found, Recl. 5B-93 (4B fdr #2) T/R 1x Ctr: 92-93. Patrolled the line & found, High Trees under power line at near pole #4B-52 & #4B-43. Cause: Tree. | 3013630 | 1 | 17:50 | Afternoon | Monday | 2015 | 2
277 | 2015-02-23 17:51 | 2015-02-23 17:51 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 58 | 4B OCB fdr #1 T/R 1x. Not checked yet. | 3013630 | 1 | 17:51 | Afternoon | Monday | 2015 | 2
278 | 2015-02-23 17:51 | 2015-02-25 17:51 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 58 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 239-240 R/F: 51@1. Patrolled the line & found: -@1 Bropken Dead end Insulator o/p #4B-92. -@1 Broken Dead end Insulator on the Structure 3D Subst. Cause: Lightning. | 3013630 | 1 | 17:51 | Afternoon | Monday | 2015 | 2
279 | 2015-02-23 17:58 | 2015-02-23 17:58 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 128 | 17:58 6D OCB fdr #1 T/R 1x. 18:04 6D OCB fdr #1 T/R 1x again. Not checked yet. | 3013630 | 1 | 17:58 | Afternoon | Monday | 2015 | 2
280 | 2015-02-23 17:58 | 2015-02-24 17:58 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 128 | Checked & found, 6D OCB fdr #1 T/R 2x Ctr: 284-286 R/F: 51@1,@2. Patrolled the line & found: -@1 Broken Dead end Insulator o/p #5C-44. -@1 Broken L/A on TP of Well #6B-27A. -@1,@2 Broken L/As on TP of Well #5B-69. -@1 Broken Dead end Insulator o/p #NN. (near Well #5C-83) -High palm Trees between poles #5C-67 and #5C-68. -High Trees & touching to power line near Well #5C-89. -High Trees near pole #5B-171. Cause: Lightning. | 3013630 | 1 | 17:58 | Afternoon | Monday | 2015 | 2
281 | 2015-02-23 17:58 | 2015-02-23 17:58 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Unidentified | 22 | 6D fdr #2 Load dropped 94A (194-100A). (Prod loss 22 Bbls, 12 wells). 6D fdr #3 Load dropped 42A (128-86A). T/O WIP at GS-3. Not checked yet. | 3013630 | 1 | 17:58 | Afternoon | Monday | 2015 | 2
282 | 2015-02-23 17:58 | 2015-02-25 17:58 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Unidentified | 22 | Checked 2 Reclosers at downstream of 6D fdr #2 & found, normal. (Ctr: Did not change) Patrolled the line, but found nothing. Cause: Unidentified. (Suspected some wells were down due to voltage dip when 6D OCB fdr #1 T/R) | 3013630 | 1 | 17:58 | Afternoon | Monday | 2015 | 2
283 | 2015-02-23 18:01 | 2015-02-23 18:01 | 13.8KV 3D TX-1 GFPC | Rain and Lightning | Tree | 0 | 3D GFPC-Tx #1 T/R 1x. (Ground fault alarm on 3D fdr #3) Not checked yat. | 3013630 | 1 | 18:01 | Afternoon | Monday | 2015 | 2
284 | 2015-02-23 18:01 | 2015-02-25 18:01 | 13.8KV 3D TX-1 GFPC | Rain and Lightning | Tree | 0 | Checked & found, 3D GFPC-TX #1 T/R 3x Ctr: 4044-4047. Patrolled 3D fdr #3 line & found: -High Trees under power line near pole #3D-147. -High Trees under power line near pole #4C-157. Cause: Tree. | 3013630 | 1 | 18:01 | Afternoon | Monday | 2015 | 2
285 | 2015-02-23 22:30 | 2015-02-23 22:30 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 0 | 22:30 It was reported that no power at downstream of Recl. 5C-42 (6D fdr #1). Checked & found, Recl. 5C-42 (6D fdr #1) T/LO. Last Ctr: 16. 23:00 Blocked & Closed Recl. 5C-42, Ok. Then released the Block. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3013630 | 1 | 22:30 | Night | Monday | 2015 | 2
286 | 2015-02-24 11:00 | 2015-02-24 11:00 | 13.8KV 8D FEEDER #1 | Fair | Transformer Failure | 8 | 11:00 It was reported b/o fuse for Tx at Well #9E-12. 11:30 Checked & found, @1, @2 b/o 3.5SF fuses for 150Kva Tx at Well #9E-12. Performed Megger, TTR test the Tx & found, Unbalance TTR & Low megger reading. Cause: The Tx failure. (The Tx will be replaced tomorrow) | 3013630 | 1 | 11:00 | Morning | Tuesday | 2015 | 2
287 | 2015-02-24 11:00 | 2015-02-25 10:49 | 13.8KV 8D FEEDER #1 | Fair | Transformer Failure | 8 | Repalced Transformer low megger 150Kva Tx with the same size & energized the Tx. Cause: Transformer low megger reading. | 3013630 | 1 | 11:00 | Morning | Tuesday | 2015 | 2
288 | 2015-02-25 06:19 | 2015-02-25 06:19 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Animal | 0 | Duri Community ACB fdr #2 T/R 1x. Not checked yet. | 3013629 | 1 | 6:19 | Morning | Wednesday | 2015 | 2
289 | 2015-02-25 06:19 | 2015-02-28 11:37 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Animal | 0 | Checked & found, Duri Community ACB fdr #2 T/R 1x Ctr: 46-47 R/F: 51N(@1). Patrolled the line & found, a Dead Squirrel near Transformer at Duri WTP. Cause: Animal. (Squirrel) | 3013629 | 1 | 6:19 | Morning | Wednesday | 2015 | 2
290 | 2015-02-25 15:08 | 2015-02-25 15:08 | 13.8KV 3D FEEDER #2 | Fair | Tree | 42 | 3D OCB fdr #2 T/R 1x. 3D fdr #3 load dropped 27A (173-146A). 3D fdr #4 load dropped 44A (281-237A). Not checked yet. | 3013630 | 1 | 15:08 | Afternoon | Wednesday | 2015 | 2
291 | 2015-02-25 15:08 | 2015-02-28 15:08 | 13.8KV 3D FEEDER #2 | Fair | Tree | 42 | Checked & found, 3D OCB fdr #2 T/R 1x Ctr: 482-483 R/F: 51@2. Patrolled the line & found: -High Trees & touching to power line near poles #3E-13, #3E-58 & #3E-06. Cause: Tree. | 3013630 | 1 | 15:08 | Afternoon | Wednesday | 2015 | 2
292 | 2015-02-25 16:12 | 2015-02-25 16:12 | 13.8KV MENGGALA FEEDER #2 | Heavy Rain | Lightning | 19 | Menggala fdr #2 load dropped 25A (88-63A). Menggala GFPC T/R 1x. (Fault alarm on Menggala fdr #2) Not checked yet. | 3013629 | 1 | 16:12 | Afternoon | Wednesday | 2015 | 2
293 | 2015-02-25 16:12 | 2015-02-28 08:12 | 13.8KV MENGGALA FEEDER #2 | Heavy Rain | Lightning | 19 | Checked & found, Recl. 27AL-21 (Menggala fdr #2) T/R 1x Ctr: 107-108. Also found, Menggala GFPC T/R 2x Ctr: 1085-1087. Patrolled the line & found, @3 broken L/A on TP of Well Sikladi #20. Cause: Lightning. | 3013629 | 1 | 16:12 | Afternoon | Wednesday | 2015 | 2
294 | 2015-02-25 16:30 | 2015-02-25 16:30 | 13.8KV 6D FEEDER #3 | Cloudy and Lightning | Lightning | 66 | 6D OCB fdr #3 T/R 1x. 6D fdr #1 Load dropped 276A (351-75A). 6D fdr #2 Load dropped 156A (192-36A). Not checked yet. | 3013630 | 1 | 16:30 | Afternoon | Wednesday | 2015 | 2
295 | 2015-02-25 16:30 | 2015-02-28 16:30 | 13.8KV 6D FEEDER #3 | Cloudy and Lightning | Lightning | 66 | Checked & found, 6D OCB fdr #3 T/R 1x Ctr: 211. (Did not checnge) R/F: 51@1,@2. Patrolled the line, but found nothing. Also found, Recl. 6D-03 (6D fdr #3) T/R 1x Ctr: 49-50. Patrolled the line & found, @2 F/O Pin Insulator o/p #6D-04. Cause: Lightning. | 3013630 | 1 | 16:30 | Afternoon | Wednesday | 2015 | 2
296 | 2015-02-26 10:15 | 2015-02-26 10:15 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 10:15 It was reported that b/o fuse for Tx o/p #08-M1-34. 11:27 Checked & found, @2 b/o 2.1SF fuse for 112.5KVA Tx o/p #08-M1-34. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3013629 | 1 | 10:15 | Morning | Thursday | 2015 | 2
297 | 2015-02-26 10:45 | 2015-02-26 10:45 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 2 | 10:45 It was reported that b/o fuse for Tx o/p #13-F6-17. 11:50 Checked & found, @2 b/o 2.1SF fuse for 112.5KVA Tx o/p #13-F6-17. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3013629 | 1 | 10:45 | Morning | Thursday | 2015 | 2
298 | 2015-02-26 17:38 | 2015-02-26 17:38 | 13.8KV SINTONG GFPC | Fair | Capasitor Bank | 0 | Sintong GFPC T/R 1x. Ground fault alarm at Sintong fdr #2. (No load dropped at any feeders) Not checked yet. | 3013629 | 1 | 17:38 | Afternoon | Thursday | 2015 | 2
299 | 2015-02-26 17:38 | 2015-02-28 08:38 | 13.8KV SINTONG GFPC | Fair | Capasitor Bank | 0 | Checked & found, Sintong GFPC T/R 2x Ctr: 715-717. Patrolled Sintong fdr #2 line & found, @1 b/o fuse of Cap Bank on TP at OBS Well Sintong #02. Cause: Capacitor Bank. | 3013629 | 1 | 17:38 | Afternoon | Thursday | 2015 | 2
300 | 2015-02-27 08:56 | 2015-02-27 08:56 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Pin Insulator | 0 | Duri Community ACB fdr #2 T/R 1x. Not checked yet. | 3013629 | 1 | 8:56 | Morning | Friday | 2015 | 2
301 | 2015-02-27 08:56 | 2015-02-03 15:32 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Pin Insulator | 0 | Checked & found, Duri Community ACB fdr #2 T/R 1x Ctr: 64-65 R/F: 51N(@2). Patrolled the line & found, @2 broken Pin Insulator o/p #2F-15-9. Cause: Pin Insulator. | 3013629 | 1 | 8:56 | Morning | Friday | 2015 | 2
302 | 2015-02-28 23:55 | 2015-02-28 23:55 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI power system normal condition & normal operation. |  | 1 | 23:55 | Night | Saturday | 2015 | 2
303 | 2015-01-03 10:10 | 2015-01-03 10:10 | 13.8KV S. BALAM FEEDER #1 | Fair | Theft | 0 | It was reported secondary cable cut by thieves at wells: 1. Balam #173 well OFF status No fluida support (Tx has been taken to Bangko TDO). 2. Balam #314 well OFF status No pumping (Tx will be taken tomorrow). 3. Balam #150 well OFF status Long Time Close (Tx will be taken tomorrow). No Production loss. Cause: Vandalism. | 3026922 | 1 | 10:10 | Morning | Saturday | 2015 | 1
304 | 2015-01-03 15:00 | 2015-01-03 15:00 | 13.8KV 4D FEEDER #4 | Fair | Animal | 5 | 15:00 It was reported that b/o fuse for 300Kva Tx at Well #4E 52R. 17:30 Checked & found, @1,@2 b/o 15K fuses for 300KVA Tx at Well #4E 52R. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Chicken) | 3026923 | 1 | 15:00 | Afternoon | Saturday | 2015 | 1
305 | 2015-01-03 16:30 | 2015-01-03 16:30 | 13.8KV MINAS FEEDER #3 | Fair | Transformer Failure | 53 | 16:30 It was reported b/o fuse link for Tx at Well #7D-93. 19:00 Checked & found, @1, @3 b/o 7.8SF fuses for 250Kva Tx. Perform TTR, Megger test & found, Low megger reading. Cause: Tx failure. (The failure Tx is not replaced yet) | 3026923 | 1 | 16:30 | Afternoon | Saturday | 2015 | 1
306 | 2015-01-03 16:30 | 2015-03-03 16:30 | 13.8KV MINAS FEEDER #3 | Fair | Transformer Failure | 53 | Replaced low megger 250Kva Tx with the same size & energized the Tx. Cause: Tx failure. (Low megger reading) | 3026923 | 1 | 16:30 | Afternoon | Saturday | 2015 | 1
307 | 2015-02-03 08:00 | 2015-02-03 08:00 | DURI POWER PLANT |  |  | - | 08:00 S/U DGT #7, then on line the Unit at 08:30. |  | 1 | 8:00 | Morning | Tuesday | 2015 | 2
308 | 2015-02-03 09:10 | 2015-02-03 09:10 | CENTRAL DURI POWER PLANT |  |  | - | 09:10 Off line CGT #3, then S/D the Unit for S/B. (Prior to closing Gouletine of HRSG) 16:18 S/U CGT #3, then on line the Unit at 16:38. |  | 1 | 9:10 | Morning | Tuesday | 2015 | 2
309 | 2015-02-03 10:27 | 2015-02-03 10:27 | 13.8KV 6D FEEDER #2 | Fair | Tree | 23 | 10:27 6D fdr #2 Load dropped 113A (192-79A). 11:26 Checked & found, Recl. 6D-298 (6D fdr #2) T/LO. Ctr: 28-31. Patrolled the line & found, Vilager triming hight trees near pole #7C-37. 11:30 Blocked & closed Recl. 6D-298, Ok. Then release the block. Cause: Trees. | 3026923 | 1 | 10:27 | Morning | Tuesday | 2015 | 2
310 | 2015-02-03 13:22 | 2015-02-03 13:22 | CENTRAL DURI POWER PLANT | Rain | Equipment Failure | 0 | 13:22 CGT #1 Tripped By Alarm: Generator Lock Out Trip. Cause: Equipment failure. (Electronic over speed control failure) 13:31 Closed ACB #19. (Tie breaker) 17:06 S/U CGT #1, then on line the Unit at 17:32. 17:30 Opened ACB #19. (Tie breaker) | 3026922 | 1 | 13:22 | Afternoon | Tuesday | 2015 | 2
311 | 2015-02-03 15:38 | 2015-02-03 15:38 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 57 | Sintong OCB fdr #2 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. | 3026922 | 1 | 15:38 | Afternoon | Tuesday | 2015 | 2
312 | 2015-02-03 15:38 | 2015-04-03 15:38 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 57 | Checked & found, Sintong VCB fdr #2 T/R 1x Ctr: 371-372 R/F: 51N. Also found, Sintong GFPC T/R 1x Ctr: 717-718. Patrolled the line, but found nothing. Cause: Lightning. | 3026922 | 1 | 15:38 | Afternoon | Tuesday | 2015 | 2
313 | 2015-02-03 16:45 | 2015-02-03 16:45 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Unidentified | 0 | C.Duri ACB fdr #16 T/R 1x. Not checked yet. | 3026922 | 1 | 16:45 | Afternoon | Tuesday | 2015 | 2
314 | 2015-02-03 16:45 | 2015-03-03 16:45 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Unidentified | 0 | Checked & found, C.Duri ACB fdr #16 T/R 1x Ctr: 278-279 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3026922 | 1 | 16:45 | Afternoon | Tuesday | 2015 | 2
315 | 2015-02-03 18:40 | 2015-02-03 18:40 | 13.8KV MENGGALA FEEDER #2 | Fair | Unidentified (Fuse) | 15 | 18:40 It was reported b/o fuse for Tx at Well Sekladi #23. 20:30 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Sekladi #23. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3026922 | 1 | 18:40 | Afternoon | Tuesday | 2015 | 2
316 | 2015-03-03 13:55 | 2015-03-03 13:55 | NORTH DURI POWER PLANT | Fair | Equipment Failure | 570 | 13:55 NDC #3 Tripped By Alarm: Generator Breaker Lock out (86-1). Cause: Equipment failure. (MW Transducer failed & bad reading High) Frequency system dropped to 59.12Hz. (Load shedding level-3) Some feeders tripped: 3D OCB fdr #3 T/O, then closed at 15:38. 3D OCB fdr #5 T/O, then closed at 14:11. 4D OCB fdr #2 T/O, then closed at 15:38. 4D OCB fdr #3 T/O, then closed at 15:39. 4D OCB fdr #4 T/O, then closed at 15:40. 4D OCB fdr #5 T/O, then cloaed at 15:40. 4D OCB fdr #6 T/O, then closed at 14:11. 4B OCB fdr #4 T/O, then closed at 14:09. 5B OCB fdr #4 T/O, then closed at 15:42. 5B OCB fdr #5 T/O, then closed at 15:43. 8D OCB fdr #1 T/O, then closed at 14:55. 8D OCB fdr #3 T/O, then closed at 14:55. 14:23 Manually Opened 3D OCB fdr #4, then closed at 15:37. 15:00 S/U NDC #3, then on line the Unit at 15:34 (After replacing the failure Tranducer above) Cause: Equipment failure. (MW Transducer failure). Production loss: GS #1: 48 BBls / 21 wells. GS #2: 86 BBls / 38 wells. GS #3: 97 BBls / 28 wells. GS #4: 73 BBls / 26 wells. GS #5: 410 BBls / 119 wells. GS #6: 84 BBls / 40 wells. Grand Total: 798 Bbls / 272 wells. | 3026922 | 1 | 13:55 | Afternoon | Tuesday | 2015 | 3
317 | 2015-03-03 16:06 | 2015-03-03 16:06 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 56 | 6D OCB fdr #1 T/R 1x. 6D fdr #2 Load dropped 45A (190-145A). Not checked yet. | 3026923 | 1 | 16:06 | Afternoon | Tuesday | 2015 | 3
318 | 2015-03-03 16:06 | 2015-09-03 08:06 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 56 | Checked & found, 6D OCB fdr #1 T/R 1x Ctr: 286-287 R/F: 51@2. Patrolled the line & found, @1,@2 broken Dead end Insulators o/p #5C-48. Cause: Lightning. | 3026923 | 1 | 16:06 | Afternoon | Tuesday | 2015 | 3
319 | 2015-04-03 01:52 | 2015-04-03 01:52 | 13.8KV MENGGALA FEEDER #2 | Rain and Lightning | Lightning | 27 | Menggala OCB fdr #2 T/R 1x. Menggala GFPC T/R 1x. Not checked yet. | 3026922 | 1 | 1:52 | Night | Friday | 2015 | 4
320 | 2015-04-03 01:52 | 2015-07-03 17:52 | 13.8KV MENGGALA FEEDER #2 | Rain and Lightning | Lightning | 27 | Checked & found, Menggala VCB fdr #2 T/R 1x Ctr: 509-510 R/F: 51N. Also found, Menggala GFPC T/R 2x Ctr: 1089-1091. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3026922 | 1 | 1:52 | Night | Friday | 2015 | 4
321 | 2015-04-03 09:13 | 2015-04-03 09:13 | 13.8KV NORTH DURI GFPC | Fair | Unidentified | 0 | N.Duri GFPC-Tx #12 T/R 1x. Ground fault alarm on N.Duri fdr #8. (No load dropped at any feeders) Not checked yet. | 3026922 | 1 | 9:13 | Morning | Friday | 2015 | 4
322 | 2015-04-03 09:13 | 2015-10-03 08:39 | 13.8KV NORTH DURI GFPC | Fair | Unidentified | 0 | Checked & found, No.Duri GFPC-TX #12 T/R 1x Ctr: 79-80. Patrolled No.Duri fdr #8 line, but found nothing. Cause: Unidentified. | 3026922 | 1 | 9:13 | Morning | Friday | 2015 | 4
323 | 2015-04-03 10:26 | 2015-04-03 10:26 | CENTRAL DURI POWER PLANT | Fair |  | - | 10:26 CGT #2 Tripped By Alarm: High Exhaust spread protection Trip. (The unit tripped off While fuel transferring test from Gas to Distilate) Cause: Fuel Nozzle pressure (Flow divider output) fluctuate at 300 Psi. (The Unit S/B Status, Prior to replacing Fuel Nozzle set) |  | 1 | 10:26 | Morning | Friday | 2015 | 4
324 | 2015-04-03 15:22 | 2015-04-03 15:22 | 13.8KV NORTH DURI FEEDER #6 | Cloudy | Unidentified | 0 | No.Duri VCB fdr #6 T/R 1x. Not checked yet. | 3026922 | 1 | 15:22 | Afternoon | Friday | 2015 | 4
325 | 2015-04-03 15:22 | 2015-10-03 15:22 | 13.8KV NORTH DURI FEEDER #6 | Cloudy | Unidentified | 0 | Checked & found, No.Duri VCB fdr #6 T/R 2x Ctr: 281-283 R/F: 51@1, @2. Patrolled the line, but found nothing. Cause: Unidentified. | 3026922 | 1 | 15:22 | Afternoon | Friday | 2015 | 4
326 | 2015-04-03 15:35 | 2015-04-03 15:35 | 115KV N. DURI SUBST - CD. SW. YARD LINE | Cloudy and Lightning | Lightning | 0 | 15:35 115KV CDSY GCB #53 T/R 1x R/F: 21@A-G Zone-1 (6.3 KM). 115KV CDSY GCB #55 T/R 1x 115KV N.Duri GCB #3 T/SO. (115KV N.Duri-CDSY line T/SO) 17:56 Manually open 115KV CDSY GCB #53 & GCB #55. 18:06 Closed 115KV N.Duri GCB #3. 18:35 Closed 115KV CDSY GCB #53. Closed 115KV CDSY GCB #55. Cause: Not checked & patrolled yet. | 3026922 | 1 | 15:35 | Afternoon | Friday | 2015 | 4
327 | 2015-04-03 15:35 | 2015-10-03 15:35 | 115KV N. DURI SUBST - CD. SW. YARD LINE | Cloudy and Lightning | Lightning | 0 | Checked & found: -115KV CDSY GCB #53 T/R 2x Ctr: 151-153 R/F: 87L & 21@1. -115KV CDSY GCB #55 T/R 2x Ctr: 102-104. -115KV No.Duri GCB #3 T/SO Ctr: 229-230 R/F: 87L & 21@1. Patrolled the line & found, @1 flashed over Dead end Insulator o/p #3H-56. (Tonngak-8) Cause: Lightning. | 3026922 | 1 | 15:35 | Afternoon | Friday | 2015 | 4
328 | 2015-05-03 03:43 | 2015-05-03 03:43 | MINAS POWER PLANT |  |  | - | 03:43 Off line MGT #9, then S/D the Unit for S/B. (Prior to checking Gas Control Valve problem) (P2 Gas peressure swing up & down from 190Psig to 270 Psig) (GT load (MW) swing up & down from 9MW to 16MW) Cause: Under Investigation. 17:38 S/U MGT #9, then On line the Unit at 18:05. |  | 1 | 3:43 | Night | Sunday | 2015 | 5
329 | 2015-05-03 23:59 | 2015-05-03 23:59 | CPI POWER SYSTEM | Rain | Normal Condition | - | CPI power system Normal Condition. |  | 1 | 23:59 | Night | Sunday | 2015 | 5
330 | 2015-06-03 09:06 | 2015-06-03 09:06 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 1 | 09:06 C.Duri fdr #14 Load dropped 79A (129-50A). 10:10 Checked & found, Recl. 06-P8-02 (C.Duri fdr #14) T/SO. Ctr: 141-142. Blocked & closed Recl. 06-P8-02, ok. Then relesed the block. The line is not patrolled yet. | 3026922 | 1 | 9:06 | Morning | Wednesday | 2015 | 6
331 | 2015-06-03 09:06 | 2015-10-03 15:46 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 1 | Patrolled the line, but found nothing. Cause: Unidentified. | 3026922 | 1 | 9:06 | Morning | Wednesday | 2015 | 6
332 | 2015-06-03 11:17 | 2015-06-03 11:17 | CENTRAL DURI POWER PLANT |  |  | - | 11:17 S/U CGT #2, then On line the Unit at 12:05. |  | 1 | 11:17 | Morning | Wednesday | 2015 | 6
333 | 2015-06-03 13:20 | 2015-06-03 13:20 | 13.8KV S. BALAM GFPC | Rain and Lightning | Lightning | 0 | So.Balam GFPC T/R 1x. Ground fault alarm on So.Balam fdr #4. (No Load dropped at any feeders) Not checked yet. | 3026922 | 1 | 13:20 | Afternoon | Wednesday | 2015 | 6
334 | 2015-06-03 13:20 | 2015-08-03 13:20 | 13.8KV S. BALAM GFPC | Rain and Lightning | Lightning | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 180-181 R/F: 51N. Patrolled So.Balam fdr #4 line, but found nothing. Cause: Lightning. | 3026922 | 1 | 13:20 | Afternoon | Wednesday | 2015 | 6
335 | 2015-06-03 17:41 | 2015-06-03 17:41 | 13.8KV 4D FEEDER #3 | Foggy and Smoke | Unidentified | 100 | 17:41 4D OCB fdr #3 TLO. 4D fdr #2 Load dropped 160A (190-30A). 4D fdr #1 Load dropped 185A (265-71A). T/O WIP at GS-5. 19:00 Checked & found, 4D OCB fdr #3 T/LO. Ctr: Did not change. R/F: 51@2,@3. Patrolled the line, but found nothing. 20:21 Blocked & Closed 4D OCB fdr #3, Ok. Then release the block. Cause: Unidentified. | 3026923 | 1 | 17:41 | Afternoon | Wednesday | 2015 | 6
336 | 2015-06-03 22:33 | 2015-06-03 22:33 | 13.8KV BEKASAP FEEDER #6 | Fair | Dead End Insulator | 0 | Bekasap fdr #6 Load dropped 50A (82-32A). Not checked yet. | 3026922 | 1 | 22:33 | Night | Wednesday | 2015 | 6
337 | 2015-06-03 22:33 | 2015-10-03 14:33 | 13.8KV BEKASAP FEEDER #6 | Fair | Dead End Insulator | 0 | Checked & found, Recl. 38BE-10 (Bekasap fdr #6) T/R 1x Ctr: 85-86. Patrolled the line & found, @1 broken Dead end Insulator o/p #39BF-14. Cause: Dead end Insulator. | 3026922 | 1 | 22:33 | Night | Wednesday | 2015 | 6
338 | 2015-07-03 06:37 | 2015-07-03 06:37 | 13.8KV NORTH DURI GFPC | Fair | Unidentified | 0 | No.Duri GFPC-Tx #13 T/R 1x. Ground fault alarm on No.Duri fdr #9. (No load dropped at any fdrs.) Not checked yet. | 3026922 | 1 | 6:37 | Morning | Friday | 2015 | 7
339 | 2015-07-03 06:37 | 2015-09-03 16:37 | 13.8KV NORTH DURI GFPC | Fair | Unidentified | 0 | Checked & found, No.Duri GFPC-TX #13 T/R 1x Ctr: 79-80 R/F: 51G. Patrolled No.Duri fdr #9 line, but found nothing. Cause: Unidentified. | 3026922 | 1 | 6:37 | Morning | Friday | 2015 | 7
340 | 2015-07-03 08:32 | 2015-07-03 08:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Theft | 0 | 08:32 It was reported broken secondary cable of Tx o/p #08-L5-33. 10:18 Checked & found, opened all FCOs for 112.5Kva Tx & lost of secondary cable o/p #08-L5-33. 18:30 Replaced broken secodary cable above & energized The Tx o/p #08-L5-33. Cause: Theft. | 3026922 | 1 | 8:32 | Morning | Friday | 2015 | 7
341 | 2015-07-03 10:42 | 2015-07-03 10:42 | NORTH DURI POWER PLANT | Fair | Equipment Failure | 1136 | 10:42 NDC #3 Tripped Off, By Alarm: “3ZS5303C LP BLEED VLV LIMIT SWITCH NCLOSE 0”. Cause: Equipment failure. (LP Bleed Vlv Limit switch has problem) Frequency system dropped to 59.23Hz. (Load shedding level-3). Tripped off some feeder: 3D OCB fdr #3 T/O, then closed at 16:25. 3D OCB fdr #5 T/O, then closed at 11:07. / 16:25. 4D OCB fdr #2 T/O, then closed at 16:26. 4D OCB fdr #3 T/O, then closed at 16:26. 4D OCB fdr #4 T/O, then closed at 11:19. 4D OCB fdr #5 T/O, then cloaed at 11:20. 4D OCB fdr #6 T/O, then closed at 16:26. 4B OCB fdr #4 T/O, then closed at 11:05. 5B OCB fdr #4 T/O, then closed at 12:11. 5B OCB fdr #5 T/O, then closed at 12:11. 8D OCB fdr #1 T/O, then closed at 12:21. 8D OCB fdr #3 T/O, then closed at 12:22. Rokan OCB fdr #2 T/O then closed at 11:42. 15:45 S/U NDC #3, then on line the Unit at 16:16 (After replacing the LP bleed valve limit switch) Cause: Equipment failure. (LP bleed valve limit switch). Production Loss: GS#1 : 96 Bbls, 21 wells. GS#2 : 114 Bbls, 38 wells. GS#3 : 78 Bbls, 28 wells. GS#4 : 48 Bbls, 26 wells. GS#5 : 771 Bbls, 94 wells. GS#6 : 246 Bbls, 113 wells. TOTAL Prod. Loss : 1353 Bbls, 320 wells. | 3026922 | 1 | 10:42 | Morning | Friday | 2015 | 7
342 | 2015-07-03 18:15 | 2015-07-03 18:15 | MINAS POWER PLANT |  |  | - | Off line MGT #6, then S/D the Unit for S/B. (Prior to repairing Generator endshield) |  | 1 | 18:15 | Afternoon | Friday | 2015 | 7
343 | 2015-07-03 18:57 | 2015-07-03 18:57 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 19 | 5B fdr #4 Load dropped 237A (314-77A). Not checked yet. | 3026923 | 1 | 18:57 | Afternoon | Friday | 2015 | 7
344 | 2015-07-03 18:57 | 2015-10-03 08:22 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 19 | Checked & found, Recl. 4B-73 (5B fdr #4) T/R 1x Ctr: 25-26. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3026923 | 1 | 18:57 | Afternoon | Friday | 2015 | 7
345 | 2015-07-03 19:23 | 2015-07-03 19:23 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 302 | 19:23 CKBS VCB fdr #5 T/R 3x. CKBS fdr #6 Load dropped 186A (207-21A). 19:38 It was reported that no power at Well KB #59. CKBS fdr #5 Load is 245A more to normal. 21:15 Checked & found, CKBS VCB fdr #5 T/R 3x Ctr: 123-126 R/F: 51@1. Also found, Recl. 36CU-29 (CKBS fdr #5) T/SO. Ctr: 80-83. 21:20 Blocked & closed Recl. 36CU-29, Ok. (Then released the Block) The line is not patrolled yet. | 3026923 | 1 | 19:23 | Night | Friday | 2015 | 7
346 | 2015-07-03 19:23 | 2015-08-03 14:23 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 302 | Patrolled the line at downstream of CKBS fdr #5, but found nothing. Patrolled the line at downstream of Recl. 36CU-29 (CKBS fdr #5) & found: -@1 Broken Pin Insulator o/p #34CT-59. -@1 Broken L/A o/p #34CS-35. Cause: Lightning. | 3026923 | 1 | 19:23 | Night | Friday | 2015 | 7
347 | 2015-07-03 23:30 | 2015-07-03 23:30 | 13.8KV PUNGUT FEEDER #1 | Fair | ESP Failure | - | It was reported b/o fuse for Tx at Well Pungut #24. Also found Reda motor Low megger reading. Not Checked yet. | 3026922 | 1 | 23:30 | Night | Friday | 2015 | 7
348 | 2015-07-03 23:30 | 2015-08-03 14:00 | 13.8KV PUNGUT FEEDER #1 | Fair | ESP Failure | - | 14:00 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Pungut #24. Replaced the b/o fuse above with same size & energized the Tx. (The Well is not S/U yet due to Reda motor Low megger reading) Cause: Reda motor failure. | 3026922 | 1 | 23:30 | Night | Friday | 2015 | 7
349 | 2015-08-03 07:50 | 2015-08-03 07:50 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Animal | 1 | 07:50 It was reported b/o fuses for Tx o/p #04-07-12. 11:20 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-07-12. Replaced the b/o fuse above with same size & energized the Tx. Cause: Animal. (Monkey) | 3026922 | 1 | 7:50 | Morning | Monday | 2015 | 8
350 | 2015-08-03 14:30 | 2015-08-03 14:30 | MINAS POWER PLANT |  |  | - | 14:30 Off line MGT #5, then S/D the Unit for S/B. (Prior to repairing Gas Control Valve (P2) problem) |  | 1 | 14:30 | Afternoon | Monday | 2015 | 8
351 | 2015-08-03 23:59 | 2015-08-03 23:59 | MINAS POWER PLANT | Fair | Under investigation | - | 23:59 MGT #11 T/O by Alarm Scubber Liquid Level Hig Trip. Cause: Under investigation. |  | 1 | 23:59 | Night | Monday | 2015 | 8
352 | 2015-09-03 09:33 | 2015-09-03 09:33 | MINAS POWER PLANT |  |  | - | 09:33 S/U MGT #11, then On Line the Unit at 10:15. (After replacing all Gas Scubber Level Switch) |  | 1 | 9:33 | Morning | Thursday | 2015 | 9
353 | 2015-09-03 12:12 | 2015-09-03 12:12 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy and Lightning | Lightning | 9 | So.Bekasap fdr #1 dropped 123A (165-41A). Not checked yet. | 3026922 | 1 | 12:12 | Afternoon | Thursday | 2015 | 9
354 | 2015-09-03 12:12 | 2015-12-03 09:12 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy and Lightning | Lightning | 9 | Checked & found, Recl. 36BI-04 (So.Bekasap fdr #1) T/R 1x Ctr: 166-167. Patrolled the line & found, @1 broken Pin Insulator o/p #35BL-02. Cause: Lightning. | 3026922 | 1 | 12:12 | Afternoon | Thursday | 2015 | 9
355 | 2015-09-03 12:13 | 2015-09-03 12:13 | NORTH DURI POWER PLANT | Rain and Lightning | Under investigation | 1098 | 12:13 NDC-CT #3 Tripped Off, By Alarm: Turbine Over Frequency & 86-1. 230Kv GCB #33 & GCB #35 T/O. Frequency system dropped to 59.00Hz. (Load Shedding Level-4) Rokan fdr #2 T/O, then closed at 12:26. - Prod. Loss = 15 Bbls, 14 Wells 8D Fdr #1 T/O, then closed at 13:04. 48 Bbls, 21 Wells 8D Fdr #3 T/O, then closed at 13:05. 81 Bbls, 38 Wells 4D Fdr #4 T/O, then closed at 14:25. 94 Bbls, 23 Wells 4D Fdr #5 T/O, then closed at 14:25. 60 Bbls, 24 Wells 6D Fdr #1 T/O, then closed at 12:31. 53 Bbls, 26 Wells 6D Fdr #2 T/O, then closed at 14:24. 100 Bbls, 11 Wells 6D Fdr #5 T/O, then closed at 14:25. 15 Bbls, 14 Wells 5B Fdr #1 T/O, then closed at 12:49. 32 Bbls, 23 Wells 5B Fdr #3 T/O, then closed at 13:19. 111 Bbls, 20 Wells 6DN Fdr #4 T/O, then closed at 12:26. WIP 6DN Fdr #5 T/O, then closed at 14:26. 191 Bbls, 24 Wells 6D Fdr #3 T/O, then closed at 12:29. 38 Bbls, 13 Wells 3D Fdr #3 T/O, then closed at 12:47. 55 Bbls, 22 Wells 3D Fdr #5 T/O, then closed at14:25. WIP 4D Fdr #2 T/O,then closed at 12:52. 92 Bbls, 36 Wells 4D Fdr #3 T/O, then closed at 14:25. 60 Bbls, 15 Wells 4D Fdr #6 T/O, then closed at 12:28. WIP 4B Fdr #4 T/O, then closed at 12:30. WIP 5B Fdr #4, then closed at 14:24. 92 Bbls, 25 Wells 5B Fdr #5 T/O, then closed at 13:18. 10 Bbls, 17 Wells Tatal Prod. Loss = 1147 Bbls, 366 Wells 13:18 S/U NDC-CT #3, then On Line the Unit at 14:22. Cause: Under Investigation. | 3026922 | 1 | 12:13 | Afternoon | Thursday | 2015 | 9
356 | 2015-09-03 14:22 | 2015-09-03 14:22 | MINAS POWER PLANT |  |  | - | 14:22 S/U MGT #5, then On Line to the system at 14:35. ( After repairing Gas Control Valve LVDT) |  | 1 | 14:22 | Afternoon | Thursday | 2015 | 9
357 | 2015-09-03 18:41 | 2015-09-03 18:41 | 13.8KV ROKAN FEEDER #4 | Cloudy | Animal | 0 | Rokan VCB fdr #4 T/R 1x. Not checked yet. | 3026922 | 1 | 18:41 | Afternoon | Thursday | 2015 | 9
358 | 2015-09-03 18:41 | 2015-10-03 14:41 | 13.8KV ROKAN FEEDER #4 | Cloudy | Animal | 0 | Checked & found, Rokan VCB fdr #4 T/R 1x Ctr: 745-746 R/F: 50N(@1). Patrolled the line & found, a Dead Monkey under Terminal pole of Well Kirana #01. Cause: Animal. (Monkey) | 3026922 | 1 | 18:41 | Afternoon | Thursday | 2015 | 9
359 | 2015-10-03 09:00 | 2015-10-03 09:00 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Planned Maintenance | 59 | 09:00 Manually open Recl. 30CZ-01 (Petapahan fdr #1). To repairing the falling down conductor from Pin Insulator o/p #31DA-25. (8 Wells were off during the job done) 10:00 Manually closed Recl. 30CZ-01. Cause: Maintenance Job. | 123 | 1 | 9:00 | Morning | Saturday | 2015 | 10
360 | 2015-10-03 09:15 | 2015-10-03 09:15 | MINAS POWER PLANT |  |  | - | 09:15 MGT #5 T/O, By Alarm: High vibration at BB-10. Cause: Suspected sensor Vibration problem. 14:25 S/U MGT #5, then on line the Unit at 14:36. (After replacing sensor Vibration above) |  | 1 | 9:15 | Morning | Saturday | 2015 | 10
361 | 2015-10-03 11:28 | 2015-10-03 11:28 | 13.8KV BANGKO GFPC | Cloudy | Unidentified | 0 | Bangko GFPC T/R 1x. Ground fault alarm on Bangko fdr #1. (No load dropped at any fdrs.) Not checked yet. | 3026922 | 1 | 11:28 | Morning | Saturday | 2015 | 10
362 | 2015-10-03 11:28 | 15/03/2015 14:28 | 13.8KV BANGKO GFPC | Cloudy | Unidentified | 0 | Checked & found, Bangko GFPC T/R 1x Ctr: 446-447. Patrolled Bangko fdr #1 line, but found nothing. Cause: Unidentified. | 3026922 | 1 | 11:28 | Morning | Saturday | 2015 | 10
363 | 2015-10-03 15:04 | 2015-10-03 15:04 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Pinang VCB fdr #1 T/R 1x. Not checked yet. | 3026922 | 1 | 15:04 | Afternoon | Saturday | 2015 | 10
364 | 2015-10-03 15:04 | 13/03/2015 09:45 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Pinang VCB fdr #1 T/R 1x Ctr: 335-336 R/F: 51@3. Patrolled the line & found, @3 broken Pin Insulator o/p #11E-03. Cause: Lightning. | 3026922 | 1 | 15:04 | Afternoon | Saturday | 2015 | 10
365 | 2015-10-03 16:22 | 2015-10-03 16:22 | 115KV SINTONG - BANGKO LINE | Rain and Lightning | Lightning | 847 | 16:22 115Kv Sintong GCB #22 (line to Bangko) T/R 1x. Bangko VCB fdr #1 T/SO. Bangko VCB fdr #4 T/SO. 16:45 Checked & found, Bangko VCB fdr #1 T/O, Ctr: 30-31 R/F: 81. Bangko VCB fdr #4 T/O, Ctr: 99954-99955 R/F: 81. 16:53 Blocked & Closed Bangko VCB fdr #1, then release the block. Blocked & Closed Bangko VCB fdr #4, then release the block. Cause: 115KV Sintong GCB #22 is not checked yet & the line is not patrolled yet. - Bangko Prod. Loss 280 Bbls, 77 Wells. - Prod. Loss 117 Bbls, 36 Wells. - Balam Prod. Loss 356 Bbls, 199 Wells. Total Prod. Loss 753 Bbls, 312 Wells. EC report: Bangko Prod. loss = 554 Bbls / 179 Wells. Balam Prod. loss = 203 Bbls / 173 Wells. Total = 757 Bbls / 352 Wells. | 3026922 | 1 | 16:22 | Afternoon | Saturday | 2015 | 10
366 | 2015-10-03 16:22 | 2015-11-03 13:22 | 115KV SINTONG - BANGKO LINE | Rain and Lightning | Lightning | 847 | Checked & found, 115KV Sintong GCB #22 (line to Bangko) T/R 1x Ctr: 610-611 R/F: 21@1 to G. Patrolled the line & found, @1 broken Dead end Insulator o/p #BKO-23. Cause: Lightning. | 3026922 | 1 | 16:22 | Afternoon | Saturday | 2015 | 10
367 | 2015-10-03 17:18 | 2015-10-03 17:18 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Tree | 33 | 17:18 CKBS fdr #5 Load dropped 245A (321-76A). 17:45 Checked & found, Recl. 36CU-29 (CKBS fdr #5) T/LO. Ctr: 85-87 R/F: 51@3. Patrolled the line & found, High Palm Trees near pole #35CU-10. 18:25 Blocked & closed Recl. 36CU-29, Ok. Then release the block. Cause: Suspected by Tree. (The line would be Re-patrolled) | 3026923 | 1 | 17:18 | Afternoon | Saturday | 2015 | 10
368 | 2015-10-03 17:18 | 2015-11-03 09:18 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Tree | 33 | Re-patrolled the line & found, Vilager cut Palm Tree & hung on the power line near pole #35CU-10. Then clearing its Tree. Cause: Tree. | 3026923 | 1 | 17:18 | Afternoon | Saturday | 2015 | 10
369 | 2015-10-03 17:46 | 2015-10-03 17:46 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Unidentified | 0 | Menggala fdr #1 Load dropped 100A (158-58A). Menggala GFPC did not operate. Not checked yet. | 3026922 | 1 | 17:46 | Afternoon | Saturday | 2015 | 10
370 | 2015-10-03 17:46 | 2015-12-03 14:46 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked & found, Recl. 19AN-04 (Menggala fdr #1) T/R 1x Ctr: 296-297 R/F: 51@2,@3. Patrolled the line, but found nothing. Cause: Unidentified. | 3026922 | 1 | 17:46 | Afternoon | Saturday | 2015 | 10
371 | 2015-11-03 05:43 | 2015-11-03 05:43 | 13.8KV 6DN FEEDER #5 | Fair | Others | - | 05:43 GS-3 operator requested to S/D some wells at downstream of 6DN fdr #5. (Due to 2 WIPs failed to start up / WIPs problem at GS-3) 05:43-15:35 Mannually opened 6DN OCB fdr #5. To trouble shooting of 2 WIPs failed to Start up at GS #3. Cause: WIP problem. (No Prod. loss charged to PGT) | 123 | 1 | 5:43 | Morning | Tuesday | 2015 | 11
372 | 2015-11-03 12:18 | 2015-11-03 12:18 | 13.8KV 6DN FEEDER #6 | Fair | Others | - | 12:18 GS-3 operator Requested to add S/D some wells at downstream of 6DN fdr #6. To anticipate spill at GS-3 due to the Two WIPs were still in trouble shooting. 12:18-13:08 Manually opened 6DN OCB fdr #6. EQR team continue to trouble shooting of 2 WIPs problem at GS-3. Cause: WIP problem. (No Prod. loss charged to PGT) | 123 | 1 | 12:18 | Afternoon | Tuesday | 2015 | 11
373 | 2015-11-03 23:58 | 2015-11-03 23:58 | 115KV KOTABATAK - PETAPAHAN LINE | Rain and Lightning | Tree | 456 | Petapahan fdr #2 load dropped 119A (150-31A). Petapahan fdr #1 load dropped 55A (86-31A). Not checked yet. BOPD: 458 barrels / 65 wells. BOPD: 63 barrels / 16 wells. | 3026923 | 1 | 23:58 | Night | Tuesday | 2015 | 11
374 | 2015-11-03 23:58 | 14/03/2015 08:40 | 115KV KOTABATAK - PETAPAHAN LINE | Rain and Lightning | Tree | 456 | Checked Recl. 28CW-01 & Recl. 28CX-05A (Petapahan fdr #2), found normal. (Reclosers Counter did not change) Patrolled the line, but found nothing. Cause: Unidentified. Checked Petapahan OCB fdr #1 & OCB fdr #2, found Normal. (Ctr: Did not change & R/F: Did not appeare) Recloser at downstream of Petapahan fdr #1 is not checked yet. | 3026923 | 1 | 23:58 | Night | Tuesday | 2015 | 11
375 | 2015-11-03 23:58 | 16/03/2015 11:01 | 115KV KOTABATAK - PETAPAHAN LINE | Rain and Lightning | Tree | 456 | Checked & found, Recl. 30CZ-01 (Petapahan fdr #1) T/R 1x Ctr: 65-66. Patrolled Petapahan fdr #1 line, but found nothing. Cause: Suspected by Lightning. | 3026923 | 1 | 23:58 | Night | Tuesday | 2015 | 11
376 | 2015-11-03 23:58 | 18/03/2015 13:58 | 115KV KOTABATAK - PETAPAHAN LINE | Rain and Lightning | Tree | 456 | Found, 115KV CKBS GCB #1 (line to Petapahan) T/R 1x Ctr: 21-22 R/F: 21@1,@3 to G. No Alarm Trip for 115KV CKBS GCB #1 at DSC. (just appeared alarm Load dropped at Petapahan fdr #1 & fdr #2) The line is not patrolled yet. | 3026923 | 1 | 23:58 | Night | Tuesday | 2015 | 11
377 | 2015-11-03 23:58 | 19/03/2015 16:11 | 115KV KOTABATAK - PETAPAHAN LINE | Rain and Lightning | Tree | 456 | Patrolled 115KV CKBS - Petapahan line & found: -High Trees & touching to power line between poles #KP-41 & KP-42. Cause: Tree. | 3026923 | 1 | 23:58 | Night | Tuesday | 2015 | 11
378 | 2015-12-03 06:52 | 2015-12-03 06:52 | 13.8KV PEMATANG FEEDER #1 | Fair | Dead End Insulator | 33 | Pematang OCB fdr #1 T/R 1x. Pematang fdr #2 load dropped 16A (73-57A). Not checked yet. | 3026922 | 1 | 6:52 | Morning | Thursday | 2015 | 12
379 | 2015-12-03 06:52 | 13/03/2015 15:52 | 13.8KV PEMATANG FEEDER #1 | Fair | Dead End Insulator | 33 | Checked & found, Pematang OCB fdr #1 T/R 1x Ctr: 106-107 R/F: 51N(@1). Patrolled the line & found, @1 broken Dead end Insulator o/p #35BC-02. Cause: Dead end Insulator. | 3026922 | 1 | 6:52 | Morning | Thursday | 2015 | 12
380 | 2015-12-03 07:43 | 2015-12-03 07:43 | 13.8KV LIBO FEEDER #1 | Cloudy and Lightning | Unidentified | 14 | Libo OCB fdr #1 T/R 1x Ctr: 345-346 R/F: 51N. Not patrolled yet. | 3026923 | 1 | 7:43 | Morning | Thursday | 2015 | 12
381 | 2015-12-03 07:43 | 13/03/2015 15:43 | 13.8KV LIBO FEEDER #1 | Cloudy and Lightning | Unidentified | 14 | Patrolled the line, but found nothing. Cause: Unidentified. (Suspected by Lightning) | 3026923 | 1 | 7:43 | Morning | Thursday | 2015 | 12
382 | 2015-12-03 13:37 | 2015-12-03 13:37 | MINAS POWER PLANT | Fair | Under investigation | - | 13:37 MGT #1 Tripped, By Alarm: Hydraulic Pressure low Trip & Excessive Vibration. Cause: Under Investigation. (MGT #1 - NSB status for trouble shooting) |  | 1 | 13:37 | Afternoon | Thursday | 2015 | 12
383 | 2015-03-13 07:34 | 2015-03-13 07:34 | 13.8KV SINTONG GFPC | Fair | Unidentified | 0 | Sintong GFPC T/R 1x. Ground fault alarm at Sintong fdr #2. (No load drop at any feeders) Not checked yet. | 3026922 | 1 | 7:34 | Morning | Friday | 2015 | 3
384 | 2015-03-13 07:34 | 2015-03-17 15:34 | 13.8KV SINTONG GFPC | Fair | Unidentified | 0 | Checked & found, Sintong GFPC T/R 1x Ctr: 270-271 R/F: 51@3. Patrolled Sintong fdr #2 line, but found nothing. Cause: Unidentified. | 3026922 | 1 | 7:34 | Morning | Friday | 2015 | 3
385 | 2015-03-13 07:43 | 2015-03-13 07:43 | 13.8KV 6DN FEEDER #5 | Fair | Unidentified | 92 | 6DN OCB fdr #5 T/R 1x. 6DN OCB fdr #4 load dropped 144A (211-67A). 6DN OCB fdr #6 load dropped 188A (227-39A). Not checked yet. | 3026922 | 1 | 7:43 | Morning | Friday | 2015 | 3
386 | 2015-03-13 07:43 | 2015-03-18 08:43 | 13.8KV 6DN FEEDER #5 | Fair | Unidentified | 92 | Checked & found, 6DN OCB fdr #5 T/R 1x Ctr: 171-172 R/F: 51@3. Patrolled the line, but found nothing. Cause: Unidentified. | 3026922 | 1 | 7:43 | Morning | Friday | 2015 | 3
387 | 2015-03-13 09:38 | 2015-03-13 09:38 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified | 23 | CKBS fdr #6 load dropped 128A (209-81A). CKBS GFPC-TX #2 (no alarm trip appeare at DSC) Not checked yet. | 3026923 | 1 | 9:38 | Morning | Friday | 2015 | 3
388 | 2015-03-13 09:38 | 2015-03-16 08:38 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified | 23 | Checked & found, Recl. 34CT-34 (CKBS fdr #6) T/R 1x Ctr: 16-17. Patrolled the line, but fund nothing. Cause: Unidentified. | 3026923 | 1 | 9:38 | Morning | Friday | 2015 | 3
389 | 2015-03-13 21:59 | 2015-03-13 21:59 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Duri Community ACB fdr #3 T/R 1x. Not checked yet. | 3026922 | 1 | 21:59 | Night | Friday | 2015 | 3
390 | 2015-03-13 21:59 | 2015-03-17 15:30 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #3 T/R 1x Ctr: 47-48 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3026922 | 1 | 21:59 | Night | Friday | 2015 | 3
391 | 2015-03-13 22:44 | 2015-03-13 22:44 | 13.8KV S. BALAM GFPC | Fair | Tree | 0 | So.Balam GFPC T/R 1x. Ground fault alarm on So.Balam fdr #1. (No load drop at any feeders) Not checked yet. | 3026922 | 1 | 22:44 | Night | Friday | 2015 | 3
392 | 2015-03-13 22:44 | 2015-03-16 14:00 | 13.8KV S. BALAM GFPC | Fair | Tree | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 181-182. Patrolled the line & found, High palm Tree & hit to power line near pole of Recl. 16Z-25. Cause: Tree. | 3026922 | 1 | 22:44 | Night | Friday | 2015 | 3
393 | 2015-03-14 07:30 | 2015-03-14 07:30 | 13.8KV PUNGUT FEEDER #2 | Fair | Animal | 9 | 07:30 It was reported b/o fuse for Tx at Well Intan #9. (Pungut fdr #2) 11:25 Checked & found, @2 b/o 2.1SF fuse for 100Kva Tx at Well Intan #09. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Squirrel) | 3026922 | 1 | 7:30 | Morning | Saturday | 2015 | 3
394 | 2015-03-14 07:42 | 2015-03-14 07:42 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Animal | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3026922 | 1 | 7:42 | Morning | Saturday | 2015 | 3
395 | 2015-03-14 07:42 | 2015-03-17 15:25 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Animal | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 72-73 R/F: 50N(@1). Patrolled the line & found, a Dead Squirrel under Tx pole #NN. (Tx for Helipad facility) Cause: Animal. (Squirrel) | 3026922 | 1 | 7:42 | Morning | Saturday | 2015 | 3
396 | 2015-03-14 09:00 | 2015-03-14 09:00 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | 09:00 It was reported no power at REM, Teladan, Beta & Water plant Office. (DC fdr #3) 09:34 Checked & found 13.8Kv Recloser for 4160V at Mini Substation Singgalang T/O. Checked 13.8Kv-4160V Tx & found, normal operation. Then Closed 13.8Kv Recloser for 4160V Tx at Singgalan Mini SS, Ok. Cause: Unidentified. | 3026922 | 1 | 9:00 | Morning | Saturday | 2015 | 3
397 | 2015-03-14 09:48 | 2015-03-14 09:48 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 09:48 It was reported b/o fuse for Tx o/p #03-2-08. (D.Field fdr #4) 11:30 Checked & found, @3 b/o 2.1SF fuse for 112.5Kva Tx o/p #03-2-08. Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3026922 | 1 | 9:48 | Morning | Saturday | 2015 | 3
398 | 2015-03-14 10:15 | 2015-03-14 10:15 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified (Fuse) | 28 | 10:15 It was reported b/o fuse for Tx at Well Pudu #17. (So.Bekasap fdr #1) 14:15 Checked & found, @2 b/o 7.8SF fuse for 250Kva Tx at Well Pudu #17. Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3026922 | 1 | 10:15 | Morning | Saturday | 2015 | 3
399 | 2015-03-15 10:20 | 2015-03-15 10:20 | CENTRAL DURI POWER PLANT |  |  | - | 10:20 Off line CGT #1, then S/D the Unit for load controller investigation. (CGT #1 load gradually dropped to lowest MW) 10:30 Manually closed ACB #19. (Tie breaker) 13:22 S/U CGT #1, then On line to system at 13:44. 13:38 Manually open ACB #19 (Tie breaker) Cause: Under investigation. |  | 1 | 10:20 | Morning | Sunday | 2015 | 3
400 | 2015-03-15 11:34 | 2015-03-15 11:34 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 0 | 11:34 It was reported b/o fuses for Tx o/p #02-02-03. 12:30 Checked & found, @1,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #02-02-03. (Also found oil leakage from on the top of the Tx) Cause: Suspected Tx filure. (The Tx will be replaced tomorrow) | 3026922 | 1 | 11:34 | Morning | Sunday | 2015 | 3
401 | 2015-03-15 11:34 | 2015-03-16 10:10 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 0 | 10:10 Replaced 112.5Kva Tx with the same size o/p #02-02-03. Also replaced @1,@2,@3 broken FCOs & energized The Tx. Cause: Transformer failure. | 3026922 | 1 | 11:34 | Morning | Sunday | 2015 | 3
402 | 2015-03-15 21:19 | 2015-03-15 21:19 | 13.8KV NELLA GFPC | Fair | Unidentified (L/A) | 0 | Nella GFPC T/R 1x. Ground fault alarm on Nella fdr #2. (Nella fdr #2 ampere reading error & manual override in SCADA HMI) Bangko GS to check wells under Nella fdr #2 & found, normal. (No load dropped at any fdrs) Not Checked yet. | 3026922 | 1 | 21:19 | Night | Sunday | 2015 | 3
403 | 2015-03-15 21:19 | 2015-03-18 07:19 | 13.8KV NELLA GFPC | Fair | Unidentified (L/A) | 0 | Checked & found, Nella GFPC T/R 3x Ctr: 671-674 R/F: 51N. Patrolled Nella fdr #2 line & found, @1 broken L/A on TP of Well Bangko #84. Cause: Unidentified (L/A). | 3026922 | 1 | 21:19 | Night | Sunday | 2015 | 3
404 | 2015-03-16 09:43 | 2015-03-16 09:43 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified (Fuse) | 6 | 09:43 It was reported b/o fuses for Tx at Well So.Bekasap #14. 11:15 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well above. Replaced the b/o fuse above with same size & energized the Tx. Cause: Unidentified (fuse). | 3026922 | 1 | 9:43 | Morning | Monday | 2015 | 3
405 | 2015-03-16 09:54 | 2015-03-16 09:54 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | - | 09:54 Manually open Bangko OCB fdr #1. (To prevent oil spills during EOR team replaced Pit Pump Main Breaker). 11:19 Manually closed Bangko OCB fdr #1. Cause: Maintenance Job. (By Bangko EOR Team) Prod. loss by EC report = 323 Bbls / 71 Wells. (The LPO is not charged to PGT) | 123 | 1 | 9:54 | Morning | Monday | 2015 | 3
406 | 2015-03-16 17:15 | 2015-03-16 17:15 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Low mega-ohm reading | 0 | 17:15 It was reported b/o fuse for Tx o/p #03-04-20. 18:40 Checked & found, @1 b/o 2.1SF fuse for 112.5Kva Tx o/p #03-04-20. Performed Megger, TTR test the Tx & found, Low Megger reading. Cause: Low Megger reading. (The Tx would be replaced tomorrow) | 3026922 | 1 | 17:15 | Afternoon | Monday | 2015 | 3
407 | 2015-03-16 17:15 | 2015-03-17 11:00 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Low mega-ohm reading | 0 | Replaced 112.5Kva Tx failure with the same size & energized the Tx. Cause: Tx Low megger reading. | 3026922 | 1 | 17:15 | Afternoon | Monday | 2015 | 3
408 | 2015-03-17 | 2015-03-17 | CENTRAL DURI POWER PLANT |  |  | - | 00:00 Off line CGT #3, then S/D the Unit for S/B. (Prior to opening Guillotine of WHRSG-3 after Certification schedule) 10:27 S/U CGT #3, then On Line the Unit to the system at 10:43. (after racking up Guillotine Gate of WHRSG-3) |  | 1 | 0:00 | Night | Tuesday | 2015 | 3
409 | 2015-03-17 10:20 | 2015-03-17 10:20 | 13.8KV S. BALAM FEEDER #1 | Fair | Transformer Failure | 106 | So.Balam VCB fdr #1 T/R 1x. So.Balam fdr #2 Load dropped 129A (131-2A) T/O WIP at Balam GS. So.Balam fdr #3 Load dropped 67A (67-0A) T/O WIP at Balam GS. So.Balam fdr #4 Load dropped 21A (136-115A). Not checked yet. | 3026922 | 1 | 10:20 | Morning | Tuesday | 2015 | 3
410 | 2015-03-17 10:20 | 2015-03-20 14:25 | 13.8KV S. BALAM FEEDER #1 | Fair | Transformer Failure | 106 | Checked & found, So.Balam VCB fdr #1 T/R 1x Ctr: 333-334 R/F: 51N(@1,@2) Patrolled the line & found, 150Kva Tx failure at Well Balam #346. Cause: Tx failure. | 3026922 | 1 | 10:20 | Morning | Tuesday | 2015 | 3
411 | 2015-03-17 16:44 | 2015-03-17 16:44 | 13.8KV 6D FEEDER #2 | Cloudy and Lightning | Lightning | 40 | 6D fdr #2 dropped 118A ( 189-78A) 6D fdr #1 dropped 47A (352-305A). Not patrolled yet. | 3026923 | 1 | 16:44 | Afternoon | Tuesday | 2015 | 3
412 | 2015-03-17 16:44 | 2015-03-24 13:44 | 13.8KV 6D FEEDER #2 | Cloudy and Lightning | Lightning | 40 | Checked & found, Recl. 6D-298 (6D fdr #2) T/R 1x Ctr: 31-32. Patrolled the line & found: -@1 b/o fuse for Tx at Well #7C-17. -@3 broken L/A on TP of Well #6B-36. Cause: Lightning. | 3026923 | 1 | 16:44 | Afternoon | Tuesday | 2015 | 3
413 | 2015-03-18 00:37 | 2015-03-18 00:37 | CENTRAL DURI POWER PLANT |  |  | - | 00:37 Off line CGT #1, then S/D the Unit for S/B. (Prior to close Guillotine of WHRSG-1 for Certification schedule) 09:45 S/U CGT #1, then On Line the Unit to the system at 10:00. (after racking down Guillotine Gate of WHRSG-1) | 123 | 1 | 0:37 | Night | Wednesday | 2015 | 3
414 | 2015-03-18 08:45 | 2015-03-18 08:45 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 6 | 08:45 It was reported b/o fuses for Tx o/p #07-T7-04. 09:37 Checked & found @2, @3 b/o 2.1SF fuses for 112.5Kva Tx o/p #07-T7-04. Replaced the b/o fuses above with same size, then energized the Tx. Cause: Unidentified (Fuse). (Suspected by Animal) | 3026922 | 1 | 8:45 | Morning | Wednesday | 2015 | 3
415 | 2015-03-18 15:30 | 2015-03-18 15:30 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified (Fuse) | 26 | 15:30 It was reported b/o fuses at well Benar #37. 16:30 Checked & found, @1 b/o 14.0SF fuse for 550Kva Tx at Well Benar #37. Megger & TTR test the Tx & found, normal. (good reading) Replaced the b/o fuse above with same size & energized the Tx. Cause: Unidentified (fuse). | 3026922 | 1 | 15:30 | Afternoon | Wednesday | 2015 | 3
416 | 2015-03-18 23:40 | 2015-03-18 23:40 | 13.8KV 6DN FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx at Well #5E-84E. (6DN fdr #1). Not checked yet. | 3026923 | 1 | 23:40 | Night | Wednesday | 2015 | 3
417 | 2015-03-18 23:40 | 2015-03-19 11:00 | 13.8KV 6DN FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well #5E-84E. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3026923 | 1 | 23:40 | Night | Wednesday | 2015 | 3
418 | 2015-03-19 03:22 | 2015-03-19 03:22 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 57 | 8D OCB fdr #11 T/R 1x. Not checked yet. | 3026923 | 1 | 3:22 | Night | Thursday | 2015 | 3
419 | 2015-03-19 03:22 | 2015-03-24 13:09 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 57 | Checked & found, 8D VCB fdr #11 T/R 1x Ctr: 99891-99892 R/F: 51@2,@3. Patrolled the lne & found, @2 broken Pin Insulator o/p #8D-95. Cause: Lightning. | 3026923 | 1 | 3:22 | Night | Thursday | 2015 | 3
420 | 2015-03-19 03:22 | 2015-03-19 03:22 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 46 | 8D OCB fdr #3 T/R 1x Ctr: 558-559 R/F: 51@1,@2,@3. The line is not patrolled yet. | 3026923 | 1 | 3:22 | Night | Thursday | 2015 | 3
421 | 2015-03-19 03:22 | 2015-03-24 13:22 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 46 | Patrolled the line & found: -@2 Broken L/A on TP of Well #8D-85. -@2 Broken Pin Insulator and, -@1 Broken L/A on TP of Well #8D-75. Cause: Lightning. | 3026923 | 1 | 3:22 | Night | Thursday | 2015 | 3
422 | 2015-03-19 03:33 | 2015-03-19 03:33 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 39 | 8C VCB fdr #4 T/R 1x. (GS Pump). 8C fdr #1 Load dropped 200A (280-80A). 8C fdr #3 Load dropped 60A (74-14A). Not checked yet. | 3026923 | 1 | 3:33 | Night | Thursday | 2015 | 3
423 | 2015-03-19 03:33 | 2015-03-24 13:33 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 39 | Checked & found, 8C VCB fdr #4 T/R 1x Ctr: 572-573 R/F: 51@2,@3. Patrolled the line & found, @3 broken Pin Insulator o/p #8D-75. Cause: Lightning. | 3026923 | 1 | 3:33 | Night | Thursday | 2015 | 3
424 | 2015-03-19 03:51 | 2015-03-19 03:51 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | 13.8KV Minas ACB #21 (44KV line to Rumbai) T/R 1x Ctr: 65-66 R/F: 51G1,G2. Not patrolled yet. | 3026923 | 1 | 3:51 | Night | Thursday | 2015 | 3
425 | 2015-03-19 03:51 | 2015-03-24 13:06 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Patrolled the line & found, @3 flashed over Dead end Insulator o/p #MR-54. Cause: Lightning. | 3026923 | 1 | 3:51 | Night | Thursday | 2015 | 3
426 | 2015-03-19 03:52 | 2015-03-19 03:52 | 4.16KV NO RUMBAI FEEDER #2 | Rain and Lightning | Lightning | 0 | No.Rumbai VCB fdr #2 T/R 1x. Not checked yet. | 3026923 | 1 | 3:52 | Night | Thursday | 2015 | 3
427 | 2015-03-19 03:52 | 2015-03-24 13:52 | 4.16KV NO RUMBAI FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, 4.16KV No.Rumbai VCB fdr #2 T/R 1x Ctr: 324-325 R/F: 51@2,@3. Patrolled the line & found, @3 flashed over Dead end Insulator o/p #1RD-05. Cause: Lightning. | 3026923 | 1 | 3:52 | Night | Thursday | 2015 | 3
428 | 2015-03-19 07:38 | 2015-03-19 07:38 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 7 | 07:38 Duri Field Switchgear RTU Failed. It was reported power outage at Khayangan and Gabus Office. 08:45 Checked & found, Duri Field VCB fdr #4 T/R 2x Ctr: 435-437 R/F: 51N & 51@1,@2,@3. 10:10 It was reported no power at Road #07-U3. (d/s of Duri Field fdr #4) 10:49 Checked & found, Recl. 07-U3-02 (Duri Field fdr #4) T/SO. Ctr: 563-565. Also found Recloser bushing was broken by an animal. (Monkey) 11:58 Removed the above animal & isolated Recl. 07-U3-02. 12:05 Closed LBS #07-U3-17 to transfer load to Duri Field fdr #2. (Under Recl. 07-U3-21). Cause: Animal (Monkey). | 3026922 | 1 | 7:38 | Morning | Thursday | 2015 | 3
429 | 2015-03-19 09:30 | 2015-03-19 09:30 | 4.16KV NO RUMBAI FEEDER #1 | Fair | Others | - | 09:30 It was reported low voltage at Hibrida complex #101, #102, #104. 10:15 Checked & found @1 b/o fuse for 6x75 Kva Tx o/p #3RD-5. (TX House #83) Performed TTR, Megger Test the Tx & found, failure U/G Cable. Checked the 4.16kV U/G Cable for the TX & found burnt out 1 of 3 phases U/G Cable. (Then it is replaced the U/G Cable phase that burnt out to other good phase) 15:25 Replaced b/o fuse with the same size & energized the Tx. Cause: Others. (one of 3 phases U/G Cable was b/o) | 3026922 | 1 | 9:30 | Morning | Thursday | 2015 | 3
430 | 2015-03-19 11:52 | 2015-03-19 11:52 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Unidentified | 49 | Batang VCB fdr #3 T/R 2x. (Batang GFPC did not operate) Not checked yet. | 3026922 | 1 | 11:52 | Morning | Thursday | 2015 | 3
431 | 2015-03-19 11:52 | 2015-03-23 15:21 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Unidentified | 49 | Checked & found, Batng OCB fdr #3 T/R 2x Ctr: 265-267 R/F: 50N(@1). Patrolled the line, but found nothing. Cause: Unidentified. (Suspected by Lightning) | 3026922 | 1 | 11:52 | Morning | Thursday | 2015 | 3
432 | 2015-03-19 16:08 | 2015-03-19 16:08 | 13.8KV 5B FEEDER #4 | Cloudy and Lightning | Tree | 0 | 5B fdr #4 load dropped 242A (310-68A). (at the times Manual S/D Pump & Wells) Not checked yet. (See report 20-Mar-2015 at 05:10) 05:10 5B fdr #4 load dropped 214A (273-96A). 07:51 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO 3x Ctr: 28-31. 09:10 Patrolled the line & found, high trees & touching to powerline, between pole #4B-136 and #4B-138. (Then Cut the high trees above) 10:20 Blocked & closed Recl. 4B-73, Ok. Then released the block. Cause: Trees. | 3026923 | 1 | 16:08 | Afternoon | Thursday | 2015 | 3
433 | 2015-03-19 18:32 | 2015-03-19 18:32 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 21 | C.Duri fdr #1 Load dropped 30A (192-68A). Not checked yet. | 3026992 | 1 | 18:32 | Afternoon | Thursday | 2015 | 3
434 | 2015-03-19 18:32 | 2015-03-20 17:04 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 21 | Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/R 2x Ctr: 217-219 R/F: 51@1,@2. Patrolled the line & found, @2 broken Dead end Insulator o/p #35AV-10. Cause: Lightning. | 3026992 | 1 | 18:32 | Afternoon | Thursday | 2015 | 3
435 | 2015-03-20 05:10 | 2015-03-20 05:10 | 13.8KV 5B FEEDER #4 | Fair | Tree | 107 | 05:10 5B fdr #4 load dropped 214A (273-96A). 07:51 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO 3x Ctr: 28-31. 09:10 Patrolled the line & found, high trees & touching to powerline, between pole #4B-136 and #4B-138. (Then Cut the high trees above) 10:20 Blocked & closed Recl. 4B-73, Ok. Then released the block. Cause: Tree. (Also see report 19-Mar-2015 at 16:08) | 3026923 | 1 | 5:10 | Morning | Friday | 2015 | 3
436 | 2015-03-20 13:00 | 2015-03-20 13:00 | 13.8KV 4B FEEDER #4 | Fair | Transformer Failure | 0 | 13:00 It was reported b/o fuse for Tx at Well #4A-34N. (4B fdr #4) 16:21 Checked & found, @1, @2 b/o 14SF fuses for 550Kva Tx at Well #4A-34N. Performed TTR, Megger Test the Tx & found, Zero megger reading. Cause: TX failure. (The Tx failure is not replaced yet) | 3026923 | 1 | 13:00 | Afternoon | Friday | 2015 | 3
437 | 2015-03-20 13:00 | 2015-03-27 16:10 | 13.8KV 4B FEEDER #4 | Fair | Transformer Failure | 0 | Replaced 550Kva Tx failure with the same size & Energized the Tx. Cause: Tx failure. (Low megger reading) | 3026923 | 1 | 13:00 | Afternoon | Friday | 2015 | 3
438 | 2015-03-20 17:55 | 2015-03-20 17:55 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 13 | 4D fdr #5 load dropped 103A (152-49A). 4D fdr #4 load dropped 34A (339-305A). Not checked yet. | 3026923 | 1 | 17:55 | Afternoon | Friday | 2015 | 3
439 | 2015-03-20 17:55 | 2015-03-25 15:50 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 13 | Checked all Reclosers at downstream of 4D fdr #5 & found, normal. Also checked all Reclosers at downstream of 4D fdr #4 & found, normal. (all Reclosers Counter did not operate) Patrolled the line, but found nothing. Cause: Unidentified. | 3026923 | 1 | 17:55 | Afternoon | Friday | 2015 | 3
440 | 2015-03-20 18:08 | 2015-03-20 18:08 | 115KV MINAS - 5B LINE | Rain and Lightning | Lightning | 410 | 18:08 115KV MSY GCB #51 T/SO, then closed at 20:38. GCB #53 T/SO, then closed at 20:38. 115KV 5B GCB #22 T/SO, then closed at 20:33. GCB #25 T/SO, then closed at 20:33. (115KV MSY - 5B Substation line Trip & Stay Open) 18:08:01 Also 115KV 6D GCB #21 T/SO, then closed at 19:53. 115KV 5B GCB #21 T/SO, then closed at 20:32. GCB #23 T/SO, then closed at 20:33. (115KV 6D - 5B Substation line Trip & Stay Open) (5B Substation Scada failed at that time) 5B Substation TX #1 black out at that time, then energized TX #1 at 20:33. (Load of 5B TX #1 are 5B fdr #1, fdr #2, fdr #3 & 5B fdr #6) Respectively load dropped: 3D fdr #2 Load dropped 23A (212-189A). 3D fdr #3 Load dropped 25A (174-149A). 3D fdr #4 Load dropped 16A (259-243A). 3D fdr #7 Load dropped 58A (180-122A). T/O WIP at GS-5. 4D fdr #4 Load dropped 39A (339-300A). 4D fdr #5 Load dropped 28A (152-124A). 4B fdr #3 Load dropped 66A (131-65A). T/O WIP at GS-6. 4B fdr #1 Load dropped 76A (321-274A). 6D fdr #1 Load dropped 59A (233-215A). T/O WIP at GS-4. 6D fdr #4 Load dropped 70A (189-119A), T/O WIP at GS-4. 6D fdr #5 Load dropped 47A (257-210A). 6D fdr #6 Load dropped 133A (246-133A). 8C fdr #4 Load dropped 57A (303-246A). T/O WIP at GS-2. 8D fdr #6 Load dropped 57A (191-134A). T/O WIP at GS-1. 8D fdr #8 Load dropped 180A (194-14A). T/O WIP at GS-1. 8D fdr #9 Load dropped 56A (182-126A). T/O WIP at GS-1. 8D fdr #10 Load dropped 64A (183-116A). 8D fdr #11 Load dropped 115A (314-199A). Libo fdr #1 Load dropped 21A (98-77A). OKB fdr #2 Load dropped 42A (291-249A). NKB fdr #3 Load dropped 149A (299-150A). NKB fdr #5 Load dropped 185A (232-47A). T/O WIP at KB GS. CKB fdr #2 Load dropped 240A (259-19A). T/O WIP at KB GS. CKB fdr #5 Load dropped 13A (325-312A). CKB fdr #6 Load dropped 23A (215-192A). Petapahan fdr #2 Load dropped 55A (138-83A). Manually opened Minas fdr #3, then closed at 19:42. (Req. by GS-2 due to failed to S/U WIP) (115KV MSY-5B Substation & 6D - 5B Substation are not patrolled yet. Production loss: GS#1 : 0 Bbls, 0 wells. GS#2 : 174 Bbls, 48 wells. GS#3 : 126 Bbls, 63 wells. GS#4 : 349 Bbls, 53 wells. GS#5 : 17 Bbls, 21 wells. GS#6 : 175 Bbls, 81 wells. KB GS : 0 Bbls, 0 wells. Petapahan GS: 99 Bbls, 8 wells. TOTAL Prod loss : 940 bbls, 274 wells. | 3026923 | 1 | 18:08 | Afternoon | Friday | 2015 | 3
441 | 2015-03-20 18:08 | 2015-03-25 13:57 | 115KV MINAS - 5B LINE | Rain and Lightning | Lightning | 410 | Checked & found, 115KV MSY OCB #51 T/SO. Ctr: 320-321 OCB #53 T/SO. Ctr: 330-331 R/F: 87L(@1,@3) & 21@1,@3. 115KV 5B OCB #22 T/SO. Ctr: 659-660 OCB #25 T/SO. Ctr: 202-203 R/F: 87L(@1,@3) & 21@1,@3. (115KV MSY - 5B Line) Patrolled the line at night day & rain, but found nothing. (The line would be Re-patrolled) 16:36 Re-Patrolled 115KV Minas - 5B line, but found nothing. Cause: Suspected by Lightning. | 3026923 | 1 | 18:08 | Afternoon | Friday | 2015 | 3
442 | 2015-03-20 18:08 | 2015-03-20 18:08 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 0 | 18:08 5B fdr #4 Load dropped 177A (273-97A). 24:00 Checked & found, Recl. 4B-73 (5B fdr #4) T/LO. Ctr: 31-35. Patrolled the line, but found nothing. (Patrolled not completed yet) | 3026923 | 1 | 18:08 | Afternoon | Friday | 2015 | 3
443 | 2015-03-20 18:08 | 2015-03-21 01:26 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 0 | 01:26 Open LBS #KN-36 (5B fdr #4). (11 Wells were off) 01:27 Blocked & closed, Recl. 4B-73, Ok. Then released the block. 09:29 Continued patrolling the line under LBS #KN-36 , but found nothing. 09:40 Block Recl. 4B-73 & closed LBS #KN-36, but the Recl. 4B-73 T/O. Re-Opened LBS #KN-36 & closed Recl. #4B-73, Ok. Then released the block. 10:50 Opened LBS #2D-79 to separate part load of under LBS #KN-36. Blocked Recl. 2D-38 (3D fdr #4) & closed LBS #2D-88, Ok. Then released the block. (Part load under LBS #KN-36 transfered to 3D fdr #4 under Recl. 2D-38) 11:40 Open line switch o/p #3C-12 to separated part of powerline under LBS #KN-36. Blocked Recl. 4B-73 & closed LBS #KN-36, Ok. Then released the block. (All 11 wells off were energized) 12:06 Recl. 4B-73 T/LO again. Ctr: 37-41. Opened LBS #KN-36. 13:10 Blocked & closed Recl. 4B-73, Ok. Then released the block. (4 wells under LBS above are still off) 13:51 Re-patrolled the line & found, @3 broken Pin support Insulator on TP of Well #3C-73. 16:18 Replaced @3 broken Pin insulator above & closed line switch o/p #3C-12. 16:26 Blocked Recl. 4B-73 & closed LBS #KN-36, Ok. Then released the block. Cause: Lightning. | 3026923 | 1 | 18:08 | Afternoon | Friday | 2015 | 3
444 | 2015-03-20 18:08 | 2015-03-20 18:08 | 13.8KV 6DN FEEDER #4 | Rain and Lightning | Unidentified | 0 | 6DN OCB fdr#4 T/R 1x. 6DN fdr #6 Load dropped 18A (233-215A). 6DN fdr #2 Load dropped 17A (95-78A). Not checked yet. | 3026923 | 1 | 18:08 | Afternoon | Friday | 2015 | 3
445 | 2015-03-20 18:08 | 2015-03-27 09:02 | 13.8KV 6DN FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked & found, 6DN OCB fdr #4 T/R 1x Ctr: 41 (Did not change) R/F: Did not appear. Patrolled the line, but found nothing. Cause: Unidentified. | 3026923 | 1 | 18:08 | Afternoon | Friday | 2015 | 3
446 | 2015-03-20 18:08 | 2015-03-20 18:08 | 115KV 5B - 6D LINE | Rain and Lightning | Lightning | 0 | 115KV 6D GCB #21 T/SO, then closed at 19:53. 115KV 5B GCB #21 T/SO, then closed at 20:32. GCB #23 T/SO, then closed at 20:33. (115KV 6D - 5B Substation line Trip & Stay Open) (5B Substation Scada failed at that time) 115KV MSY GCB #51 T/SO, then closed at 20:38. GCB #53 T/SO, then closed at 20:38. 115KV 5B GCB #22 T/SO, then closed at 20:33. GCB #25 T/SO, then closed at 20:33. (115KV MSY - 5B Substation line Trip & Stay Open) 5B TX #1 Black out at That time, Energized at 20:33. (Load of 5B TX #1 are 5B fdr #1, fdr #2, fdr #3 & 5B fdr #6) (Also see report at 18:08:00 on 20 Mar 2015 / in the same time of event) Not checked & patrolled yet. | 3026923 | 1 | 18:08 | Afternoon | Friday | 2015 | 3
447 | 2015-03-20 18:08 | 2015-03-25 13:59 | 115KV 5B - 6D LINE | Rain and Lightning | Lightning | 0 | Checked & found, 115KV 6D OCB #21 T/SO. Ctr: 712-713 R/F: 87L(@2) 5B OCB #21 T/SO. Ctr: 978-979 OCB #23 T/SO. Ctr: 1021-1022 R/F: 87L(@2). (115KV 6D - 5B Line) Patrolled the line at night day & rain, but found nothing. (The line would be Re-patrolled) 16:45 Re-Patrolled 115KV 6D - 5B line, but found nothing. Cause: Suspected by Lightning. | 3026923 | 1 | 18:08 | Afternoon | Friday | 2015 | 3
448 | 2015-03-20 18:36 | 2015-03-20 18:36 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 19 | 4B OCB fdr #2 T/R 1x. 4B fdr #1 Load dropped 225A (332-107A). 4B fdr #3 Load dropped 129A (131-2A). T/O WIP at GS-6 Not checked yet. | 3026923 | 1 | 18:36 | Afternoon | Friday | 2015 | 3
449 | 2015-03-20 18:36 | 2015-03-24 13:33 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 19 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 205-206 R/F: 50@1,@2. Patrolled the line & found: -@1 Broken Dead end Insulator o/p #4B-58. -@1 Broken Dead end Insulator o/p #3A-27. Cause: Lightning. | 3026923 | 1 | 18:36 | Afternoon | Friday | 2015 | 3
450 | 2015-03-20 18:44 | 2015-03-20 18:44 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 53 | 18:44 6DN OCB fdr #6 T/R 1x. 19:13 6DN OCB fdr #6 T/R 1x again. Not checked yet. | 3026923 | 1 | 18:44 | Afternoon | Friday | 2015 | 3
451 | 2015-03-20 18:44 | 2015-03-24 16:26 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 53 | Checked & found, 6DN OCB fdr #6 T/R 2x Ctr: 305-307 R/F: 50@1,@2,@3. Patrolled the line, but found nothing. Also found, Recl. 6E-64 (6DN fdr #6) T/R 2x Ctr: 24-26. Patrolled the line & found, @1 broken L/A on TP of Well #6E-43. Cause: Lightning. | 3026923 | 1 | 18:44 | Afternoon | Friday | 2015 | 3
452 | 2015-03-20 18:44 | 2015-03-20 18:44 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 0 | 6DN fdr #5 load dropped 76A (130-54A). 6DN fdr #4 load dropped 55A (222-167A). T/O WIP at GS-3. Not checked yet. | 3026923 | 1 | 18:44 | Afternoon | Friday | 2015 | 3
453 | 2015-03-20 18:44 | 2015-03-24 16:44 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 6D-16A (6DN fdr #5) T/R 1x Ctr: 1204-1205. Patrolled the line & found, @2 broken Dead end Insulator o/p #6D-128. Cause: Lightning. | 3026923 | 1 | 18:44 | Afternoon | Friday | 2015 | 3
454 | 2015-03-20 18:50 | 2015-03-20 18:50 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 49 | 6D OCB fdr #5 T/R 1x. Not checked yet. | 3026923 | 1 | 18:50 | Afternoon | Friday | 2015 | 3
455 | 2015-03-20 18:50 | 2015-03-25 11:07 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 49 | Checked & found, 6D OCB fdr #5 T/R 1x Ctr: 715-716 R/F: 51@1. Patrolled the line & found, @1 broken Pin Insulator o/p #5D-02. Cause: Lightning. | 3026923 | 1 | 18:50 | Afternoon | Friday | 2015 | 3
456 | 2015-03-20 19:02 | 2015-03-20 19:02 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 0 | 3D OCB fdr #2 T/R 1x. Not checked yet. | 3026923 | 1 | 19:02 | Night | Friday | 2015 | 3
457 | 2015-03-20 19:02 | 2015-03-25 16:12 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, 3D OCB fdr #2 T/R 1x Ctr: 483-484 R/F: 51@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3026923 | 1 | 19:02 | Night | Friday | 2015 | 3
458 | 2015-03-20 19:31 | 2015-03-20 19:31 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Lightning | 118 | Minas ACB fdr #4 T/R 1x Ctr: 58-59 R/F: 51@1. Not patrolled yet. | 3026923 | 1 | 19:31 | Night | Friday | 2015 | 3
459 | 2015-03-20 19:31 | 2015-03-25 15:31 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Lightning | 118 | Patrolled the line & found, @1 flashed over Dead end Insulator o/p #7D-105. Cause: Loghtning. | 3026923 | 1 | 19:31 | Night | Friday | 2015 | 3
460 | 2015-03-21 07:30 | 2015-03-21 07:30 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified (Fuse) | 7 | 07:30 It was reported b/o fuse at Well Petani #50. (Petani fdr #2) 11:26 Checked & found, @2, @3 b/o 3.5SF fuses for 150Kva Tx at Well Petani #50. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). (Suspected by Thieves) | 3026922 | 1 | 7:30 | Morning | Saturday | 2015 | 3
461 | 2015-03-21 15:39 | 2015-03-21 15:39 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Unidentified | 0 | 44kV No.Duri GCB #1 (44KV No.Duri - Dumai line) T/R 1x. (Dumai RTU failed at the time & back to online at 15:42) Not checked yet. | 3026922 | 1 | 15:39 | Afternoon | Saturday | 2015 | 3
462 | 2015-03-21 15:39 | 2015-03-25 15:13 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Unidentified | 0 | Checked & found, 44KV No.Duri GCB #1 T/R 1x Ctr: 147-148 R/F: 51@1,@2. Patrolled the line, but found nothing. (Just found a kite hanging on @1 conductor at near pole #DD-135) Cause: Unidentified. | 3026922 | 1 | 15:39 | Afternoon | Saturday | 2015 | 3
463 | 2015-03-21 17:29 | 2015-03-21 17:29 | 13.8KV MINAS FEEDER #3 | Rain | Lightning | 44 | Minas fdr #3 load dropped 65A (330-265A). Not checked yet. | 3026923 | 1 | 17:29 | Afternoon | Saturday | 2015 | 3
464 | 2015-03-21 17:29 | 2015-03-25 14:29 | 13.8KV MINAS FEEDER #3 | Rain | Lightning | 44 | Checked & found, Recl. 7D-93 (Minas fdr #3) T/R 1x Ctr: 19. (Did not change) Patrolled the line & found, @1 broken Pin Insulator o/p #7D-94D. Cause: Lightning. (Needed functioning test the Recl. 7D-93) | 3026923 | 1 | 17:29 | Afternoon | Saturday | 2015 | 3
465 | 2015-03-22 08:54 | 2015-03-22 08:54 | 13.8KV 4D FEEDER #4 | Fair | Unidentified (Fuse) | 8 | 08:54 It was reported b/o fuse for Tx at Well #4D-59. (4D fdr #4) 16:31 Checked & found, @1 b/o 7.8SF fuse for 225Kva Tx at Well #4D-59. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3026923 | 1 | 8:54 | Morning | Sunday | 2015 | 3
466 | 2015-03-22 11:03 | 2015-03-22 11:03 | 13.8KV SINTONG FEEDER #2 | Fair | Pin Insulator | 55 | Sintong OCB fdr #2 T/R 1x. (Sintong GFPC did not operate) Not checked yet. | 3026922 | 1 | 11:03 | Morning | Sunday | 2015 | 3
467 | 2015-03-22 11:03 | 2015-03-24 07:32 | 13.8KV SINTONG FEEDER #2 | Fair | Pin Insulator | 55 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 372-373 R/F: 51@1. Patrolled the line & found, @1,@2 broken Pin Insulators o/p #NN. (1 span before TX pole for Sintong GS) Cause: Pin Insulator. | 3026922 | 1 | 11:03 | Morning | Sunday | 2015 | 3
468 | 2015-03-23 14:30 | 2015-03-23 14:30 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Unidentified (Fuse) | 20 | 14:30 It was reported b/o fuse for Tx at Well KB #277. Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well KB #277. Replaced the b/o fuse above with same size & energized the Tx. Cause: Unidentified (fuse). | 3026923 | 1 | 14:30 | Afternoon | Monday | 2015 | 3
469 | 2015-03-23 16:00 | 2015-03-23 16:00 | 13.8KV 6DN FEEDER #6 | Fair | Switchboard Problem | - | 16:00 It was reported b/o fuses for Tx at Well #5E-94. 16:30 Checked & found, @2 b/o 1.0SF fuse for 50Kva Tx at Well #5E-94. Performed Megger, TTR test the Tx & found, Normal. (good reading) Cause: Switchboard problem. | 3026923 | 1 | 16:00 | Afternoon | Monday | 2015 | 3
470 | 2015-03-23 16:00 | 2015-03-24 17:00 | 13.8KV 6DN FEEDER #6 | Fair | Switchboard Problem | - | Electrician replaced the failure Vacuum contactor at the Switchboard. Then energized the Tx & S/U the Well. Cause: Switchboard problem. | 3026923 | 1 | 16:00 | Afternoon | Monday | 2015 | 3
471 | 2015-03-23 20:24 | 2015-03-23 20:24 | CENTRAL DURI POWER PLANT |  |  | - | 20:24 Off line CGT #1, then S/D the Unit for S/B. (Prior to opening Guillotine of WHRSG-1 after Certification schedule) 20:29 Closed ACB #19. (Tie Breaker) |  | 1 | 20:24 | Night | Monday | 2015 | 3
472 | 2015-03-24 07:17 | 2015-03-24 07:17 | 13.8KV NORTH DURI FEEDER #5 | Rain and Lightning | Lightning | 88 | 07:17 No.Duri VCB fdr #5 T/SO. (No.Duri GFPC-TX #12 did not trip) 07:23 Blocked & Closed, North Duri VCB fdr #5, but failed. (from DSC) 08:15 Checked & found, North Duri VCB fdr #5 T/SO. Ctr: 96-97 R/F: 51N. (Found Spring charging Motor problem / Suspected it is motor burnt out) 09:13 Closed LBS #12-E5-02, but Failed. (LBS problem) (to transfer all load of North Duri fdr #5 to North Duri fdr # 1) 09:35 Closed LBS #12-E9-02. (to transfer all load of North Duri fdr#5 to North Duri fdr # 1) 26-Mar-2015 Switching to retransfer part load of No.Duri fdr #1 to No.Duri fdr #5. (Load No.Duri fdr #5 back to normal) The line is not patrolled yet. | 3026922 | 1 | 7:17 | Morning | Tuesday | 2015 | 3
473 | 2015-03-24 07:17 | 2015-03-27 07:26 | 13.8KV NORTH DURI FEEDER #5 | Rain and Lightning | Lightning | 88 | Patrolled No.Duri fdr #5 line, but found nothing. Cause: Suspected by Lightning. | 3026922 | 1 | 7:17 | Morning | Tuesday | 2015 | 3
474 | 2015-03-24 07:32 | 2015-03-24 07:32 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 39 | Sintong OCB fdr #1 T/R 1x. Sintong fdr #2 load dropped 35A (190-155A). (Sintong GFPC did not trip) Not checked yet. | 3026922 | 1 | 7:32 | Morning | Tuesday | 2015 | 3
475 | 2015-03-24 07:32 | 2015-03-26 07:38 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 39 | Checked & found, OCB fdr #1 T/R 1x Ctr: 352-353 R/F: 51@1. Patrolled the line & found, @1 flashed over Pin Insulator o/p #25AD-15. Cause: Lightning. | 3026922 | 1 | 7:32 | Morning | Tuesday | 2015 | 3
476 | 2015-03-24 11:20 | 2015-03-24 11:20 | CENTRAL DURI POWER PLANT |  |  | - | 11:20 CGT #5 Tripped. (while re booting computer "S") Frequency system dropped to 59.78Hz. (No load shedding) Cause: Under investigation. | 123 | 1 | 11:20 | Morning | Tuesday | 2015 | 3
477 | 2015-03-24 11:22 | 2015-03-24 11:22 | MINAS POWER PLANT |  |  | - | 11:22 Started Up MGT #6, then On Line at 11:52 for testing. 12:00 Off line MGT #6, then S/D the Unit for balancing. | 123 | 1 | 11:22 | Morning | Tuesday | 2015 | 3
478 | 2015-03-24 13:18 | 2015-03-24 13:18 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 1 | Libo fdr #1 load dropped 80A (94-14A). Not patrolled yet. | 3026922 | 1 | 13:18 | Afternoon | Tuesday | 2015 | 3
479 | 2015-03-24 13:18 | 2015-03-25 14:18 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 1 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 346-347 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3026922 | 1 | 13:18 | Afternoon | Tuesday | 2015 | 3
480 | 2015-03-24 16:13 | 2015-03-24 16:13 | CENTRAL DURI POWER PLANT |  |  | - | 16:13 S/U CGT #1, then On Line the Unit at 16:32. (After racking Up Guillotine Gate of WHRSG-1) | 123 | 1 | 16:13 | Afternoon | Tuesday | 2015 | 3
481 | 2015-03-24 17:45 | 2015-03-24 17:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 28 | It was reported b/o fuse link for Tx o/p #08-L3-18. Not checked yet. | 3026922 | 1 | 17:45 | Afternoon | Tuesday | 2015 | 3
482 | 2015-03-24 17:45 | 2015-03-25 10:10 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 28 | 10:10 Checked & found, @2 b/o 2.1SF fuse for 112.5Kva Tx o/p #08-L3-18. (C.Duri fdr #1) Replaced the b/o fuse above with same size & energized the Tx. Cause: Animal. (Monkey) | 3026922 | 1 | 17:45 | Afternoon | Tuesday | 2015 | 3
483 | 2015-03-25 09:15 | 2015-03-25 09:15 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Secondary Cable | 9 | It was reported b/o fuse for Tx o/p #01-02-02. Not checked yet. | 3026923 | 1 | 9:15 | Morning | Wednesday | 2015 | 3
484 | 2015-03-25 09:15 | 2015-03-27 08:15 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Secondary Cable | 9 | Checked & found, @1,@2 b/o 2.1SF fuses for 112.5Kva Tx o/p #01-02-02. (Also found, burnt out Secondary cable of the Tx) Tested the Tx & found, normal. (good reading) The Tx is not energized yet. (w/o replaced b/o Secandary cable) | 3026923 | 1 | 9:15 | Morning | Wednesday | 2015 | 3
485 | 2015-03-25 09:15 | 2015-06-04 16:25 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Secondary Cable | 9 | Replaced b/o Secondary Cable, then energized the Tx. Cause: Secondary Cable (Burnt Out). | 3026923 | 1 | 9:15 | Morning | Wednesday | 2015 | 3
486 | 2015-03-25 11:54 | 2015-03-25 11:54 | 13.8KV 8D FEEDER #11 | Fair | Low mega-ohm reading | 46 | 11:54 It was reported b/o fuses for Tx at Well #9E-53. Checked & found, @2 b/o 14.0SF fuse for 550Kva Tx at Well #9E-53. Megger & TTR tested the Tx, found Low megger reading. Then replaced the Tx with the same size & energized the Tx. Cause: Low megger reading. | 3026923 | 1 | 11:54 | Morning | Wednesday | 2015 | 3
487 | 2015-03-25 12:20 | 2015-03-25 12:20 | CENTRAL DURI POWER PLANT |  |  | - | 11:10 S/U CGT #5, then On Line the Unit at 12:30 (After trouble shooting its Starting Motor) | 123 | 1 | 12:20 | Afternoon | Wednesday | 2015 | 3
488 | 2015-03-25 13:29 | 2015-03-25 13:29 | 13.8KV 4B FEEDER #1 | Heavy Rain | Lightning | 50 | 13:29 4B fdr #1 Load dropped 138A (325-187A). 14:50 Checked & found, Recl. 4B-101 (4B fdr #1) T/SO. Ctr: 48-49 14:53 Blocked & closed Recl. 4B-101, Ok. Then released the Block. The Line is not patrolled yet. | 3026923 | 1 | 13:29 | Afternoon | Wednesday | 2015 | 3
489 | 2015-03-25 13:54 | 2015-03-25 13:54 | MINAS POWER PLANT |  |  | - | 13:54 S/U MGT #6, then On Line the Unit at 14:13. (Running for rotor vibration balancing test) 14:45 Off Line MGT #6, then S/D the Unit, for rotor vibration balancing. 17:05 S/U MGT #6, then On Line the Unit at 17:24. (Running for rotor vibration balancing test) 17:57 Off Line MGT #6, then S/D the Unit for S/B. (Prior to continuing rotor vibration balancing test) | 123 | 1 | 13:54 | Afternoon | Wednesday | 2015 | 3
490 | 2015-03-25 14:15 | 2015-03-25 14:15 | 13.8KV 8D FEEDER #3 | Fair | Transformer Failure | 0 | 14:15 It was reported b/o fuses for Tx at Well #9D-45A. Checked & found, @1, @2 b/o 1.0SF fuses for 50Kva Tx at Well #9E-45A. Megger & TTR tested the Tx & found, the Tx failure. Replaced the Tx with 150Kva & energized the Tx. Cause: Tx failure. | 3026923 | 1 | 14:15 | Afternoon | Wednesday | 2015 | 3
491 | 2015-03-25 15:27 | 2015-03-25 15:27 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 21 | Nella MSU VCB fdr #2 T/R 1x. Not checked yet. | 3026923 | 1 | 15:27 | Afternoon | Wednesday | 2015 | 3
492 | 2015-03-25 15:27 | 2015-03-29 14:27 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 21 | Checked & found, MSU-2 VCB fdr #2 T/R 1x Ctr: 202-203 R/F: 51@1,@3. Patrolled the line & found, @1,@3 flashed over Pin Insulators o/p #19W-04. Cause: Lightning. | 3026923 | 1 | 15:27 | Afternoon | Wednesday | 2015 | 3
493 | 2015-03-25 16:16 | 2015-03-25 16:16 | 13.8KV 8D FEEDER #10 | Cloudy and Lightning | Lightning | 42 | 8D OCB fdr #10 T/R 1x. 8D fdr #9 dropped 110A (122-12A). T/O WIP at GS-1. 8D fdr #11 dropped 7A (303-296A). Not checked yet. | 3026923 | 1 | 16:16 | Afternoon | Wednesday | 2015 | 3
494 | 2015-03-25 16:16 | 2015-03-31 13:20 | 13.8KV 8D FEEDER #10 | Cloudy and Lightning | Lightning | 42 | Checked & found, 8D OCB fdr #10 T/R 1x Ctr: 207-208 R/F: 51@1,@2,@3. Patrolled the line & found, @1,@2,@3 flashed over Bypass Sw of Recl. 7E-21. Cause: Lightning. | 3026923 | 1 | 16:16 | Afternoon | Wednesday | 2015 | 3
495 | 2015-03-26 00:12 | 2015-03-26 00:12 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 75 | 5B OCB fdr #2 T/R 1x. 5B fdr #1 load dropped 70A (100-30A). 5B fdr #3 load dropped 60A (123-63A). Not checked yet. | 3026923 | 1 | 0:12 | Night | Thursday | 2015 | 3
496 | 2015-03-26 00:12 | 2015-03-31 15:00 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 75 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 327-328 R/F: 51@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3026923 | 1 | 0:12 | Night | Thursday | 2015 | 3
497 | 2015-03-26 00:13 | 2015-03-26 00:13 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 23 | 6D OCB fdr #4 T/R 1x. 6D fdr #6 load dropped 73A (251-178A). Not checked yet. | 3026923 | 1 | 0:13 | Night | Thursday | 2015 | 3
498 | 2015-03-26 00:13 | 2015-03-31 15:11 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 23 | Checked & found, 6D OCB fdr #4 T/R 1x Ctr: 530-531 R/F: 51@2,@3. Patrolled the line & found, @3 broken Pin Insulator o/p #5C-118. Cause: Lightning. | 3026923 | 1 | 0:13 | Night | Thursday | 2015 | 3
499 | 2015-03-26 00:59 | 2015-03-26 00:59 | 13.8KV BANGKO GFPC | Rain and Lightning | Powerline - Conductor | 0 | Bangko GFPC T/R 1x. Ground fault alarm on Bangko fdr #1. (No load dropped at any fdrs.) Not checked yet. | 3026922 | 1 | 0:59 | Night | Thursday | 2015 | 3
500 | 2015-03-26 00:59 | 2015-03-29 14:20 | 13.8KV BANGKO GFPC | Rain and Lightning | Powerline - Conductor | 0 | Checked & found, Bangko GFPC T/R 5x Ctr: 448-453. Patrolled Bangko fdr #1 line & found, @2 broken Conductor toward Well Bangko #25. Cause: Broken conductor. | 3026922 | 1 | 0:59 | Night | Thursday | 2015 | 3
501 | 2015-03-26 12:21 | 2015-03-26 12:21 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 15 | 4D fdr #4 load dropped 288A ( 338-50A). 4D fdr #5 load dropped 103A ( 162-59A). Not patrolled yet. | 3026923 | 1 | 12:21 | Afternoon | Thursday | 2015 | 3
502 | 2015-03-26 12:21 | 2015-03-31 15:21 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 15 | Checked & found, Recl. 4D-51A (4D fdr #4) T/R 2x Ctr: 02-04. Patrolled the line & found, @1 broken L/A o/p #4E-21. Cause: Lightning. Also found, Recl. 4D-85 (4D fdr #4) T/R 1x Ctr: 1612-1613. Patrolled the line & found, @1 broken Pin Insulator o/p #NN. (near Well #5D-12) Cause: Lightning. | 3026923 | 1 | 12:21 | Afternoon | Thursday | 2015 | 3
503 | 2015-03-26 12:32 | 2015-03-26 12:32 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 57 | 00:13 6D fdr #5 load dropped 141A (255-114A). 12:32 6D fdr #5 load dropped 72A ( 262-190A). Not checked yet. | 3025923 | 1 | 12:32 | Afternoon | Thursday | 2015 | 3
504 | 2015-03-26 12:32 | 2015-03-31 15:32 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 57 | Checked & found, Recl. 5D-10 (6D fdr #5) T/R 1x Ctr: 09-10. Patrolled the line & found, @3 flashed over L/A on TP of Well #5D-35. | 3025923 | 1 | 12:32 | Afternoon | Thursday | 2015 | 3
505 | 2015-03-26 12:45 | 2015-03-26 12:45 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 56 | 6D OCB fdr #1 T/R 1x. 6D fdr #2 load dropped 112A (187-75A). Not checked yet. | 3026923 | 1 | 12:45 | Afternoon | Thursday | 2015 | 3
506 | 2015-03-26 12:45 | 2015-03-31 15:45 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 56 | Checked & found, 6D OCB fdr #1 T/R 1x Ctr: 288-289 R/F: 51N. Patrolled the line & found, @2 flashed over Pin Insulator o/p #NN. (near Well #5C-66) Cause: Lightning. | 3026923 | 1 | 12:45 | Afternoon | Thursday | 2015 | 3
507 | 2015-03-26 13:00 | 2015-03-26 13:00 | 13.8KV BATANG FEEDER #3 | Fair | Animal | 0 | It was reported b/o fuse for Tx at Well Candi #12. (Batang fdr #3) Checked & found, @2,@3 b/o 3.1SF fuses for 150Kva Tx at Well Candi #12. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3026922 | 1 | 13:00 | Afternoon | Thursday | 2015 | 3
508 | 2015-03-26 14:15 | 2015-03-26 14:15 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Animal | 0 | 14:15 It was reported that b/o fuse for Tx o/p #03-06-16B. (C.Duri fdr #5) 16:49 Checked & found, @1 b/o 14.0SF fuse for 500Kva Tx o/p #03-06-16B. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3026922 | 1 | 14:15 | Afternoon | Thursday | 2015 | 3
509 | 2015-03-26 16:45 | 2015-03-26 16:45 | MINAS POWER PLANT |  |  | - | 16:45 S/U MGT #6, then on line the Unit at 17:00. (Running test due to Generator rotor Trim Balancing Programe) | 123 | 1 | 16:45 | Afternoon | Thursday | 2015 | 3
510 | 2015-03-26 18:43 | 2015-03-26 18:43 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 0 | 18:43 Sintong fdr #2 Load dropped 31A (190-159A). Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #2) Not checked yet. 19:02 Sintong GFPC T/R 1x again. Fault alarm on Sintong fdr #2. (No load dropped at any feeders) Not checked yet. | 3026922 | 1 | 18:43 | Afternoon | Thursday | 2015 | 3
511 | 2015-03-26 18:43 | 2015-03-29 15:43 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 29Z-13 (Sintong fdr #2) T/R 1x Ctr: 70-71. Also found Sintong GFPC T/R 11x Ctr: 721-732. (Also see report 26 Mar 2015 at 19:12) Patrolled the line & found, seriously broken Pin Insulator o/p #27AF-17. (near Well Sintong #47) Cause: Suspected by Lightning. | 3026922 | 1 | 18:43 | Afternoon | Thursday | 2015 | 3
512 | 2015-03-26 19:12 | 2015-03-26 19:12 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 50 | Sintong OCB fdr #2 T/R 1x. Sintong GFPC T/R 1x again. Not checked yet. | 3026922 | 1 | 19:12 | Night | Thursday | 2015 | 3
513 | 2015-03-26 19:12 | 2015-03-29 15:45 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 50 | Checked & found, Sintong OCB fdr #2 T/R 7x Ctr: 373-380 R/F: 51N & 51@1. Also found, Sintong GFPC T/R 11x Ctr: 721-732. (See report 26 Mar 2015 at 18:43) Patrolled the line & found, @1 seriously broken Pin Insulator o/p #27AF-17. (Near Well Sintong #47) Cause: Lightning. | 3026922 | 1 | 19:12 | Night | Thursday | 2015 | 3
514 | 2015-03-26 22:34 | 2015-03-26 22:34 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Powerline - Conductor | 281 | 22:34 Bangko OCB fdr #1 T/SO. Ctr: 32-33 R/F: 50N. Bangko GFPC T/R 2x Ctr: 447-449. 23:05 Blocked & closed Bangko OCB #1, Ok. Bangko GFPC T/R 1x again. 23:06 Bangko OCB fdr #1 T/O. (In block position). 27-Mar-2015 00:12 Patrolled the line toward LBS #23W-01, but found nothing. Then Open LBS #23W-01 above & closed Bangko OCB fdr #1, Ok. 01:42 Patrolled the line under LBS #23W-01 & found nothing. Then Closed LBS #23W-01, Ok. 01:48 Checked & found, Recl. 23X-08 (Bangko fdr #1) T/SO. Ctr: 364-366. Blocked & closed Recl. 23X-08, but trip again. 02:10 Patrolled under Recl. 23X-08 above & found, @2 broken conductor toward Well Bangko #25. Then repaired broken conductor above. 09:30 Blocked & closed Recl. 23X-08, Ok. Then released the Block. (After completed repairing broken conductor above) Cause: Broken Conductor. | 3026922 | 1 | 22:34 | Night | Thursday | 2015 | 3
515 | 2015-03-27 00:23 | 2015-03-27 00:23 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 788 | 00:23 Sintong OCB fdr #2 T/LO. Ctr: 373-378 R/F: 51N & 51@1. Sintong GFPC T/R 1x. Then Patrolled the line, but found nothing. (The weather is still rain) 04:14 Blocked & closed Sintong OCB fdr #2, but T/O Again. And also Sintong OCB fdr #1 T/R 1x. Sintong GFPC T/R 1x again. (Counter GFPC is not reported yet) 04:25 Manually opened Recl. 28AF-17 & Recl. 28AF-02 (Sintong fdr #2). 04:31 Blocked & closed Sintong OCB fdr #2, but T/O again. Also Sintong OCB fdr #1 T/R 1x again. (Counter & R/F are not reported yet) 05:05 Re-Patrolled & found, @1 seriously broken Pin Insulator o/p #NN. (Near Well Sintong #04) 07:23 Blocked & closed Sintong OCB fdr #2, Ok. Then released the Block. (After replacing broken Pin Insulator above) 07:25 Closed Recl. 28AF-02 (Sintong fdr #2), Ok. 07:30 Closed Recl. 28AF-17 (Sintong fdr #2), Ok. Cause: Broken Pin Insulator. | 3026923 | 1 | 0:23 | Night | Friday | 2015 | 3
516 | 2015-03-27 02:47 | 2015-03-27 02:47 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Rain and Lightning | Animal | 0 | 02:47 It was reported b/o fuse for Tx at Well Bangko #41. (MSU-2 fdr #1) 13:30 Checked & found, @1 b/o 1.0SF fuse for 50Kva Tx at Well Bangko #41. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Squirrel) | 3026922 | 1 | 2:47 | Night | Friday | 2015 | 3
517 | 2015-03-27 05:14 | 2015-03-27 05:14 | CENTRAL DURI POWER PLANT |  |  | - | 05:14 Off line CGT #2, then S/D the Unit for S/B. 05:19 Closed ACB #19. (Tie Breaker) (Prior to replacing Distilate tubing & its connector) 15:08 S/U CGT #2, then online the Unit at 16:00. 15:59 Opened ACB #19. (Tie Breaker) (After completing to replace Distilate tubing & Connector) | 123 | 1 | 5:14 | Morning | Friday | 2015 | 3
518 | 2015-03-27 16:00 | 2015-03-27 16:00 | 13.8KV CENTRAL DURI FEEDER #14 | Cloudy | Animal | 0 | 16:00 It was reported b/o fuse for Tx o/p #06-04-03. (C.Duri fdr #14) (power for Main bunker area #6 / Gudang dinamit) 18:25 Checked & found, @1 b/o 2.1SF fuse for 112.5Kva Tx o/p #06-04-03. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3026922 | 1 | 16:00 | Afternoon | Friday | 2015 | 3
519 | 2015-03-27 17:24 | 2015-03-27 17:24 | 13.8KV BATANG FEEDER #3 | Cloudy | Animal | 92 | 17:24 Batang fdr#3 Load dropped 13A (32-19A). 22:05 Checked & found Recl. 36AL-13 (Batang fdr #3) T/SO. Ctr: 113-114. Blocked & closed Recl. 36AL-13, Ok. Then released the block. The line is not patrolled yet. | 3026922 | 1 | 17:24 | Afternoon | Friday | 2015 | 3
520 | 2015-03-27 17:24 | 2015-02-04 07:41 | 13.8KV BATANG FEEDER #3 | Cloudy | Animal | 92 | Patrolled the line & found a Dead Monkey & b/o fuse for Tx at Well Candi #12. Cause: Animal. (Monkey) | 3026922 | 1 | 17:24 | Afternoon | Friday | 2015 | 3
521 | 2015-03-28 11:08 | 2015-03-28 11:08 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Theft | 0 | 11:08 It was reported no power at Well Puncak #08. (C.Duri fdr #1) 16:42 Checked & found, Secondary Cable was Loss by Theft. The fuses were open position for 100Kva Tx. Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced the Secondary Cable above & Energized the Tx. Cause: Theft. (Loss secondary cable) | 3026922 | 1 | 11:08 | Morning | Saturday | 2015 | 3
522 | 2015-03-28 16:41 | 2015-03-28 16:41 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 17 | 4D OCB fdr #4 T/R 1x Ctr: 241-242 R/F: 51N. 4D fdr #5 Load dropped 6A (163-157A). Not patrolled yet. | 3026922 | 1 | 16:41 | Afternoon | Saturday | 2015 | 3
523 | 2015-03-28 16:41 | 2015-03-31 14:21 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 17 | Patrolled the line & found, @1 broken Pin Insulator o/p #36DN-38. Cause: Lightning. | 3026922 | 1 | 16:41 | Afternoon | Saturday | 2015 | 3
524 | 2015-03-28 16:58 | 2015-03-28 16:58 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | 5B fdr #1 load dropped 48A (108-52A). Not checked yet. | 3026923 | 1 | 16:58 | Afternoon | Saturday | 2015 | 3
525 | 2015-03-28 16:58 | 2015-07-04 07:58 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 5B-06 (5B fdr #1) T/R 1x Ctr: 24-25. Patrolled the line & found, @1,@2 broken Dead end Insulator o/p #5B-52. Cause: Lightning. | 3026923 | 1 | 16:58 | Afternoon | Saturday | 2015 | 3
526 | 2015-03-28 22:38 | 2015-03-28 22:38 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Theft | 22 | 22:38 It was reported, unbalance voltage Tx at Well KB #452. (CKBS fdr #6) 23:45 Checked & found, 500Kva Tx Unload Tap changer was changed position and, also found Tx pressure gauge was broken at Well KB #452. Then S/D the Tx to Perform TTR, Megger test the Tx & found, normal) (Energized the Tx, after testing the Tx & put the Unload Tap changer at Tap-3 position) Cause: Theft. | 3026923 | 1 | 22:38 | Night | Saturday | 2015 | 3
527 | 2015-03-29 09:45 | 2015-03-29 09:45 | 13.8KV PETANI FEEDER #1 | Cloudy | Low mega-ohm reading | 18 | 09:45 It was reported b/o fuse for Tx at Well Petani #100. (Petani fdr #1) 11:30 Checked & found, @1,@2 b/o 3.1SF fuses for 150Kva Tx at Well Petani #100. Performed TTR, Megger test & found, Low megger reading. Cause: Low megger reading. (Tx will be replaced tomorrow) | 3026922 | 1 | 9:45 | Morning | Sunday | 2015 | 3
528 | 2015-03-29 09:45 | 2015-03-29 09:45 | 13.8KV PETANI FEEDER #2 | Cloudy | Animal | 11 | 09:45 It was reported b/o fuse for Tx at Well Petani #124. (Petani fdr #2) 13:20 Checked & found, @1,@2 b/o 7.0SF fuses for 250Kva Tx at Well Petani #124. Replaced b/o fuse above with the same size & energized the TX. Cause: Animal. (Rat) | 3026922 | 1 | 9:45 | Morning | Sunday | 2015 | 3
529 | 2015-03-29 09:45 | 2015-03-29 09:45 | 13.8KV BEKASAP FEEDER #6 | Cloudy | Theft | 0 | 09:45 It was reported No power at Well Aman #12. (Bekasap fdr #6) 16:00 Checked & found opened Fuses & lost of Secondary cable of 50Kva Tx. Replaced the Secondary cable above & Energized the Tx. Cause: Theft. | 3026922 | 1 | 9:45 | Morning | Sunday | 2015 | 3
530 | 2015-03-29 10:30 | 2015-03-29 10:30 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 1 | 10:30 It was reported b/o fuse for Tx at Well BKO #88. (BKO fdr #1) 14:13 Checked & found, @2 ,@3 b/o 7.0SF fuses for 225Kva Tx at Well BKO #88. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (RAT) | 3026922 | 1 | 10:30 | Morning | Sunday | 2015 | 3
531 | 2015-03-29 14:00 | 2015-03-29 14:00 | 13.8KV MINAS FEEDER #3 | Fair | Animal | 12 | 14:00 It was reported b/o fuse for Tx at Well #7D-62. (MNS fdr #3) 17:30 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well #7D-62. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Snake) | 3026923 | 1 | 14:00 | Afternoon | Sunday | 2015 | 3
532 | 2015-03-29 14:10 | 2015-03-29 14:10 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 14:10 It was reported b/o fuse for Tx o/p #13-G61-01. (N.Duri fdr #2) 15:30 Checked & found, @2 b/o 2.1SF fuse for 112.5Kva Tx o/p #13-G61-01. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3026922 | 1 | 14:10 | Afternoon | Sunday | 2015 | 3
533 | 2015-03-31 07:42 | 2015-03-31 07:42 | 13.8KV ROKAN FEEDER #2 | Fair | Animal | 6 | Rokan VCB fdr #2 T/R 1x . Not checked yet. | 3026922 | 1 | 7:42 | Morning | Tuesday | 2015 | 3
534 | 2015-03-31 07:42 | 2015-02-04 18:42 | 13.8KV ROKAN FEEDER #2 | Fair | Animal | 6 | Checked & found, Rokan VCB fdr #1 T/R 1x Ctr: 971-972 R/F: 51@1. Patrolled the line & found, @1 broken L/A & a dead Monkey under pole #28AV-23. Cause: Animal. (Monkey) | 3026922 | 1 | 7:42 | Morning | Tuesday | 2015 | 3
535 | 2015-03-31 08:26 | 2015-03-31 08:26 | DURI POWER PLANT |  |  | - | DGT #7 Tripped By Alarm: Revers power relay operate. (32) Cause: Undenr Investigation. Frequency system dropped to 59.84Hz. (No load shedding) |  | 1 | 8:26 | Morning | Tuesday | 2015 | 3
536 | 2015-03-31 14:52 | 2015-03-31 14:52 | CENTRAL DURI POWER PLANT |  |  | - | 14:52 Started Up CGT #4, then On line to system at 20:20. (Running on test after M/O) 21:50 Off line CGT #4 & then tripped off while running test to Distilate fuel. |  | 1 | 14:52 | Afternoon | Tuesday | 2015 | 3
537 | 2015-03-31 16:21 | 2015-03-31 16:21 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 11 | 16:21 5B fdr #3 Load dropped 85A (123-38A). 19:15 Checked & found, Recl. 4C-65 (5B fdr #3) T/SO. Ctr: 08-09. Blocked & closed Recl. 4C-65, but failed. 19:28 Manually Open 5B OCB fdr #3, to by pass Recl. 4C-65. 19:35 Manually closed 5B OCB fdr #3, Ok. Not Patrolled yet. | 3026923 | 1 | 16:21 | Afternoon | Tuesday | 2015 | 3
538 | 2015-03-31 16:21 | 2015-02-04 07:21 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 11 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3026923 | 1 | 16:21 | Afternoon | Tuesday | 2015 | 3
539 | 2015-03-31 16:24 | 2015-03-31 16:24 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 40 | 16:24 4D fdr #2 Load dropped 132A (198-66A). 19:52 Checked & found, Recl. 4D-204 (4D fdr #2) T/SO. Ctr: 73-74. Blocked & closed Recl. 4D-204, Ok. Then released the blok. Not patrolled yet. | 3026923 | 1 | 16:24 | Afternoon | Tuesday | 2015 | 3
540 | 2015-03-31 16:24 | 2015-06-04 09:39 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 40 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3026923 | 1 | 16:24 | Afternoon | Tuesday | 2015 | 3
541 | 2015-03-31 16:32 | 2015-03-31 16:32 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 0 | 4D OCB fdr #3 T/R 1x. Not checked yet. | 3026922 | 1 | 16:32 | Afternoon | Tuesday | 2015 | 3
542 | 2015-03-31 16:32 | 2015-06-04 09:33 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found, 4D OCB fdr #3 T/R 1x Ctr: 357. (Counter unit is broken) R/F: 51@2. Patrolled the line & found, @2 broken Pin Insulator o/p #4C-135. Cause: Lightning. | 3026922 | 1 | 16:32 | Afternoon | Tuesday | 2015 | 3
543 | 2015-03-31 17:34 | 2015-03-31 17:34 | 230KV N. DURI SW. YARD - KBJ LINE - 2 | Rain and Lightning | Unidentified | 0 | 230KV North Duri GCB #11 T/R 1x. 230KV North Duri GCB #13 T/R 1x. 230KV KBJ GCB #93 T/R 1x. 230KV KBJ GCB #94 T/R 1x. (230KV North Duri - KBJ Line-2 T/R) Not checked yet. | 3026922 | 1 | 17:34 | Afternoon | Tuesday | 2015 | 3
544 | 2015-03-31 17:34 | 2015-03-31 16:34 | 230KV N. DURI SW. YARD - KBJ LINE - 2 | Rain and Lightning | Unidentified | 0 | Checked & found: 230KV KBJ GCB #93 T/R 1x Ctr: 243-244. GCB #94 T/R 1x Ctr: 272-273 R/F: 87L@3-G (10.6KM), 21@3-G & 67N(Inst) Patrolled part of the line from KBJ toward Tower #172, but found nothing. (No.Duri 230KV Breaker is not checked & the line toward KBJ is not patrolled yet) | 3026922 | 1 | 17:34 | Afternoon | Tuesday | 2015 | 3
545 | 2015-03-31 17:34 | 2015-07-04 09:11 | 230KV N. DURI SW. YARD - KBJ LINE - 2 | Rain and Lightning | Unidentified | 0 | Checked & found, 230KV No.Duri GCB #11 T/R 1x Ctr: 285-286. GCB #13 T/R 1x Ctr: 266-267 R/F: 21@3-G & 67N(Inst). Completed patrolling the line from Tower #172 toward No.Duri Substation, but found nothing. Cause: Unidentified. (Suspected by Lightning) | 3026922 | 1 | 17:34 | Afternoon | Tuesday | 2015 | 3
546 | 2015-03-31 22:30 | 2015-03-31 22:30 | 13.8KV 6D FEEDER #1 | Fair | Low mega-ohm reading | 35 | 22:30 It was reported b/o fuses for Tx at Well #5C-85. 23:30 Checked & found, @1, @3 b/o 3.1SF fuses for 150Kva Tx at Well #5C-85. Performed Megger, TTR tested the Tx & found, Low Megger reading. Cause: Low Megger reading. (The Tx would be replaced tomorrow) | 3026923 | 1 | 22:30 | Night | Tuesday | 2015 | 3
547 | 2015-03-31 22:30 | 2015-02-04 11:23 | 13.8KV 6D FEEDER #1 | Fair | Low mega-ohm reading | 35 | 11:23 Replaced 150 Kva tx with same size & energized the Tx. Cause: Trafo failure (Low megger). | 3026923 | 1 | 22:30 | Night | Tuesday | 2015 | 3
548 | 2015-03-31 23:40 | 2015-03-31 23:40 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 0 | 5B fdr #4 load dropped 188A (265-77A). Not patrolled yet. | 3026923 | 1 | 23:40 | Night | Tuesday | 2015 | 3
549 | 2015-03-31 23:40 | 2015-06-04 09:04 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 4B-73 (5B fdr #4) T/R 1x Ctr: 41-42. Patrolled the line & found, @2 broken L/A o/p #3C-34. Cause: Lightning. | 3026923 | 1 | 23:40 | Night | Tuesday | 2015 | 3
550 | 2015-03-31 00:33 | 2015-03-31 00:33 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain and Lightning | Lightning | 0 | 00:33 NKBS VCB fdr #3 T/R 1x. NKBS GFPC T/R 1x. 17:00 Checked & found, NKBS VCB fdr #3 T/R 1x Ctr: 268-269 R/F: 50/51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3026923 | 1 | 0:33 | Night | Tuesday | 2015 | 3
551 | 2015-03-31 07:17 | 2015-02-03 07:27 | 13.8KV SINTONG GFPC | Cloudy and Lightning | Lightning | 0 | Checked & found, Sintong GFPC T/R 3x Ctr: 732-735 R/F: 51N. Patrolled Sintong fdr #2 line, but found nothing. Cause: Suspected by Lightning. | 3026922 | 1 | 7:17 | Morning | Tuesday | 2015 | 3
552 | 2015-03-31 07:17 | 2015-03-31 07:17 | 13.8KV SINTONG GFPC | Cloudy and Lightning | Lightning | 0 | Sintong GFPC T/R 1x. Fault alarm on Sintong fdr #2. No load dropped at any feeder. Not checked yet. | 3026922 | 1 | 7:17 | Morning | Tuesday | 2015 | 3
553 | 2015-03-31 08:00 | 2015-03-31 08:00 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 6 | 08:00 It was reported that B/O fuse for Tx at Well Bangko #291. 09:30 Checked & found,@2,@3 B/O 15K fuses for 300KVA Tx at well Bangko #291. Tested the Tx & found normal ( good reading). Then replaced B/O fuse above with the same size & energized the Tx. Cause: Animal (snake). | 3026922 | 1 | 8:00 | Morning | Tuesday | 2015 | 3
554 | 2015-03-31 10:17 | 2015-03-31 10:17 | 13.8KV PETANI FEEDER #2 | Fair | Animal | 0 | 10:17 Petani fdr #2 load dropped 15A (71-56A). 11:10 Checked & found, Recl. 38AW-09 (Petani fdr #2) T/O. Patrolled the line, but found nothing. 12:08 Blocked & closed Recl. 38AW-09, Ok. Then released the block. The line is not Re-patrolled yet. | 3026922 | 1 | 10:17 | Morning | Tuesday | 2015 | 3
555 | 2015-03-31 10:17 | 2015-02-04 17:01 | 13.8KV PETANI FEEDER #2 | Fair | Animal | 0 | Patrolled the line & found, @1 b/o fuse & F/O of FCO on TP of Well Petani #97. Cause: Animal. | 3026922 | 1 | 10:17 | Morning | Tuesday | 2015 | 3
556 | 2015-03-31 10:56 | 2015-03-31 10:56 | CENTRAL DURI POWER PLANT |  |  | - | 10:56 S/U CGT #4, then On line the unit at 11:56. |  | 1 | 10:56 | Morning | Tuesday | 2015 | 3
557 | 2015-03-31 11:03 | 2015-03-31 11:03 | 13.8KV PETANI FEEDER #1 | Fair | Animal | 0 | Petani fdr #1 load dropped 37A (217-180A). Not checked yet. | 3026922 | 1 | 11:03 | Morning | Tuesday | 2015 | 3
558 | 2015-03-31 11:03 | 2015-02-04 13:36 | 13.8KV PETANI FEEDER #1 | Fair | Animal | 0 | Checked & found, Recl. 32AW-09 (Petanin fdr #1) T/R 1x Ctr: 496-497. Patrolled the line & found, a dead Bird under Recl. 32AW-09. (No material damaged) Cause: Animal. (Bird) | 3026922 | 1 | 11:03 | Morning | Tuesday | 2015 | 3
559 | 2015-03-31 11:12 | 2015-03-31 11:12 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 21 | 11:12 It was reported no power at Road #H1-2. 13:45 Checked & found, Recl. 13-G71-13 (No.Duri fdr #2) T/O. (In Block position) Patrolled the line, but found nothing. 14:01 Blocked & Closed Recl. 13-G71-13, Ok. Then released the Block. Cause: Unidentified. | 3026922 | 1 | 11:12 | Morning | Tuesday | 2015 | 3
560 | 2015-03-31 12:02 | 2015-03-31 12:02 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified (Fuse) | 11 | 12:02 It was reported no power at Well Petani # 97 14:30 Checked & found, @1 b/o 3.1SF fuse for 150kva Tx at Well Petani #97. 15:10 Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Caused: Unidentified (Fuse). | 3026922 | 1 | 12:02 | Afternoon | Tuesday | 2015 | 3
561 | 2015-03-31 17:38 | 2015-03-31 17:38 | MINAS POWER PLANT |  |  | - | 17:38 S/U MGT #2, then on line the Unit at 17:56. |  | 1 | 17:38 | Afternoon | Tuesday | 2015 | 3
562 | 2015-03-31 19:31 | 2015-03-31 19:31 | 13.8KV CENTRAL DURI FEEDER #8 | Rain and Lightning | Lightning | 0 | C.Duri ACB fdr #8 T/R 1x Ctr: 296. (did not change) R/F: 51N. Not patrolled yet. | 3026922 | 1 | 19:31 | Night | Tuesday | 2015 | 3
563 | 2015-03-31 19:31 | 2015-03-04 17:51 | 13.8KV CENTRAL DURI FEEDER #8 | Rain and Lightning | Lightning | 0 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3026922 | 1 | 19:31 | Night | Tuesday | 2015 | 3
564 | 2015-03-31 19:48 | 2015-03-31 19:48 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | C.Duri fdr #1 Load dropped 50A (231-181). Not checked yet. | 3026922 | 1 | 19:48 | Night | Tuesday | 2015 | 3
565 | 2015-03-31 19:48 | 2015-03-04 17:48 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 2x Ctr: 178-180. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3026922 | 1 | 19:48 | Night | Tuesday | 2015 | 3
566 | 2015-03-31 20:43 | 2015-03-31 20:43 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Rangau VCB fdr #2 T/R 1x. (Scada Rangau RTU failed at that time) Not checked yet. | 3026922 | 1 | 20:43 | Night | Tuesday | 2015 | 3
567 | 2015-03-31 20:43 | 2015-02-04 18:43 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked Rangau VCB fdr #2 & found, normal. (Counter: Did not operate & No R/F appeare) Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 3x Ctr: 111-114. Patrolled the line, but found nothing. Cause: Suspected by Ligthning. | 3026922 | 1 | 20:43 | Night | Tuesday | 2015 | 3
568 | 2015-03-31 21:30 | 2015-03-31 21:30 | MINAS POWER PLANT |  |  | - | Off line MGT #3, then S/D the Unit for S/B. |  | 1 | 21:30 | Night | Tuesday | 2015 | 3
569 | 2015-01-04 09:14 | 2015-01-04 09:14 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 10 | 09:14 It was reported that B/O fuse for Tx o/p #05-P3-09. 18:17 Checked & found, @1, @2 b/o 2.1SF fuse for 112.5Kva Tx o/p #05-P3-09. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3041212 | 1 | 9:14 | Morning | Sunday | 2015 | 1
570 | 2015-01-04 09:15 | 2015-01-04 09:15 | CENTRAL DURI POWER PLANT |  |  | - | 09:15 S/U CGT #1, then On line the Unit at 09:46. |  | 1 | 9:15 | Morning | Sunday | 2015 | 1
571 | 2015-01-04 12:40 | 2015-01-04 12:40 | MOBILE SUBSTATION 1 | Cloudy | Equipment Failure | 900 | 12:40 115KV Minas - 8C line Load dropped 57A (158-101A). (MSU RTU was failed at that time) 12:57 Manually open Minas ACB fdr #3. (Requested by Suryatno GL GS-2) 13:16 Checked & found, 115KV MSU-1 C/S #1 T/O. By: Relay 86 HR. 13:25 Open 13.8KV MSU VCB fdr #1 & MSU VCB fdr #2. 13:35 Open Line Switch of MSU fdr #1 & MSU fdr #2. Transfered Load of MSU to other feeder: 13:53 MSU fdr #1 (8C fdr #5) transfer to 8C fdr #3, by closing LBS #8D-274. 14:57 Transfer 8C fdr #1 to 8D fdr #3, by closing LBS #9D-07 & open LBS #9C-14. 15:10 Transfer load 8C fdr #6 to 8C fdr #1, by closing LBS #8C-45. 15:12 Close Minas ACB fdr #3. 15:34 Transfer load Minas fdr #3 to 8C fdr #3, by closing Recl. 8D-18A. 15:37 Open LBS #7D-117. 16:00 Checked load of 8D fdr #3 & found: 460 A. (overload) 17:00 Close 115KV MSU-1 C/S #1, but failed. 17:45 Open Recl. 9D-25 to reduce load of 8D fdr #3. (Load 8D fdr #3 = 340 A from 460A) 18:12 Close 115KV MSU-1 C/S #1, Ok. Then observe the Tx cooling system. 21:47 Ensure 13.8KV MSU VCB fdr #1 & fdr #2 are open position. 21:48 Closed Disconnecting Switch of MSU fdr #1 & fdr #2 at 8C Substation. 23:04 Closed MSU VCB fdr #2 at 8C Substation. 23:05 Closed LBS #9C-14 & Opened LBS #9D-07. 23:03 Closed Recl. 9D-25. (MSU fdr #2 at 8C Substation back to normal, to feed 8C fdr #6) 23:16 Closed 13.8KV MSU VCB fdr #1 at 8C Substation. 23:20 Opened LBS #8D-247. (MSU fdr #1 at 8C Substation back to normal, to feed 8C fdr #5) Cause: Equipment failure. (The cooling system failed caused the circuit switcher open to protect the transformer) GS-2 operator reported Prod. loss: Prod. Loss GS #1: 188 Bbls / 18 Wells. GS #2: 858 Bbls / 112 Wells. TOTAL Prod. Loss : 1046 Bbls / 130 Wells. | 3041214 | 1 | 12:40 | Afternoon | Sunday | 2015 | 1
572 | 2015-02-04 01:31 | 2015-02-04 01:31 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 44 | MSU (Nella) VCB fdr #2 T/R 1x. MSU (Nella) fdr #1 Load dropped 19A (169-150A). Not checked yet. | 3041212 | 1 | 1:31 | Night | Wednesday | 2015 | 2
573 | 2015-02-04 01:31 | 2015-04-04 07:31 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 44 | Checked & found, MSU-2 (Nella #2) VCB fdr #2 T/R 1x Ctr: 203-204 R/F: 51@1,@2,@3. Patrolled the line & found, @1,@2 broken Pin Insulators o/p #19W-04. Cause: Lightning. | 3041212 | 1 | 1:31 | Night | Wednesday | 2015 | 2
574 | 2015-02-04 08:43 | 2015-02-04 08:43 | 13.8KV S. BALAM GFPC | Cloudy and Lightning | Lightning | 0 | So.Balam GFPC T/R 1x. Ground fault alarm on So.Balam fdr #4. (No load dropped at any feeders) Not checked yet. | 3041212 | 1 | 8:43 | Morning | Wednesday | 2015 | 2
575 | 2015-02-04 08:43 | 2015-04-04 07:43 | 13.8KV S. BALAM GFPC | Cloudy and Lightning | Lightning | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 183-184 R/F: 51N. Patrolled So.Balam fdr #4 line, but found nothing. Cause: Suspected by Lightning. | 3041212 | 1 | 8:43 | Morning | Wednesday | 2015 | 2
576 | 2015-02-04 12:57 | 2015-02-04 12:57 | 13.8KV SINTONG FEEDER #2 | Heavy Rain | Lightning | 0 | Sintong fdr #2 Load dropped 90A (191-101A). Sintong GFPC T/R 1x. (Ground fault alarm at Sintong fdr #2) Not checked yet. | 3041212 | 1 | 12:57 | Afternoon | Wednesday | 2015 | 2
577 | 2015-02-04 12:57 | 2015-04-04 07:57 | 13.8KV SINTONG FEEDER #2 | Heavy Rain | Lightning | 0 | Checked & found, Recl. 28AF-02 (Sintong fdr #2) T/R 1x Ctr: 245-246 R/F: 51@1,@3. Also found, Sintong GFPC T/R 2x Ctr: 735-737. Patrolled the line & found, @1,@3 broken Pin Insulators o/p #29AA-14. Cause: Lightning. | 3041212 | 1 | 12:57 | Afternoon | Wednesday | 2015 | 2
578 | 2015-02-04 14:10 | 2015-02-04 14:10 | MINAS POWER PLANT |  |  | - | 14:10 Off line MGT #7, then S/D the Unit for S/B. (Prior to Fixing the Leakage of Distilate fuel line at Fuel Nozzle Connections) 16:37 S/U MGT #7, then On line the Unit at 16:54. | 123 | 1 | 14:10 | Afternoon | Wednesday | 2015 | 2
579 | 2015-03-04 08:55 | 2015-03-04 08:55 | CENTRAL DURI POWER PLANT |  |  | - | 08:55 Off line CGT #4, to Reseting Excitation setting. 09:56 Re-Online CGT #4 to the system. |  | 1 | 8:55 | Morning | Wednesday | 2015 | 3
580 | 2015-03-04 10:00 | 2015-03-04 10:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 10:00 It was reported b/o fuse for Tx at Well Kulin #14. 15:20 Checked & found, @2 b/o 1.4SF fuse link for 75Kva Tx at Well Kulin #14. Performed TTR, Megger test & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unindentified (Fuse). | 3041212 | 1 | 10:00 | Morning | Wednesday | 2015 | 3
581 | 2015-03-04 15:43 | 2015-03-04 15:43 | MINAS POWER PLANT |  |  | - | 15:43 Off line MGT #5, then S/D the Unit for S/B. (S/D the unit to reduce using Gas related S/D Gas Copi program) |  | 1 | 15:43 | Afternoon | Wednesday | 2015 | 3
582 | 2015-04-04 08:00 | 2015-04-04 08:00 | 13.8KV 4B FEEDER #1 | Fair | Unidentified (Fuse) | 8 | 08:00 It was reported b/o fuse for Tx at Well #3C-53. (4B fdr #1) 15:57 Checked & found, @1 b/o 7.8SF fuse link for 300Kva Tx at Well #3C-53. Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unindentified (Fuse). | 3041214 | 1 | 8:00 | Morning | Saturday | 2015 | 4
583 | 2015-04-04 08:00 | 2015-04-04 08:00 | 13.8KV 3D FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 08:00 It was reported b/o fuse for Tx at Well #1D-85. (3D fdr #2) 16:30 Checked & found, @1,@3 b/o 14.0SF fuses for 550Kva Tx at Well #1D-85. Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuses above with the same size then energized the Tx. Cause: Unindentified (Fuse). | 3041214 | 1 | 8:00 | Morning | Saturday | 2015 | 4
584 | 2015-04-04 14:42 | 2015-04-04 14:42 | 13.8KV BATANG FEEDER #1 | Cloudy and Lightning | Unidentified | 13 | 07:21 Batang VCB fdr #1 T/R 1x. 14:42 Batang VCB fdr #1 T/SO. 15:30 Patrolled the line by PHE Team & found nothing. 16:30 Blocked & closed Batang VCB fdr #1, but failed to close. 20:20 Checked & found, Batang VCB fdr #1 T/SO. Ctr: 104-105 R/F: 51@1,@2,@3. Also found, Charging Motor for Batang VCB fdr #1 burnt out. (Then Manual charged the Closing Spring for Batang VCB fdr #1) 20:26 Blocked & closed Batang VCB fdr #1, Ok. Then released the block. (Manual re-charged the Closing Spring of Batang VCB fdr #1, for readiness the Breaker) Note: Batang VCB fdr #1 will only reclose for 1 time operation then T/SO due to b/o Charging Motor. Cause: Unidentified. | 3041212 | 1 | 14:42 | Afternoon | Saturday | 2015 | 4
585 | 2015-04-04 18:55 | 2015-04-04 18:55 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 57 | 18:55 It was reported b/o fuse for Tx at well Petani #66 (Petani fdr #1). 21:21 Checked & found, @1, @2 b/o 7.8SF fuses for 300 Kva Tx at well Petani #66. Performed TTR, Megger test the Tx & found, Zero Mega-ohm reading Tx. Cause: Transformer failure. | 3041212 | 1 | 18:55 | Afternoon | Saturday | 2015 | 4
586 | 2015-04-04 18:55 | 2015-05-04 13:30 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 57 | Replaced failure 300 Kva Tx with 225 Kva Tx, then energized the Tx. Cause: Transformer failure. | 3041212 | 1 | 18:55 | Afternoon | Saturday | 2015 | 4
587 | 2015-05-04 01:02 | 2015-05-04 01:02 | 13.8KV 5B FEEDER #6 | Cloudy and Lightning | Lightning | 0 | 5B OCB fdr #6 T/R 1x. Not checked yet. | 3041214 | 1 | 1:02 | Night | Monday | 2015 | 5
588 | 2015-05-04 01:02 | 2015-07-04 07:14 | 13.8KV 5B FEEDER #6 | Cloudy and Lightning | Lightning | 0 | Checked & found, 5B OCB fdr #6 T/R 1x Ctr: 242-243 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #6D5B-12. Cause: Lightning. | 3041214 | 1 | 1:02 | Night | Monday | 2015 | 5
589 | 2015-05-04 13:01 | 2015-05-04 13:01 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain and Lightning | Lightning | 0 | 4.16KV Dumai (Housing) ACB fdr #4 T/R 1x. Not checked yet. | 3041212 | 1 | 13:01 | Afternoon | Monday | 2015 | 5
590 | 2015-05-04 13:01 | 2015-06-04 12:27 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain and Lightning | Lightning | 0 | Chhecked & found, 4.16KV Dumai (Hsg.) VCB fdr #4 T/R 1x Ctr: 256-257 R/F: 51@3. Patrolled the line & found, @3 broken L/A of Transformer o/p #H66-05. Cause: Lightning. | 3041212 | 1 | 13:01 | Afternoon | Monday | 2015 | 5
591 | 2015-05-04 15:32 | 2015-05-04 15:32 | 13.8KV 5B FEEDER #4 | Fair | ESP Failure | - | 08:32 It was reported by SPS that Well #4B-59 was off. (5B fdr #4) 15:30 Checked & found, @1 b/o 7.0SF fuse for 225Kva Tx at Well #4B-89. Performed TTR, Megger test the Tx & found, Low Mega-ohm reading Tx. Cause: Transformer failure. (Reda Motor Zero Megger) (The failure Tx Would be Replaced tomorow) | 3041212 | 1 | 15:32 | Afternoon | Monday | 2015 | 5
592 | 2015-05-04 21:50 | 2015-05-04 21:50 | 13.8KV RANGAU FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Rangau OCB fdr #2 T/R 1x. (Rangau RTU failed at the same time & online at 21:53) Not checked yet. | 3041212 | 1 | 21:50 | Night | Monday | 2015 | 5
593 | 2015-05-04 21:50 | 2015-07-04 13:50 | 13.8KV RANGAU FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Checked & found, Rangau VCB fdr #2 T/R 3x Ctr: 111-114 R/F: 51N(@1). Patrolled the line & found, @1 broken L/A o/p #23BD-17. Cause: Lightning. | 3041212 | 1 | 21:50 | Night | Monday | 2015 | 5
594 | 2015-06-04 00:45 | 2015-06-04 00:45 | 13.8KV DURI FIELD FEEDER #1 | Rain and Lightning | Broken Fuse Holder | 0 | 00:45 It was reported b/o fuse for Tx #5 at CGS #1. (Duri Field fdr #1). 02:29 Checked & found, @2 b/o 7.8SF fuse & broken fuse holder for 300Kva Tx #5 at CGS #1. Replaced b/o fuse & holder above, then energized the Tx. Cause: Broken Fuse Holder. | 3041212 | 1 | 0:45 | Night | Thursday | 2015 | 6
595 | 2015-06-04 04:45 | 2015-06-04 04:45 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified (Fuse) | 0 | 04:45 It was reported b/o fuse for Tx o/p #09-M1-12. (C.Duri fdr #16) 11:30 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #09-M1-12. Replaced b/o fuse above with same size then energized the Tx. Cause: Unidentified (Fuse). | 3041212 | 1 | 4:45 | Morning | Thursday | 2015 | 6
596 | 2015-06-04 08:46 | 2015-06-04 08:46 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | 08:46 It was reported b/o fuse for Tx for Training Centre building. 09:59 Checked & found, @1, @2 b/o 3.5SF fuses for 150Kva Tx o/p #SD-03C. Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size then energized the Tx. Caused: Animal. (Bird) | 3041212 | 1 | 8:46 | Morning | Thursday | 2015 | 6
597 | 2015-06-04 10:12 | 2015-06-04 10:12 | 13.8KV PETAPAHAN FEEDER #2 | Fair | ESP Failure | 0 | 10:12 It was reported b/o fuse for Tx at Well Topaz #06. (Petapahan fdr #2) Checked & found, @1 b/o 7.0SF fuse for 250Kva Tx at Well Topaz #06. Performed TTR, Megger Test the Tx & found, normal. (good reading) Replaced b/o fuse above with same size then energize the Tx. (no load). Cause: ESP Failure. (Reda motor Zero Megger) (No production loss charge to PGT) | 3041212 | 1 | 10:12 | Morning | Thursday | 2015 | 6
598 | 2015-06-04 11:45 | 2015-06-04 11:45 | MINAS POWER PLANT |  |  | - | 11:45 S/U MGT # 5, then On line the Unit at 12:07. | 123 | 1 | 11:45 | Morning | Thursday | 2015 | 6
599 | 2015-06-04 15:16 | 2015-06-04 15:16 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Transformer Failure | 8 | 15:16 It was reported b/o fuse for Tx o/p #09-P3-02 (C.Duri fdr #16) 17:30 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx o/p #09-P3-02. (Also found, Transformer Oil leak at Primary Bushing of Tx) Cause: Transformer Failure. (The Tx would be replaced tomorrow) | 3041212 | 1 | 15:16 | Afternoon | Thursday | 2015 | 6
600 | 2015-06-04 15:16 | 2015-08-04 16:05 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Transformer Failure | 8 | Replaced Tx failure & b/o fuses with the same size & energized the TX o/p #09-P3-02. Cause: Tx failure. | 3041212 | 1 | 15:16 | Afternoon | Thursday | 2015 | 6
601 | 2015-07-04 11:19 | 2015-07-04 11:19 | MINAS POWER PLANT |  |  | - | 11:19 Started Up MGT #10, then On Line the Unit at 12:27. (Running on test after replacing Generator Rotor) 16:20 Off line MGT #10, then S/D the Unit for balancing. |  | 1 | 11:19 | Morning | Saturday | 2015 | 7
602 | 2015-07-04 14:54 | 2015-07-04 14:54 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 2 | Sintong fdr #2 dropped 74A (191-117A). (Sintong GFPC did not operate) Ground Fault Alrm On Sintong fdr #2. Not patrolled yet. | 3041212 | 1 | 14:54 | Afternoon | Saturday | 2015 | 7
603 | 2015-07-04 14:54 | 2015-09-04 07:54 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 2 | Checked & found, Recl. 28AF-17 (Sintong fdr #2) T/R 1x Ctr: 420-421. Patrolled the line & found, @3 broken Pin Insulator o/p #28AJ-06. Cause: Lightning. | 3041212 | 1 | 14:54 | Afternoon | Saturday | 2015 | 7
604 | 2015-07-04 15:23 | 2015-07-04 15:23 | 13.8KV 8D FEEDER #11 | Cloudy and Lightning | Lightning | 52 | 8D OCB fdr #11 T/R 1x. 8D fdr #10 dropped 14A (187-173A). Not Checked yet. | 3041214 | 1 | 15:23 | Afternoon | Saturday | 2015 | 7
605 | 2015-07-04 15:23 | 2015-10-04 10:23 | 13.8KV 8D FEEDER #11 | Cloudy and Lightning | Lightning | 52 | Checked & found, 8D OCB fdr #11 T/R 1x Ctr: 99892-99893 R/F: 51@1. Patrolled the line, but found nothing. Also found, Recl. 9E-02 (8D fdr #11) T/R 1x Ctr: 1054-1055. Patrolled the line & found, @1 broken L/A o/p #9E-27E. Cause: Lightning. | 3041214 | 1 | 15:23 | Afternoon | Saturday | 2015 | 7
606 | 2015-07-04 15:32 | 2015-07-04 15:32 | 13.8KV 8D FEEDER #10 | Cloudy | Lightning | 36 | 8D OCB fdr #10 T/R 1x. Not checked yet. | 3041214 | 1 | 15:32 | Afternoon | Saturday | 2015 | 7
607 | 2015-07-04 15:32 | 2015-10-04 10:32 | 13.8KV 8D FEEDER #10 | Cloudy | Lightning | 36 | Checked & found, 8D OCB fdr #10 T/R 1x Ctr: 208-209 R/F: 50@1,@2. Patrolled the line & found, @2 broken Pin Insulator o/p #M8D-17. Cause: Lightning. | 3041214 | 1 | 15:32 | Afternoon | Saturday | 2015 | 7
608 | 2015-07-04 15:36 | 2015-07-04 15:36 | 13.8KV MENGGALA FEEDER #1 | Cloudy and Lightning | Lightning | 29 | Menggala OCB fdr #1 T/R 1x. Menggala fdr #2 dropped 13A (95-82A). Ground fault alarm On Menggala fdr #1. Not checked yet. | 3041212 | 1 | 15:36 | Afternoon | Saturday | 2015 | 7
609 | 2015-07-04 15:36 | 2015-10-04 07:45 | 13.8KV MENGGALA FEEDER #1 | Cloudy and Lightning | Lightning | 29 | Checked & found, Menggala OCB fdr #1 T/R 1x Ctr: 298-299 R/F: 51N(@1). Patrolled the line & found, @1 broken L/A on TP of Well No.Menggala #34. Cause: Lightning. | 3041212 | 1 | 15:36 | Afternoon | Saturday | 2015 | 7
610 | 2015-07-04 15:37 | 2015-07-04 15:37 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 46 | 8C VCB fdr #3 T/R 1x. 8C fdr #1 dropped 201A (280-79A). 8C fdr #4 dropped 250A (302-52A). T/O WIP at GS-2. Not checked yet. | 3041214 | 1 | 15:37 | Afternoon | Saturday | 2015 | 7
611 | 2015-07-04 15:37 | 2015-11-04 07:30 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 46 | Checked & found, 8C VCB fdr #3 T/R 1x Ctr: 476-477 R/F: 51@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041214 | 1 | 15:37 | Afternoon | Saturday | 2015 | 7
612 | 2015-07-04 16:30 | 2015-07-04 16:30 | MINAS POWER PLANT |  |  | - | 16:30 Off line MGT #8, then S/D the Unit for S/B. (Prior to replacing Fuel Nozzle set) |  | 1 | 16:30 | Afternoon | Saturday | 2015 | 7
613 | 2015-07-04 17:55 | 2015-07-04 17:55 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 109 | 3D OCB fdr #2 T/R 1x. 3D fdr #3 dropped 147A (175-28A). 3D fdr #4 dropped 239A (323-84A). 3D fdr #5 dropped 220A (226-6A). T/O WIP at GS-5. Not checked yet. | 3041214 | 1 | 17:55 | Afternoon | Saturday | 2015 | 7
614 | 2015-07-04 18:04 | 2015-07-04 18:04 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 17 | 5B OCB fdr #5 T/R 1x. 5B fdr #1 dropped 94A (100-6A). 5B fdr #2 dropped 157A (180-23A). 5B fdr #6 dropped 187A (190-3A). Not checked yet. | 3041214 | 1 | 18:04 | Afternoon | Saturday | 2015 | 7
615 | 2015-07-04 18:04 | 2015-10-04 08:04 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 17 | Checked & found, 5B OCB fdr #3 T/R 1x Ctr; 349-350 R/F: 51@1. Patrolled the line & found, @1 broken Dead end Insulator o/p #5B-112. Cause: Lightning. | 3041214 | 1 | 18:04 | Afternoon | Saturday | 2015 | 7
616 | 2015-07-04 18:09 | 2015-07-04 18:09 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 13 | 6D OCB fdr #4 T/R 1x. 6D fdr #6 dropped 71A (252-181A). Not checked yet. | 3041214 | 1 | 18:09 | Afternoon | Saturday | 2015 | 7
617 | 2015-07-04 18:09 | 2015-09-04 13:09 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 13 | Checked & found, 6D OCB fdr #4 T/R 1x Ctr: 531-532 R/F: 51@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041214 | 1 | 18:09 | Afternoon | Saturday | 2015 | 7
618 | 2015-07-04 18:12 | 2015-07-04 18:12 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 233 | 6D OCB fdr #5 T/R 1x. Not checked yet. | 3041214 | 1 | 18:12 | Afternoon | Saturday | 2015 | 7
619 | 2015-07-04 18:12 | 2015-09-04 13:12 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 233 | Checked & found, 6D OCB fdr #5 T/R 2x Ctr: 716-718 R/F: 51@2. Patrolled the line & found: -@3 Flashed over Dead end Insulator, and -@2 Broken Pin Insulator o/p #6D-07. -@2 Flashed over Pin Insulator o/p #NN. (near Well #5D-82E) Cause: Lightning. | 3041214 | 1 | 18:12 | Afternoon | Saturday | 2015 | 7
620 | 2015-08-04 00:33 | 2015-08-04 00:33 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 30 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3041212 | 1 | 0:33 | Night | Tuesday | 2015 | 8
621 | 2015-08-04 00:33 | 2015-10-04 07:33 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 30 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 143-144 R/F: 51N(@1). Patrolled the line & found, a dead Bird under pole #32AK-75. Cause: Animal. (Bird) | 3041212 | 1 | 0:33 | Night | Tuesday | 2015 | 8
622 | 2015-08-04 06:37 | 2015-08-04 06:37 | 13.8KV MENGGALA FEEDER #2 | Fair | Pin Insulator | 33 | Menggala OCB fdr #2 T/R 1x. Menggala GFPC T/R 1x. (Ground fault alarm on Menggala fdr#1 & fdr#2) Not checked yet. | 3041212 | 1 | 6:37 | Morning | Tuesday | 2015 | 8
623 | 2015-08-04 06:37 | 2015-11-04 07:38 | 13.8KV MENGGALA FEEDER #2 | Fair | Pin Insulator | 33 | Checked & found, Menggala OCB fdr #2 T/R 1x Ctr: 510-511 R/F: 51N. Patrolled the line & found, @1 flashed over Pin Insulator o/p #26AK-01. Cause: Pin Insulator. | 3041212 | 1 | 6:37 | Morning | Tuesday | 2015 | 8
624 | 2015-08-04 15:14 | 2015-08-04 15:14 | 13.8KV 6D FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 15:14 It was reported b/o fuse for Tx at Well #6B-66. (6D fdr #2) 18:35 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well #6B-66. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3041214 | 1 | 15:14 | Afternoon | Tuesday | 2015 | 8
625 | 2015-08-04 17:20 | 2015-08-04 17:20 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 40 | Bangko OCB fdr #4 T/R 1x. Ground fault alarm on Bangko fdr #1. Bangko GFPC, did not operate. (in blocked block for RIG HPS #09 Job) Not checked yet. | 3041212 | 1 | 17:20 | Afternoon | Tuesday | 2015 | 8
626 | 2015-08-04 17:20 | 2015-12-04 15:33 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 40 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99955-99956 R/F: 51N(@1). Patrolled the line & found, @1 broken Pin Insulator o/p #25Y-18. Cause: Pin Insulator. | 3041212 | 1 | 17:20 | Afternoon | Tuesday | 2015 | 8
627 | 2015-08-04 20:27 | 2015-08-04 20:27 | MINAS POWER PLANT |  |  | - | Off line MGT #10, then S/D the unit for S/B. (Prior to continue Generator Balancing) | 123 | 1 | 20:27 | Night | Tuesday | 2015 | 8
628 | 2015-09-04 06:25 | 2015-09-04 06:25 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | No.Duri VCB fdr #5 T/R 1x. No.Duri GFPC-TX #12 (Did not operate). Not checked yet. | 3041212 | 1 | 6:25 | Morning | Friday | 2015 | 9
629 | 2015-09-04 06:25 | 13/04/2015 09:25 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | Checked & found, No.Duri VCB fdr #5 T/R 1x Ctr: 100-101 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3041212 | 1 | 6:25 | Morning | Friday | 2015 | 9
630 | 2015-09-04 09:15 | 2015-09-04 09:15 | 13.8KV 8D FEEDER #11 | Fair | ESP Failure | - | 09:15 It was reported b/o fuse for Tx at Well #9E-22. (8D fdr #11) Checked & found, @1, @2 b/o 3.5SF fuses for 150Kva Tx at Well #9E-22. Performed TTR, Megger test the Tx & found, Zero Mega-Ohm Reading. Cause: ESP problem. (Reda motor Zero megger reading) (The Tx failure is not replaced yet) | 3041214 | 1 | 9:15 | Morning | Friday | 2015 | 9
631 | 2015-09-04 13:44 | 2015-09-04 13:44 | MINAS POWER PLANT |  |  | - | 13:44 S/U MGT #10, then online the Unit at 14:10. (Running on test for balancing after replacing Rotor) 15:28 Off line MGT #10, then S/D the Unit for S/B. (Prior to Continue balancing program) | 123 | 1 | 13:44 | Afternoon | Friday | 2015 | 9
632 | 2015-09-04 16:58 | 2015-09-04 16:58 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 135 | 16:58 OKB fdr #2 load dropped 190A (302-112A). 18:12 Checked & found, Recl. 38CW-08 (OKB fdr #2) T/SO. Ctr: 25-26. 18:15 Blocked & closed Recl. 38CW-08, Ok. Then release the block. Not patrolled yet. | 3041214 | 1 | 16:58 | Afternoon | Friday | 2015 | 9
633 | 2015-09-04 16:58 | 2015-11-04 08:00 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 135 | Patrolled the line, but found nothing. Cause: Suspected by Ligthning. | 3041214 | 1 | 16:58 | Afternoon | Friday | 2015 | 9
634 | 2015-10-04 08:30 | 2015-10-04 08:30 | MINAS POWER PLANT |  |  | - | 08:30 S/U MGT #8, then on line then Unit at 08:57. |  | 1 | 8:30 | Morning | Sunday | 2015 | 10
635 | 2015-10-04 10:10 | 2015-10-04 10:10 | MINAS POWER PLANT |  |  | - | 10:10 Off line MGT #6, then S/D the unit for S/B. 15:28 S/U MGT #6, then on line the Unit at 15:51. 17:15 Off line MGT #6, then S/D the Unit for S/B. |  | 1 | 10:10 | Morning | Sunday | 2015 | 10
636 | 2015-10-04 10:24 | 2015-10-04 10:24 | MINAS POWER PLANT |  |  | - | 10:24 S/U MGT #10, then on line the Unit at 10:57. 16:10 Off line MGT #10, then S/D the Unit for S/B. |  | 1 | 10:24 | Morning | Sunday | 2015 | 10
637 | 2015-10-04 10:45 | 2015-10-04 10:45 | DURI POWER PLANT |  |  | - | 10:45 S/U DGT #7, then on line the Unit at 11:05. |  | 1 | 10:45 | Morning | Sunday | 2015 | 10
638 | 2015-10-04 12:41 | 2015-10-04 12:41 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Rain and Lightning | Lightning | 162 | MSU #2 VCB fdr #1 (Nella fdr #1) T/R 1x. Not checked yet. | 3041212 | 1 | 12:41 | Afternoon | Sunday | 2015 | 10
639 | 2015-10-04 12:41 | 13/04/2015 13:41 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Rain and Lightning | Lightning | 162 | Checked & found, MSU-2 VCB fdr #1 (Neela fdr #1) T/R 1x Ctr: 192-193 R/F: 51@1,@2,@3. Patrolled the line & founs, @1 broken Pin Insulator o/p #21V-19. Cause: Lightning. | 3041212 | 1 | 12:41 | Afternoon | Sunday | 2015 | 10
640 | 2015-10-04 12:56 | 2015-10-04 12:56 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 56 | MSU#2 VCB fdr #2 (Nella fdr #2) T/R 1x. Not checked yet. | 3041212 | 1 | 12:56 | Afternoon | Sunday | 2015 | 10
641 | 2015-10-04 12:56 | 13/04/2015 13:56 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 56 | Checked & found, MSU-2 VCB fdr #2 (Nella fdr #2) T/R 1x Ctr: 204-205 R/F: 51@1,@2,@3. Patrolled the line & found, @1,@2 broken Pin Insulators o/p #19W-04. Cause: Lightning. | 3041212 | 1 | 12:56 | Afternoon | Sunday | 2015 | 10
642 | 2015-11-04 07:57 | 2015-11-04 07:57 | 13.8KV 8C FEEDER #2 | Fair | Low mega-ohm reading | 22 | 07:57 It was reported b/o fuse for Tx at Well #9D-26N. (8C fdr #2) 10:37 Checked & found, @1, @3 b/o 7.8SF fuses for 300Kva Tx at Well #9D-26N. Performed TTR, Megger test the Tx & found, Low Mega-ohm reading Tx. Cause: Low Mega-ohm reading Tx. (Will be replaced on Monday) | 3041214 | 1 | 7:57 | Morning | Wednesday | 2015 | 11
643 | 2015-11-04 07:57 | 13/04/2015 10:00 | 13.8KV 8C FEEDER #2 | Fair | Low mega-ohm reading | 22 | Replaced 300Kva Tx low megger reading with the same size at Well #9D-26N. Cause: Tx low megger reading. | 3041214 | 1 | 7:57 | Morning | Wednesday | 2015 | 11
644 | 2015-11-04 09:25 | 2015-11-04 09:25 | MINAS POWER PLANT |  |  | - | 09:25 S/U MGT #10, then online the unit at 09:47. 11:10 Offline MGT #10, then S/D the unit for S/B. 15:42 S/U MGT #10, then online the Unit at 15:28. |  | 1 | 9:25 | Morning | Wednesday | 2015 | 11
645 | 2015-11-04 09:46 | 2015-11-04 09:46 | MINAS POWER PLANT |  |  | - | 09:46 S/U MGT #6, then online the Unit at 10:28. 11:16 Offline MGT #6, then S/D the Unit for S/B. 14:40 S/U MGT #6, then online the Unit at 14:56. |  | 1 | 9:46 | Morning | Wednesday | 2015 | 11
646 | 2015-11-04 17:55 | 2015-11-04 17:55 | MINAS POWER PLANT |  |  | - | 17:55 Offline MGT #8, then S/D the Unit for S/B. (Prior to replacing Hydraulic pump) |  | 1 | 17:55 | Afternoon | Wednesday | 2015 | 11
647 | 2015-11-04 21:57 | 2015-11-04 21:57 | MINAS POWER PLANT |  |  | - | 21:57 Off line MGT #7, then S/D the Unit for S/B. | 123 | 1 | 21:57 | Night | Wednesday | 2015 | 11
648 | 2015-12-04 12:01 | 2015-12-04 12:01 | MINAS POWER PLANT |  |  | - | 12:01 Off line and then S/D MGT #6 for vibration balancing. 14:36 S/U MGT #6, then On line the Unit at 14:56. |  | 1 | 12:01 | Afternoon | Friday | 2015 | 12
649 | 2015-12-04 13:59 | 2015-12-04 13:59 | MINAS POWER PLANT |  |  | - | 13:59 S/U MGT #1, then On line at 14:43. (Running on Vibration test after replacing Generator Rotor) 16:14 Off line MGT #1, then S/D the Unit for S/B. (Prior to vibration balancing) |  | 1 | 13:59 | Afternoon | Friday | 2015 | 12
650 | 2015-12-04 18:00 | 2015-12-04 18:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | - | It was reported b/o fuses for Tx at Well Kulim #54. Not checked yet. | 3041212 | 1 | 18:00 | Afternoon | Friday | 2015 | 12
651 | 2015-12-04 18:00 | 13/04/2015 19:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | - | Checked Well Kulin #54 & found, normal. (The Tx is still in energize / No fuses for Tx burnt out) Checked at the HPU panel box & found, burnt out fuse for Pumping Unit motor. Cause: Unidentified (Fuse) at HPU panel box. | 3041212 | 1 | 18:00 | Afternoon | Friday | 2015 | 12
652 | 2015-12-04 19:00 | 2015-12-04 19:00 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 13 | So.Bekasap fdr #1 Load dropped 60A (155-95A). Not checked yet. | 3041212 | 1 | 19:00 | Night | Friday | 2015 | 12
653 | 2015-12-04 19:00 | 14/04/2015 08:35 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 13 | Checked & found, Recl. 34BI-18 (So.Bekasap fdr #1) T/R 1x Ctr: 133-134. Patrolled the line, but found nothing. Cause: Unidentified. | 3041212 | 1 | 19:00 | Night | Friday | 2015 | 12
654 | 2015-04-13 10:25 | 2015-04-13 10:25 | MINAS POWER PLANT |  |  | - | 10:25 S/U MGT #3, then On line the Unit at 10:49. (to restore the load during NDC #1 down) |  | 1 | 10:25 | Morning | Monday | 2015 | 4
655 | 2015-04-13 12:12 | 2015-04-13 12:12 | MINAS POWER PLANT |  |  | - | 12:12 S/U MGT #8, then On line the Unit at 12:50. (to restore the load during NDC #1 down) |  | 1 | 12:12 | Afternoon | Monday | 2015 | 4
656 | 2015-04-13 14:00 | 2015-04-13 14:00 | MINAS POWER PLANT |  |  | - | 14:00 S/U MGT #1, then On line the Unit at 14:24. (to restore the load during NDC #1 down) 14:38 Off line MGT #1, then S/D the Unit for vibration balancing. 15:13 S/U MGT #1, then on line the Unit at 15:30. |  | 1 | 14:00 | Afternoon | Monday | 2015 | 4
657 | 2015-04-13 14:43 | 2015-04-13 14:43 | MINAS POWER PLANT |  |  | - | 14:43 S/U MGT #7, then On Line the Unit at 14:59. | 123 | 1 | 14:43 | Afternoon | Monday | 2015 | 4
658 | 2015-04-13 15:43 | 2015-04-13 15:43 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 0 | 15:43 It was reported b/o fuses for Tx o/p #04-07-12. 17:00 Checked & found @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-07-12. Replaced the b/o fuse above with same size then energized the Tx. Cause: Unidentified (fuse). | 3041212 | 1 | 15:43 | Afternoon | Monday | 2015 | 4
659 | 2015-04-13 17:13 | 2015-04-13 17:13 | MINAS POWER PLANT | Rain and Lightning | Under investigation | - | 17:13 MGT #4 Tripped, By Alarm: Emergency Trip. (When the weather Rain & Lightning) Cause: Under investigation. 18:58 S/U MGT #4, then Online at 19:14. | 3041212 | 1 | 17:13 | Afternoon | Monday | 2015 | 4
660 | 2015-04-13 17:13 | 2015-04-13 17:13 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 40 | 8D OCB fdr #10 T/R 1x. 8D fdr #9 Load dropped 115A (187-72A). 8D fdr #11 Load dropped 58A (196-138A). Not checked yet. | 3041214 | 1 | 17:13 | Afternoon | Monday | 2015 | 4
661 | 2015-04-13 17:13 | 2015-04-17 08:50 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 40 | Checked & found, 8D OCB fdr #10 T/R 2x Ctr: 209-211 R/F: 51@1, @2, @3. Patrolled the Line & found, flashed over on Bypass Sw of Recl. 7E-21. Caused: Lightning. | 3041214 | 1 | 17:13 | Afternoon | Monday | 2015 | 4
662 | 2015-04-13 17:18 | 2015-04-13 17:18 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 24 | 8C VCB fdr #3 T/R 1x. 8C fdr #4 Load dropped 202A (246-44A). T/O WIP at GS-2. 8C fdr #1 Load dropped 136A (281-145A). Not checked yet. | 3041214 | 1 | 17:18 | Afternoon | Monday | 2015 | 4
663 | 2015-04-13 17:18 | 2015-04-16 13:18 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 24 | Checked & found, 8C VCB fdr #3 T/R 1x Ctr: 477-478 R/F: 51@1. Patrolled the line & found, @1 broken L/A o/p #8D-08. Cause: Lightning. | 3041214 | 1 | 17:18 | Afternoon | Monday | 2015 | 4
664 | 2015-04-13 17:21 | 2015-04-13 17:21 | MINAS POWER PLANT | Rain and Lightning | Under investigation | - | 17:21 MGT #1 Generator Breaker Tripped Off. By Alarm: Emergency Trip. (When the Weather Rain & Lightning) 17:28 Re-Closed MGT #1 Generator Breaker. (On line to the system) Cause: Under Investigation. | 3041212 | 1 | 17:21 | Afternoon | Monday | 2015 | 4
665 | 2015-04-13 17:21 | 2015-04-13 17:21 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 10 | Minas ACB fdr #1 T/R 1x Ctr: 046. (did not change) R/F: Not appear. Minas fdr #2 Load dropped 70A (172-102A). Minas fdr #3 Load dropped 70A (180-110A). Not checked yet. | 3041214 | 1 | 17:21 | Afternoon | Monday | 2015 | 4
666 | 2015-04-13 17:21 | 2015-04-15 11:01 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 10 | Patrolled Minas fdr #1 line & found, @2 broken Dead end Insulator o/p #NN. (near Well #6D-99A) Cause: Lightning. Also found, Recl. M2-01 (Minas fdr #2) T/R 1x Ctr: 31-32. Patrolled the line, but found nothing. Cause: Unidentified. | 3041214 | 1 | 17:21 | Afternoon | Monday | 2015 | 4
667 | 2015-04-13 17:24 | 2015-04-13 17:24 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Lightning | 108 | Minas ACB fdr #4 T/R 2x Ctr: 59-61 R/F: 51N. The line is not Patrolled yet. | 3041214 | 1 | 17:24 | Afternoon | Monday | 2015 | 4
668 | 2015-04-13 17:24 | 2015-04-16 13:24 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Lightning | 108 | Patrolled Minas fdr #4 line, but found nothing. Cause: Suspected by Lightning. Also found, Recl. 7D-121 (Minas fdr #4) T/R 2x Ctr: 04-06. Patrolled the line & found, @2 broken Dead end Insulator o/p #7D-136. Cause: Lightning. | 3041214 | 1 | 17:24 | Afternoon | Monday | 2015 | 4
669 | 2015-04-13 17:33 | 2015-04-13 17:33 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Minas 13.8KV ACB #21 (44KV Minas - Rumbai line) T/R 1x Ctr: 66-67 R/F: not checked yet. Not checked Yet. | 3041214 | 1 | 17:33 | Afternoon | Monday | 2015 | 4
670 | 2015-04-13 17:33 | 2015-04-16 13:04 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Patrolled 44KV Minas - Rumbai line, but found nothing. Cause: Suspected by Lightning. | 3041214 | 1 | 17:33 | Afternoon | Monday | 2015 | 4
671 | 2015-04-13 17:45 | 2015-04-13 17:45 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 17:45 It was reported b/o fuse for Tx at Well North Menggala #21. (Menggala fdr #1) Checked & found, @3 b/o 14.0SF fuse for 500Kva Tx at Well North Menggala #21. Performed TTR, Megger test the TX & found, normal. (good reading) Replaced b/o fuse above with the same size & Energized the Tx. Cause: Unidentified (Fuse). | 3041212 | 1 | 17:45 | Afternoon | Monday | 2015 | 4
672 | 2015-04-13 19:38 | 2015-04-13 19:38 | NORTH DURI POWER PLANT |  |  | - | 19:38 Off line NDC-CT #1, then S/D the Unit at 19:41. (For NSB - Prior to C/I program) | 123 | 1 | 19:38 | Night | Monday | 2015 | 4
673 | 2015-04-14 07:56 | 2015-04-14 07:56 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 0 | It was reported b/o fuses for Tx o/p #03-03-05. Not checked yet. | 3041212 | 1 | 7:56 | Morning | Tuesday | 2015 | 4
674 | 2015-04-14 07:56 | 2015-04-15 08:00 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 0 | 08:00 Checked & found, @1,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #03-03-05. Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Squirrel) | 3041212 | 1 | 7:56 | Morning | Tuesday | 2015 | 4
675 | 2015-04-14 09:30 | 2015-04-14 09:30 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified | 5 | 09:30 C.Duri fdr #9 load dropped 36A (149-113A). It was reported by CGS-4, that no power at CGS-4 office. 10:34 Checked & found, Recl. 04-05-02 (C.Duri fdr #9) T/SO. Ctr: 163-164. 10:40 Blocked & closed Recl. 04-05-02, Ok. Then released the block. 10:57 Patrolled the line, but found nothing. Caused: Unidentified. | 3041212 | 1 | 9:30 | Morning | Tuesday | 2015 | 4
676 | 2015-04-15 06:18 | 2015-04-15 06:18 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 87 | Sintong OCB fdr #1 T/R 1x. Sintong fdr #2 Load dropped 133A (190-57A). Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #1) Not checked yet. | 3041212 | 1 | 6:18 | Morning | Wednesday | 2015 | 4
677 | 2015-04-15 06:18 | 2015-04-17 16:18 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 87 | Checked & found, Sintong OCB fdr #1 T/R 1x Ctr: 355-356 R/F: 51@2,@3. Patrolled the line & found, @3 broken jumper on TOP of Well Seruni #32. Cause: Lightning. | 3041212 | 1 | 6:18 | Morning | Wednesday | 2015 | 4
678 | 2015-04-15 14:35 | 2015-04-15 14:35 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 8 | Pungut OCB fdr #2 T/R 1x. Pungut fdr #1 load dropped 10A (64-54A). Pungut RTU was Failed. Not checked yet. | 3041212 | 1 | 14:35 | Afternoon | Wednesday | 2015 | 4
679 | 2015-04-15 14:35 | 2015-04-17 17:35 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 8 | Checked & found, Pungut OCb fdr #2 T/R 1x Ctr: 51-52 R/F: 51N(@1). Patrolled the line & found, @1 broken Pin Insulator o/p #44BY-10. Cause: Lightning. | 3041212 | 1 | 14:35 | Afternoon | Wednesday | 2015 | 4
680 | 2015-04-15 17:21 | 2015-04-15 17:21 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 17:21 It was reported b/o fuse for Tx o/p #04-05-08. (C.Duri fdr #9) 19:30 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-05-08. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentfied (Fuse). | 3041212 | 1 | 17:21 | Afternoon | Wednesday | 2015 | 4
681 | 2015-04-15 17:27 | 2015-04-15 17:27 | 13.8KV MENGGALA FEEDER #1 | Fair | Broken Fuse Holder | 140 | 17:27 Menggala fdr #1 load dropped 137A (177-40A). Menggala GFPC T/R 1x. 18:53 Checked & found, Recl. 19AN-04 (Menggala fdr #1) T/SO. Ctr: 298-299 R/F: 51@1@2. (The Recloser was blocked for Rig aktivity) 19:00 Blocked & closed Recl. 19AN-04, Ok. Then release the block. The line is not patrolled yet. | 3041212 | 1 | 17:27 | Afternoon | Wednesday | 2015 | 4
682 | 2015-04-15 17:27 | 2015-04-17 07:52 | 13.8KV MENGGALA FEEDER #1 | Fair | Broken Fuse Holder | 140 | Patrolled the line & found, @1,@2 b/o fuses & broken Fuse holder for 500Kva Tx. (at Well No.Menggala #21) Cause: Broken Jumper. | 3041212 | 1 | 17:27 | Afternoon | Wednesday | 2015 | 4
683 | 2015-04-15 18:00 | 2015-04-15 18:00 | 13.8KV SINTONG FEEDER #1 | Rain | Powerline - Jumper | 25 | It was reported that b/o fuse for Tx at Well Seruni #32. Not checked yet. | 3041212 | 1 | 18:00 | Afternoon | Wednesday | 2015 | 4
684 | 2015-04-15 18:00 | 2015-04-16 10:24 | 13.8KV SINTONG FEEDER #1 | Rain | Powerline - Jumper | 25 | 09:02 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Seruni #32. Also found, @3 broken Jumper on FCO on TP of Well Seruni #32. Performed TTR, Megger test the Tx & found, normal. (good reading) 10:24 Repaired the boken jumper & replaced b/o fuse above, then energized the Tx. Cause: Broken Jumper. | 3041212 | 1 | 18:00 | Afternoon | Wednesday | 2015 | 4
685 | 2015-04-15 18:21 | 2015-04-15 18:21 | 13.8KV MENGGALA FEEDER #1 | Rain | Unidentified (Fuse) | 7 | It was reported that b/o fuse for Tx at Well No.Menggala #21. Not checked yet. | 3041212 | 1 | 18:21 | Afternoon | Wednesday | 2015 | 4
686 | 2015-04-15 18:21 | 2015-04-16 11:40 | 13.8KV MENGGALA FEEDER #1 | Rain | Unidentified (Fuse) | 7 | 09:20 Checked & found, @1,@2 b/o 14.0SF fuses for 500Kva Tx at Well No.Menggala #21. Performed TTR, Megger test the Tx & found, normal. (good reading) 11:40 Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3041212 | 1 | 18:21 | Afternoon | Wednesday | 2015 | 4
687 | 2015-04-16 15:51 | 2015-04-16 15:51 | 13.8KV PETANI FEEDER #2 | Fair | Dead End Insulator | 12 | Petani OCB fdr#2 T/R 1x. Not checked yet. | 3041212 | 1 | 15:51 | Afternoon | Thursday | 2015 | 4
688 | 2015-04-16 15:51 | 2015-04-17 17:51 | 13.8KV PETANI FEEDER #2 | Fair | Dead End Insulator | 12 | Checked & found, Petani OCB fdr #2 T/R 1x Ctr: 169-170 R/F: 51N(@1). Patrolled the line & found, @1 F/O Dead end Insulator o/p #33AX-47. Cause: Dead end Insulator. | 3041212 | 1 | 15:51 | Afternoon | Thursday | 2015 | 4
689 | 2015-04-16 21:53 | 2015-04-16 21:53 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 21:53 It was reported b/o fuses for Tx at Well Topas #06. 23:10 Checked & found, @1 b/o 7.8SF fuse for 250Kva Tx at Well Topas #06. Replaced the b/o fuse with same size, then energized the Tx. Cause: Unidentified (fuse). | 3041214 | 1 | 21:53 | Night | Thursday | 2015 | 4
690 | 2015-04-17 02:36 | 2015-04-17 02:36 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Transformer Failure | 60 | 02:36 It was reported b/o fuse for Tx at Well KB #325. (CKBS fdr #5) 16:00 Checked & found, @1 b/o 7.8SF fuse for 250Kva Tx at Well KB #325. (Also found, burnt out Surface cable from Switchboard toward junction box) Performed TTR, Megger test the Tx & found, unbalance TTR. (Tx failure) 17:30 Then replaced 250Kva Tx failure with 300Kva Tx & energized the Tx. Cause: Tx failure. | 3041214 | 1 | 2:36 | Night | Friday | 2015 | 4
691 | 2015-04-17 06:37 | 2015-04-17 06:37 | 13.8KV S. BALAM GFPC | Fair | Unidentified (Fuse) | 0 | 06:37 So.Balam GFPC T/R 1x. Fault alarm on So.Balam fdr #4. No load dropped at any fdrs. 11:35 Checked & found, So.Balam GFPC T/R 1x Ctr: 184-185. Patrollede So.Balam fdr #4 line & found, b/o fuse for Tx at Well SE.Balam #19. Cause: Transformer Failure. | 3041212 | 1 | 6:37 | Morning | Friday | 2015 | 4
692 | 2015-04-17 09:59 | 2015-04-17 09:59 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified (Fuse) | 2 | 09:59 It was reported b/o fuse for Tx at Well SE.Balam #19. (So.Balam fdr #4) 12:07 Checked & found, @2 b/o 3.1SF fuse for 150Kva Tx at Well SE.Balam #19. Performed TTR, Megger test the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & Energized The Tx. Cause: Unidentified (Fuse). | 3041212 | 1 | 9:59 | Morning | Friday | 2015 | 4
693 | 2015-04-17 11:03 | 2015-04-17 11:03 | 13.8KV S. BALAM FEEDER #1 | Fair | Lightning Arrester | 0 | 11:03 So.Balam GFPC T/R 1x. Fault alarm on So.Balam fdr #1. No load dropped at any fdrs. 11:35 It was reported that no power at Antara Test Sta. 13:40 Checked & found, So.Balam GFPC T/R 2x Ctr: 185-187. Also found, Recl. 15Y-01 (So.Balam fdr #1) T/SO. Ctr: 209-210 R/F: 51@3. Patrolled the line & found, @3 broken L/A & the jumper touching to cross arm o/p #15Y-08. 14:00 Blocked & closed Recl. 15Y-01, Ok. Then released the block. Cause: Lightning Arrester. Note: Load of Recl. 15Y-01 (So.Balam fdr #1) is Security lighting & Antara Test sta. The load is less then 4A, it is not detected by DSC alarm setting. | 3041212 | 1 | 11:03 | Morning | Friday | 2015 | 4
694 | 2015-04-17 14:58 | 2015-04-17 14:58 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified (Fuse) | 1 | 14:58 It was reported b/o fuse for Tx o/p #09-P3-06. 16:58 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #09-P3-06. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3041212 | 1 | 14:58 | Afternoon | Friday | 2015 | 4
695 | 2015-04-17 15:50 | 2015-04-17 15:50 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 53 | Sintong OCB fdr #2 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. | 3041212 | 1 | 15:50 | Afternoon | Friday | 2015 | 4
696 | 2015-04-17 15:50 | 2015-04-19 15:00 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 53 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 380-381 R/F: 51N. Also found Sintong GFPC T/R 2x Ctr: 741-743. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041212 | 1 | 15:50 | Afternoon | Friday | 2015 | 4
697 | 2015-04-17 16:53 | 2015-04-17 16:53 | 13.8KV PETAPAHAN FEEDER #1 | Rain and Lightning | Lightning | 12 | 16:53 Petapahan fdr #1 load dropped 30A (85-55A). 17:34 Checked & found, Recl. 30CZ-01 (Petapahan fdr #1) T/R 1x Ctr: 66-67. The line is not patrolled yet. | 3041214 | 1 | 16:53 | Afternoon | Friday | 2015 | 4
698 | 2015-04-17 16:53 | 2015-04-18 07:43 | 13.8KV PETAPAHAN FEEDER #1 | Rain and Lightning | Lightning | 12 | Patrolled the Line under Recl. 30CZ-01, but found nothing. Cause: Suspected by Lightning. | 3041214 | 1 | 16:53 | Afternoon | Friday | 2015 | 4
699 | 2015-04-17 18:03 | 2015-04-17 18:03 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 1 | Pematang fdr #1 load dropped 145A (167-22A). Pematang fdr #2 load dropped 24A (71-47A)> Not checked yet. | 3041212 | 1 | 18:03 | Afternoon | Friday | 2015 | 4
700 | 2015-04-17 18:03 | 2015-04-21 15:27 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 1 | Checked & found, Recl. 35BC-14 (Pematang fdr #1) T/R 1x Ctr: 34-35. Patrolled the line & found, @1 broken Pin Insulator o/p #34BC-40. Cause: Lightning. | 3041212 | 1 | 18:03 | Afternoon | Friday | 2015 | 4
701 | 2015-04-17 21:05 | 2015-04-17 21:05 | 13.8KV PEMATANG FEEDER #1 | Fair | Low mega-ohm reading | 0 | 21:05 It was reported b/o fuse for Tx at Well Pematang #49. (Pematang fdr #1) 22:10 Checked & found, @2 b/o 3.5SF fuse for 150Kva Tx at Well Pematang #49. Performed TTR, Megger tested the Tx & found, Low megger reading. Cause: Tx Low megger reading. (The Tx is not replaced yet) | 3041212 | 1 | 21:05 | Night | Friday | 2015 | 4
702 | 2015-04-17 21:05 | 2015-04-19 10:05 | 13.8KV PEMATANG FEEDER #1 | Fair | Low mega-ohm reading | 0 | Replaced 150Kva Tx failure with the same size & energized the Tx. Cause: Tx low megger reading. | 3041212 | 1 | 21:05 | Night | Friday | 2015 | 4
703 | 2015-04-18 00:38 | 2015-04-18 00:38 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Unidentified (Fuse) | 41 | 00:38 It was reported b/o fuse for Tx at Well Petapahan#25. (Petapahan fdr #1) 09:50 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Petapahan #25. Replaced b/o fuse above with the same size & Energized the Tx. Cause: Unidentified (Fuse). | 3041214 | 1 | 0:38 | Night | Saturday | 2015 | 4
704 | 2015-04-18 00:40 | 2015-04-18 00:40 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified (Fuse) | 5 | 00:40 It was reported b/o fuse for Tx at Well Benar #07. (Sintong fdr #2) 10:15 Checked & found, @1 b/o 2.1SF fuse for 100Kva Tx at Well Benar #07. Replaced the b/o fuse above with the same size & Energized the Tx. Cause: Unidentified (Fuse). | 3041212 | 1 | 0:40 | Night | Saturday | 2015 | 4
705 | 2015-04-18 17:13 | 2015-04-18 17:13 | 13.8KV 3D FEEDER #4 | Cloudy and Lightning | Lightning | 52 | 3D OCB fdr #4 T/R 1x. 3D fdr #2 load dropped 46A (245-199A). 3D fdr #3 load dropped 19A (173-154A). 3D fdr #5 load dropped 129A (228-99A). T/O WIP at GS-5. Not checked Yet. | 3041214 | 1 | 17:13 | Afternoon | Saturday | 2015 | 4
706 | 2015-04-18 17:13 | 2015-04-21 10:31 | 13.8KV 3D FEEDER #4 | Cloudy and Lightning | Lightning | 52 | Checked & found, 3D OCB fdr #4 T/R 1x Ctr: 149-150 R/F: 50@2,@3. Patrolled the line, but found nothing. Also found, Recl. 2D-38 (3D fdr #4) T/R 1x Ctr: 451-452. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041214 | 1 | 17:13 | Afternoon | Saturday | 2015 | 4
707 | 2015-04-18 17:50 | 2015-04-18 17:50 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | No.Duri VCB fdr #7 T/R 1x. Ground fault Alarm on No.Duri fdr #7. Not checked yet. | 3041212 | 1 | 17:50 | Afternoon | Saturday | 2015 | 4
708 | 2015-04-18 17:50 | 2015-04-22 07:18 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | Checked & found, No.Duri VCB fdr #7 T/R 1x Ctr: 183. (did not change) R/F: 51@1,@2. Patrolled the line, but found nothing. Cause: Unidentified. | 3041212 | 1 | 17:50 | Afternoon | Saturday | 2015 | 4
709 | 2015-04-19 06:06 | 2015-04-19 06:06 | MINAS POWER PLANT |  |  | - | 06:06 MGT #3 Tripped. By Alarm: SRV control problem. 10:30 S/U MGT # 3, then On Line the Unit at 10:35. (After Repairing Gas fuel valve SRV) | 123 | 1 | 6:06 | Morning | Sunday | 2015 | 4
710 | 2015-04-19 11:40 | 2015-04-19 11:40 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Transformer Failure | 57 | 11:40 It was reported b/o fuse for Tx at Well KB #321. (CKBS fdr #1) 16:30 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well KB #321. Performed TTR, Megger test the Tx & found, Low Megger reading. Cause: Transformer failure. (Low megger reading) (The Tx is not replaced yet) | 3041214 | 1 | 11:40 | Morning | Sunday | 2015 | 4
711 | 2015-04-19 11:40 | 2015-04-20 10:48 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Transformer Failure | 57 | Replaced 150Kva Tx with 300Kva Tx, then energized the Tx at Well KB #321. Cause: Low Mega-ohm Reading Tx. | 3041214 | 1 | 11:40 | Morning | Sunday | 2015 | 4
712 | 2015-04-19 13:00 | 2015-04-19 13:00 | 13.8KV RANGAU FEEDER #2 | Fair | Transformer Failure | 43 | 13:00 It was reported b/o fuse for Tx at Well Jurong #13. (Rangau fdr #2) 16:00 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Jurong #13. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Transformer failure. (Low megger reading) (The Tx is not replaced yet) | 3041212 | 1 | 13:00 | Afternoon | Sunday | 2015 | 4
713 | 2015-04-19 13:00 | 2015-04-20 13:00 | 13.8KV RANGAU FEEDER #2 | Fair | Transformer Failure | 43 | Replaced 150Kva Tx with the same size, then energized the Tx. Cause: Low Mega-ohm Reading Tx. | 3041212 | 1 | 13:00 | Afternoon | Sunday | 2015 | 4
714 | 2015-04-19 23:57 | 2015-04-19 23:57 | DURI POWER PLANT |  |  | - | 23:57 DGT #7 tripped off, By Alarm: Generator Differential. R/F: 40, 62GN, 86G & 87 @1, @2 &@3. Cause: Under investigation. (Suspected Excitation proublem) (DGT #7 - Status S/B) | 123 | 1 | 23:57 | Night | Sunday | 2015 | 4
715 | 2015-04-20 06:34 | 2015-04-20 06:34 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Low mega-ohm reading | 0 | 06:34 It was reported b/o fuse for Tx o/p #03-01-17. (C.Duri fdr #7) 14:00 Checked & found, @1,@2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #03-01-17. Performed TTR, Megger test the Tx & found, Low mega Ohm reading Tx. 18:33 Replaced 112.5KvaTx with the same size & Energized the Tx. Cause: Low Mega Ohm Megger. | 3041212 | 1 | 6:34 | Morning | Monday | 2015 | 4
716 | 2015-04-21 10:34 | 2015-04-21 10:34 | 115KV KOTABATAK JUNCTION - 3D LINE | Rain and Lightning | Lightning | 0 | 10:34 115KV 3D OCB #21 T/O. 115KV KBJ GCB #23 (In open position for Maintenance) 115KV KBJ GCB #27 T/R 1x. (115KV KBJ - 3D line) 11:33 Checked & found, 115KV 3D GCB #21 T/O. (In block position) Ctr: 125-126. Closed 115KV 3D GCB #21, Ok. (then put 79SEL on S/C) Not checked & patrolled yet. | 3041214 | 1 | 10:34 | Morning | Tuesday | 2015 | 4
717 | 2015-04-21 10:34 | 2015-04-24 07:14 | 115KV KOTABATAK JUNCTION - 3D LINE | Rain and Lightning | Lightning | 0 | Checked & found: -115KV 3D GCB #21 T/SO. Ctr: 125-126 -115KV KBJ OCB #23 (In open position for Maintenance) -115KV KBJ OCB #27 T/R 1x Ctr: 61-62 R/F: 87L@1 & 21G-@1. (115KV KBJ - 3D line) Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041214 | 1 | 10:34 | Morning | Tuesday | 2015 | 4
718 | 2015-04-21 10:42 | 2015-04-21 10:42 | 13.8KV 5B FEEDER #5 | Rain and Lightning | Lightning | 0 | 5B OCB fdr #5 T/R 1x. Not checked yet. | 3041214 | 1 | 10:42 | Morning | Tuesday | 2015 | 4
719 | 2015-04-21 10:42 | 2015-04-23 15:35 | 13.8KV 5B FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, 5B OCB fdr #5 T/R 1x Ctr: 258-259 R/F: 51N. Patrolled the line & found, @1 broken Pin Insulator o/p #NN. (near Well #5B-38) Cause: Lightning. | 3041214 | 1 | 10:42 | Morning | Tuesday | 2015 | 4
720 | 2015-04-21 10:44 | 2015-04-21 10:44 | 13.8KV 5B FEEDER #8 | Rain and Lightning | Lightning | 0 | 5B OCB fdr #8 T/R 1x. Not checked yet. | 3041214 | 1 | 10:44 | Morning | Tuesday | 2015 | 4
721 | 2015-04-21 10:44 | 2015-04-23 15:44 | 13.8KV 5B FEEDER #8 | Rain and Lightning | Lightning | 0 | Checked & found, 5B OCB fdr #8 T/R 1x Ctr: 9947-9948 R/F: Not appear. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041214 | 1 | 10:44 | Morning | Tuesday | 2015 | 4
722 | 2015-04-21 10:45 | 2015-04-21 10:45 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 108 | 3D OCB fdr #3 T/R 1x. 3D fdr #2 Load dropped 133A (237-104A). 3D fdr #4 Load dropped 123A (286-163A). 3D fdr #5 Load dropped 225A (230-5A). (T/O WIP at GS-5) Not checked yet. | 3041214 | 1 | 10:45 | Morning | Tuesday | 2015 | 4
723 | 2015-04-21 10:45 | 2015-04-24 07:45 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 108 | Checked & found, 3D OCB fdr #3 T/R 2x Ctr: 573-575 R/F: 50@1,@2,@3. Patrolled the line & found: -@1 Broken Dead end Insulator o/p #4C-37. -@1 Broken Dead end Insulator o/p #4C-33. Cause: Lightning. | 3041214 | 1 | 10:45 | Morning | Tuesday | 2015 | 4
724 | 2015-04-21 10:47 | 2015-04-21 10:47 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 49 | 6D OCB fdr #1 T/R 1x. Not checked yet. | 3041314 | 1 | 10:47 | Morning | Tuesday | 2015 | 4
725 | 2015-04-21 10:47 | 2015-04-24 07:47 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 49 | Checked & found, 6D OCB fdr #1 T/R 1x Ctr: 289-290 R/F: 51N. Patrolled the line & found, @3 flashed over Dead end Insulator o/p #5C-43. Cause: Lightning. | 3041314 | 1 | 10:47 | Morning | Tuesday | 2015 | 4
726 | 2015-04-21 10:59 | 2015-04-21 10:59 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 0 | 5B OCB fdr #2 T/R 1x. 5B fdr #1 Load dropped 61A (93-32A). 5B fdr #3 Load dropped 42A (123-81A). Not checked yet. | 3041214 | 1 | 10:59 | Morning | Tuesday | 2015 | 4
727 | 2015-04-21 10:59 | 2015-04-23 13:30 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 328-329 R/F: 51@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041214 | 1 | 10:59 | Morning | Tuesday | 2015 | 4
728 | 2015-04-21 15:39 | 2015-04-21 15:39 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 0 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3041212 | 1 | 15:39 | Afternoon | Tuesday | 2015 | 4
729 | 2015-04-21 15:39 | 2015-04-24 15:39 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 972-973 R/F: 51N(@2) Patrolled the line & found, @2 flashed over FCO for Tx on TP of Well Kopar #09. Cause: Lightning. | 3041212 | 1 | 15:39 | Afternoon | Tuesday | 2015 | 4
730 | 2015-04-21 15:42 | 2015-04-21 15:42 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Pematang fdr #1 load dropped 78A (168-90A). Not checked yet. | 3041212 | 1 | 15:42 | Afternoon | Tuesday | 2015 | 4
731 | 2015-04-21 15:42 | 2015-04-22 16:18 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 35BC-14 (Pematang fdr #1) T/R 1x Ctr: 35-36. Patrolled the line & found, @1 flashed over Dead end Insulator on TP of Well Pematang #42. Cause: Lightning. | 3041212 | 1 | 15:42 | Afternoon | Tuesday | 2015 | 4
732 | 2015-04-21 15:43 | 2015-04-21 15:43 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 46 | Petani fdr #2 load dropped 57A (63-6A). (Petani-Rangau RTU failed at that time) Not checked yet. | 3041212 | 1 | 15:43 | Afternoon | Tuesday | 2015 | 4
733 | 2015-04-21 15:43 | 2015-04-24 15:47 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 46 | Checked & found, Petani OCB fdr #2 T/R 1x Ctr: 170-171 R/F: 51@2. Patrolled the line & found, @2 broken Pin Insulator o/p #33AX-51. Cause: Lightning. | 3041212 | 1 | 15:43 | Afternoon | Tuesday | 2015 | 4
734 | 2015-04-21 16:09 | 2015-04-21 16:09 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 4 | Bekasap Main fdr #2 load dropped 92A (173-81A). Bekasap GFPC T/R 1x. (Fault alarm on Bekasap Main fdr #2) Not checked yet. | 3041212 | 1 | 16:09 | Afternoon | Tuesday | 2015 | 4
735 | 2015-04-21 16:25 | 2015-04-21 16:25 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 70 | Bekasap Main OCB fdr #2 T/R 1x. Bekasap GFPC T/R 1x. (Fault alarm on Bekasap Main fdr #2) Not checked yet. | 3041212 | 1 | 16:25 | Afternoon | Tuesday | 2015 | 4
736 | 2015-04-21 16:25 | 2015-04-22 16:25 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 70 | Checked & found, Bekasap OCB fdr #2 T/R 1x Ctr: 863-864 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041212 | 1 | 16:25 | Afternoon | Tuesday | 2015 | 4
737 | 2015-04-21 17:00 | 2015-04-21 17:00 | 13.8KV 4D FEEDER #1 | Fair | Transformer Failure | 108 | It was reported that no power at Well #4D-35. Checked & found, @1, @3 14.0SF fuses for 550Kva Tx at Well #4D-35. Perform TTR, Megger test the Tx & found, Low megger reading. Cause: Tx failure. (The Tx is not replaced yet) | 3041214 | 1 | 17:00 | Afternoon | Tuesday | 2015 | 4
738 | 2015-04-21 17:00 | 2015-04-22 18:07 | 13.8KV 4D FEEDER #1 | Fair | Transformer Failure | 108 | Replaced 550Kva Tx with the same size, then energized the Tx at Well #4D-35. Cause: Tx Failure. | 3041214 | 1 | 17:00 | Afternoon | Tuesday | 2015 | 4
739 | 2015-04-21 17:06 | 2015-04-21 17:06 | 13.8KV CENTRAL DURI FEEDER #11 | Rain and Lightning | Capasitor Bank | 118 | 17:06 C.Duri ACB fdr #11 T/LO. Ctr: 251 (did not change) R/F: 51N. 18:53 Patrolled the line toward LBS #05-M7-24, but found nothing. Then Opened LBS #05-M7-24. Blocked & close, C.Duri ACB fdr #11, Ok. Continued patrolled downstream of LBS #05-M7-24, but found nothing. 19:50 Manually Open C.Duri ACB fdr #11, to Close LBS #05-M7-24. 19:53 Blocked & Closed C.Duri ACB fdr #11, but the feeder trip again. Re-patrolled the line & found, broken 600KVAR Cap Bank at CGS-5. Then Isolated it is Cap Bank. 20:14 Blocked & Closed C.Duri ACB fdr #11, Ok. Then released the Block. Cause: Capacitor Bank. | 3041212 | 1 | 17:06 | Afternoon | Tuesday | 2015 | 4
740 | 2015-04-21 17:10 | 2015-04-21 17:10 | DURI POWER PLANT |  |  | - | 17:10 S/U DGT #7, then on line the Unit at 18:00. |  | 1 | 17:10 | Afternoon | Tuesday | 2015 | 4
741 | 2015-04-22 11:27 | 2015-04-22 11:27 | 13.8KV PEMATANG FEEDER #1 | Fair | Planned Maintenance | 2 | 11:27 Blocked Pematang fdr #1 to replace @2 serious broken Pin insulator o/p #34-BC-40. (2 Wells were off during this job done) 12:10 Normalized blocked Pematang fdr #1. Cause: Planned Maintenance. | 123 | 1 | 11:27 | Morning | Wednesday | 2015 | 4
742 | 2015-04-22 13:17 | 2015-04-22 13:17 | 13.8KV LIBO FEEDER #2 | Fair | Theft | 25 | 13:17 It was reported theft case on Tx at Well Hitam #02. (Libo fdr #2) 15:08 Checked & found, Opened all Fuses & vandalism on 300Kva Tx at Well Hitam #02. (Tx oil volume: +/- 400 liters) Cause: Theft. | 3041212 | 1 | 13:17 | Afternoon | Wednesday | 2015 | 4
743 | 2015-04-22 14:31 | 2015-04-22 14:31 | 13.8KV BATANG FEEDER #2 | Fair | Planned Maintenance | 0 | 14:31-15:31 Shutdown Well Rantaubais #15, to replace 150Kva Tx leakage oil with the same size. (Well Rantaubais #15 was off during the job done) Cause: Planned Maintenance. | 123 | 1 | 14:31 | Afternoon | Wednesday | 2015 | 4
744 | 2015-04-22 17:58 | 2015-04-22 17:58 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified (Fuse) | 17 | 17:58 It was reported b/o fuse for Tx at Well Cebakan #05. (Bekasap fdr #6) 12:25 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Cebakan #5. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3041212 | 1 | 17:58 | Afternoon | Wednesday | 2015 | 4
745 | 2015-04-22 20:44 | 2015-04-22 20:44 | 13.8KV 4D FEEDER #2 | Heavy Rain | Lightning | 134 | 20:44 4D OCB fdr #2 T/R 1x. 4D fdr #1 load dropped 195A (198-3A). 4D fdr #3 load dropped 58A (80-22A). Not checked & patrolled yet. (Load 4D fdr #2 is 48A more to normal load / 188A) 22:23 Checked & found, Recl. 4D-204 (4D fdr #2) T/SO. Ctr: 74-75. Blocked & closed Recl. 4D-204, Ok. Then released the Block. The line is not patrolled yet. | 3041214 | 1 | 20:44 | Night | Wednesday | 2015 | 4
746 | 2015-04-22 20:44 | 2015-04-24 14:44 | 13.8KV 4D FEEDER #2 | Heavy Rain | Lightning | 134 | Checked & found, 4D OCB fdr #2 T/R 1x Ctr: 205-206 R/F: 51@1,@2. Patrolled the line & found, @1,@2 b/o 0.5Kva Tx o/p #2D-204. (PT for Recl. 2D-204) Cause: Suspected by: Lightning. Patrolled downstream of Rec. 2D-204 & found, @1 F/O PIn & @3 broken Dead end Insulator o/p #NN. (near Well #3D-86) Cause: Lightning. | 3041214 | 1 | 20:44 | Night | Wednesday | 2015 | 4
747 | 2015-04-23 10:15 | 2015-04-23 10:15 | 13.8KV PEMATANG FEEDER #2 | Fair | Animal | 7 | 10:15 It was reported b/o fuse for Tx at Well Pematang #50. (Pematang fdr #1) 11:30 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Pematang #50. Then replaced b/o fuse above with the same size & energized the Tx. Caused: Animal. (Monkey) | 3041212 | 1 | 10:15 | Morning | Thursday | 2015 | 4
748 | 2015-04-23 16:10 | 2015-04-23 16:10 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri ACB fdr #16 T/R 1x Ctr: 279-280 R/F: 51N & 51@1,@2. The line is not patrolled yet. | 3041212 | 1 | 16:10 | Afternoon | Thursday | 2015 | 4
749 | 2015-04-23 16:10 | 2015-04-27 17:10 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3041212 | 1 | 16:10 | Afternoon | Thursday | 2015 | 4
750 | 2015-04-23 16:40 | 2015-04-23 16:40 | NORTH DURI POWER PLANT |  |  | - | 16:40 S/U NDC-CT #1, then on line the Unit at 17:08. (Running on test after C/I) |  | 1 | 16:40 | Afternoon | Thursday | 2015 | 4
751 | 2015-04-23 18:45 | 2015-04-23 18:45 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Transformer Failure | 3 | It was reported b/o fuse for Tx o/p #09-P3-06. (C.Duri fdr #16) Not checked yet. | 3041212 | 1 | 18:45 | Afternoon | Thursday | 2015 | 4
752 | 2015-04-23 18:45 | 2015-04-25 10:25 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Transformer Failure | 3 | 10:25 Checked & found @2@3 B/O fuse for 112.5 Kva Tx o/p 09-P3-06. 11:50 Replaced B/O 112.5Kva Tx with the same size. Cause: Tx Failure (Over load). | 3041212 | 1 | 18:45 | Afternoon | Thursday | 2015 | 4
753 | 2015-04-24 10:00 | 2015-04-24 10:00 | 13.8KV MINAS FEEDER #3 | Fair | Transformer Failure | 54 | 10:00 It was reported b/o fuse for Tx at Well #8C-48E. (Minas fdr #3) 14:15 Checked & found, @2,@3 b/o 3.5SF fuses for 150Kva Tx at Well #8C-48E. Performed TTR, Megger the Tx & found, Low megger reading. 16:00 Replaced 150Kva Tx with the same size & energized the Tx. Cause: Tx Failure. (Low megger reading) | 3041214 | 1 | 10:00 | Morning | Friday | 2015 | 4
754 | 2015-04-24 14:35 | 2015-04-24 14:35 | MINAS POWER PLANT |  |  | - | Off line MGT #2, then S/D the Unit for Maintenance. |  | 1 | 14:35 | Afternoon | Friday | 2015 | 4
755 | 2015-04-24 14:42 | 2015-04-24 14:42 | 13.8KV MINAS FEEDER #3 | Fair | ESP Failure | - | 14:42 It was reported b/o fuse for Tx at Well #7D-96N. (Minas fdr #3) 16:00 Checked & found, @3 b/o 14.0SF fuse for 550Kva Tx at Well #7D-96N. Replaced b/o fuse above wth the same size & energized the Tx. Cause: ESP problem. (Reda motor Low Megger reading) (No Prod. loss charge to PGT / Charged to SP) | 3041214 | 1 | 14:42 | Afternoon | Friday | 2015 | 4
756 | 2015-04-24 14:42 | 2015-04-24 14:42 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified (Fuse) | 22 | 14:42 It was reported b/o fuse for Tx at Well #7D-33E. (Minas fdr #1) 16:15 Checked & found, @3 b/o 7.8SF fuse for 250Kva Tx at Well #7D-33E. Replaced b/o fuse above with the same size & energized tha Tx. Cause: Undentified (Fuse). | 3041214 | 1 | 14:42 | Afternoon | Friday | 2015 | 4
757 | 2015-04-25 05:14 | 2015-04-25 05:14 | 13.8KV ROKAN FEEDER #2 | Cloudy | Animal | 128 | 05:14 Roan VCB fdr #2 T/LO. 07:20 Checked & found, Rokan VCB fdr #2 T/LO. Ctr: 973-977 R/F: 51N. 08:00 Patrolled the line & found, a dead Monkey & @1 broken FCO for 50Kva Tx o/p #29AV-27. Isolated broken FCO above by opening HLC o/p #29AV-27. (The Tx for Security ligh is still off) 08:19 Blocked & closed Rokan VCB fdr #2, Ok. Then release the block. Cause: Animal. (Monkey) | 3041212 | 1 | 5:14 | Morning | Saturday | 2015 | 4
758 | 2015-04-25 08:55 | 2015-04-25 08:55 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 57 | Sintong OCB fdr #2 T/R 1x. Sintong GFPC did not operate. Not checked yet. | 3041212 | 1 | 8:55 | Morning | Saturday | 2015 | 4
759 | 2015-04-25 08:55 | 2015-04-30 07:25 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 57 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 381-382 R/F: 51N(@3). Patrolled the line, but found nothing. Cause: Unidentified. | 3041212 | 1 | 8:55 | Morning | Saturday | 2015 | 4
760 | 2015-04-25 16:13 | 2015-04-25 16:13 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified | 23 | C.Duri ACB fdr #1 T/R 1x Ctr: 176-177 R/F: 51N(@1), 51G(@1). Not patrolled yet. | 3041212 | 1 | 16:13 | Afternoon | Saturday | 2015 | 4
761 | 2015-04-25 16:13 | 2015-04-28 16:55 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified | 23 | Patrolled the line, but found nothing. Cause: Unidentified. | 3041212 | 1 | 16:13 | Afternoon | Saturday | 2015 | 4
762 | 2015-04-26 08:00 | 2015-04-26 08:00 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified (Fuse) | 4 | 08:00 It was reported b/o fuse for Tx at Well Jambon #04. 09:45 Checked & found, @2, @3 b/o 3.5SF fuses for 150Kva Tx at Well Jambon #04. Replaced the b/o above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3041212 | 1 | 8:00 | Morning | Sunday | 2015 | 4
763 | 2015-04-26 17:48 | 2015-04-26 17:48 | NORTH DURI POWER PLANT |  |  | - | 17:44 Off line NDC-CT #3, then S/D the Unit at 17:48 for S/B. (Prior to Off Line Wash program) | 123 | 1 | 17:48 | Afternoon | Sunday | 2015 | 4
764 | 2015-04-27 14:15 | 2015-04-27 14:15 | 13.8KV LIBO FEEDER #1 | Fair | Pin Insulator | 10 | 14:15 It was reported No Power at downstream of Libo fdr #1 at 13:00. (At that time DSC monitor & Server down due to UPS problem) Not checked yet. | 3041212 | 1 | 14:15 | Afternoon | Monday | 2015 | 4
765 | 2015-04-27 14:15 | 2015-04-29 15:24 | 13.8KV LIBO FEEDER #1 | Fair | Pin Insulator | 10 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 347-348 R/F: 51N(@2). Patrolled the line & found, @2 flashed over Pin Insulator o/p #34CA-2B. Cause: Pin Insulator. | 3041212 | 1 | 14:15 | Afternoon | Monday | 2015 | 4
766 | 2015-04-27 15:11 | 2015-04-27 15:11 | MINAS POWER PLANT |  |  | - | 15:11 S/U MGT #2, then On Line at 15:36. 15:38 Open 13.8Kv ACB #25. (Tie breker) | 123 | 1 | 15:11 | Afternoon | Monday | 2015 | 4
767 | 2015-04-27 17:27 | 2015-04-27 17:27 | NORTH DURI POWER PLANT |  |  | - | 17:27 S/U NDC-CT #3, then On Line to the system at 17:55. (After Off Line Wash program) | 123 | 1 | 17:27 | Afternoon | Monday | 2015 | 4
768 | 2015-04-27 17:40 | 2015-04-27 17:40 | 13.8KV 8C FEEDER #3 | Fair | Unidentified (Fuse) | 37 | It was reported b/o fuse for Tx at Well #8C-69E. Not checked yet. | 3041214 | 1 | 17:40 | Afternoon | Monday | 2015 | 4
769 | 2015-04-27 17:40 | 2015-04-28 10:30 | 13.8KV 8C FEEDER #3 | Fair | Unidentified (Fuse) | 37 | 10:30 Checked & found, @1 b/o 7.8SF fuse for 260Kva Tx at Well #8C-69E. (8C fdr #3) Tested the Tx & foud, normal. (good reading) Replaced the b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3041214 | 1 | 17:40 | Afternoon | Monday | 2015 | 4
770 | 2015-04-27 18:05 | 2015-04-27 18:05 | 13.8KV MENGGALA FEEDER #2 | Rain and Lightning | Lightning | 0 | Menggala fdr #2 dropped 20A (86-66A). Menggala GFPC T/R 1x. (Ground fault alarm on Menggala fdr #1 & fdr #2) Not checked yet. | 3041212 | 1 | 18:05 | Afternoon | Monday | 2015 | 4
771 | 2015-04-27 18:05 | 2015-04-30 08:28 | 13.8KV MENGGALA FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 27AL-21 (Menggala fdr #2) T/R 2x Ctr: 108-110. Patrolled the line & found, @2 broken Pin Insulator o/p #27AM-21. Cause: Lightning. | 3041212 | 1 | 18:05 | Afternoon | Monday | 2015 | 4
772 | 2015-04-27 18:40 | 2015-04-27 18:40 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Lightning | 31 | Pungut OCB fdr #1 T/R 1x. Pungut fdr #2 dropped 68A (92-24A). Not checked yet. | 3041212 | 1 | 18:40 | Afternoon | Monday | 2015 | 4
773 | 2015-04-27 18:40 | 2015-04-29 15:40 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Lightning | 31 | Checked & found, Pungut OCB fdr #1 T/R 1x Ctr: 342-343 R/F: 51N(@1). Patrolled the line & found, @1 flashed over Dead end Insulator o/p #44BN-05. Cause: Lightning. | 3041212 | 1 | 18:40 | Afternoon | Monday | 2015 | 4
774 | 2015-04-27 18:47 | 2015-04-27 18:47 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 32 | So.Bekasap fdr #1 dropped 68A (160-92A). Not patrolled yet. | 3041212 | 1 | 18:47 | Afternoon | Monday | 2015 | 4
775 | 2015-04-27 18:47 | 2015-04-29 15:47 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 32 | Checked & found, Recl. 36BI-04 (So.Bekasap fdr #1) T/R 1x Ctr: 137-138. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041212 | 1 | 18:47 | Afternoon | Monday | 2015 | 4
776 | 2015-04-27 19:22 | 2015-04-27 19:22 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 212 | 19:22 6D OCB fdr #1 T/LO. 20:00 Checked & found, 6D OCB fdr #1 T/LO. Ctr: 290-294 R/F: 51@1,@2. Patrolled the Line, but found Nothing. 22:30 Blocked & Closed 6D OCB fdr #1, Ok. Then released the block. Cause: Suspected by Lightning. | 3041214 | 1 | 19:22 | Night | Monday | 2015 | 4
777 | 2015-04-27 19:31 | 2015-04-27 19:31 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Lightning | 45 | 19:31 C.Duri ACB fdr #5 T/SO. (in Blocked Status, for Rig jobs at Well #6Q-55A) 20:30 Checked & found, C.Duri ACB fdr #5 T/SO. Ctr: 219-220 R/F: 51@1,@2,@3. Patrolled the Line, but found nothing. 21:00 Blocked & Closed C.Duri ACB fdr #5, Ok. Then released the Block. Cause: Suspected by Lightning. Not Re-patrolled yet. | 3041212 | 1 | 19:31 | Night | Monday | 2015 | 4
778 | 2015-04-27 19:31 | 2015-04-29 16:49 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Lightning | 45 | Patrolled the line & found: -@1 Broken Pin Insulator o/p #03-7-01A. -@2 Broken L/A o/p #03-8-14. Cause: Lihgtning. | 3041212 | 1 | 19:31 | Night | Monday | 2015 | 4
779 | 2015-04-27 19:31 | 2015-04-27 19:31 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Lightning | 144 | C.Duri ACB fdr #7 T/R 1x Ctr: 434-435 R/F: 51N. The line is not Patrolled yet. | 3041212 | 1 | 19:31 | Night | Monday | 2015 | 4
780 | 2015-04-27 19:31 | 2015-04-29 16:54 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Lightning | 144 | Patrolled the line & found, @3 flashed over Dead end Insulator o/p #03-1-13. Cause: Lightning. | 3041212 | 1 | 19:31 | Night | Monday | 2015 | 4
781 | 2015-04-27 19:43 | 2015-04-27 19:43 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 5 | So.Bekasap OCB fdr #1 T/R 1x. Not checked yet. | 3041212 | 1 | 19:43 | Night | Monday | 2015 | 4
782 | 2015-04-27 19:43 | 2015-04-29 15:43 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 5 | Checked & found, So.Bekasap OCB fdr #1 T/R 1x Ctr: 247-248 R/F: 51N(@3). Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041212 | 1 | 19:43 | Night | Monday | 2015 | 4
783 | 2015-04-28 | 2015-04-28 | NORTH DURI POWER PLANT |  |  | - | 00:00 Off line NDC-CT #2, then S/D the Unit for S/B. (Prior to HGPI program) | 123 | 1 | 0:00 | Night | Tuesday | 2015 | 4
784 | 2015-04-28 06:20 | 2015-04-28 06:20 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 0 | C.Duri fdr #1 Load dropped 37A (222-185A). Not checked yet. | 3041212 | 1 | 6:20 | Morning | Tuesday | 2015 | 4
785 | 2015-04-28 06:20 | 2015-04-30 17:45 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 181-182. Patrolled the line & found: -@3 Broken Dead end Insulator o/p #40AW-20. -@1 Flashed over Dead end Insulator o/p #40AW-16. Cause: Lightning. | 3041212 | 1 | 6:20 | Morning | Tuesday | 2015 | 4
786 | 2015-04-28 06:31 | 2015-04-28 06:31 | 13.8KV KETIGUL FEEDER#1 | Cloudy and Lightning | Lightning | 0 | Ketigul fdr #1 load dropped 75A (201-126A). Not checked yet. | 3041212 | 1 | 6:31 | Morning | Tuesday | 2015 | 4
787 | 2015-04-28 06:31 | 2015-01-05 10:31 | 13.8KV KETIGUL FEEDER#1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 122-123 R/F: 51N(@1). Patrolled the line & found, @1 broken L/A o/p #32AK-71. Cause: Lightning. | 3041212 | 1 | 6:31 | Morning | Tuesday | 2015 | 4
788 | 2015-04-28 08:38 | 2015-04-28 08:38 | MINAS POWER PLANT |  |  | - | 08:38 Off line MGT #4, then S/D the Unit for minor repair. |  | 1 | 8:38 | Morning | Tuesday | 2015 | 4
789 | 2015-04-28 23:37 | 2015-04-28 23:37 | 6 DELTA SUBSTATION | Rain | Lightning | 946 | 23:37 6D fdr #1 load dropped 343A (343-0A). 6D fdr #2 load dropped 187A (187-0A). 6D fdr #3 load dropped 118A (118-0A). 6D bus #1 indicated 0 Kv. (No breakers & C/S open indication at HMI) Apr, 29th 2015 --------------------------------------- 00:04 Manual opened 6DN fdr #5. Closed at: 04:01. 00:24 Checked & found 6D C/S #1 T/O ctr: 114-115 R/F: 51 @1. Also found: - B/O fuse for Sta. Service Tx & PT. - Broken primary jumper for Sta. Service Tx. - Broken & Flashed over Pin Support for PT. 02:36 Manual opened 6DN fdr #6. Closed at: 04:51. 04:01 Closed LBS #6D-15. (to transfered load 6D fdr #3 to 6DN fdr #5). 04:05 Opened Recl #6D-78A. Closed LBS #6D-68. (to transfered part load 6D fdr #2 to 6DN fdr #5). 04:20 6D RTU failed. 04:25 Closed LBS #6D-87. (to transfered other part load 6D fdr #2 to 6D fdr #5). 04:41 Opened LBS #5C-59. Closed LBS #6D-500. (to transfered part load 6D fdr #1 to 6D fdr #4). 04:44 Closed Recl. #5B-50A (to transfered other part load 6D fdr #1 to 5B fdr #1). Cause: Lightning. Prod. loss: GS #3: 6D fdr #2 : 175 bbls/17 wells 6D fdr #3 : 122 bbls/13 wells 6DN fdr #5: 266 bbls/23 wells 6DN fdr #6: 210 bbls/36 wells GS #4: 6D fdr #1: 271 bbls/ 22 wells ------------------------- Total : 1044 bbls/ 111 wells 15:55 Manually Closed 115KV 6D C/S #1, to Energize 6D TX #1. After replacing F/O Pin Insulator & broken FCO also Sta. service Primary jumper. (6D TX #1 is not loaded yet) | 3041214 | 1 | 23:37 | Night | Tuesday | 2015 | 4
790 | 2015-04-29 06:45 | 2015-04-29 06:45 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Animal | 0 | Duri Community ACB fdr #5 T/R 1x. Not checked yet. | 3041212 | 1 | 6:45 | Morning | Wednesday | 2015 | 4
791 | 2015-04-29 06:45 | 2015-04-30 16:30 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Animal | 0 | Checked & found, Duri Community ACB fdr #5 T/R 1x Ctr: 93-94 R/F: 51N(@1). Patrolled the line & found, @1 broken Bushing of LBS #1KT-41. Cause: Animal. | 3041212 | 1 | 6:45 | Morning | Wednesday | 2015 | 4
792 | 2015-04-29 21:09 | 2015-04-29 21:09 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Pematang fdr #1 load dropped 148A (171-23A). Not checked yet. | 3041212 | 1 | 21:09 | Night | Wednesday | 2015 | 4
793 | 2015-04-29 21:09 | 2015-04-05 11:34 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Pematang OCB fdr #1 T/R 1x Ctr: 109-110 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041212 | 1 | 21:09 | Night | Wednesday | 2015 | 4
794 | 2015-04-29 21:58 | 2015-04-29 21:58 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 0 | 3D OCB fdr #8 T/R 1x. 3D fdr #7 load dropped 26A (161-145A). Not checked yet. | 3041214 | 1 | 21:58 | Night | Wednesday | 2015 | 4
795 | 2015-04-29 21:58 | 2015-04-30 14:00 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 0 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 156-157 R/F: 50@3. Patrolled the line, but found nothing. Cause: Lightning. | 3041214 | 1 | 21:58 | Night | Wednesday | 2015 | 4
796 | 2015-04-29 21:59 | 2015-04-29 21:59 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 19 | Rokan VCB fdr #2 T/R 2x. Not checked yet. | 3041212 | 1 | 21:59 | Night | Wednesday | 2015 | 4
797 | 2015-04-29 21:59 | 2015-04-05 11:36 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 19 | Checked & found, Rokan VCB fdr #2 T/R 2x Ctr: 31-33 R/F: 51N(@1). Patrolled the line & found, @1 broken Pin Insulator o/p #29AV-45. Cause: Lightning. | 3041212 | 1 | 21:59 | Night | Wednesday | 2015 | 4
798 | 2015-04-29 22:09 | 2015-04-29 22:09 | CENTRAL DURI POWER PLANT | Rain and Lightning | Under investigation | - | 22:09 CGT #2 Tripped By alarm: Exciter Failure to Stop. 22:20 Manual closed ACB #19. (Tie Breaker) 30-APR-2015 02:17 Opened ACB #19. (Tie Breaker) 01:55 S/U CGT #2, then online the unit at 02:55. Cause: Under Investigation. | 3041212 | 1 | 22:09 | Night | Wednesday | 2015 | 4
799 | 2015-04-29 22:16 | 2015-04-29 22:16 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Unidentified | 24 | 5B fdr #1 load dropped 310A (384-74A). Not checked yet. | 3041214 | 1 | 22:16 | Night | Wednesday | 2015 | 4
800 | 2015-04-29 22:16 | 2015-04-05 11:43 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Unidentified | 24 | Checked Recloser #5B-06 (5B fdr #1) & found, normal. Ctr: 25. (Did not operate) Recloser #5B-50A (5B fdr #1) & found, normal. Ctr: 23. (Did not operate) Checked Breaker 5B fdr #1 & found, normal. (No Relay flag & Counter did not change. Patrolled the line, but found nothing. Cause: Unidentified. | 3041214 | 1 | 22:16 | Night | Wednesday | 2015 | 4
801 | 2015-04-29 22:23 | 2015-04-29 22:23 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 36 | 6D OCB fdr #5 T/R 1x. Not checked yet. | 3041214 | 1 | 22:23 | Night | Wednesday | 2015 | 4
802 | 2015-04-29 22:23 | 2015-04-05 11:23 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 36 | Checked & found, 6D OCB fdr #5 T/R 1x Ctr: 718-719 R/F: 51@2,@3. Patrolled the line & found: -@2 Broken Dead end Insulator o/p #6D-504. -@3 Flashed over Pin Insulator o/p #5D-04. Cause: Lightning. | 3041214 | 1 | 22:23 | Night | Wednesday | 2015 | 4
803 | 2015-04-29 22:23 | 2015-04-29 22:23 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 12 | 4D OCB fdr #4 T/R 2x. 4D fdr #5 load dropped 291A (351-60A). Not checked yet. | 3041214 | 1 | 22:23 | Night | Wednesday | 2015 | 4
804 | 2015-04-29 22:23 | 2015-04-30 13:01 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 12 | Checked & found, 4D OCB fdr #4 T/R 2x Ctr: 242-244 R/F: 51@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041214 | 1 | 22:23 | Night | Wednesday | 2015 | 4
805 | 2015-04-29 22:23 | 2015-04-29 22:23 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 35 | 6DN OCB fdr #6 T/R 1x. 6DN fdr #5 load dropped 291A (351-60A). Not checked yet. | 3041214 | 1 | 22:23 | Night | Wednesday | 2015 | 4
806 | 2015-04-29 22:23 | 2015-04-05 11:45 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 35 | Checked & found, 6DN OCB fdr #6 T/R 5x Ctr: 307-312 R/F: 5)@1,@2,@3. Patrolled the line & found: -@1,@2 Broken Dead end Insulators o/p #NN. (near Well #6E-21) -@1 Broken L/A on TP of Well #6E-43. Cause: Lightning. | 3041214 | 1 | 22:23 | Night | Wednesday | 2015 | 4
807 | 2015-04-29 22:30 | 2015-04-29 22:30 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 0 | 8D fdr #10 Load dropped 109A (182-73A). Not checked yet. | 3041214 | 1 | 22:30 | Night | Wednesday | 2015 | 4
808 | 2015-04-29 22:30 | 2015-05-05 07:12 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 7E-21 (8D fdr #10) T/R 1x Ctr: 29-30. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3041214 | 1 | 22:30 | Night | Wednesday | 2015 | 4
809 | 2015-04-29 22:47 | 2015-04-29 22:47 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 105 | 8C VCB fdr #3 T/R 1x. 8C fdr #1 Load dropped 126A (279-153A). Not checked yet. | 3041214 | 1 | 22:47 | Night | Wednesday | 2015 | 4
810 | 2015-04-29 22:47 | 2015-04-05 11:47 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 105 | Checked & found, 8C VCB fdr #3 T/R 1x Ctr: 478-479 R/F: 51@1,@2. Patrolled the line & found: -@2 Broken Dead end Insulator o/p #8D-16. -@2 Broken Dead end Insulator o/p #NN. (near Well #8C-49) -@1 Broken L/A o/p #8D-08. -@1 Broken L/A on TP of Well #8C-29E. Cause: Lightning. | 3041214 | 1 | 22:47 | Night | Wednesday | 2015 | 4
811 | 2015-04-29 22:54 | 2015-04-29 22:54 | MINAS POWER PLANT | Rain and Lightning | Under investigation | - | 22:54 MGT #10 Tripped By alarm: High Vibration trip. 30-APR-2015 00:08 S/U MGT #10, then online the unit at 00:34. Cause: Under Investigation. |  | 1 | 22:54 | Night | Wednesday | 2015 | 4
812 | 2015-04-30 00:08 | 2015-04-30 00:08 | MINAS POWER PLANT |  |  | - | 00:08 S/U MGT #10, then online the unit at 00:34. Cause: Under Investigation. (After trip, By Alarm: High vibration trip) |  | 1 | 0:08 | Night | Thursday | 2015 | 4
813 | 2015-04-30 01:55 | 2015-04-30 01:55 | CENTRAL DURI POWER PLANT |  |  | - | 01:55 S/U CGT #2, then online the unit at 02:55. 02:17 Opened ACB #19. (Tie Breaker) Cause: Under Investigation. (After Trip, By Alarm: Exciter failure to stop) |  | 1 | 1:55 | Night | Thursday | 2015 | 4
814 | 2015-04-30 17:50 | 2015-04-30 17:50 | 13.8KV 6D FEEDER #2 | Fair | Unidentified | 25 | 17:50 6D fdr #2 Load dropped 106A (178-72A). It was reported no power at downstream of 6D fdr #2. 18:34 Checked & found, Recl. 6D-298 (6D fdr #2) T/SO. Ctr: 33-34. Blocked & closed Rcl. 6D-298, Ok. Then released the Block. The line is not patrolled yet. | 3041214 | 1 | 17:50 | Afternoon | Thursday | 2015 | 4
815 | 2015-04-30 17:50 | 2015-02-05 07:15 | 13.8KV 6D FEEDER #2 | Fair | Unidentified | 25 | Patrolled the line, but found nothing. Cause: Unidentified. | 3041214 | 1 | 17:50 | Afternoon | Thursday | 2015 | 4
816 | 2015-04-30 23:20 | 2015-04-30 23:20 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified (Fuse) | 5 | 23:20 It was reported b/o fuse for Tx at Well KB #134. Checked & found, @1 b/o 7.8SF fuses for 250Kva Tx at Well KB #134. Replaced b/o fuse above with same size & energized the Tx. Cause: Unidentified (Fuse). | 3041214 | 1 | 23:20 | Night | Thursday | 2015 | 4
817 | 2015-01-05 11:07 | 2015-01-05 11:07 | 13.8KV SINTONG FEEDER #2 | Fair | Recloser | 0 | 11:07 Sintong fdr #2 Load dropped 17A(188-171A). Sintong GFPC T/R 1x. Ground fault alarm at sintong fdr #2. 11:45 Checked & found, Recl. 29AK-24 (Sintong fdr #2) T/SO. Ctr: 195-196. Blocked & Closed the Recloser above, but Failed. 12:53 Jumpered Battery for Recloser DC voltage control, to close Recloser closing coil. Blocked & closed the Recloser above, but failed to close. Then patrolled the line at downstream of Recl. 29AK-24, but found nothing. 13:50-14:05 Open LBS #29AI-05, to Bypass Recl. 29AK-24. (line toward Pagar Gas plant) Cause: Recloser problem. (Closing Coil problem) | 3056406 | 1 | 11:07 | Morning | Monday | 2015 | 1
818 | 2015-01-05 13:50 | 2015-01-05 13:50 | 13.8KV 5B FEEDER #1 | Fair | Low mega-ohm reading | 20 | 13:50 It was reported b/o fuse for Tx at Well #5B-75. (5B fdr #1) 17:30 Checked & found, @1,@2,@3 b/o 14.0SF fuse for 550Kva Tx at Well #5B-75. Performed TTR, Megger test & found, Low Mega Ohm reading. Cause: Tx Failure. (Low Megger reading) The Tx is not replaced yet. | 3056411 | 1 | 13:50 | Afternoon | Monday | 2015 | 1
819 | 2015-01-05 13:50 | 2015-04-05 16:00 | 13.8KV 5B FEEDER #1 | Fair | Low mega-ohm reading | 20 | Replaced 550Kva Tx Low megger reading with the same size & energized the Tx. Cause: Transformer Low megger reading. | 3056411 | 1 | 13:50 | Afternoon | Monday | 2015 | 1
820 | 2015-01-05 17:03 | 2015-01-05 17:03 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning Arrester | 32 | Menggala OCB fdr #1 T/R 1x. Menggala GFPC T/R 1x. Not checked yet. | 3056406 | 1 | 17:03 | Afternoon | Monday | 2015 | 1
821 | 2015-01-05 17:03 | 2015-03-05 15:42 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning Arrester | 32 | Checked & found, Menggala VCB fdr #1 T/R 1x Ctr: 299-300 R/F: 51N. Also found, Menggala GFPC T/R 1x Ctr: 1102-1103 R/F: 50N. Patrolled the line & found, @1 broken L/A on TP of Well So.Menggala #10. Cause: Lightning Arrester. | 3056406 | 1 | 17:03 | Afternoon | Monday | 2015 | 1
822 | 2015-01-05 17:34 | 2015-01-05 17:34 | 13.8KV PEMATANG FEEDER #2 | Fair | Animal | 10 | 17:34 It was reported b/o fuse for Tx at Well Pematang #50. (Pematang fdr #2) Not checked yet. | 3056406 | 1 | 17:34 | Afternoon | Monday | 2015 | 1
823 | 2015-01-05 17:34 | 2015-02-05 08:45 | 13.8KV PEMATANG FEEDER #2 | Fair | Animal | 10 | 08:45 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Pematang #50. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3056406 | 1 | 17:34 | Afternoon | Monday | 2015 | 1
824 | 2015-01-05 21:00 | 2015-01-05 21:00 | MINAS POWER PLANT |  |  | - | 21:00 Off line MGT #9, then S/D the Unit for S/B. (Prior to Repairing Gas Control Valve / GCV problem) 02-May-2015. 12:50 S/U MGT #9, then On Line at 13:20. (After repairing Gas Control Valve / GCV) |  | 1 | 21:00 | Night | Monday | 2015 | 1
825 | 2015-02-05 11:15 | 2015-02-05 11:15 | MINAS POWER PLANT |  |  | - | 11:15 MGT #4 S/U, the On line at 11:30. (After servicing Battery & Some minor repair) | 123 | 1 | 11:15 | Morning | Thursday | 2015 | 2
826 | 2015-02-05 12:50 | 2015-02-05 12:50 | MINAS POWER PLANT |  |  | - | 12:50 S/U MGT #9, then On Line at 13:20. (After repairing Gas Control Valve / GCV) | 123 | 1 | 12:50 | Afternoon | Thursday | 2015 | 2
827 | 2015-02-05 14:49 | 2015-02-05 14:49 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | 3 | 14:49-17:25 Open HLC o/p #25X-28 to replace cross arm. (Bangko Fdr #1) (Bangko #239 was off during the Job done)1). Cause: Planned Maintenance. | 3056406 | 1 | 14:49 | Afternoon | Thursday | 2015 | 2
828 | 2015-02-05 21:44 | 2015-02-05 21:44 | 13.8KV MINAS FEEDER #6 | Rain | Unidentified | 0 | 21:44 Minas fdr #6 load dropped 24A (224-200A). It was reported no power at Cewa., Dahlia & Kenanga Complex. 22:18 Checked & found, 13.8Kv Recl. 6E-73 for 2.5MVA Tx at Cewa. Mini Subst. T/O. Ctr: 883-884. Also found, 4.16Kv Recl. at Cewa. Mini Subst. T/O Ctr: 682-683. Visual checked 2.5MVA Tx and found normal. Patrolled the line & found nothing. 22:30 Blocked & closed 13.8Kv Recl. 6E-73, Ok. Then released the block. 22:34 Blocked & closed 4.16Kv Recl., Ok. Then released the block. Cause: Unidentified. (Also see report 03 May 2015 at 02:24) | 3056411 | 1 | 21:44 | Night | Thursday | 2015 | 2
829 | 2015-03-05 02:24 | 2015-03-05 02:24 | 13.8KV MINAS FEEDER #6 | Rain | Lightning | 0 | 02:24 Minas fdr #6 load dropped 24A (224-200A). again. It was reported no power again at Minas Cewa., Dahlia & Kenanga Complex. 03:10 Checked & found, 13.8Kv Recl. 6E-73 for 2.5MVA Tx at Cewa. Mini Subst. T/O. Ctr: 884-885. Also found, 4.16Kv Recl. at Cewa. Mini Subst. T/O. Ctr: 683-684. Visual checked 2.5MVA Tx and found normal. Patrolled the line & found nothing. 03:35 Blocked & closed 13.8Kv Recl. 6E-73, Ok. Then released the block. 03:47 Blocked & closed 4.16Kv Cewa Recl., Ok. Then released the block. 10:00 Re-patrolled the line & found, @1 broken Dead end Insulator on pole #CW-04. Cause: Lightning. | 3056411 | 1 | 2:24 | Night | Thursday | 2015 | 3
830 | 2015-03-05 02:39 | 2015-03-05 02:39 | CENTRAL DURI POWER PLANT | Fair | Others | - | 02:39 CGT #1 Tripped by Alarm: - Generator R/F: 40, 51(@1@2@3), 87G, 86G - Hydraulic Trip Circuit Gas Fuel. 16:18 CGT #1 S/U, then On Line at 17:15. (after Clean, Dry, & re Calibrated the Relays). Cause: Other. (Control cab Roof was leaks, Relay cubicle wet by Rain water) | 3056406 | 1 | 2:39 | Night | Thursday | 2015 | 3
831 | 2015-03-05 04:15 | 2015-03-05 04:15 | MINAS POWER PLANT |  |  | - | 04:15 Offline MGT #10, then S/D the unit, due to MVAR Problem. | 3056411 | 1 | 4:15 | Morning | Thursday | 2015 | 3
832 | 2015-04-05 13:00 | 2015-04-05 13:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 0 | 13:00 It was reported b/o fuse for Tx at Well Pagar #11. (Ketigul fdr#2) 18:00 Checked & found, @1,@2 b/o fuse for 150Kva Tx at Well Pagar #11. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 13:00 | Afternoon | Sunday | 2015 | 4
833 | 2015-04-05 23:32 | 2015-04-05 23:32 | DURI POWER PLANT | Fair | Under investigation | - | 23:32 DGT #7 Tripped, By Alarm: Compressor blade valve. (IGV trouble) & Relay: 32. Cause: Under investigation. 05 May 2015. 01:00 S/U DGT #7, then on line at 01:25. | 3056406 | 1 | 23:32 | Night | Sunday | 2015 | 4
834 | 2015-05-05 01:00 | 2015-05-05 01:00 | DURI POWER PLANT |  |  | - | 01:00 S/U DGT #7, then on line at 01:25. (after Tripped at 23:32 on 04 May 2015) |  | 1 | 1:00 | Night | Tuesday | 2015 | 5
835 | 2015-05-05 04:02 | 2015-05-05 04:02 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Unidentified | 66 | Petapahan fdr #2 Load dropped 49A (150-101A). Not checked yet. | 3056411 | 1 | 4:02 | Morning | Tuesday | 2015 | 5
836 | 2015-05-05 04:02 | 2015-07-05 17:02 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Unidentified | 66 | Checked & found, Recl. 28CW-01 (Petapahan fdr #2) T/R 1x Ctr: 42-43. Patrolled the line, but found nothing. Cause: Unidentified. | 3056411 | 1 | 4:02 | Morning | Tuesday | 2015 | 5
837 | 2015-05-05 12:00 | 2015-05-05 12:00 | 13.8KV 6D FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 12:00 It was reported b/o fuse for Tx at GS #4. (6D fdr #1). 14:41 Checked & found, @2 b/o 100K fuse for 2.5Mva Tx at GS #4. Performed TTR & Megger Test the Tx, found good reading. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3056411 | 1 | 12:00 | Afternoon | Tuesday | 2015 | 5
838 | 2015-05-05 16:41 | 2015-05-05 16:41 | 13.8KV 4B FEEDER #6 | Fair | Low mega-ohm reading | 28 | It was reported that Well #4B-24 was off. (4B fdr #6) Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well #4B-24. Tested the Tx & found, Low megger reading. Replaced Tx low megger reading with the same size & energized the Tx. Cause: Low Mega-ohm Reading Tx. | 3056411 | 1 | 16:41 | Afternoon | Tuesday | 2015 | 5
839 | 2015-05-05 18:00 | 2015-05-05 18:00 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified (Fuse) | 17 | 18:00 It was reported b/o fuses for Tx at Well Sintong #34. 23:30 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Sintong #34. Replaced b/o above with same size, then energized the Tx. Cause: Unidentified (fuse). | 3056406 | 1 | 18:00 | Afternoon | Tuesday | 2015 | 5
840 | 2015-05-05 20:30 | 2015-05-05 20:30 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 20:30 It was reported b/o fuse for Tx o/p #SLI-1A- 08. 22:30 Checked & found, @1@2 b/o fuse holder for 25Kva Tx o/p #SLI-1A-08. (Power for shelter at Gate-3) The Tx is not checked yet. | 3056406 | 1 | 20:30 | Night | Tuesday | 2015 | 5
841 | 2015-05-05 20:30 | 2015-06-05 14:30 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified (Fuse) | 0 | Performed Megger & TTR test for 25 Kva Tx o/p #SLI-1A-08 (d/s Duri Comm. fdr #2), good reading. Replaced @1, @2 b/o fuse with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 20:30 | Night | Tuesday | 2015 | 5
842 | 2015-06-05 10:35 | 2015-06-05 10:35 | 13.8KV 3D FEEDER #8 | Cloudy and Lightning | Lightning | 7 | 3D OCB fdr #8 T/R 2x. GFPC-TX #2 T/R 2x. (Fault alarm on 3D fdr #8) Not checked yet. | 3056411 | 1 | 10:35 | Morning | Friday | 2015 | 6
843 | 2015-06-05 10:35 | 2015-07-05 10:35 | 13.8KV 3D FEEDER #8 | Cloudy and Lightning | Lightning | 7 | Checked & found, 3D OCB fdr #8 T/R 2x Ctr: 157-159 R/F: 51N. Patrolled the line & found: -@1 Flashed over Dead end Insulator o/p #3D-15A. -@1 Flashed over Dead end Insulator o/p #3D-89. Cause: Lightning. | 3056411 | 1 | 10:35 | Morning | Friday | 2015 | 6
844 | 2015-06-05 11:08 | 2015-06-05 11:08 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 0 | 11:08 It was reported no power at Petani GS. (Petani fdr #1) 12:07 Checked & found, @1, @2 b/o 1.0SF fuses for 50Kva Tx. (single phase) Also found, Tx failure. (by visual checked) 18:22 Replaced b/o 50Kva Tx above with 75Kva Tx, then energized the Tx. Cause: Tx failure. | 3056406 | 1 | 11:08 | Morning | Friday | 2015 | 6
845 | 2015-07-05 13:57 | 2015-07-05 13:57 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 13 | So.Balam fdr #4 load drop 75 A (123-48) So.Balam fdr #2 load drop 105 A (131-26) So.Balam fdr #3 load drop 29 A (30-1) So.Balam GFPC T/R 1x (Ground fault alarm on So.Balam fdr #1 & fdr #4) Not checked yet. | 3056406 | 1 | 13:57 | Afternoon | Sunday | 2015 | 7
846 | 2015-07-05 13:57 | 2015-12-05 13:10 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 13 | Checked & found, Recl. 16AA-08 (So.Balam fdr #4) T/R 1x Ctr: 16-17. Also found, So.Balam GFPC T/R 1x Ctr: 187-188. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3056406 | 1 | 13:57 | Afternoon | Sunday | 2015 | 7
847 | 2015-07-05 14:03 | 2015-07-05 14:03 | 13.8KV NORTH DURI FEEDER #9 | Rain and Lightning | Lightning | 0 | 14:03 North Duri VCB fdr #9 T/O. (in blocked for PT WIS pilling Job) Checked at the PT WIS Job spot & found, normal. (Clear) 14:10 Closed ND VCB #9, Ok. Then released the block. Not checked & patrolled yet. | 3056406 | 1 | 14:03 | Afternoon | Sunday | 2015 | 7
848 | 2015-07-05 14:03 | 2015-12-05 11:03 | 13.8KV NORTH DURI FEEDER #9 | Rain and Lightning | Lightning | 0 | Checked & found, No.Duri VCB fdr #9 T/R 1x Ctr: 2904-2805 R/F: 50N(@1). Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3056406 | 1 | 14:03 | Afternoon | Sunday | 2015 | 7
849 | 2015-07-05 14:23 | 2015-07-05 14:23 | 13.8KV NORTH DURI FEEDER #6 | Rain and Lightning | Lightning | 0 | North Duri VCB fdr #6 T/R 1x. Not checked & patrolled yet. | 3056406 | 1 | 14:23 | Afternoon | Sunday | 2015 | 7
850 | 2015-07-05 14:23 | 2015-12-05 11:23 | 13.8KV NORTH DURI FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked & found, No.Duri VCB fdr #6 T/R 1x Ctr: 283-284 R/F: 50N(@1). Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3056406 | 1 | 14:23 | Afternoon | Sunday | 2015 | 7
851 | 2015-07-05 14:29 | 2015-07-05 14:29 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Unidentified | 82 | 14:29 Sintong fdr #2 load drop 84 A (187-103) Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #2) 14:56 Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #2) 15:33 Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #2) Not checked yet. | 3056406 | 1 | 14:29 | Afternoon | Sunday | 2015 | 7
852 | 2015-07-05 14:29 | 2015-12-05 16:29 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Unidentified | 82 | Checked & found, Sintong GFPC T/R 3x Ctr: 752-755 R/F: 51N. Patrolled Sintoing fdr #2, but found nothing. Cause: Unidentified. | 3056406 | 1 | 14:29 | Afternoon | Sunday | 2015 | 7
853 | 2015-07-05 14:38 | 2015-07-05 14:38 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Unidentified | 10 | Menggala fdr #1 load dropped 114A (166-52A). Menggala GFPC T/R 1x. (Ground fault alarm on Menggala fdr #1) Not checked yet. | 3056406 | 1 | 14:38 | Afternoon | Sunday | 2015 | 7
854 | 2015-07-05 14:38 | 13/05/2015 11:38 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Unidentified | 10 | Checked & found Recl. 19AO-01 (Menggala fdr #1), in Bypass. (Recloser problem) Patrolled the line, but found nothing. Cause: Unidentified. | 3056406 | 1 | 14:38 | Afternoon | Sunday | 2015 | 7
855 | 2015-07-05 14:42 | 2015-07-05 14:42 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 48 | 14:42 Sintong OCB fdr #1 T/R 1x. Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #1) 14:53 Sintong GFPC T/R 1x again. (Ground fault alarm on Sintong fdr #1) 15:00 Sintong OCB fdr #1 T/R 1x again. Sintong GFPC T/R 1x again. Not checked yet. | 3056406 | 1 | 14:42 | Afternoon | Sunday | 2015 | 7
856 | 2015-07-05 14:42 | 2015-12-05 16:42 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 48 | Checked & found, Sintong OCB fdr #1 T/R 2x Ctr: 356-358 R/F: 51@2,@3. Also found, Sintong GFPC T/R 3x Ctr: 749-752. Patrolled the line & found, @1 F/O Pin Insulator o/p #STG-01. Cause: Lightning. | 3056406 | 1 | 14:42 | Afternoon | Sunday | 2015 | 7
857 | 2015-07-05 14:46 | 2015-07-05 14:46 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 170 | 14:46 Sintong OCB fdr #2 T/R 1x Sintong GFPC T/R 1x. 15:01 Sintong OCB fdr #2 T/R 1x again. Sintong GFPC T/R 1x again. 15:23 Sintong OCB fdr #2 T/R 1x again. Sintong GFPC T/R 1x again. Not checked yet. | 3056406 | 1 | 14:46 | Afternoon | Sunday | 2015 | 7
858 | 2015-07-05 15:11 | 2015-07-05 15:11 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Powerline - Jumper | 33 | Menggala OCB fdr #1 T/R 1x. Menggala GFPC T/R 1x. (Ground fault alarm on Menggala fdr #1) Not checked & patrolled yet. | 3056406 | 1 | 15:11 | Afternoon | Sunday | 2015 | 7
859 | 2015-07-05 15:11 | 13/05/2015 15:11 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Powerline - Jumper | 33 | Checked & found, Menggala VCB fdr #1 T/R 1x (Counter & Relay flag are not reported yet) Patrolled the line & found, @1 broken Jumper o/p #19AO-04. (for metering PHE MESO) Cause: Jumper. | 3056406 | 1 | 15:11 | Afternoon | Sunday | 2015 | 7
860 | 2015-07-05 17:08 | 2015-07-05 17:08 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Unidentified (Fuse) | 0 | 17:08 It was reported b/o fuse for Tx at Well So.Balam #364. 18:20 Checked & found, @3 b/o 2.1SF fuse for 100Kva Tx at Well So.Balam #364. Performed TTR, Megger test & found, normal. (good condition) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3056406 | 1 | 17:08 | Afternoon | Sunday | 2015 | 7
861 | 2015-07-05 19:52 | 2015-07-05 19:52 | MENGGALA SUBSTATION | Rain and Lightning | Transformer Failure | 7258 | 19:52 It was reported unbalance voltage at So.Menggala fields. 20:52 Checked & found unbalance voltage at Menggala Substation Buss. Transfered Load Menggala fdr #2 to Sintong fdr #2 23:20 Closed LBS #28AL-21. 23:28 Opened Menggala OCB fdr #2 & Opened both side isolation switches. 23:30 Closed LBS #28AL-05. (Menggala fdr #2 fed by Sintong fdr #2) 23:31 Open Menggala VCB fdr #1 & open both side isolation switches. Shutdown Menggala Power Transformer. 23:33 Open 115KV Menggala C/S at Menggala Substation. 23:34 Closed By Pass switch of VR at Menggala Substation. Checked Voltage at Menggala Substation Buss & found unbalance. 23:53 By Pass Recl. 26AL-08 by Un-plugging Recloser control. Prod. loss Reported by GS: 07 May 2015 Menggala South = 121 Bbls / 8 Wells. 07 May 2015 Menggala North = 44 Bbls / 25 Wells. Grand Total Menggala South & North = 165 Bbls / 33 Wells. (07 May 2015) Prod. loss by EC Report: 07 May 2015 Menggala South & North = 30 Bbls / 24 Wells. (07 May 2015) | 3056406 | 1 | 19:52 | Night | Sunday | 2015 | 7
862 | 2015-07-05 19:52 | 2015-08-05 00:30 | MENGGALA SUBSTATION | Rain and Lightning | Transformer Failure | 7258 | 00:30 By Pass Recl. 28AF-17, by Un-plugging Recloser control. 01:13 Opened Recl. 25Z-07. 01:38 Open Recl. 28AF-02 & Open its Visual Opening. 01:42 Closed Line switch o/p #29Z21. (Ex Recl.) 01:57 Closed Recl. 25Z-07. (Benar Field fed by Bangko fdr #4) 02:28 Closed LBS #NN at Menggala Substation. (Menggala fdr #1 fed by Sintong fdr #2) Requested to S/D 11 wells. (7 Wells at Menggala, 4 wells at Sintong fields) Cause: TX Unbalance. 02:51 It was reported un balance at So.Menggala fields. 04:30 Patrolled the line & found, @3 broken jumper o/p #19AO-04. 05:15 Open Recl. 19AO-01. (Menggala fdr #1) Then repaired @3 broken jumper o/p #19AO-04. 06:00 Blocked & closed Recl. 19AO-01, but failed. (Found by DC batt low) 06:50 Replaced Batt of Recl. 19AO-01. 06:55 Blocked & closed Recl. 19AO01, but failed 07:30 Opened LBS #NN at Menggala Substation, to close bypass Switch of Recl. 19AO-01. 07:35 Closed LBS #NN at Menggala Substation. Cause: Under Investigation. Prod. loss Reported by GS: 07 May 2015 Menggala South = 121 Bbls / 8 Wells. 08-10 May 2015 Menggala South = 1059 Bbls / 8 Wells. (07-10 May 2015) Total Menggala South= 1180 Bbls / 16 Wells. 07 May 2015 Menggala North = 44 Bbls / 25 Wells. 08-09 May 2015 Menggala North = 2116 Bbls / 23 Wells. 10 May 2015 Menggala North = 1741 Bbls / 24 Wells. 07-10 May 2015 Total Menggala North = 3901 Bbls / 72 Wells. Grand Total 07-10 May 2015 Menggala South & North = 1180 + 3901 = 5081 Bbls / 88 Wells. Prod. loss by EC Report: 07 May 2015 Menggala South & North = 30 Bbls / 24 Wells. 08 May 2015 Menggala South & North = 1525 Bbls / 68 Wells. 09 May 2015 Menggala South & North = 1701 Bbls / 32 Wells. Grand Total Menggala South & North = 3256 Bbls / 124 Wells. (07-09 May 2015) | 3056406 | 1 | 19:52 | Night | Sunday | 2015 | 7
863 | 2015-07-05 19:52 | 2015-09-05 23:59 | MENGGALA SUBSTATION | Rain and Lightning | Transformer Failure | 7258 | Prod. loss Reported by GS: 07 May 2015 Menggala South = 121 Bbls / 8 Wells. 08-10 May 2015 Menggala South = 1059 Bbls / 8 Wells. (07-10 May 2015) Total Menggala South= 1180 Bbls / 16 Wells. 07 May 2015 Menggala North = 44 Bbls / 25 Wells. 08-09 May 2015 Menggala North = 2116 Bbls / 23 Wells. 10 May 2015 Menggala North = 1741 Bbls / 24 Wells. 07-10 May 2015 Total Menggala North = 3901 Bbls / 72 Wells. Grand Total 07-10 May 2015 Menggala South & North = 1180 + 3901 = 5081 Bbls / 88 Wells. Prod. loss by EC Report: 07 May 2015 Menggala South & North = 30 Bbls / 24 Wells. 08 May 2015 Menggala South & North = 1525 Bbls / 68 Wells. 09 May 2015 Menggala South & North = 1701 Bbls / 32 Wells. Grand Total Menggala South & North = 3256 Bbls / 124 Wells. (07-09 May 2015) | 3056406 | 1 | 19:52 | Night | Sunday | 2015 | 7
864 | 2015-07-05 19:52 | 2015-10-05 23:59 | MENGGALA SUBSTATION | Rain and Lightning | Transformer Failure | 7258 | Prod. loss Reported by GS: 07 May 2015 Menggala South = 121 Bbls / 8 Wells. 08-10 May 2015 Menggala South = 1059 Bbls / 8 Wells. 11 May 2015 Menggala South = 353 Bbls / 8 Wells (07-11 May 2015) Total Menggala South= 1533 Bbls / 24 Wells. 07 May 2015 Menggala North = 44 Bbls / 25 Wells. 08-09 May 2015 Menggala North = 2116 Bbls / 23 Wells. 10 May 2015 Menggala North = 1741 Bbls / 24 Wells. 11 May 2015 Menggala North = 2072 Bbls / 24 Wells. 07-11 May 2015 Total Menggala North = 5973 Bbls / 96 Wells. Grand Total Menggala South & North = 1533 + 5973 = 7506 Bbls / 120 Wells. (07-11 May 2015) Prod. loss by EC Report: 07 May 2015 Menggala South & North = 30 Bbls / 24 Wells. 08 May 2015 Menggala South & North = 1525 Bbls / 68 Wells. 09 May 2015 Menggala South & North = 1701 Bbls / 32 Wells. 10 May 2015 Menggala South & North = 2016 Bbls / 32 Wells. 11 May 2015 Menggala South & North = 1986 Bbls / 32 Wells. Grand Total Menggala South & North = 7258 Bbls / 188 Wells. (07-11 May 2015) 12 May 2015 (33 Wells Menggala South & North are still off, due to Prod. line Congealed reason) | 3056406 | 1 | 19:52 | Night | Sunday | 2015 | 7
865 | 2015-08-05 14:17 | 2015-08-05 14:17 | DURI POWER PLANT | Rain and Lightning | Under investigation | 108 | 14:17 DGT#7 Tripped (no alarm appear). Frequency system dropped to 59.60Hz. (Load shedding level-1) 3D fdr #5 T/O, then closed ta 14:21. 4D fdr #3 T/O, then closed at 14:47. 4D fdr #5 T/O, then closed at 14:52. Cause: Under investigation. 22:00 S/U DGT #7, then on line the Unit at 22:38. | 3056406 | 1 | 14:17 | Afternoon | Wednesday | 2015 | 8
866 | 2015-08-05 14:54 | 2015-08-05 14:54 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 22 | 14:54 4D OCB fdr #5 T/SO. Ctr: 242. 15:03 Blocked & closed 4D OCB fdr #5, but T/O again. 15:50 Opened both side Isolation switch of 4D OCB fdr #5, to function test the breaker, Ok. 17:21 Patrolled the line & found, @2 broken FCO on TP of OBS Well #4D-75. Then replaced @2 broken FCO on TP Well #4D-75 above. 17:46 Blocked & closed Recl. 4D-14A (4D fdr #5), but trip again. 18:18 Opened Recl. 4D-14A. 18:21 Blocked & closed 4D OCB fdr #5, Ok. then release the block. 19:20 Continued patrolling the line at downsream of Recl. 4D-14A, but found nothing. 19:28 Blocked & closed Recl. 4D-14A, Ok. Then release the block. Cause: Lightning. 22:24 4D OCB fdr #5 T/LO. 23:30 Opened Recl. 4D-14A (4D fdr #5) 23:32 Blocked & closed 4D OCB fdr #5, but T/O again. Patrolled the line & found nothing. 00:21 Blocked & closed 4D OCB fdr#5, but T/O again. Re-Patrolled the line & found, @2,@3 broken Pin Insulators o/p #4D-11. (Then replaced @2, @3 broken Pin Insulators above) 01:57 Blocked & closed 4D OCB fdr #5, Ok. Then release the block. 02:05 Blocked & closed Recl. 4D-14A (4D fdr #5), Ok. Then release the block. Cause: Lightning. | 3056411 | 1 | 14:54 | Afternoon | Wednesday | 2015 | 8
867 | 2015-08-05 15:12 | 2015-08-05 15:12 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | 15:12 Bangko fdr #4 Load dropped 48A (217-169A) Bangko GFPC T/R 1x. (ground fault alarm on Bangko fdr #4) Not checked yet. 15:30 Bangko GFPC T/R 1x again. (Ground fault alarm on Bangko fdr #1,2,3,4) No load dropped at any feeders. Not checked yet. | 3056406 | 1 | 15:12 | Afternoon | Wednesday | 2015 | 8
868 | 2015-08-05 15:12 | 13/05/2015 12:12 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 2x Ctr: 455-457. Patrolled the line & found, @3 broken Pin Insulator o/p #27Y-40. Cause: Lightning. | 3056406 | 1 | 15:12 | Afternoon | Wednesday | 2015 | 8
869 | 2015-08-05 15:30 | 2015-08-05 15:30 | 13.8KV CENTRAL DURI FEEDER #6 | Rain and Lightning | Lightning | 107 | C.Duri ACB fdr #6 T/R 1x Ctr: 440-441 R/F: 51G & 51N. Not patrolled yet. | 3056406 | 1 | 15:30 | Afternoon | Wednesday | 2015 | 8
870 | 2015-08-05 15:30 | 13/05/2015 11:30 | 13.8KV CENTRAL DURI FEEDER #6 | Rain and Lightning | Lightning | 107 | Patrolled the line & found, @1 broken Dead end Insulator o/p #01-1-01B. Cause: Lightning. | 3056406 | 1 | 15:30 | Afternoon | Wednesday | 2015 | 8
871 | 2015-08-05 15:32 | 2015-08-05 15:32 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Lightning | 0 | Duri Community ACB fdr #5 T/R 1x. Not checked yet. | 3056406 | 1 | 15:32 | Afternoon | Wednesday | 2015 | 8
872 | 2015-08-05 15:32 | 2015-12-05 11:32 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, Duri Community ACB fdr #5 T/R 1x Ctr: 94-95 R/F: 51N(@1). Patrolled the line & found, @1 broken Dead end Insulator o/p #P2F-16. Cause: Lightning. | 3056406 | 1 | 15:32 | Afternoon | Wednesday | 2015 | 8
873 | 2015-08-05 16:08 | 2015-08-05 16:08 | 13.8KV RANGAU FEEDER #1 | Rain and Lightning | Lightning | 0 | Rangau VCB fdr #1 T/R 1x. Not checked yet. | 3056406 | 1 | 16:08 | Afternoon | Wednesday | 2015 | 8
874 | 2015-08-05 16:08 | 2015-12-05 11:08 | 13.8KV RANGAU FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Rangau VCB fdr #1 T/R 1x Ctr: 002-003 R/F: 51N(@1). Patrolled the line & found, @1 broken Dead end Insulator o/p #RGU-93. Cause: Lightning. | 3056406 | 1 | 16:08 | Afternoon | Wednesday | 2015 | 8
875 | 2015-08-05 16:35 | 2015-08-05 16:35 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Guy Wire | 13 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3056406 | 1 | 16:35 | Afternoon | Wednesday | 2015 | 8
876 | 2015-08-05 16:35 | 13/05/2015 07:35 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Guy Wire | 13 | Checked & found, Rokan VCB fdr #2 T/R 3x Ctr: 979-982 R/F: 51@1,@2,@3. Patrolled the line & found, broken Guy wire of pole #29AW-13. Cause: Lightning. | 3056406 | 1 | 16:35 | Afternoon | Wednesday | 2015 | 8
877 | 2015-09-05 07:13 | 2015-09-05 07:13 | 13.8KV 3D FEEDER #8 | Fair | Animal | 37 | 07:13 3D OCB fdr #8 T/LO. GFPC-TX #2 did not operate. 09:06 Checked & found, 3D OCB fdr #8 T/LO Ctr: 159-163 R/F: 51N. 10:00 Patrolled the line & found: -@1 Broken L/A jumper touching cross arm, and -@2 Broken jumper to HLC for Cap. Bank o/p #2D-03. (Suspected broken U/G Cable toward Well #2D-49 from o/p #2D-03) 10:12 Isolated broken jumper above. Opened Solid Blade FCO for U/G Cable above. 10:13 Blocked & closed 3D OCB fdr #8, Ok. Then released the block. Cause: Animal. (Monkey) | 3056411 | 1 | 7:13 | Morning | Saturday | 2015 | 9
878 | 2015-10-05 06:57 | 2015-10-05 06:57 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 17 | 8C fdr #1 Load dropped 177A (275-98A). 8C fdr #2 Load dropped 14A (192-178A). Not checked yet. | 3056411 | 1 | 6:57 | Morning | Monday | 2015 | 10
879 | 2015-10-05 06:57 | 2015-11-05 14:57 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 17 | Checked & found, Recl. 9D-25 (8C fdr #1) T/R 1x Ctr: 45-46. Patrolled the line, but found nothing. Cause: Unidentified. | 3056411 | 1 | 6:57 | Morning | Monday | 2015 | 10
880 | 2015-10-05 10:00 | 2015-10-05 10:00 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 7 | 10:00 It was reported power outage at Libo fdr #2. (Libo RTU failed at that time) Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 390-391 R/F: 51N. 15:45 Patrolled the line and found nothing. Cause: Suspected Lightning. | 356406 | 1 | 10:00 | Morning | Monday | 2015 | 10
881 | 2015-10-05 10:01 | 2015-10-05 10:01 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 10:01 It was reported b/o fuse for Tx o/p #11-J2-15. 13:50 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #11-J2-15. Replaced the b/o fuse with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 10:01 | Morning | Monday | 2015 | 10
882 | 2015-10-05 10:25 | 2015-10-05 10:25 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Switchboard Problem | 0 | 10:25 It was reported b/o fuse for Tx o/p #03-01-31 (2 Wells were Off). 13:20 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-01-31. Also found, burn out Switch Board. (The fuse is still Off prior to replacing the broken Switch Board) Cause: Switchboard Problem | 305406 | 1 | 10:25 | Morning | Monday | 2015 | 10
883 | 2015-10-05 13:55 | 2015-10-05 13:55 | 13.8KV S. BALAM FEEDER #4 | Fair | Animal | 28 | It was reported b/o fuse for Tx at Well So.Balam #348. (Balam fdr #4) Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well So.Balam #348. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Rat) | 3056406 | 1 | 13:55 | Afternoon | Monday | 2015 | 10
884 | 2015-10-05 14:21 | 2015-10-05 14:21 | DURI POWER PLANT | Fair | Under investigation | 0 | 14:21 DGT #7 Tripped by alarm: Compressor bleed valve (IGV trouble) & R/F # 32. Cause: under investigation. 21:10 Re-S/U DGT #7, then Online at 21:40. (After replacing pressure switch) | 3056406 | 1 | 14:21 | Afternoon | Monday | 2015 | 10
885 | 2015-11-05 03:50 | 2015-11-05 03:50 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Rain and Lightning | Lightning | 59 | CKB fdr #6 load dropped 192A (216-24A). Not checked yet. | 3056411 | 1 | 3:50 | Night | Thursday | 2015 | 11
886 | 2015-11-05 03:50 | 2015-12-05 06:50 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Rain and Lightning | Lightning | 59 | Checked & found, Recl. 34CU-34 (CKBS fdr #6) T/R 1x Ctr: 17-18. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3056411 | 1 | 3:50 | Night | Thursday | 2015 | 11
887 | 2015-11-05 08:00 | 2015-11-05 08:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Animal | 0 | 08:00 It was reported b/o fuse for Tx o/p #SD-03C. (DC fdr #1) 09:20 Checked & found, @1, @3 b/o 3.5SF fuses for 3x50Kva Tx o/p #SD-03C. Replaced b/o fuses above with the same size, then energized the Tx. Cause: Animal. (Bird) | 3056406 | 1 | 8:00 | Morning | Thursday | 2015 | 11
888 | 2015-11-05 13:40 | 2015-11-05 13:40 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 0 | 13:40 It was reported no power at TX #B Pematang-GS. (Pematang fdr #1) 17:30 Checked & found, Recl. for 5MVA Tx #B at Pematang-GS T/O. Performed TTR & Megger Test the Tx & found, good reading. Closed Recl. above, ok. Cause: Unidentified. | 3056406 | 1 | 13:40 | Afternoon | Thursday | 2015 | 11
889 | 2015-11-05 16:29 | 2015-11-05 16:29 | 115KV KOTABATAK JUNCTION - 4B LINE | Rain and Lightning | Lightning | 36 | 16:29 115KV KBJ GCB #33 T/SO. 115KV KBJ GCB #35 T/SO. 115KV 4B GCB #21 T/R. R/F: 87L (@2-G) & 67N. (2.4KM) Ctr: Not reported yet. (115KV KBJ-4B line T/SO) 13.8KV 4B fdr #1 Load dropped 171A (350-179A) 17:06 Closed 115KV KBJ GCB #33 & GCB #35. KBJ is not checked & The line is not patrolled yet. | 3056411 | 1 | 16:29 | Afternoon | Thursday | 2015 | 11
890 | 2015-11-05 16:29 | 15/05/2015 10:44 | 115KV KOTABATAK JUNCTION - 4B LINE | Rain and Lightning | Lightning | 36 | Patrolled the line & found, @2 Flash over Dead End Insulator o/p #K4B-20. Cause: Lightning. | 3056411 | 1 | 16:29 | Afternoon | Thursday | 2015 | 11
891 | 2015-12-05 09:00 | 2015-12-05 09:00 | 13.8KV DURI FIELD FEEDER #3 | Fair | Pin Insulator | 31 | 09:00 Duri Field fdr #3 Load dropped 68A (180-112A) It was reported that no Power at downstream of pole #01-07-01. 09:55 Checked & found, Recl. 01-07-01 (Duri Field fdr #3) T/O. (In blocked for PT. Multi Job) Checked at the Spot of PT. Multi Job & found, normal. (Clear) 10:02 Blocked & closed Recl. 01-07-01, Ok. (The line is still in block for PT. Multi Job) The line is not patrolled yet. | 3056406 | 1 | 9:00 | Morning | Saturday | 2015 | 12
892 | 2015-12-05 09:00 | 18/05/2015 13:36 | 13.8KV DURI FIELD FEEDER #3 | Fair | Pin Insulator | 31 | Patrolled the line & found, @1 broken Pin Insulator o/p 01 07 13. Cause: Pin Insulator. | 3056406 | 1 | 9:00 | Morning | Saturday | 2015 | 12
893 | 2015-12-05 10:13 | 2015-12-05 10:13 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 73 | 10:13 5B fdr #3 load dropped 116A (119-3A). (no Alarm Trip at DSC) 5B fdr #1 load dropped 72A (93-21A) 5B fdr #2 load dropped 152A (183-31A) 5B fdr #6 load dropped 114A (119-5A). 11:16 Checked & found 5B OCB fdr #3 T/R 1x Ctr: 350-351 R/F: 51@1,@2. The line is not patrolled yet. | 3056411 | 1 | 10:13 | Morning | Saturday | 2015 | 12
894 | 2015-12-05 10:13 | 15/05/2015 10:47 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 73 | Checked & found 5B OCB Fdr #3 T/R 1x Ctr: 350-351 R/F: 51 @1,@2. Patrolled the line found,@1 Flash over Dead End Insulator o/p 4C 11. Cause: Lightning. | 3056411 | 1 | 10:13 | Morning | Saturday | 2015 | 12
895 | 2015-12-05 15:49 | 2015-12-05 15:49 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Bangko fdr #4 Load dropped 64A (216-147A). (Bangko GFPC did not operate) Ground fault alarm on Bangko fdr #4. Not checked yet. | 3056406 | 1 | 15:49 | Afternoon | Saturday | 2015 | 12
896 | 2015-12-05 15:49 | 13/05/2015 12:49 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 457-458. Patrolled the line, but found nothing. Cause: Unidentified. | 3056406 | 1 | 15:49 | Afternoon | Saturday | 2015 | 12
897 | 2015-12-05 16:22 | 2015-12-05 16:22 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Pinang OCB fdr #1 T/R 1x. Not checked yet. | 3056406 | 1 | 16:22 | Afternoon | Saturday | 2015 | 12
898 | 2015-12-05 16:22 | 17/05/2015 17:28 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found Pinang VCB Fdr# 1 T/R 1X counter:336-337 R/F: 51 on phase # 2. Patrolled the line,found @2 broken pin insulator o/p 12 E 06 on Pinang main road. Cause: Lightning. | 3056406 | 1 | 16:22 | Afternoon | Saturday | 2015 | 12
899 | 2015-05-13 14:40 | 2015-05-13 14:40 | 13.8KV PEMATANG FEEDER #1 | Fair | Dead End Insulator | 36 | Pematang OCB fdr #1 T/R 1x. Pematang fdr #2 load dropped 59A (69-10A). (Pematang RTU failed at that time) Not checked yet. | 3056406 | 1 | 14:40 | Afternoon | Wednesday | 2015 | 5
900 | 2015-05-13 14:40 | 2015-05-18 11:10 | 13.8KV PEMATANG FEEDER #1 | Fair | Dead End Insulator | 36 | Checked & found, Pematang OCB fdr #1 T/R 1x Ctr: 110-111 R/F: 51N. Patrolled the line & found, @1 F/O Dead end insulator o/p #35BC-11. Cause: Dead end insulator. | 3056406 | 1 | 14:40 | Afternoon | Wednesday | 2015 | 5
901 | 2015-05-13 14:54 | 2015-05-13 14:54 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Animal | 0 | 14:54 It was reported b/o fuse for Tx o/p #04-03-11. (C.Duri fdr #9) 16:26 Checked & found, @1 b/o 2.1SF fuse for 112.5KVA Tx o/p #04-03-11. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal (Bird). | 3056406 | 1 | 14:54 | Afternoon | Wednesday | 2015 | 5
902 | 2015-05-13 15:45 | 2015-05-13 15:45 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 5 | 15:45 It was reported b/o fuse for Tx at Well Pagar #30. (Ketigul fdr #2) 16:13 Checked & found, @1 b/o fuse for 300KVA Tx at Well Pagar #30. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Monkey) | 3056406 | 1 | 15:45 | Afternoon | Wednesday | 2015 | 5
903 | 2015-05-13 17:52 | 2015-05-13 17:52 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 123 | 17:52-18:19 Manually opened Recl. 9D-25 (18 Wells were off) to reduce Load of 8C fdr #1. (Due to switching to transfer load of MSU-1 C/S TX #1 to 8C fdr #3 & 8C fdr #1 ) for Shutdown MSU-1 (8C Substation), to add low SF-6 Gas of 115KV MSU-1 C/S TX #1. Cause: Planned Maintenance. | 3056411 | 1 | 17:52 | Afternoon | Wednesday | 2015 | 5
904 | 2015-05-14 05:10 | 2015-05-14 05:10 | 13.8KV 6D FEEDER #5 | Fair | Unidentified | 27 | 6D OCB fdr #5 T/R 1x. Not checked yet. | 3056411 | 1 | 5:10 | Morning | Thursday | 2015 | 5
905 | 2015-05-14 05:10 | 2015-05-17 17:15 | 13.8KV 6D FEEDER #5 | Fair | Unidentified | 27 | Checked & found, 6D OCB fdr #5 T/R 2x Ctr: 718-720 R/F: 51@2,@3. Patrolled the line, but found nothing. Cause: Unidentified. | 3056411 | 1 | 5:10 | Morning | Thursday | 2015 | 5
906 | 2015-05-14 12:18 | 2015-05-14 12:18 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 17 | 12:18 Sintong OCB fdr #2 T/R 1x. Sintong GFPC T/R 1x (Ground fault alarm on Sintong fdr #2) 12:23 It was reported no power at Pagar-GS. (Sintong fdr #2) 13:11 Checked & found, Recl. 28AF-17 (Sintong fdr #2) T/SO. Ctr: 422-423. Blocked & closed Recl. 28AF-17, Ok. Then released the block. 14:30 Checked & Sintong OCB fdr #2 T/R 1x Ctr: 761-762 R/F: 50N.. Not patrolled yet. | 3056406 | 1 | 12:18 | Afternoon | Thursday | 2015 | 5
907 | 2015-05-14 12:18 | 2015-05-17 17:06 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 17 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3056406 | 1 | 12:18 | Afternoon | Thursday | 2015 | 5
908 | 2015-05-14 13:53 | 2015-05-14 13:53 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Pinang OCB fdr #1 T/R 1x. Not checked yet. | 3056406 | 1 | 13:53 | Afternoon | Thursday | 2015 | 5
909 | 2015-05-14 13:53 | 2015-05-16 10:00 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Pinang OCB fdr #1 T/R 1x Ctr: 337-338 R/F: 51@1. Patrolled the line & found, @1 broken Pin Insulator o/p #12F-06. Cause: Lightning. | 3056406 | 1 | 13:53 | Afternoon | Thursday | 2015 | 5
910 | 2015-05-14 14:20 | 2015-05-14 14:20 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 14:20 It was reported b/o fuse for Tx Near Dentist Building Medical. (DC fdr #5) 15:59 Checked & found, @3 b/o 3.5SF fuse for 150KVA Tx o/p #NN. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 14:20 | Afternoon | Thursday | 2015 | 5
911 | 2015-05-14 21:12 | 2015-05-14 21:12 | 13.8KV SINTONG FEEDER #2 | Fair | Powerline - Jumper | 3 | 21:12 It was reported unbalance voltage at well Sintong #34 & #40. (Sintong fdr #2) 22:54 Checked & found, @2 Broken Jumper o/p #NN. (TOP of Well Sintong #34 & #40) 23:42 Blocked Sintong OCB fdr #2 & GFPC. Repaired @2 Broken Jumper o/p #NN above. 00:33 Normalized block Sintong fdr #2 & GFPC. Then energized Tx for Well Singtong #34 & #40. Cause: Broken Jumper. | 3056406 | 1 | 21:12 | Night | Thursday | 2015 | 5
912 | 2015-05-15 02:10 | 2015-05-15 02:10 | CENTRAL DURI POWER PLANT | Fair | Under investigation | - | 02:10 CGT #2 Tripped, By Alarm: Fire Detector (Not Real). Frequency system dropped to 59.80Hz. (No Load shedding) 02:16 Closed ACB #19. (Tie Breaker) 02:54 Re-S/U CGT #2, then on line the unit at 03:17. 03:10 Opened Tie Breaker ACB#19. 09:25 CGT #2 Tripped again, By Alarm: Fire Detector (Not Real). Frequency system dropped to 59.68Hz. (No Load shedding) 09:40 Closed ACB #19. (Tie Breaker) 12:00 S/U CGT #2 then Online the unit at 12:20. 12:18 Opened Tie Breaker ACB #19. Cause: Under Investigation. | 3056406 | 1 | 2:10 | Night | Friday | 2015 | 5
913 | 2015-05-15 07:09 | 2015-05-15 07:09 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Broken Fuse Cut Out | 0 | 07:09 It was reported b/o fuse for Tx o/p #08-M1-23. (C.Duri fdr #1) 10:18 Checked & found, @1 broken FCO for 112.5Kva Tx o/p #08-M1-23. Cause: Broken Fuse Cut Out. | 3056406 | 1 | 7:09 | Morning | Friday | 2015 | 5
914 | 2015-05-15 07:09 | 2015-05-16 10:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Broken Fuse Cut Out | 0 | Replaced broken FCO for 112.5Kva & energized the Tx o/p #08-M1-23. Cause: Broken FCO. | 3056406 | 1 | 7:09 | Morning | Friday | 2015 | 5
915 | 2015-05-15 10:00 | 2015-05-15 10:00 | 13.8KV S. BALAM FEEDER #1 | Fair | Main breaker | 21 | 10:00 It was reported b/o fuse for Tx at well S. Balam #106 (Balam fdr #1). 11:05 Checked & found, @1 b/o fuse for 50KVA Tx. Also found b/o secondary Main Breaker. Performed TTR & Megger Test the Tx, found good reading. (The Tx still de-energized for Replacing Main Breaker). Cause: Main Breaker. | 3056406 | 1 | 10:00 | Morning | Friday | 2015 | 5
916 | 2015-05-15 10:05 | 2015-05-15 10:05 | 13.8KV 8C FEEDER #3 | Cloudy | Lightning | 0 | 8C VCB fdr #3 load dropped 110A (183-73A). Not checked yet. | 3056411 | 1 | 10:05 | Morning | Friday | 2015 | 5
917 | 2015-05-15 10:05 | 2015-05-20 13:06 | 13.8KV 8C FEEDER #3 | Cloudy | Lightning | 0 | Checked & found Recl. 8D-18A T/R 1x Ctr:21-22. Patrolled the line found, @1 Flashed over pin insulator o/p 8C-59 near Loc: 8C 49. Cause: Lightning. | 3056411 | 1 | 10:05 | Morning | Friday | 2015 | 5
918 | 2015-05-16 03:41 | 2015-05-16 03:41 | 5 BRAVO SUBSTATION | Fair | Under investigation | 99 | 03:41 115Kv 5B OCB #25 & OCB #26. (for 5B Tx-2) T/O. 05:07 Checked & found: 115 Kv OCB #25 T/O. Ctr: Not reported yet. 115 Kv OCB #26 T/O. Ctr: Not reported yet. R/F: 87T @3 & 86T-2 (Checked 5B TX #2, Normal condition) 05:10 Open 5B OCB fdr #8, then closed at 02:12. Open 5B OCB fdr #5, then closed at 06:13. 05:28 Man Open 5B OCB fdr #4 (not operated from DSC), then closed at: 08:00. 05:35 Open isolation switch 5B OCB fdr #4. 06:09 Closed 115Kv OCB #25 (79C/O to D/L), Ok. 06:10 Closed 115Kv OCB #26 (79C/O to S/C), Ok. 07:35 Also found, DC Breaker for 5B OCB fdr #4 Tripped. (Relay did not work) Closed DC Breaker, OK. Then Function Test 5B OCB fdr #4. 07:54 Patrolled the line under 5B OCB fdr #4, found nothing. 08:00 Blocked & closed 5B OCB fdr #4, Ok. Then released the block. Not patrolled yet. | 3056411 | 1 | 3:41 | Night | Saturday | 2015 | 5
919 | 2015-05-16 17:56 | 2015-05-16 17:56 | 115KV CENTRAL DURI - BATANG LINE | Rain and Lightning | Lightning | 16 | 17:56 115KV C.Duri OCB #31 T/R 1x Ctr: Not reported yet. 115Kv C.Duri OCB #33 T/SO Ctr: Not reported yet. 115Kv Sintong GCB #25 T/R 1x Ctr: Not reported yet. (115KV C.Duri Sintong line) Respectively: So.Balam fdr #2 load dropped 69A (69-0A). T/O WIP at Balam GS. So. Balam fdr #3 load dropped 66A (66-0A). T/O WIP at Balam GS. So. Balam fdr #4 load dropped 20A (119-99A). Bangko fdr #1 load dropped 66A (259-193A). Bangko fdr #2 load dropped 193A (243-50A). T/O WIP at Bangko GS. Bangko fdr #3 load dropped 169A (192-23A). T/O WIP at Bangko GS. Bangko fdr #4 load dropped 69A (215-146A). 19:56 Closed 115KV C.Duri OCB #33. Not checked yet. | 3056406 | 1 | 17:56 | Afternoon | Saturday | 2015 | 5
920 | 2015-05-16 17:56 | 2015-05-19 14:11 | 115KV CENTRAL DURI - BATANG LINE | Rain and Lightning | Lightning | 16 | Checked & found, 115KV C.Duri GCB # 31 T/R 2x Ctr: 20-22 R/F: 51N. Patrolled 115KV C.Duri-Sintong line, but found nothing. Cause: Suspected by Lightning. | 3056406 | 1 | 17:56 | Afternoon | Saturday | 2015 | 5
921 | 2015-05-16 18:08 | 2015-05-16 18:08 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 57 | Batang VCB fdr #3 T/R 1x. Not checked yet. | 3056406 | 1 | 18:08 | Afternoon | Saturday | 2015 | 5
922 | 2015-05-16 18:08 | 2015-05-19 15:28 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 57 | Checked & found VCB fdr#3 T/R 1 x Ctr: 267-268 R/F: 51N. Patrolled the line found, @1 Broken Dead End Insulator o/p 35 AK 18. @1 Flash Over Dead End Insulator o/p 35 AK 08. Cause: Lightning. | 3056406 | 1 | 18:08 | Afternoon | Saturday | 2015 | 5
923 | 2015-05-16 19:23 | 2015-05-16 19:23 | KETIGUL SUBSTATION | Rain and Lightning | Relay Failure | 1692 | 19:23 Pagar GS informed no incoming fluid to GS. (Ketigul RTU failed at 17:00). 20:03 It was reported no power d/s Ketigul fdr #1, #2, #3. 22:00 Checked & found, Ketigul GCB #2 T/O ctr: 162-165. Ketigul GCB #3 T/O ctr: 139-140. R/F:.... Also found GFPC Ketigul TX #1 T/SO ctr: 613. (The weather was still rain). 22:40 Checked Ketigul TX #1 & other equipments, found Normal. 22:45 Manual opened Ketigul VCB fdr #1. Manual opened Ketigul VCB fdr #2. Manual opened Ketigul VCB fdr #3. By-passed GFPC Ketigul TX #1. 23:22 Closed Ketigul GCB #2. Ketigul TX #1 re-energized. 23:27 Closed Ketigul GCB #3. Monitored Ketigul TX #1 for abnormal condition. 23:35 Also found Ketigul fdr #1 relay failed. 23:39 Blocked & closed Ketigul VCB fdr #3, ok, then released the block. 23:41 Blocked & closed Ketigul VCB fdr #2, ok, then released the block. 17-MAY-2015 00:55 Patrolled the line & found nothing. 00:56 Blocked Ketigul VCB fdr #2. Released at: 01:05. 00:58 Closed LBS #31AL-4A (Ketigul fdr #1 transfered to Ketigul fdr #2). Cause: Under Investigation. Prod loss: Ketigul fdr #1: 744 bbls/33 Wells. Ketigul fdr #2: 854 bbls/46 Wells. Prod loss : Ketigul fdr #1 (17-May-15 from 00:00 to 00:58) 125 bbls / 33 wells | 3056406 | 1 | 19:23 | Night | Saturday | 2015 | 5
924 | 2015-05-16 21:27 | 2015-05-16 21:27 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Dead End Insulator | 0 | C. Duri ACB #17 fdr #13 T/R 2x ctr: 179-181 R/F: 51N @1, @2. Not patrolled yet. | 3056406 | 1 | 21:27 | Night | Saturday | 2015 | 5
925 | 2015-05-16 21:27 | 2015-05-20 11:34 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Dead End Insulator | 0 | Checked & found C. Duri ACB #17 fdr #13 T/R 2x Ctr:179-181 R/F: 51N @1, @2. Patrolled the line found,@1 Broken Dead end Insulator o/p 05 M5 A6. Cause: Dead end Insulator. | 3056406 | 1 | 21:27 | Night | Saturday | 2015 | 5
926 | 2015-05-16 21:33 | 2015-05-16 21:33 | 13.8KV BEKASAP FEEDER #3 | Fair | Unidentified (Fuse) | 18 | It was reported b/o fuse for Tx at well Jambon #01 (Bekasap Main fdr #3). Not checked yet. | 3056406 | 1 | 21:33 | Night | Saturday | 2015 | 5
927 | 2015-05-16 21:33 | 2015-05-17 09:12 | 13.8KV BEKASAP FEEDER #3 | Fair | Unidentified (Fuse) | 18 | Checked & found, @2 b/o fuse for 300Kva Tx at well Jambon #01. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 21:33 | Night | Saturday | 2015 | 5
928 | 2015-05-17 06:40 | 2015-05-17 06:40 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3056406 | 1 | 6:40 | Morning | Sunday | 2015 | 5
929 | 2015-05-17 06:40 | 2015-05-18 11:10 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 73-74 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3056406 | 1 | 6:40 | Morning | Sunday | 2015 | 5
930 | 2015-05-17 07:08 | 2015-05-17 07:08 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 07:08 CGT #2 Tripped By: Fire detector alarm. (45 FT-3) 07:16 Closed ACB #19. (Tie Breaker) 15:05 S/U CGT #2, then Online the unit at 15:26. 15:22 Opened ACB #19. (Tie Breaker) Cause: Under Investigation. | 3056406 | 1 | 7:08 | Morning | Sunday | 2015 | 5
931 | 2015-05-17 08:20 | 2015-05-17 08:20 | DARLING SUBSTATION | Fair | Under investigation | 91 | 08:20 It was reported B/O TX at CSS-5 (DIF). 08:36 Also reported no power on one road nearest pole #05-N3-15. (Darling RTU failed at that time) 09:10 Checked TX at CSS-5 & found, normal. 11:36 Checked Darling Substation, found @1 b/o fuse for 50KVA Tx (Station service). Replaced b/o fuse above with the same size then energized the Tx. 12:06 Darling RTU back to Online, but the Metering at Darling Substation could not be read. 13:02 Manually Opened Darling VCB fdr #8. 13:26 Blocked & Closed Darling VCB fdr #8. 14:06 Checked & found: 115Kv Darling GCB #1 T/O. Ctr. & R/F are not reported yet 115Kv Darling GCB #3 T/O. Ctr. & R/F are not reported yet. 14:16 Opened Darling VCB fdr #8. 14:18 Checked Darling TX #2 & found, Normal. Closed 115Kv Darling GCB #1 & GCB #3, but failed. 14:26 Isolated Darling TX #2. Closed 115Kv Darling GCB #1 & GCB #3, but still failed. 14:40 Closed 13.8Kv Tie Breaker for Darling Bus #1 & Bus #2. 14:45 Blocked & closed Darling VCB fdr #8, Ok. Then released the block. Cause: Under Investigation. | 3056406 | 1 | 8:20 | Morning | Sunday | 2015 | 5
932 | 2015-05-17 08:50 | 2015-05-17 08:50 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 114 | 08:50 Batang fdr #3 Load dropped 19A (47-28A) 11:30 Checked & found, Recl. 36AL-13 (Batang fdr #3) T/SO. Ctr: 114-115. Patrolled the line, but found nothing. 12:10 Blocked & Closed Recl. 36AL-13, Ok. Then released the block. Cause: Unidentified. | 3056406 | 1 | 8:50 | Morning | Sunday | 2015 | 5
933 | 2015-05-17 09:05 | 2015-05-17 09:05 | 13.8KV PUNGUT FEEDER #1 | Fair | Unidentified (Fuse) | 58 | 09:05 It was reported b/o fuse for Tx at Well Pungut #23. 17:00 Checked & found, @1 b/o 2.1SF fuse for 100Kva Tx at Well Pungut #23. 17:20 Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 9:05 | Morning | Sunday | 2015 | 5
934 | 2015-05-17 18:59 | 2015-05-17 18:59 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 28 | MSU-2 VCB fdr #2 (Nella fdr #2) T/R 1x. Not checked yet. | 3056406 | 1 | 18:59 | Afternoon | Sunday | 2015 | 5
935 | 2015-05-17 18:59 | 2015-05-19 11:05 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 28 | Checked & found, MSU-2 VCB fdr #2 T/R 1x Ctr: 205-206 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected Lightning. | 3056406 | 1 | 18:59 | Afternoon | Sunday | 2015 | 5
936 | 2015-05-18 15:00 | 2015-05-18 15:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 15:00 It was reported B/O fuse for Tx at Well KB #336. (while start after troubleshoot the switchboard) 15:51 Checked & found, @1 b/o 3.1Sf fuse for 150Kva Tx at Well KB #336. Performed megger & TTR test the TX, found. Replaced b/o fuse above with same size, then energized Tx. Cause: Unidentified (fuse). | 3056406 | 1 | 15:00 | Afternoon | Monday | 2015 | 5
937 | 2015-05-18 18:03 | 2015-05-18 18:03 | 13.8KV 3D FEEDER #2 | Fair | Planned Maintenance | 26 | 18:03 It was reported Hot Spot on 600Kva Tx at Well #3E-65. (Hot Spot inside of the TX radiator as result of infra metric scanning) Replaced 600Kva Tx with 550Kva Tx, then energized the Tx. Cause: Maintenance Job. | 123 | 1 | 18:03 | Afternoon | Monday | 2015 | 5
938 | 2015-05-19 06:29 | 2015-05-19 06:29 | 13.8KV SINTONG FEEDER #1 | Fair | Pin Insulator | 1 | 06:29 Sintong fdr #1 Load dropped 10A (86-76A). Ground fault alarm on Sintong fdr #1. 08:33 It was reported no power at Menggala GS a& Menggala north fields. 09:47 Checked & found, Recl. 19AN-04 (Sintong fdr #1) T/LO. Ctr: 301-305. Patrolled line & found, @2 broken support Pin insulator o/p #19AK-10. (Then replaced its Pin insulator o/p #19AK-10) 11:24 Blocked & closed Recl. 19AN-04, Ok. Then released the block. Cause: Pin Insulator. | 3056406 | 1 | 6:29 | Morning | Tuesday | 2015 | 5
939 | 2015-05-19 18:50 | 2015-05-19 18:50 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | 18:50 No.Duri VCB fdr #9 T/O. N0.Duri GFPC Tx-13 T/R 1x. 18:56 Blocked & Closed No.Duri VCB fdr #9, Ok. Then release the block. Not checked yet. | 3056406 | 1 | 18:50 | Afternoon | Tuesday | 2015 | 5
940 | 2015-05-19 18:50 | 2015-05-22 13:50 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | Chcked & found, No.Duri VCB fdr #9 T/R 1x Ctr: 031-032 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3056406 | 1 | 18:50 | Afternoon | Tuesday | 2015 | 5
941 | 2015-05-19 21:48 | 2015-05-19 21:48 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 16 | 5B OCB fdr #4 T/R 1x. Not checked yet. | 3056411 | 1 | 21:48 | Night | Tuesday | 2015 | 5
942 | 2015-05-19 21:48 | 2015-05-21 14:50 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 16 | Checked & found, 5B OCB fdr #4 T/R 1x Ctr: 314-315 R/F: 51N. Patrolled the line & found, @1 F/O Dead end Insulator o/p #NN. (near Well #4C-91) Cause: Lightning. | 3056411 | 1 | 21:48 | Night | Tuesday | 2015 | 5
943 | 2015-05-19 21:49 | 2015-05-19 21:49 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 93 | 4B OCB fdr #2 T/R 1x. 4B fdr #1 dropped 239A (343-104A). 4B fdr #3 dropped 66A (68-2A). Not checked yet. | 3056411 | 1 | 21:49 | Night | Tuesday | 2015 | 5
944 | 2015-05-19 21:49 | 2015-05-20 11:49 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 93 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 206-207 R/F: 51@2. Patrolled the line & found, @2 F/O Dead end Insulator o/p #4B-46. Cause: Lightning. | 3056411 | 1 | 21:49 | Night | Tuesday | 2015 | 5
945 | 2015-05-20 06:24 | 2015-05-20 06:24 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3056406 | 1 | 6:24 | Morning | Wednesday | 2015 | 5
946 | 2015-05-20 06:24 | 2015-05-22 14:24 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 074-075 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3056406 | 1 | 6:24 | Morning | Wednesday | 2015 | 5
947 | 2015-05-20 09:00 | 2015-05-20 09:00 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 281 | 09:00-16:30 Shut down 12 Wells at downstream of So.Balam fdr #4 for Tie in new power line. (So.Balam #175, #373, #375, #185, #77, #78, #166, #58, 367, #22, #162 & #234). Cause: Plan Maintenance. | 123 | 1 | 9:00 | Morning | Wednesday | 2015 | 5
948 | 2015-05-20 10:09 | 2015-05-20 10:09 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 10:09 It was reported b/o fuse for Tx o/p #08-L5-12. (C.Duri fdr #2) 14:26 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #08-L5-12. Replaced fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 10:09 | Morning | Wednesday | 2015 | 5
949 | 2015-05-20 10:25 | 2015-05-20 10:25 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 10:25 It was reported b/o fuse for Tx o/p #13-F8-19. (3 Wells were off) 15:55 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #13-F8-19. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (fuse). | 3056406 | 1 | 10:25 | Morning | Wednesday | 2015 | 5
950 | 2015-05-20 14:15 | 2015-05-20 14:15 | 13.8KV 3D FEEDER #4 | Fair | Unidentified (Fuse) | 12 | 14:15 It was reported b/o fuse for Tx at Well #1D-35. (3D fdr #4) 17:31 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well #1D-35. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (fuse). | 3056411 | 1 | 14:15 | Afternoon | Wednesday | 2015 | 5
951 | 2015-05-20 16:48 | 2015-05-20 16:48 | 13.8KV BANGKO GFPC | Fair | Unidentified | 0 | Bangko fdr #1 dropped 7A (214-207A). Bangko GFPC T/R 1x. (Ground fault alarm on Bangko fdr #1) Not checked yet. | 3056406 | 1 | 16:48 | Afternoon | Wednesday | 2015 | 5
952 | 2015-05-20 16:48 | 2015-05-26 09:14 | 13.8KV BANGKO GFPC | Fair | Unidentified | 0 | Checked & found, Bangko GFPC T/R 1x Ctr: 458-459. Patrolled Bangko fdr #1 line, but found nothing. Cause: Unidentified. | 3056406 | 1 | 16:48 | Afternoon | Wednesday | 2015 | 5
953 | 2015-05-21 12:57 | 2015-05-21 12:57 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 42 | Ketigul VCB fdr #1 T/R 1x. Ketigul GFPC T/R 1x. Not checked yet. | 3056406 | 1 | 12:57 | Afternoon | Thursday | 2015 | 5
954 | 2015-05-21 12:57 | 2015-05-26 07:29 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 42 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 156-157 R/F: 51N(@1). Patrolled the line & found, @1 flash over Dead end insulator o/p #32AJ-01. Cause: Dead end insulator. | 3056406 | 1 | 12:57 | Afternoon | Thursday | 2015 | 5
955 | 2015-05-21 15:24 | 2015-05-21 15:24 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 14 | 15:24 It was reported b/o fuse for Tx o/p #05-P3-09. (C.Duri fdr #14) 16:30 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #05-P3-09. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 15:24 | Afternoon | Thursday | 2015 | 5
956 | 2015-05-21 17:00 | 2015-05-21 17:00 | NORTH DURI POWER PLANT |  |  | - | 17:00 S/U NDC-CT #2, then online the unit at 21:06. |  | 1 | 17:00 | Afternoon | Thursday | 2015 | 5
957 | 2015-05-21 22:51 | 2015-05-21 22:51 | 13.8KV 5B FEEDER #3 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx at Well #4D-56. (5B fdr #3) Not checked yet. | 3056411 | 1 | 22:51 | Night | Thursday | 2015 | 5
958 | 2015-05-21 22:51 | 2015-05-22 10:10 | 13.8KV 5B FEEDER #3 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1,@2 b/o 3.1SF fuses for 150Kva Tx at Well #4D-56. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3056411 | 1 | 22:51 | Night | Thursday | 2015 | 5
959 | 2015-05-22 08:14 | 2015-05-22 08:14 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 492 | 08:14 Ketigul VCB fdr #2 T/O. 10:10 Checked & found Ketigul VCB fdr #2 T/O. Ctr: 62-63 R/F: 51N. 10:03 Patrolled the line & found, @1 Broken Dead End Insulator o/p #26AI-19. 10:05 Open LBS #28AL-05 line to Ubi & Sikeladi Field. 10:13 Blocked & closed Ketigul VCB fdr #2, then release the block. Replaced @1 Broken Dead End Insulator o/p #26AI-19. 11:40 Closed LBS #28AL-05 for Ubi & Sikeladi Field. Cause: Dead End Insulator. | 3056406 | 1 | 8:14 | Morning | Friday | 2015 | 5
960 | 2015-05-22 14:10 | 2015-05-22 14:10 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 0 | 14:10 It was reported no power at Well Sam-Sam #06. (Libo fdr #1) 14:27 Checked & found, Recl. 34CA-04 (Libo fdr #1) T/O. (In blocked Position) Ctr: 23-24. 14:29 Closed Recl. 34CA-04, then release the block. Patrolled the line, but found nothing. Cause: Unidentified. | 3056406 | 1 | 14:10 | Afternoon | Friday | 2015 | 5
961 | 2015-05-22 17:37 | 2015-05-22 17:37 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | 17:37 It was reported b/o fuse for Tx o/p #03-0-09. (C.Duri fdr #6) 18:50 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-0-09. Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 17:37 | Afternoon | Friday | 2015 | 5
962 | 2015-05-23 09:05 | 2015-05-23 09:05 | MINAS POWER PLANT | Fair | Equipment Failure | 0 | 09:05 MGT #11 Trip by alarm: Gen Diff. Trip. Freq: 59.84. No load shedding occured. Cause: Gen AVR Capacitor burnt out. | 3056411 | 1 | 9:05 | Morning | Saturday | 2015 | 5
963 | 2015-05-23 22:55 | 2015-05-23 22:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 0 | 22:55 It was reported b/o fuse for Tx at Well Puncak #31. (C.Duri fdr #1) 00:49 Checked & found, @2, @3 b/o 3.5SF fuses for 150Kva Tx at Well Puncak #31. Replaced b/o fuses above with the same size then energized the Tx. Cause: Animal (Eagle). | 3056406 | 1 | 22:55 | Night | Saturday | 2015 | 5
964 | 2015-05-23 23:17 | 2015-05-23 23:17 | 13.8KV PEMATANG FEEDER #2 | Fair | Animal | 25 | 23:17 It was reported b/o fuse for Tx at Well Pematang #97. (Pematang fdr #2) 25-MAY-2015 01:53 Checked & found, @3 b/o 7.8SF fuse for 300Kva Tx at Well Pematang #97. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal (Eagle). | 3056406 | 1 | 23:17 | Night | Saturday | 2015 | 5
965 | 2015-05-23 23:23 | 2015-05-23 23:23 | MINAS POWER PLANT |  |  | - | 23:23 Offline MGT #1 then S/D the unit for S/B. |  | 1 | 23:23 | Night | Saturday | 2015 | 5
966 | 2015-05-24 00:09 | 2015-05-24 00:09 | 13.8KV SINTONG FEEDER #1 | Fair | Theft | 55 | 00:09 It was reported vandalism Tx at Well So.Menggala #14. (Sintong fdr #1) 02:08 Checked & found, @1, @2, @3 Manual opened fuses by outsider & vandalism 500Kva Tx. (Will be replaced tomorrow). Cause: Theft. | 3056406 | 1 | 0:09 | Night | Sunday | 2015 | 5
967 | 2015-05-24 00:09 | 2015-05-25 12:00 | 13.8KV SINTONG FEEDER #1 | Fair | Theft | 55 | Replaced vandalism 500Kva Tx with the same size & energized the Tx. Cause: Theft. | 3056406 | 1 | 0:09 | Night | Sunday | 2015 | 5
968 | 2015-05-24 07:43 | 2015-05-24 07:43 | NORTH DURI POWER PLANT | Fair | Under investigation | 256 | 07:43 NDC-CT #2 T/O. (while Increasing Load from 65MW) Tripped By Alarm: Blade Path Spread On & followed with Master Trip SOE. Frequency system dropped to 59.41Hz. (Load shedding Level #1) Respectively: 3D fdr #5 T/O, then closed at 07:46. Minas GS #5. (T/O WIP 4 Units) 4D fdr #3 T/O, then closed at 08:10. Minas GS #5 Well. 4D fdr #5 T/O, then closed at 08:09. Minas GS #5 Well. 5B fdr #4 T/O, then closed at 08:36. Minas GS #6 Well. 5B fdr #5 T/O, then closed at 08:04. Minas GS #6 Well. 09:00 Re-S/U NDC-CT #2, then Online at 10:14. 19:46 NDC-CT #2 T/O again by alarm: Gas Valve Bad Quality Trip. Cause: Under Investigation. Frequency system dropped to 59.35Hz. (Load shedding level #2) Respectively: 3D fdr #5 T/O, Closed at 19:51. 4D fdr #2 T/O, Closed at 20:46. 4D fdr #3 T/O, Closed at 20:27. 4D fdr #4 T/O, Closed at 21:12. 4D fdr #5 T/O, Closed at 20:38. 4D fdr #6 T/O, Closed at 19:58. 4B fdr #4 T/O, Closed at 19:54. 5B fdr #4 T/O, Closed at 20:21. 5B fdr #5 T/O, Closed at 20:28. Prod. Loss at 07:43 : GS #5: 0 bbls GS #6: 53 bbls / 33 wells. Prod. Loss at 19:46 : GS #4: 64 bbls / 26 wells. GS #5: 79 bbls / 72 wells. GS #6: 69 bbls / 45 wells. Total Prod loss : 265 bbls / 143 bbls. | 3056406 | 1 | 7:43 | Morning | Sunday | 2015 | 5
969 | 2015-05-24 07:43 | 2015-05-25 10:32 | NORTH DURI POWER PLANT | Fair | Under investigation | 256 | 09:05 Request GS-6 to shut down some wells and WIPs (total 5 MW) 09:08 Manual S/D WIP SBP 66S at GS-6 09:10 Manual S/D WIP BJU 52S at GS-5 09:50 Manual S/D WIP SBP 42S at GS-4 10:32 Auto Load shedding level-1. (Frequency dropped to 59,60Hz) 3D fdr #5 T/O at 10:32 and closed at 10:41 4D fdr #3 T/O at 10:32 and closed at 12:38 10:47 Frequency dropped to 59,62Hz. 10:48 Manual opened 4D fdr #5 and then closed at 12:38 11:50 S/U NDC-CT #2, then Online at 12:35 Prod. Loss : GS #5 : 48 bbls / 36 wells. GS #6 : 6 bbls / 20 wells. Total Prod loss : 54 bbls / 56 wells. Grand total Prod. Loss: 265 Bbls + 54 Bbls = 319 Bbls. 143 Wells + 56 Wells = 199 Wells. | 3056406 | 1 | 7:43 | Morning | Sunday | 2015 | 5
970 | 2015-05-24 08:51 | 2015-05-24 08:51 | MINAS POWER PLANT |  |  | - | 08:51 S/U MGT #1, then On Line at 09:06. (Due to NDC-CT #2 T/O) | 123 | 1 | 8:51 | Morning | Sunday | 2015 | 5
971 | 2015-05-24 09:38 | 2015-05-24 09:38 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 10 | 09:38 It was reported b/o fuse for Tx o/p #09-T3-04. (CD fdr #4) 13:30 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #09-T3-04. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (fuse). | 3056406 | 1 | 9:38 | Morning | Sunday | 2015 | 5
972 | 2015-05-24 11:20 | 2015-05-24 11:20 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | 11:20 It was reported b/o fuse for Tx o/p #03-03-03. (CD fdr #6) Not checked yet. | 3056406 | 1 | 11:20 | Morning | Sunday | 2015 | 5
973 | 2015-05-24 11:20 | 2015-05-25 16:20 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | 16:20 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-03-03. Replaced b/o fuse above withe the same size, then energized the Tx. Cause: Unidentified (fuse). | 3056406 | 1 | 11:20 | Morning | Sunday | 2015 | 5
974 | 2015-05-24 12:30 | 2015-05-24 12:30 | 13.8KV BEKASAP FEEDER #2 | Fair | Secondary Cable | 7 | 12:30 It was reported no power at Well Bekasap #131. (BKS fdr #2) 15:45 Checked & found, broken Secondary cable of the Tx. Then replaced broken Cable above, then energized the Tx. Cause: Secondary cable. | 3056406 | 1 | 12:30 | Afternoon | Sunday | 2015 | 5
975 | 2015-05-24 12:45 | 2015-05-24 12:45 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 12:45 It was reported b/o fuse for Tx at Well BKO #82. (Nella fdr #1) 15:15 Checked & found, @3 b/o 2.1SF fuse for 100KvaTx at Well BKO #82. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (fuse). | 3056406 | 1 | 12:45 | Afternoon | Sunday | 2015 | 5
976 | 2015-05-25 04:47 | 2015-05-25 04:47 | 4.16KV NO RUMBAI FEEDER #1 | Fair | Lightning Arrester | 0 | 04:47 It was reported no power at Hibrida & Gardenia Rumbai complex. 05:49 Checked & found, 4160V North Rumbai VCB fdr #1 T/LO. Ctr: 372-374 R/F: 51N. 05:55 Blocked & closed, North Rumbai VCB fdr #1, but trip again. Ctr: 374-375 R/F: 51N. 07:01 Opened LBS #2RD-07, to isolate line toward Gardenia complex. 07:02 Opened LBS #3RD-17, to isolate line toward Hibrida complex. 07:03 Blocked & closed North Rumbai VCB fdr #1, Ok. 07:05 Closed LBS #2RD-07, but North Rumbai VCB fdr #1 T/O. Ctr: 375-376 R/F: 51N. 07:07 Opened LBS #2RD-07 07:08 Closed LBS #3RD-17 07:10 Then Blocked & closed North Rumbai VCB fdr #1, Ok. 07:12 Patrolled line at downstream of LBS #2RD-07 07:37 Found broken L/A jumper & touching to the cross arm o/p #2RE-03, then isolate it. 07:39 Closed LBS #2RD-07 07:48 Normalized block of North Rumbai VCB fdr #1 Cause: Broken L/A. | 3056411 | 1 | 4:47 | Morning | Monday | 2015 | 5
977 | 2015-05-25 11:50 | 2015-05-25 11:50 | NORTH DURI POWER PLANT |  |  | - | 11:50 S/U NDC-CT #2, then On Lne at 12:35. (After HGPI program) | 123 | 1 | 11:50 | Morning | Monday | 2015 | 5
978 | 2015-05-25 12:41 | 2015-05-25 12:41 | DURI POWER PLANT | Fair | Equipment Failure | 0 | 12:41 DGT #7 T/O. By alarm: Lube oil bearing header pressure low. (Fals Alarm) Cause: Pressure Switch problem. 17:45 S/U DGT #7, then On line at 18:08. (After replacing Pressure Switch) | 3056406 | 1 | 12:41 | Afternoon | Monday | 2015 | 5
979 | 2015-05-25 17:42 | 2015-05-25 17:42 | MINAS POWER PLANT |  |  | - | 17:42 S/U MGT #11, then On Line at 18:12. (after Replacing the Ignation transformer) |  | 1 | 17:42 | Afternoon | Monday | 2015 | 5
980 | 2015-05-25 17:56 | 2015-05-25 17:56 | 13.8KV NORTH DURI FEEDER #10 | Rain and Lightning | Lightning Arrester | 0 | 17:56 No.Duri VCB fdr #10 T/O. (in blocked status) (for PT WIS job under Power lines) 17:58 Closed No.Duri VCB fdr #10. (in blocked Status), Ok. Then Normalize the block. Not checked yet. | 3056406 | 1 | 17:56 | Afternoon | Monday | 2015 | 5
981 | 2015-05-25 17:56 | 2015-05-28 13:13 | 13.8KV NORTH DURI FEEDER #10 | Rain and Lightning | Lightning Arrester | 0 | Checked & found, No.Duri VCB fdr #10 T/O. Ctr: 11-12 R/F: 51N. Patrolled & found, @1,@2 broken Lightning Arrester o/p #11-J2-10. Cause: Lightning Arrester. | 3056406 | 1 | 17:56 | Afternoon | Monday | 2015 | 5
982 | 2015-05-26 07:50 | 2015-05-26 07:50 | 13.8KV RANGAU FEEDER #2 | Fair | Dead End Insulator | 0 | Rangau fdr #2 dropped 71A (84-13A). Rangau fdr #1 dropped 8A (29-21A). (Rangau RTU failed at 07:46 - 07:49) Not checked yet. | 305406 | 1 | 7:50 | Morning | Tuesday | 2015 | 5
983 | 2015-05-26 07:50 | 2015-05-29 16:06 | 13.8KV RANGAU FEEDER #2 | Fair | Dead End Insulator | 0 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: 116-117. Patrolled & found, @2 broken Dead end Insulator o/p #22BD-15. (Near Well Pelita #01) Cause: Dead end insulator. | 305406 | 1 | 7:50 | Morning | Tuesday | 2015 | 5
984 | 2015-05-26 07:52 | 2015-05-26 07:52 | 13.8KV PETANI FEEDER #2 | Fair | Pin Insulator | 95 | Petani fdr #2 dropped 65A (68-3A). Petani fdr #1 dropped 98A (214-116A). Not checked yet. | 3056406 | 1 | 7:52 | Morning | Tuesday | 2015 | 5
985 | 2015-05-26 07:52 | 2015-05-29 16:03 | 13.8KV PETANI FEEDER #2 | Fair | Pin Insulator | 95 | Checked & found, Petani OCB fdr #2 T/R 1x Ctr: 171-172 R/F: 51@2. Patrolled & found, @2 broken Pin insulator o/p #33AY-04. (Near well Petani #47) Cause: Pin Insulator. | 3056406 | 1 | 7:52 | Morning | Tuesday | 2015 | 5
986 | 2015-05-26 09:47 | 2015-05-26 09:47 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified (Fuse) | 4 | 09:47 It was reported b/o fuse for Tx at Well Tilan #16. 16:15 Checked & found, @2 b/o 14.0SF fuse for 500Kva Tx at Well Tilan #16. Replaced the b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 9:47 | Morning | Tuesday | 2015 | 5
987 | 2015-05-26 15:50 | 2015-05-26 15:50 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 15:50 It was reported under Voltage o/p #10-L3-18. (4 wells were off) 18:00 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #10-L3-18. Replaced the b/o fuse above with same size, then energized the Tx. Cause: Unidentified (fuse). | 3056406 | 1 | 15:50 | Afternoon | Tuesday | 2015 | 5
988 | 2015-05-27 09:24 | 2015-05-27 09:24 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | 09:24 It was reported b/o fuse for 112.5Kva Tx o/p 03-0-09 (CD fdr #6). 11:00 Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 9:24 | Morning | Wednesday | 2015 | 5
989 | 2015-05-27 14:10 | 2015-05-27 14:10 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning Arrester | 250 | 14:10 Ketigul fdr #2 load dropped to 0A, but no trip indication at HMI. 15:56 Checked & found, Ketigul VCB fdr #2 T/SO. Ctr: 163-164 R/F: 51N. 16:01 Blocked & closed Ketigul VCB fdr #2, ok. Then released the block. Not patrolled yet. | 3056406 | 1 | 14:10 | Afternoon | Wednesday | 2015 | 5
990 | 2015-05-27 14:10 | 2015-05-29 10:36 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning Arrester | 250 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 163-164 R/F: 51N. Patrolled the line & found, broken jumper of L/A o/p #26AL-20. (near Location UBI #3) Cause: Lightning Arrester. | 3056406 | 1 | 14:10 | Afternoon | Wednesday | 2015 | 5
991 | 2015-05-27 16:00 | 2015-05-27 16:00 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 16 | Sintong OCB fdr #2 T/R 1x. Not checked yet. | 3056406 | 1 | 16:00 | Afternoon | Wednesday | 2015 | 5
992 | 2015-05-27 16:00 | 2015-05-28 15:18 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 16 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 386-387 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3056406 | 1 | 16:00 | Afternoon | Wednesday | 2015 | 5
993 | 2015-05-28 15:50 | 2015-05-28 15:50 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 15:50 It was reported @2 b/o fuse for 112.5Kva Tx o/p #12-F9-11. 17:36 Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 15:50 | Afternoon | Thursday | 2015 | 5
994 | 2015-05-28 17:31 | 2015-05-28 17:31 | 13.8KV KOTABATAK FEEDER #2 | Fair | Lightning Arrester | 85 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3056411 | 1 | 17:31 | Afternoon | Thursday | 2015 | 5
995 | 2015-05-28 17:31 | 2015-05-30 08:33 | 13.8KV KOTABATAK FEEDER #2 | Fair | Lightning Arrester | 85 | Checked & found OKB OCB fdr #2 T/r 1x Ctr: 1243-1244 R/F: 51N @3. Patrolled & found, @3 broken Lightning Arrester at Terminal pole of Well KB #137. Cause: Lightning Arrester. | 3056411 | 1 | 17:31 | Afternoon | Thursday | 2015 | 5
996 | 2015-05-28 18:22 | 2015-05-28 18:22 | MINAS POWER PLANT |  |  | - | 18:22 Offline MGT #1 then S/D the unit for S/B. | 123 | 1 | 18:22 | Afternoon | Thursday | 2015 | 5
997 | 2015-05-28 20:12 | 2015-05-28 20:12 | DURI POWER PLANT |  |  | - | Off line DGT#7, then S/D the unit for S/B. |  | 1 | 20:12 | Night | Thursday | 2015 | 5
998 | 2015-05-28 21:20 | 2015-05-28 21:20 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 29 | It was reported B/O fuse for Tx at Well Tilan #16. (Ketigul fdr #1) Not checked yet. | 3056406 | 1 | 21:20 | Night | Thursday | 2015 | 5
999 | 2015-05-28 21:20 | 2015-05-29 00:30 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 29 | Checked & found, @3 b/o 7.8SF fuse for 300Kva Tx at Well Tilan #16. Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3056406 | 1 | 21:20 | Night | Thursday | 2015 | 5
1000 | 2015-05-29 04:37 | 2015-05-29 04:37 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 4 | Libo OCB fdr #2 T/R 1x. Not checked yet. | 3056406 | 1 | 4:37 | Morning | Friday | 2015 | 5
1001 | 2015-05-29 04:37 | 2015-05-30 08:06 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 4 | Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 391-392 R/F: 50@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3056406 | 1 | 4:37 | Morning | Friday | 2015 | 5
1002 | 2015-05-29 10:10 | 2015-05-29 10:10 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 10:10 It was reported @1 b/o fuse for 45Kva Tx at Well Kulin #49. (CD fdr #1) 16:25 Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 10:10 | Morning | Friday | 2015 | 5
1003 | 2015-05-29 14:55 | 2015-05-29 14:55 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 2 | 14:55 It was reported @2 b/o fuse for 300Kva Tx at Well Bangko #236. (Bangko fdr #1) 16:57 Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal (Bird). | 3056406 | 1 | 14:55 | Afternoon | Friday | 2015 | 5
1004 | 2015-05-29 15:25 | 2015-05-29 15:25 | MINAS POWER PLANT |  |  | - | 15:25 Offline MGT #4, then S/D the unit for S/B. | 123 | 1 | 15:25 | Afternoon | Friday | 2015 | 5
1005 | 2015-05-29 15:58 | 2015-04-05 08:15 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 96 | Checked & found, Ketigul T/O. (In block position for Rig Job) Ctr: 164-165 R/F: 51N(@1). Patrolled the line & found, @1 broken Dead end Insulator o/p #29AM-30. Cause: Dead end Insulator. | 3056406 | 1 | 15:58 | Afternoon | Friday | 2015 | 5
1006 | 2015-05-29 15:58 | 2015-05-29 15:58 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 96 | 15:58 Ketigul VCB fdr #2 T/O. (in block position) Ketigul GFPC blocked & by passed position. 16:14 Blocked & closed Ketigul VCB fdr #2, Ok. Not checked yet. | 3056406 | 1 | 15:58 | Afternoon | Friday | 2015 | 5
1007 | 2015-05-30 00:17 | 2015-05-30 00:17 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 15 | Sintong OCB fdr #2 T/R 1x. Ground fault alarm at Sintong fdr #2. Not checked yet | 3056406 | 1 | 0:17 | Night | Saturday | 2015 | 5
1008 | 2015-05-30 00:17 | 2015-04-06 08:50 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 15 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 387-388 R/F: 51N. Also found, Sintong GFPC T/R 2x Ctr: 766-768 Patrolled the line, but found nothing. Cause: Unidentified. | 3056406 | 1 | 0:17 | Night | Saturday | 2015 | 5
1009 | 2015-05-30 00:44 | 2015-05-30 00:44 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 46 | BKO fdr #4 Load dropped 76A (214-138A). Ground fault alarm at BKO fdr #4. (Bangko GFPC did not operate) Not Checked Yet. | 3056406 | 1 | 0:44 | Night | Saturday | 2015 | 5
1010 | 2015-05-30 00:44 | 2015-01-06 07:23 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 46 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 2x Ctr: 60-62. Also found, Bangko GFPC T/R 1x Ctr: 460-461 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3056406 | 1 | 0:44 | Night | Saturday | 2015 | 5
1011 | 2015-05-30 05:12 | 2015-05-30 05:12 | 13.8KV 4D FEEDER #2 | Fair | Animal | 206 | 05:11 Appear alarm Battery charger input OFF. 05:12 Appear alarm Battery charger input ON 4D OCB fdr #2 T/R 1x Ctr: 207-209 R/F: 51@1,@2. (Prod.loss 35 well,217 bbls). 4D fdr # 1 load dropped 265A (265 - 0) 4D fdr # 3 load dropped 60A (89 - 29) (Prod.loss 11 well, 17 bbls). 4D fdr # 4 load dropped 10A (306 -294) 4D fdr # 6 load dropped 64A (149 - 85 ) 07:07 Checked & found, Recl. 4D-204 (4D fdr #2) T/SO. Ctr: Display Off. Also found: -@1,@2 b/o fuse & broken FCO for PT. -Broken at load side of Recloser bushing. 08:26 Isolated Recl. 4D-204. 08:30 Manual open 4D OCB fdr #2, then closed by pass switch of Recl. 4D-204. 08:37 Blocked & closed 4D OCB fdr #2, ok. Then released the block. Cause: Suspected animal. | 3056411 | 1 | 5:12 | Morning | Saturday | 2015 | 5
1012 | 2015-05-30 08:05 | 2015-05-30 08:05 | 13.8KV 6D FEEDER #3 | Fair | Unidentified | 81 | 6D OCB fdr #3 T/R 1x. (Prod. loss 12 well, 24 bbls). 6D fdr #1 load dropped 326A (340-14A). (Prod loss 25 well, 53 bbls). 6D fdr #2 load dropped 166A (189-23A). (Prod loss 16 well, 35 bbls). Not checked yet. | 3056411 | 1 | 8:05 | Morning | Saturday | 2015 | 5
1013 | 2015-05-30 08:05 | 2015-04-06 08:05 | 13.8KV 6D FEEDER #3 | Fair | Unidentified | 81 | Checked & found, 6D OCB fdr #3 T/R 1x Ctr: 211-212 R/F: 51@2. Patrolled the line, but found nothing. Cause: Unidentified. | 3056411 | 1 | 8:05 | Morning | Saturday | 2015 | 5
1014 | 2015-05-30 17:05 | 2015-05-30 17:05 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 0 | So.Balam fdr #1 load dropped 16A (93-77A). (So.Balam GFPC in block position) Ground fault alarm on So.Balam fdr #1. Not Checked yet. | 3056406 | 1 | 17:05 | Afternoon | Saturday | 2015 | 5
1015 | 2015-05-30 17:05 | 2015-05-31 17:05 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 16Z-57 (So.Balam fdr #4) T/R 1x Ctr: 77-78. Patrolled the line, but found nothing. Cause: Unidentified. | 3056406 | 1 | 17:05 | Afternoon | Saturday | 2015 | 5
1016 | 2015-05-31 10:59 | 2015-05-31 10:59 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Animal | 0 | 10:59 It was reported no power for WIP at Ampuh GS. (So.Bekasap fdr #1) 11:15 Checked & found, Recloser (for 2.5Mva Tx) at Ampuh-GS. T/O. Ctr: 28-29. 11:53 Then Re-Closed Recloser above, to energize the Tx, ok. Cause: Animal. (Monkey) | 3056406 | 1 | 10:59 | Morning | Sunday | 2015 | 5
1017 | 2015-05-31 17:58 | 2015-05-31 17:58 | 13.8KV PEMATANG FEEDER #2 | Fair | Theft | 0 | 17:58 It was reported Vandalism TX at Well Pematang #97, #50 & #17. 20:40 Checked & found, @1,@2,@3 Open FCO for Transformer at wells Above. (300Kva Tx, 150Kva Tx & 300Kva Tx) Found no abnormalities at wells above, then Energized the Tx, OK. Cause: Theft. (Suspected Vandalism) (Prod. loss charge to Scurity) | 3056406 | 1 | 17:58 | Afternoon | Sunday | 2015 | 5
1018 | 2015-05-31 17:58 | 2015-03-06 17:58 | 13.8KV PEMATANG FEEDER #2 | Fair | Theft | 0 | 10:25 It was reported b/o fuse for Tx at well Pematang #97. (Pematang fdr #1) 14:45 Replaced @3 b/0 7.8SF fuse for 300Kva Tx with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3056406 | 1 | 17:58 | Afternoon | Sunday | 2015 | 5
1019 | 2015-01-06 06:21 | 2015-01-06 06:21 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 61 | Minas ACB fdr #1 T/R 1x Ctr: 46-47 R/F: 51N. Not patrolled yet. | 3070754 | 1 | 6:21 | Morning | Tuesday | 2015 | 1
1020 | 2015-01-06 06:21 | 2015-04-06 07:21 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 61 | Patrolled the line, but found nothing. Cause: Unidentified. | 3070754 | 1 | 6:21 | Morning | Tuesday | 2015 | 1
1021 | 2015-01-06 06:58 | 2015-01-06 06:58 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Animal | 0 | C.Duri fdr #1 Load dropped 43A (223-180A). Not checked yet. | 3070752 | 1 | 6:58 | Morning | Tuesday | 2015 | 1
1022 | 2015-01-06 06:58 | 2015-04-06 17:10 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Animal | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 5x Ctr: 183-188. Patrolled the line & found, a Dead Monkey under Pole #40AV-02. Cause: Animal. (Monkey) Also found, Recl. 40AW-17 (C.Duri fdr #1) T/R 1x Ctr: 566-567. Patrolled the line & found, @3 F/O Dead end Insulator o/p #40AW-16. Cause: Lightning. | 3070752 | 1 | 6:58 | Morning | Tuesday | 2015 | 1
1023 | 2015-01-06 15:32 | 2015-01-06 15:32 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 3 | Bangko fdr #1 load dropped 21A (257-236A). Bangko GFPC T/R 1x. Not checked yet. | 3070752 | 1 | 15:32 | Afternoon | Tuesday | 2015 | 1
1024 | 2015-01-06 15:32 | 2015-02-06 15:00 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 3 | Checked & found, Bangko GFPC T/R 1x Ctr: 461-462 R/F: 50N. Patrolled Bangko fdr #1 line & found, b/o fuse for 100Kva Tx at Well Bangko #73. Cause: Lightning. | 3070752 | 1 | 15:32 | Afternoon | Tuesday | 2015 | 1
1025 | 2015-01-06 17:00 | 2015-01-06 17:00 | 13.8KV BANGKO FEEDER #1 | Fair | Switchboard Problem | 0 | 17:00 It was reported B/O fuse for Tx at Well BKO #73. (BKO fdr #1) 21:22 Checked & found, @3 b/o 2.1SF fuse for 100Kva Tx at Well BKO #73. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Switchboard problem. | 3070752 | 1 | 17:00 | Afternoon | Tuesday | 2015 | 1
1026 | 2015-01-06 17:15 | 2015-01-06 17:15 | 13.8KV BEKASAP FEEDER #3 | Fair | Transformer Failure | 38 | It was reported Well Jambon #01 was off. Checked & found, @1, @3 b/o 7.8SF fuses for 300Kva Tx at Well Jambon #01. Performed TTR, Megger test & found, Zero Megger, & Sudden pressure appears. Cause: Transformer failure. (It would be replaced tomorrow) | 3070752 | 1 | 17:15 | Afternoon | Tuesday | 2015 | 1
1027 | 2015-01-06 17:15 | 2015-03-06 10:00 | 13.8KV BEKASAP FEEDER #3 | Fair | Transformer Failure | 38 | Replaced 300Kva Tx failure with the same size at Well Jambon #01. Cause: Tx failure. | 3070752 | 1 | 17:15 | Afternoon | Tuesday | 2015 | 1
1028 | 2015-01-06 21:39 | 2015-01-06 21:39 | CENTRAL DURI POWER PLANT |  |  | - | CGT #4 T/O. By Alarm: Distillate fuel Low Pressure Trip. Checked & found, failed Auto Transfer to Distilate fuel. (The alarm Gas pressure Low, it is not real conditions) Then blocked the Signal Relays of Distilate Low pressure Trip. (Not allowed to Run by Dist. fuel) Cause: Distillate fuel Low Press Trip. | 123 | 1 | 21:39 | Night | Tuesday | 2015 | 1
1029 | 2015-01-06 22:08 | 2015-01-06 22:08 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Planned Maintenance | 0 | 22:08 It was reported any spark o/p #03-06-08. (C.Duri fdr #5) 23:20 Checked & found, Tx Oil leaks at Socondary bushing of 112.5Kva Tx o/p #03-06-08. (It is intermittent spark at the bushing) 24:00 Switched Off the Main breaker, for Tx Replacing. (Wells #4R-36A, 4R-36B, 4R-46B were off). Cause: Maintenance Job. | 123 | 1 | 22:08 | Night | Tuesday | 2015 | 1
1030 | 2015-01-06 22:08 | 2015-02-06 10:08 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Planned Maintenance | 0 | Repaired 112.5Kva Tx, then energized the Tx o/p #03-06-08. Cause: Maintenance Job. | 123 | 1 | 22:08 | Night | Tuesday | 2015 | 1
1031 | 2015-02-06 01:45 | 2015-02-06 01:45 | CENTRAL DURI POWER PLANT |  |  | - | 01:45 S/U CGT #4, then On Line at 02:02. After Blocked the Signal Relays of Distilate Low press. Trip. (Its not allowed to Run by Distilate fuel) Cause: Distillate fuel Low Press Trip. | 123 | 1 | 1:45 | Night | Friday | 2015 | 2
1032 | 2015-02-06 09:30 | 2015-02-06 09:30 | 13.8KV 6D FEEDER #2 | Fair | Unidentified | 88 | 09:30 It was reported no power at downstream of 6D fdr #2 & 6D fdr #3. (the RTU failed since 09:05, due to IT communication problem). 19:45 Checked & found, 6D OCB fdr #2 T/R 1x Ctr: 225-226 R/F: 51@2,@3. Not patrolled yet. | 3070754 | 1 | 9:30 | Morning | Friday | 2015 | 2
1033 | 2015-02-06 09:30 | 2015-04-06 17:30 | 13.8KV 6D FEEDER #2 | Fair | Unidentified | 88 | Patrolled the line, but found nothing. Cause: Unidentified. | 3070754 | 1 | 9:30 | Morning | Friday | 2015 | 2
1034 | 2015-02-06 11:52 | 2015-02-06 11:52 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 31 | Pematang OCB fdr #1 T/R 1x. Not checked yet. | 3070752 | 1 | 11:52 | Morning | Friday | 2015 | 2
1035 | 2015-02-06 11:52 | 2015-03-06 15:52 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 31 | Checked & found, Pematang OCb fdr #1 T/R 1x Ctr: 111-112 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3070752 | 1 | 11:52 | Morning | Friday | 2015 | 2
1036 | 2015-02-06 12:14 | 2015-02-06 12:14 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 120 | 12:14 Libo OCB fdr #2 T/LO. 12:45 Checked & found, Libo OCB fdr #2 T/LO. Ctr: 392-397 R/F: 51N. Patrolled the line, but found nothing. 13:05 Blocked & closed Libo OCB fdr #2, but Tripped again. Ctr: 397-398. 16:35 Patrolled the line & found, @1,@3 broken Pin Insulators o/p #23BV-02. 18:25 Replaced broken insulators o/p #23BV-02 above. 18:48 Blocked & closed Libo OCB fdr #2, ok. Then released the blocked. Cause: Lightning. | 3070752 | 1 | 12:14 | Afternoon | Friday | 2015 | 2
1037 | 2015-02-06 13:36 | 2015-02-06 13:36 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 0 | Bangko fdr #4 Load dropped 70A (200-130A). Bangko GFPC T/R 1x. Not checked yet. | 3070752 | 1 | 13:36 | Afternoon | Friday | 2015 | 2
1038 | 2015-02-06 13:36 | 2015-03-06 12:12 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 62-63. Also found, Bangko GFPC T/R 1x Ctr: 462-463. Patrolled the line & found, @1 broken Pin insulator on TOP of Well Benar #35. Cause: Pin insulator. | 3070752 | 1 | 13:36 | Afternoon | Friday | 2015 | 2
1039 | 2015-02-06 15:15 | 2015-02-06 15:15 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 357 | 15:15 It was reported no power at Well #4B-61. (4B fdr #1) (RTU failed since 09:05, due to IT problem) 15:37 Checked & found, 4B OCB fdr #1 T/R 2x Ctr: 253-254 R/F: 50@1 & 51@2,@3. 16:05 Also found, Recl. 4B-148 (4B fdr #1) T/SO. Ctr: 23-24. (The Recloser is indirect power source / Due to it is transfered to 4B fdr #1 from 4B fdr #6) Then patrolled the line, but found nothing. 18:15 Opened LBS #4B-29. 18:26 Closed bypass Switch of Recl. 4B-148. 18:30 Re-Closed LBS #4B-29. Cause: Suspected by Lightning. | 3070754 | 1 | 15:15 | Afternoon | Friday | 2015 | 2
1040 | 2015-03-06 10:45 | 2015-03-06 10:45 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 10:25 It was reported b/o fuse for Tx at well Pematang #97. (Pematang fdr #1) 14:45 Replaced @3 b/0 7.8SF fuse for 300Kva Tx with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3070754 | 1 | 10:45 | Morning | Friday | 2015 | 3
1041 | 2015-03-06 14:30 | 2015-03-06 14:30 | MINAS POWER PLANT |  |  | - | 14:30 S/U MGT #1, then On Line at 15:00. (Running on test after Vibration Balancing) 15:18 Off Line MGT #1, then S/D the Unit for S/B. (Prior to fixing the Vibration Balancing) | 123 | 1 | 14:30 | Afternoon | Friday | 2015 | 3
1042 | 2015-03-06 19:19 | 2015-03-06 19:19 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 8 | 19:19 It was reported b/o fuse for Tx at Well Bangko #133. 21:20 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Bangko #133. Replaced the b/o fuse with same size, then energized the Tx. Cause: Unidentified (fuse). | 3070752 | 1 | 19:19 | Night | Friday | 2015 | 3
1043 | 2015-04-06 08:00 | 2015-04-06 08:00 | 13.8KV 3D FEEDER #4 | Fair | Unidentified (Fuse) | 78 | 08:00 It was reported b/o fuse for Tx at Well #1D-74. (3D fdr #4) 15:00 Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well #1D-74. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3070754 | 1 | 8:00 | Morning | Monday | 2015 | 4
1044 | 2015-04-06 10:05 | 2015-04-06 10:05 | MINAS POWER PLANT |  |  | - | 10:05 S/U MGT #1, then online the unit for balancing job. 11:00 Offline MGT #1, then S/D the unit for S/B. | 123 | 1 | 10:05 | Morning | Monday | 2015 | 4
1045 | 2015-04-06 12:03 | 2015-04-06 12:03 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Minas ACB #21 (44Kv Minas-Rumbai line) T/R 1x Ctr: 67-68 R/F: 51G@1,@2. Not patrolled yet. | 3070754 | 1 | 12:03 | Afternoon | Monday | 2015 | 4
1046 | 2015-04-06 12:03 | 2015-06-06 15:03 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Patrolled 44KV Minas-Rumbai line, but found nothing. Cause: Suspected by Lightning. | 3070754 | 1 | 12:03 | Afternoon | Monday | 2015 | 4
1047 | 2015-04-06 12:19 | 2015-04-06 12:19 | MINAS POWER PLANT | Rain | Under investigation | 0 | 12:19 MGT #5 Open Generator Breaker, By Alarm: Generator Breaker trip. 12:29 Re-On Line MGT #5. Cause: Under Investigation. | 3070754 | 1 | 12:19 | Afternoon | Monday | 2015 | 4
1048 | 2015-05-06 16:38 | 2015-05-06 16:38 | 13.8KV MINAS FEEDER #6 | Fair | Animal | 54 | Minas fdr #6 Load dropped 106A (206-100A). Not checked yet. | 3070754 | 1 | 16:38 | Afternoon | Wednesday | 2015 | 5
1049 | 2015-05-06 16:38 | 2015-09-06 08:38 | 13.8KV MINAS FEEDER #6 | Fair | Animal | 54 | Checked & found, Recl. 6E-23A (Minas fdr #6) T/R 4x Ctr: 03-07. Patrolled the line & found, a Dead Monkey touching source side Recloser bushing o/p #6E-23A. (Then tookdown its Monkey by opening the Recl. 6E-23E) Cause: Animal. (Monkey) (See report 08 June 2015 at 14:35) | 3070754 | 1 | 16:38 | Afternoon | Wednesday | 2015 | 5
1050 | 2015-05-06 18:30 | 2015-05-06 18:30 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 62 | 18:30 5B fdr #4 Load dropped 220A (242-22A). 21:52 It was reported no power at some wells Downstream of 5B fdr #4. 23:03 checked & found, Recl. 4B-73 (5B fdr #4) T/LO. Ctr: 43-47. 23:53 Patrolled the line, but found nothing. 23:54 Blocked & closed Recl. 4B-73, Ok. Then released the block. Cause: Suspected by Lightning. | 3070354 | 1 | 18:30 | Afternoon | Wednesday | 2015 | 5
1051 | 2015-05-06 18:35 | 2015-05-06 18:35 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 9 | 18:35 3D OCB fdr #2 T/R 1x. 18:39 3D OCB fdr #2 T/R 1x again. Not checked yet. | 3070754 | 1 | 18:35 | Afternoon | Wednesday | 2015 | 5
1052 | 2015-05-06 18:35 | 2015-07-06 16:35 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 9 | Checked & found, 3D OCB fdr #2 T/R 2x Ctr: 485-487 R/F: 51@1,@2,@3. Patrolled the line & found, @2 broken L/A o/p #3E-42. Cause: Lightning. | 3070754 | 1 | 18:35 | Afternoon | Wednesday | 2015 | 5
1053 | 2015-05-06 18:36 | 2015-05-06 18:36 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 98 | 18:36 5B OCB fdr #3 T/R 2x. 5B fdr #2 Load dropped 162A (182-20A). 5B fdr #6 Load dropped 123A (128-5A). 19:05 5B OCB fdr #3 T/R 1x again. Not checked yet. | 3070754 | 1 | 18:36 | Afternoon | Wednesday | 2015 | 5
1054 | 2015-05-06 18:36 | 2015-11-06 14:36 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 98 | Checked & found, 5B OCB fdr #3 T/R 2x Ctr: 351-353 R/F: 51@1,@3. Patrolled the line & found: -@3 Broken Dead end Insulator o/p #NN. (near Well #4D-52N) -@1 Broken Dead end Insulator o/p #4C-62. Cause: Lightning. | 3070754 | 1 | 18:36 | Afternoon | Wednesday | 2015 | 5
1055 | 2015-05-06 18:39 | 2015-05-06 18:39 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 23 | 18:39 3D OCB fdr #3 T/R 1x. 18:58 3D OCB fdr #3 T/R 1x again. Not checked yet. | 3070754 | 1 | 18:39 | Afternoon | Wednesday | 2015 | 5
1056 | 2015-05-06 18:39 | 2015-07-06 16:39 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 23 | Checked & found, 3D OCB fdr #3 T/R 4x Ctr: 575-579 R/F: 51@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3070754 | 1 | 18:39 | Afternoon | Wednesday | 2015 | 5
1057 | 2015-05-06 18:45 | 2015-05-06 18:45 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 8 | 4D OCB fdr #5 T/R 1x. 4D fdr #4 load dropped 266A (313-67A). 4D fdr #6 load dropped 150A (151-1A). T/O WIP at GS-5. Not checked yet. | 3070754 | 1 | 18:45 | Afternoon | Wednesday | 2015 | 5
1058 | 2015-05-06 18:45 | 2015-07-06 16:45 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 8 | Checked & found, 4D OCB fdr #5 T/R 1x Ctr: 251-252 R/F: 51N(@1,@2) Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3070754 | 1 | 18:45 | Afternoon | Wednesday | 2015 | 5
1059 | 2015-05-06 18:46 | 2015-05-06 18:46 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 55 | 4D OCB fdr #3 T/R 1x. 4D fdr #1 load dropped 138A (269-131A). 4D fdr #2 load dropped 137A (171-34A). Not checked yet. | 3070754 | 1 | 18:46 | Afternoon | Wednesday | 2015 | 5
1060 | 2015-05-06 18:46 | 2015-07-06 16:46 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 55 | Checked & found, 4D OCB fdr #3 T/R 1x Ctr: 374-375 R/F: 51N(@2,@3) Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3070754 | 1 | 18:46 | Afternoon | Wednesday | 2015 | 5
1061 | 2015-05-06 19:00 | 2015-05-06 19:00 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 44 | 4B fdr #1 load dropped 185A (269-131A). 4B fdr #2 load dropped 21A (125-4A). 4B fdr #3 load dropped 66A (68-2A). 4B fdr #5 load dropped 72A (192-125A). T/O WIP at GS-6. Not checked yet. | 3070754 | 1 | 19:00 | Night | Wednesday | 2015 | 5
1062 | 2015-05-06 19:00 | 2015-09-06 08:20 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 44 | Checked & found, Recl. 4B-101 (4B fdr #1) T/R 4x Ctr: 50-54. Patrolled the line & found, @1 broken Pin Insulator o/p #4A-09. Cause: Lightning. | 3070754 | 1 | 19:00 | Night | Wednesday | 2015 | 5
1063 | 2015-05-06 20:12 | 2015-05-06 20:12 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Static Wire | 80 | 20:12 5B OCB fdr #1 T/LO. Ctr: 198-202 R/F: 51N(@2). (5B RTU failed at 19:05). 21:28 Patrolled the line & found, broken Static Wire o/p #5C-172, 5C-174 & 5C-175. (Then Isolated broken Static Wire above) 21:32 Blocked & closed 5B OCB fdr #1, Ok. Then released the block. Cause: Static Wire. | 3070754 | 1 | 20:12 | Night | Wednesday | 2015 | 5
1064 | 2015-06-06 08:45 | 2015-06-06 08:45 | 13.8KV CENTRAL DURI FEEDER #9 | Cloudy | Unidentified (Fuse) | 6 | 08:45 It was reported b/o fuse for Tx o/p #04-3-11. (C.Duri fdr #9) 15:45 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx o/p #04-3-11. Replaced b/o above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3070752 | 1 | 8:45 | Morning | Saturday | 2015 | 6
1065 | 2015-06-06 08:46 | 2015-06-06 08:46 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified (Fuse) | 2 | 08:46 It was reported b/o fuse for Tx at Well Kulin #62. (C.Duri fdr #1) Not checked yet. | 3070752 | 1 | 8:46 | Morning | Saturday | 2015 | 6
1066 | 2015-06-06 08:46 | 2015-07-06 11:48 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified (Fuse) | 2 | 11:48 Checked & found, @2 b/o 1.0SF fuse for 45Kva Tx at Well Kulin #62. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3070752 | 1 | 8:46 | Morning | Saturday | 2015 | 6
1067 | 2015-06-06 09:03 | 2015-06-06 09:03 | MINAS POWER PLANT |  |  | - | 09:03 S/U MGT #1, then online the unit at 09:29. (Generator Rotor Balancing test) 09:49 Offline MGT #1, then S/D the unit for S/B. 11:02 S/U MGT #1, then online the unit at 11:19. (Running on test after Generator rotor balancing) |  | 1 | 9:03 | Morning | Saturday | 2015 | 6
1068 | 2015-06-06 12:36 | 2015-06-06 12:36 | MINAS POWER PLANT |  |  | - | 12:36 Offline MGT #3, then S/D the unit for S/B. |  | 1 | 12:36 | Afternoon | Saturday | 2015 | 6
1069 | 2015-06-06 14:38 | 2015-06-06 14:38 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 359 | 14:38 Batang OCB fdr #3 T/O. (In block position for Rig Job) Confirmation with ACS #05 Rig team, no any touching to power lines. 14:45 Manually Closed from DSC but failed. 17:10 Checked & found, Batang OCB fdr #3 T/O. Ctr: 268-269 R/F: 50@2,@3. 17:21 Blocked & Closed Batang OCB fdr #3, Ok. Then released the block. (form local) Not Patrolled yet. | 3070752 | 1 | 14:38 | Afternoon | Saturday | 2015 | 6
1070 | 2015-06-06 14:38 | 2015-09-06 09:38 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 359 | Checked & found, Batang OCB fdr #3 Ctr: 268-270 R/F: 50@2,@3. Patrolled Batang fdr #3 line, but found nothing. Cause: Suspected by Lightning. | 3070752 | 1 | 14:38 | Afternoon | Saturday | 2015 | 6
1071 | 2015-06-06 15:33 | 2015-06-06 15:33 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 30 | Pematang OCB fdr #1 T/R 1x. Pematang fdr #2 load dropped 61A (66-5A). Not checked yet. | 3070752 | 1 | 15:33 | Afternoon | Saturday | 2015 | 6
1072 | 2015-06-06 15:33 | 2015-11-06 15:33 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 30 | Checked & found, Pematang OCB fdr #1 T/R 1x Counter & Relay Flag are not checked yet. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3070752 | 1 | 15:33 | Afternoon | Saturday | 2015 | 6
1073 | 2015-06-06 15:33 | 2015-01-06 15:33 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Lightning | 44 | Checked & found, Petani OCB fdr #1 T/R 1x Counter & Relay Flag are not checked yet. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3070752 | 1 | 15:33 | Afternoon | Saturday | 2015 | 6
1074 | 2015-06-06 15:33 | 2015-06-06 15:33 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Lightning | 44 | Petani OCB fdr #1 T/R 1x. Petani fdr #2 load dropped 43A (65-22A). Not checked yet. | 3070752 | 1 | 15:33 | Afternoon | Saturday | 2015 | 6
1075 | 2015-06-06 15:38 | 2015-06-06 15:38 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Powerline - Conductor | 261 | 15:38 Pematang OCB fdr #2 T/LO. 15:50 It was reported broken conductor o/p #34BC-66. (line toward Well Pematang #15) 17:30 Checked & found, Pematang OCB fdr #2 T/LO. Ctr: 438-442 R/F: 51N & 51@1. Patrolled the line & found, @1 broken Pin insulator & conductor o/p #34BC-66. 18:00 Isolated broken jumper, by cutting jumper o/p #34BC-97. (7 Wells are still off: PMT #89,#74,#32,#81,#65,#47,#38) 18:27 Blocked & Closed, Pematang OCB fdr #2, Ok. Then released the block. Cause: Broken Conductor. (Prod. loss: 378 bbls / 32 wells) | 3070752 | 1 | 15:38 | Afternoon | Saturday | 2015 | 6
1076 | 2015-06-06 15:38 | 2015-07-06 13:00 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Powerline - Conductor | 261 | 13:00 Blocked Pematang OCB fdr #2. 13:15 Replaced @1 Broken Pin insulator & Repair broken Conductor o/p #34BC-66. 14:00 Energized All Transformer & S/U Wells PMT #89, #74, #32, #81, #65, #47, #38. (Prod. loss: 239 bbls / 7 wells). & yesterday (Prod. loss: 378 bbls / 32 wells) Grand Total Prod. loss = 617 Bbls / 39 Wells. | 3070752 | 1 | 15:38 | Afternoon | Saturday | 2015 | 6
1077 | 2015-06-06 15:53 | 2015-06-06 15:53 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Unidentified (Fuse) | 0 | 15:53 It was reported b/o fuse for Tx o/p #09-M1-13. (C.Duri fdr #16) Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #09-M1-13. 16:14 Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (fuse). | 3070752 | 1 | 15:53 | Afternoon | Saturday | 2015 | 6
1078 | 2015-06-06 18:03 | 2015-06-06 18:03 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #2 | Rain and Lightning | Lightning | 39 | MSU-1 VCB fdr #2 (8C fdr #6) T/R 1x. MSU-1 VCB fdr #1 load dropped 167A (167-0A). T/O WIP at GS-2. Not checked yet. | 3070754 | 1 | 18:03 | Afternoon | Saturday | 2015 | 6
1079 | 2015-06-06 18:03 | 2015-11-06 07:21 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #2 | Rain and Lightning | Lightning | 39 | Checked & found, MSU-1 VCB fdr #2 (8C fdr #6) T/R 1x Ctr: 236-237 R/F: Did not appear. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3070754 | 1 | 18:03 | Afternoon | Saturday | 2015 | 6
1080 | 2015-07-06 06:57 | 2015-07-06 06:57 | 13.8KV DURI FIELD FEEDER #1 | Fair | Animal | 0 | 06:57 It was reported b/o fuse for Tx at SS-5S Block station Area-1. (DF fdr #1) 10:56 Checked & found, @1, @2 b/o 100K fuses for 1000Kva Tx at SS-5S Area-1. Replaced the b/o fuse above with the same size, then energized the Tx. Cause: Animal (monkey). | 3070752 | 1 | 6:57 | Morning | Monday | 2015 | 7
1081 | 2015-07-06 09:35 | 2015-07-06 09:35 | 13.8KV PUNGUT FEEDER #1 | Fair | Transformer Failure | 54 | 09:35 It was reported b/o fuse for Tx at Well Pungut #23. (Pungut fdr #1) 13:30 Checked & found, @1 b/o 2.1SF fuse & holder for 100Kva Tx at Well Pungut #23. Performed TTR & Megger test, found unbalance Tx. Cause: Transformer failure. (Will be replace tomorrow). | 3070752 | 1 | 9:35 | Morning | Monday | 2015 | 7
1082 | 2015-07-06 09:35 | 2015-08-06 17:35 | 13.8KV PUNGUT FEEDER #1 | Fair | Transformer Failure | 54 | Replaced 100Kva Tx failure with the same size & energized the Tx at Well Pungut #23. Cause: Transformer failure. | 3070752 | 1 | 9:35 | Morning | Monday | 2015 | 7
1083 | 2015-07-06 14:45 | 2015-07-06 14:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Low mega-ohm reading | 17 | 14:45 It was reported b/o fuse for Tx at Well Kulin #66. (C.Duri fdr #1) 17:15 Checked & found, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx at Well Kulin #66. Performed TTR & Megger test the TX, found Low Mega-ohm reading Tx. Cause: Low Mega-ohm Reading Tx. (Will be replace tomorrow). | 3070752 | 1 | 14:45 | Afternoon | Monday | 2015 | 7
1084 | 2015-07-06 14:45 | 2015-10-06 17:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Low mega-ohm reading | 17 | 17:30 Replaced 112.5Kva Tx low megger reading with 75Kva Tx at well Kulim#66. Then energized the Tx. Cause: Low megger reading Tx. | 3070752 | 1 | 14:45 | Afternoon | Monday | 2015 | 7
1085 | 2015-07-06 21:29 | 2015-07-06 21:29 | 13.8KV MINAS FEEDER #6 | Rain | Animal | 52 | 21:29 Minas fdr #6 load dropped 174A ( 218-44A). 22:11 Checked & found, Recl. 6E-23A (Minas fdr #6) T/R 4x Ctr: 03-07. Not patrolled yet. | 3070754 | 1 | 21:29 | Night | Monday | 2015 | 7
1086 | 2015-07-06 21:29 | 2015-09-06 07:29 | 13.8KV MINAS FEEDER #6 | Rain | Animal | 52 | Patrolled the line & found, a Dead Monkey touching source side Recloser bushing o/p #6E-23A. (Then opened Recl. 6E-23A, to taking down its Monkey) Cause: Animal. (Monkey) (See report 08 June 2015 at 14:35) | 3070754 | 1 | 21:29 | Night | Monday | 2015 | 7
1087 | 2015-07-06 23:01 | 2015-07-06 23:01 | 13.8KV PEMATANG FEEDER #1 | Fair | Powerline - Hot Line Clamp | 10 | It was reported spark at HLC on TP of Well Pematang #52. (Will be checked at the morning) | 3070752 | 1 | 23:01 | Night | Monday | 2015 | 7
1088 | 2015-07-06 23:01 | 2015-08-06 15:30 | 13.8KV PEMATANG FEEDER #1 | Fair | Powerline - Hot Line Clamp | 10 | Checked & found, spark at HLC on TP of Well Pematang #52. (Then Shut off the Transformer, to anticipate broken jumper on TP above) Cause: Hot line clamp. | 3070752 | 1 | 23:01 | Night | Monday | 2015 | 7
1089 | 2015-07-06 23:01 | 2015-09-06 11:15 | 13.8KV PEMATANG FEEDER #1 | Fair | Powerline - Hot Line Clamp | 10 | 11:15 Repaired hot spot on terminal pole of well Pematang#52 12:00 Energized the TX. Cause:Loss connection at Hot line clamp. | 3070752 | 1 | 23:01 | Night | Monday | 2015 | 7
1090 | 2015-08-06 14:35 | 2015-08-06 14:35 | 13.8KV MINAS FEEDER #6 | Fair | Animal | 36 | 14:35 Manually Opened Recl. 6E-23A. (Minas fdr #6) to Remove a Dead Monkey on @2 bushing Recloser above. 14:44 Closed Recl. 6E-23A. (Minas fdr #6) (After removing the a Dead Monkey above) Cause: Animal. (Monkey) (See report 05 June 2015 at 16:34 & 07 June 2015 at 21:29) | 3070754 | 1 | 14:35 | Afternoon | Thursday | 2015 | 8
1091 | 2015-08-06 15:35 | 2015-08-06 15:35 | 13.8KV 6D FEEDER #2 | Fair | Transformer Failure | 49 | 15:35 It was reported b/o fuse for Tx at Well #6B-69. (6D fdr #2) 17:50 Checked & found @1 b/o 7.0SF fuse for 225Kva Tx at Well #6B-69. Tested TTR & Megger the TX above, found Low reading. Cause: Transformer failure. Would be Replaced tomorrow. | 3070754 | 1 | 15:35 | Afternoon | Thursday | 2015 | 8
1092 | 2015-08-06 15:35 | 2015-09-06 15:37 | 13.8KV 6D FEEDER #2 | Fair | Transformer Failure | 49 | Replaced Transformer Low megger reading with the same size & energized the Tx. Cause: Transformer failure. | 3070754 | 1 | 15:35 | Afternoon | Thursday | 2015 | 8
1093 | 2015-09-06 13:41 | 2015-09-06 13:41 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 21 | 13:41 Ketigul VCB fdr #2 T/O. (in block position for Rig ACS #01 activity at Well Pagar #32) 13:45 Get verification from Rig ACS #01. (Rig had moved to Well Tilan #11 yesterday) 13:50 Blocked & closed Ketigul VCB fdr #2, Ok. Then released the blocked. Not checked & patrolled yet. | 3070752 | 1 | 13:41 | Afternoon | Sunday | 2015 | 9
1094 | 2015-09-06 14:30 | 2015-09-06 14:30 | DURI POWER PLANT |  |  | - | 14:30 S/U DGT #7, then On line at 15:00. (S/D NDC-CT #2 for removing Blanking Plate) | 123 | 1 | 14:30 | Afternoon | Sunday | 2015 | 9
1095 | 2015-09-06 15:09 | 2015-09-06 15:09 | MINAS POWER PLANT |  |  | - | 15:09 S/U MGT #4, then On Line at 16:22. (S/D NDC-CT #2 for removing Blanking Plate) | 123 | 1 | 15:09 | Afternoon | Sunday | 2015 | 9
1096 | 2015-09-06 18:18 | 2015-09-06 18:18 | MINAS POWER PLANT |  |  | - | 18:18 S/U MGT #3, then On line at 18:29. (S/D NDC-CT #2 for removing Blanking Plate) 18:35 Open ACB #25. (Tie Breaker) | 123 | 1 | 18:18 | Afternoon | Sunday | 2015 | 9
1097 | 2015-09-06 19:51 | 2015-09-06 19:51 | NORTH DURI POWER PLANT |  |  | - | 19:51 Off line NDC-CT #2, then S/D the unit for S/B. (Prior to removing Blanking Plate) 10 June 2015. 21:45 S/U NDC-CT #2, then Online the Unit at 22:33. (After removing Blanking plate for HRSG #2) |  | 1 | 19:51 | Night | Sunday | 2015 | 9
1098 | 2015-09-06 20:08 | 2015-09-06 20:08 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 20:08 It was reported b/o fuse for Tx o/p #05-P3-08. (C.Duri fdr #14) 22:00 Checked & found, @1,@2 b/o 14.0SF fuses for 500Kva Tx o/p #05-P3-08. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3070752 | 1 | 20:08 | Night | Sunday | 2015 | 9
1099 | 2015-10-06 06:00 | 2015-10-06 06:00 | 13.8KV PETANI FEEDER #1 | Fair | Planned Maintenance | 0 | 06:00 Manually opened Rokan VCB fdr #2. 06:05 Manually opened Petani OCB fdr #2. 06:20 Manually opened Petani OCB fdr #1. (Production Team (Petani GS) performed Tie in Gas outlet gas boot) 23:26 Manually closed Petani OCB fdr #1. 00:15 Manually closed Petani OCB fdr #2. 00:19 Manually closed Rokan VCB fdr #2. (After finishing to Tie in Gas outlet gas boot at Petani GS) Cause: Maintenance Job. (No production loss charge to PGT) | 123 | 1 | 6:00 | Morning | Tuesday | 2015 | 10
1100 | 2015-10-06 08:07 | 2015-10-06 08:07 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 13 | Sintong OCB fdr #2 T/R 3x. Sintong fdr #1 dropped 128A (196-68A). (Sintong GFPC did not trip) Not checked yet. | 3070752 | 1 | 8:07 | Morning | Tuesday | 2015 | 10
1101 | 2015-10-06 08:07 | 2015-12-06 08:35 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 13 | Checked & found, Sintong OCB fdr #2 T/R 3x Ctr: 388-391 R/F: 51@1,@2. Patrolled the line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 8:07 | Morning | Tuesday | 2015 | 10
1102 | 2015-10-06 08:08 | 2015-10-06 08:08 | 13.8KV MENGGALA FEEDER #2 | Fair | Unidentified | 31 | Mengala fdr #2 dropped 37A (99-62A). Not checked yet. | 3070752 | 1 | 8:08 | Morning | Tuesday | 2015 | 10
1103 | 2015-10-06 08:08 | 2015-12-06 08:08 | 13.8KV MENGGALA FEEDER #2 | Fair | Unidentified | 31 | Checked all Recloser at downstream, but found normal. (Counter did not operate) Patrolled the line, but found nothing. Cause: Unidetified. | 3070752 | 1 | 8:08 | Morning | Tuesday | 2015 | 10
1104 | 2015-10-06 21:45 | 2015-10-06 21:45 | NORTH DURI POWER PLANT |  |  | - | 21:45 S/U NDC-CT #2, then Online the Unit at 22:33. (After removing Blanking plate for HRSG #2) |  | 1 | 21:45 | Night | Tuesday | 2015 | 10
1105 | 2015-11-06 06:26 | 2015-11-06 06:26 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 06:26 It was reported b/o fuse for Tx o/p #11-H7-11. 10:45 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #11-H7-11. Replaced the b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3070752 | 1 | 6:26 | Morning | Friday | 2015 | 11
1106 | 2015-11-06 10:03 | 2015-11-06 10:03 | DURI POWER PLANT |  |  | - | 10:03 Offline DGT #7, then S/D the unit at 10:04 for S/B. | 123 | 1 | 10:03 | Morning | Friday | 2015 | 11
1107 | 2015-11-06 10:10 | 2015-11-06 10:10 | MINAS POWER PLANT |  |  | - | 10:10 Offline MGT #2, then S/D the unit for S/B. | 123 | 1 | 10:10 | Morning | Friday | 2015 | 11
1108 | 2015-11-06 10:28 | 2015-11-06 10:28 | 13.8KV DARLING VCB FEEDER #8 | Fair | Dead End Insulator | 0 | Darling VCB fdr #8 T/R 1x. Darling GFPC T/R 1x. (Fault alarm on Darling fdr #8) Not checked yet. | 3070752 | 1 | 10:28 | Morning | Friday | 2015 | 11
1109 | 2015-11-06 10:28 | 2015-12-06 14:28 | 13.8KV DARLING VCB FEEDER #8 | Fair | Dead End Insulator | 0 | Checked & found, Darling VCB fdr #8 T/R 1x Ctr: 386-387 R/F: 51N. Patrolled the line & found, @1 F/O Dead end Insulator o/p #05-N3-18. Cause: Dead end Insulator. | 3070752 | 1 | 10:28 | Morning | Friday | 2015 | 11
1110 | 2015-11-06 10:37 | 2015-11-06 10:37 | MINAS POWER PLANT |  |  | - | 10:37 Offline MGT #5, then S/D the unit for S/B. | 123 | 1 | 10:37 | Morning | Friday | 2015 | 11
1111 | 2015-11-06 14:41 | 2015-11-06 14:41 | CENTRAL DURI POWER PLANT |  |  | - | 14:41 Off line, CGT #2, then S/d the Unit for Repairing 88FD-01. (Appear alarm "Bearing Header Temprature High") Frequency system dropped to 59.86Hz. (No load shedding) Cause: 88FD-01 problem. 14:43 Closed ACB #19. (Tie Breaker) 23:40 S/U CGT #2, then on line the Unit at 01:15. 12-June-2015. 00:00 Open ACB #19. (Tie Breaker) |  | 1 | 14:41 | Afternoon | Friday | 2015 | 11
1112 | 2015-11-06 16:56 | 2015-11-06 16:56 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 30 | Sintong fdr #1 dropped 94A (193-99A). Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #2) Not checked yet. | 3070752 | 1 | 16:56 | Afternoon | Friday | 2015 | 11
1113 | 2015-11-06 16:56 | 2015-12-06 16:00 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 30 | Checked & found, Recl. 19AN-04 (Sintong fdr #1) T/R 1x Ctr: 305-306. Also found, Sintong GFPC T/R 3x Ctr: 768-771. Patrolled the line & found, a Dead Monkey on Capacitor Bank o/p #NN. (near Well No.Menggala #12) Cause: Animal. (Monkey) | 3070752 | 1 | 16:56 | Afternoon | Friday | 2015 | 11
1114 | 2015-11-06 16:59 | 2015-11-06 16:59 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 20 | Batang OCB fdr #2 T/R 1x. (Batang RTU failed at that time) Not checked yet. | 3070752 | 1 | 16:59 | Afternoon | Friday | 2015 | 11
1115 | 2015-11-06 16:59 | 2015-12-06 15:59 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 20 | Checked & found, Batang OCB fdr #2 T/R 1x Ctr: 96-97 R/F: 51N(@1). Patrolled the line & found, @1 broken Pin Insulator o/p #38AI-09. Cause: Lightning. | 3070752 | 1 | 16:59 | Afternoon | Friday | 2015 | 11
1116 | 2015-11-06 17:16 | 2015-11-06 17:16 | 13.8KV BANGKO FEEDER #4 | Cloudy | Lightning | 22 | Bangko fdr #4 load dropped 65A (202-137A). Bangko GFPC T/R 1x. (Ground fault alarm on Bangko fdr #4) Not checked yet. | 3070752 | 1 | 17:16 | Afternoon | Friday | 2015 | 11
1117 | 2015-11-06 17:16 | 2015-12-06 15:16 | 13.8KV BANGKO FEEDER #4 | Cloudy | Lightning | 22 | Checked & found, Recl. 29Y-16 (Bangko fdr #4) T/R 1x Ctr: 83-84. Also found, Bangko GFPC T/R 1x Ctr: 463-464 R/F: 51N. Patrolled the line & found, @1 broken L/A on TP of Well Benar #14. Cause: Lightning. Also found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 60-61. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3070752 | 1 | 17:16 | Afternoon | Friday | 2015 | 11
1118 | 2015-12-06 17:54 | 2015-12-06 17:54 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 28 | 6D OCB fdr #5 T/R 1x. 6D fdr #4 load dropped 138A (202-64A). T/O WIP at GS-4. 6D fdr #6 load dropped 240A (247-7A). Not checked yet. | 3070754 | 1 | 17:54 | Afternoon | Sunday | 2015 | 12
1119 | 2015-12-06 17:54 | 13/06/2015 17:00 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 28 | Checked & found, 6D OCB fdr #5 T/R 1x Ctr: 720-721 R/F: 51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3070754 | 1 | 17:54 | Afternoon | Sunday | 2015 | 12
1120 | 2015-06-13 10:37 | 2015-06-13 10:37 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 32 | Sintong fdr #1 load dropped 135A (224-89A). (Sintong GFPC did not operate) Not checked yet. | 3070752 | 1 | 10:37 | Morning | Saturday | 2015 | 6
1121 | 2015-06-13 10:37 | 2015-06-14 15:37 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 32 | Checked & found, Recl. 19AN-04 (Sintong fdr #1) T/R 1x Ctr: 305-306. Patrolled the line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 10:37 | Morning | Saturday | 2015 | 6
1122 | 2015-06-13 16:47 | 2015-06-13 16:47 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified | 13 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3070752 | 1 | 16:47 | Afternoon | Saturday | 2015 | 6
1123 | 2015-06-13 16:47 | 2015-06-18 15:47 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified | 13 | Checked & found, Rokan VCB fdr #2 T/R 2x Ctr: 982-984 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 16:47 | Afternoon | Saturday | 2015 | 6
1124 | 2015-06-13 18:41 | 2015-06-13 18:41 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 130 | 18:41 C.Duri ACB fdr #1 T/LO. Ctr: 177-181 R/F: 51@1,@2. 20:35 Patrolled the line, but found nothing. Blocked & closed C.Duri ACB fdr #1, Ok. Then released the block. Cause: Unidentified. | 3070752 | 1 | 18:41 | Afternoon | Saturday | 2015 | 6
1125 | 2015-06-13 22:16 | 2015-06-13 22:16 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 4 | Libo OCB fdr #2 T/R 2x. Not checked yet. | 3070752 | 1 | 22:16 | Night | Saturday | 2015 | 6
1126 | 2015-06-13 22:16 | 2015-06-19 09:58 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 4 | Checked & found, Libo OCB fdr #2 T/R 2x Ctr: 398-400 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected Lightning. | 3070752 | 1 | 22:16 | Night | Saturday | 2015 | 6
1127 | 2015-06-14 10:18 | 2015-06-14 10:18 | 13.8KV NORTH DURI FEEDER #1 | Fair | Others | 0 | 10:18 It was reported open jumper of primary Tx Bushing for 112.5Kva Tx o/p #11-H3-18. (ND fdr #1) 12:39 Checked & found, @1 broken terminal connector of Tx primary bushing for jumper. Then De-energized the Tx, to replaced broken terminal jumper then re-energized the Tx. Cause: Others. (Broken Primary Bushing Terminal) | 3070752 | 1 | 10:18 | Morning | Sunday | 2015 | 6
1128 | 2015-06-14 10:40 | 2015-06-14 10:40 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 9 | 10:40 It was reported that b/o fuse for Tx o/p #08-L5-27. (C.Duri fdr #1) 13:13 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #08-L5-27. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3070752 | 1 | 10:40 | Morning | Sunday | 2015 | 6
1129 | 2015-06-14 15:08 | 2015-06-14 15:08 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Rain and Lightning | Lightning | 0 | 4.16Kv Dumai VCB fdr #5 T/R 1x. Not checked yet. | 3070752 | 1 | 15:08 | Afternoon | Sunday | 2015 | 6
1130 | 2015-06-14 15:08 | 2015-06-16 15:24 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, 4.16KV Dumai VCB fdr #5 T/R 1x Ctr: 267-268 R/F: 50@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3070752 | 1 | 15:08 | Afternoon | Sunday | 2015 | 6
1131 | 2015-06-14 21:49 | 2015-06-14 21:49 | 13.8KV BANGKO FEEDER #1 | Cloudy and Lightning | Lightning | 24 | Bangko fdr #1 dropped 86A (251-167A). Ground fault alarm on Bangko fdr #1 & fdr #4. (Bangko GFPC T/R 1x) Not checked yet. | 3070752 | 1 | 21:49 | Night | Sunday | 2015 | 6
1132 | 2015-06-14 21:49 | 2015-06-17 13:21 | 13.8KV BANGKO FEEDER #1 | Cloudy and Lightning | Lightning | 24 | Checked & found, Recl. 25Z-07 (Bangko fdr #1) T/R 1x Ctr: 62-63. Also found, Bangko GFPC T/R 1x Ctr: 462-463. Patrolled the line & found, @1 flashed over Dead end Insulator o/p #27Y-39. Cause: Lightning. | 3070752 | 1 | 21:49 | Night | Sunday | 2015 | 6
1133 | 2015-06-15 07:52 | 2015-06-15 07:52 | 13.8KV BEKASAP FEEDER #3 | Fair | Theft | 0 | It was reported vandalism of 300Kva Tx at Well Bekasap #93. Cause: Theft. (The Tx is not replaced yet) | 3070752 | 1 | 7:52 | Morning | Monday | 2015 | 6
1134 | 2015-06-15 07:52 | 2015-06-16 12:52 | 13.8KV BEKASAP FEEDER #3 | Fair | Theft | 0 | Replaced 300Kva Tx Vandalism with 225Kva Tx at Well Bekasap #93. Then energized the Tx. Cause: Theft. | 3070752 | 1 | 7:52 | Morning | Monday | 2015 | 6
1135 | 2015-06-15 10:22 | 2015-06-15 10:22 | 13.8KV 3D FEEDER #7 | Fair | Planned Maintenance | 3 | 10:22 Manually Open LBS #3D-218. Replaced @2 broken Pin Insulator at Minas GS-5. (Shut down 2 wells during this job) 10:49 Closed LBS #3D-218. Cause: Maintenance job. | 123 | 1 | 10:22 | Morning | Monday | 2015 | 6
1136 | 2015-06-15 16:28 | 2015-06-15 16:28 | DURI POWER PLANT |  |  | - | 16:28 S/U DGT #7, then On Line the unit at 17:06. |  | 1 | 16:28 | Afternoon | Monday | 2015 | 6
1137 | 2015-06-15 20:12 | 2015-06-15 20:12 | MINAS POWER PLANT |  |  | - | 20:12 S/U MGT #5, then On Line at 20:50. 16-June-2015. 00:30 Off line MGT #5, then S/D the Unit for trouble shooting. (Load swing up & down) | 123 | 1 | 20:12 | Night | Monday | 2015 | 6
1138 | 2015-06-15 20:30 | 2015-06-15 20:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 17 | 20:30 It was reported b/o fuse for Tx at Well Tilan #26. 23:20 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Tilan #26. Replaced the b/o fuse with same size, then energized the Tx. Cause: Animal. (Monkey) | 3070752 | 1 | 20:30 | Night | Monday | 2015 | 6
1139 | 2015-06-16 02:51 | 2015-06-16 02:51 | 5 BRAVO SUBSTATION | Rain | Under investigation | 25 | 02:51 115KV 5B OCB #25 T/O. 115KV 5B OCB #26 T/O. (115KV 5B power TX-2 no Power) 13.8KV 5B fdr #4 close position. 13.8KV 5B fdr #5 close position. 13.8KV 5B fdr #8 close position. (WIP at GS-4) 04:15 Checked & found, 115KV 5B OCB #25 T/O. Ctr: 205-206 R/F: 87T-@3 & 86T. 115KV 5B OCB #26 T/O. Ctr: 832-833. Manually open 13.8KV 5B OCB fdr #4. Manually open 13.8KV 5B OCB fdr #5. Manually open 13.8KV 5B OCB fdr #8. 04:22 Closed 115 KV 5B OCB #25. Closed 115 KV 5B OCB #26. Closed 13.8KV 5B OCB fdr #4. (Ctr: 318-319) Closed 13.8KV 5B OCB fdr #5. (Ctr: 262-263) Closed 13.8KV 5B OCB fdr #8. (Ctr: 99949-99950) Cause: Under investigation. | 3070754 | 1 | 2:51 | Night | Tuesday | 2015 | 6
1140 | 2015-06-16 07:25 | 2015-06-16 07:25 | 13.8KV S. BALAM FEEDER #1 | Cloudy | Lightning | 83 | So.Balam VCB fdr #1 T/R 1x. So.Balam GFPC T/R 1x. Not checked yet. | 3070752 | 1 | 7:25 | Morning | Tuesday | 2015 | 6
1141 | 2015-06-16 07:25 | 2015-06-18 09:06 | 13.8KV S. BALAM FEEDER #1 | Cloudy | Lightning | 83 | Checked & found, So.Balam VCB fdr #1 T/R 1x Ctr: 333-334 R/F: 51N. Patrolled the line & found: -@1 & @2 Broken Lightning Arrester. -@2 Broken Pin Insulator on TP of Well So.Balam #231. Cause: Lightning. | 3070752 | 1 | 7:25 | Morning | Tuesday | 2015 | 6
1142 | 2015-06-16 08:03 | 2015-06-16 08:03 | 44KV NORTH DURI - DUMAI LINE | Cloudy | Unidentified | 0 | 44KV No.Duri GCB #1 (44KV Duri-Dumai line) T/R 1x. Not checked yet. | 3070752 | 1 | 8:03 | Morning | Tuesday | 2015 | 6
1143 | 2015-06-16 08:03 | 2015-06-22 20:03 | 44KV NORTH DURI - DUMAI LINE | Cloudy | Unidentified | 0 | Checked & found, 44Kv No.Duri GCB #1 (line to Dumai) T/R 1x Ctr: 148-149 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 8:03 | Morning | Tuesday | 2015 | 6
1144 | 2015-06-16 09:03 | 2015-06-16 09:03 | 13.8KV 4B FEEDER #2 | Fair | Animal | 25 | 09:03 4B OCB fdr #2 T/O. 09:36 Checked & found 4B OCB #2 T/SO. Ctr: 207-209 R/F: 51N. (Breaker Spring charge problem) 10:07 Blocked & closed 4B OCB fdr #2, but T/O again. Patrolled the line & found, a Dead Monkey & @2 broken Pin Insulator o/p #4B-158. Then isolated the fault by opening HLC o/p #4B-157. 11:02 Blocked & closed 4B OCB fdr #2, Ok. Then released the Block. Cause: Animal. (Monkey) | 3070754 | 1 | 9:03 | Morning | Tuesday | 2015 | 6
1145 | 2015-06-16 09:10 | 2015-06-16 09:10 | MINAS POWER PLANT |  |  | - | 09:10 S/U MGT #5, then O/L the unit at 09:35. |  | 1 | 9:10 | Morning | Tuesday | 2015 | 6
1146 | 2015-06-16 09:50 | 2015-06-16 09:50 | MINAS POWER PLANT |  |  | - | 09:50 OFF Line MGT #8, then S/D the unit for Stand By. |  | 1 | 9:50 | Morning | Tuesday | 2015 | 6
1147 | 2015-06-16 15:00 | 2015-06-16 15:00 | 13.8KV SINTONG FEEDER #1 | Fair | Transformer Failure | 29 | 15:00 It was reported b/o fuse for Tx at Well No.Menggala #13. 17:45 Checked & found, @2 b/o 12K fuse for 225Kva Tx at Well No.Menggala #13. Tested the Tx & found, Low megger reading. Cause: Tx Failure. (The Transformer will be replaced tomorrow morning) | 3070752 | 1 | 15:00 | Afternoon | Tuesday | 2015 | 6
1148 | 2015-06-16 15:00 | 2015-06-17 15:50 | 13.8KV SINTONG FEEDER #1 | Fair | Transformer Failure | 29 | 15:50 Replaced the failure 225 KVA Tx with 300 KVA Tx at Well North Menggala #13 & energized the Tx. Cause: Tx low megger reading. | 3070752 | 1 | 15:00 | Afternoon | Tuesday | 2015 | 6
1149 | 2015-06-17 08:07 | 2015-06-17 08:07 | 13.8KV 8D FEEDER #3 | Fair | Unidentified | 21 | 8D OCB fdr #3 T/R 1x. Not checked yet. | 3070754 | 1 | 8:07 | Morning | Wednesday | 2015 | 6
1150 | 2015-06-17 08:07 | 2015-06-19 10:34 | 13.8KV 8D FEEDER #3 | Fair | Unidentified | 21 | Checked & found, 8D OCB fdr #3 T/R 1x Ctr: 561-562 R/F: 51N. Patrolled the line & found nothing. Cause: Unidentified. | 3070754 | 1 | 8:07 | Morning | Wednesday | 2015 | 6
1151 | 2015-06-17 08:07 | 2015-06-17 08:07 | 13.8KV 8D FEEDER #5 | Fair | Lightning Arrester | 51 | 8D OCB fdr #5 T/R 1x. Not checked yet. | 3070754 | 1 | 8:07 | Morning | Wednesday | 2015 | 6
1152 | 2015-06-17 08:07 | 2015-06-19 09:40 | 13.8KV 8D FEEDER #5 | Fair | Lightning Arrester | 51 | Checked & found, 8D OCB fdr #5 T/R 1x Ctr: 1498-1499 R/F: 51N. Patrolled the line & found, @1, @3 broken L/As on TP of Well #8E-22. Cause: Lightning Arrester. | 3070754 | 1 | 8:07 | Morning | Wednesday | 2015 | 6
1153 | 2015-06-17 12:30 | 2015-06-17 12:30 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified (Fuse) | 26 | 12:30 It was reported b/o fuse for Tx at Well Petani #123. 14:39 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Petani #123. Perform TTR, Megger test the Tx & found, normal. (Good reading) Replaced b/o fuse with the same size and energized the Tx. Cause: Unidentified (fuse). | 3070752 | 1 | 12:30 | Afternoon | Wednesday | 2015 | 6
1154 | 2015-06-17 14:45 | 2015-06-17 14:45 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 14:45 It was reported b/o fuse for Tx at Well No.Menggala #30. (Well OFF status for servicing) Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well No.Menggala #30. Perform TTR, Megger test the Tx & found, normal. (Good reading) Replaced b/o fuse with the same size and energized the Tx. Cause: Unidentified (fuse). | 3070752 | 1 | 14:45 | Afternoon | Wednesday | 2015 | 6
1155 | 2015-06-18 08:42 | 2015-06-18 08:42 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 70 | 08:42 It was reported no power at Road pole #03-06-. (CD fdr #5) 09:30 Checked & found, Recl. 03-06-03 (C.Duri fdr #5) T/SO. Ctr: 269-270. Blocked & closed Recl. 03-06-03, but failed. 10:40 Transfer part load of C.Duri fdr #5 to C.Duri fdr #7, by closing LBS #03-06-29. (Load downstream of Recl. 03-06-03 fed by C.Duri #7) Cause: Unidentified. | 3070752 | 1 | 8:42 | Morning | Thursday | 2015 | 6
1156 | 2015-06-18 09:26 | 2015-06-18 09:26 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Secondary Cable | 73 | 09:26 It was reported b/o fuse for Tx o/p #04-02-12. 16:20 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx o/p #04-02-12. (Also found corrosion at the panel box) Replaced b/o fuse above with the same size, but the Tx is not energized yet. (w/o electrician replacing the corrosion panel box) Cause: Unidentified (Fuse). | 3070752 | 1 | 9:26 | Morning | Thursday | 2015 | 6
1157 | 2015-06-18 09:26 | 2015-06-20 17:30 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Secondary Cable | 73 | 17:30 Replaced b/o fuse above with the same size & energized the Tx. (after replacing corrosion panel box) Cause: Unidentified (Fuse). | 3070752 | 1 | 9:26 | Morning | Thursday | 2015 | 6
1158 | 2015-06-18 12:48 | 2015-06-18 12:48 | 13.8KV CENTRAL DURI FEEDER #7 | Cloudy | Animal | 10 | 12:48 C.Duri ACB fdr #7 T/LO. Ctr: 435-438 R/F: 51N. 13:10 Emergency call 123 reported b/o Tx o/p #03-06-21. 13:23 Opened LBS #03-06-29. 13:24 Blocked & closed C.Duri ACB fdr #7, Ok. Then released the block. 13:36 Checked the Tx o/p #03-06-21 & found, @1,@2,@3 Broken L/As and a Dead monkey. 13:45 Open HLC o/p #03-06-21, to isolate the Tx above. (4 Wells were still off) 13:48 Then Close LBS #03-06-29. Cause: Animal. (Monkey) | 3070752 | 1 | 12:48 | Afternoon | Thursday | 2015 | 6
1159 | 2015-06-19 03:06 | 2015-06-19 03:06 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | C.Duri ACB fdr #14 T/R 1x Ctr: 311-312 R/F: 50@1,@2. Not patrolled yet. | 3070752 | 1 | 3:06 | Night | Friday | 2015 | 6
1160 | 2015-06-19 03:06 | 2015-06-22 04:50 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | Checked & found C.Duri ACB fdr #14 T/R 1x Ctr: 311-312 R/F: 50@1,@2. Patrolled the Lines, but found nothing. Cause: Unidentified. | 3070752 | 1 | 3:06 | Night | Friday | 2015 | 6
1161 | 2015-06-19 06:51 | 2015-06-19 06:51 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | No.Duri fdr #11 load dropped 30A (280-250A). No.Duri GFPC-Tx #13 T/R 1x. Not checked yet. | 3070752 | 1 | 6:51 | Morning | Friday | 2015 | 6
1162 | 2015-06-19 06:51 | 2015-06-22 17:12 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | Checked & found, No.Duri VCB fdr #11 T/R 1x Ctr: 135-136 R/F: 51N. Also found, No.Duri GFPC-Tx #13 T/R 1x Ctr: Not reported yet. Patrolled the line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 6:51 | Morning | Friday | 2015 | 6
1163 | 2015-06-19 20:41 | 2015-06-19 20:41 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Duri Field fdr #1 load dropped 33A (102-69A). It was reported power T/R at CGS #1. Not checked yet. | 3070752 | 1 | 20:41 | Night | Friday | 2015 | 6
1164 | 2015-06-19 20:41 | 2015-06-22 16:50 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 01-08-31 (DF fdr #1). Recloser display problem. (Blinking) Patrolled the Line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 20:41 | Night | Friday | 2015 | 6
1165 | 2015-06-19 20:41 | 2015-06-19 20:41 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Duri Field fdr #3 load dropped 42A (165-123A). Not checked yet. | 3070752 | 1 | 20:41 | Night | Friday | 2015 | 6
1166 | 2015-06-19 20:41 | 2015-06-22 16:41 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Checked & found, Recl. 01-05-01 (DF fdr #3) T/R 1x Ctr: Not reported yet. Patrolled the line & found, @1 b/o fuse for Cap. Bank o/p #01-05-14. Cause: Unidentified. | 3070752 | 1 | 20:41 | Night | Friday | 2015 | 6
1167 | 2015-06-20 06:03 | 2015-06-20 06:03 | 13.8KV PINANG FEEDER #1 | Fair | Pin Insulator | 23 | 06:03 Pinang OCB fdr #1 T/R 1x. 17:23 Checked & found, Pinang OCB fdr #1 T/R 1x Ctr: 338-339 R/F: 51@3. Patrolled the Line & found, @3 F/O Pin Insulator o/p #27AN-29. Cause: Pin Insulator. | 3070752 | 1 | 6:03 | Morning | Saturday | 2015 | 6
1168 | 2015-06-20 12:12 | 2015-06-20 12:12 | 13.8KV MENGGALA FEEDER #2 | Fair | Animal | 14 | 12:12 It was reported b/o fuse for Tx at Well Sikladi #11. (Sintong fdr #1) 16:45 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx at Well Sikladi #11. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Squirrel) | 3070752 | 1 | 12:12 | Afternoon | Saturday | 2015 | 6
1169 | 2015-06-20 16:00 | 2015-06-20 16:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 0 | 16:00 It was reported No Power at Well Kulin #21. (C.Duri fdr #1) 16:30 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx at Well Kulin #21. Replaced b/o fuse above with the same size, then energized the TX. (Also found Recl. 40AW-17 (C.Duri fdr #1) T/R 1x Ctr: 567-568. Cause: Animal. (Snake) | 3070752 | 1 | 16:00 | Afternoon | Saturday | 2015 | 6
1170 | 2015-06-20 23:10 | 2015-06-20 23:10 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | No.Duri VCB fdr #7 T/R 1x. No.Duri GFPC-Tx #12 T/R 1x. (Ground fault alarm on No.Duri fdr #7) Not checked yet. | 3070752 | 1 | 23:10 | Night | Saturday | 2015 | 6
1171 | 2015-06-20 23:10 | 2015-06-22 22:10 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | Checked & found, No.Duri VCB fdr #7 T/R 1x Ctr: 182-183 R/F: 51N . Patrolled the line & found, @2 F/O Dead end Insulator o/p #NN. Cause: Unidentified. | 3070752 | 1 | 23:10 | Night | Saturday | 2015 | 6
1172 | 2015-06-21 07:36 | 2015-06-21 07:36 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 4 | So.Balam fdr #1 dropped 77A (102-25A). So.Balam fdr #4 dropped 13A (132-119). (Ground fault alarm on So.Balam fdr #1) Not checked yet. | 3070752 | 1 | 7:36 | Morning | Sunday | 2015 | 6
1173 | 2015-06-21 07:36 | 2015-06-22 15:18 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 4 | Checked & Patrolled, found nothing. Cause: Unidentified. | 3070752 | 1 | 7:36 | Morning | Sunday | 2015 | 6
1174 | 2015-06-21 20:55 | 2015-06-21 20:55 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 7 | 20:55 It was reported b/o fuse for Tx at Well Seruni #35. 22:15 Checked & found, @2, @3 b/o 3.5SF fuses for 150Kva Tx at Well Seruni #35. Performed TTR, Megger Test the Tx & found, normal. (good reading) Replaced b/o fuses above with the same size then energized the Tx. Cause: Animal. (Bird) | 3070752 | 1 | 20:55 | Night | Sunday | 2015 | 6
1175 | 2015-06-22 06:54 | 2015-06-22 06:54 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 6 | C.Duri ACB fdr #8 T/R 2x Ctr: 296-297 R/F: 51@2,@3 & 51N. Not patrolled yet. | 3070752 | 1 | 6:54 | Morning | Monday | 2015 | 6
1176 | 2015-06-22 06:54 | 2015-06-23 12:16 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 6 | Patrolled the Line & found, b/o fuse for PT Recl. 09-N6-06. Cause: Unidentified. | 3070752 | 1 | 6:54 | Morning | Monday | 2015 | 6
1177 | 2015-06-23 05:48 | 2015-06-23 05:48 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Fair | Unidentified | 25 | MSU-2 VCB fdr #2 (Nella fdr #2) T/R 1x. Not checked yet. | 3070752 | 1 | 5:48 | Morning | Tuesday | 2015 | 6
1178 | 2015-06-23 05:48 | 2015-06-25 15:52 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Fair | Unidentified | 25 | Checked & found, MSU-2 VCB fdr #2 (Nella fdr #2) T/R 1x Ctr: 206-207 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 5:48 | Morning | Tuesday | 2015 | 6
1179 | 2015-06-23 09:52 | 2015-06-23 09:52 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Unidentified (Fuse) | 0 | 09:52 It was reported b/o fuse for Tx o/p #04-00-02. 14:30 Checked & found, @2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #04-00-02. Replaced the b/o fuse with same size, then energized the Tx. Cause: Unidentified (fuse). | 3070752 | 1 | 9:52 | Morning | Tuesday | 2015 | 6
1180 | 2015-06-23 11:00 | 2015-06-23 11:00 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 1 | 11:00 De-energized 300Kva Tx at Well So.Balam #349. for squeezing jumper o/p #16Z-89. 12:30 Re-energize the TX. Cause: Planned Maintenance. | 3070752 | 1 | 11:00 | Morning | Tuesday | 2015 | 6
1181 | 2015-06-23 11:29 | 2015-06-23 11:29 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 15 | 11:29 Manually opened CKBS VCB fdr #5, to repairing loss connection at HLC of Recl. 36CU-29. 11:48 Manually closed CKBS VCB fdr #5. Cause: Planned Maintenance. | 3070754 | 1 | 11:29 | Morning | Tuesday | 2015 | 6
1182 | 2015-06-23 14:21 | 2015-06-23 14:21 | MINAS POWER PLANT |  |  | - | 14:21 S/U MGT #8, then on line at 15:03. | 123 | 1 | 14:21 | Afternoon | Tuesday | 2015 | 6
1183 | 2015-06-23 15:27 | 2015-06-23 15:27 | MINAS POWER PLANT |  |  | - | 15:27 Off line MGT #5, then S/D the Unit for S/B. | 123 | 1 | 15:27 | Afternoon | Tuesday | 2015 | 6
1184 | 2015-06-24 14:43 | 2015-06-24 14:43 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Dead End Insulator | 74 | C.Duir ACB fdr #3 T/R 1x Ctr: 180-181 R/F: 51N(@2). Not patrolled yet. | 3070752 | 1 | 14:43 | Afternoon | Wednesday | 2015 | 6
1185 | 2015-06-24 14:43 | 2015-06-26 13:43 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Dead End Insulator | 74 | Checked & found, C.Duri ACB fdr #3 T/R 1x Ctr: 180-181 R/F: 51N(@2). Patrolled the line & found: -@2 Broken Dead end Insulator o/p #01-1-32. -@2 Flashed over Dead end Insulator o/p #TL-05. Cause: Dead end Insulator. | 3070752 | 1 | 14:43 | Afternoon | Wednesday | 2015 | 6
1186 | 2015-06-25 14:30 | 2015-06-25 14:30 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 32 | Sintong OCB fdr #1 T/R 1x. Ground fault alarm on Sintong fdr #1. Not checked yet. | 3070752 | 1 | 14:30 | Afternoon | Thursday | 2015 | 6
1187 | 2015-06-25 14:30 | 2015-06-27 10:30 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 32 | Checked & found, Sintong OCB fdr #1 T/R 1x Ctr: 358-359 R/F: 51N. Also found, Sintong GFPC T/R 1x Ctr: 771-772 R/F: 51N. Patrolled the line & found, @1 broken L/A on TP of Well Kerang #13. Cause: Lightning. | 3070752 | 1 | 14:30 | Afternoon | Thursday | 2015 | 6
1188 | 2015-06-25 19:24 | 2015-06-25 19:24 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified (Fuse) | 6 | 19:24 It was reported b/o fuse for Tx at Well So.Balam #114. 20:42 Checked & found, @2 b/o 2.1SF fuse for 100Kva Tx at Well So.Balam #114. Perform TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuse with same size & Energized it. Cause: Unidentified (fuse). | 3070752 | 1 | 19:24 | Night | Thursday | 2015 | 6
1189 | 2015-06-26 01:45 | 2015-06-26 01:45 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 0 | 01:45 It was reported b/o fuse for Tx at Well Tiang #03. (Ketigul fdr #1) 10:50 Checked & found, @1, @2 b/o 14.0SF fuses for 500Kva Tx. Performed TTR & Megger Test the Tx & found, good reading. Replaced b/o fuses above with the same size then energized the Tx. Cause: Animal. (Monkey) | 3070752 | 1 | 1:45 | Night | Friday | 2015 | 6
1190 | 2015-06-26 07:18 | 2015-06-26 07:18 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified | 33 | Pematang OCB fdr #2 T/R 1x Ctr: 442-443 R/F: 51N. Not patrolled yet. | 3070752 | 1 | 7:18 | Morning | Friday | 2015 | 6
1191 | 2015-06-26 07:18 | 2015-06-30 15:18 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified | 33 | Patrolled the line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 7:18 | Morning | Friday | 2015 | 6
1192 | 2015-06-26 08:13 | 2015-06-26 08:13 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified (Fuse) | 12 | 08:13 It was reported b/o fuse for Tx o/p #01-7-25E. (Duri Field #3) 16:25 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-7-25E. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3070752 | 1 | 8:13 | Morning | Friday | 2015 | 6
1193 | 2015-06-26 16:47 | 2015-06-26 16:47 | 13.8KV 4D FEEDER #5 | Fair | Lightning Arrester | 0 | 4D fdr #5 load dropped 62A (138-76A). Not checked yet. | 3070754 | 1 | 16:47 | Afternoon | Friday | 2015 | 6
1194 | 2015-06-26 16:47 | 2015-06-29 16:47 | 13.8KV 4D FEEDER #5 | Fair | Lightning Arrester | 0 | Checked & found, Recl. 4D-51A (4D fdr #4) T/R 1x Ctr: 04-05. Patrolled the line & found, @1 broken L/A o/p #4E-21. Cause: Lightning Arrester. | 3070754 | 1 | 16:47 | Afternoon | Friday | 2015 | 6
1195 | 2015-06-27 06:45 | 2015-06-27 06:45 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | C.Duri ACB fdr #15 T/R 1x Ctr: 352-353 R/F: 50@1,@2. Not patrolled yet. | 3070752 | 1 | 6:45 | Morning | Saturday | 2015 | 6
1196 | 2015-06-27 06:45 | 2015-01-07 12:15 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 6:45 | Morning | Saturday | 2015 | 6
1197 | 2015-06-27 07:53 | 2015-06-27 07:53 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified (Fuse) | 50 | 07:53 It was reported b/o fuse for Tx at Well Pematang #65. (Pematang fdr #2) 09:40 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Pematang #65. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3070752 | 1 | 7:53 | Morning | Saturday | 2015 | 6
1198 | 2015-06-27 16:23 | 2015-06-27 16:23 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 4 | It was reported b/o fuse for Tx o/p #01-6-18. (Duri Field fdr #1) Not checked yet. | 3070752 | 1 | 16:23 | Afternoon | Saturday | 2015 | 6
1199 | 2015-06-27 16:23 | 2015-06-28 13:08 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 4 | Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-6-18. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3070752 | 1 | 16:23 | Afternoon | Saturday | 2015 | 6
1200 | 2015-06-27 21:12 | 2015-06-27 21:12 | 8 DELTA SUBSTATION | Fair | Under investigation | 682 | 21:12 8D OCB fdr #6 T/R 1x (At the same time 8D 115KV C/S-Tx #2 T/O) Minas GS #1 request to Open some feeder to anticipate spill at Minas GS-1. 21:26 Opened Minas fdr #2, then closed at 22:53 21:28 Opened Minas fdr #4, then closed at 22:58 21:31 Opened 8C fdr #1, then closed at 22:51 21:32 Opened 8D fdr #10, then closed at 23:02 21:37 Opened 8D fdr #1, then closed at 23:02 Opened 8D fdr #11, then closed at 23:03 21:50 Checked & found: 13.8KV 8D OCB fdr #6 T/R 1x Ctr: 197-198 R/F: 51@2,@3. Also found: 115KV 8D C/S-TX #2 T/O. By Relay: 51@A. (8D Substation TX #2 no Power) (Checked the Tx at 8D Sbustation & found, normal) Patrolled the line at downstream of 8D fdr #6, but found nothing. 21:55 Opened 8C fdr #3, then closed at 22.57 Opened 8D fdr #5, then closed at 22:31 Opened 8D fdr #2, then closed at 23:03 22:10 Opened 8D fdr #6, then closed at 22:12 Opened 8D fdr #7, then closed at 22:26 Opened 8D fdr #8, then closed at 22:33 22:12 Closed 115KV 8D C/S-TX #2. Cause: Under Investigation. | 3070754 | 1 | 21:12 | Night | Saturday | 2015 | 6
1201 | 2015-06-28 02:48 | 2015-06-28 02:48 | 115KV CENTRAL DURI - BATANG LINE | Fair | Suspension Insulator | 890 | 02:48 115Kv C.Duri OCB #31 T/LO. Ctr: 22-26 R/F: 21@1-G(Z-1), 67N (Instan) & 87L@1. OCB #33 T/LO. Ctr: 586. (Did not change) 115Kv Sintong GCB #25 T/LO. Ctr: 282-285 R/F: 21@1-G(Z-1), 67N (Instan) & 87L@1. (115KV C.Duri - Batang line) Batang Substation Black Out: (Closed Batang fdrs at 09:30). - Btg fdr #1. (Prod. Loss : 404 Bbls, 63 Wells) - Btg fdr #2. (Prod. Loss : 231 Bbls, 36 Wells) - Btg fdr #3. (Prod. Loss : 725 Bbls, 16 Wells) Total Loss :1360 Bbls,115 Wells Voltage system dropped at Bangko & Balam field. 04:10 Adjusted LTC at KBJ from R-13 to R-8 to R-6. 04:11 Adjusted LTC at ND Tx-4 from R-7 to R-10 to R-12. Adjusted LTC at ND Tx-5 from R-7 to R-10 to R-12. Checked & found, @1 Broken Suspension Insulator o/p #BTG-80. @1 Conductor fell down & touched to PLN service drop cable (220V). 05:30 Opened Isolation Switch GCB #31 & GCB #33 at C.Duri Switchyard. Opened Isolation Switch GCB #25 at Sintong. 09:02 Replaced @1 broken suspension o/p #BTG-80 & connected the Conductor to suspension. 09:06 Closed Isolation Switch GCB #31 & GCB #33 at C.Duri Switchyard. 09:24 Closed Isolation Switch GCB #25 at Sintong. 09:26 Closed 115Kv GCB #25 at Sintong. 09:28 Closed 115Kv GCB #31 at C.Duri Switchyard. 09:30 Closed 115Kv GCB #33 at C.Duri Switchyard. (Batang Substation energized & Back to Normal) Cause: Suspension Insulator. Prod. loss reported by Balam-GS. Batang fdr #3, Prod. loss = 728 Bbls / 16 Wells. Batang fdr #1 & fdr #2, Prod. loss = 162 Bbls / 33 Wells. Total = 890 Bbls/ 49 Wells. | 3070752 | 1 | 2:48 | Night | Sunday | 2015 | 6
1202 | 2015-06-28 10:59 | 2015-06-28 10:59 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 14 | Sintong OCB fdr #2 T/R 1x. Not checked yet. | 3070752 | 1 | 10:59 | Morning | Sunday | 2015 | 6
1203 | 2015-06-28 10:59 | 2015-06-29 14:00 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 14 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 391-392 R/F: 51N. Also found, Sintong GFPC T/R 3x Ctr: 772-775. Patrolled the line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 10:59 | Morning | Sunday | 2015 | 6
1204 | 2015-06-28 15:39 | 2015-06-28 15:39 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning Arrester | 21 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3070752 | 1 | 15:39 | Afternoon | Sunday | 2015 | 6
1205 | 2015-06-28 15:39 | 2015-01-07 13:02 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning Arrester | 21 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 167-168 R/F: 51N(@1). Patrolled the line & found, @1 broken L/A on TP of Well Pagar #40. Cause: Lightning Arrester. | 3070752 | 1 | 15:39 | Afternoon | Sunday | 2015 | 6
1206 | 2015-06-29 07:10 | 2015-06-29 07:10 | 13.8KV 5B FEEDER #1 | Fair | Unidentified | 0 | 5B fdr #1 load dropped 41A (91-50A). Not checked yet. | 3070754 | 1 | 7:10 | Morning | Monday | 2015 | 6
1207 | 2015-06-29 07:10 | 2015-02-07 11:06 | 13.8KV 5B FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 5B-06 (5B fdr #1) T/R 1x Ctr: 26-27. Patrolled the line, but found nothing. Cause: Unidentified. | 3070754 | 1 | 7:10 | Morning | Monday | 2015 | 6
1208 | 2015-06-29 07:27 | 2015-06-29 07:27 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 111 | 07:27 So.Bekasap fdr #1 load dropped 52A (161-109A). 08:44 It was reported no power at Ampuh Field. 10:00 Checked & found, Recl. 34BI-18 (So.Bekasap fdr #1) T/O. (block position) Ctr: 139-140. Checked Rig. Job at Well Ampuh #14 & found, normal. (The Rig was moving) 10:21 Closed Recl. 34BI-18, Ok. Then release the block. Not patrolled yet. | 3070752 | 1 | 7:27 | Morning | Monday | 2015 | 6
1209 | 2015-06-29 21:52 | 2015-06-29 21:52 | DURI POWER PLANT |  |  | - | 21:50 Off line DGT #7, then S/D the Unit at 21:52. (For S/B-Prior to trouble shooting MVAR hunting) | 123 | 1 | 21:52 | Night | Monday | 2015 | 6
1210 | 2015-06-30 10:13 | 2015-06-30 10:13 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 10:13 It was reported b/o fuse for Tx o/p #04-8-20. (C.Duri fdr #9) 15:07 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-8-20. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3070752 | 1 | 10:13 | Morning | Tuesday | 2015 | 6
1211 | 2015-06-30 13:09 | 2015-06-30 13:09 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 21 | 13:09 Ketigul VCB fdr #2 T/SO. 13:30 Blocked & closed Ketigul VCB fdr #2, Ok. Then released the block. 14:13 Checked & found, Ketigul VCB fdr #2 T/SO. Ctr: 167-168 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3070752 | 1 | 13:09 | Afternoon | Tuesday | 2015 | 6
1212 | 2015-06-30 13:47 | 2015-06-30 13:47 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 13:47 It was reported b/o fuse for Tx o/p #05-N3-06. (C.Duri fdr #14) 15:26 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #05-N3-06. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3070752 | 1 | 13:47 | Afternoon | Tuesday | 2015 | 6
1213 | 2015-06-30 16:03 | 2015-06-30 16:03 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 16:03 It was reported b/o fuse for Tx o/p #04-01-21. 17:10 Checked & found, @2 b/o 3.1SF fuse for 112,5 Kva Tx o/p #04-01-21. Perform TTR, Megger test the Tx & found, good reading. Replaced b/o fuse above with same size & Energized the Tx. Cause: Unidentified (fuse). | 3070752 | 1 | 16:03 | Afternoon | Tuesday | 2015 | 6
1214 | 2015-06-30 17:38 | 2015-06-30 17:38 | 44KV NORTH DURI - DUMAI LINE | Fair | Others | 0 | 44KV No.Duri GCB #1 (44KV Line to Dumai) T/R 1x. (Dumai RTU failed at that time) Not checked yet. | 3070752 | 1 | 17:38 | Afternoon | Tuesday | 2015 | 6
1215 | 2015-06-30 19:29 | 2015-06-30 19:29 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified | 0 | 19:29 It was reported no power at HCT Booster Pump. 21:30 Checked & found, 13.8Kv Recl. for 3.75MVA TX at HCT Mini Substation. T/O. Ctr: 1613. (Found 4.16Kv Recloser on close position) Open 4.16Kv Recloser, to check the Tx & found, normal. (good reading) Then checked and exercised 13.8Kv Recloser & found, spark on @3 FCO. 22:30 Closed 13.8Kv Recl. for 3.75MVA TX, Ok. Blocked & closed 4.16Kv Recloser, Ok. Then released the Block. Then Running one of Boioster Pump, Ok. Cause: Unidentified. (Suspected loss connection on FCO) | 3070752 | 1 | 19:29 | Night | Tuesday | 2015 | 6
1216 | 2015-06-30 22:35 | 2015-06-30 22:35 | 13.8KV BANGKO FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 22:35 It was reported b/o fuse for Tx at Well Bangko #311. 23:00 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Bangko #311. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3070752 | 1 | 22:35 | Night | Tuesday | 2015 | 6
1217 | 2015-01-07 07:07 | 2015-01-07 07:07 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri ACB fdr #16 T/R 1x Ctr: 280-281 R/F: 51N & 51@1,@2. Not patrolled yet. | 3084138 | 1 | 7:07 | Morning | Wednesday | 2015 | 1
1218 | 2015-01-07 07:07 | 2015-02-07 15:07 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 7:07 | Morning | Wednesday | 2015 | 1
1219 | 2015-01-07 09:39 | 2015-01-07 09:39 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 0 | 09:39 It was reported b/o fuse for TX o/p #05-N3-06. (C.Duri fdr #14) 15:31 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #05-N3-06. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (fuse). | 3084138 | 1 | 9:39 | Morning | Wednesday | 2015 | 1
1220 | 2015-01-07 10:16 | 2015-01-07 10:16 | 13.8KV NORTH DURI FEEDER #1 | Fair | Theft | 0 | 10:16 It was reported stolen secondary cable of Tx o/p #10-J8-04. Cause: Theft. | 3084138 | 1 | 10:16 | Morning | Wednesday | 2015 | 1
1221 | 2015-01-07 10:16 | 2015-02-07 17:05 | 13.8KV NORTH DURI FEEDER #1 | Fair | Theft | 0 | Replaced stolen secondary cable for 112.5Kva Tx o/p #10-J8-04 then energized the Tx. Cause: Theft. | 3084138 | 1 | 10:16 | Morning | Wednesday | 2015 | 1
1222 | 2015-01-07 16:35 | 2015-01-07 16:35 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | 16:35 It was reported b/o fuse for Tx o/p #IF34-7. (for complex Talang #187) 17:50 Checked & found, @1 b/o 1.0SF fuse for 50KVA TX o/p #IF34-7. Replaced b/o fuse above with same size, then energized the TX. Cause: Animal. (Squirrel) | 3084138 | 1 | 16:35 | Afternoon | Wednesday | 2015 | 1
1223 | 2015-02-07 12:37 | 2015-02-07 12:37 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 12:37 CGT #4 Tripped by alarm: Fire Detective. (Not Real) Frequency system dropped to 59.84 Hz. (No Load shedding) 12:45 Closed ACB #39. (Tie Breaker) Cause: Under Investigation. 03-Jul-2015. 18:05 S/U CGT #4 then Online the unit at 18:27. 18:26 Opened ACB #39. (Tie Breaker) | 3084139 | 1 | 12:37 | Afternoon | Saturday | 2015 | 2
1224 | 2015-03-07 16:14 | 2015-03-07 16:14 | 13.8KV S. BALAM GFPC | Fair | Unidentified | 0 | So.Balam GFPC T/R 1x. Fault alarm on So.Balam fdr #1. No load dropped at any feeder. Not checked yet. | 3084138 | 1 | 16:14 | Afternoon | Saturday | 2015 | 3
1225 | 2015-03-07 16:14 | 2015-06-07 11:14 | 13.8KV S. BALAM GFPC | Fair | Unidentified | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 190-191. Patrolled So.Balam fdr #1 line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 16:14 | Afternoon | Saturday | 2015 | 3
1226 | 2015-03-07 18:05 | 2015-03-07 18:05 | CENTRAL DURI POWER PLANT |  |  | - | 18:05 S/U CGT #4 then Online the unit at 18:27. 18:26 Opened Tie Breaker ACB #39. | 123 | 1 | 18:05 | Afternoon | Saturday | 2015 | 3
1227 | 2015-04-07 03:25 | 2015-04-07 03:25 | 13.8KV RANGAU FEEDER #1 | Fair | Unidentified | 0 | Rangau OCB fdr #1 T/R 1x. Not checked yet. | 3084138 | 1 | 3:25 | Night | Tuesday | 2015 | 4
1228 | 2015-04-07 03:25 | 2015-07-07 13:25 | 13.8KV RANGAU FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Rangau OCB fdr #1 T/R 1x Ctr: 0003-0004 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 3:25 | Night | Tuesday | 2015 | 4
1229 | 2015-04-07 12:00 | 2015-04-07 12:00 | 13.8KV KOTABATAK FEEDER #2 | Fair | Switchboard Problem | 5 | 12:00 It was reported b/o fuse for Tx at Well Kota Batak #269. (OKB fdr #2) 14:21 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Kotabatak #269. Replaced b/o fuse above with the same size then energized the Tx. Cause: Switchboard Problem. | 3084139 | 1 | 12:00 | Afternoon | Tuesday | 2015 | 4
1230 | 2015-04-07 14:31 | 2015-04-07 14:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 146 | 14:31 C.Duri fdr #1 load dropped 80A (200-120A). It was reported that animal (Monkey) caused short circuit o/p #41-AW-54. 16:00 Checked & found, Recl. #41-AW-62 (C.Duri fdr #1) T/LO. Ctr: 188-192. Also found the animal above near pole #41-AW-54. 16:04 Blocked & closed Recl. 41AW-62, Ok. Then released the block. Cause: Animal. (Monkey) | 3084138 | 1 | 14:31 | Afternoon | Tuesday | 2015 | 4
1231 | 2015-04-07 22:30 | 2015-04-07 22:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 11 | 22:30 It was reported b/o fuse for Tx at Well Pagar #15. 22:45 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Pagar #15. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 22:30 | Night | Tuesday | 2015 | 4
1232 | 2015-05-07 22:00 | 2015-05-07 22:00 | MINAS POWER PLANT |  |  | - | 22:00 Off line MGT #8, then S/D the Unit for S/B. (Prior to trouble shooting the Mvar Excitation Hunting to 38.9 Mvar) |  | 1 | 22:00 | Night | Thursday | 2015 | 5
1233 | 2015-05-07 23:59 | 2015-05-07 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI power system Normal Condition. |  | 1 | 23:59 | Night | Thursday | 2015 | 5
1234 | 2015-06-07 07:31 | 2015-06-07 07:31 | 13.8KV KETIGUL FEEDER#1 | Fair | Low mega-ohm reading | 7 | 07:31 It was reported b/o fuse for Tx at Well Tilan #18. 11:15 Checked & found, @1&@3 B/O 15K fuses for 300KVA Tx at Well Tilan #18. Tested the Tx & found, Low megger reading. 13:00 Then replaced the failure 300KVA Tx with the same size & energized the Tx. Cause: Tx low megger reading. | 3084138 | 1 | 7:31 | Morning | Sunday | 2015 | 6
1235 | 2015-06-07 09:00 | 2015-06-07 09:00 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 09:00 It was reported that b/o fuse for Tx at Well KB #28. 12:20 Checked & found, @1 b/o 15K fuse for 300KVA Tx at Well KB #28. Tested the Tx & found normal, ( good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3084139 | 1 | 9:00 | Morning | Sunday | 2015 | 6
1236 | 2015-06-07 09:28 | 2015-06-07 09:28 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 56 | OKB OCB fdr #2 T/R 1x Ctr: 1244-1245 R/F: 51N. Not patrolled yet. | 3084139 | 1 | 9:28 | Morning | Sunday | 2015 | 6
1237 | 2015-06-07 09:28 | 2015-07-07 09:28 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 56 | Patrolled the line, but found nothing. Cause: Unidentified. | 3084139 | 1 | 9:28 | Morning | Sunday | 2015 | 6
1238 | 2015-07-07 05:53 | 2015-07-07 05:53 | 13.8KV 5B FEEDER #1 | Fair | Unidentified (Fuse) | 6 | 05:53 It was reported b/o fuse for Tx at Well #5B-85. (5B fdr #1) 13:00 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well #5B-85. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3084139 | 1 | 5:53 | Morning | Tuesday | 2015 | 7
1239 | 2015-07-07 06:31 | 2015-07-07 06:31 | 13.8KV BATANG FEEDER #3 | Fair | Lightning Arrester | 49 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3084138 | 1 | 6:31 | Morning | Tuesday | 2015 | 7
1240 | 2015-07-07 06:31 | 14/07/2015 13:31 | 13.8KV BATANG FEEDER #3 | Fair | Lightning Arrester | 49 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 270-271 R/F: 51@1. Patrolled the line & found, @1 broken L/A o/p #38AK-10. Cause: Lightning Arrester. | 3084138 | 1 | 6:31 | Morning | Tuesday | 2015 | 7
1241 | 2015-07-07 08:11 | 2015-07-07 08:11 | 13.8KV MINAS FEEDER #6 | Fair | Lightning Arrester | 65 | Minas fdr #6 load dropped 103A (220-117A). Not checked yet. | 3084139 | 1 | 8:11 | Morning | Tuesday | 2015 | 7
1242 | 2015-07-07 08:11 | 2015-09-07 13:22 | 13.8KV MINAS FEEDER #6 | Fair | Lightning Arrester | 65 | Checked & found, Recl. 6E-23A (Minas fdr #6) T/R 1x Ctr: 11-12. Patrolled the line & found, @3 broken L/A on TP of Well #6F-21. Cause: Lightning Arrester. | 3084139 | 1 | 8:11 | Morning | Tuesday | 2015 | 7
1243 | 2015-07-07 08:21 | 2015-07-07 08:21 | 13.8KV BANGKO FEEDER #4 | Fair | Relay Failure | 432 | 08:09 Bangko fdr #4 load dropped 96A (219-113A). Not checked yet. 08:21 Bangko OCB fdr #4 T/R 1x. 08:33 Bangko OCB fdr #4 T/R 1x. 08:44 Bangko OCB fdr #4 T/R 1x. 11:19 Bangko OCB fdr #4 T/R 1x. 11:41 Bangko OCB fdr #4 T/R 1x. 12:01 Bangko OCB fdr #4 T/R 1x. 14:10 Bangko OCB fdr #4 T/R 1x. 14:34 Bangko OCB fdr #4 T/R 1x. Not checked yet. (Suspected Relay Type F-60 problem, then none activate it) Note: Bangko fdr #4 use Backup relay F-35 if any fault it will T/SO. | 3084138 | 1 | 8:21 | Morning | Tuesday | 2015 | 7
1244 | 2015-07-07 08:21 | 2015-08-07 08:21 | 13.8KV BANGKO FEEDER #4 | Fair | Relay Failure | 432 | Patrolled the line, but found nothing. Cause: Relay failure. (Relay Type F-60) | 3084138 | 1 | 8:21 | Morning | Tuesday | 2015 | 7
1245 | 2015-07-07 17:49 | 2015-07-07 17:49 | 13.8KV ROKAN FEEDER #2 | Fair | Pin Insulator | 13 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3084138 | 1 | 17:49 | Afternoon | Tuesday | 2015 | 7
1246 | 2015-07-07 17:49 | 2015-08-07 15:49 | 13.8KV ROKAN FEEDER #2 | Fair | Pin Insulator | 13 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 984-985 R/F: 51N(@1). Patrolled the line & found, @1 broken Pin Insulator o/p #35BI-14. Cause: Pin Insulator. | 3084138 | 1 | 17:49 | Afternoon | Tuesday | 2015 | 7
1247 | 2015-08-07 08:37 | 2015-08-07 08:37 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 10 | 08:37 It was reported b/o fuse for Tx o/p #06-S5-05. (C.Duri fdr #2) 16:45 Checked & found, @1 b/o 3.1SF fuse for 112.5 Kva Tx o/p #06-S5-05. Perform TTR, Megger test the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3084138 | 1 | 8:37 | Morning | Friday | 2015 | 8
1248 | 2015-08-07 14:26 | 2015-08-07 14:26 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Dead End Insulator | 0 | C.Duri ACB fdr #16 T/R 2x Ctr: 281-283 R/F: 51@1,@2. Not patrolled yet. | 3084138 | 1 | 14:26 | Afternoon | Friday | 2015 | 8
1249 | 2015-08-07 14:26 | 2015-09-07 15:00 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Dead End Insulator | 0 | Patrolled the line & found, @1 broken Dead end Insulator o/p #3H-03. Cause: Dead end Insulator. | 3084138 | 1 | 14:26 | Afternoon | Friday | 2015 | 8
1250 | 2015-09-07 07:35 | 2015-09-07 07:35 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 0 | 07:35 C.Duri fdr #7 load dropped 79A (154-75A). 10:02 Checked & found, Recl. 03-03-42 (C.Duri fdr #7) T/R 1x Ctr: 102-103. Patrolled the line & found, a death Lizard o/p #03-03-25. Cause: Animal. (Lizard) | 3084138 | 1 | 7:35 | Morning | Monday | 2015 | 9
1251 | 2015-09-07 09:22 | 2015-09-07 09:22 | 13.8KV 4B FEEDER #1 | Fair | Dead End Insulator | 141 | 4B OCB fdr #4 T/R 1x. 4B fdr #2 load dropped 66A (125-59). 4B fdr #3 load dropped 128A (129-1A). Not checked yet. | 3084139 | 1 | 9:22 | Morning | Monday | 2015 | 9
1252 | 2015-09-07 09:22 | 2015-11-07 10:22 | 13.8KV 4B FEEDER #1 | Fair | Dead End Insulator | 141 | Checked & found, 4B OCB fdr #1 T/R 2x Ctr: 255-257 R/F: 51@1,@2. Patrolled the line & found, @2 broken Dead end Insulator o/p #4B-92. Cause: Dead end Insulator. | 3084139 | 1 | 9:22 | Morning | Monday | 2015 | 9
1253 | 2015-09-07 11:50 | 2015-09-07 11:50 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 0 | 11:50 It was reported b/o fuse for Tx o/p #01-06-06. (C.Duri fdr #14) 15:45 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-06-06. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 11:50 | Morning | Monday | 2015 | 9
1254 | 2015-10-07 02:53 | 2015-10-07 02:53 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 97 | 02:53 Duri Field fdr #2 load dropped 80A (165-85). 03:16 It was reported no power at (6 roads) at Area-7 Duri Field. 05:00 Checked & found, Recl. 07-U3-21 (Duri Field fdr #2) T/SO. Ctr: 123-124. 05:40 Patrolled the line, due to reported broken jumper o/p #07-U3-02 by Security, but found nothing. Blocked & closed Recl. 07-U3-21, Ok. Then released the block. Cause: Unidentified. | 3084138 | 1 | 2:53 | Night | Wednesday | 2015 | 10
1255 | 2015-10-07 10:20 | 2015-10-07 10:20 | 13.8KV 4B FEEDER #1 | Fair | Planned Maintenance | 0 | 10:20 Blocked 4B fdr #1, then opened HLC due to Trimming Danger high Trees. (Well #4B-44 was off during the job done) 11:00 Closed HLC & re-S/U Well #4B-44, then release the block. Cause: Maintenance Job. | 123 | 1 | 10:20 | Morning | Wednesday | 2015 | 10
1256 | 2015-10-07 15:45 | 2015-10-07 15:45 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Secondary Cable | 0 | 15:45 It was reported b/o fuse for Tx o/p #01-6-06. (C.Duri fdr #14) 16:00 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-6-06. Then replaced b/o fuse above with the same size & energized the Tx. Cause: Short circuit Underground cable. | 3084138 | 1 | 15:45 | Afternoon | Wednesday | 2015 | 10
1257 | 2015-10-07 19:40 | 2015-10-07 19:40 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | 0 | 19:40 It was reported b/o fuse for Tx o/p #06-Q3-19. (C.Duri fdr #15) Not checked yet. | 3084138 | 1 | 19:40 | Night | Wednesday | 2015 | 10
1258 | 2015-10-07 19:40 | 2015-11-07 12:35 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1,@2 b/o 3.1SF fuss for 112.5Kva Tx o/p #06-Q3-14. (C.Duri fdr #15) Replaced the fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 19:40 | Night | Wednesday | 2015 | 10
1259 | 2015-11-07 04:34 | 2015-11-07 04:34 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 27 | 04:34 It was reported b/o fuse for Tx at Well BKO #273. (BKO fdr #4) 09:17 Checked & found, @1 broken 2.1SF fuse for 100Kva Tx at Well BKO #273. Replaced b/o fuse above with the same size & energized the Tx. Cause : Unidentified (Fuse). | 3084138 | 1 | 4:34 | Morning | Saturday | 2015 | 11
1260 | 2015-11-07 11:15 | 2015-11-07 11:15 | MINAS POWER PLANT |  |  | - | 11:15 S/U MGT #2, then On line the Unit at 11:45. (Running on Test) 20:39 MGT #2 Tripped, by Alarm: No alarm appeare (Under Running on Test) |  | 1 | 11:15 | Morning | Saturday | 2015 | 11
1261 | 2015-11-07 18:02 | 2015-11-07 18:02 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified | 0 | C.Duri ACB fdr #13 T/R 1x Ctr: 281-282 R/F: 51N @2. Not Patrolled yet. | 3084138 | 1 | 18:02 | Afternoon | Saturday | 2015 | 11
1262 | 2015-11-07 18:02 | 14/07/2015 13:02 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 18:02 | Afternoon | Saturday | 2015 | 11
1263 | 2015-12-07 06:07 | 2015-12-07 06:07 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified (Fuse) | 51 | It was reported b/o fuse for Tx o/p #13-F10-16. (N.Duri fdr #11) Not checked yet. | 3084138 | 1 | 6:07 | Morning | Monday | 2015 | 12
1264 | 2015-12-07 06:07 | 13/07/2015 11:40 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified (Fuse) | 51 | 11:40 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #13-F10-16. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 6:07 | Morning | Monday | 2015 | 12
1265 | 2015-12-07 08:38 | 2015-12-07 08:38 | CENTRAL DURI POWER PLANT | Fair | Equipment Failure | - | 08:38 CGT #4 Tripped Off, by Alarm: -DC under voltage 125V DC. -Fire Detected Trip (45FT) & CO2 release. Cause: Equipment failure. (Fire detector cable broken) 08:39 Closed C.Duri ACB #39. (Tie Breaker) 14-July-2015 15:30 S/U CGT #4, then on line the Unit at 15:54. 15:53 Opened ACB #39. (Tie Breaker) | 3084138 | 1 | 8:38 | Morning | Monday | 2015 | 12
1266 | 2015-12-07 11:06 | 2015-12-07 11:06 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | No.Duri VCB fdr #5 T/R 1x. Not checked yet | 3084138 | 1 | 11:06 | Morning | Monday | 2015 | 12
1267 | 2015-12-07 11:06 | 14/07/2015 13:06 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | Checked & found, No.Duri VCB fdr #5 T/R 1x Ctr: 101-102 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 11:06 | Morning | Monday | 2015 | 12
1268 | 2015-07-13 07:19 | 2015-07-13 07:19 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Pin Insulator | 0 | C.Duri ACB fdr #15 T/R 1x Ctr: 253-254 R/F: 51N. Not Patrolled yet. | 3084138 | 1 | 7:19 | Morning | Monday | 2015 | 7
1269 | 2015-07-13 07:19 | 2015-07-14 13:19 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Pin Insulator | 0 | Patrolled the line & found, @1 broken Pin Insulator o/p #06-R3-01. Cause: Pin Insulator. | 3084138 | 1 | 7:19 | Morning | Monday | 2015 | 7
1270 | 2015-07-13 09:30 | 2015-07-13 09:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 6 | 09:30 It was reported b/o fuse for Tx o/p #09-M1-04. (C.Duri fdr #1) 10:45 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #09-M1-04. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3084138 | 1 | 9:30 | Morning | Monday | 2015 | 7
1271 | 2015-07-13 20:23 | 2015-07-13 20:23 | CENTRAL KOTABATAK SUBSTATION | Fair | Under investigation | 497 | 20:23 115KV CKBS C/S-TX #2 T/O. 21:15 Checked & found, CKBS C/S-TX #2 T/O. Ctr: 229-230 R/F: 51N. 21:19 Manual opened 13.8KV CKBS VCB fdr #5. Manual opened 13.8KV CKBS VCB fdr #6. 21:21 Opened Isolation Switch of CKBS C/S-TX #2. Visual checked Power TX, VR & Bus, found normal. 21:44 Closed Isolation Switch of CKBS C/S-TX #2. Closed 115KV CKBS C/S-TX #2, OK. 21:47 Closed 13.8KV CKBS VCB fdr #5, OK. 21:48 Closed 13.8KV CKBS VCB fdr #6, OK. Cause: Under Investigation. Prod Loss: CKB fdr #5: 66 Wells/303 bbls. CKB fdr #6: 49 Wells/181 bbls. Total : 115 Wells/484 bbls. | 3084139 | 1 | 20:23 | Night | Monday | 2015 | 7
1272 | 2015-07-14 10:10 | 2015-07-14 10:10 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 2 | 10:10 It was reported b/o fuse for Tx at Well Bangko #107. (Bangko fdr #1) 11:40 Checked & found, @1,@2 b/o 2.1SF fuses for 100Kva Tx at Well Bangko #107. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Chicken) | 3084138 | 1 | 10:10 | Morning | Tuesday | 2015 | 7
1273 | 2015-07-14 15:30 | 2015-07-14 15:30 | CENTRAL DURI POWER PLANT |  |  | - | 15:30 S/U CGT #4, then on line the Unit at 15:54. 15:53 Opened ACB #39. (Tie Breaker) (See report on 12-July-2015 at 08:38) |  | 1 | 15:30 | Afternoon | Tuesday | 2015 | 7
1274 | 2015-07-14 15:31 | 2015-07-14 15:31 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Animal | 10 | 15:31 It was reported b/o fuse for Tx o/p #05-M5-21. (C.Duri fdr #2) 17:45 Checked & found, @1,@3 b/o 3.1SF fuse for 112.5Kva Tx o/p #05-M5-21. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3084138 | 1 | 15:31 | Afternoon | Tuesday | 2015 | 7
1275 | 2015-07-14 19:18 | 2015-07-14 19:18 | 13.8KV PETANI FEEDER #1 | Fair | Others | - | 19:18 It was reported no Power at Petani-GS. 21:05 Checked & found, Open Tie Breaker for shipping Pump & Lighting at Petani-GS. Also found, burnt out wiring cable for ATS. (Automatic Transfer Switch) 22:17 Opened FCO for 300Kva Tx #3, to dismanthle wiring cable above. Then re-energize 300Kva Tx #3. (after dismanthling the ATS) Petani-GS back to normal. Cause: Others. (burnt out wiring cable for ATS) | 3084138 | 1 | 19:18 | Night | Tuesday | 2015 | 7
1276 | 2015-07-15 10:00 | 2015-07-15 10:00 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 2 | 10:00-11:36 Blocked Recl. 29Z-13 (Bangko fdr #4). To replacing @1 broken FCO on TP of Well Genting #06. (Wells Genting #06 & #11 were off during the job done) Cause: Maintenance Job. | 3084138 | 1 | 10:00 | Morning | Wednesday | 2015 | 7
1277 | 2015-07-15 11:00 | 2015-07-15 11:00 | DURI POWER PLANT | Fair |  | - | 11:00 Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 11:00 | Morning | Wednesday | 2015 | 7
1278 | 2015-07-15 14:32 | 2015-07-15 14:32 | 13.8KV 4D FEEDER #4 | Fair | Others | 0 | 14:32 Manually open 4D OCB fdr #4. (to anticipate spill at Minas GS-4) (It was Requested by GS-4 operator, due to 3 WIPs at Minas GS-4 were off) DB Pump #4/3 & #4/4 (6D fdr #4) & BJU Pump #4/1 (5B fdr #8) Cause: Others. (WIP control problem) 16:09 Manually closed 4D OCB fdr #4. (requested by GS-4 operator) (No prod. loss charge to PGT) | 3084139 | 1 | 14:32 | Afternoon | Wednesday | 2015 | 7
1279 | 2015-07-15 18:24 | 2015-07-15 18:24 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Bangko fdr #4 Load dropped 20A (228-208). Bangko GFPC T/R 1x. (Fault alarm on Bangko fdr #4) Not checked yet. | 3084138 | 1 | 18:24 | Afternoon | Wednesday | 2015 | 7
1280 | 2015-07-15 18:24 | 2015-07-19 20:24 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Cheked & found, Recl. 29Y-16 (Bangko fdr #4) T/R 1x Ctr: 84-85. Also found, Bangko GFPC T/R 1x Ctr: 464-465 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 18:24 | Afternoon | Wednesday | 2015 | 7
1281 | 2015-07-16 07:50 | 2015-07-16 07:50 | 13.8KV DURI FIELD FEEDER #3 | Fair | Dead End Insulator | 0 | Duri Field ACB fdr #3 T/R 1x. Not checked yet. | 3084138 | 1 | 7:50 | Morning | Thursday | 2015 | 7
1282 | 2015-07-16 07:50 | 2015-07-17 17:50 | 13.8KV DURI FIELD FEEDER #3 | Fair | Dead End Insulator | 0 | Checked & found, D.Field VCB fdr #3 T/R 12x Ctr: 99527-99539 R/F: 51N. Patrolled the line, but found nothing. Also found, Recl. 01-7-01 (D.Field fdr #3) T/R 1x Ctr: 1178-1179. Patrolled the line & found, @3 flashed over Dead end Insulator o/p #01-7-13. Cause: Dead end Insulator. | 3084138 | 1 | 7:50 | Morning | Thursday | 2015 | 7
1283 | 2015-07-16 10:21 | 2015-07-16 10:21 | MINAS POWER PLANT |  |  | - | 10:21 S/U MGT #8, then the Unit Online at 10:40. |  | 1 | 10:21 | Morning | Thursday | 2015 | 7
1284 | 2015-07-17 06:20 | 2015-07-17 06:20 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 17 | 06:20 Sintong OCB fdr #2 T/R 1x. (Ground fault alarm on Sintong fdr #1 & #2) 18:32 Sintong OCB fdr #2 T/R 1x again. Sintong GFPC T/R 1x again. (Ground fault alarm on Sintong fdr #1 & #2) Not checked yet. | 3084138 | 1 | 6:20 | Morning | Friday | 2015 | 7
1285 | 2015-07-17 06:20 | 2015-07-19 10:30 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 17 | Checked & found, Sintong OCB fdr #2 T/R 2x Ctr: 392-394 R/F: 51N. Also found, Sintong GFPC T/R 4x Ctr: 775-779. Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 6:20 | Morning | Friday | 2015 | 7
1286 | 2015-07-17 12:43 | 2015-07-17 12:43 | 13.8KV 3D FEEDER #8 | Fair | Dead End Insulator | 45 | 3D fdr #8 load dropped 227A (264-37A). 3D fdr #7 load dropped 72A (145-73A). Not checked yet. | 3084139 | 1 | 12:43 | Afternoon | Friday | 2015 | 7
1287 | 2015-07-17 12:43 | 2015-07-23 09:43 | 13.8KV 3D FEEDER #8 | Fair | Dead End Insulator | 45 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 164-165 R/F: 51@1. Patrolled the line & found: -@1,@2 Broken Dead end Insulator o/p #3E-10. -@1 Flashed over Recloser bushing (Source side) o/p #2F-11C. Cause: Dead end Insulator. | 3084139 | 1 | 12:43 | Afternoon | Friday | 2015 | 7
1288 | 2015-07-18 09:47 | 2015-07-18 09:47 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 14 | 09:47 It was reported no power at one road, downstream of pole #07-T1-18. (DF fdr #2) 10:30 Checked & found, Recl. 07-T1-19 (D.Field fdr #2) T/SO. Ctr: 499-500. 10:55 Blocked & closed Recl 07-T1-19, but Tripped again. Checked & found b/o of PT fuse & a dead Monkey, also flash over at bushing of the Recloser. 11:00 Blocked & closed Recl. 07-T1-19, but Tripped again. 11:05 Prepared Switching Procedure, to transfer part of the load to DF fdr #4. 11:10 Opened visual opening of Recl 07-T1-19 and pull the Recloser yellow lever switch. 11:30 Closed LBS #07-T1-02. (fed from D.Field fdr #4) Cause: Animal. (Monkey) | 3084138 | 1 | 9:47 | Morning | Saturday | 2015 | 7
1289 | 2015-07-18 10:28 | 2015-07-18 10:28 | 13.8KV DARLING VCB FEEDER #8 | Fair | Unidentified (Fuse) | 0 | 10:28 It was reported b/o fuse for Tx o/p #05-N3-12. (3 Wells were off) 14:50 Checked & found, @1 b/o 2.1SF fuse for 112.5Kva Tx o/p #05-N3-12. Replaced b/o fuse above with same size then energized the Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 10:28 | Morning | Saturday | 2015 | 7
1290 | 2015-07-19 05:42 | 2015-07-19 05:42 | 13.8KV ROKAN FEEDER #2 | Fair | Animal | 10 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3084138 | 1 | 5:42 | Morning | Sunday | 2015 | 7
1291 | 2015-07-19 05:42 | 2015-07-21 09:42 | 13.8KV ROKAN FEEDER #2 | Fair | Animal | 10 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 104-105 R/F: 51N(@1). Patrolled the line & found, a dead Monkey under TP of Well Kopar #03. Cause: Animal. (Monkey). | 3084138 | 1 | 5:42 | Morning | Sunday | 2015 | 7
1292 | 2015-07-19 10:04 | 2015-07-19 10:04 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 0 | 10:04 It was reported b/o fuse for Tx at Well Pilar #01. (OBS well) 16:36 Checked & found, @2,@3 b/o 3.5SF fuses for 150Kva Tx at Well Pilar #01. Replaced fuse above with same size then energized the Tx. Cause: Animal. (Monkey) | 3084138 | 1 | 10:04 | Morning | Sunday | 2015 | 7
1293 | 2015-07-19 10:20 | 2015-07-19 10:20 | 13.8KV 8D FEEDER #7 | Fair | Transformer leakage | 67 | 8D fdr #7 Load dropped 7A (212-205A). It was reported manually shutdown Well #7E-94E. Cause: Transformer leakage. | 3084139 | 1 | 10:20 | Morning | Sunday | 2015 | 7
1294 | 2015-07-19 10:20 | 2015-07-20 12:30 | 13.8KV 8D FEEDER #7 | Fair | Transformer leakage | 67 | Replaced 300Kva Tx leakage with the same size & energized the Tx. Cause: Tx leakage. | 3084139 | 1 | 10:20 | Morning | Sunday | 2015 | 7
1295 | 2015-07-19 15:38 | 2015-07-19 15:38 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 83 | Bangko fdr #4 load drop 101A (230-129). Bangko GFPC T/R 1x. Not checked yet. | 3084138 | 1 | 15:38 | Afternoon | Sunday | 2015 | 7
1296 | 2015-07-19 15:38 | 2015-07-20 15:30 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 83 | Checked & found, Recl. 25Z-07 (Bangko #4) T/R 1x Ctr: 63-64. Also found, Bangko GFPC T/R 2x Ctr: 465-467 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 15:38 | Afternoon | Sunday | 2015 | 7
1297 | 2015-07-20 03:10 | 2015-07-20 03:10 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Broken Fuse Cut Out | 0 | 03:10 It was reported no power at Talang #74, #75, #76. 04:30 Checked & found, @1 b/o fuse & broken FCO for 50Kva Tx o/p #2DG-6. 10:30 Replaced FCO & fuses above with the same size, then energized the Tx. Cause: Broken Fuse Cut Out. (FCO) | 3084138 | 1 | 3:10 | Night | Monday | 2015 | 7
1298 | 2015-07-20 06:13 | 2015-07-20 06:13 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 9 | Sintong OCB fdr #2 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. | 3084138 | 1 | 6:13 | Morning | Monday | 2015 | 7
1299 | 2015-07-20 06:13 | 2015-07-22 10:13 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 9 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 394-395 R/F: 51N. Also found, Sintong GFPC T/R 2x Ctr: 779-781 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 6:13 | Morning | Monday | 2015 | 7
1300 | 2015-07-20 07:00 | 2015-07-20 07:00 | 13.8KV 8D FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 07:00 It was reported that b/o fuse for Tx at Well #8D-19N. 12:54 Checked & found, @1 b/o 15K fuse for 300Kva Tx at Well #8D-19N. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3084139 | 1 | 7:00 | Morning | Monday | 2015 | 7
1301 | 2015-07-20 13:25 | 2015-07-20 13:25 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Powerline - Jumper | 112 | 13:25 CKBS VCB fdr #1 T/R 1x. 13:27 CKBS VCB fdr #1 T/R 2x. 13:28 CKBS VCB fdr #1 T/R 2x. 13:29 CKBS VCB fdr #1 T/R 1x. 13:30 CKBS VCB fdr #1 T/R 1x. 13:31 CKBS VCB fdr #1 T/R 1x. 13:32 CKBS VCB fdr #1 T/R 1x. 13:33 CKBS VCB fdr #1 T/R 1x. 13:28 CKBS fdr #3 load dropped 13A (59-46A). 13:33 CKBS fdr #2 load dropped 246A (264-18A). T/O some WIPs at KB GS. 14:44 It was reported by Pumper that broken jumper of LBS #36CW-22. (near Well KB-36) 14:47 Manually open CKBS VCB #1. (from DSC) 14:52 Checked & found, @2 broken jumper of LBS #36CW-22. 15:00 Checked & found, CKBS VCB fdr #1 T/R 12x Ctr: 175-187 R/F: 51N & 51@1,@2. 15:21 Opened both side isolation switches of 13.8Kv VCB fdr #1. To dismantle @2 broken jumper of LBS #36CW-22. 16:35 Closed LBS #36CU-05. (CKBS fdr #1 fed by NKBS fdr #3) (NKBS fdr #3 Total load, 75A + 300A = 375A) Cause: Broken jumper of LBS #36CW-22. | 3084139 | 1 | 13:25 | Afternoon | Monday | 2015 | 7
1302 | 2015-07-21 06:27 | 2015-07-21 06:27 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Dead End Insulator | 0 | C.Duri ACB fdr #16 T/R 1x Ctr: 283-284 R/F: 51@1,@2. Not patrolled yet. | 3084138 | 1 | 6:27 | Morning | Tuesday | 2015 | 7
1303 | 2015-07-21 06:27 | 2015-07-23 16:27 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Dead End Insulator | 0 | Patrolled the line & found, @1 broken Dead end Insulator o/p #3H-03. Cause: Dead end Insulator. | 3084138 | 1 | 6:27 | Morning | Tuesday | 2015 | 7
1304 | 2015-07-21 07:34 | 2015-07-21 07:34 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Unidentified | 0 | C.Duri ACB fdr #11 T/R 1x Ctr: 251. (Did not change) R/F: 51@1 & 51N. C.Duri fdr #13 Load dropped 128A (140-12A). T/O Some Steam Unit at CSS-Area #6. Not patrolled yet. | 3084138 | 1 | 7:34 | Morning | Tuesday | 2015 | 7
1305 | 2015-07-21 07:34 | 2015-07-23 17:34 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 7:34 | Morning | Tuesday | 2015 | 7
1306 | 2015-07-21 08:41 | 2015-07-21 08:41 | 115KV KOTABATAK JUNCTION - LIBO LINE | Fair | Unidentified | 38 | 115Kv KBJ GCB #53 T/R 1x. 115Kv KBJ GCB #55 T/R 1x. (115Kv KBJ - Libo line) Not checked yet. | 3084138 | 1 | 8:41 | Morning | Tuesday | 2015 | 7
1307 | 2015-07-21 08:41 | 2015-07-24 10:21 | 115KV KOTABATAK JUNCTION - LIBO LINE | Fair | Unidentified | 38 | Checked & found: 115KV KBJ GCB #53 T/R 1x Ctr: 207-208 115KV KBJ GCB #55 T/R 1x Ctr: 304-305 R/F: 67N (Instan) & 21@1-G (Z-1). Patrolled the line from KBJ toward Pole #KW-21, but found nothing. Completed patrolling the line from Pole #KW-21 toward Libo Substation, but found nothing. Cause: Unidentified. | 3084138 | 1 | 8:41 | Morning | Tuesday | 2015 | 7
1308 | 2015-07-21 10:16 | 2015-07-21 10:16 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Animal | 0 | 10:16 It was reported that b/o fuse for Tx o/p #04-02-12B. Checked & found, @1, @2 b/o 2.1SF fuses for 112.5Kva Tx o/p #04-02-12B. 14:46 Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Civet) | 3084138 | 1 | 10:16 | Morning | Tuesday | 2015 | 7
1309 | 2015-07-21 10:17 | 2015-07-21 10:17 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 11 | 10:17 It was reported that b/o fuse for Tx o/p #09-N4-09. Checked & found, @1, @2 b/o 2.1SF fuses for 112.5Kva Tx o/p #09-N4-09. 11:48 Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3084138 | 1 | 10:17 | Morning | Tuesday | 2015 | 7
1310 | 2015-07-21 15:36 | 2015-07-21 15:36 | 13.8KV BEKASAP FEEDER #2 | Heavy Rain | Lightning | 181 | 15:36 Bekasap fdr #2 load dropped 63A (140-77A). 18:35 Checked & found, Recl. 37BD-12 (Bekasap fdr #2) T/SO. Ctr: 169-170. Blocked & Closed Recl. 37BD-12, Ok. Then released the block. The line is not patrolled yet. | 3084138 | 1 | 15:36 | Afternoon | Tuesday | 2015 | 7
1311 | 2015-07-21 15:36 | 2015-07-23 15:36 | 13.8KV BEKASAP FEEDER #2 | Heavy Rain | Lightning | 181 | Patrolled the line & found, @1 broken L/A on TP of Well Bekasap #21. Cause: Lightning. | 3084138 | 1 | 15:36 | Afternoon | Tuesday | 2015 | 7
1312 | 2015-07-21 16:37 | 2015-07-21 16:37 | CENTRAL DURI POWER PLANT | Heavy Rain | Equipment Failure | - | 16:37 CGT #4 Tripped open by Alarm: DC Ground & CO2 released. 16:50 Closed C.Duri ACB #39. (Tie breaker) Cause: Equipment failure. (Found, DC Ground at 45FT-2) (Due to Fire detector cable broken & shortcircuit when Rain) 23-July-2015 14:30 S/U CGT #4, then On line the Unit at 15:20. 15:21 Opened C.Duri ACB #39. (Tie Breaker) (After replacing broken Fire detector cable) |  | 1 | 16:37 | Afternoon | Tuesday | 2015 | 7
1313 | 2015-07-21 18:20 | 2015-07-21 18:20 | DURI POWER PLANT |  |  | - | 18:20 S/U DGT #7, then on line the Unit at 18:43. |  | 1 | 18:20 | Afternoon | Tuesday | 2015 | 7
1314 | 2015-07-22 07:14 | 2015-07-22 07:14 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 119 | So.Balam VCB fdr #4 T/R 1x. Not checked yet. | 3084138 | 1 | 7:14 | Morning | Wednesday | 2015 | 7
1315 | 2015-07-22 07:14 | 2015-07-24 11:14 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 119 | Checked & found, So.Balam VCB fdr #4 T/R 1x Ctr: 280-281 R/F: 51N. Also found So.Balam GFPC T/R 1x Ctr: 193-194. Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 7:14 | Morning | Wednesday | 2015 | 7
1316 | 2015-07-22 07:14 | 2015-07-22 07:14 | 13.8KV S. BALAM FEEDER #1 | Cloudy | Unidentified | 73 | So.Balam fdr #1 load dropped 70A (101-31A). Not checked yet. | 3084138 | 1 | 7:14 | Morning | Wednesday | 2015 | 7
1317 | 2015-07-22 07:14 | 2015-07-24 09:30 | 13.8KV S. BALAM FEEDER #1 | Cloudy | Unidentified | 73 | Checked & found, Recl. 16Z-25 (So.Balam fdr #1) T/R 1x Ctr: 20. (Did not change) Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 7:14 | Morning | Wednesday | 2015 | 7
1318 | 2015-07-22 12:38 | 2015-07-22 12:38 | 115KV DURI - KOTABATAK JUNCTION LINE | Fair | Unidentified | 0 | 115Kv KBJ GCB #43 T/R 1x. 115Kv KBJ GCB #45 T/R 1x. 115Kv DRB OCB #26 T/R 1x. Ctr: 98-99. 115Kv DRB OCB #28. T/R 1x. Ctr: 114-115 R/F: 87L (@3-G). (115 KV KBJ - DRB line). Not checked yet. | 3084138 | 1 | 12:38 | Afternoon | Wednesday | 2015 | 7
1319 | 2015-07-22 12:38 | 2015-07-24 10:38 | 115KV DURI - KOTABATAK JUNCTION LINE | Fair | Unidentified | 0 | Checked & found: 115Kv KBJ GCB #43 T/R 1x Ctr: 405-406. 115Kv KBJ GCB #45 T/R 1x Ctr: 295-296 R/F: 87L(@3-G). 115Kv DRB OCB #26 T/R 1x. Ctr: 98-99. 115Kv DRB OCB #28. T/R 1x. Ctr: 114-115 R/F: 87L (@3-G). (115 KV KBJ - DRB line). Patrolled the line from KBJ toward Simpang Belutu (Pole #DK-161), but found nothing. (Line Simpang Belutu (Pole #DK-161) toward Duri Ring Bus, is not patrolled yet. Cause: Patrolled the line is not completed yet. (w/O TDO North & Libo Team to completed patrolling the line) | 3084138 | 1 | 12:38 | Afternoon | Wednesday | 2015 | 7
1320 | 2015-07-22 12:38 | 2015-07-28 14:38 | 115KV DURI - KOTABATAK JUNCTION LINE | Fair | Unidentified | 0 | Completed patrolling the line from pole #DK-174 toward Duri Ring Bus & found: - High Trees under line near pole #DK–56. -@3 Flashed over Dead end Insulator o/p #DK–11. -@3 Flashed over Dead end Insulator o/p #DK–41. -@3 Flashed over Dead end Insulator o/p #DK–48. -@3 Flashed over Dead end Insulator o/p #DK–54. Cause: Suspected by Tree. | 3084138 | 1 | 12:38 | Afternoon | Wednesday | 2015 | 7
1321 | 2015-07-22 15:16 | 2015-07-22 15:16 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 15:16 It was reported b/o fuse for Tx o/p #04-07-17. Not checked yet. | 3084138 | 1 | 15:16 | Afternoon | Wednesday | 2015 | 7
1322 | 2015-07-22 15:16 | 2015-07-23 09:45 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 09:45 Checked & found @1 b/o fuse for 112.5 Kva Tx o/p #04-07-17. Perform TTR & Megger --> Good. Replaced b/o fuse above with the same size & energize the Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 15:16 | Afternoon | Wednesday | 2015 | 7
1323 | 2015-07-22 19:48 | 2015-07-22 19:48 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 10 | It was reported b/o fuse for Tx o/p #08-L7-20. Not checked yet. | 3084138 | 1 | 19:48 | Night | Wednesday | 2015 | 7
1324 | 2015-07-22 19:48 | 2015-07-23 10:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 10 | Checked & found, @1 b/o 2.1SF fuse for 112.5Kva Tx o/p #08-L7-20. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 19:48 | Night | Wednesday | 2015 | 7
1325 | 2015-07-22 21:14 | 2015-07-22 21:14 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified (Fuse) | 1 | It was reported b/o fuse for Tx at Well Pematang #74. Not checked yet. | 3084138 | 1 | 21:14 | Night | Wednesday | 2015 | 7
1326 | 2015-07-22 21:14 | 2015-07-23 14:00 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified (Fuse) | 1 | Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Pematang #74. Perform TTR & Megger the Tx, found good reading. Replaced b/o fuse above with the same size, then energized Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 21:14 | Night | Wednesday | 2015 | 7
1327 | 2015-07-23 09:26 | 2015-07-23 09:26 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Unidentified (Fuse) | 0 | 09:26 It was reported that b/o fuse for Tx o/p #13-F1-05. 11:07 Checked & found, @3 b/o 2.1SF fuse for 112.5Kva Tx o/p #13-F1-05. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3084138 | 1 | 9:26 | Morning | Thursday | 2015 | 7
1328 | 2015-07-23 14:30 | 2015-07-23 14:30 | CENTRAL DURI POWER PLANT |  |  | - | 14:30 S/U CGT #4, then On line the Unit at 15:20. (After replacing broken fire detector cable) 15:21 Opened C.Duri ACB #39. (Tie Breaker) (See report 21-July-2015 at 16:37) |  | 1 | 14:30 | Afternoon | Thursday | 2015 | 7
1329 | 2015-07-23 16:07 | 2015-07-23 16:07 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | 0 | 16:07 It was reported that b/o fuse for Tx o/p #05-P1-06. 17:44 Checked & found, @3 b/o 2.1SF fuse for 112.5Kva Tx o/p #05-P1-06. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3084138 | 1 | 16:07 | Afternoon | Thursday | 2015 | 7
1330 | 2015-07-23 18:07 | 2015-07-23 18:07 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Dead End Insulator | 0 | C.Duri fdr #1 load dropped 50A (222-172A). It was reported that outage at Puncak-GS. Not checked yet. | 3084138 | 1 | 18:07 | Afternoon | Thursday | 2015 | 7
1331 | 2015-07-23 18:07 | 2015-07-24 15:07 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Dead End Insulator | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 2x Ctr: 192-194. Patrolled the line & found: -@1 Broken Dead end Insulators o/p #40AW-20 & #39AV-29. -@1 Broken Pin Insulator o/p #40AW-16. Cause: Dead end Insulator. | 3084138 | 1 | 18:07 | Afternoon | Thursday | 2015 | 7
1332 | 2015-07-24 02:41 | 2015-07-24 02:41 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 60 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3084139 | 1 | 2:41 | Night | Friday | 2015 | 7
1333 | 2015-07-24 02:41 | 2015-07-26 07:41 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 60 | Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1245-1246 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3084139 | 1 | 2:41 | Night | Friday | 2015 | 7
1334 | 2015-07-24 15:28 | 2015-07-24 15:28 | 13.8KV BATANG FEEDER #3 | Cloudy and Lightning | Lightning | 45 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3084138 | 1 | 15:28 | Afternoon | Friday | 2015 | 7
1335 | 2015-07-24 15:28 | 2015-07-28 15:00 | 13.8KV BATANG FEEDER #3 | Cloudy and Lightning | Lightning | 45 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 271-272 R/F: 51N. Batang GFPC in Bypassed. (control problem) Patrolled the line & found, @1 broken L/A o/p #40AK-08. Cause: Lightning. | 3084138 | 1 | 15:28 | Afternoon | Friday | 2015 | 7
1336 | 2015-07-25 08:05 | 2015-07-25 08:05 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 08:05 It was reported b/o fuse for Tx o/p #03-3-21. (C.Duri fdr #7) 10:45 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-3-21. Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 8:05 | Morning | Saturday | 2015 | 7
1337 | 2015-07-25 09:00 | 2015-07-25 09:00 | DURI POWER PLANT |  |  | - | 09:00 Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 9:00 | Morning | Saturday | 2015 | 7
1338 | 2015-07-25 09:25 | 2015-07-25 09:25 | 13.8KV DURI FIELD FEEDER #4 | Fair | Pin Insulator | 37 | 09:25 It was reported No power at Gabus Building. (D.Field RTU Failed at the time). 09:47 Checked & found, D.Field ACB fdr #4 T/LO. Ctr: 437-441 R/F: 51@2. Patrolled the line & found, @1 Broken Pin Insulator o/p #07-V1-06. 09:54 Blocked & Closed D.Filed ACB fdr #4, Ok. Then release the block. Cause: Pin Insulator. | 3084138 | 1 | 9:25 | Morning | Saturday | 2015 | 7
1339 | 2015-07-25 11:45 | 2015-07-25 11:45 | MINAS POWER PLANT |  | Unidentified | - | MGT #7 Tripped by Alarm: Aux. Hydraulic Oil Pump Running. Frequency system dropped to 59:.90Hz. (No Load Shedding) Cause: Under Investigation. 26-July-2015. 13:23 S/U MGT #7, then online the Unit at 14:41. (After resetting the Alarm & back to normal) Cause: Unidentified. |  | 1 | 11:45 | Morning | Saturday | 2015 | 7
1340 | 2015-07-26 06:22 | 2015-07-26 06:22 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 72 | Sintong OCB fdr #1 T/R 1x Ctr: 359-360 R/F: 51@1. Also found, Sintong GFPC T/R 2x Ctr: 783-785 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3084138 | 1 | 6:22 | Morning | Sunday | 2015 | 7
1341 | 2015-07-26 13:23 | 2015-07-26 13:23 | MINAS POWER PLANT |  |  | - | 13:23 S/U MGT #7, then on line the Unit at 14:41. (See report 25 July 2015 at 11:45) |  | 1 | 13:23 | Afternoon | Sunday | 2015 | 7
1342 | 2015-07-27 08:51 | 2015-07-27 08:51 | CENTRAL DURI POWER PLANT |  |  | - | 08:51 Off line CGT #1, then S/D for Dismantling Spool Flow meter. 10:08 S/U CGT #1, then on line the Unit at 10:25. |  | 1 | 8:51 | Morning | Monday | 2015 | 7
1343 | 2015-07-27 21:50 | 2015-07-27 21:50 | 13.8KV BANGKO FEEDER #1 | Fair | Unidentified (Fuse) | 1 | It was reported b/o fuse for Tx at Well Bangko #311. (Bangko fdr #1) Not checked yet. | 3084138 | 1 | 21:50 | Night | Monday | 2015 | 7
1344 | 2015-07-27 21:50 | 2015-07-28 09:59 | 13.8KV BANGKO FEEDER #1 | Fair | Unidentified (Fuse) | 1 | Checked & found, @2 b/o 3.5SF fuse for 150Kva Tx at Well Bangko #311. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 21:50 | Night | Monday | 2015 | 7
1345 | 2015-07-28 04:13 | 2015-07-28 04:13 | CENTRAL DURI POWER PLANT |  |  | - | 04:13 Off line CGT #1, then S/D the Unit for S/B. (Prior to Repairing HRSG Diverter Gear box crack) 04:19 Close ACB #39. (Tie Breaker) 09:43 S/U CGT #1, then on line the Unit at 10:00. 09:58 Opened ACB #39. (Tie Breaker) (After repairing the Cracking HRSG diverter Gear box) | 123 | 1 | 4:13 | Morning | Tuesday | 2015 | 7
1346 | 2015-07-28 14:40 | 2015-07-28 14:40 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 14:40 It was reported b/o fuse for Tx o/p #03-3-03. (C.Duri fdr #7) 17:30 Checked & found, @1,@2,@3 b/o fuses for 112.5Kva Tx o/p #03-3-03. Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3084138 | 1 | 14:40 | Afternoon | Tuesday | 2015 | 7
1347 | 2015-07-29 07:22 | 2015-07-29 07:22 | 13.8KV 3D FEEDER #8 | Foggy and Smoke | Lightning Arrester | 0 | 3D OCB fdr #8 T/R 1x. 3D fdr #7 dropped 35A (165-130A). (Ground fault alarm from 3D fdr #8). Not checked yet. | 3084139 | 1 | 7:22 | Morning | Wednesday | 2015 | 7
1348 | 2015-07-29 07:22 | 2015-07-31 13:22 | 13.8KV 3D FEEDER #8 | Foggy and Smoke | Lightning Arrester | 0 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 165-166 R/F: 51@1. Also found, 3D GFPC-TX #2 T/R 1x Ctr: 597-598. Patrolled the line & found, @1 broken L/A o/p #3E-42. Cause: Lightning Arrester. | 3084139 | 1 | 7:22 | Morning | Wednesday | 2015 | 7
1349 | 2015-07-29 16:57 | 2015-07-29 16:57 | 13.8KV 6D FEEDER #3 | Heavy Rain | Unidentified | 108 | 6D OCB fdr #3 T/R 1x. 6D fdr #1 dropped 282A (355-73A). 6D fdr #2 dropped 150A (190-40A). Not checked yet. | 3084139 | 1 | 16:57 | Afternoon | Wednesday | 2015 | 7
1350 | 2015-07-29 16:57 | 2015-07-31 13:57 | 13.8KV 6D FEEDER #3 | Heavy Rain | Unidentified | 108 | Checked & found, 6D OCB fdr #3 T/R 1x Ctr: 211-212 R/F: 51@1,@2. Patrolled the line, but found nithing. Cause: Unidentified. | 3084139 | 1 | 16:57 | Afternoon | Wednesday | 2015 | 7
1351 | 2015-07-30 23:59 | 2015-07-30 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power System normal Condition. |  | 1 | 23:59 | Night | Thursday | 2015 | 7
1352 | 2015-07-31 10:28 | 2015-07-31 10:28 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified | 80 | 10:28 CKBS fdr #6 load dropped 188A (246-58A). (When switching to transfer part load of CKB fdr #5 to CKB fdr #6 by opening LBS #34CT-58) 10:40 Checked & found, Recl. 34CU-34 (CKBS fdr #6) T/R 1x Ctr: Not reported yet. (Suspected over load setting of the Recloser was near the maximum setting) Not checked & patrolled yet. | 3084139 | 1 | 10:28 | Morning | Friday | 2015 | 7
1353 | 2015-07-31 10:28 | 2015-01-08 16:28 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified | 80 | Checked & found, Recl. 34CU-34 (CKBS fdr #6) T/R 1x Ctr: 18-19. Patrolled the line, but found nothing. Cause: Unidentified. | 3084139 | 1 | 10:28 | Morning | Friday | 2015 | 7
1354 | 2015-07-31 16:43 | 2015-07-31 16:43 | 13.8KV CENTRAL DURI FEEDER #3 | Cloudy and Lightning | Lightning | 0 | C.Duri ACB fdr #3 T/R 1x Ctr: 181-182 R/F: 51@2,@3. Not patrolled yet. | 3084138 | 1 | 16:43 | Afternoon | Friday | 2015 | 7
1355 | 2015-07-31 16:43 | 2015-03-08 15:43 | 13.8KV CENTRAL DURI FEEDER #3 | Cloudy and Lightning | Lightning | 0 | Patrolled the line & found: -@1,@3 Broken Pin Insulators o/p #03-08-13. -@1 Broken Pin Insulator o/p #NN. (Near Well #5R-81B) Cause: Lightning. | 3084138 | 1 | 16:43 | Afternoon | Friday | 2015 | 7
1356 | 2015-07-31 18:10 | 2015-07-31 18:10 | MINAS POWER PLANT |  | Under investigation | - | 18:10 MGT #5 Tripped by Alarm: High vibration. Frequency dropped to 59.95Hz. (No load shedding) Cause: Under Investigation. | 123 | 1 | 18:10 | Afternoon | Friday | 2015 | 7
1357 | 2015-07-31 18:44 | 2015-07-31 18:44 | MINAS POWER PLANT |  |  | - | 18:44 S/U MGT #4, then on line the Unit at 19:00. |  | 1 | 18:44 | Afternoon | Friday | 2015 | 7
1358 | 2015-01-08 07:27 | 2015-01-08 07:27 | 13.8KV CENTRAL DURI FEEDER #9 | Cloudy | Lightning | 0 | C.Duri ACB fdr #9 T/R 3x Ctr: 338-341 R/F: 50@1,@2 The line is not patrolled yet. | 3097797 | 1 | 7:27 | Morning | Thursday | 2015 | 1
1359 | 2015-01-08 07:27 | 2015-03-08 15:27 | 13.8KV CENTRAL DURI FEEDER #9 | Cloudy | Lightning | 0 | Patrolled the line & found: -@3 Flashed over Dead end Insulator o/p #04-7-33. -@2 Flashed over Dead end Insulator o/p #04-7-27. -@1 Flashed over Dead end Insulator o/p #04-7-20. -@1,@3 Flashed over Dead end Insulators o/p #04-7-10. -@1,@3 Flashed over Dead end Insulators o/p #04-7-04. Cause: Lightning. | 3097797 | 1 | 7:27 | Morning | Thursday | 2015 | 1
1360 | 2015-01-08 15:15 | 2015-01-08 15:15 | DURI POWER PLANT |  |  | - | 15:15 S/U DGT #7, then Online at 16:05. (After combustion inspection program) | 123 | 1 | 15:15 | Afternoon | Thursday | 2015 | 1
1361 | 2015-01-08 20:10 | 2015-01-08 20:10 | 13.8KV BANGKO FEEDER #1 | Fair | Transformer Failure | 22 | 20:10 It was reported b/o fuse for Tx at Well Bangko #155. (Nella fdr #1) 21:10 Checked & found, @1, @3 b/o 2.1SF fuses for 100Kva Tx at Well Bangko #155. Perform TTR, Meger test the Tx & found, zero mega-ohm reading Tx. Cause: Transformer failure. (Would be replaced tomorrow) | 3097797 | 1 | 20:10 | Night | Thursday | 2015 | 1
1362 | 2015-01-08 20:10 | 2015-02-08 09:58 | 13.8KV BANGKO FEEDER #1 | Fair | Transformer Failure | 22 | Replaced the failure 100Kva Tx with 300Kva Tx, then energized the Tx at Well BKO #155. Cause: Transformer Failure. | 3097797 | 1 | 20:10 | Night | Thursday | 2015 | 1
1363 | 2015-01-08 21:59 | 2015-01-08 21:59 | CENTRAL DURI POWER PLANT |  |  | - | 01-Aug-2015. 21:59 Off line CGT #3, then S/D the unit for S/B. (Prior to repairing the leaking of Atomizing Head exchanger) 08-Aug-2015. 14:44 S/U CGT #3, then on line the Unit at 15:10. (After repairing the leaking of Atomazing Head Exchanger) |  | 1 | 21:59 | Night | Thursday | 2015 | 1
1364 | 2015-02-08 17:46 | 2015-02-08 17:46 | 13.8KV LIBO FEEDER #1 | Fair | Lightning Arrester | 21 | Libo OCB fdr #1 T/R 1x. Not checked yet. | 3097797 | 1 | 17:46 | Afternoon | Sunday | 2015 | 2
1365 | 2015-02-08 17:46 | 2015-03-08 15:46 | 13.8KV LIBO FEEDER #1 | Fair | Lightning Arrester | 21 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 348-349 R/F: 51N(@3). Patrolled the line & found, @3 broken L/A on TP of Well S.E Libo #09. Cause: Lightning Arrester. | 3097797 | 1 | 17:46 | Afternoon | Sunday | 2015 | 2
1366 | 2015-02-08 22:22 | 2015-02-08 22:22 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 22:22 It was reported b/o fuse for Tx at Well Benar #14. (Bangko fdr #4) 23:25 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Benar #14. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3097797 | 1 | 22:22 | Night | Sunday | 2015 | 2
1367 | 2015-03-08 11:52 | 2015-03-08 11:52 | 13.8KV BATANG FEEDER #2 | Fair | Pin Insulator | 0 | Batang OCB fdr #2 T/R 1x. Not checked yet. | 3097797 | 1 | 11:52 | Morning | Sunday | 2015 | 3
1368 | 2015-03-08 11:52 | 2015-04-08 14:52 | 13.8KV BATANG FEEDER #2 | Fair | Pin Insulator | 0 | Checked & found, Batang OCB fdr #2 T/R 1x Ctr: 99-100 R/F: 51N(1). Patrolled the line & found, @1 broken Pin Insulator o/p #35AE-20. Cause: Pin Insulator. | 3097797 | 1 | 11:52 | Morning | Sunday | 2015 | 3
1369 | 2015-03-08 15:30 | 2015-03-08 15:30 | 13.8KV 8D FEEDER #10 | Fair | Transformer Failure | 20 | 15:30 It was reported b/o fuse for Tx at Well #7E-84N. (8D fdr #10) 19:00 Checked & found, @2,@3 b/o 14.0SF fuses for 550Kva Tx at Well #7E-84N. Perform TTR, megger test the Tx & found, Low megger reading. Cause: Transformer failure. (The Tx failure is not replaced yet, w/o Standby Tx from Duri) | 3097798 | 1 | 15:30 | Afternoon | Sunday | 2015 | 3
1370 | 2015-03-08 15:30 | 2015-12-08 14:00 | 13.8KV 8D FEEDER #10 | Fair | Transformer Failure | 20 | Replaced 550Kva Tx failure with the same size & energized the Tx at Well #7E-84N. Cause: Transformer failure. | 3097798 | 1 | 15:30 | Afternoon | Sunday | 2015 | 3
1371 | 2015-04-08 23:59 | 2015-04-08 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI POWER SYSTEM NORMAL CONDITION. |  | 1 | 23:59 | Night | Wednesday | 2015 | 4
1372 | 2015-05-08 11:38 | 2015-05-08 11:38 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Accident | 322 | 11:38 C.Duri ACB fdr #8 T/LO. Ctr: 297. (not change) R/F: 51N(@1). 11:51 Blocked & closed C.Duri ACB fdr #8, but tripped again. 12:58 Patrolled & found, @1 Pin Insulator pulled out & Conductor touched cross arm o/p #04-02-21. (d/s of Recl. 04-02-22), but the Recloser problem. (Did not Trip) 13:03 Manually Opened Recl. 04-02-22. (to isolate the fault above) 13:05 Blocked & closed C.Duri ACB fdr #8, but tripped again. 13:30 Opened Yellow Switch of Recl. 04-02-22. 13:33 Blocked & closed C.Duri ACB fdr #8, Ok. Then released the block. (1 Road under Recl. 04-2-22 is still off) 13:45 It was reported that Boom Crane of PT. ADK (8x351) touched the powerline, & cause Pin Insulator pulled out, also Conductor touched to cross arm. (No injury to this case) 15:15 Repaired Pin Insulator & Conductor above (for temporary) o/p #04-2-21. 15:17 Transfered load under Recl. 04-02-22 (C.Duri fdr #8) to C.Duri fdr #9, By closing LBS o/p #04-2-02. Cause: Accident. (Recl. 04-02-22 & the conductor would be replaced & repairing tomorrow) | 3097797 | 1 | 11:38 | Morning | Friday | 2015 | 5
1373 | 2015-05-08 12:39 | 2015-05-08 12:39 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified (Fuse) | 0 | 12:39 It was reported b/o fuse for Tx o/p #13-F6-17. (N.Duri fdr #11) 17:21 Checked & found, @1 b/o 2.1SF fuse for 112.5Kva Tx o/p #13-F6-17. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3097797 | 1 | 12:39 | Afternoon | Friday | 2015 | 5
1374 | 2015-05-08 14:46 | 2015-05-08 14:46 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 3 | 14:46 It was reported b/o fuse for Tx o/p #06-Q3-03. (C.Duri fdr #15) 16:34 Checked & found, @1 b/o 2.1SF fuse for 112.5Kva Tx o/p #06-Q3-03. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Monkey) | 3097797 | 1 | 14:46 | Afternoon | Friday | 2015 | 5
1375 | 2015-05-08 22:37 | 2015-05-08 22:37 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Dead End Insulator | 0 | C.Duri fdr #1 Load dropped 50A (217-167A). Not checked yet. | 3097797 | 1 | 22:37 | Night | Friday | 2015 | 5
1376 | 2015-05-08 22:37 | 2015-07-08 13:37 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Dead End Insulator | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 194-195. Patrolled the line & found, @1 flashed over Dead end Insulator o/p #40AW-16. Cause: Dead end Insulator. | 3097797 | 1 | 22:37 | Night | Friday | 2015 | 5
1377 | 2015-06-08 10:45 | 2015-06-08 10:45 | 13.8KV PUNGUT FEEDER #2 | Fair | Animal | 134 | 10:45 It was reported b/o fuse for Tx at Well Tandun #07. (Pungut fdr #2) 15:57 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Tandun #07. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Monkey) | 3097797 | 1 | 10:45 | Morning | Monday | 2015 | 6
1378 | 2015-06-08 17:05 | 2015-06-08 17:05 | 13.8KV BATANG FEEDER #2 | Cloudy | Powerline - Conductor | 372 | 17:05 It was reported no power at Rantau Bais field & Batang RTU failed at this time. 20:07 Checked & found, Batang OCB fdr #2 T/LO. Ctr: 100-104 R/F: 50/51N & 51@1,@2. 20:30 Patrolled the line & found, @2 broken conductor o/p #36AH-09. (It is late to restore the load feeder due to Traffic Jammed for cementing this main Road) 00:23 Opened both side isolation switches of Batang OCB fdr #2 & Install personal ground. 01:32 Repaired broken conductor. 02:14 Opened personal ground and closed isolation switches of Batang OCB fdr #2. 02:20 Blocked & closed, Batang OCB fdr #2, Ok. Then normalized the block. 02:24 Batang Substation RTU back to normal. Cause: Broken Conductor. | 3097797 | 1 | 17:05 | Afternoon | Monday | 2015 | 6
1379 | 2015-07-08 11:01 | 2015-07-08 11:01 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 82 | 11:01 Bangko OCB fdr #4 T/O. (In block position for Rig ACS-10 Job) Bangko fdr #1 load dropped 55A (268-213A). 11:07 Closed Bangko OCB fdr #4, Ok. (After got clearance from Rig ACS-10) Not checked & patrolled yet. | 3097797 | 1 | 11:01 | Morning | Wednesday | 2015 | 7
1380 | 2015-07-08 11:01 | 2015-08-08 10:00 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 82 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99967-99968 R/F: 51@3. Patrolled the line, btu found nothing. Cause: Unidentified. | 3097797 | 1 | 11:01 | Morning | Wednesday | 2015 | 7
1381 | 2015-07-08 16:08 | 2015-07-08 16:08 | 13.8KV DURI FIELD FEEDER #4 | Fair | Main breaker | 2 | 16:08 It was reported b/o fuse for Tx o/p #07-V5-03. (Duri Field fdr #4) 18:35 Checked & found, @1 b/o 2.1SF fuse for 112.5Kva Tx o/p #07-V5-03. (also found short circuit at Main Breaker) (The Tx is not energized yet, waiting of electrician to replace main Breaker) Cause: Main Breaker. | 3097797 | 1 | 16:08 | Afternoon | Wednesday | 2015 | 7
1382 | 2015-07-08 16:08 | 2015-09-08 13:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Main breaker | 2 | Energized 112.5Kva Tx o/p #07-V5-03, after Electrician C/O Main Breaker. Cause: Main Breaker. | 3097797 | 1 | 16:08 | Afternoon | Wednesday | 2015 | 7
1383 | 2015-08-08 11:30 | 2015-08-08 11:30 | 13.8KV BEKASAP FEEDER #2 | Fair | Low mega-ohm reading | 72 | 11:30 It was reported b/o fuse for Tx at Well Bekasap #89. (Bekasap fdr #2) 13:30 Checked & found, @1, @3 b/o 3.5SF fuses for 150Kva Tx at Well Bekasap #89. Perform TTR & Megger Test, found Low Mega-ohm Reading Tx. Cause: Low Mega-ohm Reading Tx. (The Tx will be replace tomorrow). | 3097797 | 1 | 11:30 | Morning | Saturday | 2015 | 8
1384 | 2015-08-08 11:30 | 2015-02-09 15:15 | 13.8KV BEKASAP FEEDER #2 | Fair | Low mega-ohm reading | 72 | Replaced 150Kva with 100Kva Tx then energized the Tx at Well Bekasap #89 (Bekasap fdr #2). Cause: Low Mega-ohm reading Tx. | 3097797 | 1 | 11:30 | Morning | Saturday | 2015 | 8
1385 | 2015-08-08 12:57 | 2015-08-08 12:57 | CENTRAL DURI SWITCH YARD | Fair | Equipment Failure | 124 | 12:57 115KV C.Duri SWY GCB #41 T/O. Ctr: Not checked yet. 115KV C.Duri SWY GCB #43 T/O. Ctr: Not checked yet. 13.8KV C.Duri SWG ACB #34 T/O. Ctr: Not checked yet. R/F: 51@1,@2, 87T-3(@1,@2) & 86T-3. (C.Duri power TX-3 de-energized) (When Closing Generator Breaker ACB #36 of CGT #3 & C.Duri Buss-3 Islanding fed by CGT #3) Respectively Load dropped: Pematang fdr #1 Load dropped 151A (163-12A). Pematang fdr #2 Load dropped 58A (59-1A). Petani fdr #1 Load dropped 186A (200-14A). Petani fdr #2 Load dropped 66A (68-2A). Rangau RTU failed . 13:20 Open Generator Breaker ACB #36 of CGT #3. (C.Duri Buss-3 no Power) 13:21 Closed Tie Breaker ACB #39. (to Energize C.Duri Buss-3) 15:00 Visual Checked Tx-3 C.Duri, found Normal condition. 15:02 Closed 115KV GCB #41 (to energize C.Duri power TX-3) 15:03 Closed 115KV GCB #43. 15:04 Closed 13.8KV ACB #34. (C.Duri Buss-3 paralled to the system) 15:09 Closed Generator Breaker ACB #36 of CGT #3 on line to the system. 15:10 Opened Tie breaker ACB #39. Cause: Equipment Failure. (Auto Synchronizing Relay problem) | 3097797 | 1 | 12:57 | Afternoon | Saturday | 2015 | 8
1386 | 2015-08-08 13:04 | 2015-08-08 13:04 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Recloser | 1821 | 13:04 C.Duri ACB fdr #5 T/LO. Ctr: 439-442 R/F: 51N. 14:07 Bloked & Closed C.Duri ACB fdr #5, but trip again. (by the same R/F) 15:30 Opened Recl. 03-4-16 to separate load. (D/S C.Duri fdr #5) 15:35 Blocked & closed C.Duri ACB fdr #5, but trip again. (by the same R/F) (The team changes focused to restoring C.Duri ACB fdr #7) 16:35 Checked & found, Recl. 03-6-03 in open position & Recloser oil leaks) (Load of Recl. 03-6-03 was transfered to C.duri fdr #7) (Recl. 03-6-03 was manually opened, but all jumpers & visual opening are still connected) (Source side of the Recloser is still connect to C.Duri fdr #5 & Load side connect to C.Duri fdr #7) 16:52 Blocked & closed C.Duri fdr #5, Ok. Then release the block. (After isolating Recl. 03-6-03 by open jumpers & Disconnecting Switches) 18:20 Blocked & closed Recl. 03-4-16 (C.Duri fdr #5), but Tripped again. 18:41 Patrolled the line & found @2 broken L/A & jumper touching to cross arm o/p #03-4-39. 19:05 Then isolated @2 Broken L/A & the jumper. 19:15 Blocked & closed Recl. 03-4-16, Ok. Then release the block. (Power to CGS #3 from CD fdr #5 back to normal). Cause: Recloser Failure & broken L/A arrester. | 3097797 | 1 | 13:04 | Afternoon | Saturday | 2015 | 8
1387 | 2015-08-08 13:11 | 2015-08-08 13:11 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Recloser | 0 | 13:11 C.Duri ACB fdr #7 T/LO. Ctr: 220-224 R/F: 51N. 14:08 Bloked & Closed C.Duri ACB fdr #7, but trip again. 15:55 Opened LBS #03-7-25 Main line. (D/S of C.Duri fdr #7) 15:58 Blocked & closed C.Duri ACB fdr #7, Ok. Then re-open C.Duri ACB fdr #7. 16:10 To Close LBS #03-7-25. Opened LBS #03-3-44 & LBS #03-6-29 to separate load. 16:15 Blocked & closed C.Duri ACB fdr #7, Ok. 16:19 Manual open C.Duri fdr #4, then closed at 17:25. (Req. by CGS-3, to anticipate Spill) 16:20 Opened C.Duri ACB fdr #7, then closed LBS #03-6-29. 16:21 Blocked & closed C.Duri ACB fdr #7, but trip again. 16:25 Opened LBS #03-6-29, then Blocked & closed C.Duri fdr #7, Ok. 16:35 Checked & found, Recl. 03-6-03 failure. (found oil leaks) (Recl. 03-6-03 was manually opened, but all jumpers & visual opening are still connected) (Source side of the Recloser is still connect to C.Duri fdr #5 & Load side connect to C.Duri fdr #7) 16:36 Closed LBS #03-6-29, then Blocked & closed C.Duri ACB fdr #7, Ok. (After isolated Recl. 03-6-03 by opening Recloser Jumpers & Visual opening) 16:42 Closed LBS #03-4-43 to feed power to CGS#3 from C.Duri fdr #7. 16:54 C.Duri ACB fdr #7 Tripped again. 17:05 Then Re-open LBS #03-6-29, then Blocked & closed C.Duri ACB fdr #7, Ok. 17:27 C.Duri ACB fdr #7 T/LO again. 17:49 Re-open LBS #03-4-43, then Blocked & closed C.Duri ACB fdr #7, Ok. (Power to CGS #3 feed from C.Duri fdr #7 & back to normal operation) 09-AUG-2015 Focused to restoring load at Road-06 Area-03. 00:20 Closed LBS #03-5-03, then opened LBS #03-5-27 at 01:59. 00:31 Closed LBS #03-3-02, then opened Recl. 03-3-42 at 02:08. 00:50 Closed LBS 03-1-02, then opened Recl. 03-1-09 at 02:17. 00:58 Closed LBS 03-7-03, then opened Recl. 03-7-24 at 01:49. (All load d/s C.Duri fdr #7 transferred to C.Duri fdr #6 & C.Duri fdr #5) 01:27 Opened C.Duri ACB fdr #7, to Close LBS #03-6-29. 01:34 Blocked & closed C.Duri ACB fdr #7, Ok. Then release the block. 01:48 Completed to re-transfering all load of C.Duri fdr #7. 02:18 All load of C. Duri fdr #7 back to normal. Cause: Recloser Failure. (See report 08-Aug-2015 at 13:04 / Prod. loss = 1821 BBLS / 313 Wells.) | 3097797 | 1 | 13:11 | Afternoon | Saturday | 2015 | 8
1388 | 2015-08-08 14:44 | 2015-08-08 14:44 | CENTRAL DURI POWER PLANT |  |  | - | 14:44 S/U CGT #3, then on line the Unit at 15:10. (After repairing the leaking of Atomazing Head Exchanger) |  | 1 | 14:44 | Afternoon | Saturday | 2015 | 8
1389 | 2015-08-08 17:16 | 2015-08-08 17:16 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 21 | Libo OCB fdr #1 T/R 1x. Not checked yet. | 3097797 | 1 | 17:16 | Afternoon | Saturday | 2015 | 8
1390 | 2015-08-08 17:16 | 2015-09-08 14:10 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 21 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 349-350 R/F: 51N. Patrolled the line & found, @1 flash over Pin insulator o/p #34CA-02. Cause: Lightning. | 3097797 | 1 | 17:16 | Afternoon | Saturday | 2015 | 8
1391 | 2015-08-08 18:11 | 2015-08-08 18:11 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 29 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3097797 | 1 | 18:11 | Afternoon | Saturday | 2015 | 8
1392 | 2015-08-08 20:00 | 2015-08-08 20:00 | MINAS POWER PLANT |  |  | - | 20:00 S/U MGT #5, then on line the Unit at 20:26. |  | 1 | 20:00 | Night | Saturday | 2015 | 8
1393 | 2015-08-08 20:30 | 2015-08-08 20:30 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified (Fuse) | 114 | It was reported b/o fuse for Tx at Well Pematang #73. (Pematang fdr #2) Not checked yet. | 3097797 | 1 | 20:30 | Night | Saturday | 2015 | 8
1394 | 2015-08-08 20:30 | 2015-09-08 09:45 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified (Fuse) | 114 | Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Pematang #73. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (fuse). | 3097797 | 1 | 20:30 | Night | Saturday | 2015 | 8
1395 | 2015-08-08 20:31 | 2015-08-08 20:31 | MINAS POWER PLANT |  |  | - | 20:31 S/U MGT #2, then on line the Unit at 20:27. 20:50 Open Minas ACB #25. (Tie Breaker) |  | 1 | 20:31 | Night | Saturday | 2015 | 8
1396 | 2015-08-08 21:21 | 2015-08-08 21:21 | NORTH DURI POWER PLANT |  |  | - | 08-Aug-2015. 21:21 Off line NDC-CT #1, then S/D the Unit for Maintenance HRSG-1. (for installing Blanking Plate, due to repair the leaking tube of HRSG #1) 09-Aug-2015. 18:59 S/U NDC-CT #1, then on line the Unit at 19:38. (After installing blanking plate, due to repairing tube leaks of HRSG #1) |  | 1 | 21:21 | Night | Saturday | 2015 | 8
1397 | 2015-09-08 16:45 | 2015-09-08 16:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Main breaker | 2 | 16:45 It was reported b/o fuse for Tx o/p #08-L3-10. (C.Duri fdr #1) 18:30 Checked & found, @2 b/o 2.1SF fuse for 112.5Kva Tx o/p #08-L3-10. Replaced b/o fuse above with the same size & energized the Tx. Cause: Main Breaker. | 3097797 | 1 | 16:45 | Afternoon | Tuesday | 2015 | 9
1398 | 2015-09-08 18:59 | 2015-09-08 18:59 | NORTH DURI POWER PLANT |  |  | - | 18:59 S/U NDC-CT #1, then on line the Unit at 19:38. (After installing blanket plate, due to repairing tube leaks of HRSG #1) |  | 1 | 18:59 | Afternoon | Tuesday | 2015 | 9
1399 | 2015-09-08 20:50 | 2015-09-08 20:50 | MINAS POWER PLANT |  |  | - | Off line MGT #5, then S/D the Unit for S/B. |  | 1 | 20:50 | Night | Tuesday | 2015 | 9
1400 | 2015-09-08 21:00 | 2015-09-08 21:00 | DURI POWER PLANT |  |  | - | Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 21:00 | Night | Tuesday | 2015 | 9
1401 | 2015-10-08 06:29 | 2015-10-08 06:29 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Unidentified | 0 | C.Duri fdr #10 Load dropped 110A (246-136A). Not checked yet. | 3097797 | 1 | 6:29 | Morning | Thursday | 2015 | 10
1402 | 2015-10-08 06:29 | 2015-11-08 15:29 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Unidentified | 0 | Checked & found, Recl. 05-M7-24 (C.Duri fdr #10) T/R 1x Ctr: 64-65. Patrolled the line, but found nothing. Cause: Unidentified. | 3097797 | 1 | 6:29 | Morning | Thursday | 2015 | 10
1403 | 2015-10-08 07:59 | 2015-10-08 07:59 | 13.8KV ROKAN FEEDER #2 | Cloudy and Lightning | Lightning | 10 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3097797 | 1 | 7:59 | Morning | Thursday | 2015 | 10
1404 | 2015-10-08 07:59 | 2015-12-08 14:59 | 13.8KV ROKAN FEEDER #2 | Cloudy and Lightning | Lightning | 10 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 986-987 R/F: 51N(@1). Patrolled the line & found, @1 broken Pin Insulator o/p #NN. (Near Well Kopar #17) Cause: Lightning. | 3097797 | 1 | 7:59 | Morning | Thursday | 2015 | 10
1405 | 2015-10-08 10:30 | 2015-10-08 10:30 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Transformer Failure | 0 | 10:30 It was reported b/o fuse for Tx o/p #05-N1-08A. (Station 5-NE) 11:30 Checked & found, @1,@2 b/o 50K fuses & @1,@2 flash over bushing of 650Kva Tx. 18:30 Replaced 650Kva with 750Kva Tx, then energized the Tx. Cause: Tx failure. | 3097797 | 1 | 10:30 | Morning | Thursday | 2015 | 10
1406 | 2015-10-08 22:45 | 2015-10-08 22:45 | 13.8KV MINAS FEEDER #6 | Fair | Animal | 58 | Minas ACB fdr #6 T/R 1x Ctr: 153-154 R/F: 51N & 51G. The line is not patrolled yet. | 3097798 | 1 | 22:45 | Night | Thursday | 2015 | 10
1407 | 2015-10-08 22:45 | 2015-12-08 13:45 | 13.8KV MINAS FEEDER #6 | Fair | Animal | 58 | Patrolled the line & found, a dead Squirrel under TP of Well #6E-96. (no materials damage) Cause: Animal. (Squirrel) | 3097798 | 1 | 22:45 | Night | Thursday | 2015 | 10
1408 | 2015-11-08 04:36 | 2015-11-08 04:36 | 13.8KV 4D FEEDER #4 | Fair | Unidentified | 30 | 4D OCB fdr #4 T/R 1x. Not checked yet. | 3097798 | 1 | 4:36 | Morning | Sunday | 2015 | 11
1409 | 2015-11-08 04:36 | 2015-12-08 14:36 | 13.8KV 4D FEEDER #4 | Fair | Unidentified | 30 | Checked & found, 4D OCB fdr #4 T/R 1x Ctr: 246-247 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3097798 | 1 | 4:36 | Morning | Sunday | 2015 | 11
1410 | 2015-11-08 16:51 | 2015-11-08 16:51 | 13.8KV NORTH DURI FEEDER #5 | Fair | Lightning Arrester | 0 | No.Duri VCB fdr #5 T/R 1x. Not checked yet. | 3097797 | 1 | 16:51 | Afternoon | Sunday | 2015 | 11
1411 | 2015-11-08 16:51 | 2015-12-08 13:51 | 13.8KV NORTH DURI FEEDER #5 | Fair | Lightning Arrester | 0 | Checked & found, No.Duri VCB fdr #5 T/R 1x Ctr: 102-103 R/F: 51@3. Patrolled the line & found, @3 broken L/A jumper o/p #NN. (Near Well #3H-0302A) Cause: Lightning Arrester. | 3097797 | 1 | 16:51 | Afternoon | Sunday | 2015 | 11
1412 | 2015-12-08 09:03 | 2015-12-08 09:03 | 13.8KV 5B FEEDER #2 | Cloudy and Lightning | Lightning | 51 | 5B OCB fdr #2 T/R 1x. Not checked yet. | 3097798 | 1 | 9:03 | Morning | Tuesday | 2015 | 12
1413 | 2015-12-08 09:03 | 13/08/2015 15:31 | 13.8KV 5B FEEDER #2 | Cloudy and Lightning | Lightning | 51 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 329-330 R/F: 51@2. Patrolled the line & found, @1.@2 b/o fuses for 0.5Kva Tx for control of Recl. 5C-07. Cause: Suspected by Lightning. | 3097798 | 1 | 9:03 | Morning | Tuesday | 2015 | 12
1414 | 2015-12-08 10:00 | 2015-12-08 10:00 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 50 | 10:00 It was reported b/o fuse for Tx at Well So.Menggala #08. 11:30 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well So.Menggala #08. Perform TTR & Megger --> Good reading. Replaced b/o fuse with the same size & Energized the Tx. Cause: Animal. (Monkey) | 3097797 | 1 | 10:00 | Morning | Tuesday | 2015 | 12
1415 | 2015-08-13 07:32 | 2015-08-13 07:32 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Fair | Unidentified | 22 | MSU #2 (North) VCB fdr #2 (Nella fdr #2) T/R 1x. Not checked yet. | 3097797 | 1 | 7:32 | Morning | Thursday | 2015 | 8
1416 | 2015-08-13 07:32 | 2015-08-14 15:32 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Fair | Unidentified | 22 | Checked & found, MSU-2 VCB fdr #2 (Nella fdr #2) T/R 1x Ctr: 207-208 R/F: 51@2,@3. Patrolled the line, but found nothing. Cause: Unidentified. | 3097797 | 1 | 7:32 | Morning | Thursday | 2015 | 8
1417 | 2015-08-13 16:08 | 2015-08-13 16:08 | 13.8KV NORTH DURI FEEDER #11 | Fair | Transformer Failure | 0 | 16:08 It was reported that b/o fuse for Tx o/p #10-J6-12. Checked & found, @1,@3 b/o 3.1SF fuses for 112.5 Kva Tx o/p #10-J6-12. Tested the Tx & found, Low megger reading. Cause: Tx failure. (The Tx is not replaced yet) | 3097797 | 1 | 16:08 | Afternoon | Thursday | 2015 | 8
1418 | 2015-08-13 16:08 | 2015-08-14 11:20 | 13.8KV NORTH DURI FEEDER #11 | Fair | Transformer Failure | 0 | Replaced 112.5Kva Tx failure with the same size & energized the Tx o/p #10-J6-12. | 3097797 | 1 | 16:08 | Afternoon | Thursday | 2015 | 8
1419 | 2015-08-13 17:11 | 2015-08-13 17:11 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Dead End Insulator | 0 | 44KV N.Duri VCB #1 (N.Duri-Dumai line) T/R 1x. Not checked yet. | 3097797 | 1 | 17:11 | Afternoon | Thursday | 2015 | 8
1420 | 2015-08-13 17:11 | 2015-08-19 13:11 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Dead End Insulator | 0 | Checked & found, 44KV No.Duri VCB #1 (line to Dumai) T/R 1x Ctr: 151-152 R/F: 50@1 & 50N(@2). Patrolled the line & found, @1 flashed over Dead end Insulator o/p #DD-173. Cause: Lightning. | 3097797 | 1 | 17:11 | Afternoon | Thursday | 2015 | 8
1421 | 2015-08-13 17:32 | 2015-08-13 17:32 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 14 | 3D OCB fdr #8 T/R 1x. 3D fdr #6 load dropped 125A (126-1A). 3D fdr #7 load dropped 148A (170-22A). Not checked yet. | 3097798 | 1 | 17:32 | Afternoon | Thursday | 2015 | 8
1422 | 2015-08-13 17:32 | 2015-08-14 16:32 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 14 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 166-167 R/F: 50@3. Patrolled the line & found: -@3 Flashed over Dead end Insulator o/p #3D-99. -@3 Flashed over Dead end Insulator o/p #3D-75. Cause: Lightning. | 3097798 | 1 | 17:32 | Afternoon | Thursday | 2015 | 8
1423 | 2015-08-13 17:45 | 2015-08-13 17:45 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Lightning | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3097797 | 1 | 17:45 | Afternoon | Thursday | 2015 | 8
1424 | 2015-08-13 17:45 | 2015-08-19 13:45 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 75-76 R/F: 51@1 & 51N. Patrolled the line & found, @1 flashed over Dead end Insulator o/p #KT-34. Cause: Lightning. | 3097797 | 1 | 17:45 | Afternoon | Thursday | 2015 | 8
1425 | 2015-08-13 17:46 | 2015-08-13 17:46 | 13.8KV BATANG FEEDER #3 | Cloudy | Unidentified | 453 | 17:46 Batang OCB fdr #3 T/LO. Ctr: 272-276 R/F: 50@1. 18:24 Blocked & closed Batang OCB fdr #3, but Tripped again. 20:52 Opened Recl. 36AL-13 (Candi field) to separated load. Then blocked & closed Batang OCB fdr #3, but Tripped again. (Traffic jammed at main road to Batang Substation) 21:54 Patrolled the line, but found nothing. 21:58 Blocked & closed Batang OCB fdr #3 (from Control Room), Ok. Then released the block. 22:48 Blocked & closed Recl. 36AL-13, Ok. Then released the block. Cause: Unidentified. | 3097797 | 1 | 17:46 | Afternoon | Thursday | 2015 | 8
1426 | 2015-08-13 17:49 | 2015-08-13 17:49 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 79 | 17:49 Batang fdr #2 load dropped 34A (38-4A). 20:16 Checked & found, Recl. 36AG-11 (Batang fdr #2) T/LO. Ctr: 2983-2987. 20:35 Patrolled the line & found: -@2 Broken L/A & Jumper touched cross arm o/p #35AF-29. -@2 Broken Pin Insulator o/p #35-AF-27. 20:43 Blocked & closed Recl. 36AG-11, Ok. Then released the block. (Afer Isolating broken L/A above) Cause: Lightning. | 3097797 | 1 | 17:49 | Afternoon | Thursday | 2015 | 8
1427 | 2015-08-13 18:13 | 2015-08-13 18:13 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Unidentified | 111 | 18:13 So.Bekasap fdr #1 load dropped 57A (157-100A). 20:22 Checked & found, Recl. 34BI-18 (So.Bekasap fdr #1) T/LO. Ctr: 140-144. 20:41 Patrolled the line, but found nothing. 20:42 Blocked & closed Recl. 34BI-18, Ok. Then released the block. Cause: Unidentified. | 3097797 | 1 | 18:13 | Afternoon | Thursday | 2015 | 8
1428 | 2015-08-14 10:00 | 2015-08-14 10:00 | DURI POWER PLANT |  |  | - | 10:00 S/U DGT #7, then on line the Unit at 10:15. |  | 1 | 10:00 | Morning | Friday | 2015 | 8
1429 | 2015-08-14 11:17 | 2015-08-14 11:17 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 39 | 11:17 It was reported no power at Well So.Balam #303, #216, #289, #190. (D/S So.Balam fdr #4) So.Balam fdr#4 Load dropped 6A (123-117A). 11:55 Checked & found, Recl. 17AA-43 (So.Balam fdr #4) T/O. (In block position) Ctr: 19-20. Patrolled the line, but found Nothing. 12:00 Blocked & closed Recl. 17AA-43, Ok. Then released the Block. Cause: Unidentified. | 3097797 | 1 | 11:17 | Morning | Friday | 2015 | 8
1430 | 2015-08-14 14:00 | 2015-08-14 14:00 | MINAS POWER PLANT |  |  | - | 14:00 S/U MGT #5, then on line the Unit at 14:25. |  | 1 | 14:00 | Afternoon | Friday | 2015 | 8
1431 | 2015-08-14 15:13 | 2015-08-14 15:13 | MINAS POWER PLANT | Fair | Equipment Failure | - | 15:13 MGT #2 Tripped Off, By Alarm: Mechanical Over Speed Trip. Cause: Under Investigation. 21:50 S/U MGT #2, then online the Unit at 22:18. (After resetting the Alarm) Cause: Under Investigation. 17 - 20 August 2015. Checked & found, Suspected over Speed bolt / Switch spurious Trip. Cause: Equipment failure. | 3097798 | 1 | 15:13 | Afternoon | Friday | 2015 | 8
1432 | 2015-08-14 19:06 | 2015-08-14 19:06 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 36 | 8D OCB fdr #10 T/R 1x. 8D fdr #11 load dropped 35A (337-302A). Not checked yet. | 3097798 | 1 | 19:06 | Night | Friday | 2015 | 8
1433 | 2015-08-14 19:06 | 2015-08-16 06:24 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 36 | Checked & found, 8D OCB fdr #10 T/R 1x Ctr: 212-213 R/F: 51@1,@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3097798 | 1 | 19:06 | Night | Friday | 2015 | 8
1434 | 2015-08-14 23:27 | 2015-08-14 23:27 | NORTH DURI POWER PLANT |  |  | - | 14-Aug-2015. 23:27 Offline NDC-CT #1, then S/D the Unit for removing blanking plate. 15-Aug-2015. 21:12 S/U NDC-CT #1, then online the unit at 21:42. (After removing Blanking plate of HRSG-1) | 123 | 1 | 23:27 | Night | Friday | 2015 | 8
1435 | 2015-08-15 09:34 | 2015-08-15 09:34 | MINAS POWER PLANT | Cloudy | Equipment Failure | - | 09:34 MGT #2 Tripped Off, By Alarm: Mechanical Over speed. (Not real) Cause : Under Investigation. 17 - 20 August 2015. Checked & found, Suspected over Speed bolt / Switch spurious Trip. Cause: Equipment failure. | 123 | 1 | 9:34 | Morning | Saturday | 2015 | 8
1436 | 2015-08-15 10:58 | 2015-08-15 10:58 | 13.8KV MINAS FEEDER #3 | Cloudy and Lightning | Lightning | 77 | Minas ACB fdr #3 T/R 1x Ctr: 82-83 R/F: 51N. Not Patrolled yet. | 3097798 | 1 | 10:58 | Morning | Saturday | 2015 | 8
1437 | 2015-08-15 10:58 | 2015-08-16 16:00 | 13.8KV MINAS FEEDER #3 | Cloudy and Lightning | Lightning | 77 | Patrolled the line & found, @3 broken L/A o/p #7D-98. Cause: Lightning. | 3097798 | 1 | 10:58 | Morning | Saturday | 2015 | 8
1438 | 2015-08-15 13:06 | 2015-08-15 13:06 | 13.8KV BANGKO FEEDER #4 | Cloudy | Animal | 17 | 13:06 It was reported b/o fuse for Tx at Well Banko #75. (BKO fdr #4) 14:15 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Bangko #75. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3097797 | 1 | 13:06 | Afternoon | Saturday | 2015 | 8
1439 | 2015-08-15 21:12 | 2015-08-15 21:12 | NORTH DURI POWER PLANT |  |  | - | 21:12 S/U NDC-CT #1, then online the unit at 21:42. (After removing Blanking plate of HRSG-1) |  | 1 | 21:12 | Night | Saturday | 2015 | 8
1440 | 2015-08-15 22:30 | 2015-08-15 22:30 | DURI POWER PLANT |  |  | - | 22:30 Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 22:30 | Night | Saturday | 2015 | 8
1441 | 2015-08-16 11:00 | 2015-08-16 11:00 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified (Fuse) | 4 | 11:00 It was reported b/o fuse for Tx o/p #13-H4-03. (N.Duri fdr #11) 13:30 Checked & found, @3 b/o 2.1SF fuse for 112.5Kva Tx o/p #13-H4-03. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3097797 | 1 | 11:00 | Morning | Sunday | 2015 | 8
1442 | 2015-08-16 18:58 | 2015-08-16 18:58 | 13.8KV KETIGUL FEEDER#3 | Cloudy and Lightning | Lightning | 25 | Ketigul VCB fdr #3 T/R 1x. Ketigul fdr #2 Load dropped 39A (109-70A). Not checked yet. | 3097797 | 1 | 18:58 | Afternoon | Sunday | 2015 | 8
1443 | 2015-08-16 18:58 | 2015-08-18 15:58 | 13.8KV KETIGUL FEEDER#3 | Cloudy and Lightning | Lightning | 25 | Checked & found, Ketigul VCB fdr #3 T/R 3x Ctr: 155-158 R/F: 51N(@1). Patrolled the line & found, @1 broken Dead end Insulator o/p #31AR-21. Cause: Lightning. | 3097797 | 1 | 18:58 | Afternoon | Sunday | 2015 | 8
1444 | 2015-08-17 01:12 | 2015-08-17 01:12 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 8 | 01:12 It was reported b/o fuse for Tx at Well Bangko #75. 01:59 Checked & found, @2 b/o 3.5SF fuse for 150Kva Tx at Well Bangko #75. Perform TTR & Megger --> Good. Replaced b/o fuse above with the same size & Energized it. Cause: Unidentified (fuse). | 3097797 | 1 | 1:12 | Night | Monday | 2015 | 8
1445 | 2015-08-17 23:19 | 2015-08-17 23:19 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Dead End Insulator | 0 | C.Duri fdr #1 load dropped 45A (241-196A). Not checked yet. | 3097797 | 1 | 23:19 | Night | Monday | 2015 | 8
1446 | 2015-08-17 23:19 | 2015-08-19 10:19 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Dead End Insulator | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 195-196. Patrolled the line & found, @1 flashed over Dead end Insulator o/p #40AW-16. Cause: Dead end Insulator. | 3097797 | 1 | 23:19 | Night | Monday | 2015 | 8
1447 | 2015-08-18 23:59 | 2015-08-18 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system normal condition. | 123 | 1 | 23:59 | Night | Tuesday | 2015 | 8
1448 | 2015-08-19 17:10 | 2015-08-19 17:10 | NORTH DURI SUBSTATION | Fair | Transformer Failure | 988 | 17:10 No.Duri 115KV C/S-TX #13 T/O. Ctr: 3528-3529 R/F: 86HR. 18:19 Opened N.Duri VCB fdr #9. Opened N.Duri VCB fdr #10. Opened N.Duri VCB fdr #11 Ctr: 136. Transferred load N.Duri VCB #11 to N.Duri VCB #2. (to anticipate water discharge at CIF) 18:30 Opened Isolation switch of N.Duri VCB fdr #11. Closed Isolation switch of N.Duri VCB fdr #2. 18:32 Blocked & closed No.Duri VCB fdr #2, Ok. Then released the block. 18:40 Adjust LTC of No.Duri Voltage Regulator of Tx #11. (from R11 - R16) 18:50 Opened Isolation switch for Tx #13. 18:53 Opened No.Duri VCB fdr #8. 18:57 Closed Tie Bus Tx #12 & Tx #13. 19:00 Blocked & closed No.Duri VCB fdr #8, then released the block. Ctr: 56-57. Blocked & closed No.Duri VCB fdr #9, then released the block. Ctr: 38-39. Blocked & closed No.Duri VCB fdr #10, then released the block Ctr: 12-13. Cause: Transformer Failure. (Pressure Relief device released) Prod. loss Reported by GS: Per EMAIL. Area-10 = 684.7 Bbls. / 304 Wells. Area-11 = 307.8 Bbls. / 277 Wells. Area-13 = 546.5 Bbls. / ..... Wells. Grand Total = 1539.0 Bbls. / 581 Wells. Prod. loss Reported by EC: Area-10 = 400 Bbls. / 344 Wells. Area-11 = 200 Bbls. / 275 Wells. Area-13 = 388 Bbls. / 316 Wells. Grand Total = 988 Bbls. / 935 Wells. | 3097797 | 1 | 17:10 | Afternoon | Wednesday | 2015 | 8
1449 | 2015-08-20 15:05 | 2015-08-20 15:05 | MINAS POWER PLANT |  |  | - | 15:05 S/U MGT #2, then on line the Unit at 15:44. (for Running on test) 17 - 20 August 2015. After checking & found, Suspected over Speed bolt / Switch spurious Trip. (Then fixed the over speed bolt / Switch) Cause: Equipment failure. |  | 1 | 15:05 | Afternoon | Thursday | 2015 | 8
1450 | 2015-08-20 15:14 | 2015-08-20 15:14 | 13.8KV SINTONG FEEDER #1 | Fair | Switchboard Problem | 10 | Sintong fdr #1 load dropped 66A (218-152A). Sintong GFPC T/R 1x. Not checked yet. | 3097797 | 1 | 15:14 | Afternoon | Thursday | 2015 | 8
1451 | 2015-08-20 15:14 | 2015-08-21 10:30 | 13.8KV SINTONG FEEDER #1 | Fair | Switchboard Problem | 10 | Checked & found, Recl. 19AN-04 (Sintong fdr #1) T/R 1x Ctr: 306. (Not change) Also found, Sintong GFPC T/R 2x Ctr: 785-787. 16:30 It was reported b/o fuse for Tx at Well No.Menggala #13. (Sintong fdr #1) 18:46 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well No.Menggala #13. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Switchboard Problem. | 3097797 | 1 | 15:14 | Afternoon | Thursday | 2015 | 8
1452 | 2015-08-20 17:10 | 2015-08-20 17:10 | MINAS POWER PLANT |  |  | - | Off line MGT #3, then S/D the Unit for S/B. |  | 1 | 17:10 | Afternoon | Thursday | 2015 | 8
1453 | 2015-08-20 21:49 | 2015-08-20 21:49 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 7 | Libo fdr #2 load dropped 27A (44-17A). Not checked yet. | 3097797 | 1 | 21:49 | Night | Thursday | 2015 | 8
1454 | 2015-08-20 21:49 | 2015-08-21 19:00 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 7 | Checked & found, Recl. 23BW-02 (Libo fdr #2) T/R 1x Ctr: 222-223. Patrolled the line & found: -@3 Broken Pin Insulator o/p #22BV-02 & #22BV-05. -@1,@2 Broken Pin Insulator o/p #21BV-09. Cause: Lightning. | 3097797 | 1 | 21:49 | Night | Thursday | 2015 | 8
1455 | 2015-08-21 08:57 | 2015-08-21 08:57 | 13.8KV DURI FIELD FEEDER #4 | Fair | Dead End Insulator | 0 | Duri Field VCB fdr #4 T/R 1x. Not checked yet. | 3097797 | 1 | 8:57 | Morning | Friday | 2015 | 8
1456 | 2015-08-21 08:57 | 2015-08-25 14:57 | 13.8KV DURI FIELD FEEDER #4 | Fair | Dead End Insulator | 0 | Checked & found, Duri Field VCB fdr #4 T/R 1x Ctr: 441-442 R/F: 51N. Patrolled the line & found, @1 flashed over Dead end Insulator o/p #07-V5-26. Cause: Dead end Insulator. | 3097797 | 1 | 8:57 | Morning | Friday | 2015 | 8
1457 | 2015-08-21 16:38 | 2015-08-21 16:38 | 13.8KV PETANI FEEDER #2 | Fair | Animal | 11 | 16:38 It was reported b/o fuse for Tx at Well Petani #36. (Petani fdr #1) 18:25 Checked & found, @2, @3 b/o 3.5SF fuses for 150Kva Tx at Well Petani #36. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3097797 | 1 | 16:38 | Afternoon | Friday | 2015 | 8
1458 | 2015-08-21 17:15 | 2015-08-21 17:15 | 13.8KV BEKASAP MAIN GFPC | Fair | Unidentified | 0 | Bekasap Main GFPC TX-C T/R 2x. Ground fault alarm on Bekasap Main fdr #2. (No load dropped at any fdrs.) Not checked yet. | 3097797 | 1 | 17:15 | Afternoon | Friday | 2015 | 8
1459 | 2015-08-21 17:15 | 2015-08-25 15:15 | 13.8KV BEKASAP MAIN GFPC | Fair | Unidentified | 0 | Checked & found, Bekasap GFPC T/R 2x Ctr: 329-331. Patrolled the line at downstream of Bekasap fdr #2, but found nothing. Cause: Unidentified. | 3097797 | 1 | 17:15 | Afternoon | Friday | 2015 | 8
1460 | 2015-08-21 23:20 | 2015-08-21 23:20 | 13.8KV BEKASAP FEEDER #2 | Fair | Transformer Failure | 19 | 23:20 It was reported b/o fuse for Tx at Well Bekasap #42. Not checked yet. | 3097787 | 1 | 23:20 | Night | Friday | 2015 | 8
1461 | 2015-08-21 23:20 | 2015-08-22 01:05 | 13.8KV BEKASAP FEEDER #2 | Fair | Transformer Failure | 19 | 01:05 Checked & found, @1 b/o 2.1SF fuses for 100Kva Tx at Well Bekasap #42. Perform TTR, Megger test the Tx & found, Low megger reading. Cause: Tx failure. (The Tx is not replaced yet) | 3097787 | 1 | 23:20 | Night | Friday | 2015 | 8
1462 | 2015-08-21 23:20 | 2015-02-09 16:51 | 13.8KV BEKASAP FEEDER #2 | Fair | Transformer Failure | 19 | Replaced 100Kva Tx with the same size then energized the Tx at Well Bekasap #42. (Bekasap fdr #2) Cause: Transformer Failure. (Low megger reading) | 3097787 | 1 | 23:20 | Night | Friday | 2015 | 8
1463 | 2015-08-22 18:27 | 2015-08-22 18:27 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning Arrester | 0 | C.Duri fdr #1 load dropped 44A (249-205A). Not checked yet. | 3097797 | 1 | 18:27 | Afternoon | Saturday | 2015 | 8
1464 | 2015-08-22 18:27 | 2015-08-25 15:27 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning Arrester | 0 | Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/R 1x Ctr: 223-224. Patrolled the line & found, @1 broken L/A of LBS o/p #37AR-05. Cause: Lightning Arrester. | 3097797 | 1 | 18:27 | Afternoon | Saturday | 2015 | 8
1465 | 2015-08-22 21:31 | 2015-08-22 21:31 | 13.8KV S. BALAM FEEDER #1 | Fair | Secondary Cable | 4 | 21:31 It was reported b/o fuse for Tx at Well So.Balam #352. (So.Balam fdr #1) 22:46 Checked & found, @1 b/o 2.1SF fuse for 100Kva Tx at Well So.Balam #352. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Secondary Cable. | 3097797 | 1 | 21:31 | Night | Saturday | 2015 | 8
1466 | 2015-08-22 22:56 | 2015-08-22 22:56 | 13.8KV KETIGUL FEEDER#3 | Fair | Post Pin Insulator | 5 | Ketigul VCB fdr #3 T/R 1x. Not checked yet. | 3097797 | 1 | 22:56 | Night | Saturday | 2015 | 8
1467 | 2015-08-22 22:56 | 2015-08-25 14:56 | 13.8KV KETIGUL FEEDER#3 | Fair | Post Pin Insulator | 5 | Checked & found, Ketigul VCB fdr #3 T/R 1x Ctr: 158-159 R/F: 51N. Patrolled the line & found, @1 broken Pin Post Insulator o/p #31AR-22. Cause: Pin Insulator. | 3097797 | 1 | 22:56 | Night | Saturday | 2015 | 8
1468 | 2015-08-23 01:19 | 2015-08-23 01:19 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified | 75 | CKBS fdr #6 load dropped 151A (210-59A). Checked & found, Recl. 34CT-34 (CKBS fdr #6) T/R 2x Ctr: 21-23. Patrolled the line, but found nothing. Cause: Unidentified. | 3097798 | 1 | 1:19 | Night | Sunday | 2015 | 8
1469 | 2015-08-23 08:40 | 2015-08-23 08:40 | 44KV NORTH DURI - DUMAI LINE | Cloudy and Lightning | Lightning | 0 | 44KV No.Duri GCB #1 (Line to Dumai) T/R 1x. Not checked yet. | 3097797 | 1 | 8:40 | Morning | Sunday | 2015 | 8
1470 | 2015-08-23 08:40 | 2015-08-25 15:00 | 44KV NORTH DURI - DUMAI LINE | Cloudy and Lightning | Lightning | 0 | Checked & found, 44KV No.Duri GCB #1 (Line to Dumai) T/R 1x Ctr: 152-153 R/F: 50@2. Patrolled the line & found, @2 flashed over Dead end Insulator o/p #DD-62. Cause: Lightning. | 3097797 | 1 | 8:40 | Morning | Sunday | 2015 | 8
1471 | 2015-08-23 10:55 | 2015-08-23 10:55 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 10:55 It was reported b/o fuse for Tx o/p #06-Q5-11. 14:23 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #06-Q5-11. Perform TTR & Megger test, found good reading. Replace b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3097797 | 1 | 10:55 | Morning | Sunday | 2015 | 8
1472 | 2015-08-24 09:30 | 2015-08-24 09:30 | MINAS POWER PLANT |  |  | - | 09:30 S/U MGT #3, then Online the Unit at 09:44. 09:45 Open Minas ACB #25. (Tie Breaker) | 123 | 1 | 9:30 | Morning | Monday | 2015 | 8
1473 | 2015-08-24 11:30 | 2015-08-24 11:30 | MINAS POWER PLANT |  |  | - | Offline MGT #9, then S/D the Unit for S/B. (Prior to Rotor Boroscope inspection & Gas Scraber PM cleaning) 28-Aug-2015 16:37 S/U MGT #9, then Online the Unit at 16:52. (After Rotor Boroscope inspection & Gas Scraber PM cleaning) | 123 | 1 | 11:30 | Morning | Monday | 2015 | 8
1474 | 2015-08-24 18:08 | 2015-08-24 18:08 | 44KV PEMATANG MAIN - RANGAU LINE | Cloudy | Unidentified | 52 | Pematang Main 44KV OCB #2 (To Rangau) T/R 1x Pematang fdr #1 dropped 111A (164-53A). Petani fdr #1 Load dropped 42A (212-170A). (Rangau RTU failed at the time) Not checked yet. | 3097797 | 1 | 18:08 | Afternoon | Monday | 2015 | 8
1475 | 2015-08-24 18:08 | 2015-08-28 16:08 | 44KV PEMATANG MAIN - RANGAU LINE | Cloudy | Unidentified | 52 | Checked & found 44KV Pematang Main OCB #2 (line to Rangau), Ctr: 99993. (Not change) R/F: Not appeare. Patrolled the line, but found nothing. Cause: Unidentified. | 3097797 | 1 | 18:08 | Afternoon | Monday | 2015 | 8
1476 | 2015-08-24 23:00 | 2015-08-24 23:00 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 0 | 21:52 It was reported that Spark at Jumper on TOP of Well #9D-96. (8C fdr #1) Checked & found, @2 Spark at HLC jumper o/p #9D-110. (line toward Well #9D-96) 23:00 Shutdown Well #9D-96, to anticipate broken conductor, due to its spark. Cause: HLC jumper Loose connection. (It would be repaired tomorrow) | 123 | 1 | 23:00 | Night | Monday | 2015 | 8
1477 | 2015-08-24 23:00 | 2015-08-25 14:49 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 0 | 14:49-15:26 Blocked Recl. 9D-14A (8C fdr #1) Repaired loose connection HLC jumper o/p #9D-110. (Then energized the Tx & S/U Well #9D-96) Cause: HLC problem. | 123 | 1 | 23:00 | Night | Monday | 2015 | 8
1478 | 2015-08-25 23:59 | 2015-08-25 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power Power System normal Condition. |  | 1 | 23:59 | Night | Tuesday | 2015 | 8
1479 | 2015-08-26 09:48 | 2015-08-26 09:48 | 13.8KV SINTONG FEEDER #1 | Fair | Suspension Insulator | 70 | Sintong OCB fdr #1 T/R 1x. Sintong GFPC Did not Trip. (In block position for Rig Job) (Ground fault alarm on Sintong fdr #1) Sintong fdr #2 Load dropped 50A (101-51A). Not checked yet. | 3097797 | 1 | 9:48 | Morning | Wednesday | 2015 | 8
1480 | 2015-08-26 09:48 | 2015-08-27 15:30 | 13.8KV SINTONG FEEDER #1 | Fair | Suspension Insulator | 70 | Checked & found, Sintong OCB fdr #1 T/R 1x Ctr: 640-641 R/F: 51@1. Patrolled the line & found, @1 broken Suspension Insulator o/p #21AJ-03. Cause: Suspecsion Insulator. | 3097797 | 1 | 9:48 | Morning | Wednesday | 2015 | 8
1481 | 2015-08-26 10:25 | 2015-08-26 10:25 | 13.8KV 3D FEEDER #3 | Fair | Planned Maintenance | 38 | 10:25 Opened LBS #4C-138 for replacing Pin to Post Insulator & broken Dead end Insulator o/p #4C-17. (5 wells were off during this job) 14:49 Closed LBS #4C-138 and Started up all the wells.. Cause: Planned Maintenance. | 123 | 1 | 10:25 | Morning | Wednesday | 2015 | 8
1482 | 2015-08-27 15:37 | 2015-08-27 15:37 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Animal | 43 | 15:37 It was reported b/o fuse for Tx o/p #04-01-14. (C.Duri fdr #9) 17:49 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-01-14. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Monkey) | 3097797 | 1 | 15:37 | Afternoon | Thursday | 2015 | 8
1483 | 2015-08-27 16:05 | 2015-08-27 16:05 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 2 | 16:05 It was reported b/o fuse for Tx o/p #07-T5-09. (D. field fdr #2) Not checked yet. | 3097797 | 1 | 16:05 | Afternoon | Thursday | 2015 | 8
1484 | 2015-08-27 16:05 | 2015-08-28 15:10 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 2 | 15:10 Checked & found, @2, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T5-09 (d/s DF fdr#2). Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3097797 | 1 | 16:05 | Afternoon | Thursday | 2015 | 8
1485 | 2015-08-27 18:00 | 2015-08-27 18:00 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Animal | 14 | C. Duri ACB fdr #11 T/R 1x Ctr: 251. (not change) R/F: 51N(@3). Not patrolled yet. | 3097797 | 1 | 18:00 | Afternoon | Thursday | 2015 | 8
1486 | 2015-08-27 18:00 | 2015-08-28 16:45 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Animal | 14 | Patrolled the line & found, a Dead Monkey hung on @3 conductor o/p #05-M7-06. Cause: Animal. (Monkey. | 3097797 | 1 | 18:00 | Afternoon | Thursday | 2015 | 8
1487 | 2015-08-28 10:07 | 2015-08-28 10:07 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 68 | 10:07 OKB OCB fdr #2 T/R 1x. 18:26 Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1246-1247 RF: 51N. Patrolled the Line, but found nothing. Cause: Unidentified. | 3097798 | 1 | 10:07 | Morning | Friday | 2015 | 8
1488 | 2015-08-28 10:27 | 2015-08-28 10:27 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Animal | 5 | 10:27 It was reported b/o fuse for Tx o/p #04-03-11. (d/s C.Duri fdr #9) 11:10 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5KvaTx o/p #04-03-11. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3097797 | 1 | 10:27 | Morning | Friday | 2015 | 8
1489 | 2015-08-28 13:30 | 2015-08-28 13:30 | 13.8KV 6D FEEDER #2 | Fair | Animal | 0 | 13:30 It was reported b/o fuse for Tx at Well #7C-45E. (d/s 6D fdr #2) 15:05 Checked & found, @1, @2 b/o 7.8SF fuses for 300Kva Tx at Well #7C-45E. Replaced b/o fuse above with the same size, then energized the Tx. Cause : Animal. (Snake) | 3097798 | 1 | 13:30 | Afternoon | Friday | 2015 | 8
1490 | 2015-08-28 15:30 | 2015-08-28 15:30 | 13.8KV 8D FEEDER #11 | Fair | Secondary Cable | 3 | 15:30 It was reported b/o fuse for Tx at Well #9D-76. (d/s 8D fdr #11) 16:00 Checked & found, @1, @2 b/o 3.5SF fuses for 150Kva Tx at Well #9D-76. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Secondary Cable. | 3097798 | 1 | 15:30 | Afternoon | Friday | 2015 | 8
1491 | 2015-08-28 16:37 | 2015-08-28 16:37 | MINAS POWER PLANT |  |  | - | 16:37 S/U MGT #9, then Online the Unit at 16:52. (After Rotor Boroscope inspection & Gas Scraber PM cleaning) | 123 | 1 | 16:37 | Afternoon | Friday | 2015 | 8
1492 | 2015-08-28 16:57 | 2015-08-28 16:57 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 2 | C.Duri ACB fdr #16 T/R 1x Ctr: 284-285 R/F: 51N(@1,@2). Not patrolled yet. | 3097797 | 1 | 16:57 | Afternoon | Friday | 2015 | 8
1493 | 2015-08-28 16:57 | 2015-08-31 17:39 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 2 | Patrolled the line, but found nothing. Cause: Unidentified. | 3097797 | 1 | 16:57 | Afternoon | Friday | 2015 | 8
1494 | 2015-08-28 17:40 | 2015-08-28 17:40 | MINAS POWER PLANT |  |  | - | 17:40 Offline MGT #2, then S/D the Unit for S/B. | 123 | 1 | 17:40 | Afternoon | Friday | 2015 | 8
1495 | 2015-08-28 17:50 | 2015-08-28 17:50 | MINAS POWER PLANT |  |  | - | 17:50 Offline MGT #4, then S/D the Unit for S/B. | 123 | 1 | 17:50 | Afternoon | Friday | 2015 | 8
1496 | 2015-08-29 08:02 | 2015-08-29 08:02 | 13.8KV MENGGALA FEEDER #2 | Fair | Unidentified | 42 | Menggala OCB fdr #2 T/R 1x. Menggala GFPC T/R 1x. Not checked yet. | 3097797 | 1 | 8:02 | Morning | Saturday | 2015 | 8
1497 | 2015-08-29 08:02 | 2015-08-30 10:00 | 13.8KV MENGGALA FEEDER #2 | Fair | Unidentified | 42 | Checked & found, Menggala OCB fdr #2 T/R 1x Ctr: 523-524 R/F: 51N(@1). Also found, Menggala GFPC T/R 1x Ctr: 1113-1114. Patrolled the line, but found nothing. Cause: Unidentified. | 3097797 | 1 | 8:02 | Morning | Saturday | 2015 | 8
1498 | 2015-08-29 14:40 | 2015-08-29 14:40 | MINAS POWER PLANT |  |  | - | 14:40 S/U MGT #4, then Online the Unit at 15:10. (To back up power, due to MGT #6 will be S/D for Maintenance) | 123 | 1 | 14:40 | Afternoon | Saturday | 2015 | 8
1499 | 2015-08-29 15:25 | 2015-08-29 15:25 | MINAS POWER PLANT |  |  | - | 15:25 Offline MGT #6, then S/D the Unit for S/B. (Prior to Inspect Load gear) | 123 | 1 | 15:25 | Afternoon | Saturday | 2015 | 8
1500 | 2015-08-30 07:12 | 2015-08-30 07:12 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | 07:12 D.Field fdr #1 Load dropped 78A (117-39A). 11:30 Checked & found, Recl. 01-6-30 (D.Field fdr #1) T/R 1x Ctr: 80-81. Patrolled the Line, but found nothing. Cause: Unidentified. | 3097797 | 1 | 7:12 | Morning | Sunday | 2015 | 8
1501 | 2015-08-31 11:50 | 2015-08-31 11:50 | 13.8KV BEKASAP FEEDER #6 | Foggy and Smoke | Recloser | 254 | 11:50 Bekasap Main VCB fdr #6 T/R 1x. Bekasap Main fdr #3 Load dropped 60A (166-106A). 13:00 Checked & found, Bekasap Main VCB fdr #6 T/R 1x Ctr: 323-324 R/F: 51@1,@2. Patrolled the line & found, Recl. 38BE-10 (Bekasap fdr #6) T/LO. Ctr: Not reported yet. Also found burn out @1, @2 Recloser primary Bushing and @1 broken jumper. 15:20 Manually open Bekasap Main VCB fdr #6. To replace broken jumper & Bypass Recl. above. 15:53 Blocked & closed Bekasap Main VCB fdr #6, Ok. Then released the block. (last Ctr: 325) Cause: Recloser problem. | 3097797 | 1 | 11:50 | Morning | Monday | 2015 | 8
1502 | 2015-08-31 15:05 | 2015-08-31 15:05 | 13.8KV CENTRAL DURI FEEDER #1 | Foggy and Smoke | Animal | 0 | 15:05 It was reported b/o fuse for Tx o/p #SAA-14. (C.Duri fdr #1) 16:30 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #SAA-14. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3097797 | 1 | 15:05 | Afternoon | Monday | 2015 | 8
1503 | 2015-08-31 16:48 | 2015-08-31 16:48 | 13.8KV CENTRAL DURI FEEDER #8 | Foggy and Smoke | Unidentified | 44 | 16:48 It was reported no power at Area-9, Road-N6 and Road-P1. (C.Duri fdr #8) 17:30 Checked & found, Recl. 09.N6.06 (C.Duri fdr #8) T/O. (On blocked position, for Rig job ACS-06) Patrolled the Line, but found nothing. Closed the Recloser above & success. Cause: Unidentified. | 3097797 | 1 | 16:48 | Afternoon | Monday | 2015 | 8
1504 | 2015-08-31 20:05 | 2015-08-31 20:05 | 13.8KV SO BEKASAP FEEDER #1 | Foggy and Smoke | Unidentified | 105 | 20:05 So.Bekasap RTU failed. 20:09 So.Bekasap fdr #1 Load dropped 154A (163-9A). (When So.Bekasap RTU back to Online / normal) It is Supected So.Bekasap OCB fdr #1 T/R. Not checked yet. | 3097797 | 1 | 20:05 | Night | Monday | 2015 | 8
1505 | 2015-08-31 20:05 | 2015-02-09 08:46 | 13.8KV SO BEKASAP FEEDER #1 | Foggy and Smoke | Unidentified | 105 | Checked & found, So.Bekasap OCB fdr #1 T/R 1x Ctr: 248-249 R/F: 51@1. Patrolled the line, but found nothing. Cause: Unidentified. | 3097797 | 1 | 20:05 | Night | Monday | 2015 | 8
1506 | 2015-01-09 06:01 | 2015-01-09 06:01 | 13.8KV DURI FIELD FEEDER #1 | Foggy and Smoke | Unidentified | 0 | Duri Field ACB fdr #1 T/R 1x. Duri Field fdr #3 load drop 23A (149-126). Not checked yet. | 3097797 | 1 | 6:01 | Morning | Friday | 2015 | 1
1507 | 2015-01-09 06:01 | 2015-02-09 08:39 | 13.8KV DURI FIELD FEEDER #1 | Foggy and Smoke | Unidentified | 0 | Checked & found, Duri Field VCB fdr #1 T/R 1x Ctr: 623-624 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3097797 | 1 | 6:01 | Morning | Friday | 2015 | 1
1508 | 2015-01-09 07:21 | 2015-01-09 07:21 | 13.8KV CENTRAL DURI FEEDER #2 | Foggy and Smoke | Unidentified | 0 | C.Duri ACB fdr #2 T/R 1x Crt: 260-261 R/F: 51N(@1). Not patrolled yet. | 3097797 | 1 | 7:21 | Morning | Friday | 2015 | 1
1509 | 2015-01-09 07:21 | 2015-03-09 14:45 | 13.8KV CENTRAL DURI FEEDER #2 | Foggy and Smoke | Unidentified | 0 | Patrolled the line & found, @1 Flashed over Dead end Insulator o/p #ADDA-03. Cause: Unidentified. Also found, Recl. 08-M1-38 (C.Duri fdr #2) T/R 1x Ctr: 360-361. Patrolled the line, but found nothing. Cause: Unidentified. | 3097797 | 1 | 7:21 | Morning | Friday | 2015 | 1
1510 | 2015-01-09 11:15 | 2015-01-09 11:15 | 13.8KV CENTRAL DURI FEEDER #1 | Foggy and Smoke | Switchboard Problem | 16 | 11:15 It was reported b/o fuse for Tx at Well Kulim #54. 17:00 Checked & found, @3 b/o 1.4SF fuse for 75Kva Tx at Well Kulim #54. Replaced b/o fuse above with same size then energized the Tx. (after replaced broken Disconnect swith). Couse: Switchboard problem. (broken Disconnect switch) | 3111028 | 1 | 11:15 | Morning | Friday | 2015 | 1
1511 | 2015-01-09 18:00 | 2015-01-09 18:00 | 13.8KV 5B FEEDER #2 | Fair | Unidentified | 36 | 5B fdr #2 Load dropped 156A (180-24A). Not checked yet. | 3111029 | 1 | 18:00 | Afternoon | Friday | 2015 | 1
1512 | 2015-01-09 18:00 | 2015-02-09 13:41 | 13.8KV 5B FEEDER #2 | Fair | Unidentified | 36 | Checked & found, Recl. 5C-07 (5B fdr #2) T/R 1x Ctr: 44-45. Patrolled the line, but found nothing. Cause: Unidentified. | 3111029 | 1 | 18:00 | Afternoon | Friday | 2015 | 1
1513 | 2015-02-09 16:27 | 2015-02-09 16:27 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 0 | OKB fdr #2 load dropped 94A (289-195A). Not checked yet. | 3111029 | 1 | 16:27 | Afternoon | Monday | 2015 | 2
1514 | 2015-02-09 16:27 | 2015-04-09 17:50 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recl. 38CW-08 (OKB fdr #2) T/R 2x Ctr: 24-26. Patrolled the line, but found nothing. Cause: Unidentified. | 3111029 | 1 | 16:27 | Afternoon | Monday | 2015 | 2
1515 | 2015-02-09 17:18 | 2015-02-09 17:18 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | C.Duri ACB fdr #4 T/R 1x Ctr: 261-262 R/F: 51N. Not patrolled yet. | 3111028 | 1 | 17:18 | Afternoon | Monday | 2015 | 2
1516 | 2015-02-09 17:18 | 2015-03-09 17:48 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3111028 | 1 | 17:18 | Afternoon | Monday | 2015 | 2
1517 | 2015-03-09 11:13 | 2015-03-09 11:13 | MINAS POWER PLANT |  |  | - | 11:13 S/U MGT #2, then online the Unit at 11:38. |  | 1 | 11:13 | Morning | Monday | 2015 | 3
1518 | 2015-03-09 11:13 | 2015-03-09 11:13 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 82 | 44Kv Pematang Main OCB #1 (line to Petani) T/R 1x. Not checked yet. | 3111028 | 1 | 11:13 | Morning | Monday | 2015 | 3
1519 | 2015-03-09 11:13 | 2015-04-09 16:27 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 82 | Checked & found, 44KV Pematang Main OCB #1 (line to Petani) T/R 1x Ctr: 547-548 R/F: 50N(1). Patrolled the line, but found nothing. Cause: Unidentified. | 3111028 | 1 | 11:13 | Morning | Monday | 2015 | 3
1520 | 2015-03-09 13:10 | 2015-03-09 13:10 | MINAS POWER PLANT |  |  | - | 13:10 Offline MGT #5, then S/D the Unit for maintenance. (Prior to fixing MGT-5 Load Hunting) |  | 1 | 13:10 | Afternoon | Monday | 2015 | 3
1521 | 2015-03-09 14:45 | 2015-03-09 14:45 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Bangko fdr #4 load dropped 104A (220-116A). Bangko GFPC T/R 1x. (Ground fault alarm on Bangko fdr #4) Not checked yet. | 3111028 | 1 | 14:45 | Afternoon | Monday | 2015 | 3
1522 | 2015-03-09 14:45 | 2015-04-09 17:45 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x. Also found, Bangko GFPC T/R 2x Ctr: 469-471 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3111028 | 1 | 14:45 | Afternoon | Monday | 2015 | 3
1523 | 2015-04-09 09:48 | 2015-04-09 09:48 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 0 | 09:48 It was reported b/o fuse for Tx o/p #11-J2-09. (No.Duri fdr #1) 15:30 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #11-J2-09. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Monkey) | 3111028 | 1 | 9:48 | Morning | Thursday | 2015 | 4
1524 | 2015-04-09 12:44 | 2015-04-09 12:44 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Bangko fdr #4 load dropped 104A (220-116A). Not checked yet. | 3111028 | 1 | 12:44 | Afternoon | Thursday | 2015 | 4
1525 | 2015-04-09 12:44 | 2015-08-09 13:02 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 65-66. Also found, Bangko GFPC T/R 2x Ctr: 471-473 R/F: 50N. Patrolled the line, but found nothing. Cause: Unidentified. | 3111028 | 1 | 12:44 | Afternoon | Thursday | 2015 | 4
1526 | 2015-04-09 14:46 | 2015-04-09 14:46 | DURI POWER PLANT |  |  | - | 14:46 S/U DGT #7, then online the Unit at 15:12. |  | 1 | 14:46 | Afternoon | Thursday | 2015 | 4
1527 | 2015-04-09 16:45 | 2015-04-09 16:45 | MINAS POWER PLANT | Fair |  | - | 16:45 S/U MGT #5, then online the Unit at 18:00. |  | 1 | 16:45 | Afternoon | Thursday | 2015 | 4
1528 | 2015-04-09 17:17 | 2015-04-09 17:17 | MINAS POWER PLANT |  |  | - | 17:17 S/U MGT #6, then online the Unit at 17:54. |  | 1 | 17:17 | Afternoon | Thursday | 2015 | 4
1529 | 2015-05-09 15:51 | 2015-05-09 15:51 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Unidentified | 18 | 15:51 Petapahan fdr #1 load dropped 45A (80-35A). 16:41 Checked & found, Recl. 30CZ-23 (Petapahan fdr #1) T/R 1x Ctr: 145-146. Not Patrolled yet. | 3111029 | 1 | 15:51 | Afternoon | Saturday | 2015 | 5
1530 | 2015-05-09 15:51 | 2015-06-09 07:51 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Unidentified | 18 | Patrolled the line, but found nothing. Cause: Unidentified. | 3111029 | 1 | 15:51 | Afternoon | Saturday | 2015 | 5
1531 | 2015-05-09 16:24 | 2015-05-09 16:24 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain and Lightning | Tree | 0 | 16:24 4.16KV Dumai fdr #4 (Housing) Load dropped 114A (114-0A). 16:49 It was reported fall down Tree & hit to powerline at Dumai housing camp. (Between Borobudur & Mendut housing) 17:00 Checked & found, Recl. H33-07 (Dumai fdr #4) T/O. Ctr: 95-96. Patrolled & found, fall down Tree & hit to powerline between pole #H-62 & pole #H-64. (Affected pole #H-63 aslant) 18:30 Also found, fall down pole #H33-05. (Pole for 3x10Kva Tx power to supply Dumai Swage Water Plant) 19:15 Isolated Pole above by cutting jumper o/p #H33-25-03 & o/p #H-65. (no Power supply to Dumai Swage Water Plant & Land field) 19:35 Cut jumper o/p #H-62, o/p #H-60. (to isolate the fall down Tree) 20:20 Close Line Switch o/p #H-71. (line toward Mendut complex) 20:29 Closed Recl. H33-07 (Dumai fdr #4), Ok. (Borobudur & Mendut Housing back to energize) Cause: Tree. | 3111028 | 1 | 16:24 | Afternoon | Saturday | 2015 | 5
1532 | 2015-05-09 19:37 | 2015-05-09 19:37 | NORTH DURI POWER PLANT |  |  | - | 05-Sep-2015. 19:37 Off line NDC-CT #1, then S/D the Unit at 19:40. (Prior to perform OFF Line Wash program) 06-Sep-2015. 19:45 S/U NDC-CT #1, then Online at 20:14. (After Off Line wash program) | 123 | 1 | 19:37 | Night | Saturday | 2015 | 5
1533 | 2015-06-09 12:03 | 2015-06-09 12:03 | 44KV NORTH DURI - DUMAI LINE | Fair | Equipment Failure | 0 | 12:03 44KV No.Duri GCB #1 (Line to Dumai) T/LO. (Dumai RTU failed at the time) 12:16 Blocked & Closed 44KV No.Duri GCB #1, but failed. 13:45 Checked & found 44KV No.Duri GCB #1 T/LO. Ctr: 153-160 RF: 51G. Patrolled the Lines, but found nothing. 14:03 Blocked & Closed 44KV No.Duri GCB #1, but Tripped again. 15:05 Isolate 9Kva Transformer for Catodic Protection o/p #DD-256. 15:09 Blocked & Closed 44KV GCB #1, but Tripped again. 15:15 Isolate 4Sets L/As o/p #DD-49 15:30 Open both side Isolation Switches of 44KV No.Duri GCB #1. 15:50 Blocked & Closed 44KV No.Duri GCB #1, but Triped again. (Normalize the Block, then Closed 44KV No.Duri GCB #1, but Tripped again. 16:15 Open 13.8KV VCB #14 (for 44KV No.Duri TX-14) 16:17 Closed Bypass Switches of 44KV No.Duri GCB #1. (found that solid blade of bypass SW cannot fully close) 16:30 Open isolation Switches of 13.8KV No.Duri VCB #14. (for 44KV No.Duri TX-14) 16:40 Install Personal ground to repair Bypass Switches of 44KV No.Duri GCB #1. 16:53 Opened & Racked Out 4.16KV Dumai VCB #1 & VCB #2. 16:55 Opened Dumai 4.16KV VCB-12 fdr #1. (wharf) 16:56 Opened Dumai 4.16KV VCB-23 fdr #5. (Industrial) 16:57 Opened Dumai 4.16KV VCB-22 fdr #4. (Housing) 17:24 Opened Dumai 4.16KV VCB-13 fdr #2. (CPS). Note: 15:00 S/U Dumai Standby GENSET at Dumai CPS. 18:00 On Line CPS Genset to System. 19:45 Offline Dumai Standby GENSET, then S/D the Unit for S/B. 18:15 Closed No.Duri 13.8KV No.Duri VCB #14, after bypassing 44KV No.Duri GCB #1. (44KV No.Duri - Dumai line energize with Bypassing 44KV No.Duri GCB #1) 18:54 Racked In Dumai 44KV VCB #1 & VCB #2. 19:07 Closed Dumai 44KV Dumai VCB #2. (for 4.16KV TX-2). Last Ctr: 118. 19:10 Closed Dumai 4.16KV Dumai VCB fdr #4 (for Housing). Last Ctr: 258. 19:11 Closed Dumai 4.16KV Dumai VCB fdr #5 (for Industrial). Last Ctr: 271. 19:29 Closed Dumai 44KV VCB #1. (for 4.16KV TX-1) Last Ctr: 140. 19:30 Closed Dumai 4.16KV Dumai fdr #1 (for Wharf) Last Ctr: 243. 19:42 Closed Dumai 4.16Kv Dumai fdr #2 (for CPS) Last Ctr: 148. 19:45 Off Line Dumai Standby GENSET at Dumai CPS. Cause: Equipment failure. (44KV No.Duri GCB #1 problem) | 3111029 | 1 | 12:03 | Afternoon | Tuesday | 2015 | 6
1534 | 2015-06-09 19:45 | 2015-06-09 19:45 | NORTH DURI POWER PLANT |  |  | - | 19:45 S/U NDC-CT #1, then Online at 20:14. (After Off Line wash program) | 123 | 1 | 19:45 | Night | Tuesday | 2015 | 6
1535 | 2015-06-09 23:27 | 2015-06-09 23:27 | NORTH DURI POWER PLANT |  |  | - | 06-Aug-2015. 23:27 ND CT #3 Off Line, then S/D at 23:30. To Perform Off Line Wash. 07-Aug-2015. 22:07 S/U NDC-CT #3, then On line the Unit at 22:34 (After performing Off Line Wash program) | 123 | 1 | 23:27 | Night | Tuesday | 2015 | 6
1536 | 2015-07-09 08:00 | 2015-07-09 08:00 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | Sintong fdr #1 load dropped 52A (204-152A). Sintong GFPC T/R 1x. (Fault alarm on Sintong fdr #1) Not checked yet. | 3111028 | 1 | 8:00 | Morning | Thursday | 2015 | 7
1537 | 2015-07-09 08:00 | 2015-08-09 13:10 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | Checked & found: -Recl. 19AN-04 (Sintong fdr #1) -Recl. 25AD-26 (Sintong fdr #1) are normal. Ctr: Did not change. Checked Sintong GFPC T/R 1x Ctr: 788-789 R/F: 50N. Patrolled the line, but found nothing. Cause: Unidentified. | 3111028 | 1 | 8:00 | Morning | Thursday | 2015 | 7
1538 | 2015-07-09 08:50 | 2015-07-09 08:50 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 08:50 It was reported b/o fuse for Tx o/p #11-H5-09. 15:02 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #11-H5-09. Performed TTR & Megger test the Tx & found good reading. Replaced b/o fuse above with same size then energized the Tx. Cause: Unidentified (Fuse). | 3111028 | 1 | 8:50 | Morning | Thursday | 2015 | 7
1539 | 2015-07-09 14:52 | 2015-07-09 14:52 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 0 | 14:52 It was reported b/o fuse for Tx o/p #05-N3-09. 15:40 Checked & found, @1,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #05-N3-09. Performed TTR & Megger the Tx & found, good reading. Replaced b/o fuse above with same size then energized the Tx. Cause: Unidentified (Fuse). | 3111028 | 1 | 14:52 | Afternoon | Thursday | 2015 | 7
1540 | 2015-07-09 22:07 | 2015-07-09 22:07 | NORTH DURI POWER PLANT |  |  | - | 22:07 S/U NDC-CT #3, then On line the Unit at 22:34 (After performing Off Line Wash program) | 123 | 1 | 22:07 | Night | Thursday | 2015 | 7
1541 | 2015-08-09 01:20 | 2015-08-09 01:20 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 44 | 4B OCB fdr #1 T/R 1x. 4B fdr #2 Load dropped 67A (128-67A). 4B fdr #3 Load dropped 66A (132-66A). Not checked yet. Prod. loss Reported by GS-6. (4B fdr #1) Prod loss= 78 Bbls / 64 Wells. (4B fdr #2) Prod loss= 20 Bbls / 21 Wells. Total = 98 Bbls / 85 Wells. Prod. loss Reported by EC= 44 Bbls / 50 Wells. | 3111029 | 1 | 1:20 | Night | Sunday | 2015 | 8
1542 | 2015-08-09 01:20 | 2015-09-09 13:50 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 44 | Checked & found 4B OCB fdr#1 T/R 1x Ctr: 257-258 R/F: 51(@2, @3) Patrolled the line, but found nothing. Cause: Unidentified. | 3111029 | 1 | 1:20 | Night | Sunday | 2015 | 8
1543 | 2015-08-09 04:50 | 2015-08-09 04:50 | MINAS POWER PLANT |  |  | - | Off line MGT #6, then S/D the Unit for S/B. (Prior to inspect Load gear) | 123 | 1 | 4:50 | Morning | Sunday | 2015 | 8
1544 | 2015-08-09 05:10 | 2015-08-09 05:10 | MINAS POWER PLANT |  |  | - | Off line MGT #4, then S/D the Unit for S/B. | 123 | 1 | 5:10 | Morning | Sunday | 2015 | 8
1545 | 2015-08-09 10:30 | 2015-08-09 10:30 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 5 | 10:30 It was reported b/o fuse for Tx o/p #12-E3-06 11:56 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #12-E3-06. Performed TTR, Megger test the Tx & found, good reading. Replaced b/o fuse above with same size then energized the TX. Cause: Animal. (Bird) | 3111028 | 1 | 10:30 | Morning | Sunday | 2015 | 8
1546 | 2015-08-09 15:20 | 2015-08-09 15:20 | DURI POWER PLANT |  |  | - | Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 15:20 | Afternoon | Sunday | 2015 | 8
1547 | 2015-08-09 18:00 | 2015-08-09 18:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx o/p #13-H53-08. (N.Duri fdr #2) Not checked yet. | 3111028 | 1 | 18:00 | Afternoon | Sunday | 2015 | 8
1548 | 2015-08-09 18:00 | 2015-09-09 15:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #13-H53-08. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3111028 | 1 | 18:00 | Afternoon | Sunday | 2015 | 8
1549 | 2015-08-09 18:10 | 2015-08-09 18:10 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 116 | CKBS VCB fdr #5 T/R 1x. Not checked yet. | 3111029 | 1 | 18:10 | Afternoon | Sunday | 2015 | 8
1550 | 2015-08-09 18:10 | 2015-10-09 10:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 116 | Checked & found, CKBS VCB fdr #5 T/R 1x Ctr: 128-129 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3111029 | 1 | 18:10 | Afternoon | Sunday | 2015 | 8
1551 | 2015-08-09 18:10 | 2015-08-09 18:10 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified | 68 | CKBS VCB fdr #6 T/R 1x. Not checked yet. | 3111029 | 1 | 18:10 | Afternoon | Sunday | 2015 | 8
1552 | 2015-08-09 18:10 | 2015-10-09 10:10 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified | 68 | Checked & found, CKBS VCB fdr #6 T/R 1x ctr: 118-119 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3111029 | 1 | 18:10 | Afternoon | Sunday | 2015 | 8
1553 | 2015-08-09 18:10 | 2015-08-09 18:10 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 0 | OKB fdr #2 load drop 46A (288-242A). Not checked yet. | 3111029 | 1 | 18:10 | Afternoon | Sunday | 2015 | 8
1554 | 2015-08-09 18:10 | 2015-10-09 16:29 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recl. 38CX-25 (OKBS fdr #2) T/R 1x Ctr: 87-88. Patrolled the line, but found nothing. Cause: Unidentified. | 3111029 | 1 | 18:10 | Afternoon | Sunday | 2015 | 8
1555 | 2015-09-09 03:27 | 2015-09-09 03:27 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 4 | Ketigul VCB fdr #1 T/R 1x Ctr: 159-160 R/F: 51N(@1). Patrolled the line & found, @1 flashed over Pin Post Insulator o/p #31AN=36A. Cause: Lightning. | 3111028 | 1 | 3:27 | Night | Wednesday | 2015 | 9
1556 | 2015-09-09 06:22 | 2015-09-09 06:22 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 4 | 06:22 It was reported b/o fuse for Tx at Well KULIM #12. 10:57 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx at Well Kulim #12. Performed TTR & Megger test the Tx & found, good reading. Replaced b/o fuse above with same size then energized the Tx. Cause : Animal. (lizard in breaker) | 3111028 | 1 | 6:22 | Morning | Wednesday | 2015 | 9
1557 | 2015-09-09 11:35 | 2015-09-09 11:35 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 11:35 It was reported b/o fuse for Tx o/p #12-F1-09. (No.Duri fdr #5) 13:05 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #12-F1-09. Performed TTR & Megger test the Tx & found, good reading. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3111028 | 1 | 11:35 | Morning | Wednesday | 2015 | 9
1558 | 2015-09-09 14:18 | 2015-09-09 14:18 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 16 | 14:18 Blocked Bangko fdr #4 & GFPC for open HLC of Well Bangko #52. To replaced @1 broken FCO on TP of Well Bangko #52. (Bangko #52 was off during the job done) 14:46 Normalized Block & energized Well Bangko #52. Cause: Planned Maintenance. | 123 | 1 | 14:18 | Afternoon | Wednesday | 2015 | 9
1559 | 2015-09-09 19:30 | 2015-09-09 19:30 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Transformer Failure | 0 | 19:30 It was reported b/o fuse Tx at Talang Complex. (6 Houses were no power) 22:35 Checked & found: -@1,@2 b/o 1.0SF fuses & broken FCO for 50Kva Tx. -Broken Pin insulator o/p #NN. Perform TTR, Megger test the Tx & found, Low megger reading. Cause: Transformer failure. (The Tx is not replaced yet) | 3111028 | 1 | 19:30 | Night | Wednesday | 2015 | 9
1560 | 2015-09-09 19:30 | 2015-10-09 16:10 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Transformer Failure | 0 | 16:10 Replaced 50Kva Tx with the same size for housing Talang Complex. (6 Houses ). Cause: Tx Failure. | 3111028 | 1 | 19:30 | Night | Wednesday | 2015 | 9
1561 | 2015-09-09 21:31 | 2015-09-09 21:31 | 13.8KV CENTRAL DURI FEEDER #8 | Cloudy and Lightning | Lightning | 74 | 21:31 C.Duri ACB fdr #8 T/R 2x Ctr: 300. (Did not change) R/F: 51@1,@2. C.Duri fdr #7 load dropped 37A (217-180A). C.Duri fdr #12 load dropped 39A (119-80A). Not Patrolled yet. 21:49 It was reported by HO DSC team, that no power at Area-9, Road #N-6. 10-Sep-2015. 00:22 Checked & found, Recl. 09-N6-06 (C.Duri fdr #8) T/O. Ctr: 65-66. (In Block position for Rig Job) Blocked & closed Recl. 09-N6-06, Ok. The Recloser is still in Block. (After check at the Rig Activity) Not Patrolled yet. 14:53 Patrolled the line downstream of C.Duri fdr #8 & Recl. 09-N6-06, but found nothing. Cause: Suspected by Lightning. | 3111028 | 1 | 21:31 | Night | Wednesday | 2015 | 9
1562 | 2015-10-09 10:44 | 2015-10-09 10:44 | 13.8KV 4B FEEDER #2 | Fair | Dead End Insulator | 18 | 4B OCB fdr #2 T/R 1x. Not checked yet. | 3111029 | 1 | 10:44 | Morning | Friday | 2015 | 10
1563 | 2015-10-09 10:44 | 14/09/2015 08:13 | 13.8KV 4B FEEDER #2 | Fair | Dead End Insulator | 18 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 216-217 R/F: 51N(@3). Patrolled & found @3 broken Dead end insulator o/p#4B-58. Cause: Dead end insulator. | 3111029 | 1 | 10:44 | Morning | Friday | 2015 | 10
1564 | 2015-10-09 15:14 | 2015-10-09 15:14 | 13.8KV S. BALAM FEEDER #1 | Rain | Lightning Arrester | 204 | 15:14 So.Balam fdr #1 Load dropped 72A (92-20A). So.Balam fdr #4 load dropped 48A (132-84A). 16:50 Checked & found, Recl. 17Z-01 (So.Balam fdr #1) T/LO. Ctr: 51-55. Patrolled the line & found, @2 broken L/A o/p #NN. (Then isolated L/A above) 18:23 Blocked & closed Recl 17Z-01, Ok. Then release the block. Cause: Lightning Arrester. | 3111028 | 1 | 15:14 | Afternoon | Friday | 2015 | 10
1565 | 2015-10-09 16:23 | 2015-10-09 16:23 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 5 | 16:23 It was reported b/o fuse for Tx o/p #04-0-06. (C.Duri fdr #9) 17:55 Checed & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-0-06. Replaced b/o fuse above with the same sizethen enercized the Tx. Cause: Unidentified (Fuse). | 3111028 | 1 | 16:23 | Afternoon | Friday | 2015 | 10
1566 | 2015-10-09 16:44 | 2015-10-09 16:44 | 13.8KV PINANG FEEDER #1 | Rain | Lightning | 30 | Pinang OCB fdr #1 T/R 1x. Not checked yet. | 3111028 | 1 | 16:44 | Afternoon | Friday | 2015 | 10
1567 | 2015-10-09 16:44 | 13/09/2015 07:53 | 13.8KV PINANG FEEDER #1 | Rain | Lightning | 30 | Checked & found, Pinang OCB fdr #1 T/R 2x Ctr: 339-341 R/F: 51N(@2). Patrolled the line & found, @2 broken L/A on TOP of Well Pinang #12 & #15., Cause: Lightning. | 3111028 | 1 | 16:44 | Afternoon | Friday | 2015 | 10
1568 | 2015-10-09 18:40 | 2015-10-09 18:40 | 13.8KV PEMATANG FEEDER #1 | Fair | Powerline - Conductor | 581 | 18:40 Pematang OCB fdr #1 T/R 1x. 19:50 It was reported no power at some wells: (Pematang: 85,86,87,65,94,98 &100) 21:20 Checked & found, @1 broken conductor o/p #34BC-34. 23:12 Manually open Pematang OCB fdr #1. (form DSC) -Open booth sides isolation switches of Pematang OCB fdr #1. -Installed temporary Ground at job side. -Isolate broken conductor by cutting jumper o/p #34BC-32. (Well at Pematang: 85,86,87,65,94,98 &100 is still down) -Close booth sides isolation switches of Pematang OCB fdr #1. 23:30 Blocked & close Pematang OCB fdr #1, Ok. Then released the Block. (from DSC) Cause: Broken conductor. (The broken conductor will be repaired tomorrow) | 3111028 | 1 | 18:40 | Afternoon | Friday | 2015 | 10
1569 | 2015-10-09 18:40 | 2015-11-09 10:00 | 13.8KV PEMATANG FEEDER #1 | Fair | Powerline - Conductor | 581 | 10:00 Preparation for repairing the broken conductor o/p #34BC-34. 15:24 Opened Pematang VCB fdr #1. 15:26 Opened Isolation Switch Pematang VCB fdr #1. Connected Jumper o/p 34BC-34. Closed isolation switch Pematang VCB fdr #1. 16:15 Blocked & Closed Pematang VCB fdr #1, then release the block. (Pematang VCB fdr #1 back to normal) Reported by GS. Prod. loss: 581 BBls / 7 wells. Reported by EC. Prod. loss: 581 Bbls / 24 Wells. | 3111028 | 1 | 18:40 | Afternoon | Friday | 2015 | 10
1570 | 2015-11-09 08:09 | 2015-11-09 08:09 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Animal | 0 | 08:09 Ketigul fdr #2 Load dropped 93A (110-17A). 17:12 Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 170-171 R/F: 51N(@1). Patrolled the line & found, a Dead Monkey under TP of Well Pagar #30. Cause: Animal. (Monkey) | 3111028 | 1 | 8:09 | Morning | Monday | 2015 | 11
1571 | 2015-11-09 10:36 | 2015-11-09 10:36 | 13.8KV PUNGUT FEEDER #2 | Fair | Animal | 0 | 10:36 It was reported b/o fuse for Tx at Well Tandun #04. (Pungut fdr #2) 15:00 Checked & found, @2,@3 b/o 3.5SF fuses for 150Kva Tx at Well Tandun #04. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3111028 | 1 | 10:36 | Morning | Monday | 2015 | 11
1572 | 2015-11-09 15:24 | 2015-11-09 15:24 | 13.8KV PEMATANG FEEDER #1 | Fair | Planned Maintenance | 23 | 15:24 Manually Open Pematang OCB fdr #1. To Repair Main line broken conductor o/p #34BC-34. 16:15 Blocked & closed, Pematang OCB fdr #1, Ok. Then released the Block. (After repairing broken conductor o/p #34BC-34) Cause: Maintenance Job. | 123 | 1 | 15:24 | Afternoon | Monday | 2015 | 11
1573 | 2015-11-09 16:36 | 2015-11-09 16:36 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 24 | 16:36 It was reported b/o fuse at Well Pagar #30. 19:00 Checked & found, @2 b/o 7.8SF fuse & FCO for 300Kva Tx at Well Pagar #30. Cause: Animal. (Monkey) (The broken FCO will be replaced tomorrow) | 3111028 | 1 | 16:36 | Afternoon | Monday | 2015 | 11
1574 | 2015-11-09 16:36 | 2015-12-09 09:50 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 24 | 09:50 Blocked Ketigul VCB fdr #2, to Open HLC on TP of Well Pagar #30. Replaced @2 b/o fuse & FCO on Terminal Pole of Well Pager #30. 10:20 Energized 300Kva Tx & S/U the Well Pagar #30. Cause: Animal. (Monkey) | 3111028 | 1 | 16:36 | Afternoon | Monday | 2015 | 11
1575 | 2015-12-09 05:58 | 2015-12-09 05:58 | 13.8KV 6DN FEEDER #5 | Fair | Unidentified | 48 | 6DN fdr #5 load dropped 54A (123-69A). Not checked yet. | 3111029 | 1 | 5:58 | Morning | Wednesday | 2015 | 12
1576 | 2015-12-09 05:58 | 16/09/2015 07:31 | 13.8KV 6DN FEEDER #5 | Fair | Unidentified | 48 | Checked & found, Recl. 6D-16A (6DN fdr #5) T/R 1x Ctr: 1205-1206. Patrolled the line, but found nothing. Cause: Unidentified. | 3111029 | 1 | 5:58 | Morning | Wednesday | 2015 | 12
1577 | 2015-12-09 09:22 | 2015-12-09 09:22 | 13.8KV DURI FIELD FEEDER #2 | Foggy and Smoke | Animal | 3 | 09:22 It was reported b/o fuse for Tx o/p #07-V3-27. (D.Field fdr #2) 12:30 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-V3-27. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3111028 | 1 | 9:22 | Morning | Wednesday | 2015 | 12
1578 | 2015-12-09 10:07 | 2015-12-09 10:07 | 13.8KV CENTRAL DURI FEEDER #15 | Foggy and Smoke | Animal | 4 | 10:07 It was reported b/o fuse for Tx o/p #06-R1-05. (C.Duri fdr #15) 12:20 Checked & found, @2,@3 b/o 3.1SF fuses fr 112.5Kva Tx o/p #06-R1-05. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3111028 | 1 | 10:07 | Morning | Wednesday | 2015 | 12
1579 | 2015-12-09 14:16 | 2015-12-09 14:16 | 13.8KV 6DN FEEDER #6 | Foggy and Smoke | Unidentified (Fuse) | 9 | 14:16 It was reported b/o fuse for Tx at Well #6E-52E. (6DN fdr #6) 16:10 Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well #6E-52E. Replaced b/o fuse fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3111029 | 1 | 14:16 | Afternoon | Wednesday | 2015 | 12
1580 | 2015-12-09 20:53 | 2015-12-09 20:53 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 398 | 20:53 Bangko OCB fdr #4 T/LO. 21:30 Checked & found, Bangko OCB fdr #4 T/LO. Ctr: 99968-99972 R/F: 51N. 22:36 Patrolled & found, a dead Monkey o/p #25AC-38. (Then removed the Monkey) 22:48 Blocked & closed Bangko OCB fdr #4. Ok. Then normalized the block. Cause: Animal. (Monkey) 22:49 It was informed no power at Benar-GS. 23:09 Checked & found Recl. 25Z-07 (Bangko fdr #4) T/LO. Ctr: 66-71. 23:12 Blocked & closed Recl. 25Z-07, Ok. Then normalized the block. The line is not patrolled yet. | 3111028 | 1 | 20:53 | Night | Wednesday | 2015 | 12
1581 | 2015-09-13 23:59 | 2015-09-13 23:59 | CPI POWER SYSTEM | Foggy and Smoke | Normal Condition | - | CPI power system normal condition. |  | 1 | 23:59 | Night | Sunday | 2015 | 9
1582 | 2015-09-14 06:53 | 2015-09-14 06:53 | 13.8KV SINTONG FEEDER #2 | Foggy and Smoke | Unidentified | 6 | Sintong OCB fdr #2 T/R 1x. Not checked yet. | 3111028 | 1 | 6:53 | Morning | Monday | 2015 | 9
1583 | 2015-09-14 06:53 | 2015-09-16 12:45 | 13.8KV SINTONG FEEDER #2 | Foggy and Smoke | Unidentified | 6 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 395-396 R/F: 51N. Also found, Sintong GFPC T/R 2x Ctr: 789-791. Patrolled the line, but found nothing. Cause: Unidentified. | 3111028 | 1 | 6:53 | Morning | Monday | 2015 | 9
1584 | 2015-09-14 06:54 | 2015-09-14 06:54 | 13.8KV CENTRAL DURI FEEDER #7 | Foggy and Smoke | Broken Fuse Cut Out | 0 | 06:54 C.Duri ACB fdr #7 T/R 1x Ctr: 456-457 R/F: 51@1 & 51N. 07:49 C.Duri ACB fdr #7 T/R 2x Ctr: 457-459 R/F: 51@1 & 51N. Not patrolled yet. | 3111028 | 1 | 6:54 | Morning | Monday | 2015 | 9
1585 | 2015-09-14 06:54 | 2015-09-15 18:15 | 13.8KV CENTRAL DURI FEEDER #7 | Foggy and Smoke | Broken Fuse Cut Out | 0 | Patrolled the line & found, @2,@3 broken FCO for 500Kva Tx at CSS Area-3 o/p #03-6-16B. (Then replaced it with the new one & energized the Tx) Cause: Broken Fuse Cut Out. | 3111028 | 1 | 6:54 | Morning | Monday | 2015 | 9
1586 | 2015-09-14 07:21 | 2015-09-14 07:21 | 13.8KV 8D FEEDER #11 | Foggy and Smoke | Lightning Arrester | 41 | 8D OCB fdr #11 T/R 1x. Not checked yet. | 3111029 | 1 | 7:21 | Morning | Monday | 2015 | 9
1587 | 2015-09-14 07:21 | 2015-09-16 07:29 | 13.8KV 8D FEEDER #11 | Foggy and Smoke | Lightning Arrester | 41 | 8D OCB fdr #11 T/R 1x Ctr: 99895-99896 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. Also found Recl. 9E-02 (8D fdr #11) T/R 1x Ctr: 1056-1057. Patrolled the line & found, @1 broken L/A on TP of Well #9E-27E. Cause: Lightning Arrester. | 3111029 | 1 | 7:21 | Morning | Monday | 2015 | 9
1588 | 2015-09-14 09:10 | 2015-09-14 09:10 | 13.8KV CENTRAL DURI FEEDER #4 | Foggy and Smoke | Dead End Insulator | 0 | C.Duri ACB fdr #4 T/R 1x Ctr: 462-463 R/F: 51N(@3). Not patrolled yet. | 3111028 | 1 | 9:10 | Morning | Monday | 2015 | 9
1589 | 2015-09-14 09:10 | 2015-09-16 07:10 | 13.8KV CENTRAL DURI FEEDER #4 | Foggy and Smoke | Dead End Insulator | 0 | Patrolled the line & found, @3 broken Dead end Insulator o/p #09-P8-04. Cause: Dead end Insulator. | 3111028 | 1 | 9:10 | Morning | Monday | 2015 | 9
1590 | 2015-09-14 09:26 | 2015-09-14 09:26 | 13.8KV BEKASAP FEEDER #6 | Foggy and Smoke | Pin Insulator | 35 | Bekasap VCB fdr #6 T/R 1x. Not checked yet. | 3111028 | 1 | 9:26 | Morning | Monday | 2015 | 9
1591 | 2015-09-14 09:26 | 2015-09-15 10:23 | 13.8KV BEKASAP FEEDER #6 | Foggy and Smoke | Pin Insulator | 35 | Checked & found, Bekasap Main VCB fdr #6 T/R 1x Ctr: 325-326 R/F: 51N(@2). Patrolled the line & found, @2 F/O Pin Insulator o/p #39BE-02. Cause: Pin Insulator. | 3111028 | 1 | 9:26 | Morning | Monday | 2015 | 9
1592 | 2015-09-14 10:33 | 2015-09-14 10:33 | 13.8KV CENTRAL DURI FEEDER #7 | Foggy and Smoke | Broken Fuse Cut Out | 0 | 10:33 It was reported b/o fuse for Tx o/p #03-06-16B. 15:37 Checked & found, @2, @3 b/o fuses & broken FCO for 500Kva Tx o/p #03-6-16B. Performed TTR, Megger test the Tx & found, normal. (good reading) 17:49 Open HLC to replace broken FCO & fuse link with the same size, then energized the Tx o/p #03-06-16B. Cause: Broken Fuse Cut Out. | 3111028 | 1 | 10:33 | Morning | Monday | 2015 | 9
1593 | 2015-09-14 12:13 | 2015-09-14 12:13 | MINAS POWER PLANT | Foggy and Smoke | Under investigation | - | MGT #2 Tripped By Alarm: 12T Active & Mechanical over speed. Cause: Under Investigation. |  | 1 | 12:13 | Afternoon | Monday | 2015 | 9
1594 | 2015-09-14 14:48 | 2015-09-14 14:48 | 13.8KV SINTONG FEEDER #1 | Fair | Planned Maintenance | 3 | 14:48 Manually opened Recl. 25AD-26, to cut danger high Tress at near Well Seruni #22. 15:00 Close Recl. 25AD-26. Cause: Maintenance Job. | 123 | 1 | 14:48 | Afternoon | Monday | 2015 | 9
1595 | 2015-09-14 21:39 | 2015-09-14 21:39 | 13.8KV 5B FEEDER #4 | Foggy and Smoke | Dead End Insulator | 34 | 5B fdr #4 load dropped 216A (278-62A). Not checked yet. | 3111029 | 1 | 21:39 | Night | Monday | 2015 | 9
1596 | 2015-09-14 21:39 | 2015-09-16 13:03 | 13.8KV 5B FEEDER #4 | Foggy and Smoke | Dead End Insulator | 34 | Checked & found, Recl. 4B-73 (5B fdr #4) T/R 1x Ctr: 47-48. Patolled the line & found, @1 broken Dead end Insulator o/p #4B-76. Cause: Dead end Insulator. | 3111029 | 1 | 21:39 | Night | Monday | 2015 | 9
1597 | 2015-09-15 09:29 | 2015-09-15 09:29 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Animal | 5 | 09:29 It was reported b/o fuse for Tx o/p #04-07-28. (C.Duri fdr #8) 14:55 Checked & found, @2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #04-07-28. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Bird) | 3111028 | 1 | 9:29 | Morning | Tuesday | 2015 | 9
1598 | 2015-09-15 10:14 | 2015-09-15 10:14 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning | 6 | Sintong OCB fdr #2 T/R 1x. Not checked yet. | 3111028 | 1 | 10:14 | Morning | Tuesday | 2015 | 9
1599 | 2015-09-15 10:14 | 2015-09-16 12:40 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning | 6 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 396-397 R/F: 51N. Also found, Sintong GFPC T/R 2x Ctr: 791-793. Patrolled the line, but found nothing. Cause: Lightning. | 3111028 | 1 | 10:14 | Morning | Tuesday | 2015 | 9
1600 | 2015-09-15 14:55 | 2015-09-15 14:55 | MINAS POWER PLANT | Fair |  | - | 14:55 S/U MGT #4 and O/L the Unit at 15:52. |  | 1 | 14:55 | Afternoon | Tuesday | 2015 | 9
1601 | 2015-09-15 16:30 | 2015-09-15 16:30 | MINAS POWER PLANT |  |  | - | Off line MGT #5, then S/D the unit for S/B. |  | 1 | 16:30 | Afternoon | Tuesday | 2015 | 9
1602 | 2015-09-15 17:22 | 2015-09-15 17:22 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 87 | Bangko OCB fdr #4 T/R 1x. Not checked yet. | 3111028 | 1 | 17:22 | Afternoon | Tuesday | 2015 | 9
1603 | 2015-09-15 17:22 | 2015-09-20 09:00 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 87 | Checked & found, Bangko VCB fdr #4 T/R 1x Ctr: 99972-99973 R/F: 51@3. Patrolled the line, but found nothing. Cause: Unidentified. | 3111028 | 1 | 17:22 | Afternoon | Tuesday | 2015 | 9
1604 | 2015-09-16 03:43 | 2015-09-16 03:43 | 13.8KV 4D FEEDER #3 | Fair | Unidentified | 31 | 03:43 4D OCB fdr #3 T/LO. 4D fdr #2 load dropped 130A (165-35A). 4D fdr #1 load dropped 195A (264-69A). 05:02 Checked & found, 4D OCB fdr #3 T/LO. Ctr: 357. (not change) R/F: 51@2,@3. Patrolled the line, but found nothing. 05:53 Blocked & closed 4D OCB fdr #3, Ok. Then normalized the block. Cause: Unidentified. | 3111029 | 1 | 3:43 | Night | Wednesday | 2015 | 9
1605 | 2015-09-16 21:15 | 2015-09-16 21:15 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Lightning | 0 | 21:15 Duri Field RTU failed. 21:17 Duri Field RTU back to normal. Appear alarm Duri Community fdr #1 Load dropped 45A (149-104A) (It was reported that no power at Sibayak Camp.) Not checked yet. | 3111028 | 1 | 21:15 | Night | Wednesday | 2015 | 9
1606 | 2015-09-16 21:15 | 2015-09-18 14:15 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked Duri Community ACB fdr #1 & found, normal. (R/F: Did not appear & Ctr: Did not change) Checked & found, Recloser o/p #KT-74 (Duri Community fdr #1) T/R 1x Ctr: 112-113. Patrolled the line & found, @1 broken Dead end Insulator o/p #SY-02. Cause: Lightning. | 3111028 | 1 | 21:15 | Night | Wednesday | 2015 | 9
1607 | 2015-09-17 23:59 | 2015-09-17 23:59 | CPI POWER SYSTEM | Foggy and Smoke | Normal Condition | - | CPI power system normal condition. |  | 1 | 23:59 | Night | Thursday | 2015 | 9
1608 | 2015-09-18 16:40 | 2015-09-18 16:40 | MINAS POWER PLANT |  |  | - | 16:40 S/U MGT #2, then Online the Unit at 17:15. (For running on test) |  | 1 | 16:40 | Afternoon | Friday | 2015 | 9
1609 | 2015-09-18 23:30 | 2015-09-18 23:30 | 115KV CENTRAL DURI - BATANG LINE | Foggy and Smoke | Lightning Arrester | 0 | 23:30 115KV C.Duri GCB #31 T/R 1x Ctr: 26-27 R/F: 67N, 87L & 21(@3-G) (Zone-2). 115KV C.Duri OCB #33 T/SO Ctr: 586-587. 115KV Sintong GCB #25 T/R 1x Ctr: Not reported yet. (115KV C.Duri-Sintong line) 23:32 Closed 115KV C.Duri OCB #33. Not checked yet. | 3111028 | 1 | 23:30 | Night | Friday | 2015 | 9
1610 | 2015-09-18 23:30 | 2015-09-25 08:30 | 115KV CENTRAL DURI - BATANG LINE | Foggy and Smoke | Lightning Arrester | 0 | 115KV C.Duri GCB #31 T/R 1x Ctr: 586-587. 115KV C.Duri OCB #33 T/SO Ctr: 26-27 R/F: 67N, 87L & 21(@3-G) (Zone-2). 115KV Sintong GCB #25 T/R 1x Ctr: 285-286 R/F: 67N, 87L & 21(@3-G) (Zone-2). (115KV C.Duri-Sintong line) Patrolled the line from Sintong toward Ujung Tanjung, but found nothing. Patrolled the line from C.Duri toward Ujung Tanjung & found, @3 broken L/A o/p #BTG-92. Cause: Lightning Arrester. | 3111028 | 1 | 23:30 | Night | Friday | 2015 | 9
1611 | 2015-09-19 13:10 | 2015-09-19 13:10 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 43 | Batang fdr #3 load dropped 42A (45-3A). Not checked yet. | 3111028 | 1 | 13:10 | Afternoon | Saturday | 2015 | 9
1612 | 2015-09-19 13:10 | 2015-09-22 10:10 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 43 | Checked & found, Recl. 36AL-13 (Batang fdr #3) T/R 1x Ctr: 117-118. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3111028 | 1 | 13:10 | Afternoon | Saturday | 2015 | 9
1613 | 2015-09-19 13:57 | 2015-09-19 13:57 | 13.8KV BANGKO FEEDER #4 | Heavy Rain | Lightning | 0 | Bangko fdr #4 load dropped 95A (215-120A). Not checked yet. | 3111028 | 1 | 13:57 | Afternoon | Saturday | 2015 | 9
1614 | 2015-09-19 13:57 | 2015-09-20 10:30 | 13.8KV BANGKO FEEDER #4 | Heavy Rain | Lightning | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 71-72. Also founs, Bangko GFPC T/R 1x Ctr: 473-474. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3111028 | 1 | 13:57 | Afternoon | Saturday | 2015 | 9
1615 | 2015-09-19 14:20 | 2015-09-19 14:20 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 14:20 It was reported b/o fuse for Tx o/p #01-09-20. (Duri Field fdr #3) 15:56 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-09-20. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3111028 | 1 | 14:20 | Afternoon | Saturday | 2015 | 9
1616 | 2015-09-19 14:35 | 2015-09-19 14:35 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 19 | 14:35 It was reported b/o fuse for Tx at Well So.Menggala #08. 15:34 Checked & found, @1 b/o 7.8SF fuse for 300kva Tx at Well So.Menggala #08. Performed TTR, Megger test the Tx & found, normal (good reading) Replaced b/o fuse above with same size then energized the Tx. Cause: Animal. (Monkey) | 3111028 | 1 | 14:35 | Afternoon | Saturday | 2015 | 9
1617 | 2015-09-19 19:00 | 2015-09-19 19:00 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 22 | 19:00 It was reported b/o fuse for Tx at Well Benar #16. (Bangko fdr #4) 20:52 Checked & found, @1 b/o 2.1Sf fuse for 100Kva Tx at Well Benar #16. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3111028 | 1 | 19:00 | Night | Saturday | 2015 | 9
1618 | 2015-09-20 18:07 | 2015-09-20 18:07 | 13.8KV NORTH DURI FEEDER #11 | Fair | Dead End Insulator | 0 | North Duri VCB fdr #11 T/R 1x. Not checked yet. | 3111028 | 1 | 18:07 | Afternoon | Sunday | 2015 | 9
1619 | 2015-09-20 18:07 | 2015-09-22 10:07 | 13.8KV NORTH DURI FEEDER #11 | Fair | Dead End Insulator | 0 | Checked & found, No.Duri VCB fdr #11 T/R 1x Ctr: 137-138 R/F: 51N(@2). Patrolled the line & found, @2 broken Dead end Insulator o/p #13-G7.2-33. Cause: Dead end Insulator. | 3111028 | 1 | 18:07 | Afternoon | Sunday | 2015 | 9
1620 | 2015-09-21 07:55 | 2015-09-21 07:55 | MINAS POWER PLANT |  |  | - | 07:55 Offline MGT #1, then S/D the Unit for S/B. (Prior to repairing Inlet Haust) |  | 1 | 7:55 | Morning | Monday | 2015 | 9
1621 | 2015-09-21 14:30 | 2015-09-21 14:30 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 14:30 It was reported b/o fuse for Tx at Well Pudu #18. (So.Bekasap fdr #1) 17:40 Checked & found, @1,@2 b/o 7.8SF fuses for 300kva Tx at Well Pudu #18. Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3111028 | 1 | 14:30 | Afternoon | Monday | 2015 | 9
1622 | 2015-09-22 08:00 | 2015-09-22 08:00 | 13.8KV 6DN FEEDER #5 | Fair | Secondary Cable | 30 | 08:00 It was reported b/o fuse for Tx at Well #6D-95. (6DN fdr #5) 13:45 Checked & found, @1 b/o 7.8SF fuse for 250Kva Tx at Well #6D-95. Performed TTR, Megger test the Tx & found. normal. (good reading) Replaced b/o fuse above with same size, then energized the Tx. Cause: B/O underground cable to switchboard. | 3111029 | 1 | 8:00 | Morning | Tuesday | 2015 | 9
1623 | 2015-09-22 20:09 | 2015-09-22 20:09 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 24 | Nella fdr #1 load dropped 94A (150-56A). Nella GFPC T/R 1x. (Ground fault alarm on Nella fdr #1) Not checked yet. | 3111028 | 1 | 20:09 | Night | Tuesday | 2015 | 9
1624 | 2015-09-22 20:09 | 2015-09-25 14:10 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 24 | Checked & found, Recl. 21V-01 (Nella fdr #1) T/R 1x Ctr: 93-94. Also found, Nella GFPC T/R 2x Ctr: 677-679 R/F: 51N(@3). Patrolled the line & found, @3 broken L/A on TP of Well Bangko #67. Cause: Lightning. | 3111028 | 1 | 20:09 | Night | Tuesday | 2015 | 9
1625 | 2015-09-23 08:42 | 2015-09-23 08:42 | 13.8KV S. BALAM FEEDER #4 | Fair | Lightning | 139 | So.Balam VCB fdr #4 T/R 1x. So.Balam GFPC T/R 1x. Not checked yet. | 3111028 | 1 | 8:42 | Morning | Wednesday | 2015 | 9
1626 | 2015-09-23 08:42 | 2015-09-25 13:42 | 13.8KV S. BALAM FEEDER #4 | Fair | Lightning | 139 | Checked & found, So.Balam VCB fdr #4 T/R 1x Ctr: 281-282 R/F: 51N(@1). Patrolled the line & found, @1 broken L/A on TP of Well Balam #19. Cause: Lightning. | 3111028 | 1 | 8:42 | Morning | Wednesday | 2015 | 9
1627 | 2015-09-23 11:44 | 2015-09-23 11:44 | 13.8KV NORTH DURI FEEDER #2 | Fair | Secondary Cable | 70 | 11:44 It was reported no power o/p #10-J6-18. (N.Duri fdr #2) 16:20 Checked & found, b/o fuse for 112.5Kva Tx o/p #10-J6-18. Also found broken secondary cable. Cause: Secondary Cable. (Will be replaced tomorrow) | 3111028 | 1 | 11:44 | Morning | Wednesday | 2015 | 9
1628 | 2015-09-23 11:44 | 2015-09-24 16:05 | 13.8KV NORTH DURI FEEDER #2 | Fair | Secondary Cable | 70 | Replaced broken secondary cable & fuse link for 112.5Kva Tx & energized the Tx o/p #10-J6-18. Cause: Secondary Cable. | 3111028 | 1 | 11:44 | Morning | Wednesday | 2015 | 9
1629 | 2015-09-23 14:25 | 2015-09-23 14:25 | MINAS POWER PLANT | Fair | Equipment Failure | - | 14:25 MGT #9 Tripped By Alarm: Bearing Header Temperature High. (Found T/O 480Volt Main Breaker) Cause: Short circuit of 88BT. 16:04 S/U MGT #9, then on line the unit at 16:35. |  | 1 | 14:25 | Afternoon | Wednesday | 2015 | 9
1630 | 2015-09-23 21:36 | 2015-09-23 21:36 | 13.8KV SINTONG FEEDER #1 | Cloudy | Equipment Failure | 151 | 21:36 Sintong OCB fdr #1 T/R 2x. Sintong GFPC T/R 2x. Ground fault alarm from Sintong fdr #1. 22:00 Sintong OCB fdr #1 T/R 1x again. Sintong GFPC T/R 1x. Ground fault alarm from at Sintong fdr #1. Not checked yet. Prod loss: 50 Bbls / 21 wells. (Bangko GS). Prod loss: 124 Bbls / 30 wells. (Balam GS). ---------------------------------- + Total : 174 Bbls / 51 Wells. | 3111028 | 1 | 21:36 | Night | Wednesday | 2015 | 9
1631 | 2015-09-23 21:36 | 2015-09-25 07:36 | 13.8KV SINTONG FEEDER #1 | Cloudy | Equipment Failure | 151 | Checked & found, Sintong OCB fdr #1 T/R 4x Ctr: 361-365 R/F: 51N. Also found, Sintong GFPC T/R 6x Ctr: 795-801. Patrolled the line & found, burnt out Main Breaker & @1,@3 b/o fuse holders for 150Kva Tx. (at Multi Structure yard) Cause: Equipment failure. (Burnt out Main Breaker) | 3111028 | 1 | 21:36 | Night | Wednesday | 2015 | 9
1632 | 2015-09-24 09:49 | 2015-09-24 09:49 | 13.8KV BATANG FEEDER #3 | Fair | Dead End Insulator | 42 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3111028 | 1 | 9:49 | Morning | Thursday | 2015 | 9
1633 | 2015-09-24 09:49 | 2015-09-29 14:30 | 13.8KV BATANG FEEDER #3 | Fair | Dead End Insulator | 42 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 278-279 R/F: 51N & 51@1. Patrolled the line & found, @1 flashed over Dead end Insulator o/p #37AL-17. Cause: Dead end Insulator. | 3111028 | 1 | 9:49 | Morning | Thursday | 2015 | 9
1634 | 2015-09-24 19:33 | 2015-09-24 19:33 | 13.8KV LIBO FEEDER #1 | Rain | Normal Condition | - | Libo fdr #1 load dropped 34A (103-69A). Not checked yet. 01-Oct-2015. Checked Libo OCB fdr #1 & found, No Relay flag & Counter did not change. (No recloser at downstream of Libo fdr #1 line) Cause: Suspected T/O WIP at Libo GS. Note: There is Prod. loss reported by EC. (13 Bbls / 12 Wells) | 3111028 | 1 | 19:33 | Night | Thursday | 2015 | 9
1635 | 2015-09-24 20:12 | 2015-09-24 20:12 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 33 | 20:12 So.Bekasap RTU Failed. 20:16 So.Bekasap fdr #1 load dropped 140A (162-22A). (Suspected So.Bekasap OCB fdr #1 T/R 1x) Not checked yet. | 3111028 | 1 | 20:12 | Night | Thursday | 2015 | 9
1636 | 2015-09-24 20:12 | 2015-09-29 14:46 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 33 | Checked & found, So.Bekasap OCB fdr #1 T/R 1x Ctr: 249-250 R/F: 51N(@1). Patrolled the line & found, @1 broken Dead end Insulator o/p #37BH-04. Cause: Lightning. | 3111028 | 1 | 20:12 | Night | Thursday | 2015 | 9
1637 | 2015-09-24 20:47 | 2015-09-24 20:47 | 13.8KV DURI FIELD FEEDER #1 | Rain and Lightning | Powerline - Conductor | 0 | 20:47 D.Field fdr #1 load dropped 34A (114-80A). 21:12 It was reported broken conductor at Road-4 toward CGS #1. 22:57 Checked & found Recl. 01-04-39 (D.Field fdr #1) T/LO. Ctr: 164-167. Patrolled the line & found, broken conductor between pole #01-04-22 and #01-04-25. Open Visual opening of Recl. 01-04-39, to isolate the broken conductor. Cut jumpers o/p #01-04-25. Closed Recl. 01-04-39. 25-Sep-2015. 00:21 Cut jumpers o/p #01-04-22. Closed LBS #01-04-01, to feed part load of CGS #1 by D.Field feeder #3. Cause: Broken conductor. | 3111028 | 1 | 20:47 | Night | Thursday | 2015 | 9
1638 | 2015-09-24 20:48 | 2015-09-24 20:48 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Lightning Arrester | 35 | 22:48 It was reported no power at Area-6 o/p #06-R7-03. 00:40 Checked & found, Recl. 06-R7-19 T/SO. Ctr: 638-640. Patrolled the line & found, @1 broken L/A & jumper touching to cross arm o/p #06-R7-03. 00:44 Open Visual opening of Recl. 06-R7-19. Dismantled jumper of L/A o/p #06-R7-03. 25-Sep-2015. 01:25 Blocked & closed Recl. 06-R7-19, but failed. Open Visual opening of Recl. 06-R7-19. 01:49 Transferring part load of D.Field fdr #4 to D.Field fdr #2. -Closed LBS #06-R7-02. (Load of Recl. 06-R7-19 feed by D.Field fdr #2) Cause: Broken L/A & jumper touching to cross arm. | 3111028 | 1 | 20:48 | Night | Thursday | 2015 | 9
1639 | 2015-09-25 10:00 | 2015-09-25 10:00 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified (Fuse) | 20 | 10:00 It was reported b/o fuse for Tx at Well KB #09. (CKBS fdr #1) 11:40 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well KB #09. Replaced b/o fuse above with the same size then Energized the Tx. Cause: Unidentified (fuse). | 3111029 | 1 | 10:00 | Morning | Friday | 2015 | 9
1640 | 2015-09-25 17:56 | 2015-09-25 17:56 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 4 | 17:56 It was reported b/o fuse for Tx o/p #08-M1-17. (C.Duri fdr #2) 20:25 Checked & found, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #08-M1-17. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3111028 | 1 | 17:56 | Afternoon | Friday | 2015 | 9
1641 | 2015-09-25 17:59 | 2015-09-25 17:59 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 0 | Ketigul fdr #2 load dropped 89A (106-17A). Not checked yet. | 3111028 | 1 | 17:59 | Afternoon | Friday | 2015 | 9
1642 | 2015-09-25 17:59 | 2015-09-29 14:45 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 0 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 171-172 R/F: 51N(@1). Patrolled the line & found: -@1 Broken L/A o/p #31AN-06. -@1 Flashed over Dead end Insulator o/p #30AN-33. Cause: Lightning. | 3111028 | 1 | 17:59 | Afternoon | Friday | 2015 | 9
1643 | 2015-09-26 07:31 | 2015-09-26 07:31 | 13.8KV CENTRAL DURI FEEDER #7 | Foggy and Smoke | Animal | 0 | C.Duri ACB fdr #7 T/R 1x Ctr: 459-460 R/F: 51N. Patrolled the line & found, a dead Squirrel under pole #03-6-16. (Found b/o fuses for 500Kva Tx o/p #03-6-16) Cause: Animal. (Squirrel) | 3111028 | 1 | 7:31 | Morning | Saturday | 2015 | 9
1644 | 2015-09-26 08:57 | 2015-09-26 08:57 | 13.8KV NORTH DURI FEEDER #2 | Foggy and Smoke | Unidentified (Fuse) | 0 | 08:57 It was reported b/o fuse for Tx o/p #10-K6-08. (N.Duri fdr #2) 11:00 Checked & found, @1, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #10-K6-08. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3111028 | 1 | 8:57 | Morning | Saturday | 2015 | 9
1645 | 2015-09-26 08:58 | 2015-09-26 08:58 | 13.8KV CENTRAL DURI FEEDER #7 | Foggy and Smoke | Animal | 0 | 08:58 It was reported b/o fuse for Tx o/p #03-6-16. (C.Duri fdr #7) 10:27 Checked & found, @2, @3 b/o 14.0SF fuses for 500Kva Tx o/p #03-6-16. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Squirrel) | 3111028 | 1 | 8:58 | Morning | Saturday | 2015 | 9
1646 | 2015-09-26 18:34 | 2015-09-26 18:34 | 13.8KV NELLA FEEDER #1 | Foggy and Smoke | Animal | 0 | 18:34 It was reported b/o fuse for Tx at Well Bangko #88. (Nella fdr #1) 19:57 Checked & found, @1, @2 b/o 7.0SF fuses for 225Kva Tx at Well Bangko #88. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Monkey) | 3111028 | 1 | 18:34 | Afternoon | Saturday | 2015 | 9
1647 | 2015-09-27 23:59 | 2015-09-27 23:59 | CPI POWER SYSTEM | Foggy and Smoke | Normal Condition | - | CPI Power System Normal Condition. |  | 1 | 23:59 | Night | Sunday | 2015 | 9
1648 | 2015-09-28 16:25 | 2015-09-28 16:25 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 7 | 16:25 It was reported b/o fuse for Tx o/p #08-M1-28. (C.Duri fdr #2) 18:15 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #08-M1-28. Replaced the b/o fuse with same size & energized the Tx. Cause: Animal. (Monkey) | 3111028 | 1 | 16:25 | Afternoon | Monday | 2015 | 9
1649 | 2015-09-28 16:50 | 2015-09-28 16:50 | 13.8KV KETIGUL FEEDER#1 | Fair | Transformer Failure | 11 | 16:50 It was reported b/o fuse for Tx at Well Kelok #05. 19:54 Performed TTR, Megger test the Tx & found, Unbalance TTR & Low megger reading. Cause: Tx failure. (Unbalance and low megger Tx) (The Tx is not replaced yet) | 3111028 | 1 | 16:50 | Afternoon | Monday | 2015 | 9
1650 | 2015-09-29 07:30 | 2015-09-29 07:30 | 13.8KV SINTONG FEEDER #1 | Fair | Pin Insulator | 8 | Sintong OCB fdr #2 T/R 1x. Fault alarm on Sintong fdr #1 & fdr #2. Not checked yet. | 3111028 | 1 | 7:30 | Morning | Tuesday | 2015 | 9
1651 | 2015-09-29 07:30 | 2015-01-10 11:30 | 13.8KV SINTONG FEEDER #1 | Fair | Pin Insulator | 8 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 397-398 R/F: 51N. Patrolled the line & found, @1 broken Pin Insulator o/p #27AF-02. Cause: Pin Insulator. | 3111028 | 1 | 7:30 | Morning | Tuesday | 2015 | 9
1652 | 2015-09-29 09:41 | 2015-09-29 09:41 | MINAS POWER PLANT |  |  | - | MGT #2 Tripped. By Alarm: Hydraulic Trip Pressure Low. Cause: Under Investigation. |  | 1 | 9:41 | Morning | Tuesday | 2015 | 9
1653 | 2015-09-29 09:45 | 2015-09-29 09:45 | MINAS POWER PLANT |  |  | - | 09:45 S/U MGT #6, then on line the Unit at 10:00. |  | 1 | 9:45 | Morning | Tuesday | 2015 | 9
1654 | 2015-09-29 10:33 | 2015-09-29 10:33 | MINAS POWER PLANT |  |  | - | 10:33 S/U MGT #1, then on line the Unit at 10:55. |  | 1 | 10:33 | Morning | Tuesday | 2015 | 9
1655 | 2015-09-29 11:17 | 2015-09-29 11:17 | 13.8KV CENTRAL DURI FEEDER #15 | Foggy and Smoke | Lightning Arrester | 3 | C.Duri ACB fdr #15 T/R 1x Ctr: 354-355 R/F: 50@2. Not patrolled yet. | 3111028 | 1 | 11:17 | Morning | Tuesday | 2015 | 9
1656 | 2015-09-29 11:17 | 2015-09-30 17:31 | 13.8KV CENTRAL DURI FEEDER #15 | Foggy and Smoke | Lightning Arrester | 3 | Patrolled the line & found, @2 broken L/A o/p #06-05-11A. Cause: Lightning Arrester. | 3111028 | 1 | 11:17 | Morning | Tuesday | 2015 | 9
1657 | 2015-09-29 14:22 | 2015-09-29 14:22 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 14:22 It was reported b/o fuse for Tx o/p #03-8A-02. (C.Duri fdr #5) 18:00 Checked & found, @3 b/o 2.1SF fuse for 112.5Kva Tx o/p #03-8A-02. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3111028 | 1 | 14:22 | Afternoon | Tuesday | 2015 | 9
1658 | 2015-09-29 14:55 | 2015-09-29 14:55 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 14:55 It was reported b/o fuse for Tx o/p #08-M1-33. (C.Duri fdr #2) 16:30 Checked & found, @3 b/o 2.1SF fuse for 112.5Kva Tx o/p #08-M1-33. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3111028 | 1 | 14:55 | Afternoon | Tuesday | 2015 | 9
1659 | 2015-09-29 15:20 | 2015-09-29 15:20 | MINAS POWER PLANT |  |  | - | 15:20 S/U MGT #5, then On line the Unit at 15:29. |  | 1 | 15:20 | Afternoon | Tuesday | 2015 | 9
1660 | 2015-09-29 16:00 | 2015-09-29 16:00 | MINAS POWER PLANT |  |  | - | 16:00 Off line MGT #9, then S/D the Unit at 16:01. (For S/B - Prior to replacing 88BT) |  | 1 | 16:00 | Afternoon | Tuesday | 2015 | 9
1661 | 2015-09-30 15:15 | 2015-09-30 15:15 | NORTH DURI POWER PLANT | Fair | Under investigation | 5217 | 15:15 NDC-CT #1, #2, #3 Tripped. By Alarm: .......................... Cause: Under Investigation. Frequency system dropped to 58.25Hz. (Load shedding Level-9): S.Balam fdr#1 T/O, then Closed at 17:05 fdr#2 T/O, then Closed at 17:05 Nella fdr#1 T/O, then Closed at 16:36 fdr#2 T/O, then Closed at 16:36 Bangko fdr#1 T/O, then Closed at 16:37 fdr#4 T/O, then Closed at 16:37 Bks main fdr#2 T/O, then Closed at 15:35 fdr#3 T/O, then Closed at 15:36 fdr#5 T/O, then Closed at 15:33 fdr#6 T/O, then Closed at 15:36 Pematang fdr#2 T/O, then Closed at 15:54 Petani fdr#2 T/O, then Closed at 17:57 Rokan fdr#2 T/O, then Closed at 18:23 fdr#3 T/O, then Closed at 18:23 fdr#4 T/O, then Closed at 18:24 Rangau fdr#2 T/O, then Closed at 16:28 Ketigul fdr#2 T/O, then Closed at 20:25 OKB fdr#2 T/O, then Closed at 17:29 CKB fdr#1 T/O, then Closed at 17:09 fdr#2 T/O, then Closed at 16:40 fdr#3 T/O, then Closed at 16:39 fdr#5 T/O, then Closed at 16:40 fdr#6 T/O, then Closed at 16:40 Minas fdr#1 T/O, then Closed at 16:51 fdr#3 T/O, then Closed at 16:51 fdr#4 T/O, then Closed at 16:51 3D fdr#3 T/O, then Closed at 16:54 fdr#4 T/O, then Closed at 16:53 fdr#5 T/O, then Closed at 15:39 fdr#6 T/O, then Closed at 15:5 4D fdr#1 T/O, then Closed at 15:55 fdr#2 T/O, then Closed at 16:56 fdr#3 T/O, then Closed at 16:56 fdr#4 T/O, then Closed at 16:56 fdr#5 T/O, then Closed at 16:57 fdr#6 T/O, then Closed at 16:55 6DN fdr#3 T/O, then Closed at 15:35 fdr#4 T/O, then Closed at 15:38 fdr#5 T/O, then Closed at 15:38 fdr#6 T/O, then Closed at 17:04 4B fdr#1 T/O, then Closed at 17:03 4B fdr#4 T/O, then Closed at 15:46 fdr#5 T/O, then Closed at 17:03 5B fdr#1 T/O, then Closed at 17:21 fdr#2 T/O, then Closed at 17:21 fdr#3 T/O, then Closed at 17:21 fdr#4 T/O, then Closed at 17:21 fdr#5 T/O, then Closed at 17:21 6D fdr#1 T/O, then Closed at 17:04 fdr#2 T/O, then Closed at 17:04 fdr#3 T/O, then Closed at 17:04 fdr#4 T/O, then Closed at 17:04 fdr#5 T/O, then Closed at 17:04 8D fdr#1 T/O, then Closed at 16:45 fdr#3 T/O, then Closed at 16:45 fdr#10 T/O, then Closed at 16:45 fdr#11 T/O, then Closed at 16:45 8C fdr#1 T/O, then Closed at 16:46 fdr#3 T/O, then Closed at 16:46 fdr#4 T/O, then Closed at 16:46 fdr#5 T/O, then Closed at 16:43 (MSU1 fdr#1) fdr#6 T/O, then Closed at 16:43 (MSU1 fdr#2) Manually Open, to unticipate spil at GS-5 & GS-6. 16:00 3D fdr#7 M/O, then Closed at 16:47 16:00 3D fdr#8 M/O, then Closed at 16:47 16:04 4B fdr#2 M/O, then Closed at 17:03 Continued to other page.... | 3111028 | 1 | 15:15 | Afternoon | Wednesday | 2015 | 9
1662 | 2015-09-30 15:15 | 2015-09-30 15:15 | NORTH DURI POWER PLANT | Fair | Under investigation | 5217 | 16:10 S/U NDC-CT #1, then On line at 16:32. 16:28 S/U NDC-CT #2, then On line at 16:58. 16:31 S/U MGT #9, then On line at 16:55. 17:00 S/U DGT #7, then On line at 17:20 17:00 S/U NDC-CT #3, then Online at 17:25. Prod. Loss North : Bekasap GS : 223 Bbls, 140 Wells. Pematang GS : 119 Bbls, 23 Wells. Petani GS : 260 Bbls, 33 Wells. Bangko GS : 884 Bbls, 182 Wells. Balam GS : 840 Bbls, 123 Wells. Prod Loss South : GS #1 : 1290 Bbls, 175 Wells. GS #2 : 909 Bbls, 172 Wells. GS #3 : 773 Bbls, 155 Wells. GS #4 : 691 Bbls, 140 Wells. GS #5 : 699 Bbls, 154 Wells. GS #6 : 280 Bbls, 103 Wells. KB GS : 494 Bbls, 192 Wells. Petapahan GS : 160 Bbls, 22 Wells. Total Production Loss : 7622 Bbls, 1614 Wells. Production loss Reported by EC : SLS (Minas + Kopet) = 3406 Bbls / 789 Wells. SLN (Bekasap + Bangko + Balam) = 1811 Bbls / 339 Wells. Grand Total Prod. loss = 5217 Bbls / 1128 Wells. | 3111028 | 1 | 15:15 | Afternoon | Wednesday | 2015 | 9
1663 | 2015-09-30 16:10 | 2015-09-30 16:10 | NORTH DURI POWER PLANT |  |  | - | 16:10 NDC#1 S/U, then On line at 16:32. | 123 | 1 | 16:10 | Afternoon | Wednesday | 2015 | 9
1664 | 2015-09-30 16:28 | 2015-09-30 16:28 | NORTH DURI POWER PLANT |  |  | - | 16:28 NDC#2 S/U, then On line at 16:58. | 123 | 1 | 16:28 | Afternoon | Wednesday | 2015 | 9
1665 | 2015-09-30 16:31 | 2015-09-30 16:31 | MINAS POWER PLANT |  |  | - | 16:31 MGT#9 S/U, then On line at 16:55. | 123 | 1 | 16:31 | Afternoon | Wednesday | 2015 | 9
1666 | 2015-09-30 17:00 | 2015-09-30 17:00 | DURI POWER PLANT |  |  | - | 17:00 DGT #7 S/U, then On line at 17:20. | 123 | 1 | 17:00 | Afternoon | Wednesday | 2015 | 9
1667 | 2015-09-30 17:00 | 2015-09-30 17:00 | NORTH DURI POWER PLANT |  |  | - | 17:00 S/U NDC-Ct #3, then Online at 17:25. |  | 1 | 17:00 | Afternoon | Wednesday | 2015 | 9
1668 | 2015-09-30 22:29 | 2015-09-30 22:29 | CENTRAL DURI POWER PLANT | Rain | Under investigation | - | 22:29 CGT #2 Tripped, By Alarm: Unknown Alarm and indication. (480Volt supply to GT MCC Tripped Off) 22:32 Closed C.Duri ACB #19. (Tie Breaker) Cause: Under investigation. |  | 1 | 22:29 | Night | Wednesday | 2015 | 9
1669 | 2015-01-10 05:46 | 2015-01-10 05:46 | 13.8KV 3D FEEDER #3 | Fair | Dead End Insulator | 24 | 3D OCB fdr #3 T/R 1x. Not checked yet. | 3123374 | 1 | 5:46 | Morning | Saturday | 2015 | 1
1670 | 2015-01-10 05:46 | 2015-05-10 06:58 | 13.8KV 3D FEEDER #3 | Fair | Dead End Insulator | 24 | Checked & found, 3D OCB fdr #3 T/R 2x Ctr: 579-581 R/F: 51@2,@3. Patrolled the line & found, @3 flashed over Dead end Insulator o/p #3C-25A. Cause: Dead end Insulator. | 3123374 | 1 | 5:46 | Morning | Saturday | 2015 | 1
1671 | 2015-01-10 08:50 | 2015-01-10 08:50 | DURI POWER PLANT |  |  | - | Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 8:50 | Morning | Saturday | 2015 | 1
1672 | 2015-01-10 16:33 | 2015-01-10 16:33 | CENTRAL DURI POWER PLANT |  |  | - | 16:33 S/U CGT #2, the on line the Unit at 17:10. 17:09 Open C.Duri ACB #19. (Tie Breaker) |  | 1 | 16:33 | Afternoon | Saturday | 2015 | 1
1673 | 2015-02-10 09:32 | 2015-02-10 09:32 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Secondary Cable | 0 | 09:32 It was reported b/o fuse for Tx o/p #08-M1-17. (C.Duri fdr #2) 15:56 checked & found, @1, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #08-M1-17. Also found spark at Tx Secondary Cable. Cause: Secondary Cable. (Will be replaced tomorrow) | 3123373 | 1 | 9:32 | Morning | Tuesday | 2015 | 2
1674 | 2015-02-10 09:32 | 2015-03-10 15:10 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Secondary Cable | 0 | Replaced broken secondary cable for 112.5Kva Tx o/p #08-M1-17, then energized the Tx. Cause: Secondary Cable. | 3123373 | 1 | 9:32 | Morning | Tuesday | 2015 | 2
1675 | 2015-02-10 09:59 | 2015-02-10 09:59 | 13.8KV PEMATANG FEEDER #2 | Foggy and Smoke | Pin Insulator | 44 | Pematang OCB fdr #2 T/R 1x. Not checked yet. | 3123373 | 1 | 9:59 | Morning | Tuesday | 2015 | 2
1676 | 2015-02-10 09:59 | 2015-06-10 13:40 | 13.8KV PEMATANG FEEDER #2 | Foggy and Smoke | Pin Insulator | 44 | Checked & found, Pematang OCB fdr #2 T/R 1x Ctr: 444-445 R/F: 51N. Patrolled the line & found, @1 broken Pin Insualtor o/p #34BC-80. Cause: Pin Insulator. | 3123373 | 1 | 9:59 | Morning | Tuesday | 2015 | 2
1677 | 2015-02-10 10:42 | 2015-02-10 10:42 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 10:42 It was reported b/o fuse for Tx o/p #04-03-07. (C.Duri fdr #9) 11:30 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-03-07. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3123373 | 1 | 10:42 | Morning | Tuesday | 2015 | 2
1678 | 2015-02-10 13:10 | 2015-02-10 13:10 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified (Fuse) | 6 | 13:10 It was reported b/o fuse for Tx at Well Tilan #16. (Ketigul fdr #1) 18:00 Checked & found, @1, @2 b/o 7.8SF fuses for 300Kva Tx at Well Tilan #16. Performed TTR & Megger Test the Tx, found good reading. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3123373 | 1 | 13:10 | Afternoon | Tuesday | 2015 | 2
1679 | 2015-02-10 17:20 | 2015-02-10 17:20 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified (Fuse) | 0 | It was reported @1,@2,@3 b/o fuses for 550Kva Tx at Well KB #362. (CKBS fdr #6) Performed TTR & Megger test the Tx, found Low Mega-ohm Reading Tx. Cause: Low Mega-ohm Reading Tx. (Will be replaced tomorrow) | 3123373 | 1 | 17:20 | Afternoon | Tuesday | 2015 | 2
1680 | 2015-02-10 17:20 | 2015-03-10 12:08 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified (Fuse) | 0 | Re-performed Megger test 550Kva Tx at Well KB #362 & found, good reading. Replaced @1, @2, @3 b/o fuse for Tx above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3123373 | 1 | 17:20 | Afternoon | Tuesday | 2015 | 2
1681 | 2015-02-10 17:25 | 2015-02-10 17:25 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 2 | It was reported b/o fuse for Tx at Well Kulin #70. (C.Duri fdr #1) Not checked yet. | 3123373 | 1 | 17:25 | Afternoon | Tuesday | 2015 | 2
1682 | 2015-02-10 17:25 | 2015-04-10 11:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 2 | Checked & found, @2 b/o 1.4SF fuse for 75Kva Tx at Well Kulin #70. Replaced b/o fuse with the same size then energized the Tx. Cause: Unidentified (fuse). | 3123373 | 1 | 17:25 | Afternoon | Tuesday | 2015 | 2
1683 | 2015-02-10 18:15 | 2015-02-10 18:15 | NORTH DURI POWER PLANT | Fair | Equipment Failure | 954 | 18:15 NDC-CT #3 Tripped, By Alarm: Gas Detected High level. Cause: Equipment failure. (DC Battery for Fire Protection System low, due to Power supply problem) Frequency system dropped to 59.01Hz. (Load shedding level-4) Rokan fdr#2 T/O, Closed at 19:00 3D fdr#3 T/O, Closed at 19:21. 3D fdr#5 T/O, Closed at 19:49. 4B fdr#4 T/O, Closed at 18:53. 4D fdr#2 T/O, Closed at 19:22. 4D fdr#3 T/O, Closed at 19:22. 4D fdr#4 T/O, Closed at 19:21. 4D fdr#5 T/O, Closed at 19:22. 4D fdr#6 T/O, Closed at 19:05. 5B fdr#1 T/O, Closed at 19:08. 5B fdr#3 T/O, Closed at 19:12. 5B fdr#4 T/O, Closed at 19:23. 5B fdr#5 T/O, Closed at 19:23. 6D fdr#2 T/O, Closed at 19:38. 6D fdr#5 T/O, Closed at 19:38. 6DN fdr#5 T/O, Closed at 19:09. 8D fdr#1 T/O, Closed at 19:19. 8D fdr#3 T/O, Closed at 19:20. 19:02 S/U MGT #9, then On Line the Unit at 19:18. 19:15 S/U DGT #7, then On Line the Unit at 19:33 21:30 S/U NDC-CT#3, then on line the Unit at 21:56. Prod Loss : GS#1 : 56 Bbls, 22 Wells. GS#2 : 56 Bbls, 25 Wells. GS#3 : 473 Bbls, 94 Wells. GS#4 : 133 Bbls, 88 Wells. GS#5 : 247 Bbls, 71 Wells. GS#6 : 156 Bbls, 57 Wells. Petani GS : 31 Bbls, 8 Wells. Total Prod Loss : 1152 Bbls, 365 Wells. Prod. loss reported by EC: SLS Prod. loss (all Minas GS) = 931 Bbls / 324 Wells. SLN Prod. loss (Rokan GS) = 23 Bbls / 7 Wells. Grand Total (Prod. loss) = 954 Bbls / 331 Wells. | 3123373 | 1 | 18:15 | Afternoon | Tuesday | 2015 | 2
1684 | 2015-02-10 19:02 | 2015-02-10 19:02 | MINAS POWER PLANT |  |  | - | 19:02 S/U MGT #9, then On Line the Unit at 19:18. | 123 | 1 | 19:02 | Night | Tuesday | 2015 | 2
1685 | 2015-02-10 19:15 | 2015-02-10 19:15 | DURI POWER PLANT |  |  | - | 19:15 S/U DGT #7, then On Line the Unit at 19:33 | 123 | 1 | 19:15 | Night | Tuesday | 2015 | 2
1686 | 2015-03-10 07:50 | 2015-03-10 07:50 | DURI POWER PLANT | Foggy and Smoke |  | - | 07:50 Offline DGT #7, then S/D the Unit for S/B. |  | 1 | 7:50 | Morning | Tuesday | 2015 | 3
1687 | 2015-03-10 19:22 | 2015-03-10 19:22 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx at Well Kulin #75. (C.Duri fdr #1) Not checked yet. | 3123373 | 1 | 19:22 | Night | Tuesday | 2015 | 3
1688 | 2015-03-10 19:22 | 2015-04-10 11:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 11:55 Checked & found, @2 b/o 1.0SF fuse for 45Kva Tx at Well Kulin #75. (C.Duri fdr #1) Replaced b/o fuse with the same size & energized the Tx. Cause: Unidentified (fuse). | 3123373 | 1 | 19:22 | Night | Tuesday | 2015 | 3
1689 | 2015-04-10 01:26 | 2015-04-10 01:26 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 38 | 01:26 It was reported b/o fuse for Tx at Well Pagar #28. (Ketigul fdr #2) 13:26 Checked & found, @2, @3 b/o 7.8SF fuses for 250Kva Tx at Well Pagar #28. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Bird) | 3123373 | 1 | 1:26 | Night | Friday | 2015 | 4
1690 | 2015-04-10 06:15 | 2015-04-10 06:15 | 13.8KV DURI FIELD FEEDER #3 | Foggy and Smoke | Unidentified | 0 | Duri Field ACB fdr #3 T/R 1x. Duri Field fdr #1 load drop 26 A (105-79A). Not checked yet. | 3123373 | 1 | 6:15 | Morning | Friday | 2015 | 4
1691 | 2015-04-10 06:15 | 2015-06-10 14:32 | 13.8KV DURI FIELD FEEDER #3 | Foggy and Smoke | Unidentified | 0 | Checked & found, Duri Field ACB fdr #3 T/R 1x Ctr: 205. (Did not operate) R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 6:15 | Morning | Friday | 2015 | 4
1692 | 2015-04-10 09:07 | 2015-04-10 09:07 | 13.8KV RANGAU FEEDER #2 | Foggy and Smoke | Lightning Arrester | 141 | 09:07 Rangau fdr #2 load dropped 73A (78-5A). 10:29 Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/SO. Ctr: 118-119. (In blocked position due to Rig activity at Well Jurong #05) 10:38 Blocked & closed Recl. 23BD-01, Ok. (and still in blocked position) Cause: Not patrolled yet. | 3123373 | 1 | 9:07 | Morning | Friday | 2015 | 4
1693 | 2015-04-10 09:07 | 2015-06-10 13:56 | 13.8KV RANGAU FEEDER #2 | Foggy and Smoke | Lightning Arrester | 141 | Patrolled the line downstream of Recl. 23BD-01 (Rangau fdr #2), but found nothing. Cause: Unidentified. Checked & found, Rangau OCB fdr #2 T/R 1x Ctr: 301-302 R/F: 51N(@3). Patrolled the line & found, @3 broken L/A o/p #25BC-07A. Cause: Lightning Arrester. | 3123373 | 1 | 9:07 | Morning | Friday | 2015 | 4
1694 | 2015-04-10 13:53 | 2015-04-10 13:53 | 13.8KV CENTRAL DURI FEEDER #10 | Foggy and Smoke | Unidentified | 0 | 13:53 C.Duri fdr #10 load dropped 101A (238-137A). 14:38 Checked & found, Recl. 05-M7-24 (C.Duri fdr #10) T/R 1x Ctr: 65-66. Not patrolled yet. | 3123373 | 1 | 13:53 | Afternoon | Friday | 2015 | 4
1695 | 2015-04-10 13:53 | 2015-06-10 15:53 | 13.8KV CENTRAL DURI FEEDER #10 | Foggy and Smoke | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 13:53 | Afternoon | Friday | 2015 | 4
1696 | 2015-04-10 17:58 | 2015-04-10 17:58 | 13.8KV CENTRAL DURI FEEDER #14 | Foggy and Smoke | Lightning Arrester | 0 | C.Duri ACB fdr #14 T/R 1x Ctr: 312-313 R/F: 50@1 & 51N. Not patrolled yet. | 3123373 | 1 | 17:58 | Afternoon | Friday | 2015 | 4
1697 | 2015-04-10 17:58 | 2015-06-10 15:58 | 13.8KV CENTRAL DURI FEEDER #14 | Foggy and Smoke | Lightning Arrester | 0 | Patrolled the line at downstream of C.Duri fdr #14, but found nothing. Cause: Unidentified. Also found, Recl. 05-P3-02 (C.Duri fdr #14) T/R 2x Ctr: 282-284. Patrolled the line & found, @3 broken L/A o/p #05-P3-09. Cause: Lightning Arrester. | 3123373 | 1 | 17:58 | Afternoon | Friday | 2015 | 4
1698 | 2015-04-10 18:30 | 2015-04-10 18:30 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Switchboard Problem | 4 | 18:30 It was reported b/o fuse for Tx at Well Kerang #17. (Sintong fdr #1) 21:12 Checked & found, @1, @2, @3 b/o 3.5SF fuses for 150Kva Tx at Well Kerang #17. Replaced b/o fuse above with the same size then energized the Tx. Cause: Switchboard Problem. (Broken Vacuum Contactor) | 3123373 | 1 | 18:30 | Afternoon | Friday | 2015 | 4
1699 | 2015-05-10 14:45 | 2015-05-10 14:45 | MINAS POWER PLANT | Foggy and Smoke | Under investigation | - | 14:45 MGT #9 Trip Off by Alarm: Exhaust Over Temperature Trip (GCV problem). Cause; Under Investigation. | 3123374 | 1 | 14:45 | Afternoon | Sunday | 2015 | 5
1700 | 2015-05-10 16:16 | 2015-05-10 16:16 | 13.8KV 8D FEEDER #1 | Foggy and Smoke | Switchboard Problem | - | It was reported no power at Well #8E-13. (8D fdr #1) Not checked yet. (Will be checked tomorrow / BOPD: 43 Bbls). | 3123373 | 1 | 16:16 | Afternoon | Sunday | 2015 | 5
1701 | 2015-05-10 16:16 | 2015-06-10 09:30 | 13.8KV 8D FEEDER #1 | Foggy and Smoke | Switchboard Problem | - | Checked & found, b/o Bus fuse for Switchboard at Well #8E-13. Open fuse holder to S/D 550Kva Tx at Well #8E-13. SPS replaced b/o fuses above with the same size & energized the Tx. (Found, Biawak at the Swithboard) Cause: Switchboard problem. (Animal / Biawak in the Switchboard) (No Prod. loss charge to PGT) | 3123373 | 1 | 16:16 | Afternoon | Sunday | 2015 | 5
1702 | 2015-05-10 17:00 | 2015-05-10 17:00 | DURI POWER PLANT |  |  | - | 17:00 S/U DGT #7, then Online the Unit at 17:20. |  | 1 | 17:00 | Afternoon | Sunday | 2015 | 5
1703 | 2015-06-10 05:37 | 2015-06-10 05:37 | 13.8KV KETIGUL FEEDER#1 | Foggy and Smoke | Animal | 10 | 05:37 It was reported b/o fuse for Tx at Well Tilan #16. (Ketigul fdr #1) 13:45 Checked & found, @1 b/o 10.4SF fuse for 500Kva Tx at Well Tilan #16. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Bird) | 3123373 | 1 | 5:37 | Morning | Wednesday | 2015 | 6
1704 | 2015-06-10 06:59 | 2015-06-10 06:59 | 13.8KV DURI FIELD FEEDER #1 | Foggy and Smoke | Unidentified | 0 | Duri Field fdr #1 load dropped 54A (85-31A). Checked & found, Recl. 01-06-30 (Duri Field fdr #1) T/R 2x Ctr: 81-83. Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 6:59 | Morning | Wednesday | 2015 | 6
1705 | 2015-06-10 08:34 | 2015-06-10 08:34 | 13.8KV CENTRAL DURI FEEDER #7 | Foggy and Smoke | Unidentified (Fuse) | 0 | 08:34 It was reported b/o fuse for Tx o/p #03-4-30A. (C.Duri fdr #7) 13:00 Checked & found, @2 b/o 7.0SF fuse for 225Kva Tx o/p #03-4-30A. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3123373 | 1 | 8:34 | Morning | Wednesday | 2015 | 6
1706 | 2015-06-10 10:58 | 2015-06-10 10:58 | 13.8KV CENTRAL DURI FEEDER #8 | Foggy and Smoke | Animal | 0 | 10:58 It was reported b/o fuse for Tx o/p #04-2-13B. (C.Duri fdr #8) 12:10 Checked & found, @2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #04-2-13B. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3123373 | 1 | 10:58 | Morning | Wednesday | 2015 | 6
1707 | 2015-07-10 10:36 | 2015-07-10 10:36 | 13.8KV CENTRAL DURI FEEDER #9 | Foggy and Smoke | Unidentified (Fuse) | 17 | 10:36 It was reported b/o fuse for Tx o/p #04-3-11A. (C.Duri fdr #9) 11:30 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-3-11A. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3123373 | 1 | 10:36 | Morning | Friday | 2015 | 7
1708 | 2015-07-10 13:19 | 2015-07-10 13:19 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Lightning | 0 | 44KV N.Duri GCB #1 (44KV N.Duri-Dumai line) T/R 1x. Not checked yet. | 3123373 | 1 | 13:19 | Afternoon | Friday | 2015 | 7
1709 | 2015-07-10 13:19 | 2015-12-10 08:58 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Lightning | 0 | Checked & found: 44KV No.Duri GCB #1 (44KV No.Duri - Dumai line) T/R 1x Ctr: 88-89 R/F: 50@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3123373 | 1 | 13:19 | Afternoon | Friday | 2015 | 7
1710 | 2015-07-10 15:17 | 2015-07-10 15:17 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 17 | So.Bekasap OCB fdr #1 T/R 1x. Not checked yet. | 3123373 | 1 | 15:17 | Afternoon | Friday | 2015 | 7
1711 | 2015-07-10 15:17 | 2015-10-10 15:38 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 17 | Checked & found, So.Bekasap OCB fdr #1 T/R 1x Ctr: 146-147 R/F: 51N(@1). Patrolled the line & found, @1 broken Dead end Insulator o/p #36BL-10. Cause: Lightning. | 3123373 | 1 | 15:17 | Afternoon | Friday | 2015 | 7
1712 | 2015-07-10 16:24 | 2015-07-10 16:24 | MINAS POWER PLANT |  |  | - | 16:24 S/U MGT #9, then on line the Unit at 16:47. |  | 1 | 16:24 | Afternoon | Friday | 2015 | 7
1713 | 2015-07-10 16:33 | 2015-07-10 16:33 | 13.8KV 8D FEEDER #11 | Foggy and Smoke | Transformer Failure | 27 | 16:33 It was reported b/o fuse for Tx at Well #8E-73E. (8D fdr #11) 17:22 Checked & found, @1,@2,@3 b/o 7.8SF fuses for 300Kva Tx at Well #8E-73E. Test TTR & Megger the Tx, found low megger reading. Cause: Transformer Failure. (The Tx would be changed tomorrow) | 3123374 | 1 | 16:33 | Afternoon | Friday | 2015 | 7
1714 | 2015-07-10 16:33 | 2015-08-10 11:15 | 13.8KV 8D FEEDER #11 | Foggy and Smoke | Transformer Failure | 27 | Replaced 300Kva Tx with the same size & Energized the Tx. | 3123374 | 1 | 16:33 | Afternoon | Friday | 2015 | 7
1715 | 2015-07-10 17:30 | 2015-07-10 17:30 | CENTRAL DURI POWER PLANT |  |  | - | 17:30 Off line CGT #3, then S/D the Unit for S/B. (Prior to repair the leaking lube oil at near Bearing-2) 17:31 Closed C.Duri ACb #39. (Tie Breaker) |  | 1 | 17:30 | Afternoon | Friday | 2015 | 7
1716 | 2015-08-10 17:05 | 2015-08-10 17:05 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 12 | Sintong fdr #1 load dropped 123A (216-93A). Sintong GFPC. (in block position) Not checked yet. | 3123373 | 1 | 17:05 | Afternoon | Monday | 2015 | 8
1717 | 2015-08-10 17:05 | 2015-10-10 13:55 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 12 | Checked & found, Recl. 19AN-04 (Sintong fdr #1) T/R 1x Ctr: 306-307. Patrolled the line & found, @1 broken Pin Insulator o/p #19AK-11. Cause: Lightning. | 3123373 | 1 | 17:05 | Afternoon | Monday | 2015 | 8
1718 | 2015-08-10 17:17 | 2015-08-10 17:17 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Lightning | 50 | Petani OCB fdr #1 T/R 1x. Not checked yet. | 3123373 | 1 | 17:17 | Afternoon | Monday | 2015 | 8
1719 | 2015-08-10 17:17 | 13/10/2015 09:48 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Lightning | 50 | Checked & found, Petani OCB fdr #1 T/R 1x Ctr: 174-175 R/F: 51@1. Patrolled the line & found, @1 flashed over Pin Insulator o/p #33AZ-34. Cause: Lightning. | 3123373 | 1 | 17:17 | Afternoon | Monday | 2015 | 8
1720 | 2015-08-10 17:17 | 2015-08-10 17:17 | CENTRAL DURI SWITCH YARD | Rain and Lightning | Under investigation | 0 | 17:17 C.Duri SY GCB #10 T/O. Ctr:..... R/F: 87B(@1) & 86B. C.Duri SY GCB #21 T/O. Ctr:..... C.Duri SY GCB #41 T/O. Ctr:..... 19:23 Blocked & closed C. Duri GCB #10, Ok. 19:24 Blocked & closed C. Duri GCB #21, but C. Duri GCB #21 & GCB #10 Trip again. 19:39 Isolated C.Duri GCB #21 by opening both Isolation Switch of GCB #21. 19:41 Blocked & closed GCB #10, ok. Then released the block. Blocked & closed GCB #41, ok. Then released the block. Cause: Under Investigation. | 3123373 | 1 | 17:17 | Afternoon | Monday | 2015 | 8
1721 | 2015-09-10 08:45 | 2015-09-10 08:45 | 13.8KV 8D FEEDER #2 | Fair | Planned Maintenance | 24 | 08:45 It was reported Leakage 300Kva Tx Tank at Well #8D-68. (8D fdr #2) (Then shutdown the Well for replacing the Tx) 15:50 Replaced 300Kva Tx with 550Kva Tx, then energized the Tx. Cause: Planned Maintenance. (Transformer Thank Leaks) | 123 | 1 | 8:45 | Morning | Thursday | 2015 | 9
1722 | 2015-09-10 10:06 | 2015-09-10 10:06 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 10:06 It was reported b/o fuse for Tx o/p #10-J6-21. (N.Duri fdr #6) 11:15 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #10-J6-21. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3123373 | 1 | 10:06 | Morning | Thursday | 2015 | 9
1723 | 2015-09-10 14:47 | 2015-09-10 14:47 | MINAS POWER PLANT |  |  | - | Off line MGT#5, then S/D the Unit for S/B. |  | 1 | 14:47 | Afternoon | Thursday | 2015 | 9
1724 | 2015-09-10 16:18 | 2015-09-10 16:18 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 25 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3123373 | 1 | 16:18 | Afternoon | Thursday | 2015 | 9
1725 | 2015-09-10 16:18 | 15/10/2015 17:31 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 25 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 296-297 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 16:18 | Afternoon | Thursday | 2015 | 9
1726 | 2015-10-10 01:38 | 2015-10-10 01:38 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 45 | 01:38 4D OCB fdr #4 T/R 1x. 4D fdr #5 load dropped 69A (136-67A). 17:34 Checked & found, 4D OCB fdr #4 T/R 1x Ctr: 249-250 R/F: 51@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3123374 | 1 | 1:38 | Night | Saturday | 2015 | 10
1727 | 2015-10-10 01:45 | 2015-10-10 01:45 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 43 | 01:45 6D OCB fdr #1 T/R 1x. 6D fdr #2 load dropped 20A (182-162A). 17:36 Checked & found, 6D OCB fdr #1 T/R 1x Ctr: 299-300 R/F: 51@1. Patrolled the line, but found nothing. Cause: Lightning. | 3123374 | 1 | 1:45 | Night | Saturday | 2015 | 10
1728 | 2015-10-10 04:51 | 2015-10-10 04:51 | 13.8KV CENTRAL DURI FEEDER #1 | Heavy Rain | Animal | 26 | C.Duri fdr #1 load dropped 46A (237-191A). Not checked yet. | 3123373 | 1 | 4:51 | Morning | Saturday | 2015 | 10
1729 | 2015-10-10 14:30 | 2015-10-10 14:30 | 13.8KV 8D FEEDER #2 | Fair | Low mega-ohm reading | 9 | 14:30 It was reported b/o fuse for Tx at Well #8E-91E. 14:55 Checked & found, @1,@2,@3 b/o 12K fuses for 225Kva Tx at Well #8E-91E. Tested the Tx & found, Low megger reading. Cause: Tx Failure. (Low megger reading) (Will be replaced Monday Oct,12,2015) | 3123374 | 1 | 14:30 | Afternoon | Saturday | 2015 | 10
1730 | 2015-10-10 14:42 | 2015-10-10 14:42 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 12 | Libo OCB fdr #1 T/R 1x Ctr: 350-351 R/F: 51N(@1). Not patrolled yet. | 3123373 | 1 | 14:42 | Afternoon | Saturday | 2015 | 10
1731 | 2015-10-10 14:42 | 2015-12-10 07:15 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 12 | Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 14:42 | Afternoon | Saturday | 2015 | 10
1732 | 2015-11-10 07:26 | 2015-11-10 07:26 | 13.8KV SINTONG FEEDER #1 | Cloudy | Animal | 0 | Sintong fdr #1 load dropped 120A (212-92A). Sintong GFPC T/R 1x. (Fault alarm on Sintong fdr #1) Not checked yet. | 3123373 | 1 | 7:26 | Morning | Tuesday | 2015 | 11
1733 | 2015-11-10 07:26 | 2015-12-10 14:26 | 13.8KV SINTONG FEEDER #1 | Cloudy | Animal | 0 | Checked & found, Recl. 19AN-04 (Sintong fdr #1) T/R 1x Ctr: 307-308. Patrolled the line & found, a dead Monkey under pole #19AL-07. (no materials damage) Cause: Animal. (Monkey) | 3123373 | 1 | 7:26 | Morning | Tuesday | 2015 | 11
1734 | 2015-11-10 07:31 | 2015-11-10 07:31 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Animal | 0 | Duri Field VCB fdr #1 T/R 1x. Not checked yet. | 3123373 | 1 | 7:31 | Morning | Tuesday | 2015 | 11
1735 | 2015-11-10 07:31 | 14/10/2015 07:47 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Animal | 0 | Checked & found, Duri Field VCB fdr #1 T/R 1x Ctr: 629-630 R/F: 51N. Patrolled the Line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 7:31 | Morning | Tuesday | 2015 | 11
1736 | 2015-11-10 10:13 | 2015-11-10 10:13 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 90 | 10:13 It was reported that b/o fuse for Tx o/p #08-M1-17. (C.Duri fdr #2) 13:30 Checked & found, @2 b/o 2.1SF fuse for 112.5Kva Tx o/p #08-M1-17. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3123373 | 1 | 10:13 | Morning | Tuesday | 2015 | 11
1737 | 2015-11-10 11:41 | 2015-11-10 11:41 | 13.8KV 6DN FEEDER #1 | Fair | Low mega-ohm reading | 42 | 11:41 It was reported b/o fuse for Tx at Well #4E-93E. (6DN fdr #1) 15:35 Checked & found, @3 b/o 7.8SF fuse for 300Kva Tx at Well #4E-93E. Performed TTR, Megger test the Tx & found, Low Megger Reading. Cause: Low Megger ohm Reading. (The Tx is not replaced yet) | 3123374 | 1 | 11:41 | Morning | Tuesday | 2015 | 11
1738 | 2015-11-10 11:41 | 2015-12-10 16:00 | 13.8KV 6DN FEEDER #1 | Fair | Low mega-ohm reading | 42 | 16:00 Replaced 300Kva Tx failure with 250Kva Tx, then energized the Tx. Cause: Tx failure. (Low megger reading) | 3123374 | 1 | 11:41 | Morning | Tuesday | 2015 | 11
1739 | 2015-11-10 12:00 | 2015-11-10 12:00 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 12:00 It was reported b/o fuse for Tx at Well N.Menggala #30. (Sintong fdr #1) 15:29 Checked & found, @1,@2, b/o 3.5SF fuses for 150Kva Tx at Well N.Menggala #30. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3123373 | 1 | 12:00 | Afternoon | Tuesday | 2015 | 11
1740 | 2015-11-10 12:22 | 2015-11-10 12:22 | 13.8KV BEKASAP FEEDER #6 | Fair | Dead End Insulator | 32 | Bekasap Main VCB fdr #6 T/R 1x. Bekasap fdr #5 Load dropped 260A (268-8A). T/O WIP at Bekasap EOR. Bekasap fdr #3 Load dropped 40A (171-131A). Not checked yet. | 3123373 | 1 | 12:22 | Afternoon | Tuesday | 2015 | 11
1741 | 2015-12-10 02:32 | 2015-12-10 02:32 | 13.8KV SO BEKASAP FEEDER #1 | Drizzle | Pin Insulator | 17 | So.Bekasap fdr #1 Load dropped 102 A (149-47A). Not Checked yet. | 3123373 | 1 | 2:32 | Night | Thursday | 2015 | 12
1742 | 2015-12-10 02:32 | 15/10/2015 14:46 | 13.8KV SO BEKASAP FEEDER #1 | Drizzle | Pin Insulator | 17 | Checked & found, Recl. 34BI-18 (So.Bekasap fdr #1) T/R 1x Ctr: 147-148 R/F: 51@2. Patrolled the line & found, @2 broken Pin Insulator o/p #33BH-12. Cause: Pin Insulator. | 3123373 | 1 | 2:32 | Night | Thursday | 2015 | 12
1743 | 2015-12-10 08:44 | 2015-12-10 08:44 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 43 | 08:44 Batang fdr #3 load dropped 49A (49-0A). (All RTU failed at that time / from 08:23-08:44) (Suspected Batang OCB fdr #3 T/R 1x) Not checked yet. | 3123373 | 1 | 8:44 | Morning | Thursday | 2015 | 12
1744 | 2015-12-10 08:44 | 15/10/2015 17:33 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 43 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 296-297 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 8:44 | Morning | Thursday | 2015 | 12
1745 | 2015-12-10 12:10 | 2015-12-10 12:10 | 13.8KV BATANG FEEDER #3 | Fair | Animal | 63 | 12:10 It was reported b/o fuses for Tx at Well Pemburu #16. 17:30 Checked and found @2, @3 b/o fuses for 150Kva Tx at well Pemburu #16. TTR and megger the Tx, Ok. Replaced the b/o fuses with same size, then energized the TX. Cause: Animal (Monkey). | 3123373 | 1 | 12:10 | Afternoon | Thursday | 2015 | 12
1746 | 2015-12-10 13:15 | 2015-12-10 13:15 | CENTRAL DURI POWER PLANT |  |  | - | 13:15 S/U CGT #3, then on line the Unit at 13:13. 13:30 C.Duri ACB #39. (Tie breaker) |  | 1 | 13:15 | Afternoon | Thursday | 2015 | 12
1747 | 2015-12-10 16:00 | 2015-12-10 16:00 | DURI POWER PLANT |  |  | - | 16:00 Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 16:00 | Afternoon | Thursday | 2015 | 12
1748 | 2015-10-13 05:56 | 2015-10-13 05:56 | 13.8KV MINAS FEEDER #6 | Fair | Unidentified | 140 | 05:56 Minas ACB fdr #6 T/LO. Ctr: 154-156 R/F: 51N. 06:50 Blocked & closed Minas ACB fdr #6, Ok. Then released the block. (After Patrolled the line, but found nothing) Cause: Unidentified. | 3123374 | 1 | 5:56 | Morning | Tuesday | 2015 | 10
1749 | 2015-10-13 11:50 | 2015-10-13 11:50 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 128 | 11:50 OKB fdr #2 Load dropped 134A (250-116A). 13:00 Checked & found, Recl. 38CW-08 (OKB fdr #2) T/SO. Ctr: 26-27. Patrolled the Line, but found nothing. 13:47 Blocked & closed Recl. 38CW-08, Ok. Then released the block. Cause: Unidentified. | 3123374 | 1 | 11:50 | Morning | Tuesday | 2015 | 10
1750 | 2015-10-13 13:05 | 2015-10-13 13:05 | 13.8KV 4B FEEDER #1 | Fair | Secondary Cable | 14 | 13:05 It was reported Smoke at Transformer, at well 2A.54N (4B fdr#1). Checked & found the 300 Kva Tx was Over heat S/D well above and Open FCO to de energized the TX. Cause : Secondary Cable | 3123374 | 1 | 13:05 | Afternoon | Tuesday | 2015 | 10
1751 | 2015-10-13 15:00 | 2015-10-13 15:00 | 13.8KV 5B FEEDER #5 | Cloudy | Low mega-ohm reading | 7 | 15:00 It was reported B/O fuse at well 4B67 (5B fdr#5). 17:00 Checked & found 225KvaTx was low megger reading. | 3123374 | 1 | 15:00 | Afternoon | Tuesday | 2015 | 10
1752 | 2015-10-13 15:45 | 2015-10-13 15:45 | 13.8KV BANGKO FEEDER #4 | Drizzle | Unidentified | 19 | Bangko fdr #4 Load dropped 45A (230-185A). Bangko GFPC T/R 1x. (Ground fault alarm at Bangko fdr #4) Not checked yet. | 3123373 | 1 | 15:45 | Afternoon | Tuesday | 2015 | 10
1753 | 2015-10-13 15:45 | 2015-10-14 14:00 | 13.8KV BANGKO FEEDER #4 | Drizzle | Unidentified | 19 | Checked Recloser at downstream & found normal. (Ctr. did not operate) Also found, Bangko GFPC T/R 1x Ctr: 476-477 R/F: 50N. Patrolled Bangko fdr #4 line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 15:45 | Afternoon | Tuesday | 2015 | 10
1754 | 2015-10-14 23:59 | 2015-10-14 23:59 | CPI POWER SYSTEM |  |  | - | Normal system condition. |  | 1 | 23:59 | Night | Wednesday | 2015 | 10
1755 | 2015-10-15 07:49 | 2015-10-15 07:49 | MINAS POWER PLANT |  |  | - | 07:49 Started Up MGT #5 and then On Line at 08:00 to restore the load. |  | 1 | 7:49 | Morning | Thursday | 2015 | 10
1756 | 2015-10-15 08:20 | 2015-10-15 08:20 | MINAS POWER PLANT |  |  | - | 08:20 Off line MGT #6 and then S/D for S/B waiting for repair. |  | 1 | 8:20 | Morning | Thursday | 2015 | 10
1757 | 2015-10-15 14:25 | 2015-10-15 14:25 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 14:25 It was reported b/o fuses o/p 06-P7-07. Checked & found @3 b/o fuse for 112.5Kva Tx. Performed TTR test & megger the Tx. Ok. Replaced the b/o fuse with same size, then energized the Tx.Ok. Cause: Animal ( Monkey). | 3123373 | 1 | 14:25 | Afternoon | Thursday | 2015 | 10
1758 | 2015-10-16 10:07 | 2015-10-16 10:07 | 13.8KV SINTONG FEEDER #1 | Cloudy | Unidentified | 0 | 10:07 Sintong fdr #1 dropped 150A (213-63A). Sintong GFPC T/R 1x. (Ground fault alarm at Sintong fdr #1) 14:00 Sintong fdr #1 load dropped again 82A (213-131A). Not checked yet. | 3123373 | 1 | 10:07 | Morning | Friday | 2015 | 10
1759 | 2015-10-16 10:07 | 2015-10-17 14:00 | 13.8KV SINTONG FEEDER #1 | Cloudy | Unidentified | 0 | Checked & found, Recl. 19AN-04 (Sintong fdr #1) T/R 1x Ctr: 308-309. Also found Sintong GFPC T/R 2x Ctr: 801-803 R/F: 51N. Patrolled the Line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 10:07 | Morning | Friday | 2015 | 10
1760 | 2015-10-17 13:51 | 2015-10-17 13:51 | 44KV MINAS - RUMBAI LINE | Foggy and Smoke | Unidentified | 0 | Minas ACB #21 (44KV Minas - Rumbai line) T/R 1x Ctr: 68-69 R/F: 51G(@1,@2). Not Patrolled yet. | 3123374 | 1 | 13:51 | Afternoon | Saturday | 2015 | 10
1761 | 2015-10-17 13:51 | 2015-10-20 12:44 | 44KV MINAS - RUMBAI LINE | Foggy and Smoke | Unidentified | 0 | Patrolled the Line, but found nothing. Cause: Unidentified. | 3123374 | 1 | 13:51 | Afternoon | Saturday | 2015 | 10
1762 | 2015-10-17 16:27 | 2015-10-17 16:27 | 13.8KV CENTRAL DURI FEEDER #12 | Foggy and Smoke | Capasitor Bank | 0 | C.Duri ACB fdr #12 T/R 1x Ctr: 471-472 R/F: 51N(@3). Not patrolled yet. | 3123373 | 1 | 16:27 | Afternoon | Saturday | 2015 | 10
1763 | 2015-10-17 16:27 | 2015-10-20 14:05 | 13.8KV CENTRAL DURI FEEDER #12 | Foggy and Smoke | Capasitor Bank | 0 | Patrolled the Line & found, @1,@3 b/o fuses for Cap. Bank o/p #05-M5-A6B Cause: Capacitor Bank. | 3123373 | 1 | 16:27 | Afternoon | Saturday | 2015 | 10
1764 | 2015-10-17 21:56 | 2015-10-17 21:56 | 13.8KV BEKASAP FEEDER #3 | Fair | Lightning Arrester | 61 | 21:56 Bekasap Main fdr #3 load dropped 32A (170-138A). 22:47 It was reported 15 Wells were no power. 18-Oct-2015. 00:25 Checked & found, Recl. 37BE-27 (Bekasap fdr #3) T/SO. Ctr: 164-165. 00:29 Blocked & closed Recl. 37BE-27, Ok. Then released the block. Total Prod loss: 87 Bbls / 15 wells. The line is not patrolled yet. | 3123373 | 1 | 21:56 | Night | Saturday | 2015 | 10
1765 | 2015-10-17 21:56 | 2015-10-20 14:53 | 13.8KV BEKASAP FEEDER #3 | Fair | Lightning Arrester | 61 | Patrolled the line & found, broken L/A o/p #37BE-30. Cause: Lightning Arrester. | 3123373 | 1 | 21:56 | Night | Saturday | 2015 | 10
1766 | 2015-10-18 16:29 | 2015-10-18 16:29 | 13.8KV BANGKO GFPC | Foggy and Smoke | Unidentified | 0 | Bangko GFPC T/R 1x. Ground fault alarm on Bangko fdr #4. (No load drop at any feeders) Not checked yet. | 3123373 | 1 | 16:29 | Afternoon | Sunday | 2015 | 10
1767 | 2015-10-18 16:29 | 2015-10-19 09:00 | 13.8KV BANGKO GFPC | Foggy and Smoke | Unidentified | 0 | Checked & found, Bangko GFPC T/R 1x Ctr: 477-478 R/F: 50N. Patrolled Bangko fdr #4 line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 16:29 | Afternoon | Sunday | 2015 | 10
1768 | 2015-10-18 18:32 | 2015-10-18 18:32 | 13.8KV RANGAU FEEDER #2 | Foggy and Smoke | Lightning Arrester | 37 | 18:32 Rangau fdr #2 load dropped 72A (79-7A). 22:16 Rangau fdr #2 load dropped again 65A (73-8A). Not checked yet. | 3123373 | 1 | 18:32 | Afternoon | Sunday | 2015 | 10
1769 | 2015-10-18 18:32 | 2015-10-22 17:30 | 13.8KV RANGAU FEEDER #2 | Foggy and Smoke | Lightning Arrester | 37 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 3x Ctr: 119-122. Patrolled the line & found, @1,@3 broken L/As o/p #NN. Cause: Lightning Arrester. | 3123373 | 1 | 18:32 | Afternoon | Sunday | 2015 | 10
1770 | 2015-10-18 23:29 | 2015-10-18 23:29 | 13.8KV 4B FEEDER #5 | Fair | Animal | 0 | 4B OCB fdr #5 T/R 1x. Not checked yet. | 3123374 | 1 | 23:29 | Night | Sunday | 2015 | 10
1771 | 2015-10-18 23:29 | 2015-10-20 12:41 | 13.8KV 4B FEEDER #5 | Fair | Animal | 0 | Checked & found, 4B OCB fdr #5 T/R 1x Ctr: 108-109 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator o/p #4B-115. Cause: Animal. (Monkey) | 3123374 | 1 | 23:29 | Night | Sunday | 2015 | 10
1772 | 2015-10-19 00:32 | 2015-10-19 00:32 | 13.8KV BANGKO FEEDER #4 | Foggy and Smoke | Animal | 0 | 00:32 It was reported b/o fuse for Tx at Well Genting #04. (Bangko fdr #4) 10:00 Checked & found, @2 b/o 1.0SF fuse for 45Kva Tx at Well Genting #04. Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal. (Squirrel) | 3123373 | 1 | 0:32 | Night | Monday | 2015 | 10
1773 | 2015-10-19 11:46 | 2015-10-19 11:46 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Animal | 86 | 11:46 Sintong VCB #1 T/R 1x. Production loss: 37 Bbls / 21 wells. (Bangko GS). Sintong GFPC T/R 1x. Production loss: 66 Bbls / 31 wells. (Balam GS). Ground fault alarm on Sintong fdr #1. Total : 103 Bbls / 52 wells. Sintong fdr #2 load dropped 41A (88-47A). Production loss: 6 Bbls / 4 wells. (Bangko GS). Not checked yet. | 3123373 | 1 | 11:46 | Morning | Monday | 2015 | 10
1774 | 2015-10-19 11:46 | 2015-10-21 16:46 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Animal | 86 | Checked & found: Sintong Fdr #1 T/R 1X, Ctr: 865-866, R/F: 51N. Sintong GFPC T/R 1X, Ctr: 803-804, R/F: Ground 1 OC 3 Trip current netral/ground. Patrolled the Line, found @1@2@3 Broken Dead-end insulator O/p 20-AP-01 toward well Meso #10. Cause : Animal (monkey). (not replaced yet) | 3123373 | 1 | 11:46 | Morning | Monday | 2015 | 10
1775 | 2015-10-19 13:27 | 2015-10-19 13:27 | 13.8KV SO BEKASAP FEEDER #1 | Foggy and Smoke | Unidentified (Fuse) | 0 | 13:27 It was reported b/o fuse for Tx at Well Ampuh #23. (So.Bekasap fdr #1) 17:30 Checked & found, @1, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx at Well Ampuh #23. Performed TTR & Megger Test, found good reading. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3123373 | 1 | 13:27 | Afternoon | Monday | 2015 | 10
1776 | 2015-10-19 17:06 | 2015-10-19 17:06 | 13.8KV KETIGUL FEEDER#3 | Foggy and Smoke | Animal | 6 | Ketigul VCB fdr #3 T/R 1x. Not checked yet. | 3123373 | 1 | 17:06 | Afternoon | Monday | 2015 | 10
1777 | 2015-10-19 17:06 | 2015-10-22 17:27 | 13.8KV KETIGUL FEEDER#3 | Foggy and Smoke | Animal | 6 | Checked & found, Ketgul VCB fdr #3 T/R 1x Ctr: 159-160 R/F: 51N(@3). Patrolled the line & found, @3 broken Dead end Insulator o/p #NN. Cause: Dead end Insulator. | 3123373 | 1 | 17:06 | Afternoon | Monday | 2015 | 10
1778 | 2015-10-20 10:10 | 2015-10-20 10:10 | 13.8KV BEKASAP FEEDER #2 | Foggy and Smoke | Planned Maintenance | 1545 | 10:10 Switching to Transfer load Pematang fdr #1 & fdr #2 to Bekasap fdr #2. (See switching procedure 20-Oct-2015 at 10:10) 11:25 Manually opened Recl. 32BD-12, Transfer load to Bekasap fdr #3 at 11:30. 11:35 Manually opened Recl. 37BD-40, then closed at 15:15. 17:20 Bekasap VCB fdr #2 T/O. (In Blocked position), then closed at 17:21. Cause: Maintenance Job. Prod. Loss: 259 bbls / 51 wells. (Pematang GS) 851 bbls / 53 wells. (Bekasap GS) Total : 1110 bbls / 104 wells. Prod. loss reported by EC = 1160 Bbls / 157 Wells. Additional Prod. loss by EC = 385 Bbls / 34 Wells. (Some wells were S/U on 21-Oct-2015) Grand Total Prod. loss by EC = 1545 Bbls / 191 Wells. | 123 | 1 | 10:10 | Morning | Tuesday | 2015 | 10
1779 | 2015-10-20 13:26 | 2015-10-20 13:26 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Pin Insulator | 0 | Sintong fdr #1 load dropped 124A (216-92A). Sintong GFPC T/R 1x. Not checked yet. | 3123373 | 1 | 13:26 | Afternoon | Tuesday | 2015 | 10
1780 | 2015-10-20 13:26 | 2015-10-21 13:26 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Pin Insulator | 0 | Checked & found, Recl. 19AN-04 (Sintong fdr #1) T/R 3x Ctr: 309-312. Also found, Sintong GFPC T/R 3x Ctr: 804-807. Patrolled the line & found, @3 broken Pin Insulator o/p #NN. (Near Well No.Menggala #05) Cause: Pin Insulator. | 3123373 | 1 | 13:26 | Afternoon | Tuesday | 2015 | 10
1781 | 2015-10-20 16:44 | 2015-10-20 16:44 | 13.8KV 4B FEEDER #5 | Foggy and Smoke | Planned Maintenance | 2 | 09:10 It was reported sparked o/p 4B-115 at GS#6 Gate. 16:44-17:00 S/D well 4B-73, 4B-53, 4B-63 D/S 4B fdr#5. Replaced @1@2@3 Broken Pin Insulator o/p 4B-115. Cause: Broken Pin Insulator. | 123 | 1 | 16:44 | Afternoon | Tuesday | 2015 | 10
1782 | 2015-10-20 18:41 | 2015-10-20 18:41 | 13.8KV KETIGUL FEEDER#1 | Foggy and Smoke | Dead End Insulator | 61 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3123373 | 1 | 18:41 | Afternoon | Tuesday | 2015 | 10
1783 | 2015-10-20 18:41 | 2015-10-23 09:49 | 13.8KV KETIGUL FEEDER#1 | Foggy and Smoke | Dead End Insulator | 61 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 161-162 R/F: 51N(@1). Patrolled the Line & found, @1 F/O Dead end Insulator o/p #NN. (Near Tilan test station) Cause: Dead end insulator. | 3123373 | 1 | 18:41 | Afternoon | Tuesday | 2015 | 10
1784 | 2015-10-20 22:11 | 2015-10-20 22:11 | 13.8KV CENTRAL DURI FEEDER #1 | Foggy and Smoke | Animal | 6 | 22:11 It was reported no power at Road-M3, Area-9. (C.Duri fdr #1) 23:01 Checked & found, Recl. 09-M3-01 (C.Duri fdr #1) T/SO. Ctr: 26-27. Blocked & closed Recl. 09-M3-01, Ok. Then released the block. Not patrolled yet. | 3123373 | 1 | 22:11 | Night | Tuesday | 2015 | 10
1785 | 2015-10-20 22:11 | 2015-10-22 17:11 | 13.8KV CENTRAL DURI FEEDER #1 | Foggy and Smoke | Animal | 6 | Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 22:11 | Night | Tuesday | 2015 | 10
1786 | 2015-10-21 11:35 | 2015-10-21 11:35 | 13.8KV CENTRAL DURI FEEDER #10 | Foggy and Smoke | Under investigation | 1187 | 11:35 C.Duri ACB fdr #10 T/LO. Ctr: 433-437 R/F: 51N(@1). 11:45 Blocked & closed C.Duri ACB fdr #10, but failed. 12:25 Opened Recl. 05-M7-24, then closed at 16:45. 12:30 Opened LBS #05-N3-24, then closed at 16:58. Opened LBS #05-N5-22, then closed at 17:05. 12:50 Patrolled the line & found, @1,@2,@3 b/o FCO for 1500Kva Tx at CGS #5. 13:13 Closed LBS #05-N1-33. (Part load of C.Duri fdr #10 fed from C.Duri fdr #2) 12:40 It was reported b/o fuse for 1500Kva Tx at CGS #5. (C.Duri fdr #10) 14:24 Then Replaced @2 b/o fuse for 1500Kva Tx at CGS #5 above. 13:55 Opened N.Duri VCB fdr #7. (Req. by Production team), then closed at 18:31. 14:40 Closed visual opening of Recl. 05-M7-24. (C.Duri fdr #10) 14:44 Blocked & closed C.Duri ACB fdr #10, but failed. Closed 4160V Tie Breaker at CGS #5 (between C.Duri fdr #10 & C.Duri fdr #11) 14:53 Opened isolation switch & by-pass VR. (D/S of C.Duri fdr #10) 14:55 Blocked & Closed C.Duri fdr #10, but failed. 14:58 Blocked C.Duri fdr #15, then release the block at 15:50. Transfer load C.Duri fdr #10 to C.Duri fdr #15 15:00 Closed LBS #05-N6-23A, but Recl. 06-P7-24 Tripped. 15:03 Opened LBS #05-N6-23A. 15:04 Blocked & closed Recl. 06-P7-24, then release the block. 15:45 Opened LBS at Riser pole of C.Duri fdr #10 at C.Duri Switch Yard. 15:50 Blocked & closed C.Duri fdr #10, but failed. (Breaker problem) 16:20 Closed LBS 05-N6-23A. 16:22 Opened C.Duri ACB fdr #2. (Req. by Production team), then Closed at 18:02. 16:45 Closed Recl. 05-M7-24. 16:53 By-passed Recl. 06-P7-24. (by Unplugged control cable Recloser) 16:56 Energized 1000Kva Tx at CGS #5. Cause: Under investigation. Prod. loss C.Duri fdr #2 = 192 Bbls/ 103 Wells C.Duri fdr #10= 492 Bbls/ 109 Wells. N.Duri fdr #7 = 739 Bbls/ 273 wells. Total = 1423 Bbls/ 485 wells. | 3123373 | 1 | 11:35 | Morning | Wednesday | 2015 | 10
1787 | 2015-10-22 12:23 | 2015-10-22 12:23 | 13.8KV RANGAU FEEDER #2 | Foggy and Smoke | Dead End Insulator | 35 | Rangau fdr #2 load dropped 67A (80-13A). Not checked yet. | 3123373 | 1 | 12:23 | Afternoon | Thursday | 2015 | 10
1788 | 2015-10-22 12:23 | 2015-10-26 19:23 | 13.8KV RANGAU FEEDER #2 | Foggy and Smoke | Dead End Insulator | 35 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: 122-123. Patrolled the line & found, Broken Dead end Insulator o/p #22BD-15. Cause: Dead End Insulator. | 3123373 | 1 | 12:23 | Afternoon | Thursday | 2015 | 10
1789 | 2015-10-22 18:21 | 2015-10-22 18:21 | 13.8KV BATANG FEEDER #3 | Foggy and Smoke | Unidentified | 43 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3123373 | 1 | 18:21 | Afternoon | Thursday | 2015 | 10
1790 | 2015-10-22 18:21 | 2015-10-26 19:21 | 13.8KV BATANG FEEDER #3 | Foggy and Smoke | Unidentified | 43 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 297-298 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 18:21 | Afternoon | Thursday | 2015 | 10
1791 | 2015-10-23 01:36 | 2015-10-23 01:36 | 13.8KV NELLA GFPC | Foggy and Smoke | Unidentified | 0 | Nella GFPC T/R 1x. (Ground fault alarm at Nella fdr #1) No load dropped at the fdrs. Checked & found Nella GFPC T/R 2x Ctr: 678-680 R/F: 51N. Patrolled Nella fdr #1 line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 1:36 | Night | Friday | 2015 | 10
1792 | 2015-10-23 06:40 | 2015-10-23 06:40 | 13.8KV PUNGUT FEEDER #1 | Foggy and Smoke | Pin Insulator | 39 | 06:40 Pungut OCB fdr #1 T/R 1x. Pungut fdr #2 load dropped 35A (77-42A). 15:24 Checked & found, Pungut OCB fdr #2 T/R 1x Ctr: 343-344 R/F: 51@1. Patrolled the Line & found: -@1 Broken Pin Insulator o/p #45BQ-19. (take of pole well Pungut #25) -@1 Broken Pin Insulator o/p #45BP-15. (toward well Pungut #21) -@1,@2 Broken Pin Insulators, and -@1,@2,@3 Broken Dead end Insulator o/p #45BP-7. (one span to Recl.45BP-9). Cause: Pin Insulator. | 3123373 | 1 | 6:40 | Morning | Friday | 2015 | 10
1793 | 2015-10-23 10:00 | 2015-10-23 10:00 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Planned Maintenance | 1 | 10:00-11:00 Blocked Sintong fdr #1 & GFPC. Open HLC o/p #20AO-08, to replace @1,@2,@3 Broken Dead End Insulators o/p #20AV-01. (S/D 1 well during the Maintenance Job) Cause: Maintenance Job. | 123 | 1 | 10:00 | Morning | Friday | 2015 | 10
1794 | 2015-10-23 23:00 | 2015-10-23 23:00 | MINAS POWER PLANT | Fair | Under investigation | - | MGT #3 Tripped by: SRV reference high alarm. Cause: Under investigation. |  | 1 | 23:00 | Night | Friday | 2015 | 10
1795 | 2015-10-24 07:28 | 2015-10-24 07:28 | 13.8KV PEMATANG FEEDER #2 | Foggy and Smoke | Transformer Failure | 0 | 07:28 It was reported b/o fuse for Tx at Well Pematang #23. (Pematang fdr #2) 15:30 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Pematang #23. Performed TTR, Megger test the Tx & found, Low mega ohm reading. Cause: Tx failure. (Low mega ohm reading) (The Tx is not replaced yet) | 3123373 | 1 | 7:28 | Morning | Saturday | 2015 | 10
1796 | 2015-10-24 11:10 | 2015-10-24 11:10 | 13.8KV CENTRAL DURI FEEDER #7 | Foggy and Smoke | Animal | 0 | 11:00 It was reported b/o fuse for Tx o/p #03-02-17. (C.Duri fdr #7) 14:15 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-02-17. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Squirrel) | 3123373 | 1 | 11:10 | Morning | Saturday | 2015 | 10
1797 | 2015-10-24 18:52 | 2015-10-24 18:52 | 13.8KV KETIGUL FEEDER#3 | Rain | Lightning Arrester | 6 | 18:52 Ketigul VCB fdr #3 T/LO. Ketigul fdr #1 load dropped 63A (165-102A). Ketigul fdr #2 load dropped 45A (108-63A). 19:07 Blocked & Closed Ketigul VCB fdr #3, ok. Then released the block. Not checked yet. | 3123373 | 1 | 18:52 | Afternoon | Saturday | 2015 | 10
1798 | 2015-10-24 18:52 | 2015-10-28 09:01 | 13.8KV KETIGUL FEEDER#3 | Rain | Lightning Arrester | 6 | Checked & found, Ketigul VCB fdr #3 T/LO. Ctr : 160-163 R/F: 51N. Patrolled the Line & found, @3 Broken L/A o/p #31AR-03. Cause: Lightning Arrester | 3123373 | 1 | 18:52 | Afternoon | Saturday | 2015 | 10
1799 | 2015-10-24 23:28 | 2015-10-24 23:28 | 13.8KV MENGGALA FEEDER #2 | Fair | Transformer Failure | 19 | 23:28 It was reported b/o fuse for Tx at Well Sikladi #10. (Menggala fdr #2) 25-Oct-2015 01:26 Checked & found, @2,@3 b/o 3.5SF fuses for 150Kva Tx at Well Sikladi #10. Performed TTR, Megger test the Tx & found, Zero megger Reading. Cause: Transformer Failure. (The Tx would be replaced tomorrow) | 3123373 | 1 | 23:28 | Night | Saturday | 2015 | 10
1800 | 2015-10-24 23:28 | 2015-10-25 12:37 | 13.8KV MENGGALA FEEDER #2 | Fair | Transformer Failure | 19 | 12:37 Replaced 150Kva Tx with 100Kva Tx at Well Sikaladi #10, then energized the Tx. Cause: Transformer Failure. | 3123373 | 1 | 23:28 | Night | Saturday | 2015 | 10
1801 | 2015-10-25 10:08 | 2015-10-25 10:08 | 13.8KV MENGGALA FEEDER #2 | Cloudy | Unidentified | 94 | Menggala OCB fdr #2 T/R 1x. Menggala GFPC was block position. Not checked yet. | 3123373 | 1 | 10:08 | Morning | Sunday | 2015 | 10
1802 | 2015-10-25 10:08 | 2015-10-27 09:30 | 13.8KV MENGGALA FEEDER #2 | Cloudy | Unidentified | 94 | Checked & found, Menggala OCB fdr #2 T/R 1x Ctr: 524-525 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 10:08 | Morning | Sunday | 2015 | 10
1803 | 2015-10-25 10:08 | 2015-10-25 10:08 | 13.8KV SINTONG FEEDER #1 | Cloudy | Animal | 27 | Sintong OCB fdr #1 T/R 1x. Sintong fdr #2 load dropped 47A (89-42A). Sintong GFPC T/R 1x. (Ground fault alarm at Sintong fdr #1) Not checked yet. | 3123373 | 1 | 10:08 | Morning | Sunday | 2015 | 10
1804 | 2015-10-25 10:08 | 2015-10-26 10:00 | 13.8KV SINTONG FEEDER #1 | Cloudy | Animal | 27 | Checked & found, Sintong OCB fdr #1 T/R 1x Ctr: 366-367 R/F: 51@2. Also found Sintong GFPC T/R 2x Ctr: 807-809. Patrolled the line & found a dead Monkey under TP of Well No.Menggala #12. Also found Recl. 19AN-04 (Sintong fdr #1), did not operate. (Ctr: 212) (Then functioned test the Recl. 19AN-04 & found, Recloser control / Push botton problem) Cause: Animal. (Monkey) | 3123373 | 1 | 10:08 | Morning | Sunday | 2015 | 10
1805 | 2015-10-25 10:30 | 2015-10-25 10:30 | 13.8KV KOTABATAK FEEDER #2 | Foggy and Smoke | Low mega-ohm reading | 1 | 10:30 It was reported b/o fuse for Tx at Well KB #275. (OKB fdr #2) 11:25 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well KB #275. Performed TTR, Megger test the Tx & found, Low Mega-ohm Reading Tx. 16:05 Replaced Tx above with the same size & energized the Tx. Cause: Tx failure. (Low Mega-ohm Reading Tx) | 3123374 | 1 | 10:30 | Morning | Sunday | 2015 | 10
1806 | 2015-10-25 11:49 | 2015-10-25 11:49 | 44KV PEMATANG MAIN - PETANI LINE | Foggy and Smoke | Unidentified | 67 | 44KV Pematang Main OCB #1 (Line to Petani) T/R 1x. Not checked yet. | 3123373 | 1 | 11:49 | Morning | Sunday | 2015 | 10
1807 | 2015-10-25 11:49 | 2015-10-30 10:49 | 44KV PEMATANG MAIN - PETANI LINE | Foggy and Smoke | Unidentified | 67 | Checked & found, 44KV Pematang Main OCB #1 (Line to Petani) T/R 1x Ctr: 548-549 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 11:49 | Morning | Sunday | 2015 | 10
1808 | 2015-10-25 15:15 | 2015-10-25 15:15 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 15:15 It was reported b/o fuse for Tx o/p #03-1-07. (C.Duri fdr #7) 17:44 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-1-07. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3123373 | 1 | 15:15 | Afternoon | Sunday | 2015 | 10
1809 | 2015-10-26 15:40 | 2015-10-26 15:40 | 13.8KV SO BEKASAP FEEDER #1 | Foggy and Smoke | Transformer Failure | 31 | 15:40 It was reported b/o fuse for Tx at Well Pudu #16. 17:00 Checked & found, @1, @2 b/o 7.8SF fuses for 300Kva Tx at Well Pudu #16. TTR & megger test the Tx, found, Low Megger reading. Cause: Tx failure. (The Tx is not replaced yet) | 3123373 | 1 | 15:40 | Afternoon | Monday | 2015 | 10
1810 | 2015-10-27 15:49 | 2015-10-27 15:49 | 13.8KV DURI FIELD FEEDER #3 | Foggy and Smoke | Animal | 0 | 15:49 It was reported b/o fuses for Tx o/p #01-05-23. 18:00 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #01-05-23. Replaced the b/o fuse with same size, then energized the Tx. Cause: Animal. (Squirrel) | 3123373 | 1 | 15:49 | Afternoon | Tuesday | 2015 | 10
1811 | 2015-10-27 17:43 | 2015-10-27 17:43 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #1 | Heavy Rain | Lightning | 0 | MSU-1 VCB fdr #1 (8C fdr #5) T/R 1x. Not checked yet. | 3123374 | 1 | 17:43 | Afternoon | Tuesday | 2015 | 10
1812 | 2015-10-27 17:43 | 2015-10-30 07:43 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #1 | Heavy Rain | Lightning | 0 | Checked & found, MSU-1 VCB fdr #1 (8C fdr #5) T/R 1x Ctr: 293-294 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3123374 | 1 | 17:43 | Afternoon | Tuesday | 2015 | 10
1813 | 2015-10-27 18:32 | 2015-10-27 18:32 | 13.8KV KETIGUL FEEDER#3 | Drizzle | Unidentified (L/A) | 6 | Ketigul VCB fdr #3 T/R 1x. Not checked yet. | 3123373 | 1 | 18:32 | Afternoon | Tuesday | 2015 | 10
1814 | 2015-10-27 18:32 | 2015-10-30 10:32 | 13.8KV KETIGUL FEEDER#3 | Drizzle | Unidentified (L/A) | 6 | Checked & found, Ketigul VCB fdr #3 T/R 1x Ctr: 163-164 R/F: 51N(@2). Patrolled the line & found, @2 broken L/A o/p #31AR-03. Cause: Lightning Arrester. | 3123373 | 1 | 18:32 | Afternoon | Tuesday | 2015 | 10
1815 | 2015-10-27 18:37 | 2015-10-27 18:37 | 115KV DURI - KOTABATAK JUNCTION LINE | Cloudy and Lightning | Lightning | 0 | 18:37 115KV DRB OCB #26 T/SO. 115KV DRB OCB #28 T/R 1x. 115Kv KBJ GCB #43 T/R 1x. 115Kv KBJ GCB #45 T/R 1x. (115Kv line Duri-KBJ). Duri Field TX #3 also de-energized at this event due to 115KV DRB OCB #22 in Open Position. (for maintenance schedule) 18:45 Closed 115KV DRB OCB #26. Not checked yet. | 3123373 | 1 | 18:37 | Afternoon | Tuesday | 2015 | 10
1816 | 2015-10-27 18:37 | 2015-10-30 10:37 | 115KV DURI - KOTABATAK JUNCTION LINE | Cloudy and Lightning | Lightning | 0 | Checked & found, 115KV DRB OCB #26 T/SO. Ctr: 898-899 115KV DRB OCB #28 T/R 1x Ctr: 115-116 R/F: 67N (Instan) & 21G-C. (Zone-1) 115KV KBJ GCB #43 T/R 1x Ctr: 410-411 115KV KBJ GCB #45 T/R 1x Ctr: 296-297 R/F: 67N (Instan), 21G-C & 87L-C. Patrolled the line from DRB toward DK-175 & found, @3 broken Dead end Insulator o/p #DK-154. Patrolled the line from KBJ toward DK-174, but found nothing. Cause: Lightning. | 3123373 | 1 | 18:37 | Afternoon | Tuesday | 2015 | 10
1817 | 2015-10-27 20:44 | 2015-10-27 20:44 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Tree | 45 | CKBS VCB fdr #1 T/R 3x. CKBS TX-1 GFPC did not operate. CKBS fdr #2 load dropped 239A (249-10A). CKBS fdr #3 load dropped 50A (58-8A). Not checked yet. | 3123374 | 1 | 20:44 | Night | Tuesday | 2015 | 10
1818 | 2015-10-27 20:44 | 2015-10-28 16:53 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Tree | 45 | Checked & found, CKBS VCB fdr #1 T/R 6x Ctr: 190-196 R/F: 51@B,@C. Patrolled the line, but found nothing. (Suspected Palm Tree thouched powerline) Cause: Tree. | 3123374 | 1 | 20:44 | Night | Tuesday | 2015 | 10
1819 | 2015-10-28 13:45 | 2015-10-28 13:45 | DURI POWER PLANT |  |  | - | 13:45 S/U DGT #7, then On line the Unit at 14:10. (CGT #2 will be S/D for repairing Inlet House) |  | 1 | 13:45 | Afternoon | Wednesday | 2015 | 10
1820 | 2015-10-28 23:59 | 2015-10-28 23:59 | CPI POWER SYSTEM | Foggy and Smoke | Normal Condition | - | CPI Power System Normal Condition. |  | 1 | 23:59 | Night | Wednesday | 2015 | 10
1821 | 2015-10-29 02:10 | 2015-10-29 02:10 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT #2, then S/D the Unit for S/B. (Prior to repairing Inlet House) |  | 1 | 2:10 | Night | Thursday | 2015 | 10
1822 | 2015-10-29 16:22 | 2015-10-29 16:22 | MINAS POWER PLANT |  |  | - | 29-Oct-2015 16:22 MGT #9 Tripped By Alarm: Hydraulic pressure supply low. Cause: Under investigation. 30-OCT-15 17:50:00 17:50 S/U MGT #9, then On line the Unit at 18:30. |  | 1 | 16:22 | Afternoon | Thursday | 2015 | 10
1823 | 2015-10-30 13:24 | 2015-04-10 15:24 | 13.8KV PETANI FEEDER #1 | Heavy Rain | Lightning | 50 | Checked & found, Petani OCB fdr #1 T/R 1x Ctr: 21-22 R/F: 51@3. Patrolled the line & found, @3 F/O Dead end Insulator o/p #33AX-28. Cause: Lightning. | 3123373 | 1 | 13:24 | Afternoon | Friday | 2015 | 10
1824 | 2015-10-30 13:24 | 2015-10-30 13:24 | 13.8KV PETANI FEEDER #1 | Heavy Rain | Lightning | 50 | Petani fdr #1 load drop 190A (210-20A). Petani fdr #2 load drop 16A (58-42). Not checked yet. | 3123373 | 1 | 13:24 | Afternoon | Friday | 2015 | 10
1825 | 2015-10-30 13:52 | 2015-10-30 13:52 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 26 | Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #1 load drop 13A (172-159A). Not checked yet. | 3123373 | 1 | 13:52 | Afternoon | Friday | 2015 | 10
1826 | 2015-10-30 13:52 | 2015-04-11 15:52 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 26 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 174-175 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3123373 | 1 | 13:52 | Afternoon | Friday | 2015 | 10
1827 | 2015-10-30 17:50 | 2015-10-30 17:50 | MINAS POWER PLANT |  |  | - | 17:50 S/U MGT #9, then On line the Unit at 18:30. |  | 1 | 17:50 | Afternoon | Friday | 2015 | 10
1828 | 2015-10-30 21:10 | 2015-10-30 21:10 | 13.8KV KETIGUL FEEDER#1 | Cloudy and Lightning | Lightning | 41 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3123373 | 1 | 21:10 | Night | Friday | 2015 | 10
1829 | 2015-10-30 21:10 | 2015-04-11 15:10 | 13.8KV KETIGUL FEEDER#1 | Cloudy and Lightning | Lightning | 41 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 162-163 R/F: 51N(@1). Patrolled the line & found, @1 F/O Dead end Insulator o/p #32AK-17B. Cause: Lightning. | 3123373 | 1 | 21:10 | Night | Friday | 2015 | 10
1830 | 2015-10-31 06:06 | 2015-10-31 06:06 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 06:06 It was reported b/o fuse for Tx at Well Kulin #82. (C.Duri fdr #1) 15:12 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx at Well Kulin #82. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3123373 | 1 | 6:06 | Morning | Saturday | 2015 | 10
1831 | 2015-10-31 12:05 | 2015-10-31 12:05 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 106 | 6D OCB fdr #2 T/R 1x. 6D fdr #1 load dropped 291A (318-27A). 6D fdr #3 load dropped 107A (115-89A). T/O WIP at GS-3. Not checked yet. | 3123374 | 1 | 12:05 | Afternoon | Saturday | 2015 | 10
1832 | 2015-10-31 12:05 | 2015-04-11 08:05 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 106 | Checked & found, 6D OCB fdr #2 T/R 1x Ctr: 231-232 R/F: 51@3. Patrolled the line & found, @3 broken Dead end Insulator o/p #6C-05. Cause: Lightning. | 3123374 | 1 | 12:05 | Afternoon | Saturday | 2015 | 10
1833 | 2015-10-31 12:05 | 2015-10-31 12:05 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 39 | 6DN fdr #5 load dropped 54A (133-79A) 6DN fdr #4 load dropped 146A (222-76A). T/O WIP at GS-3. Not checked yet. | 3123374 | 1 | 12:05 | Afternoon | Saturday | 2015 | 10
1834 | 2015-10-31 12:05 | 2015-04-11 08:05 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 39 | Checked & found, Recl. 6D-16A (6DN fdr #5) T/R 1x Ctr: 1206-1207. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3123374 | 1 | 12:05 | Afternoon | Saturday | 2015 | 10
1835 | 2015-10-31 12:32 | 2015-10-31 12:32 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 45 | 3D OCB fdr #4 T/R 1x. 3D GFPC-TX #1 T/R 1x. (Ground fault alarm on 3D fdr #4) Not checked yet. | 3123374 | 1 | 12:32 | Afternoon | Saturday | 2015 | 10
1836 | 2015-10-31 12:32 | 2015-04-11 08:32 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 45 | Checked & found, 3D OCB fdr #4 T/R 1x Ctr: 539-540 R/F: 51@1. Also found, 3D GFPC-TX #2 T/R 1x Ctr: 4060-4061. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3123374 | 1 | 12:32 | Afternoon | Saturday | 2015 | 10
1837 | 2015-10-31 16:00 | 2015-10-31 16:00 | 13.8KV ROKAN FEEDER #2 | Cloudy | Lightning Arrester | 14 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3123373 | 1 | 16:00 | Afternoon | Saturday | 2015 | 10
1838 | 2015-10-31 16:00 | 2015-06-11 17:00 | 13.8KV ROKAN FEEDER #2 | Cloudy | Lightning Arrester | 14 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 989-990 R/F: 51@2. Patrolled the line & found, @2 Broken L/A on TP of Well Kopar #08. Cause: Lightning Arrester. | 3123373 | 1 | 16:00 | Afternoon | Saturday | 2015 | 10
1839 | 2015-10-31 20:14 | 2015-10-31 20:14 | 13.8KV KOTABATAK FEEDER #2 | Heavy Rain | Lightning | 70 | OKB fdr #2 Load dropped 167A (263-96A). Not checked Yet. | 3123374 | 1 | 20:14 | Night | Saturday | 2015 | 10
1840 | 2015-10-31 20:14 | 2015-02-11 09:14 | 13.8KV KOTABATAK FEEDER #2 | Heavy Rain | Lightning | 70 | Checked & found, Recl. 38CX-25 T/R 1x Ctr: 88-89. Patrolled the line & found, @1 broken Pin Insulator o/p #40CY-04. Cause: Lightning. | 3123374 | 1 | 20:14 | Night | Saturday | 2015 | 10
1841 | 2015-10-31 20:20 | 2015-10-31 20:20 | 13.8KV CENTRAL KOTABATAK FEEDER #3 | Heavy Rain | Lightning | 61 | CKBS VCB fdr #3 T/R 1x. CKBS fdr #1 Load dropped 37A (73-36). CKBS fdr #2 Load dropped 250A (264-14A). T/O WIP at KB-GS. Not Checked Yet. | 3123374 | 1 | 20:20 | Night | Saturday | 2015 | 10
1842 | 2015-10-31 20:20 | 2015-02-11 10:20 | 13.8KV CENTRAL KOTABATAK FEEDER #3 | Heavy Rain | Lightning | 61 | Checked & found, CKBS VCB fdr #3 T/R 1x Ctr: 86-87 R/F: 51@1,@3. Patrolled the line & found: -@3 Broken Pin Insulator o/p #37CV-24. -Palm high Trees under power line & touching the line near pole #37CV-34. Cause: Lightning. | 3123374 | 1 | 20:20 | Night | Saturday | 2015 | 10
1843 | 2015-10-31 23:28 | 2015-10-31 23:28 | MINAS POWER PLANT | Fair | Under investigation | - | MGT #3 Tripped By Alarm: No alarm appear. (SRV / Gas Speed Ratio Valve problem) Cause: Under Investigation | 123 | 1 | 23:28 | Night | Saturday | 2015 | 10
1844 | 2015-01-11 09:36 | 2015-01-11 09:36 | 13.8KV 6D FEEDER #2 | Fair | Powerline - Jumper | 0 | 09:36 It was reported unbalance voltage at Well #6C-69. (6D fdr #2) 13:35 Checked & found, @1, @2 broken HLC Jumper at TOP of Well #6C-69. Opened all Fuses to de-energize the Tx. (The Jumpers are in safe condition & will be repair tomorrow) Cause: Jumper. | 3136056 | 1 | 9:36 | Morning | Sunday | 2015 | 1
1845 | 2015-01-11 09:36 | 2015-02-11 10:00 | 13.8KV 6D FEEDER #2 | Fair | Powerline - Jumper | 0 | Replaced the broken HLC Jumper, then energized the Tx & S/U Well #6C-69. Cause: Broken HLC jumper. | 3136056 | 1 | 9:36 | Morning | Sunday | 2015 | 1
1846 | 2015-01-11 15:30 | 2015-01-11 15:30 | 13.8KV 8C FEEDER #1 | Fair | Transformer Failure | 12 | 15:30 It was reported unbalance voltage at Well #10D-14. (8C fdr #1) 17:45 Checked & found, unbalance voltage at 150Kva Tx at Well #10D-14. Performed TTR, Megger test the Tx & found, low Mega-ohm reading Tx & bad TTR Test result. Cause: Transformer Failure. (Will be replaced tomorrow) | 3136056 | 1 | 15:30 | Afternoon | Sunday | 2015 | 1
1847 | 2015-01-11 15:30 | 2015-04-11 16:00 | 13.8KV 8C FEEDER #1 | Fair | Transformer Failure | 12 | Replaced 150Kva Tx with 300Kva Tx at well 10D-14 (8C fdr #1). Cause: Transformer Failure. | 3136056 | 1 | 15:30 | Afternoon | Sunday | 2015 | 1
1848 | 2015-01-11 23:48 | 2015-01-11 23:48 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 22 | It was reported b/o fuse for Tx at Well Bangko #317. Not checked yet. | 3136051 | 1 | 23:48 | Night | Sunday | 2015 | 1
1849 | 2015-01-11 23:48 | 2015-02-11 09:50 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 22 | Checked & found, @1 b/o fuse for 500Kva Tx at well Bangko #317 (Nella fdr #1). Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3136051 | 1 | 23:48 | Night | Sunday | 2015 | 1
1850 | 2015-02-11 02:22 | 2015-02-11 02:22 | CENTRAL DURI POWER PLANT | Fair | Under investigation | - | 02:22 CDGT #5 Tripped by alarm: Exhaust Over Temperature. Cause: Under Investigation. 18:16 S/U CGT #5 and then Online the unit at 18:50. |  | 1 | 2:22 | Night | Wednesday | 2015 | 2
1851 | 2015-02-11 07:04 | 2015-02-11 07:04 | 13.8KV MENGGALA FEEDER #2 | Fair | Unidentified | 39 | Menggala VCB fdr #2 T/R 1x. Menggala GFPC. (was in block position) Not checked yet. | 3136051 | 1 | 7:04 | Morning | Wednesday | 2015 | 2
1852 | 2015-02-11 07:04 | 2015-03-11 15:59 | 13.8KV MENGGALA FEEDER #2 | Fair | Unidentified | 39 | Checked & found, Menggala OCB fdr #2 T/R 1x Ctr: 525-526 R/F: 51@1. Patrolled the line, but found nothing. Cause: Unidentified. | 3136051 | 1 | 7:04 | Morning | Wednesday | 2015 | 2
1853 | 2015-02-11 10:30 | 2015-02-11 10:30 | CENTRAL DURI POWER PLANT |  |  | - | 10:30 S/U CGT #2, then online the Unit at 11:12. |  | 1 | 10:30 | Morning | Wednesday | 2015 | 2
1854 | 2015-02-11 15:45 | 2015-02-11 15:45 | MINAS POWER PLANT |  |  | - | 15:45 S/U MGT #3, then online the Unit at 16:00. |  | 1 | 15:45 | Afternoon | Wednesday | 2015 | 2
1855 | 2015-02-11 18:16 | 2015-02-11 18:16 | CENTRAL DURI POWER PLANT |  |  | - | 18:16 S/U CGT #5 and then Online the unit at 18:50. |  | 1 | 18:16 | Afternoon | Wednesday | 2015 | 2
1856 | 2015-02-11 18:17 | 2015-02-11 18:17 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 74 | 18:17 It was reported no power at Seruni field. (d/s of Sintong fdr #1) (No load drop indicated at Scada HMI at DSC) 19:20 Found, Recl. 25AD-26 (Sintong fdr #1) T/O. Ctr: 101-102. (in block for Rig HPS#08 activity at well Seruni#19) 19:35 Patrol line & found, b/o fuse for Tx at Well Seruni #26. Then Replaced @1 b/o fuse of 150Kva Tx with same size at Well Seruni #26. Cause: Animal. (Squirrel) 19:45 Blocked & closed Recl. 25AD-26, Ok. (The Recl. 25AD-26 is still in block for Rig HPS #08 activity) | 3136051 | 1 | 18:17 | Afternoon | Wednesday | 2015 | 2
1857 | 2015-03-11 10:40 | 2015-03-11 10:40 | 13.8KV 3D FEEDER #2 | Fair | Planned Maintenance | 0 | 10:40-10:50 S/D 550Kva Tx at Well #3E-65, to repair hotspot at @1, @2 FCO. Cause: Planned Maintenance. | 123 | 1 | 10:40 | Morning | Wednesday | 2015 | 3
1858 | 2015-03-11 10:45 | 2015-03-11 10:45 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 3 | 10:45 It was reported b/o fuse for Tx at Well So.Balam #82. (So.Balam fdr #4) 11:20 Checked & found, @3 b/o 2.1SF fuse for 100Kva Tx at Well So.Balam #82. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Squirrel) | 3136051 | 1 | 10:45 | Morning | Wednesday | 2015 | 3
1859 | 2015-03-11 13:16 | 2015-03-11 13:16 | 13.8KV BEKASAP FEEDER #3 | Fair | Transformer Failure | 5 | 13:16 It was reported b/o fuse for Tx at Well Jambon #02. 16:19 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Jambon #02. Performed TTR & Megger Test, found unbalance Tx. Cause: Transformer Failure. (Will be replaced tomorrow) | 3136051 | 1 | 13:16 | Afternoon | Wednesday | 2015 | 3
1860 | 2015-03-11 13:16 | 2015-07-11 10:00 | 13.8KV BEKASAP FEEDER #3 | Fair | Transformer Failure | 5 | Replaced Tx failure with the same size, energized the Tx & S/U the Well Jambon #02. Cause: Tx failure. | 3136051 | 1 | 13:16 | Afternoon | Wednesday | 2015 | 3
1861 | 2015-03-11 13:19 | 2015-03-11 13:19 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Rain and Lightning | Unidentified | 0 | 4.16Kv Dumai VCB fdr #5 (Industrial) T/R 1x Ctr: 274-275 R/F: 50@3. Not patrolled yet. | 3136051 | 1 | 13:19 | Afternoon | Wednesday | 2015 | 3
1862 | 2015-03-11 13:19 | 2015-06-11 14:19 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Rain and Lightning | Unidentified | 0 | Checked & found, 4.16Kv Dumai VCB fdr #5 (Industrial) T/R 1x Ctr: 274-275 R/F: 50@3. Patrolled the line, but found nothing. Cause: Unidentified. | 3136051 | 1 | 13:19 | Afternoon | Wednesday | 2015 | 3
1863 | 2015-03-11 16:36 | 2015-03-11 16:36 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 1661 | 16:36 Offline NDC-CT #1 then, S/D the Unit for S/B. (Prior to off line wash & close blanket plate) Manually load shedding. (Reduced 30MW at Minas area) Production loss Reported by: GS GS#1: -----> prod loss: 116 Bbls ( 39 wells and 3 WIP) GS#2: -----> prod loss: 175 Bbls ( 39 wells and 1 WIP) GS#3: -----> prod loss: 141 Bbls ( 25 wells and 1 WIP) GS#4: -----> prod loss: 178 Bbls ( 34 wells and 2 WIP) GS#5: -----> prod loss: 232 Bbls ( 42 wells and 2 WIP) GS#6: -----> prod loss: 290 Bbls ( 64 wells and 3 WIP) Total production loss :1132 Bblls (243 wells and 12 WIP). 04-Oct-2015. 17:43 S/U NDC-CT #1, then online the unit at 18:30. (after performing off line wash & closing blanket plate) Additional Prod. loss = 10MW (43 Wells & 2 WIP), Due to: -MGT #3 - Lube oil leak at Touring Fan (Load Gear compartment) -MGT #5 - Exhaust differential High Temp. (154F at load 6MW) -MGT #9 - Exhaust differential High Temp. (156F at load 26MW) Total Production Loss 04-Oct-2015 during Unit Down: -GS-1: 197 Bbls ( 51 wells and 3 WIP) -GS-2: 309 Bbls ( 45 wells and 1 WIP) -GS-3: 154 Bbls ( 19 wells and 1 WIP) -GS-4: 290 Bbls ( 44 Wells and 3 WIP) -GS-5: 424 Bbls ( 55 Wells and 2 WIP) -GS-6: 549 Bbls ( 72 Wells and 4 WIP) Total : 1923 Bbls (286 Wells and 14 WIP). Grand Total Prod. loss 03 & 04 Oct 2015 Reported by GS: 03-Oct-2015 - Total Prod. loss = 1132 Bbls. (243 Wells & 12 WIP) 04-Oct-2015 - Total Prod. loss = 1923 Bbls. (243 Wells & 12 WIP) + (43 Wells + 2 WIP) Grand Total Prod. loss = 3055 Bbls. (286 Wells & 14 WIP) Reported by EC (System): Total Prod. loss for 03 & 04 Nov 2015. (Prod. loss = 1661 Bbls & 283 Wells) + 14 WIPs. | 123 | 1 | 16:36 | Afternoon | Wednesday | 2015 | 3
1864 | 2015-04-11 10:30 | 2015-04-11 10:30 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 1 | 10:30-15:00 Open HLC o/p #40CY-01 to C/O broken Pin Insulator o/p 40CY-04. (3 wells were off during this job) Cause: Planned Maintenance. | 123 | 1 | 10:30 | Morning | Saturday | 2015 | 4
1865 | 2015-04-11 10:45 | 2015-04-11 10:45 | 13.8KV 3D FEEDER #2 | Fair | Planned Maintenance | 0 | 10:45-11:00 S/D 300Kva Tx at Well #2F-82. (d/s 3D fdr #2), to repair hotspot at Tx Primary Bushing. Cause: Planned Maintenance. | 123 | 1 | 10:45 | Morning | Saturday | 2015 | 4
1866 | 2015-04-11 17:43 | 2015-04-11 17:43 | NORTH DURI POWER PLANT |  |  | - | 17:43 S/U NDC-CT #1, then online the Unit at 18:30. Total Production Loss Today (04-Oct-2015), during Unit Down: -GS-1: 197 Bbls ( 51 wells & 3 WIP) -GS-2: 309 Bbls ( 45 wells & 1 WIP) -GS-3: 154 Bbls ( 19 wells & 1 WIP) -GS-4: 290 Bbls ( 44 Wells & 3 WIP) -GS-5: 424 Bbls ( 55 Wells & 2 WIP) -GS-6: 549 Bbls ( 72 Wells & 4 WIP) Total : 1923 Bbls (286 Wells & 14 WIP). | 123 | 1 | 17:43 | Afternoon | Saturday | 2015 | 4
1867 | 2015-05-11 06:30 | 2015-05-11 06:30 | DURI POWER PLANT |  |  | - | 06:30 Off line DGT #7, then S/D the Unit for Not S/B. (Lube Oil leaks from Header Line to Generator Bearing at Load Gear compartment) | 123 | 1 | 6:30 | Morning | Monday | 2015 | 5
1868 | 2015-05-11 08:27 | 2015-05-11 08:27 | MINAS POWER PLANT |  |  | - | Off line MGT #3, then S/D the Unit for S/B. (Prior to repairing leaking lube oil flushing sealing air) |  | 1 | 8:27 | Morning | Monday | 2015 | 5
1869 | 2015-05-11 10:00 | 2015-05-11 10:00 | MOBILE SUBSTATION 1 | Fair | Planned Maintenance | 21 | 10:00 11:25 Switching procedure to Transfer load MSU fdr #1 to 8C fdr #3. MSU fdr #2 to 8C fdr #1. (To shutdown 115KV MSU GCB for refilling SF-6 Gas) 10:24-11:23 De & Re-Energized Recl. 9D-25 (8C fdr #1). Cause: Maintenance Job. | 123 | 1 | 10:00 | Morning | Monday | 2015 | 5
1870 | 2015-05-11 10:05 | 2015-05-11 10:05 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 28 | 10:05 It was reported no power at Benar-GS. 10:45 Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/SO. (In Block position) Ctr: 72-73. Blocked & closed Recl. 25Z-07, Ok. The line is not patrolled yet. | 3136051 | 1 | 10:05 | Morning | Monday | 2015 | 5
1871 | 2015-05-11 10:05 | 2015-06-11 13:05 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 28 | Patrolled the line, but found nothing. Cause: Unidentified. | 3136051 | 1 | 10:05 | Morning | Monday | 2015 | 5
1872 | 2015-05-11 16:30 | 2015-05-11 16:30 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 28 | Bangko fdr #4 Load dropped 64A (194-130A). Bangko GFPC T/R 1x. Not Checked yet. | 3136051 | 1 | 16:30 | Afternoon | Monday | 2015 | 5
1873 | 2015-05-11 16:30 | 2015-06-11 15:30 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 28 | Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 73-74. Patrolled the line & found, @1 broken Pin support Insulator o/p #28AA-10. Cause: Pin Insulator. | 3136051 | 1 | 16:30 | Afternoon | Monday | 2015 | 5
1874 | 2015-05-11 22:32 | 2015-05-11 22:32 | 13.8KV BANGKO FEEDER #4 | Cloudy | Animal | 67 | Bangko OCB fdr #4 T/R 1x. Bangko GFPC T/R 1x. Bangko fdr #1 dropped 22A (283-261A). Not checked yet. | 3136051 | 1 | 22:32 | Night | Monday | 2015 | 5
1875 | 2015-05-11 22:32 | 2015-06-11 15:32 | 13.8KV BANGKO FEEDER #4 | Cloudy | Animal | 67 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99975-99976 R/F: 50@3. Also checked Bangko GFPC Ctr: 479. (Did not change) Patrolled the line & found, a dead Bird under TP of Well Bangko #321. Cause: Animal. (Bird) | 3136051 | 1 | 22:32 | Night | Monday | 2015 | 5
1876 | 2015-06-11 15:15 | 2015-06-11 15:15 | MINAS POWER PLANT |  |  | - | 15:15 S/U MGT #3, then on line the Unit at 15:26. |  | 1 | 15:15 | Afternoon | Thursday | 2015 | 6
1877 | 2015-06-11 16:06 | 2015-06-11 16:06 | MINAS POWER PLANT |  |  | - | Off line MGT #5, then S/D the Unit for S/B. (Prior to replacing fuel Nozzle, Cleaning Gas Strainer & Inlet House) |  | 1 | 16:06 | Afternoon | Thursday | 2015 | 6
1878 | 2015-06-11 16:09 | 2015-06-11 16:09 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 8 | 16:09 It was reported b/o fuse at Well Bangko #153. (Bangko fdr #4) 17:00 Checked & found, @1,@2 b/o 2.1SF fuses for 100Kva Tx at Well Bangko #153. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3136051 | 1 | 16:09 | Afternoon | Thursday | 2015 | 6
1879 | 2015-07-11 16:59 | 2015-07-11 16:59 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 98 | 16:59 CKB VCB fdr #1 T/SO. CKB fdr #2 load drop 258 A (265-7). CKB fdr #3 load drop 50 A (58-8). CKB fdr #5 load drop 258 A (339-81). CKB fdr #6 load drop 129 A (207-78). OKB fdr #2 load drop 20 A (268-248). NKB fdr #3 load drop 34 A (337-303). NKB fdr #5 load drop 109 A (235-36). Petapahan fdr #2 load drop 22 A (162-140). 17:40 Patrolled the line & found, @1,@2 broken L/A o/p #36CW-08. (Then isolated the broken L/A above) 18:10 Checked & found, CKBS VCB fdr #1 T/LO. Ctr: 196-200 R/F: 51@1,@2. 18:15 Blocked & closed CKBS VCB fdr #1, Ok. Then normalized the block. Cause: Lightning. | 3136056 | 1 | 16:59 | Afternoon | Saturday | 2015 | 7
1880 | 2015-08-11 01:03 | 2015-08-11 01:03 | 44KV MINAS - RUMBAI LINE | Rain | Lightning | 0 | 13.8Kv Minas ACB #21 (44Kv line Minas-Rumbai line) T/R 1x Ctr: 69-70 R/F: 51G (@1,@2). Not patrolled yet. | 3136056 | 1 | 1:03 | Night | Tuesday | 2015 | 8
1881 | 2015-08-11 01:03 | 2015-12-11 13:03 | 44KV MINAS - RUMBAI LINE | Rain | Lightning | 0 | Patrol the line & found, @1 F/O Suspension Insulator o/p #MR-35. Cause: Lightning. | 3136056 | 1 | 1:03 | Night | Tuesday | 2015 | 8
1882 | 2015-08-11 03:55 | 2015-08-11 03:55 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Pin Insulator | 159 | 03:55 Batang fdr #2 load dropped 25A (32-7A). It was reported no power at Rantau Bais-GS. 06:56 Checked & found, Recl. 36AG-11 (Batang fdr #2) T/SO. Ctr: 2988-2989. Also found @1, @2 b/o PT fuse. (Then Replaced b/o fuse for PT of Recl. 36AG-11) 07:00 Blocked & closed, Recl. 36AG-11, but failed. (Found Batt DC Voltage of Recl. 36AG-11 is LOW) 09:32 Open Batang OCB fdr #2. (from DSC) 09:35 Bypass Recl. 36AG-11. 09:40 Blocked & closed Batang OCB fdr #2, Ok. Then released the block. The line is not patrolled yet. | 3136051 | 1 | 3:55 | Night | Tuesday | 2015 | 8
1883 | 2015-08-11 03:55 | 2015-12-11 13:33 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Pin Insulator | 159 | Patrolled the line & found, @1 broken Pin Insulator o/p #36AF-10. Cause: Lightning. | 3136051 | 1 | 3:55 | Night | Tuesday | 2015 | 8
1884 | 2015-08-11 04:08 | 2015-08-11 04:08 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 0 | Batang OCB fdr #2 T/R 1x. Not checked yet. | 3136051 | 1 | 4:08 | Morning | Tuesday | 2015 | 8
1885 | 2015-08-11 04:08 | 2015-12-11 14:08 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Batang OCB fdr #2 T/R 1x Ctr: 108-109 R/F: 51N(@1). Patrolled the line & found, @1 broken Pin Insulator o/p #39AI-31. Cause: Lightning. | 3136051 | 1 | 4:08 | Morning | Tuesday | 2015 | 8
1886 | 2015-08-11 14:08 | 2015-08-11 14:08 | 13.8KV KETIGUL FEEDER#2 | Heavy Rain | Lightning | 25 | 14:08 Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #1 load dropped 11A (174-163A). 15:55 Ketigul VCB fdr #2 T/R 1x again. Not checked yet. | 3136051 | 1 | 14:08 | Afternoon | Tuesday | 2015 | 8
1887 | 2015-08-11 14:08 | 2015-12-11 14:00 | 13.8KV KETIGUL FEEDER#2 | Heavy Rain | Lightning | 25 | Checked & found, Ketigul VCB fdr #2 T/R 2x Ctr: 175-177 R/F: 51N(@1). Patrolled the ine, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 14:08 | Afternoon | Tuesday | 2015 | 8
1888 | 2015-08-11 15:54 | 2015-08-11 15:54 | 115KV MINAS - 5B LINE | Rain and Lightning | Lightning | 95 | 15:54 115Kv MSY GCB #51 T/SO. 115Kv MSY GCB #53 T/SO. 115Kv 5B GCB #22 T/R 1x. 115Kv 5B GCB #25 T/R 1x. (115Kv Minas - 5B Substation Line T/O) Respectively load dropped: 6D fdr #1 load drop 262A (314-52A). 6D fdr #2 load drop 116A (169-53A). 6D fdr #3 load drop 105A (114-9A). 6D fdr #4 load drop 73A (195-122A). 6D fdr #5 load drop 49A (265-216A). 6D fdr #6 load drop 118A (248-130A). 6DN fdr #3 load drop 50A (198-148A). 6DN fdr #4 load drop 62A (220-158A). 6DN fdr #6 load drop 55A (206-151A). 16:20 Checked and found: 115Kv MSY GCB #51 T/SO. Ctr: 175-176 R/F: 87L-@A, 21G-@A, 67N (Inst.) & 86L. 115Kv MSY GCB #53 T/SO. Ctr: 159-160. 16:24 115Kv MSY GCB #53. (auto closed when Resetting the Relays) 16:43 Closed 115Kv MSY GCB #51. Not checked yet. | 3136056 | 1 | 15:54 | Afternoon | Tuesday | 2015 | 8
1889 | 2015-08-11 15:54 | 2015-08-11 15:54 | 13.8KV 8D FEEDER #4 | Rain and Lightning | Lightning | 17 | 8D OCB fdr #4 T/R 1x. Not checked yet. | 3136056 | 1 | 15:54 | Afternoon | Tuesday | 2015 | 8
1890 | 2015-08-11 15:54 | 2015-11-11 09:54 | 13.8KV 8D FEEDER #4 | Rain and Lightning | Lightning | 17 | Checked & found, 8D OCB fdr #4 T/R 1x Ctr: 1516-1517 R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator o/p #8D-78. Cause: Lightning. | 3136056 | 1 | 15:54 | Afternoon | Tuesday | 2015 | 8
1891 | 2015-08-11 15:54 | 2015-08-11 15:54 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 25 | 8D OCB fdr #7 T/R 1x. Not checked yet. | 3136056 | 1 | 15:54 | Afternoon | Tuesday | 2015 | 8
1892 | 2015-08-11 15:54 | 2015-11-11 09:55 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 25 | Checked & found, 8D OCB fdr #7 T/R 1x Ctr: 628-629 R/F: 51N & 50@1,@2. Patrolled the line & found, @2 F/O Dead end Insulator o/p #7E-27. Cause: Lightning. | 3136056 | 1 | 15:54 | Afternoon | Tuesday | 2015 | 8
1893 | 2015-08-11 15:54 | 2015-08-11 15:54 | 13.8KV 8D FEEDER #8 | Rain and Lightning | Lightning | 0 | 8D OCB fdr #8 T/R 1x. Not checked yet. | 3136056 | 1 | 15:54 | Afternoon | Tuesday | 2015 | 8
1894 | 2015-08-11 15:54 | 2015-11-11 09:54 | 13.8KV 8D FEEDER #8 | Rain and Lightning | Lightning | 0 | Checked & found, 8D OCB fdr #8 T/R 1x Ctr: 422-423 R/F: 50@3 & 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 15:54 | Afternoon | Tuesday | 2015 | 8
1895 | 2015-08-11 15:54 | 2015-08-11 15:54 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 106 | 6DN OCB fdr #5 T/R 1x. Not checked yet. | 3136056 | 1 | 15:54 | Afternoon | Tuesday | 2015 | 8
1896 | 2015-08-11 15:54 | 2015-11-11 09:54 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 106 | Checked & found, 6DN OCB fdr #5 T/R 1x Ctr: 175-176 R/F: 51@1,@3. Patrolled the line & found, @1,@2 broken Dead end Insulator o/p #M5B-14. Cause: Lightning. | 3136056 | 1 | 15:54 | Afternoon | Tuesday | 2015 | 8
1897 | 2015-08-11 15:55 | 2015-08-11 15:55 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 17 | Sintong OCB fdr #2 T/R 1x. Not checked yet. | 3136051 | 1 | 15:55 | Afternoon | Tuesday | 2015 | 8
1898 | 2015-08-11 15:55 | 2015-11-11 10:55 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 17 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 398-399 R/F: 51N. Also found, Sintong GFPC T/R 1x Ctr: 809-810. Patrolled the line, but found nothing. Cause: Unidentified. | 3136051 | 1 | 15:55 | Afternoon | Tuesday | 2015 | 8
1899 | 2015-09-11 02:28 | 2015-09-11 02:28 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Switchboard Problem | - | 02:28 It was reported b/o fuse for Tx at Well Petapahan #17. 09:50 Checked & found, @2,@3 b/o 7.8SF fuses for 250Kva Tx at Well Petapahan #17. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size. (The Tx is not energized yet, due to Switchboard problem) Cause: Switchboard failure. | 3136056 | 1 | 2:28 | Night | Friday | 2015 | 9
1900 | 2015-09-11 02:54 | 2015-09-11 02:54 | 13.8KV NORTH DURI FEEDER #11 | Cloudy | Others | 803 | 02:54 N.Duri VCB fdr #11 T/LO. 04:48 Checked & found, N.Duri VCB fdr #11 T/LO. Ctr: 138-142 R/F: 51N. 05:43 Patrolled the line, but found nothing. Blocked & closed N.Duri VCB fdr #11, but tripped again with the same R/F. 05:47 Opened Isolation Switch of N.Duri VCB fdr #11, then function Test the VCB, OK. Closed Isolation Switch of N.Duri VCB fdr #11. 05:55 Opened LBS #13-G5.1-36 to separated load. 05:58 Closed N.Duri VCB fdr #11, OK. 06:13 Opened LBS #13-G5.1-38 to separated load. 06:15 Closed LBS #13-G5.1-36 (to energize U/G Cable toward pole 13-G5.1-38, but N.Duri VCB fdr #11 Trip again) Then Re-opened LBS #13-G5.1-36. (U/G cable problem) 06:17 Closed N.Duri VCB fdr #11, Ok. Then release the block. 06:29 Closed LBS #13-G4.1-30. (Transfer part load N.Duri fdr #11 to N.Duri fdr #2 via Recl. 13-G4.1-08 / unplugged control cable) Cause: Other. (U/G Cable problem) | 3136051 | 1 | 2:54 | Night | Friday | 2015 | 9
1901 | 2015-09-11 03:50 | 2015-09-11 03:50 | 13.8KV BANGKO GFPC | Rain | Lightning | 0 | 03:50 Bangko GFPC T/R 1x. (Ground fault alarm on Bangko fdr #4). No load dropped at any fdr. 09:52 Bangko GFPC T/R 1x again. (Ground fault alarm on Bangko fdr #4). No load drop at any fdr. Not checked yet. | 3136051 | 1 | 3:50 | Night | Friday | 2015 | 9
1902 | 2015-09-11 03:50 | 13/11/2015 07:50 | 13.8KV BANGKO GFPC | Rain | Lightning | 0 | Checked & found, Bangko GFPC T/R 2x Ctr: 479-481 R/F: 51N. Patrolled Bangko fdr #4 line, but found nothing. Cause: Suspected by Ligtning. | 3136051 | 1 | 3:50 | Night | Friday | 2015 | 9
1903 | 2015-09-11 09:16 | 2015-09-11 09:16 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 38 | 09:16 It was reported b/o fuse for Tx at Well Benar #48. (Bangko fdr #4) 09:48 Checked & found, @2 b/o 3.5SF fuse for 150Kva Tx at Well Benar #48. (Also found, a dead Bird under TP of Well Benar #48) Tested the Tx & found, low megger reading. 17:45 ReplacedTx failure with the same size & energized the Tx. Cause: Tx failure. (low megger reading) | 3136051 | 1 | 9:16 | Morning | Friday | 2015 | 9
1904 | 2015-09-11 15:00 | 2015-09-11 15:00 | DURI POWER PLANT |  |  | - | 15:00 S/U DGT #7, then online the Unit at 15:20. |  | 1 | 15:00 | Afternoon | Friday | 2015 | 9
1905 | 2015-09-11 15:45 | 2015-09-11 15:45 | MINAS POWER PLANT |  |  | - | 15:45 S/U MGT #5, then online the Unit at 16:03. |  | 1 | 15:45 | Afternoon | Friday | 2015 | 9
1906 | 2015-10-11 09:35 | 2015-10-11 09:35 | 13.8KV BANGKO FEEDER #1 | Fair | Recloser - Control Recloser | 156 | 09:35 Bangko fdr #1 load dropped 49A (288-239A). 10:30 It was reported no power at Bangko Test Station #B. 11:00 Checked & found, Recl. 23X-08 & Recl. 24Y-15 were in close position. 12:00 It was reported no power around Well BKO #09, #150 & #162. 12:20 Checked & found, Recl. 23W-12 (Bangko fdr #1) T/SO. Ctr: 237. (not changed) Patrolled the line, but found nothing. Blocked & closed Recl. 23W-12, but failed. 13:15 Manually open Bangko OCB fdr #1, to By pass Recl. 23W-12. 13:18 Blocked & Closed Bangko OCB fdr #1, Ok. Then released the block. Cause: Control Recloser (failure). | 3136051 | 1 | 9:35 | Morning | Sunday | 2015 | 10
1907 | 2015-10-11 12:42 | 2015-10-11 12:42 | 13.8KV PINANG FEEDER #1 | Heavy Rain | Lightning | 28 | 12:42 Pinang OCB fdr #1 T/R 1x. 13:12 Pinang OCB fdr #1 T/LO. 13:28 Blocked & closed, Pinang OCB fdr #1, Ok. Then released the block. Not checked & patrolled yet. | 3136051 | 1 | 12:42 | Afternoon | Sunday | 2015 | 10
1908 | 2015-10-11 12:42 | 13/11/2015 08:42 | 13.8KV PINANG FEEDER #1 | Heavy Rain | Lightning | 28 | Checked & found, Pinang OCB fdr #1 T/LO. Ctr: 340-353 R/F: 51N & 51@1,@2,@3. Patrolled the line & found, @2,@3 Seriously broken Pin Insulator o/p #12F-06. (Also found @3 conductor loose from The Pin Insulator o/p #12F-06) Then replacing the broken Pin Insulators & repairing the conductor. Cause: Lightning. | 3136051 | 1 | 12:42 | Afternoon | Sunday | 2015 | 10
1909 | 2015-10-11 13:53 | 2015-10-11 13:53 | 13.8KV BEKASAP FEEDER #6 | Cloudy | Lightning | 44 | Bekasap VCB fdr #6 T/R 1x. Not checked yet. | 3136051 | 1 | 13:53 | Afternoon | Sunday | 2015 | 10
1910 | 2015-10-11 13:53 | 2015-12-11 13:00 | 13.8KV BEKASAP FEEDER #6 | Cloudy | Lightning | 44 | Checked & found, Bekasap Main VCB fdr #6 T/R 1x Ctr: 328-329 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #39BF-19. Cause: Lightning. | 3136051 | 1 | 13:53 | Afternoon | Sunday | 2015 | 10
1911 | 2015-10-11 14:27 | 2015-10-11 14:27 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 71 | OKBS OCB fdr #2 T/R 1x. Not checked yet. | 3136056 | 1 | 14:27 | Afternoon | Sunday | 2015 | 10
1912 | 2015-10-11 14:27 | 2015-12-11 09:40 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 71 | Checked & found, OKBS OCB fdr #2 T/R 1x Ctr: 1252-1253 R/F: 51N. Patrolled the line, but found nothing. Cause: Lightning. | 3136056 | 1 | 14:27 | Afternoon | Sunday | 2015 | 10
1913 | 2015-10-11 14:31 | 2015-10-11 14:31 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Unidentified | 176 | 14:31 Sintong OCB fdr #2 T/LO. 15:25 Checked & found, Sintong OCB fdr #2 T/LO. Ctr: 398-400 R/F: 51N & 51@1. Patrolled the line, but found nothing. 16:00 Blocked & closed Sintong OCB fdr #2, Ok. Then release the block. Cause: Unidentified. | 3136051 | 1 | 14:31 | Afternoon | Sunday | 2015 | 10
1914 | 2015-10-11 14:59 | 2015-10-11 14:59 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 2227 | 14:49 Off line NCD-CT #1 By load rejection on load 10.0MW, then S/D the Unit at 15:26. (Prior to removing Blanking Plate) 10:00 Manually Load shedding around 30.0MW. Prod. loss reported by GS: GS #1 -----> 136 Bbls, S/D 48 Wells and 2 WIP. GS #2 -----> 253 Bbls, S/D 88 Wells and 2 WIP. GS #3 -----> 117 Bbls, S/D 19 Wells and 1 WIP. GS #4 -----> 71 Bbls, S/D 34 Wells and 2 WIP. GS #5 -----> 200 Bbls, S/D 36 Wells and 3 WIP. GS #6 -----> 256 Bbls, S/D 55 Wells and 2 WIP. Total Prod. loss: 1033 Bbls, 230 Wells and 12 WIPs. 11-Nov-2015. Prod. loss reported by GS: GS #1 -----> 246 Bbls, S/D 48 Wells and 2 WIP. GS #2 -----> 350 Bbls, S/D 36 Wells and 0 WIP. GS #3 -----> 214 Bbls, S/D 19 Wells and 1 WIP. GS #4 -----> 173 Bbls, S/D 34 Wells and 2 WIP. GS #5 -----> 200 Bbls, S/D 36 Wells and 3 WIP. GS #6 -----> 342 Bbls, S/D 61 Wells and 5 WIP. Total Prod. loss: 1525 Bbls, 234 Wells and 13 WIPs. Grand Total Prod. loss (10-Nov-2015 & 11-Nov-2015) = 2558 Bbls, 234 Wells and 13 WIPs. 17:40 S/U NDC-CT #1, then on line the Unit at 18:08. (After opening Blanking plate) 22:54 Off line NDC-CT #3, then S/D the Unit for S/B. (Prior to installing Blanking Plate & offline wash) Total Prod. loss Reported by EC system, for 10-Nov-2015= 1041 Bbls / 237 Wells. Total Prod. loss Reported by EC system, for 11-Nov-2015= 1186 Bbls / 237 Wells. Grand Total Prod. loss Reported by EC syste, for 10 & 11-Nov-2015= 2227 Bbls / 237 wells. | 123 | 1 | 14:59 | Afternoon | Sunday | 2015 | 10
1915 | 2015-10-11 15:23 | 2015-10-11 15:23 | 13.8KV BANGKO GFPC | Rain and Lightning | Lightning | 0 | Bangko GFPC T/R 1x. Ground fault alarm on Bangko fdr #4. (No load dropped at any fdrs.) Not checked yet. | 3136051 | 1 | 15:23 | Afternoon | Sunday | 2015 | 10
1916 | 2015-10-11 15:23 | 13/11/2015 08:23 | 13.8KV BANGKO GFPC | Rain and Lightning | Lightning | 0 | Checked & found, Bangko GFPC T/R 1x Ctr: 481-482 R/F: 51N. Patrolled Bangko fdr #4 line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 15:23 | Afternoon | Sunday | 2015 | 10
1917 | 2015-11-11 06:50 | 2015-11-11 06:50 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 06:50 It was reported no power at Complex Dempo #48 o/p #3DD-19. 10:00 Checked & found, @2 b/o 1.0SF fuse for 50Kva Tx o/p #3DD-19 at Dempo #48. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3136051 | 1 | 6:50 | Morning | Wednesday | 2015 | 11
1918 | 2015-11-11 13:55 | 2015-11-11 13:55 | 115KV DURI - KOTABATAK JUNCTION LINE | Fair | Under investigation | 0 | 13:55 115Kv DRB GCB #28 T/O. (It was occurred while resetting Duri 115Kv OCB #28 79SEL) 14:02 Manuaaly closed 115Kv DRB GCB #28, but failed. (from DSC) 14:30 Checked and found Duri 115Kv OCB #28 T/O. Ctr: 116-117 R/F: Did not appeare. Manually closed 115Kv DRB GCB #28, but failed (from Local). Checked & found, burnt out fuse & GCB Charging motor. Cause: Under investigation. (will be replaced tomorrow) | 3136051 | 1 | 13:55 | Afternoon | Wednesday | 2015 | 11
1919 | 2015-11-11 14:46 | 2015-11-11 14:46 | 13.8KV BEKASAP FEEDER #3 | Cloudy and Lightning | Lightning | 59 | Bekasap Main fdr #3 load dropped 80A (236-159A). Bekasap Main fdr #2 load dropped 15A (126-111A). Bekasap Main fdr #6 load dropped 12A (87-74A). Not checked yet. | 3136051 | 1 | 14:46 | Afternoon | Wednesday | 2015 | 11
1920 | 2015-11-11 14:46 | 16/11/2015 16:46 | 13.8KV BEKASAP FEEDER #3 | Cloudy and Lightning | Lightning | 59 | Checked & found, Recl. 37BE-27 (Bekasap fdr #3) T/R 1x Ctr: 165-166. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 14:46 | Afternoon | Wednesday | 2015 | 11
1921 | 2015-11-11 16:05 | 2015-11-11 16:05 | 13.8KV PINANG FEEDER #1 | Fair | Planned Maintenance | 254 | 16:05 Manually Opened Pinang OCB fdr #1. To Replace @2,@3 Seriously Broken Pin Insulator o/p #12F-06. 19:05 Closed Both Isolation Switch of Pinang OCB fdr #1. 19:07 Blocked & closed Pinang OCB fdr #1, Ok. Then release the block. Cause: Maintenance Job. | 123 | 1 | 16:05 | Afternoon | Wednesday | 2015 | 11
1922 | 2015-11-11 16:40 | 2015-11-11 16:40 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Recloser - Control Recloser | 188 | 16:40 4D fdr #4 Load dropped 201A (231-30A). 21:50 It was reported no power at Well #5E-42, #5E-52 & #5D-18D. 23:05 Checked & found, Recl. 5E-05 (4D fdr #4) T/SO. Ctr: 55-56. Blocked & closed Recl. 5E-05, but failed. (Would be continued tomorrow Because of Rain). 12-Nov-2015. 08:28 Open LBS #36DN-27. 08:37 By passed Recl. 5E-05. 08:40 Blocked 4D fdr #4 and closed LBS #36DN-27, Ok. Then released the Block. Cause: Control Recloser. | 3136056 | 1 | 16:40 | Afternoon | Wednesday | 2015 | 11
1923 | 2015-11-11 16:45 | 2015-11-11 16:45 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 61 | 6DN OCB fdr #5 T/R 1x. Not checked yet. | 3136056 | 1 | 16:45 | Afternoon | Wednesday | 2015 | 11
1924 | 2015-11-11 16:45 | 13/11/2015 11:45 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 61 | Checked & found, 6DN OCB fdr #5 T/R 1x Ctr: 176-177 R/F: 51@1,@3. Patrolled the line & found, @3 F/O Pin Insulator o/p #6D-01. Cause: Lightning. | 3136056 | 1 | 16:45 | Afternoon | Wednesday | 2015 | 11
1925 | 2015-11-11 16:46 | 2015-11-11 16:46 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 42 | 6DN OCB fdr #6 T/R 2x. Not checked yet. | 3136056 | 1 | 16:46 | Afternoon | Wednesday | 2015 | 11
1926 | 2015-11-11 16:46 | 13/11/2015 13:26 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 42 | Checked & found, 6DN OCB fdr #6 T/R 2x Ctr: 312-314 R/F: 51@1,@2,@3. Patrolled the line & found, @1,@3 F/O Dead end Insulators o/p #6D-121. Cause: Lightning. | 3136056 | 1 | 16:46 | Afternoon | Wednesday | 2015 | 11
1927 | 2015-11-11 17:40 | 2015-11-11 17:40 | NORTH DURI POWER PLANT |  |  | - | 17:40 S/U NDC-CT #1, then on line the Unit at 18:08. (After opening Blanking plate) |  | 1 | 17:40 | Afternoon | Wednesday | 2015 | 11
1928 | 2015-11-11 17:58 | 2015-11-11 17:58 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 111 | CKBS fdr #5 load dropped 273A (344-71A). Not checked yet. | 3136056 | 1 | 17:58 | Afternoon | Wednesday | 2015 | 11
1929 | 2015-11-11 17:58 | 14/11/2015 08:58 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 111 | Checked & found, Recl. 36CU-29 (CKBS fdr #5) T/R 1x Ctr: 68-69. Patrolled the line & found, @1 broken L/A on TP of Well KB #65. Cause: Lightning. | 3136056 | 1 | 17:58 | Afternoon | Wednesday | 2015 | 11
1930 | 2015-11-11 22:54 | 2015-11-11 22:54 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 1797 | 22:54 Off line NDC-CT #3, then S/D the Unit for S/B. (Prior to installing Blanking Plate & offline wash) | 123 | 1 | 22:54 | Night | Wednesday | 2015 | 11
1931 | 2015-11-11 22:54 | 2015-12-11 23:59 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 1797 | 11-Nov-2015. Prod. loss reported by Minas-GS: GS-1: 167 Bbls, 28 Wells & 2 WIP. GS-2: 195 Bbls, 37 Wells & 1 WIP. GS-3: 197 Bbls, 19 Wells & 1 WIP. GS-4: 125 Bbls, 27 Wells & 2 WIP. GS-5: 336 Bbls, 35 Wells & 2 WIP. GS-6: 263 Bbls, 61 Wells & 3 WIP. Total Prod. loss reported by Minas-GS= 1283 Bbls, 207 Wells & 11 WIP. Prod. loss Reported by EC system= 1186 Bbls, 237 Wells. 19:57 S/U NDC-CT #3, then on line the Unit at 20:22. (After Opened Blanking Plate) 12-Nov-2015. Prod. loss reported by Minas-GS: GS-1: 152 Bbls, 20 Wells & 2 WIP. GS-2: 192 Bbls, 37 Wells & 2 WIP. GS-3: 166 Bbls, 17 Wells & 1 WIP. GS-4: 125 Bbls, 27 Wells & 2 WIP. GS-5: 336 Bbls, 35 Wells & 2 WIP. GS-6: 263 Bbls, 61 Wells & 3 WIP. Total Prod. loss: 1234 Bbls, 197 Wells & 12 WIP. Grand Total Prod. loss, reported by Minas-GS: (Report for 11 & 12-Nov-2015) = 2517 Bbls, 207 Wells & 12 WIPs. Grand Total Prod. loss reported by EC system (11 & 12-Nov-2015)= 1797 Bbls / 249 Wells. | 123 | 1 | 22:54 | Night | Wednesday | 2015 | 11
1932 | 2015-12-11 19:18 | 2015-12-11 19:18 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 0 | OKB fdr #2 Load dropped 98A (267-17A). Not checked yet. | 3136056 | 1 | 19:18 | Night | Friday | 2015 | 12
1933 | 2015-12-11 19:18 | 15/11/2015 15:12 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 38CX-25 (OKB fdr #2) T/R 1x Ctr: 89-90. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 19:18 | Night | Friday | 2015 | 12
1934 | 2015-12-11 19:57 | 2015-12-11 19:57 | NORTH DURI POWER PLANT |  |  | - | 19:57 S/U NDC-CT #3, then on line the Unit at 20:22. (After Opened Blanking Plate) | 123 | 1 | 19:57 | Night | Friday | 2015 | 12
1935 | 2015-11-13 00:38 | 2015-11-13 00:38 | CENTRAL DURI POWER PLANT |  | Equipment Failure | - | 00:38 CGT #5 Tripped by alarm: Fire in Turbine & Accesories compartment. (CO-2 realesed) Cause: 45FT cable short circuit. 18:12 S/U CGT #5, then on line the Unit at 18:29. |  | 1 | 0:38 | Night | Friday | 2015 | 11
1936 | 2015-11-13 08:00 | 2015-11-13 08:00 | DURI POWER PLANT |  |  | - | 08:00 Off line DGT #7, then S/D the Unit for trouble shoot control problem. 17:06 S/U DGT#7, then on line the Unit for running on test. 18:02 Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 8:00 | Morning | Friday | 2015 | 11
1937 | 2015-11-13 14:04 | 2015-11-13 14:04 | 13.8KV PUNGUT FEEDER #1 | Fair | Planned Maintenance | 134 | 14:04 Manually opened Pungut OCB fdr#1. Replaced : - 9 pcs broken deadend insulators and 3 pcs broken pin o/p Pole 45 BP-06. - 3 pcs broken pin insulator o/p 46 BP-08. - 3 pcs broken pin insulator o/p 46 BP-15. - 2 pcs broken pin insulator o/p 45 BQ-19. 15:20 Closed Pungut OCB fdr #1. (Ctr: 344-345) Cause : Planned Maintenance. | 123 | 1 | 14:04 | Afternoon | Friday | 2015 | 11
1938 | 2015-11-13 15:16 | 2015-11-13 15:16 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Animal | 9 | 15:16 It was reported b/o fuse for Tx o/p #05-N1-19A. 16:40 Checked & found, @1 b/o 14SF fuse for 500Kva Tx o/p #05-N1-19A. 16:50 Replaced the b/o fuse with same size, then energized the Tx. Cause: Animal. (Monkey) | 3136051 | 1 | 15:16 | Afternoon | Friday | 2015 | 11
1939 | 2015-11-14 14:12 | 2015-11-14 14:12 | 13.8KV PETAPAHAN FEEDER #1 | Fair | ESP Failure | - | 14:12 It was reported @2,@3 b/o fuse of 250Kva Tx at Well Petapahan #17. (Petapahan fdr #1) Performed Test TTR, Megger the Tx & found, low Megger reading. Cause: Reda motor (ESP) failure. | 3136056 | 1 | 14:12 | Afternoon | Saturday | 2015 | 11
1940 | 2015-11-14 14:12 | 2015-11-15 10:21 | 13.8KV PETAPAHAN FEEDER #1 | Fair | ESP Failure | - | Replaced 250Kva with 300Kva Tx at Well Petapahan #17, then energized the Tx. Cause: Low Mega-ohm reading Tx. | 3136056 | 1 | 14:12 | Afternoon | Saturday | 2015 | 11
1941 | 2015-11-14 15:13 | 2015-11-14 15:13 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 84 | So.Balam VCB fdr #1 T/R 1x. (GFPC in block position) Not checked yet. | 3136051 | 1 | 15:13 | Afternoon | Saturday | 2015 | 11
1942 | 2015-11-14 15:13 | 2015-11-17 08:13 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 84 | Checked & found, So.Balam VCB fdr #1 T/R 1x Ctr: 343. (did not change) R/F: 51N. Also found, So.Balam GFPC T/R 1x Ctr: 194. (Did not change) Patrolled the line, but found nothing. Cause: Unidentified. | 3136051 | 1 | 15:13 | Afternoon | Saturday | 2015 | 11
1943 | 2015-11-15 06:15 | 2015-11-15 06:15 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 18 | So.Bekasap OCB fdr #1 T/R 1x. Not checked yet. | 3136051 | 1 | 6:15 | Morning | Sunday | 2015 | 11
1944 | 2015-11-15 06:15 | 2015-11-17 16:15 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 18 | Checked & found, So.Bekasap OCB fdr #1 T/R 1x Ctr: 250-251 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3136051 | 1 | 6:15 | Morning | Sunday | 2015 | 11
1945 | 2015-11-15 07:42 | 2015-11-15 07:42 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 14 | Sintong VCB fdr #2 T/R 1x. Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #2) Not checked yet. | 3136051 | 1 | 7:42 | Morning | Sunday | 2015 | 11
1946 | 2015-11-15 07:42 | 2015-11-17 08:42 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 14 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 400-401 R/F: 51N. Also found, Sintong GFPC T/R 2x Ctr: 811-813. Patrolled the line, but found nothing. Cause: Unidentified. | 3136051 | 1 | 7:42 | Morning | Sunday | 2015 | 11
1947 | 2015-11-15 10:36 | 2015-11-15 10:36 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Animal | 1 | 10:36 It was reported b/o fuse for Tx at Well Pematang Bow #17. (So.Bekasap fdr #1) 14:53 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Pematang Bow #17. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Chicken) | 3136051 | 1 | 10:36 | Morning | Sunday | 2015 | 11
1948 | 2015-11-15 12:58 | 2015-11-15 12:58 | 13.8KV BEKASAP MAIN GFPC | Rain and Lightning | Lightning | 0 | Bekasap Main GFPC-TX #C T/R 1x. Ground fault alarm on Bekasap Main fdr #2. (No load dropped at any fdr.) Not checked yet. | 3136051 | 1 | 12:58 | Afternoon | Sunday | 2015 | 11
1949 | 2015-11-15 12:58 | 2015-11-20 16:58 | 13.8KV BEKASAP MAIN GFPC | Rain and Lightning | Lightning | 0 | Checked & found, Bekasap Main GFPC T/R 1x Ctr: 332-333. Patrolled Bekasap fdr #2 line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 12:58 | Afternoon | Sunday | 2015 | 11
1950 | 2015-11-15 12:59 | 2015-11-15 12:59 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 24 | Pematang OCB fdr #1 T/R 1x. (Pematang RTU failed at that time) Not checeked yet. | 3136051 | 1 | 12:59 | Afternoon | Sunday | 2015 | 11
1951 | 2015-11-15 12:59 | 2015-11-19 15:59 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 24 | Checked & found, Pematang OCB fdr #1 T/R 1x Ctr: 115-116 R/F: 51N(@3). Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 12:59 | Afternoon | Sunday | 2015 | 11
1952 | 2015-11-15 13:17 | 2015-11-15 13:17 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 0 | So.Bekasap fdr #1 load dropped 81A (159-78A). Not checked yet. | 3136051 | 1 | 13:17 | Afternoon | Sunday | 2015 | 11
1953 | 2015-11-15 13:17 | 2015-11-17 16:17 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 34BI-18 (So.Bekasap fdr #1) T/R 1x Ctr: 148-149. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 13:17 | Afternoon | Sunday | 2015 | 11
1954 | 2015-11-15 15:03 | 2015-11-15 15:03 | 13.8KV SURAM FEEDER #2 | Rain and Lightning | Lightning | 5 | Suram OCB fdr #2 T/R 1x. Suram fdr #1 load dropped 31A (73-42A). Not checked yet. | 3136056 | 1 | 15:03 | Afternoon | Sunday | 2015 | 11
1955 | 2015-11-15 15:03 | 2015-11-16 17:07 | 13.8KV SURAM FEEDER #2 | Rain and Lightning | Lightning | 5 | Checked & found, Suram OCB fdr #2 T/R 1x Ctr: 253-254 R/F: 51@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 15:03 | Afternoon | Sunday | 2015 | 11
1956 | 2015-11-15 18:18 | 2015-11-15 18:18 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified (Fuse) | 28 | 18:18 It was reported @1,@2,@3 b/o fuse for Tx at Well Pematang #34. 20:30 Checked & found @1,2&@3 b/o fuse for 100 Kva Tx. Perform TTR & Megger --> Good reading. Replaced b/o fuse above with the same size and energized Tx. Cause: Unidentified (fuse). | 3136051 | 1 | 18:18 | Afternoon | Sunday | 2015 | 11
1957 | 2015-11-16 05:43 | 2015-11-16 05:43 | 13.8KV KETIGUL FEEDER#1 | Cloudy and Lightning | Lightning | 0 | Ketigul fdr #1 Load dropped 72A (175-103A). Not checked yet. | 3136051 | 1 | 5:43 | Morning | Monday | 2015 | 11
1958 | 2015-11-16 05:43 | 2015-11-19 15:43 | 13.8KV KETIGUL FEEDER#1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 32AK-16 (Ketigul fdr #1) T/R 1x Ctr: 114-115. Patrolled the line & found, @3 broken L/A o/p #32AK-38. Cause: Lightning. | 3136051 | 1 | 5:43 | Morning | Monday | 2015 | 11
1959 | 2015-11-16 22:49 | 2015-11-16 22:49 | 6 DELTA NEW SUBSTATION | Heavy Rain | Under investigation | 767 | 22:49 6DN 115KV C/S-Tx #2 T/O. 23:47 Checked & found, 6DN 115KV C/S-Tx #2 T/O. R/F: 86T & 86HR Ctr: 505-506. (The weather is Heavy Rain) Prod. loss 6DN fdr #5 = 59 Bbls / 21 wells. Prod. loss 6DN fdr #6 = 48 Bbls / 24 wells. ------------------------------------------------------- Total =107 Bbls / 45 wells. (till 24:00) | 3136056 | 1 | 22:49 | Night | Monday | 2015 | 11
1960 | 2015-11-16 22:49 | 2015-11-17 01:36 | 6 DELTA NEW SUBSTATION | Heavy Rain | Under investigation | 767 | 01:36 Manually open 6DN fdr #4. (by DSC) Manually open 6DN fdr #5. (by DSC) Manually open 6DN fdr #6. (by DSC) Transfer part load 6DN fdr #6 to Minas fdr #6 07:10 Opened Recl. 6E-30, then Closed LBS #6E-08. Transfer load 6DN fdr #4 to 6D fdr #3. 07:27 Closed LBS-C at GS#3. Transfer part load 6DN fdr #6 to 4D fdr #5. 07:38 Closed LBS #36DN-32B. Transfer load 6DN fdr #5 to Minas fdr #5. 07:48 Closed LBS #MK-10. Cause: Under Investigation. 17-Nov-2015. Additional Prod. loss (from 00:00 - 07:48) Prod. loss 6DN fdr #5 = 424 Bbls / 21 wells. Prod. loss 6DN fdr #6 = 363 Bbls / 24 wells. ------------------------------------------------------- Total = 787 Bbls / 45 wells. Grand Total Prod. loss= 894 bbls / 45 Wells. (Reported by Minas-GS) Grand Total Prod. loss= 767 Bbls / 45 Wells. (Reported by EC system) | 3136056 | 1 | 22:49 | Night | Monday | 2015 | 11
1961 | 2015-11-17 00:47 | 2015-11-17 00:47 | 13.8KV MINAS FEEDER #1 | Heavy Rain | Lightning | 268 | 00:47 Minas fdr #1 Load dropped 128A (148-20A). 05:11 Checked & found Recl. 7D-20 (Minas fdr #1) T/LO. Ctr: 139-143. 06:00 Blocked & Closed Recl. 7D-20, but T/O again. Patrolled the line & found, @1 seriously broken Pin Insulator o/p #7D-13. 06:55 Blocked & closed Recl. 7D-20, Ok. Then released the Block. (After replacing broken Pin Insulator above) Cause: Lightning. | 3136056 | 1 | 0:47 | Night | Tuesday | 2015 | 11
1962 | 2015-11-17 06:11 | 2015-11-17 06:11 | 13.8KV DURI COMMUNITY FEEDER #1 | Drizzle | Lightning | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3136051 | 1 | 6:11 | Morning | Tuesday | 2015 | 11
1963 | 2015-11-17 06:11 | 2015-11-19 15:11 | 13.8KV DURI COMMUNITY FEEDER #1 | Drizzle | Lightning | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 76-77 R/F: 51N(@2). Patrolled the line & found, @2 F/O Dead end Insulator o/p #SN-13. (Near Wisma Pinggir) Cause: Lightning. | 3136051 | 1 | 6:11 | Morning | Tuesday | 2015 | 11
1964 | 2015-11-17 09:49 | 2015-11-17 09:49 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 09:49 It was reported b/o fuse for Tx o/p #01-07-17. (D.Field fdr #1) 11:30 Checked & found, @1,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #01-07-17. Replaced b/o fuse above with the same size 7 energized the Tx. Cause: Unidentified (Fuse). | 3136051 | 1 | 9:49 | Morning | Tuesday | 2015 | 11
1965 | 2015-11-17 14:00 | 2015-11-17 14:00 | DURI POWER PLANT |  |  | - | 14:00 S/U DGT #7, then online the Unit at 14:30. 15:43 Generator Breaker DGT #7 T/O. (Without alarm) 17:47 On Line DGT #7. |  | 1 | 14:00 | Afternoon | Tuesday | 2015 | 11
1966 | 2015-11-17 14:05 | 2015-11-17 14:05 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx o/p #KT-45A. (Duri Community fdr #1) Checked & found, @2 b/o 7.8SF fuse for 3x100Kva Tx o/p #KT-45A. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3136051 | 1 | 14:05 | Afternoon | Tuesday | 2015 | 11
1967 | 2015-11-18 06:08 | 2015-11-18 06:08 | 13.8KV 8D FEEDER #3 | Fair | ESP Failure | 0 | Replaced @1 b/o 14.0SF fuse for 550Kva Tx at Well #8E-54, then energized the Tx. Cause: ESP Failure. | 3136056 | 1 | 6:08 | Morning | Wednesday | 2015 | 11
1968 | 2015-11-18 11:42 | 2015-11-18 11:42 | MINAS POWER PLANT |  |  | - | 11:42 S/U MGT #2, then on line the Unit at 12:00. 18:13 MGT #2 Tripped by alarm: Mechanical Over Speed Trip. Cause: Under Investigation. |  | 1 | 11:42 | Morning | Wednesday | 2015 | 11
1969 | 2015-11-18 13:45 | 2015-11-18 13:45 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 3097 | Off line NDC-CT #3, then S/D the Unit for S/B. (Prior to removing Blanking plate, after repairing HRSG-3) Prod. loss reported by Minas GS: GS-1 = 349 Bbls, 41 Wells & 3 WIP. GS-2 = 211 Bbls, 41 Wells & 1 WIP. GS-3 = 0 Bbls, 0 Wells & 0 WIP. GS-4 = 176 Bbls, 39 Wells & 2 WIP. GS-5 = 233 Bbls, 44 Wells & 2 WIP. GS-6 = 125 Bbls, 43 Wells & 2 WIP. Total Prod. loss = 1094 Bbls, 208 Wells & 10 WIP. | 123 | 1 | 13:45 | Afternoon | Wednesday | 2015 | 11
1970 | 2015-11-18 13:45 | 2015-11-19 15:42 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 3097 | 15:42 S/U NDC-CT #3, then on line the Unit at 16:10. (Found NDC-CT #3 high Vibration, it would be S/D for fixing the Vibration) 18-Nov-2015. Prod. loss reported by Minas-GS: GS-1 = 349 Bbls, 41 Wells & 3 WIP. GS-2 = 211 Bbls, 41 Wells & 1 WIP. GS-3 = 0 Bbls, 0 Wells & 0 WIP. GS-4 = 176 Bbls, 39 Wells & 2 WIP. GS-5 = 233 Bbls, 44 Wells & 2 WIP. GS-6 = 125 Bbls, 43 Wells & 2 WIP. ------------------------------------------- Total Prod. loss = 1094 Bbls, 208 Wells & 10 WIP. 19-Nov-2015. Prod. loss reported by Minas-GS: GS-1 = 305 Bbls, 41 Wells & 1 WIP. GS-2 = 364 Bbls, 41 Wells & 1 WIP. GS-3 = 0 Bbls, 0 Wells & 0 WIP. GS-4 = 331 Bbls, 39 Wells & 2 WIP. GS-5 = 429 Bbls, 44 Wells & 2 WIP. GS-6 = 245 Bbls, 43 Wells & 1 WIP. ------------------------------------------- Total Prod. loss = 1674 Bbls, 208 Wells & 7 WIP. Grand Total Prod. loss = 2768 Bbls, 208 Wells & 7 WIP. | 123 | 1 | 13:45 | Afternoon | Wednesday | 2015 | 11
1971 | 2015-11-18 13:45 | 2015-11-20 11:30 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 3097 | 11:30 Off line NDC-CT #3, then S/D the unit for Maintenance. (Trouble shooting High Vibration) 12:00 S/U NDC-CT #3, then On Line the Unit at 12:20 (After performing Hot Started up the unit) 20-Nov-2015. Prod. loss reported by Minas-GS: GS-1 = 49 Bbls, 15 Wells & 0 WIP. GS-2 = 6 Bbls, 6 Wells & 0 WIP. GS-3 = 0 Bbls, 0 Wells & 0 WIP. GS-4 = 76 Bbls, 22 Wells & 0 WIP. GS-5 = 53 Bbls, 14 Wells & 0 WIP. GS-6 = 145 Bbls, 34 Wells & 0 WIP. ------------------------------------------- Total Prod. loss = 329 Bbls, 91 Wells & 0 WIP. Grand Total Prod. loss (18, 19 & 20 Nov 2015) = 3097 Bbls, 208 Wells & 7 WIP. | 123 | 1 | 13:45 | Afternoon | Wednesday | 2015 | 11
1972 | 2015-11-18 17:25 | 2015-11-18 17:25 | 13.8KV LIBO FEEDER #1 | Fair | Secondary Cable | 9 | It was reported b/o fuse for Tx at Well SE.Libo #9. Not checked yet. | 3136051 | 1 | 17:25 | Afternoon | Wednesday | 2015 | 11
1973 | 2015-11-18 17:25 | 2015-11-19 17:00 | 13.8KV LIBO FEEDER #1 | Fair | Secondary Cable | 9 | Checked & found, @2 b/o 14SF fuse for 500Kva Tx at Well SE.Libo #09. Replaced b/o fuse above with the same size & energized the Tx. Cause: Surface cable shortcircuit. | 3136051 | 1 | 17:25 | Afternoon | Wednesday | 2015 | 11
1974 | 2015-11-18 17:47 | 2015-11-18 17:47 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 0 | 4B OCB fdr #5 T/R 1x. Not checked yet. | 3136056 | 1 | 17:47 | Afternoon | Wednesday | 2015 | 11
1975 | 2015-11-18 17:47 | 2015-11-20 15:47 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, 4B OCB fdr #5 T/R 1x Ctr: 109-110 R/F: 51@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 17:47 | Afternoon | Wednesday | 2015 | 11
1976 | 2015-11-18 19:05 | 2015-11-18 19:05 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 24 | 19:05 Libo OCB fdr #1 T/R 1x. 20:28 Libo OCB fdr #1 T/R 1x again. Not checked yet. | 3136051 | 1 | 19:05 | Night | Wednesday | 2015 | 11
1977 | 2015-11-18 19:05 | 2015-11-20 07:05 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 24 | Checked & found, Libo OCB fdr #1 T/R 2x Ctr: 351-353 R/F: 50N & 51N. Patrolled & found: -@1 Flashed over Dead end Insulator o/p #34CB-72. -@2 b/o fuse for 500Kva Tx & Shortcircuit surface cable at Well SE.Libo #09. Cause: Lightning. | 3136051 | 1 | 19:05 | Night | Wednesday | 2015 | 11
1978 | 2015-11-18 21:20 | 2015-11-18 21:20 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 66 | 4B OCB fdr #1 T/R 1x. 4B fdr #2 load dropped 81A (120-39A). Not checked yet. | 3136056 | 1 | 21:20 | Night | Wednesday | 2015 | 11
1979 | 2015-11-18 21:20 | 2015-11-20 15:20 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 66 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 259-260 R/F: 51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 21:20 | Night | Wednesday | 2015 | 11
1980 | 2015-11-18 21:51 | 2015-11-18 21:51 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 14 | Libo OCB fdr #2 T/R 1x. Not checked yet. | 3136051 | 1 | 21:51 | Night | Wednesday | 2015 | 11
1981 | 2015-11-18 21:51 | 2015-11-20 07:51 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 14 | Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 400-401 R/F: 50N. Patrolled the line & found, @1 F/O Dean end Insulator o/p #KW-117. Cause: Lightning. | 3136051 | 1 | 21:51 | Night | Wednesday | 2015 | 11
1982 | 2015-11-18 21:54 | 2015-11-18 21:54 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 0 | 21:54 Minas fdr #6 load dropped 30A (209-179A). It was reported no power at Cendrawasih & Dahlia Camp. (The weather is still rain) 23:11 Checked & found, 13.8Kv Recloser for Tx at Cewa Mini SS T/O. Ctr: 885-886. Also found 4.16Kv Recloser at Cewa Mini SS T/SO. Ctr: 689-690. 23:30 Closed 13.8Kv Recloser for Tx at Cewa Mini SS, Ok. Blocked & closed 4.16Kv Recloser at Cewa Mini SS, Ok. Then released the block. Not patrolled yet. | 3136056 | 1 | 21:54 | Night | Wednesday | 2015 | 11
1983 | 2015-11-18 21:54 | 2015-11-23 13:54 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 0 | Patrolled 416Kv line downstream of CEWA Mini Substation, but found nothing. Cause: Suspected by Lightning. Also found, Recl. 6E-23A (Minas fdr #6) T/R 2x Ctr: 13-15. Patrolled th eline & found: -@2 Broken Pin Insulator o/p #6E-09. -@3 Flashed over Dead end Insulator o/p #6E-50. -@3 Broken L/A o/p #6E-51. -@3 Broken L/A on TP of Well #6F-21. Cause: Ligtning. | 3136056 | 1 | 21:54 | Night | Wednesday | 2015 | 11
1984 | 2015-11-18 22:06 | 2015-11-18 22:06 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 0 | 4D fdr #5 load dropped 166A (264-98A). Not checked yet. | 3136056 | 1 | 22:06 | Night | Wednesday | 2015 | 11
1985 | 2015-11-18 22:06 | 24/11/2015 14:06 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 4D-51A (4D fdr #5) T/R 1x Ctr: 05-06. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 22:06 | Night | Wednesday | 2015 | 11
1986 | 2015-11-18 22:12 | 2015-11-18 22:12 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 78 | Minas ACB fdr #6 T/R 2x Ctr: 156-158 R/F: 51@1. Not patrolled yet. | 3136056 | 1 | 22:12 | Night | Wednesday | 2015 | 11
1987 | 2015-11-18 22:12 | 2015-11-23 13:12 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 78 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 22:12 | Night | Wednesday | 2015 | 11
1988 | 2015-11-18 22:18 | 2015-11-18 22:18 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 100 | 6D OCB fdr #5 T/R 1x. Not checked yet. | 3136056 | 1 | 22:18 | Night | Wednesday | 2015 | 11
1989 | 2015-11-18 22:18 | 2015-11-19 15:18 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 100 | Checked & found, 6D OCB fdr #5 T/R 1x Ctr: 723-724 R/F: 51@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 22:18 | Night | Wednesday | 2015 | 11
1990 | 2015-11-18 22:19 | 2015-11-18 22:19 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 70 | 4D fdr #4 load dropped 200A (250-50A). Not checked yet. | 3136056 | 1 | 22:19 | Night | Wednesday | 2015 | 11
1991 | 2015-11-18 22:19 | 2015-11-20 16:19 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 70 | Checked & found, Recl. 5E-83 (4D fdr #4) T/R 1x Ctr: 19-20. Patrolled the line & found: -@1 Flashed over Dead end Insulator. -@2,@3 Flashed over Pin Insulator o/p #5E-20. Cause: Lightning. | 3136056 | 1 | 22:19 | Night | Wednesday | 2015 | 11
1992 | 2015-11-18 22:24 | 2015-11-18 22:24 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 42 | 4D OCB fdr #5 T/R 1x. Not checked yet. | 3136056 | 1 | 22:24 | Night | Wednesday | 2015 | 11
1993 | 2015-11-18 22:24 | 2015-11-20 16:24 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 42 | Checked & found, 4D OCB fdr #5 T/R 1x Ctr: 254-255 R/F: 51@1. Patrolled the line & found, @1 broken Dead end Insulator o/p #4D-27. Cause: Lightning. | 3136056 | 1 | 22:24 | Night | Wednesday | 2015 | 11
1994 | 2015-11-18 22:24 | 2015-11-18 22:24 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 52 | Minas ACB fdr #1 T/R 1x Ctr: 48-49 R/F: 51@2. Not patrolled yet. | 3136056 | 1 | 22:24 | Night | Wednesday | 2015 | 11
1995 | 2015-11-18 22:24 | 2015-11-20 14:24 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 52 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 22:24 | Night | Wednesday | 2015 | 11
1996 | 2015-11-18 22:37 | 2015-11-18 22:37 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 15 | 5B fdr #3 Load dropped 92A (121-20A). (The weather is heavy rain & lightning) Not checked yet. | 3136056 | 1 | 22:37 | Night | Wednesday | 2015 | 11
1997 | 2015-11-18 22:37 | 2015-11-19 10:57 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 15 | 10:57 It was reported no power at downwstream of Recl. 4C-65A. 11:46 Checked & found, Recl. 4C-65A (5B fdr #3) T/SO. Ctr: 120-121. Patrolled the line, but found nothing. 11:54 Blocked & Closed Recl. 4C-65A, Ok. Then released the Block. Cause: Suspected by Lightning. | 3136056 | 1 | 22:37 | Night | Wednesday | 2015 | 11
1998 | 2015-11-19 10:40 | 2015-11-19 10:40 | MINAS POWER PLANT |  |  | - | 10:40 S/U MGT #2, then on line the Unit at 10:48. 13:24 MGT #2 Tripped by alarm: Hydraulic Pressure Low. Cause: Under investigation. |  | 1 | 10:40 | Morning | Thursday | 2015 | 11
1999 | 2015-11-19 13:42 | 2015-11-19 13:42 | 13.8KV MENGGALA FEEDER #2 | Rain and Lightning | Lightning | 34 | Menggala OCB fdr #2 T/R 1x. Menggala GFPC T/R 1x. Not checked yet. | 3136051 | 1 | 13:42 | Afternoon | Thursday | 2015 | 11
2000 | 2015-11-19 13:42 | 2015-11-21 17:42 | 13.8KV MENGGALA FEEDER #2 | Rain and Lightning | Lightning | 34 | Checked & found, Menggala OCB fdr #2 T/R 1x Ctr: 526-527 R/F: 51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 13:42 | Afternoon | Thursday | 2015 | 11
2001 | 2015-11-19 13:55 | 2015-11-19 13:55 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 23 | Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #1 Load dropped 55A (171-116A). Not checked yet. | 3136051 | 1 | 13:55 | Afternoon | Thursday | 2015 | 11
2002 | 2015-11-19 13:55 | 2015-11-25 08:55 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 23 | Checked & found, Ketigul VCB fdr #2 T/R 2x Ctr: 178-180 R/F: 51N(@1). Patrolled the line & found, @1 F/O Pin Insulator o/p #29AL-24. Cause: Lightning. | 3136051 | 1 | 13:55 | Afternoon | Thursday | 2015 | 11
2003 | 2015-11-19 14:22 | 2015-11-19 14:22 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 32 | 4D fdr #4 Load dropped 178A (227-49A). Not checked yet. | 3136056 | 1 | 14:22 | Afternoon | Thursday | 2015 | 11
2004 | 2015-11-19 14:22 | 24/11/2015 15:22 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 32 | Checked & found, Recl. 5B-83 (4D fdr #4) T/R 1x Ctr: 19-20. Patrolled the line & found, @2,@3 F/O Pin Insulators o/p #5E-20. Cause: Lightning. | 3136056 | 1 | 14:22 | Afternoon | Thursday | 2015 | 11
2005 | 2015-11-19 14:22 | 2015-11-19 14:22 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 27 | 4D OCB fdr#5 Load dropped 191A (211-20A). Not checked yet. | 3136056 | 1 | 14:22 | Afternoon | Thursday | 2015 | 11
2006 | 2015-11-19 14:22 | 2015-11-20 16:22 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 27 | Checked & found, Recl. 6E-64 (4D fdr #5) T/R 2x Ctr: 29-31. Patrolled the line & found: -@1 Broken Pin insulator o/p #6E-44B. -@3 Flash over Dead end insulator o/p #6E-46. -@3 Flash over Dead end insulator o/p #6E-44. Cause: Lightning. | 3136056 | 1 | 14:22 | Afternoon | Thursday | 2015 | 11
2007 | 2015-11-19 14:49 | 2015-11-19 14:49 | 13.8KV 6D FEEDER #5 | Fair | Unidentified | 29 | 6D OCB fdr #5 T/R 1x. Not checked yet. | 3136056 | 1 | 14:49 | Afternoon | Thursday | 2015 | 11
2008 | 2015-11-19 14:49 | 2015-11-20 16:49 | 13.8KV 6D FEEDER #5 | Fair | Unidentified | 29 | Checked & found, 6D OCB fdr #5 T/R 1x Ctr: 724-725 R/F: 51@3. Patrolled the line, but found nothing. Cause: Unidentified. | 3136056 | 1 | 14:49 | Afternoon | Thursday | 2015 | 11
2009 | 2015-11-19 14:49 | 2015-11-19 14:49 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 29 | 4D OCB fdr #5 T/R 1x Ctr: 255-256 R/F: 51@3. Not Patrolled yet. | 3136056 | 1 | 14:49 | Afternoon | Thursday | 2015 | 11
2010 | 2015-11-19 14:49 | 2015-11-20 17:49 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 29 | Patrolled the line & found: -@3 Broken Dead end Insulator o/p #4D-27. -@2 Broken Dead end Insulator o/p #6D-285. Cause: Lightning. | 3136056 | 1 | 14:49 | Afternoon | Thursday | 2015 | 11
2011 | 2015-11-19 15:42 | 2015-11-19 15:42 | NORTH DURI POWER PLANT |  |  | - | 15:42 S/U NDC-CT #3, then on line the Unit at 16:10. (Found NDC-CT #3 high Vibration, it would be S/D for fixing the Vibration) |  | 1 | 15:42 | Afternoon | Thursday | 2015 | 11
2012 | 2015-11-19 22:30 | 2015-11-19 22:30 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 8 | 22:30 It was reported any spark at near Well Sedinginan #2. Checked & found, some trees touch to power line near Well Sedinginan #2. Then S/D 100Kva Tx of Well Sedinginan #2, to cut jamper o/p #NN. (6 Spend from Well Sedinginan #2) 20-Nov-2015. 00:30 Re-energized 100Kva Tx & S/U Well Sedinginan #2. Cause: Tree. | 123 | 1 | 22:30 | Night | Thursday | 2015 | 11
2013 | 2015-11-20 07:51 | 2015-11-20 07:51 | 13.8KV NORTH DURI FEEDER #4 | Cloudy and Lightning | Lightning | 0 | No.Duri VCB fdr #4 T/R 1x. (Ground fault alarm at No.Duri fdr #4) Not checked yet. | 3136051 | 1 | 7:51 | Morning | Friday | 2015 | 11
2014 | 2015-11-20 07:51 | 2015-11-25 15:51 | 13.8KV NORTH DURI FEEDER #4 | Cloudy and Lightning | Lightning | 0 | Checked & found, N.Duri VCB fdr #4 T/R 1x Ctr: 164-165 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 7:51 | Morning | Friday | 2015 | 11
2015 | 2015-11-20 10:37 | 2015-11-20 10:37 | MINAS POWER PLANT |  |  | - | 10:37 S/U MGT #2, then On Line the Unit at 11:00. (After Fixing Alarm Over speed Mechanical Trip) | 123 | 1 | 10:37 | Morning | Friday | 2015 | 11
2016 | 2015-11-20 14:17 | 2015-11-20 14:17 | 13.8KV NORTH DURI FEEDER #9 | Cloudy | Unidentified (Fuse) | 7 | 14:17 It was reported b/o fuse for Tx o/p #11-J2-19. (No.Duri fdr #9) 15:45 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #11-J2-19. Replaced b/o fuse above with the same size, then Energized the Tx. Cause: Unidentified (Fuse). | 3136051 | 1 | 14:17 | Afternoon | Friday | 2015 | 11
2017 | 2015-11-20 19:22 | 2015-11-20 19:22 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 14 | C.Duri fdr #1 Load dropped 50A (222-172A). Not checked yet. | 3136051 | 1 | 19:22 | Night | Friday | 2015 | 11
2018 | 2015-11-20 19:22 | 24/11/2015 10:22 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 14 | Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/R 1x Ctr: 225-226. Patrolled the line & found, @1 broken L/A o/p #37AP-04A. Cause: Lightning. | 3136051 | 1 | 19:22 | Night | Friday | 2015 | 11
2019 | 2015-11-20 20:03 | 2015-11-20 20:03 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 76 | Bekasap Main OCB fdr #3 T/R 1x. Beaksap fdr #5 Load dropped 97A (288-191A). T/O WIP at Bekasap-GS. Not Checked yet. | 3136051 | 1 | 20:03 | Night | Friday | 2015 | 11
2020 | 2015-11-20 20:03 | 2015-11-26 17:03 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 76 | Checked & found, Bekasap Main OCB fdr #3 T/R 1x Ctr: 587-588 R/F: 51@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 20:03 | Night | Friday | 2015 | 11
2021 | 2015-11-20 20:50 | 2015-11-20 20:50 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 48 | 44KV Pematang Main OCB #2 (Line to Rangau) T/R 1x. (Rangau Substation no power at that time) Not checked & Patrolled yet. Respectively: Pematang fdr #1 Load dropped 87A(124-37A). Petani fdr #1 Load dropped 70A (188-118A). Production Loss Rangau fdr #1 : 4 Bbls, 5 Wells. Rangau fdr #2 : 40 Bbls, 19 Wells. Pematang fdr #1 : 35 Bbls, 25 Wells. Petani fdr #1 : 8 Bbls, 1 Wells. ------------------------------------------- Total Loss : 87 Bbls, 50 Wells. | 3136051 | 1 | 20:50 | Night | Friday | 2015 | 11
2022 | 2015-11-20 20:50 | 2015-11-26 13:50 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 48 | Checked & found, Pematang Main OCB #2 (Line to Rangau) T/R 1x Ctr: 003-004 R/F: 51@1. Patrolled the line & found, @1 broken Dea end Insulator o/p #RGU-59. Cause: Lightning. | 3136051 | 1 | 20:50 | Night | Friday | 2015 | 11
2023 | 2015-11-21 05:13 | 2015-11-21 05:13 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 2 | 05:13 It was reported spark at FCO for Tx at Well Kulin #40. (C.Duri fdr #1) 11:20 Checked & found, @1, @2, @3 b/o 1.4SF fuses for 75Kva Tx at Well Kulin #40. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3136051 | 1 | 5:13 | Morning | Saturday | 2015 | 11
2024 | 2015-11-21 08:15 | 2015-11-21 08:15 | DURI POWER PLANT |  |  | - | 08:15 Offline DGT #7, then S/D the Unit for S/B. |  | 1 | 8:15 | Morning | Saturday | 2015 | 11
2025 | 2015-11-21 08:20 | 2015-11-21 08:20 | MINAS POWER PLANT |  |  | - | 08:20 Offline MGT #5, then S/D the Unit for S/B. |  | 1 | 8:20 | Morning | Saturday | 2015 | 11
2026 | 2015-11-21 10:00 | 2015-11-21 10:00 | 13.8KV 3D FEEDER #7 | Fair | Transformer Failure | 204 | 10:00 It was reported b/o fuse for Tx at Well #3D-23. (3D fdr #7) 14:30 Checked & found, @1, @2, @3 b/o 14.0SF fuses for 550Kva Tx at Well #3D-23. Performed TTR & Megger Test, found low megger reading. Cause: Tx Failure. (Low megger reading Tx) (Will be replaced tomorrow). | 3136056 | 1 | 10:00 | Morning | Saturday | 2015 | 11
2027 | 2015-11-21 10:00 | 2015-11-22 17:30 | 13.8KV 3D FEEDER #7 | Fair | Transformer Failure | 204 | Replaced 550Kva Tx with the same size, then energized the Tx. Cause: Tx Failure. | 3136056 | 1 | 10:00 | Morning | Saturday | 2015 | 11
2028 | 2015-11-21 10:35 | 2015-11-21 10:35 | MINAS POWER PLANT | Fair | Under investigation | - | 10:35 MGT #2 Tripped by alarm: Hydraulic Pressure Low. Cause: Under Investigation. | 3136056 | 1 | 10:35 | Morning | Saturday | 2015 | 11
2029 | 2015-11-21 16:01 | 2015-11-21 16:01 | 44KV NORTH DURI - DUMAI LINE | Cloudy | Accident | 0 | 16:01 44KV No.Duri GCB #1 (44Kv N.Duri-Dumai line) T/LO. Ctr: 99-103 R/F: 51@2. 16:06 Blocked & closed, 44KV No.Duri GCB #1, Ok. 16:12 44KV GCB #1 (N.Duri-Dumai line) T/O. (Still in blocked position) 16:20 It was reported spark at pole near SPBU Bagan Besar Dumai. 17:00 Manually Open & rack out 4.16Kv Dumai VCB fdr #1, #2, #4, #5. (Planned to S/U Dumai Standby Genset, but cancelled) 17:40 Patrolled & found, PLN team errected power pole under CPI 44KV line & the pole touching- to CPI 44KV power line between pole #DD-212 and #DD-213. 18:04 Isolated PLN pole above from CPI 44KV power line. 18:18 Blocked & closed 44KV N.Duri GCB #1, Ok. Then released the block. 18:22 Blocked & closed 4.16Kv Dumai VCB fdr #1, #2, #4, #5, Ok. Then released the block. Cause: Accident. | 3136051 | 1 | 16:01 | Afternoon | Saturday | 2015 | 11
2030 | 2015-11-22 04:34 | 2015-11-22 04:34 | 13.8KV 8C FEEDER #1 | Rain and Lightning | Lightning | 39 | 8C VCB fdr #1 T/R 1x. Not checked yet. | 3136056 | 1 | 4:34 | Morning | Sunday | 2015 | 11
2031 | 2015-11-22 04:34 | 24/11/2015 14:34 | 13.8KV 8C FEEDER #1 | Rain and Lightning | Lightning | 39 | Checked & found, 8C VCB fdr #1 T/R 1x Ctr: 634-635 R/F: 51N. Patrolled the line & found, @2 broken Dead end Insulator o/p #9C-2D. Cause: Lightning. | 3136056 | 1 | 4:34 | Morning | Sunday | 2015 | 11
2032 | 2015-11-22 07:55 | 2015-11-22 07:55 | 13.8KV 6DN FEEDER #5 | Fair | Transformer Failure | 45 | 07:55 It was reported b/o fuse for Tx at Well #6D-48E. (6DN fdr #5) Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well #6D-48E. Perform TTR & Megger test, found Low mega Ohm reading Tx. Cause: Tx failure. (Low mega Ohm Reading Tx) (will be Replaced tomorrow). | 3136056 | 1 | 7:55 | Morning | Sunday | 2015 | 11
2033 | 2015-11-22 07:55 | 2015-11-23 10:00 | 13.8KV 6DN FEEDER #5 | Fair | Transformer Failure | 45 | Replaced 300Kva Tx failure with the same size, then energized the Tx at Well #6D-48E. Cause: Tx failure. (Low megger redaing Tx) | 3136056 | 1 | 7:55 | Morning | Sunday | 2015 | 11
2034 | 2015-11-22 16:14 | 2015-11-22 16:14 | 13.8KV PINANG FEEDER #1 | Cloudy and Lightning | Lightning | 246 | 16:14 Pinang OCB fdr #1 T/LO. 17:33 Checked & found, Pinang OCB fdr #1 T/LO. Ctr: 354-361 R/F: 51N. Patrolled the line & found, @3 Broken Pin Insulator o/p #12E-03. (TOP of Well Pinang #33) 18:29 Then replaced broken Pin Insulator on pole above. 18:30 Blocked & closed Pinang OCB fdr #1, Ok. Then released the block. Cause: Lightning. | 3136051 | 1 | 16:14 | Afternoon | Sunday | 2015 | 11
2035 | 2015-11-22 16:42 | 2015-11-22 16:42 | 13.8KV MINAS FEEDER #6 | Fair | Transformer Failure | 18 | 16:42 It was reported b/o fuse for Tx at Well #6E-82A. (Minas fdr #6) Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well #6E-82A. Performed TTR & Megger test, found low Mega-ohm Reading Tx. Cause: Tx failure. (Low Mega-ohm Reading Tx) (will be replace tomorrow) | 3136056 | 1 | 16:42 | Afternoon | Sunday | 2015 | 11
2036 | 2015-11-22 16:42 | 2015-11-23 13:00 | 13.8KV MINAS FEEDER #6 | Fair | Transformer Failure | 18 | Replaced 150Kva Tx failure with 225Kva Tx, then energized the Tx at Well #6E-82A. Cause: Tx failure. (Low megger reading Tx) | 3136056 | 1 | 16:42 | Afternoon | Sunday | 2015 | 11
2037 | 2015-11-23 05:02 | 2015-11-23 05:02 | 13.8KV 3D FEEDER #3 | Cloudy and Lightning | Lightning | 0 | 3D GFPC-TX #1 T/R 1x. Ground fault alarm on 3D fdr #3. (No load drop at any fdrs.) Not Checked yet. | 3136056 | 1 | 5:02 | Morning | Monday | 2015 | 11
2038 | 2015-11-23 05:02 | 2015-11-26 11:02 | 13.8KV 3D FEEDER #3 | Cloudy and Lightning | Lightning | 0 | Checked & found, 3D OCB fdr #3 T/R 1x Ctr: 433-434 R/F: 51@2,@3. Also 3D GFPC-Tx #1 T/R 4x Ctr: 4062-4066. Patrolled the line & found: -@2 Broken L/A o/p #3C-60. -@3 F/O Pin Insulator o/p #4C-29. -High Trees & touching power line near Well #4C-44. Cause: Lightning. | 3136056 | 1 | 5:02 | Morning | Monday | 2015 | 11
2039 | 2015-11-23 08:00 | 2015-11-23 08:00 | 13.8KV 4D FEEDER #3 | Fair | Transformer Failure | 6 | 08:00 It was reported b/o fuse for Tx at Well #4D-32. (4D fdr #3) Checked & found, b/o 7.0SF fuse for 225Kva Tx at Well #4D-32. Preformed TTR, Megger test the Tx & found, low megger reading. Cause: Tx failure. (Low megger reading Tx) 11:50 Replaced 225Kva Tx failure with same size, then energized the Tx. Cause: Tx failure. (Low megger reading Tx) | 3136056 | 1 | 8:00 | Morning | Monday | 2015 | 11
2040 | 2015-11-23 09:15 | 2015-11-23 09:15 | 13.8KV 3D FEEDER #7 | Fair | Low mega-ohm reading | 72 | 09:15 It was reported b/o fuse for Tx at Well #3D-23. (3D fdr #7) Checked & found, @1, @2 b/o 14.0SF fuses for 550Kva Tx at Well #3D-23. Performed TTR, Megger test the Tx & found, low mega ohm reading. 17:45 Replace Tx failure above with the same size & energized the Tx. Cause: Tx failure. (Low megger reading Tx) | 3136056 | 1 | 9:15 | Morning | Monday | 2015 | 11
2041 | 2015-11-24 00:25 | 2015-11-24 00:25 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 17 | 4D fdr #2 load drop 111A (164-53A). Not checked yet. | 3136056 | 1 | 0:25 | Night | Tuesday | 2015 | 11
2042 | 2015-11-24 00:25 | 2015-11-26 10:25 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 17 | Checked & found, Recl. 3D-119 (4D fdr #2) T/R 1x Ctr: 23-24. Patrolled the line & found, @1 broken fuse for 50Kva Tx o/p #4D-228. Cause: Lightning. | 3136056 | 1 | 0:25 | Night | Tuesday | 2015 | 11
2043 | 2015-11-24 00:46 | 2015-11-24 00:46 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 47 | 3D OCB fdr #4 T/R 1x. Ground fault alarm at fdr #3 & fdr #4. 3D fdr #3 load drop 23 A (155-132). 3D fdr #5 load drop 120 A (166-46). Not checked yet. | 3136056 | 1 | 0:46 | Night | Tuesday | 2015 | 11
2044 | 2015-11-24 00:46 | 2015-11-26 14:46 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 47 | Checked & found, 3D OCB fdr #4 T/R 2x Ctr: 540-542 R/F: 50@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. Also found, Recl. 2D-33 (3D fdr #4) T/R 2x Ctr: 20-22. Patrolled the line & found, High Trees at near pole #2D-23. Cause: Tree. | 3136056 | 1 | 0:46 | Night | Tuesday | 2015 | 11
2045 | 2015-11-24 01:04 | 2015-11-24 01:04 | 230KV N. DURI SW. YARD - KBJ LINE - 1 | Rain and Lightning | Lightning | 0 | N.Duri 230KV GCB #23 T/R 1x. N.Duri 230KV GCB #25 T/R 1x. KBJ 230KV GCB #91 T/R 1x Ctr: 292-293. KBJ 230KV GCB #92 T/R 1x Ctr: 366-367 R/F: 87L-@1 & 21G-@1 (Zone-1). (230KV N.Duri KBJ Line-1) (No alarm trip at Scada HMI) Not checked & patrolled yet. | 3136051 | 1 | 1:04 | Night | Tuesday | 2015 | 11
2046 | 2015-11-24 01:04 | 2015-11-27 10:25 | 230KV N. DURI SW. YARD - KBJ LINE - 1 | Rain and Lightning | Lightning | 0 | Checked & found: - N.Duri 230KV GCB #23 T/R 1x Ctr: 230-231 R/F: not reported yet. - N.Duri 230KV GCB #25 T/R 1x Ctr: 202. (Did not operate) R/F: 87L-@1. Patrolled the line & found, @1 broken L/A on Towewr #144. Cause: Lightning. | 3136051 | 1 | 1:04 | Night | Tuesday | 2015 | 11
2047 | 2015-11-24 01:32 | 2015-11-24 01:32 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Lightning | 40 | Pungut OCB fdr #1 T/R 1x. Pungut fdr #2 load dropped 68A (88-20A). Not checked yet. | 3136051 | 1 | 1:32 | Night | Tuesday | 2015 | 11
2048 | 2015-11-24 01:32 | 2015-11-26 16:32 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Lightning | 40 | Checked & found, Pungut OCB fdr #1 T/R 1x Ctr: 345-346 R/F: 51@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 1:32 | Night | Tuesday | 2015 | 11
2049 | 2015-11-24 02:10 | 2015-11-24 02:10 | 115KV DURI - KOTABATAK JUNCTION LINE | Rain and Lightning | Lightning | 0 | 02:10 115KV DRB GCB #26 T/R 1x Ctr: 99. (Not Change) R/F: 115KV DRB GCB #28 T/SO 1x Ctr: 142-143 115KV KBJ GCB #43 T/SO 1x Ctr: 411-412 115KV KBJ GCB #45 T/SO 1x Ctr: 297-298 R/F: 87L-(@A,@C) (Duri field SWGR RTU failed at this time) Duri Field SWGR TX-3 also de-eneegized due to 115Kv OCB #22 in maintenance. (Affected Duri Field 115KV TX-3 no power) 02:28 Closed 115KV KBJ GCB #43, but failed. Closed 115KV KBJ GCB #45, but failed. Closed 115KV KBJ GCB #28, but failed. 03:42 Opened 13.8KV ACB #44. (for TX-3 Duri Field SWGR) 03:48 Closed 13.8KV Tie Breaker ACB #49 Duri Field SWGR. (Bus-A of TX-3 energized from Bus-B of TX-5) Duri field fdr #1 energized. 04:31 Closed 115KV DRB GCB #28, but failed. (from local) 04:38 Checked & found, Closing Spring of 115KV DRB GCB #28 discharged. Manual charge the spring, but failed. (Mechanical Problem) 05:13 Closed 115KV KBJ GCB #43, but failed. (from local) Closed 115KV KBJ GCB #45, but failed. (from local) 10:00 Checked Relay for KBJ GCB #43, GCB #45 & found, appeared 86L. (Lock out Relay) Resetting its Relay then functional test the breaker & found, normal operation. Checked DRB GCB #28 & found, motor closing spring charge problem. Then fixed it & functional test the breaker, Ok. (normal operation) 15:28 Opened DRB GCB #26. 15:32 Closed 115KV KBJ GCB #43 & GCB #45. (to energizing 115KV KBJ - DRB line) 16:19 Closed 115KV DRB GCB #28, Ok. (115KV KBJ - DRB line, back to link & normal operation) Note: 115KV DRB GCB #26 is still in open position, for repairing Isolation SW of DRB GCB #22. Patrolled KBJ - DRB line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 2:10 | Night | Tuesday | 2015 | 11
2050 | 2015-11-24 02:10 | 2015-11-24 02:10 | 115KV N. DURI SUBST - DARLING SUB - LINE | Rain and Lightning | Lightning | - | 02:10 115KV N.Duri GCB #2 T/SO. 02:18 Closed 115KV N.Duri GCB #2, Ok. Not checked yet. | 3136051 | 1 | 2:10 | Night | Tuesday | 2015 | 11
2051 | 2015-11-24 02:10 | 2015-11-27 10:29 | 115KV N. DURI SUBST - DARLING SUB - LINE | Rain and Lightning | Lightning | - | 115KV N.Duri GCB #2 T/SO. Ctr: 85-86 R/F: 21 (zone-3). Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 2:10 | Night | Tuesday | 2015 | 11
2052 | 2015-11-24 02:31 | 2015-11-24 02:31 | 13.8KV CENTRAL DURI FEEDER #8 | Rain and Lightning | Lightning | 12 | C.Duri ACB fdr #8 T/R 1x Ctr: 300. (Not change) R/F: 51N. Not Patrolled yet. | 3136051 | 1 | 2:31 | Night | Tuesday | 2015 | 11
2053 | 2015-11-24 02:31 | 2015-11-27 06:53 | 13.8KV CENTRAL DURI FEEDER #8 | Rain and Lightning | Lightning | 12 | Checked & found C.Duri ACB fdr #8 T/R 1x Ctr: 300. (Not change) R/F: 51@1. Patrolled the line,found nothing. Cause: Suspected lightning. | 3136051 | 1 | 2:31 | Night | Tuesday | 2015 | 11
2054 | 2015-11-24 02:46 | 2015-11-24 02:46 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 281 | C.Duri ACB fdr #1 T/R 1x Ctr: 181-182 R/F: 51@3. Not patrolled yet. | 3136051 | 1 | 2:46 | Night | Tuesday | 2015 | 11
2055 | 2015-11-24 02:46 | 2015-11-27 06:55 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 281 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 2:46 | Night | Tuesday | 2015 | 11
2056 | 2015-11-24 05:59 | 2015-11-24 05:59 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 37 | Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #1 load dropped 35A (173-138A). Ketigul fdr #3 load dropped 9A (24-15A). Not checked yet. | 3136051 | 1 | 5:59 | Morning | Tuesday | 2015 | 11
2057 | 2015-11-24 05:59 | 2015-11-26 16:59 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 37 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 180-181 R/F: 51@1. Patrolled the line & found, @1 broken Dead end Insulator o/p #29AM-08. Cause: Lightning. | 3136051 | 1 | 5:59 | Morning | Tuesday | 2015 | 11
2058 | 2015-11-24 06:00 | 2015-11-24 06:00 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 43 | 06:00 It was reported no power at Area-12, Road-F3. 08:00 Checked & found, Recl. 12-F3-25 (N.Duri fdr #1) T/SO. Ctr: 76-77. Blocked & closed Recl. 12-F3-25, Ok. Then released the block. The line is not patrolled yet. | 3136051 | 1 | 6:00 | Morning | Tuesday | 2015 | 11
2059 | 2015-11-24 06:00 | 2015-11-27 07:13 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 43 | Patrolled the line, but found nothing. Cause: Unidentified. | 3136051 | 1 | 6:00 | Morning | Tuesday | 2015 | 11
2060 | 2015-11-24 08:00 | 2015-11-24 08:00 | 13.8KV 8C FEEDER #1 | Fair | Unidentified (Fuse) | 10 | 08:00 It was reported b/o fuse for Tx at Well #9C-47N. 14:10 Checked & found, @2 b/o 7.0SF fuse for 225Kva Tx at Well #9C-47N. Performed TTR & megger test the Tx, found normal. (good reading) Replaced the b/o fuse above with same size, then energized the Tx. Cause: Unidentified (fuse). | 3136056 | 1 | 8:00 | Morning | Tuesday | 2015 | 11
2061 | 2015-11-24 09:20 | 2015-11-24 09:20 | 13.8KV PUNGUT FEEDER #1 | Fair | Unidentified | 441 | 09:20 It was reported no power at Well Pungut #23, #37, #21, #21, #17 and Pungut #22. 10:03 Checked & found Recl. 45BP-09 (Pungut fdr #1) T/LO. Crt: 112-117. Patrolled the line, but found nothing. 10:48 Blocked & closed Recl. 45BP-09, Ok. Then released the block. Cause: Unidentified. | 3136051 | 1 | 9:20 | Morning | Tuesday | 2015 | 11
2062 | 2015-11-24 11:10 | 2015-11-24 11:10 | 13.8KV NORTH DURI FEEDER #9 | Fair | Secondary Cable | 0 | 11:10 It was reported b/o fuse for Tx o/p #11-H7-19. (4 Well were off) 15:00 Checked & found, @1, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #11-H7-19. (Also found burnt out Scondary Cable) Cause: Scondary Cable. | 3136051 | 1 | 11:10 | Morning | Tuesday | 2015 | 11
2063 | 2015-11-24 11:10 | 2015-11-25 17:30 | 13.8KV NORTH DURI FEEDER #9 | Fair | Secondary Cable | 0 | Replaced b/o fuse & secondary cable, also Main breaker then energized the Tx. To be continued tomorrow. | 3136051 | 1 | 11:10 | Morning | Tuesday | 2015 | 11
2064 | 2015-11-24 11:10 | 2015-11-26 17:50 | 13.8KV NORTH DURI FEEDER #9 | Fair | Secondary Cable | 0 | 17:50 Performed TTR, megger test the Tx & found, low megger reading. Cause: Tx failure. (To be continued tomorrow) | 3136051 | 1 | 11:10 | Morning | Tuesday | 2015 | 11
2065 | 2015-11-24 11:10 | 2015-12-15 12:48 | 13.8KV NORTH DURI FEEDER #9 | Fair | Secondary Cable | 0 | Replaced 112.5Kva Tx failure with the same size, then energized the Tx. Cause: Tx failure. (Low Mega-ohm reading Tx) | 3136051 | 1 | 11:10 | Morning | Tuesday | 2015 | 11
2066 | 2015-11-24 11:34 | 2015-11-24 11:34 | 115KV BATANG - SINTONG LINE | Cloudy and Lightning | Lightning | 24 | 115KV Batang GCB #23 T/R 1x. 115KV Sintong GCB #25 T/R 1x. (115KV Batang - Sintong Line) (Appeared alarm Ground fault at Batang fdr #1 & Batang fdr #2) Respectively load dropped: Sintong fdr #1 load dropped 131A (132-101A). Balam fdr #4 load dropped 21A (153-132A). Bangko fdr #1 load dropped 7A (288-281A). Bangko fdr #4 load dropped 8A (238-230A). Not checked yet. | 3136051 | 1 | 11:34 | Morning | Tuesday | 2015 | 11
2067 | 2015-11-24 11:34 | 2015-11-25 15:34 | 115KV BATANG - SINTONG LINE | Cloudy and Lightning | Lightning | 24 | Checked & found: -115KV Batang GCB #23 T/R 1x Ctr: 88-89 R/F: 51N. -115KV Sintong GCB #25 T/R 1x Ctr: 286-287 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 11:34 | Morning | Tuesday | 2015 | 11
2068 | 2015-11-24 17:00 | 2015-11-24 17:00 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Transformer Failure | 0 | 17:00 It was reported unbalance voltage for 2.5Mva Tx at CGS #5. 23:13 Checked & found, interrupter switch for 2.5Mva Tx #3 at CGS #5 could not be opened. Could not be tested the Tx, then Opened all fuses of the Tx. (Will be continued checking the Tx tomorrow) | 3136051 | 1 | 17:00 | Afternoon | Tuesday | 2015 | 11
2069 | 2015-11-24 17:00 | 2015-11-25 16:08 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Transformer Failure | 0 | 16:08 Perform TTR & megger found Low megger reading. Cause: Tx failure (Low megger reading). (The Tx is not replaced yet) | 3136051 | 1 | 17:00 | Afternoon | Tuesday | 2015 | 11
2070 | 2015-11-24 17:00 | 2015-11-28 14:34 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Transformer Failure | 0 | Replaced 2500 Kva Tx with the same size, then energized the Tx. Cause: Tx Failure. | 3136051 | 1 | 17:00 | Afternoon | Tuesday | 2015 | 11
2071 | 2015-11-25 11:00 | 2015-11-25 11:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 0 | 11:00 It was reported b/o fuse for Tx o/p #09-M1-14. (C.Duri fdr #1) 18:25 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #09-M1-14. Replaced b/o fuse above with the same size and energized Tx. Cause: Animal. (Monkey) | 3136051 | 1 | 11:00 | Morning | Wednesday | 2015 | 11
2072 | 2015-11-25 21:39 | 2015-11-25 21:39 | 13.8KV 4D FEEDER #1 | Fair | Unidentified | 0 | 4D OCB fdr #1 T/R 1x. Not checked yet. | 3136056 | 1 | 21:39 | Night | Wednesday | 2015 | 11
2073 | 2015-11-25 21:39 | 2015-11-26 14:39 | 13.8KV 4D FEEDER #1 | Fair | Unidentified | 0 | Checked & found, 4D OCB fdr #1 T/R 1x Ctr: 156-157 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 21:39 | Night | Wednesday | 2015 | 11
2074 | 2015-11-26 09:30 | 2015-11-26 09:30 | MINAS POWER PLANT | Fair |  | - | 09:30 S/U MGT #2, then On line the Unit at 09:55. 10:15 Minas ACB #25. (Tie Breaker) |  | 1 | 9:30 | Morning | Thursday | 2015 | 11
2075 | 2015-11-26 10:00 | 2015-11-26 10:00 | 13.8KV BEKASAP FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 10:00 It was reported b/o fuse for Tx at Bekasap-GS. (Bekasap fdr #5) 15:57 Checked & found, @1,@2 b/o 1.4SF fuses for 75Kva Tx at Bekasap-GS. Replaced b/o fuse above with the same size & energized Tx. Cause: Unidentified (fuse). | 3136051 | 1 | 10:00 | Morning | Thursday | 2015 | 11
2076 | 2015-11-26 11:57 | 2015-11-26 11:57 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 24 | C.Duri ACB fdr #1 T/R 1x Ctr: 182-183 R/F: 51N. Not Patrolled yet. | 3136051 | 1 | 11:57 | Morning | Thursday | 2015 | 11
2077 | 2015-11-26 11:57 | 2015-11-27 07:40 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 24 | Patrolled the line, but found nothing. Cause: Unidentified. | 3136051 | 1 | 11:57 | Morning | Thursday | 2015 | 11
2078 | 2015-11-26 15:13 | 2015-11-26 15:13 | 13.8KV PUNGUT FEEDER #1 | Heavy Rain | Lightning | 179 | 15:13 Pungut fdr #1 Load dropped 32A (76-44A). 18:16 Checked & found, Recl. 45BP-09 (Pungut fdr #1) T/LO. Ctr: 117-120. Patrolled the line, but found nothing. 19:22 Blocked & Closed Recl. 45BP-09, Ok. Then release the block. Cause: Suspected by lightning. | 3136051 | 1 | 15:13 | Afternoon | Thursday | 2015 | 11
2079 | 2015-11-26 15:26 | 2015-11-26 15:26 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Lightning | 0 | OKB fdr #2 load dropped 144A (258-114A). Not checked yet. | 3136056 | 1 | 15:26 | Afternoon | Thursday | 2015 | 11
2080 | 2015-11-26 15:26 | 2015-11-28 07:45 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Lightning | 0 | Checked & found, Recl. 28CX-25 (OKBS fdr #2) T/R 1x Ctr: 90-91. Patrolled the line & found, @3 broken Pin insulator o/p #39CY-20. Cause: Lightning. | 3136056 | 1 | 15:26 | Afternoon | Thursday | 2015 | 11
2081 | 2015-11-26 15:33 | 2015-11-26 15:33 | 13.8KV 4D FEEDER #4 | Heavy Rain | Lightning | 23 | 4D OCB fdr #4 T/R 1x. Not checked yet. | 3136056 | 1 | 15:33 | Afternoon | Thursday | 2015 | 11
2082 | 2015-11-26 15:33 | 2015-11-28 15:33 | 13.8KV 4D FEEDER #4 | Heavy Rain | Lightning | 23 | Checked & found, 4D OCB fdr #4 T/R 5x Ctr: 251-256 R/F: 51N & 51@2. Patrolled the line & found: -@2 Broken Pin Insulator, and -@2 Broken Dead end Insulator o/p #36DN-38. Cause: Lightning. | 3136056 | 1 | 15:33 | Afternoon | Thursday | 2015 | 11
2083 | 2015-11-26 15:33 | 2015-11-26 15:33 | 13.8KV 4D FEEDER #5 | Heavy Rain | Lightning | 22 | 4D OCB fdr #5 T/R 1x. Not checked yet. | 3136056 | 1 | 15:33 | Afternoon | Thursday | 2015 | 11
2084 | 2015-11-26 15:33 | 2015-11-28 15:33 | 13.8KV 4D FEEDER #5 | Heavy Rain | Lightning | 22 | Checked & found, 4D OCB fdr #5 T/R 2x Ctr: 256-258 R/F: 51N & 51@2. Patrolled the line & found, @1,@3 broken Pin Insulators o/p #4D-101. Cause: Lightning. | 3136056 | 1 | 15:33 | Afternoon | Thursday | 2015 | 11
2085 | 2015-11-26 15:33 | 2015-11-26 15:33 | 115KV KOTABATAK JUNCTION-KOTABATAK LINE | Cloudy and Lightning | Lightning | 968 | 115KV KBJ OCB #41 T/R 1x. 115KV KBJ OCB #43 T/R 1x. (115KV KBJ - KOPET line) Not checked yet. | 3136056 | 1 | 15:33 | Afternoon | Thursday | 2015 | 11
2086 | 2015-11-26 15:33 | 2015-11-28 07:15 | 115KV KOTABATAK JUNCTION-KOTABATAK LINE | Cloudy and Lightning | Lightning | 968 | Checked & found: -115KV KBJ OCB #41 T/R 1x Ctr: 415-416. -115KV KBJ OCB #43 T/R 1x Ctr: 208-209 R/F: Not reported yet. (115KV KBJ - KOPET Transmission line) Patrolled the line & found, @1, @3 broken Suspension Insulator o/p #KK-122. Cause: Lightning. | 3136056 | 1 | 15:33 | Afternoon | Thursday | 2015 | 11
2087 | 2015-11-26 16:16 | 2015-11-26 16:16 | 13.8KV 5B FEEDER #3 | Heavy Rain | Lightning | 44 | 5B OCB fdr #3 T/R 1x. Not checked yet. | 3136056 | 1 | 16:16 | Afternoon | Thursday | 2015 | 11
2088 | 2015-11-26 16:16 | 2015-11-28 16:16 | 13.8KV 5B FEEDER #3 | Heavy Rain | Lightning | 44 | Checked & found, 5B OCB fdr #3 T/R 1x Ctr: 355-356 R/F: Did not operate. Patrolled the line & found: -@1 Broken L/A o/p #4C-43. -@1 Broken Dead end Insulator o/p #NN. (near Well #4D-52N) -@1 Broken Dead end Insulator o/p #4C-62. Cause: Lightning. Also found, Recl. 4C-65A (5B fdr #3) T/R 1x Ctr: 121-122. Patrolled the line & found, danger high Trees under power line between poles #4D-01 and #4D-02. Cause: Trees. | 3136056 | 1 | 16:16 | Afternoon | Thursday | 2015 | 11
2089 | 2015-11-26 16:16 | 2015-11-26 16:16 | 13.8KV 5B FEEDER #2 | Heavy Rain | Lightning | 0 | 5B fdr #2 load dropped 117A (166-49A). Not checked yet. | 3136056 | 1 | 16:16 | Afternoon | Thursday | 2015 | 11
2090 | 2015-11-26 16:16 | 2015-11-28 17:16 | 13.8KV 5B FEEDER #2 | Heavy Rain | Lightning | 0 | Checked & found, Recl. 5C-07 (5B fdr #2) T/R 1x Ctr: 45-46. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 16:16 | Afternoon | Thursday | 2015 | 11
2091 | 2015-11-26 16:26 | 2015-11-26 16:26 | 13.8KV 5B FEEDER #2 | Heavy Rain | Lightning | 38 | 5B OCB fdr #2 T/R 1x. Not checked yet. | 3136056 | 1 | 16:26 | Afternoon | Thursday | 2015 | 11
2092 | 2015-11-26 16:26 | 2015-11-28 17:26 | 13.8KV 5B FEEDER #2 | Heavy Rain | Lightning | 38 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 331-332 R/F: Did not appear. Patrolled the line & found: -@1 Broken Dead end Insulator, and -@2 Flashed over Dead end Insulator o/p #4C-59. Cause: Lightning. | 3136056 | 1 | 16:26 | Afternoon | Thursday | 2015 | 11
2093 | 2015-11-26 16:46 | 2015-11-26 16:46 | 13.8KV 3D FEEDER #8 | Heavy Rain | Lightning | 20 | 3D OCB fdr #8 T/R 1x. Not checked yet. | 3136056 | 1 | 16:46 | Afternoon | Thursday | 2015 | 11
2094 | 2015-11-26 16:46 | 2015-11-28 16:46 | 13.8KV 3D FEEDER #8 | Heavy Rain | Lightning | 20 | Checked & found, 3D OCB fdr #8 T/R 2x Ctr: 168-170 R/F: 51@1,@3. Patrolled the line & found, @2 broken L/A o/p #3D-46. Cause: Lightning. | 3136056 | 1 | 16:46 | Afternoon | Thursday | 2015 | 11
2095 | 2015-11-26 16:58 | 2015-11-26 16:58 | 13.8KV 6DN FEEDER #2 | Heavy Rain | Lightning | 66 | 6DN OCB fdr #2 T/R 1x. Not checked yet. | 3136056 | 1 | 16:58 | Afternoon | Thursday | 2015 | 11
2096 | 2015-11-26 16:58 | 2015-02-12 09:58 | 13.8KV 6DN FEEDER #2 | Heavy Rain | Lightning | 66 | Checked & found, 6DN OCB fdr #2 T/R 1x Ctr: 295-296 R/F: 51@1,@3. Patrolled the line, but found nothing. Also found, Recl. 6D-50 (6DN fdr #2) T/R 1x Ctr: 26-27. Patrolled the line & found, @1 broken Dead end Insulator o/p #5D-59. Cause: Lightning. | 3136056 | 1 | 16:58 | Afternoon | Thursday | 2015 | 11
2097 | 2015-11-26 17:02 | 2015-11-26 17:02 | 115KV 4D - 6DN LINE | Heavy Rain | Lightning | 0 | 115Kv 6DN GCB #21 (line to 4D Substation) T/R 1x. 115KV 4D GCB #23 (Scada failed) 115KV 4D GCB #24 (Scada failed) (115KV 4D Substation - 6DN line) Not checked yet. | 3136056 | 1 | 17:02 | Afternoon | Thursday | 2015 | 11
2098 | 2015-11-26 17:02 | 2015-02-12 17:02 | 115KV 4D - 6DN LINE | Heavy Rain | Lightning | 0 | Checked & found: -115KV 4D GCB #23 T/R 1x Ctr: 480-481. -115KV 4D GCB #24 T/R 1x Ctr: 637-638. -115KV 6DN GCB #21 T/R 1x Ctr: 415-416 R/F: 87L-@C. (115KV 4D - 6DN Transmission line) Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 17:02 | Afternoon | Thursday | 2015 | 11
2099 | 2015-11-26 17:03 | 2015-11-26 17:03 | 13.8KV 6D FEEDER #5 | Heavy Rain | Lightning | 0 | 6D OCB fdr #5 T/R 1x. Not checked yet. | 3136056 | 1 | 17:03 | Afternoon | Thursday | 2015 | 11
2100 | 2015-11-26 17:03 | 2015-02-12 09:03 | 13.8KV 6D FEEDER #5 | Heavy Rain | Lightning | 0 | Checked & found, 6D OCB fdr #5 T/R 1x Ctr: 725-726 R/F: 51@1,@2,@3. Patrolled the line & found: -@1 Broken Pin Insulator o/p #6D-504. -@1 Flashed Over Dead end Insulator o/p #6D-467. Cause: Lightning. | 3136056 | 1 | 17:03 | Afternoon | Thursday | 2015 | 11
2101 | 2015-11-26 17:03 | 2015-11-26 17:03 | 115KV MINAS - 5B LINE | Heavy Rain | Lightning | 0 | 17:03 115KV MSY OCB #51 T/O. Ctr: Not checked yet. R/F: 86LK-1. 115Kv MSY OCB #53 T/O. Ctr: Not checked yet. 115KV 5B OCB #22 T/R. Ctr: 661-662. 115KV 5B OCB #25 T/O. Ctr: 207-208. R/F: Not reported yet. 115KV 5B OCB #24 T/O. Ctr: 299-300. (115KV MSY - 5B Substation line) In the same time 115KV MSY Breaker T/O: 115KV MSY OCB #10 (115KV Tie Bus #3 & Tie Bus #4) T/O. 115KV MSY OCB #41 (115KV to TX-7) T/O. 115KV MSY OCB #71 (115KV to TX-10) T/O. 115KV MSY OCB #61 (115KV to TX-9) is still in close position. Cause: Under Investigation. 19:25 Checked & found: MSY GCB #10 T/O. Ctr: Not checked yet, then closed at 19:52. MSY GCB #41 T/O. Ctr: Not checked yet, then closed at 19:53 MSY GCB #71 T/O. Ctr: Not checked yet, then closed at 19:55. 5B OCB #22 T/R 1x Ctr:661-662. 5B OCB #24 T/O. Ctr: 229-300, but failed closed. 5B OCB #25 T/O. Ctr: 207-208, Closed at 19:56. MSY GCB #51 T/O. Ctr: Not checked yet, then closed at 19:56 MSY GCB #53 T/O. Ctr: Not checked yet, Closed at 19:56. (115KV 5B Substation - MSY line, Energized) Not Checked & Patrolled yet. | 3136056 | 1 | 17:03 | Afternoon | Thursday | 2015 | 11
2102 | 2015-11-26 17:03 | 2015-02-12 17:03 | 115KV MINAS - 5B LINE | Heavy Rain | Lightning | 0 | Patrolled 5B - MSY Transimission line, but found nothing. Cause: Suspected by Lightnig. | 3136056 | 1 | 17:03 | Afternoon | Thursday | 2015 | 11
2103 | 2015-11-26 17:04 | 2015-11-26 17:04 | 13.8KV 6D FEEDER #6 | Rain and Lightning | Lightning | 4 | 6D OCB fdr #6 T/R 1x. Not checked yet. | 3136056 | 1 | 17:04 | Afternoon | Thursday | 2015 | 11
2104 | 2015-11-26 17:04 | 2015-02-12 09:04 | 13.8KV 6D FEEDER #6 | Rain and Lightning | Lightning | 4 | Checked & found, 6D OCB fdr #6 T/R 1x Ctr: 570. (not change) R/F: Did not appear. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 17:04 | Afternoon | Thursday | 2015 | 11
2105 | 2015-11-26 23:08 | 2015-11-26 23:08 | 4.16KV SO RUMBAI FEEDER #3 | Rain | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx at Complex Enau #342. (So.Rumbai fdr #3) Not checked yet. | 3136056 | 1 | 23:08 | Night | Thursday | 2015 | 11
2106 | 2015-11-26 23:08 | 2015-11-27 01:30 | 4.16KV SO RUMBAI FEEDER #3 | Rain | Unidentified (Fuse) | 0 | Checked & found, @2 b/o 1.0SF fuse for 50Kva Tx at Rumbai complex Enau #342. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3136056 | 1 | 23:08 | Night | Thursday | 2015 | 11
2107 | 2015-11-27 06:26 | 2015-11-27 06:26 | 13.8KV PEMATANG FEEDER #1 | Fair | Lightning Arrester | 173 | Pematang VCB fdr #1 T/R 1x. Pematang fdr #2 Load dropped 24A (48-24A). Not checked yet. | 3136051 | 1 | 6:26 | Morning | Friday | 2015 | 11
2108 | 2015-11-27 06:26 | 2015-01-12 14:51 | 13.8KV PEMATANG FEEDER #1 | Fair | Lightning Arrester | 173 | Checked & found, Pematang VCB fdr #1 T/R 1x Ctr: 116-117 R/F: Did not appeare. Patrolled the line & found, @1 broken L/A on TP of Well Pematang #67. Cause: Lightning Arrester. | 3136051 | 1 | 6:26 | Morning | Friday | 2015 | 11
2109 | 2015-11-27 16:44 | 2015-11-27 16:44 | 13.8KV PUNGUT FEEDER #1 | Fair | Planned Maintenance | 20 | 16:44-17:00 Manually Open Recl. 45BP-09. (Pungut fdr #1) to replacing seriously @1 broken Pin insulator o/p #44BN-01. Cause: Planned Maintenance. | 123 | 1 | 16:44 | Afternoon | Friday | 2015 | 11
2110 | 2015-11-27 18:00 | 2015-11-27 18:00 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 37 | Bekasap VCB fdr #6 T/R 1x. Not checked yet. | 3136051 | 1 | 18:00 | Afternoon | Friday | 2015 | 11
2111 | 2015-11-27 18:00 | 2015-01-12 14:53 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 37 | Checked & found, Bekasap VCB fdr #6 T/R 1x Ctr: 331-332 R/F: 51@1. Patrolled the line & found, @1 broken Dead end insulator o/p #39BF-19. Cause: Lightning. | 3136051 | 1 | 18:00 | Afternoon | Friday | 2015 | 11
2112 | 2015-11-28 14:30 | 2015-11-28 14:30 | MINAS POWER PLANT | Fair | Under investigation | - | MGT #2 Tripped By alarm: Mechanical Over speed. Cause : Under Investigation | 123 | 1 | 14:30 | Afternoon | Saturday | 2015 | 11
2113 | 2015-11-29 07:17 | 2015-11-29 07:17 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 64 | Bangko OCB fdr #4 T/R 1x. Not checked yet. | 3136051 | 1 | 7:17 | Morning | Sunday | 2015 | 11
2114 | 2015-11-29 07:17 | 2015-11-30 15:00 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 64 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99975-99976 R/F: 51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136051 | 1 | 7:17 | Morning | Sunday | 2015 | 11
2115 | 2015-11-29 08:00 | 2015-11-29 08:00 | DURI POWER PLANT |  |  | - | 08:00 S/U DGT #7, then On Line the Unit at 08:25. |  | 1 | 8:00 | Morning | Sunday | 2015 | 11
2116 | 2015-11-29 10:40 | 2015-11-29 10:40 | CENTRAL DURI POWER PLANT |  |  | - | 10:40 Off Line CGT #5, then S/D the Unit at 10:42. (for S/B prior to Combustion Inspection program / CI) |  | 1 | 10:40 | Morning | Sunday | 2015 | 11
2117 | 2015-11-29 14:03 | 2015-11-29 14:03 | 13.8KV 5B FEEDER #4 | Heavy Rain | Lightning | 0 | 5B fdr #4 load dropped 200A (260-60A). Not checked yet. | 3136056 | 1 | 14:03 | Afternoon | Sunday | 2015 | 11
2118 | 2015-11-29 14:03 | 2015-01-12 13:19 | 13.8KV 5B FEEDER #4 | Heavy Rain | Lightning | 0 | Checked & found, Recl. 4B-73 (5B fdr #4) T/R 1x Ctr: 48-49. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3136056 | 1 | 14:03 | Afternoon | Sunday | 2015 | 11
2119 | 2015-11-29 14:07 | 2015-11-29 14:07 | 13.8KV 6D FEEDER #1 | Heavy Rain | Lightning | 44 | 6D OCB fdr #1 T/R 1x. Not checked yet. | 3136056 | 1 | 14:07 | Afternoon | Sunday | 2015 | 11
2120 | 2015-11-29 14:07 | 2015-01-12 13:15 | 13.8KV 6D FEEDER #1 | Heavy Rain | Lightning | 44 | Checked & found, 6D OCB fdr #1 T/R 1x Ctr: 300-301 R/F: 51N. Patrolled the line & found, @3 broken Dead end insulator o/p #6B-43. Cause: Lightning. | 3136056 | 1 | 14:07 | Afternoon | Sunday | 2015 | 11
2121 | 2015-11-30 00:30 | 2015-11-30 00:30 | DURI POWER PLANT | Fair | Under investigation | - | 00:30 DGT #7 Opened Generator Breaker, By alarm: Generator Breaker Trip. Frequency system dropped to 59.83Hz. (No load shedding) 01:04 Re-Online DGT #7 to the system. Cause: Under Investigation. | 3136051 | 1 | 0:30 | Night | Monday | 2015 | 11
2122 | 2015-11-30 04:30 | 2015-11-30 04:30 | 13.8KV 6D FEEDER #2 | Fair | Pin Insulator | 43 | 6D fdr #2 load dropped 110A (173-63A). Not checked yet. | 3136056 | 1 | 4:30 | Morning | Monday | 2015 | 11
2123 | 2015-11-30 04:30 | 2015-02-12 15:04 | 13.8KV 6D FEEDER #2 | Fair | Pin Insulator | 43 | Checked & found, Recl. 6D-298 (6D fdr #2) T/R 1x Ctr: 34-35. Patrolled the line & found, @2 Flash Over Pin Insulator o/p #7C-45. Cause: Pin Insulator. | 3136056 | 1 | 4:30 | Morning | Monday | 2015 | 11
2124 | 2015-11-30 11:05 | 2015-11-30 11:05 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 13 | 11:05 It was reported b/o fuse for Tx o/p #12-F3-22. (N.Duri fdr #1) 14:50 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx o/p #12-F3-22. Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal. (Bird) | 3136051 | 1 | 11:05 | Morning | Monday | 2015 | 11
2125 | 2015-11-30 14:55 | 2015-11-30 14:55 | MINAS POWER PLANT |  |  | - | 14:55 S/U MGT #6, then On Line the Unit at 15:40. (For running on test after replacing Load Gear) |  | 1 | 14:55 | Afternoon | Monday | 2015 | 11
2126 | 2015-11-30 23:05 | 2015-11-30 23:05 | 13.8KV 4B FEEDER #2 | Fair | Post Pin Insulator | 18 | 4B OCB fdr #2 T/R 1x. Not checked yet. | 3136056 | 1 | 23:05 | Night | Monday | 2015 | 11
2127 | 2015-11-30 23:05 | 2015-02-12 16:07 | 13.8KV 4B FEEDER #2 | Fair | Post Pin Insulator | 18 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 218-219 R/F: 51N. Patrolled the line & found, @2 Bypass Insulator of Recl. 4B-06. Cause: Post Insulator. (Bypass Insulator of Recl. 4B-06) | 3136056 | 1 | 23:05 | Night | Monday | 2015 | 11
2128 | 2015-01-12 18:33 | 2015-01-12 18:33 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 0 | Ketigul fdr #1 Load dropped 61A (158-97A). Not checked yet. | 3150433 | 1 | 18:33 | Afternoon | Monday | 2015 | 1
2129 | 2015-01-12 18:33 | 2015-06-12 08:27 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 0 | Checked & found, Recl. 32AK-16 (Ketigul fdr #1) T/R 1x Ctr: 115-116. Patrolled the line, but nothing found. Cause: Unidentified. | 3150433 | 1 | 18:33 | Afternoon | Monday | 2015 | 1
2130 | 2015-01-12 22:23 | 2015-01-12 22:23 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 76 | Bangko OCB fdr #4 T/R 1x. Bangko fdr #1 load dropped 21A (280-259A). (Bangko GFPC was in block position) Not checked yet. | 3150433 | 1 | 22:23 | Night | Monday | 2015 | 1
2131 | 2015-01-12 22:23 | 2015-02-12 14:46 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 76 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99976-99977 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3150433 | 1 | 22:23 | Night | Monday | 2015 | 1
2132 | 2015-02-12 00:02 | 2015-02-12 00:02 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Powerline - Conductor | 397 | 00:02 Pungut fdr #1 load dropped 35A (77-42A). (The weather was still rain) 03:00 Checked & found, Recl. 45BP-09 (Pungut fdr #1) T/LO. Ctr: 123-127. Found, @2 broken conductor o/p #NN. (near Well Pungut #24 / 2 Spans from the Well) 05:00 Isolated broken conductor by cut Jumper o/p #44BN-01. (All well under this pole are OBS Wells) 05:10 Blocked & closed Recl. 45BP-09, Ok. Then released the block. 11:30 Manually Opened Recl. 45BP-09, to repairing the Broken Conductor above. 15:10 Blocked & closed Recl. 45BP-09, Ok. Then release the block. Cause: Conductor. | 3150433 | 1 | 0:02 | Night | Thursday | 2015 | 2
2133 | 2015-02-12 02:57 | 2015-02-12 02:57 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain and Lightning | Lightning | 0 | 4.16Kv Dumai ACB fdr #4 (Housing) T/R 1x. Not checked yet. | 3150433 | 1 | 2:57 | Night | Thursday | 2015 | 2
2134 | 2015-02-12 02:57 | 2015-08-12 15:00 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, 4.16KV Dumai (Housing) VCB fdr #4 T/R 1x. Ctr: 261. (Did not change) R/F: (Did not appear) Patrolled the line, but found nothing. Also found, Recl. H33-07 (Dumai fdr #4) T/R 1x Ctr: 100-101. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 2:57 | Night | Thursday | 2015 | 2
2135 | 2015-02-12 08:04 | 2015-02-12 08:04 | 13.8KV S. BALAM FEEDER #1 | Rain | Lightning | 180 | 08:04 So.Balam VCB fdr #1 T/R 1x. (So.Balam GFPC, in block position) 15:48 Checked & found, So.Balam VCB fdr #1 T/R 1x Ctr: 343. (Not change) R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 8:04 | Morning | Thursday | 2015 | 2
2136 | 2015-03-12 10:53 | 2015-03-12 10:53 | MINAS POWER PLANT |  |  | - | Off Line MGT #6, then S/D the Unit for Stand by. |  | 1 | 10:53 | Morning | Thursday | 2015 | 3
2137 | 2015-03-12 14:26 | 2015-03-12 14:26 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | 4 | 14:26 It was reported no power on pole #06-R1-15. (C.Duri fdr #15) 15:40 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #06-R1-15 Performed TTR, Megger the Tx & found, good reading. Replaced b/o fuse above with same size & Energized the Tx. Cause: Unidentified (fuse). | 3150433 | 1 | 14:26 | Afternoon | Thursday | 2015 | 3
2138 | 2015-03-12 16:45 | 2015-03-12 16:45 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 44 | CKBS VCB fdr #1 T/R 1x. Not checked yet. | 3150434 | 1 | 16:45 | Afternoon | Thursday | 2015 | 3
2139 | 2015-03-12 16:45 | 2015-06-12 16:45 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 44 | Checked & found, CKBS VCB fdr #1 T/R 1x Ctr: 200-201 R/F: 51@1,@3. Patrolled the line & found, @1,@3 broken Pin Insulators o/p #36CV-01. Cause: Lightning. | 3150434 | 1 | 16:45 | Afternoon | Thursday | 2015 | 3
2140 | 2015-03-12 16:45 | 2015-03-12 16:45 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 0 | CKBS fdr #5 Load dropped 181A (343-162A). Not checked yet. | 3150434 | 1 | 16:45 | Afternoon | Thursday | 2015 | 3
2141 | 2015-03-12 16:45 | 2015-06-12 16:45 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, the Recl. 36CU-29 (CKBS fdr #5) T/R 1x Ctr: 69. (Did not change) Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150434 | 1 | 16:45 | Afternoon | Thursday | 2015 | 3
2142 | 2015-03-12 16:50 | 2015-03-12 16:50 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Rain and Lightning | Lightning | 25 | CKBS VCB fdr #6 T/R 1x. Not checked yet. | 3150434 | 1 | 16:50 | Afternoon | Thursday | 2015 | 3
2143 | 2015-03-12 16:50 | 2015-06-12 07:27 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Rain and Lightning | Lightning | 25 | Checked & found CKBS VCB fdr #6 T/R 1x Ctr: 120-121 R/F: 51@1. Patrolled the Line & found, @1 broken Pin insulator o/p #34CV-07. Cause: Lightning. | 3150434 | 1 | 16:50 | Afternoon | Thursday | 2015 | 3
2144 | 2015-03-12 17:58 | 2015-03-12 17:58 | MINAS POWER PLANT |  |  | - | 17:58 S/U MGT #2, tehn On line the Unit at 18:22. |  | 1 | 17:58 | Afternoon | Thursday | 2015 | 3
2145 | 2015-04-12 07:00 | 2015-04-12 07:00 | MINAS POWER PLANT |  |  | - | MGT #7 T/O. By alarm: Over speed bolt trip. Cause: Under Investigation. |  | 1 | 7:00 | Morning | Sunday | 2015 | 4
2146 | 2015-04-12 11:27 | 2015-04-12 11:27 | 13.8KV DURI FIELD FEEDER #2 | Fair | Secondary Cable | 29 | 11:27 It was reported b/o fuse for Tx o/p #07-U3-39. (D.Field fdr #2) Checked & found, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #07-U3-39. Replaced b/o fuse above with the same size & energized the Tx. Checked the voltage & found, unbalance voltage. (@3 broken secondary cable) 05-Dec-2015. 11:00 Replaced broken secondary cable & Energized the TX. Cause: Secondary cable. | 3150433 | 1 | 11:27 | Morning | Sunday | 2015 | 4
2147 | 2015-04-12 16:38 | 2015-04-12 16:38 | 13.8KV BATANG FEEDER #3 | Fair | Lightning Arrester | 46 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3150433 | 1 | 16:38 | Afternoon | Sunday | 2015 | 4
2148 | 2015-04-12 16:38 | 2015-11-12 15:38 | 13.8KV BATANG FEEDER #3 | Fair | Lightning Arrester | 46 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 298-299 R/F: 51N(@1). Patrolled the line & found, @1 broken L/A on TP of Well Pemburu #14. Cause: Lightning Arrester. | 3150433 | 1 | 16:38 | Afternoon | Sunday | 2015 | 4
2149 | 2015-05-12 04:30 | 2015-05-12 04:30 | 230KV N. Duri-KBJ Line - 2 - TWR 61-128 | Rain and Lightning | Lightning | 0 | 04:30 230Kv Line N.Duri GCB #11 T/R 1x. 230Kv Line N.Duri GCB #13 T/R 1x. 230Kv Line KBJ GCB #94 T/R 1x Ctr:.... R/F: 87L-@3, 67N (Inst) & 21@3 (Zone-1). 230Kv Line KBJ GCB #93 T/O. Then closed at 06:10, but fail. (230Kv No.Duri - KBJ Line #2) Not checked & patrol yet. | 3150433 | 1 | 4:30 | Morning | Tuesday | 2015 | 5
2150 | 2015-05-12 04:30 | 2015-10-12 10:30 | 230KV N. Duri-KBJ Line - 2 - TWR 61-128 | Rain and Lightning | Lightning | 0 | Checked & found: 230KV No.Duri GCB #11 T/R 1x Ctr: 286-287. 230KV No.Duri GCB #13 T/R 1x Ctr: 272-273. R/F: 87L-@2,@3 & 67N (Instn) 230Kv KBJ GCB #94 T/R 1x Ctr: 244-246. 230Kv KBJ GCB #93 T/O. Ctr: 273-274. R/F: 87L-@3, 67N (Instn) & 21@3 (Zone-1). Patrolled 230KV line from No.Duri Tower #01 toward Tower #125, but found nothing. (By TDO North) The line 230KV from KBJ Tower #192 toward Tower #125 is not patrolled yet. (By TDO South) Patrolled 230KV KBJ - No.Duri line-2 is not completed yet. | 3150433 | 1 | 4:30 | Morning | Tuesday | 2015 | 5
2151 | 2015-05-12 04:30 | 15/12/2015 09:30 | 230KV N. Duri-KBJ Line - 2 - TWR 61-128 | Rain and Lightning | Lightning | 0 | Completed to patrolling 230KV KBJ - No.Duri Line-2 & found: -@3 Flashed over Dead end Insulator on Tower #170. Cause: Lightning. | 3150433 | 1 | 4:30 | Morning | Tuesday | 2015 | 5
2152 | 2015-05-12 04:30 | 2015-05-12 04:30 | KOTABATAK JUNCTION SW STA | Rain and Lightning | Equipment Failure | 183 | 04:30 230Kv KBJ GCB #91 T/O. Ctr: 293-294. 230Kv KBJ GCB #93 T/O. Ctr: 244-246. 115Kv GCB #22 T/O. Ctr: 166-167. (indication close at DSC) 115Kv GCB #24 T/O. Ctr: 413-414 R/F: 87@A,@B,@C & 86T. (230Kv KBJ TX #2 No power ) Respectively load dropped : 8C OCB fdr#1 Load dropped 28A (243-215A). 8C OCB fdr#3 Load dropped 17A (215-198A). 8C OCB fdr#4 Load dropped 111A (305-194A). 8D OCB fdr#3 Load dropped 11A (197-186A). 8D OCB fdr#4 Load dropped 57A (168-111A) (Pump Off). 8D OCB fdr#8 Load dropped 123A (182-59A) (Pump Off). 8D OCB fdr#9 Load dropped 123A (197-71A) (Pump Off). 6D OCB fdr#1 Load dropped 34A (293-259A). 6D OCB fdr#2 Load dropped 12A (189-177A). 6D OCB fdr#3 Load dropped 162A (355-193A) (Pump Off). 6D OCB fdr#5 Load dropped 66A (260-194A). 6D OCB fdr#6 Load dropped 53A (177-124A) (Pump Off). 3D OCB fdr#3 Load dropped 35A (155-120A). 3D OCB fdr#4 Load dropped 13A (265-252A). 3D OCB fdr#5 Load dropped 115A (218-103A) (Pump Off). 3D OCB fdr#7 Load dropped 120A (120-0A). 3D OCB fdr#8 Load dropped 37A (280-243A). 4D OCB fdr#2 Load dropped 13A (148-135A). 4D OCB fdr#4 Load dropped 59A (265-206A). 4D OCB fdr#5 Load dropped 37A (237-200A). 4B OCB fdr#1 Load dropped 39A (335-296A). 4B OCB fdr#2 Load dropped 24A (110-86A). 4B OCB fdr#3 Load dropped 130A (138-8A) (Pump Off). 4B OCB fdr#5 Load dropped 117A (194-77A) (Pump Off). 5B OCB fdr#1 Load dropped 15A (93-78A). 5B OCB fdr#2 Load dropped 17A (161-144A). 5B OCB fdr#3 Load dropped 18A (111-93A). 5B OCB fdr#4 T/SO, then closed at 04:36. 5B OCB fdr#5 T/SO, then closed at 04:36. OKB VCB fdr#2 Load dropped 39A (262-223A). NKB VCB fdr#3 Load dropped 29A (385-356A) (Pump Off). NKB OCB fdr#4 Load dropped 27A (74-47A) (Pump Off). NKB OCB fdr#5 Load dropped 192A 228-36A) (Pump Off). CKB OCB fdr#2 Load dropped 236A (266-30A) (Pump Off). CKB OCB fdr#5 Load dropped 143A (332-18930A). CKB OCB fdr#6 Load dropped 24A (266-30A). Petapahan OCB fdr#2 Load dropped 50A (149-99A). Suram OCB fdr#1 Load dropped 11A (81-70A). Suram OCB fdr#2 Load dropped 10A (29-19A). Bangko VCB fdr#1 Load dropped 18A (278-260A). Bangko VCB fdr#4 Load dropped 40A (258-218). So.Bekasap fdr#1 Load dropped 25A (183-158A). Bekasap VCB fdr#5 Load dropped 59A (267-208A) (Pump Off). Pematang VCB fdr#1 Load dropped 27A (118-97A). Petani VCB fdr#1 Load dropped 32A (200-168A). Libo VCB fdr#1 Load dropped 20A (92-70A). 09:35 Checked & found: 230 KV KBJ Power TX #2. - Winding temperature: 45/65. - Liquid temperature : 45/65. (Also found @1 Broken CCPD at 115Kv side of Power TX-2) 11:00 Open 230Kv line switch for isolate TX-2 power source from 230Kv. Open 115Kv Line switch for isolate TX-2 power from 115Kv. 11:55 Closed 230Kv KBJ GCB #91. Closed 230Kv KBJ GCB #93. 11:56 Closed 115Kv KBJ GCB #22. Closed 115Kv KBJ GCB #24, but failed. 15:15 Re-Opened 115Kv KBJ GCB #22 for trobleshooting of 115Kv KBJ GCB # 24. Cause: Equipment failure. (Broken @1 CCPD of 115KV side of KBJ Power TX-2) Prod. loss reported by SLS-GS = 259 Bbls / 56 Wells. Prod. loss reported by SLN-GS = 61 Bbls / 5 Wells. Total Prod. loss = 320 Bbls / 61 Wells. Prod. loss reported by EC system = 183 bbls / 35 Wells (On progress to replacing the broken CCPD above & testing the TX-2) | 3150434 | 1 | 4:30 | Morning | Tuesday | 2015 | 5
2153 | 2015-05-12 04:30 | 2015-11-12 16:42 | KOTABATAK JUNCTION SW STA | Rain and Lightning | Equipment Failure | 183 | Switching to Energized 230Kv Power Tx-2 at KBJ. (After replacing @1 115Kv CCPD & functioning test the Relay also breaker at KBJ) Cause: Equipment failure. (Broken @1 115Kv CCPD at KBJ) | 3150434 | 1 | 4:30 | Morning | Tuesday | 2015 | 5
2154 | 2015-05-12 14:12 | 2015-05-12 14:12 | 13.8KV 8D FEEDER #11 | Fair | Transformer Failure | 24 | It was reported b/o fuse for Tx at Well #9E-41N. (8D fdr #11) Not checked yet. | 3150434 | 1 | 14:12 | Afternoon | Tuesday | 2015 | 5
2155 | 2015-05-12 14:12 | 2015-07-12 15:00 | 13.8KV 8D FEEDER #11 | Fair | Transformer Failure | 24 | Checked & found, @1,@2 b/o 7.8SF fuses for 250Kva Tx at Well #9E-41N. Performed test the Tx & found, Low megger reading. Then replaced 250Kva Tx failure with the same size & energized the Tx. Cause: Tx failure. (Low megger reading) | 3150434 | 1 | 14:12 | Afternoon | Tuesday | 2015 | 5
2156 | 2015-05-12 17:53 | 2015-05-12 17:53 | MINAS POWER PLANT |  |  | - | 17:53 S/U MGT #6, then On Line the Unit at 18:20. (Running on test after Fixing Lube Oil leak at Load gear coupling) | 123 | 1 | 17:53 | Afternoon | Tuesday | 2015 | 5
2157 | 2015-06-12 01:47 | 2015-06-12 01:47 | MINAS SWITCH YARD | Fair | Under investigation | 0 | 01:47 115KV MSY GCB #10 T/O. Ctr: not reported yet. R/F: 86SE & 87B-@3. 115KV MSY OCB #21 T/O. 115KV MSY OCB #25 T/O. 115KV MSY GCB #31 T/O. 115KV MSY GCB #81 T/O. (115KV MSY South East BUS-4 no power) 02:40 Checked All 115KV MSY GCB & OCB are Normal condition. 03:02 Closed 115KV MSY GCB #10, Ok. (115KV MSY Tie BUS-3 & BUS-4) 03:06 Closed 115KV MSY GCB #21, Ok. 03:07 Closed 115KV MSY GCB #25, Ok. 03:08 Closed 115KV MSY GCB #31, Ok. 03:09 Closed 115KV MSY GCB #81, but failed. (115KV Breaker #81 to MSY TX-11) 03:29 Open Isolation Switch of MSY GCB #81, to function test. Found Broken Isolation SW Bar of GCB #81 to 115KV MSY Bus #4 side. Cause: Under Investigation. (It would be repaired tomorrow) | 3150434 | 1 | 1:47 | Night | Friday | 2015 | 6
2158 | 2015-06-12 02:14 | 2015-06-12 02:14 | 13.8KV MINAS FEEDER #5 | Fair | Dead End Insulator | 41 | Minas fdr #5 Load dropped 130A (227-97A). Not checked yet. | 3150434 | 1 | 2:14 | Night | Friday | 2015 | 6
2159 | 2015-06-12 02:14 | 2015-08-12 11:00 | 13.8KV MINAS FEEDER #5 | Fair | Dead End Insulator | 41 | Checked & found, Recl. 7E-148 (Minas fdr #5) T/R 1x Ctr: 18-19. Patrolled the line & found, @1,@2 broken Dead end Insulators o/p #M5B-09. Cause: Dead end Insulator. | 3150434 | 1 | 2:14 | Night | Friday | 2015 | 6
2160 | 2015-06-12 12:44 | 2015-06-12 12:44 | 13.8KV KETIGUL FEEDER#1 | Heavy Rain | Lightning | 26 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3150433 | 1 | 12:44 | Afternoon | Friday | 2015 | 6
2161 | 2015-06-12 12:44 | 2015-11-12 15:44 | 13.8KV KETIGUL FEEDER#1 | Heavy Rain | Lightning | 26 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 163-164 R/F: 51@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 12:44 | Afternoon | Friday | 2015 | 6
2162 | 2015-06-12 13:14 | 2015-06-12 13:14 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 102 | 13:14 Sintong OCB fdr #1 T/SO. Ctr: 377-378 R/F: 50@2 (In blocked position due to Rig BN #10 activity at well Kerang #13) 15:02 Blocked & closed Sintong OCB fdr #1, Ok. (Still in Block position for Rig Job) Not Patrolled yet. | 3150433 | 1 | 13:14 | Afternoon | Friday | 2015 | 6
2163 | 2015-06-12 13:14 | 2015-07-12 13:30 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 102 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 13:14 | Afternoon | Friday | 2015 | 6
2164 | 2015-06-12 13:14 | 2015-06-12 13:14 | 115KV SINTONG - MENGGALA LINE | Cloudy and Lightning | Lightning | 315 | 13:14 115KV Sintong OCB #23 T/SO. Ctr: 137-138 R/F: 87L & 21P(Zone-1) 115KV Menggala GCB #28 T/SO. Ctr: 338-339 R/F: 87L & 21@1,@2 (Zone-1) (115KV Sintong - Menggala line) Respectively load dropped, due to Voltage dropped at Bangko & Balam area: Sintong fdr #2 load dropped 42A (81-39A). Menggala fdr #2 load dropped 37A (96-59A). Bangko fdr #1 load dropped 150A (275-125A). Bangko fdr #2 load dropped 213A (263-50A). T/O Some WIPs at Bangko-GS & EOR. Bangko fdr #3 load dropped 16A (202-186A). Bangko fdr #4 load dropped 135A (260-125A). Nella fdr #1 load dropped 40A (148-108A). So.Balam fdr #1 load dropped 11A (89-78A). So.Balam fdr #4 load dropped 38A (151-113A). Pinang fdr #1 load dropped 9A (77-68A). Total load dropped at Bangko & Balam area = 691A. 16:08 Patrolled the line, but found nothing. Checked & found, Closing Coil of 115KV Sintong OCB #23 was burnt out. Cause: The line is not patrolled yet. | 3150433 | 1 | 13:14 | Afternoon | Friday | 2015 | 6
2165 | 2015-06-12 13:14 | 2015-08-12 14:45 | 115KV SINTONG - MENGGALA LINE | Cloudy and Lightning | Lightning | 315 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. 14:45 Closed 115KV Sintong OCB #23. (after replacing burnt out closing coil & functioning test the breaker) 14:50 Closed 115KV Menggala GCB #28. (115KV C.Duri - Batang - Sintong / Bangko - Menggala back to loop condition) | 3150433 | 1 | 13:14 | Afternoon | Friday | 2015 | 6
2166 | 2015-06-12 18:55 | 2015-06-12 18:55 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 21 | 18:55 It was reported b/o fuse for Tx at Well Pagar #44. (Ketigul fdr #1) 23:00 Checked & found, @2, @3 b/o 7.8SF fuses for 300Kva Tx at Well Pagar #44. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3150433 | 1 | 18:55 | Afternoon | Friday | 2015 | 6
2167 | 2015-06-12 22:37 | 2015-06-12 22:37 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 0 | Batang OCB fdr #2 T/R 1x. Not checked yet. | 3150433 | 1 | 22:37 | Night | Friday | 2015 | 6
2168 | 2015-06-12 22:37 | 2015-11-12 15:37 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Batang OCB fdr #2 T/R 1x Ctr: 109-110 R/F: 51@1. Patrolled the line & found, @1 broken Pin Insulator o/p #35AF-19. Cause: Lightning. | 3150433 | 1 | 22:37 | Night | Friday | 2015 | 6
2169 | 2015-06-12 23:42 | 2015-06-12 23:42 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | 23:42 Rangau fdr #2 load dropped 82A (87-5A). Not checked yet. | 3150433 | 1 | 23:42 | Night | Friday | 2015 | 6
2170 | 2015-06-12 23:42 | 2015-11-12 15:42 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: 123-124. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 23:42 | Night | Friday | 2015 | 6
2171 | 2015-07-12 13:56 | 2015-07-12 13:56 | BANGKO SUBSTATION | Fair | Relay Failure | 1610 | 13:56 It was no power at Bangko Subtation. (Bangko RTU failed at that time) 14:05 Checked & found, 115Kv Bangko C/S T/O. Ctr: 219 R/F: 51@2. Checked & found, all Bangko breaker fdrs are still in close position. Checked Bangko TX, VR and line, but found nothing. (Normal condition) 14:10 Manual open Bangko fdr #1 and closed at 16:11. Manual open Bangko fdr #2 and closed at 15:03. Manual open Bangko fdr #3 and closed at 15:01. Manual open Bangko fdr #4 and closed at 15:18. Manual open Bangko Capacitor Bank, and closed at 15:29. As per request Bangko-GS. (to anticipate spill at Bangko-GS / Bangko-EOR) 14:39 Manual open Nella fdr #1, and closed at 16:13. Manual open Nella fdr #2, and closed at 15:42. 14:48 Close 115Kv Bangko C/S. (to energize Bangko power Tx) Cause: Relay failure. (Tx Over load due to Improper current relay setting) | 3150433 | 1 | 13:56 | Afternoon | Sunday | 2015 | 7
2172 | 2015-08-12 01:12 | 2015-08-12 01:12 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Unidentified | 162 | 01:12 6DN fdr #2 load dropped 33A (85-52A). 15:35 Checked & found, Recl. 6D-50 (6DN fdr #2) T/SO. Ctr: 27-28. Blocked & closed Recl. 6D-50, Ok. Then released the block. The line is not patrolled yet. | 3150434 | 1 | 1:12 | Night | Wednesday | 2015 | 8
2173 | 2015-08-12 09:58 | 2015-08-12 09:58 | CENTRAL DURI POWER PLANT |  |  | - | 09:58 S/U CGT #5, then on line the Unit at 10:18. |  | 1 | 9:58 | Morning | Wednesday | 2015 | 8
2174 | 2015-08-12 10:00 | 2015-08-12 10:00 | 13.8KV PINANG FEEDER #1 | Fair | Planned Maintenance | 0 | 10:00-17:25 Manually open Pinang OCB fdr #1. Production team replaced 16" Pinang incoming Gas boot at Pinang-GS. PGT team replaced Pin insulator to Post type insulator. Cause: Maintenance Job. (No Prod. loss charge to PGT) | 123 | 1 | 10:00 | Morning | Wednesday | 2015 | 8
2175 | 2015-08-12 10:35 | 2015-08-12 10:35 | MINAS POWER PLANT |  |  | - | 10:35 S/U MGT #7, then on line the Unit at 10:50. |  | 1 | 10:35 | Morning | Wednesday | 2015 | 8
2176 | 2015-08-12 12:47 | 2015-08-12 12:47 | 115KV ROKAN - KETIGUL | Rain and Lightning | Lightning | 622 | 12:47 Rokan 115Kv GCB #11 T/R. 115Kv Ketigul GCB #1 T/SO. 115Kv Ketigul GCB #2 T/SO. (115Kv Rokan - Ketigul line) Menggala 115Kv GCB #28 still open. Sintong 115KV GCB #23 still open (Breaker problem). (Ketigu Subtation and Menggala Substation no power). 14:45 Clsed 115Kv Sintong GCB #23. (after replacing closing coil) 14:50 Closed 115Kv Menggala GCB #28. (Ketigul substation and Menggala Substation energized from Sintong) 14:58 Closed 115Kv Ketigul GCB #1, but failed. 15:00 Closed 115Kv Ketigul GCB #2, but failed. 15:09 Manually open 115KV Rokan GCB #11. 15:10 Closed 115Kv Ketigul GCB #1. 15:12 Closed 115Kv Ketigul GCB #2. 15:11 Closed 115Kv Rokan GCB #11 (C. Duri - Bangko and Rokan back to loop). Cause: Not patrolled yet. | 3150433 | 1 | 12:47 | Afternoon | Wednesday | 2015 | 8
2177 | 2015-08-12 12:47 | 15/12/2015 14:47 | 115KV ROKAN - KETIGUL | Rain and Lightning | Lightning | 622 | Checked & found: 115KV Rokan GCB #11 T/R 2x Ctr: 26-28 R/F: 87L & 21G (Zone-1). 115KV Ketigul GCB #1 T/SO Ctr: 168-169. 115KV Ketigul GCB #3 T/SO Ctr: 191-192. (115KV Rokan - Ketigul line) Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 12:47 | Afternoon | Wednesday | 2015 | 8
2178 | 2015-08-12 16:36 | 2015-08-12 16:36 | MINAS POWER PLANT |  |  | - | 16:36 Off line MGT #11, then S/D the Unit for S/B. (Prior to Major Overhaul program) |  | 1 | 16:36 | Afternoon | Wednesday | 2015 | 8
2179 | 2015-08-12 17:45 | 2015-08-12 17:45 | DURI POWER PLANT |  |  | - | 17:45 Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 17:45 | Afternoon | Wednesday | 2015 | 8
2180 | 2015-08-12 21:48 | 2015-08-12 21:48 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Secondary Cable | 0 | It was reported b/o fuse for Tx o/p #06-Q5-04B. Not checked yet. | 3150433 | 1 | 21:48 | Night | Wednesday | 2015 | 8
2181 | 2015-08-12 21:48 | 2015-09-12 14:00 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Secondary Cable | 0 | 14:00 Checked & found, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #06-Q5-04B. Performed TTR, Megger test the Tx & found, normal. (Good reading) (And also found shortcircuit @2, @3 Scondary cable to ground) (The Tx is not replaced yet) | 3150433 | 1 | 21:48 | Night | Wednesday | 2015 | 8
2182 | 2015-08-12 21:48 | 2015-11-12 10:00 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Secondary Cable | 0 | Energized 112.5Kva Tx o/p #06-Q5-04B & S/U the wells. (After Electrian replacing broken secondary cable) Cause: Secondary cable broken. | 3150433 | 1 | 21:48 | Night | Wednesday | 2015 | 8
2183 | 2015-09-12 07:47 | 2015-09-12 07:47 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 132 | Bangko OCB fdr #4 T/R 1x. Not checked yet. | 3150433 | 1 | 7:47 | Morning | Saturday | 2015 | 9
2184 | 2015-09-12 07:47 | 13/12/2015 10:00 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 132 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99978-99979 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3150433 | 1 | 7:47 | Morning | Saturday | 2015 | 9
2185 | 2015-09-12 11:10 | 2015-09-12 11:10 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 36 | 11:10 It was reported b/o fuse for Tx at Well Bangko #153. (Bangko fdr #4) 15:00 Checked & found, @3 b/o 2.1SF fuse for 100Kva Tx at Well Bangko #153. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3150433 | 1 | 11:10 | Morning | Saturday | 2015 | 9
2186 | 2015-09-12 15:56 | 2015-09-12 15:56 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 63 | Minas fdr #6 load dropped 117A (263-146A). Not checked yet. | 3150434 | 1 | 15:56 | Afternoon | Saturday | 2015 | 9
2187 | 2015-09-12 15:56 | 2015-11-12 11:00 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 63 | Checked & found, Recl. 7E-67A (Minas fdr #6) T/R 1x Ctr: 48-49. Patrolled the line, but found nothing. Also found, Recl. 6E-23A (Minas fdr #6) T/R 1x Ctr: 15-16. Patrolled the line & found, @3 broken L/A o/p #6E-51. Cause: Lightning. | 3150434 | 1 | 15:56 | Afternoon | Saturday | 2015 | 9
2188 | 2015-09-12 16:04 | 2015-09-12 16:04 | 13.8KV 8D FEEDER #9 | Rain and Lightning | Lightning | 122 | 16:04 8D OCB fdr #9 T/R 1x. 16:10 8D OCB fdr #9 T/R 1x again. 8D fdr #10 load dropped 140A (166-24A). 8D fdr #11 load dropped 220A (293-73A). Not checked yet. | 3150434 | 1 | 16:04 | Afternoon | Saturday | 2015 | 9
2189 | 2015-09-12 16:04 | 2015-11-12 11:04 | 13.8KV 8D FEEDER #9 | Rain and Lightning | Lightning | 122 | Checked & found, 8D OCB fdr #9 T/R 2x Ctr: 97-99 R/F: 50@1,@2,@3. Patrolled the line & found, @2 broken LBS Bushing Insulator o/p #0703. Cause: Lightning. Checked Recl. 7E-21 (8D fdr #10) & found normal. Ctr: 30. (Did not change) Patrolled the line, but found nothing. Checked All Reclosers at downstream of 8D fdr #11 & found, normal. (Ctr: Did not change) Patrolled the line, bt found nothing. Cause: Suspected some wells were down due to voltage dip when 8D OCB fdr #9 T/R 2x. Prod. loss reported by GS-1 & GS-2: 8D fdr #10 = 33 Bbls / 14 Wells. 8D fdr #11 = 89 Bbls / 26 Wells. Grand Total Prod. loss = 122 Bbls / 40 Wells. | 3150434 | 1 | 16:04 | Afternoon | Saturday | 2015 | 9
2190 | 2015-09-12 16:10 | 2015-09-12 16:10 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 0 | 8D OCB fdr #7 T/R 1x. Not checked yet. | 3150434 | 1 | 16:10 | Afternoon | Saturday | 2015 | 9
2191 | 2015-09-12 16:10 | 2015-11-12 11:10 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 0 | Checked & found, 8D OCB fdr #7 T/R 1x Ctr: 629-630 R/F: 51N & 50@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150434 | 1 | 16:10 | Afternoon | Saturday | 2015 | 9
2192 | 2015-09-12 16:10 | 2015-09-12 16:10 | 13.8KV 8D FEEDER #8 | Rain and Lightning | Lightning | 0 | 8D OCB fdr #8 T/R 1x. Not checked yet. | 3150434 | 1 | 16:10 | Afternoon | Saturday | 2015 | 9
2193 | 2015-09-12 16:10 | 2015-11-12 11:10 | 13.8KV 8D FEEDER #8 | Rain and Lightning | Lightning | 0 | Checked & found, 8D OCB fdr #8 T/R 1x Ctr: 423-424 R/F: 50@1,@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150434 | 1 | 16:10 | Afternoon | Saturday | 2015 | 9
2194 | 2015-09-12 16:10 | 2015-09-12 16:10 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 16 | 8C fdr #3 load dropped 148A (215-67A). Not checked yet. | 3150434 | 1 | 16:10 | Afternoon | Saturday | 2015 | 9
2195 | 2015-09-12 16:10 | 2015-11-12 11:15 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 16 | Checked & found, Recl. 8D-18A (8C fdr #3) T/R 1x Ctr: 23-24. Patrolled the line & found, @3 broken Fuse Holder for Tx on TP of Well #8D-54. Cause: Lightning. | 3150434 | 1 | 16:10 | Afternoon | Saturday | 2015 | 9
2196 | 2015-09-12 16:18 | 2015-09-12 16:18 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Minas ACB #21 (44KV Minas - Rumbai line) T/R 1x. Not checked yet. | 3150434 | 1 | 16:18 | Afternoon | Saturday | 2015 | 9
2197 | 2015-09-12 16:18 | 2015-10-12 15:10 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Checked & found, Minas ACB #21 (44KV Minas - Rumbai line) T/R 1x Ctr: 70-71 R/F: 51G(@1,@2). Patrolled the line & found, @1 broken Dead end Insulator o/p #MR-21. Cause: Lightning. | 3150434 | 1 | 16:18 | Afternoon | Saturday | 2015 | 9
2198 | 2015-09-12 18:00 | 2015-09-12 18:00 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 48 | 18:00 It was reported b/o fuse for Tx o/p #03-3-28. Not checked yet. | 3150433 | 1 | 18:00 | Afternoon | Saturday | 2015 | 9
2199 | 2015-09-12 18:00 | 2015-10-12 10:25 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 48 | 10:25 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx o/p #03-03-28. Replaced the b/o fuses with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3150433 | 1 | 18:00 | Afternoon | Saturday | 2015 | 9
2200 | 2015-09-12 18:42 | 2015-09-12 18:42 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified (Fuse) | 3 | 18:42 It was reported b/o fuse for Tx at Well Kerang #17. 21:00 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Kerang #17. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3150433 | 1 | 18:42 | Afternoon | Saturday | 2015 | 9
2201 | 2015-09-12 23:00 | 2015-09-12 23:00 | 13.8KV SINTONG FEEDER #1 | Fair | Transformer Failure | 48 | Sintong fdr #1 load dropped 118A (225-107A). Not checked yet. | 3150433 | 1 | 23:00 | Night | Saturday | 2015 | 9
2202 | 2015-09-12 23:00 | 2015-10-12 11:00 | 13.8KV SINTONG FEEDER #1 | Fair | Transformer Failure | 48 | Checked & found, Recl. 19AN-04 (Sintong fdr #1) T/R 3x Ctr: 316-319 R/F: 51N. Patrolled the line & found, 300Kva Tx low megger reading at Well MENO #15. Cause: Transformer failure. | 3150433 | 1 | 23:00 | Night | Saturday | 2015 | 9
2203 | 2015-10-12 00:05 | 2015-10-12 00:05 | 13.8KV SINTONG FEEDER #1 | Fair | Transformer Failure | 170 | 00:05 It was reported b/o fuse for Tx at Well Menggala north #15. 09:45 Checked & found, @1, @2, @3 b/o 7.8SF fuses for 300Kva Tx at Well Menggala north #15. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx failure. (Low megger reading) (The Tx failure is not replaced yet) | 3150433 | 1 | 0:05 | Night | Monday | 2015 | 10
2204 | 2015-10-12 00:05 | 2015-12-12 14:00 | 13.8KV SINTONG FEEDER #1 | Fair | Transformer Failure | 170 | Replaced 300Kva Tx failure with 150Kva Tx & energized the Tx at Well Menggala North #15. Cause: Tx failure. (Low megger reading) | 3150433 | 1 | 0:05 | Night | Monday | 2015 | 10
2205 | 2015-10-12 14:32 | 2015-10-12 14:32 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 80 | Bekasap Main fdr #6 load dropped 82A (84-2A). (Suspected Bekasap Main OCB fdr #6 T/R) Bekasap Main fdr #5 load dropped 284A (290-6A). T/O WIP at Bekasap-GS. Bekasap Main fdr #3 load dropped 109A (233-124A). Not checked yet. Prod. loss reported by EC: Prod. loss = 33 Bbls / 29 Wells. (Bekasap fdr #6) Prod. loss = 47 Bbls / 48 Wells. (Bekasap fdr #3) Total Prod. loss = 80 Bbls / 77 Wells. | 3150433 | 1 | 14:32 | Afternoon | Monday | 2015 | 10
2206 | 2015-10-12 14:32 | 16/12/2015 15:32 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 80 | Checked & found, Bekasap Main VCB fdr #6 T/R 1x Ctr: 332-333 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. Checked all Recloser at down stream of Bekasap Main fdr #3, but found normal. Counter did not change & Patrolled the line but, found nothing. Cause: Suspected some load were off, due to voltage Dip. (When Bekasap Main VCB fdr #6 T/R) | 3150433 | 1 | 14:32 | Afternoon | Monday | 2015 | 10
2207 | 2015-10-12 14:50 | 2015-10-12 14:50 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Tree | 21 | So.Bekasap fdr #1 load dropped 174A (186-12A). Not checked yet. | 3150433 | 1 | 14:50 | Afternoon | Monday | 2015 | 10
2208 | 2015-10-12 14:50 | 2015-10-12 14:50 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Tree | 21 | Checked & found, Recl. 36BI-04 (So.Bekasap fdr #1) T/R 1x Ctr: 731-732. Patrolled the line, but founfd nothing. Also found, Recl. 34BI-18 (So.Bekasap fdr #1) T/R 1x Ctr: 149-150. Patrolled the line & found, danger high Trees touching poer line near Well Pudu #11. Cause: Tree. | 3150433 | 1 | 14:50 | Afternoon | Monday | 2015 | 10
2209 | 2015-10-12 16:04 | 2015-10-12 16:04 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain | Lightning | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3150433 | 1 | 16:04 | Afternoon | Monday | 2015 | 10
2210 | 2015-10-12 16:04 | 16/12/2015 15:04 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain | Lightning | 0 | Checked & found, Duri Community VCB fdr #1 T/R 1x Ctr: 77-78 R/F: Not appear. Patrolled the line & found, @2 broken Dead end Insulator o/p #2DF-07. Cause: Lightning. | 3150433 | 1 | 16:04 | Afternoon | Monday | 2015 | 10
2211 | 2015-10-12 19:15 | 2015-10-12 19:15 | DURI POWER PLANT |  |  | - | 19:15 S/U DGT #7, then On Line the Unit at 19:40. |  | 1 | 19:15 | Night | Monday | 2015 | 10
2212 | 2015-10-12 19:54 | 2015-10-12 19:54 | CENTRAL DURI POWER PLANT |  |  | - | 19:54 Off Line CGT #5, then S/D the Unit at 19:55. (For S/B-Prior to reparing the Stack Diverter on 40Degree of HRSG-5) |  | 1 | 19:54 | Night | Monday | 2015 | 10
2213 | 2015-10-12 19:57 | 2015-10-12 19:57 | 13.8KV BANGKO FEEDER #2 | Fair | Unidentified | 0 | Bangko OCB fdr #2 T/R 1x. Bangko fdr #3 load dropped 157A (222-65A). (T/O WIP at Bangko-GS) Bangko GFPC T/R 1x. (Ground fault alarm on Bangko fdr #2 and Bangko fdr #4) Not checked yet. | 3150433 | 1 | 19:57 | Night | Monday | 2015 | 10
2214 | 2015-10-12 19:57 | 2015-12-12 11:57 | 13.8KV BANGKO FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Bangko OCB fdr #2 T/R 1x Ctr: 99952-99953 R/F: Not reported yet. Patrolled the line, but found nothing. Cause: Unidentified. | 3150433 | 1 | 19:57 | Night | Monday | 2015 | 10
2215 | 2015-10-12 23:38 | 2015-10-12 23:38 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 16 | Bekasap Main fdr #2 Load dropped 122A (212-90A). Bekasap Main GFPC T/R 1x. Not checked yet. | 3150433 | 1 | 23:38 | Night | Monday | 2015 | 10
2216 | 2015-10-12 23:38 | 22/12/2015 10:38 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 16 | Checked & found, Recl. 35BC-14 (Pematang fdr #1) T/R 1x Ctr: 36-37. Patrolled the line, but found nothing. Cause: Suspected by Lightning. Note: Since 07-Dec-2015. Pematang fdr #1 & fdr #2 are transferred to Bekasap Main fdr #2. (S/D Pematang power Tx for general servicing) | 3150433 | 1 | 23:38 | Night | Monday | 2015 | 10
2217 | 2015-11-12 00:23 | 2015-11-12 00:23 | 115KV KETIGUL - MENGGALA | Rain and Lightning | Lightning | 0 | 00:23 115KV Menggala GCB #29 T/O. 115KV Ketigul OCB #1 T/R 1x. 115KV Ketigul GCB #3 T/O. (115KV Menggala - Ketigul line) 00:52 Manually closed 115KV Menggala GCB #29, but failed. (from DSC) 00:58 Manually closed 115KV Ketigul GCB #3, Ok. (from DSC) 02:17 Checked & found, 115KV Menggala GCB #29 T/O. Ctr: 154-155 R/F: 87L-@C. Manually closed 115KV Menggala GCB #29, but failed. (from spot) 03:14 Manually opened 115KV Ketigul OCB #1. 03:15 Manually opened 115KV Ketigul GCB #3. 03:16 Manually Closed 115KV Menggala GCB #29, Ok. 03:18 Manually Closed 115KV Ketigul OCB #1, Ok. 03:20 Manually Closed 115KV Ketigul GCB #3, Ok. (115KV Menggala-Ketigul line back to loop) Cause: Not patrolled yet. | 3150433 | 1 | 0:23 | Night | Thursday | 2015 | 11
2218 | 2015-11-12 00:23 | 16/12/2015 15:23 | 115KV KETIGUL - MENGGALA | Rain and Lightning | Lightning | 0 | Checked & found: 115KV Menggala GCB #29 T/O. Ctr: 154-155 R/F: 87L-@C. 115KV Ketigul OCB #1 T/R 2x Ctr: 192-194. 115KV Ketigul GCB #3 T/R 2x Ctr: 153-155 R/F: 87L-@3, 21G-@3 (Zone-1) & 67N (Inst) (115KV Menggala - Ketigul line) Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 0:23 | Night | Thursday | 2015 | 11
2219 | 2015-11-12 01:15 | 2015-11-12 01:15 | DURI POWER PLANT |  | Under investigation | - | 01:15 DGT #7 Generator Breaker Tripped, By Alarm: Generator Breaker Trip. Frequency system dropped to 59.85Hz. (No load shedding) 01:20 Manually Closed Generator Breaker DGT #7. (Back on line to the system) Cause: Under Investigation. |  | 1 | 1:15 | Night | Thursday | 2015 | 11
2220 | 2015-11-12 03:18 | 2015-11-12 03:18 | 13.8KV SINTONG FEEDER #1 | Fair | Dead End Insulator | 0 | Sintong fdr #1 Load dropped 120A (222-102A). Sintong fdr #2 Load dropped 20A (80-60A). Not checked yet. | 3150433 | 1 | 3:18 | Night | Thursday | 2015 | 11
2221 | 2015-11-12 03:18 | 15/12/2015 07:18 | 13.8KV SINTONG FEEDER #1 | Fair | Dead End Insulator | 0 | Checked & found, Recl. 19AN-04 (Sintong fdr #1) T/R 3x Ctr: 316-319. Patrolled the line & found, @1 broken Dead end Insulator o/p #19AJ-07. Cause: Dead end Insulator. | 3150433 | 1 | 3:18 | Night | Thursday | 2015 | 11
2222 | 2015-11-12 11:37 | 2015-11-12 11:37 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 52 | Bekasap fdr #2 load drop 158A (226-68A). Not checked yet. | 3150433 | 1 | 11:37 | Morning | Thursday | 2015 | 11
2223 | 2015-11-12 11:37 | 23/12/2015 08:37 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 52 | Checked & found, Recl. 35BC-14 (Pematang fdr #1) T/R 1x Ctr: 37-38. Patrolled the line & found, @1 broken Pin Insulator o/p #35BD-36. Cause: Lightning. Note: Since 07-Dec-2015. Pematang fdr #1 & fdr #2 are transferred to Bekasap Main fdr #2. (S/D Pematang power Tx for general servicing) | 3150433 | 1 | 11:37 | Morning | Thursday | 2015 | 11
2224 | 2015-11-12 12:16 | 2015-11-12 12:16 | 13.8KV KETIGUL FEEDER#2 | Drizzle | Animal | 318 | 12:16 Ketigul VCB #2 T/O. (in block position for Rig BMS#09 at Well Pagar #01) 13:40 Checked & found, Ketigul VCB #2 T/O. Ctr: 182-183 R/F: 51N. 13:45 Blocked & closed Ketigul VCB #2, but T/O again. 14:00 Patrolled line & found, a Dead Monkey at @2 TP of Well Pagar #01. 17:26 Blocked & closed Ketigul VCB #2, Ok. Ketigul VCB fdr #2 is still in block for Rig Job. (After removing a Dead monkey above) Cause: Animal. | 3150433 | 1 | 12:16 | Afternoon | Thursday | 2015 | 11
2225 | 2015-11-12 17:28 | 2015-11-12 17:28 | MINAS POWER PLANT |  |  | - | 17:28 S/U MGT#5 and then Online at 17:40. |  | 1 | 17:28 | Afternoon | Thursday | 2015 | 11
2226 | 2015-11-12 21:25 | 2015-11-12 21:25 | MINAS POWER PLANT |  |  | - | 21:25 MGT #1 Off Line then S/D at 21:26 for S/B, to Repair Bypass valve and VPR off Atomizing air. | 123 | 1 | 21:25 | Night | Thursday | 2015 | 11
2227 | 2015-12-12 00:03 | 2015-12-12 00:03 | 13.8KV S. BALAM FEEDER #1 | Fair | Others | 20 | 00:03 It was reported b/o fuse for Tx at Well So.Balam #213. 10:15 Checked & found, @1,@2,@3 b/o 2.1SF fuses for 100Kva Tx at Well So.Balam #213. Performed Test TTR, Megger the Tx & found, normal. (good reading) Replaced b/o fuse above with same size then energized the Tx. Cause: Other. (Vandalism) | 3150433 | 1 | 0:03 | Night | Saturday | 2015 | 12
2228 | 2015-12-12 08:14 | 2015-12-12 08:14 | CENTRAL DURI POWER PLANT |  |  | - | 08:14 S/U CGT #5, then online the Unit at 08:30. (Running without HRSG) |  | 1 | 8:14 | Morning | Saturday | 2015 | 12
2229 | 2015-12-12 09:10 | 2015-12-12 09:10 | DURI POWER PLANT |  |  | - | 09:10 Off line DGT #7, then S/D the Unit for S/B at 09:11. |  | 1 | 9:10 | Morning | Saturday | 2015 | 12
2230 | 2015-12-12 11:39 | 2015-12-12 11:39 | 13.8KV 5B FEEDER #2 | Cloudy and Lightning | Lightning | 36 | 5B OCB fdr #2 T/R 1x. Not checked yet. | 3150434 | 1 | 11:39 | Morning | Saturday | 2015 | 12
2231 | 2015-12-12 11:39 | 14/12/2015 10:39 | 13.8KV 5B FEEDER #2 | Cloudy and Lightning | Lightning | 36 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 332-333 R/F: 51N. Patrolled the line & found: -@3 Broken Dead end Insulator o/p #4C-59. -@1 Flashed over Dead end Insulator o/p #4C-59. Cause: Lightning. | 3150434 | 1 | 11:39 | Morning | Saturday | 2015 | 12
2232 | 2015-12-12 13:47 | 2015-12-12 13:47 | 13.8KV CENTRAL DURI FEEDER #1 | Rain | Tree | 387 | 13:47 C.Duri fdr #1 load drop 144A (216-72A). 13:58 It was reported fallen tree onto 13.8kv Conductor, Nearest pole #08-L7-21. 15:17 Checked & found, fallen tree on conductor near pole #08-L7-21. (D/S of Recl. 08-L7-38) (Found Recl. 08-L7-38 did not operate) 15:26 Manually Opened Recl. 08-L7-38 and the Visual opening. (To isolate fallen tree from the conductor) 15:36 Blocked & closed Recl. 08-L7-38, but failed. (found No power) Checked & found, Recl. 08-L7-38, Recl. 09-L7-01, Recl. 09-L7-03 are no power. Checked Recl. SBB-07 Upstream & found, T/LO. Ctr: 522-525. 16:02 Blocked & closed Recl. SBB-07, Ok. Then released the Block. 16:52 Closed Recl. 08-L7-38, Ok. (leave the Recl. 08-L7-38 is unplug position) Cause: Tree. | 3150433 | 1 | 13:47 | Afternoon | Saturday | 2015 | 12
2233 | 2015-12-13 12:52 | 2015-12-13 12:52 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 31 | 12:52 It was reported no power at Well Sobek #05. 14:25 Checked & found, Recl. 37BG-48 (So.Bekasap fdr #1) T/LO. Ctr: 33. (Not change) (Only Well Sobek #05 active at d/s the Recl. 37BG-48) Patrolled the line, but found nothing. 16:18 Blocked & closed Recl. 37BG-48, Ok. Then released the block. Cause: Unidentified. | 3150433 | 1 | 12:52 | Afternoon | Sunday | 2015 | 12
2234 | 2015-12-13 18:36 | 2015-12-13 18:36 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 154 | 18:36 Ketigul VCB fdr #2 T/O. (In blocked position for Rig Job at Well Pagar #01) 18:46 Manually Blocked & closed Ketigul VCB fdr #2, but failed. (from DSC) 21:09 Checked & found Ketigul VCB fdr #2 T/O. Ctr: 183-184 R/F: 51@2. Manually Blocked & closed Ketigul VCB fdr #2, Ok. (from Substation) (The breaker is still in block for Rig Job) The line is not patrolled yet. | 3150433 | 1 | 18:36 | Afternoon | Sunday | 2015 | 12
2235 | 2015-12-13 18:36 | 2015-12-16 15:36 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 154 | Patrolled the line & found: -@2 Broken Dead end Insulator on TP of Well Pager #20. -@2 a Dead Monkey touching conductor on TP of Well Pager #08. Cause: Animal. (Monkey) | 3150433 | 1 | 18:36 | Afternoon | Sunday | 2015 | 12
2236 | 2015-12-14 08:25 | 2015-12-14 08:25 | 13.8KV BEKASAP FEEDER #2 | Fair | Theft | 16 | 08:25 It was reported @1,@2,@3 opened FCO by unknown person at Well Bekasap #164. 09:45 Checked & found, 150Kva Tx broken by vandalism. Cause: Theft. (Vandalism) | 3150433 | 1 | 8:25 | Morning | Monday | 2015 | 12
2237 | 2015-12-14 08:25 | 2015-12-15 15:05 | 13.8KV BEKASAP FEEDER #2 | Fair | Theft | 16 | Replaced 150KVA Tx with the same size then energized the Tx at Well Bekasap #164. Cause: Vandalism. | 3150433 | 1 | 8:25 | Morning | Monday | 2015 | 12
2238 | 2015-12-14 09:15 | 2015-12-14 09:15 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 09:15 It was reported b/o fuse for Tx o/p #07-V5-07. 10:50 Checked & found, @3 b/o 3.1SF fuse for 112.5kva Tx o/p #07-V5-07. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (fuse). | 3150433 | 1 | 9:15 | Morning | Monday | 2015 | 12
2239 | 2015-12-14 11:00 | 2015-12-14 11:00 | 13.8KV BEKASAP FEEDER #1 | Fair | Transformer Failure | 52 | 11:00 It was reported b/o fuse for Tx at Well Bekasap #63. Checked & found, @1 b/o 3.5SF fuse for 150kva Tx at Well Bekasap #63. Performed TTR, Megger test the Tx & found, unbalance TTR and zero megger reading. Cause: Transformer failure. (The Tx failure is not replaced yet) | 3150433 | 1 | 11:00 | Morning | Monday | 2015 | 12
2240 | 2015-12-14 11:00 | 2015-12-15 16:35 | 13.8KV BEKASAP FEEDER #1 | Fair | Transformer Failure | 52 | 16:35 Replaced 150Kva Tx failure with the same size then energized the Tx at Well Bekasap #63. 18:38 It was reported unbalance voltage of Tx at Well Bekasap #63. Checked the Tx & found, unbalance TTR. Cause: Transformer Failure. (The Tx failure is not replaced yet, due to No Standby 150Kva Tx at TDO) | 3150433 | 1 | 11:00 | Morning | Monday | 2015 | 12
2241 | 2015-12-14 11:00 | 2015-12-16 15:35 | 13.8KV BEKASAP FEEDER #1 | Fair | Transformer Failure | 52 | Replaced 150Kva Tx failure with the same size & energized the Tx at Well Bekasap #63. Cause: Tx failure. (Low megger reading) | 3150433 | 1 | 11:00 | Morning | Monday | 2015 | 12
2242 | 2015-12-14 14:42 | 2015-12-14 14:42 | 13.8KV DURI FIELD FEEDER #4 | Rain | Recloser - Control Recloser | 21 | 14:42 Duri Field fdr #4 load dropped 8A (145-137A). 15:17 It was reported no power at Area-7, Road-T3. 16:10 Checked & found, Recl. 07-T3-02 (Duri Field fdr #4) T/SO. Ctr: 508-509. 16:30 Patrolled the line & found nothing. 16:35 Blocked & closed Recl. 07-T3-02, but failed. Checked & found, b/o closing fuse for Recl. Control. 16:43 Blocked & closed Recl. 07-T3-02, Ok. Then released the block. (After replacing b/o closing fuse above) 17:04 Duri Field fdr #4 load dropped again 8A (145-137A). 17:30 Checked & found, Recl. 07-T3-02 T/SO again. Ctr: 513-514. Re-patrolled the line & found nothing. (The weather was rain) 18:00 Blocked & closed Recl. 07-T3-02, but failed. Checked & found, DC voltage battery control of the Recloser problem. 18:11 Blocked & closed Recl. 07-T3-02, Ok. Then released the block. (Then unplugging Recloser control cable) Cause: Recloser Control Problem. | 3150433 | 1 | 14:42 | Afternoon | Monday | 2015 | 12
2243 | 2015-12-15 13:53 | 2015-12-15 13:53 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Animal | 0 | 13:53 So.Balam fdr #4 load dropped 14A (149-135A). So.Balam GFPC T/R 1x. Ground fault alarm on So.Balam fdr #4. 16:03 So.Balam GFPC T/R 1x again. Ground fault alarm on So.Balam fdr #1. (No load dropped at any feeders) Not checked yet. | 3150433 | 1 | 13:53 | Afternoon | Tuesday | 2015 | 12
2244 | 2015-12-15 13:53 | 2015-12-17 14:53 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Animal | 0 | Checked & found, Recl. 16AB-03 (So.Balam fdr #4) T/R 1x Ctr: 114-115. Also found, So.Balam GFPC T/R 2x Ctr: 194-196. Patrolled So.Balam fdr #4 line & found, a Dead Bird under TP of Well So.Balam #278. Cause: Animal. (Bird) | 3150433 | 1 | 13:53 | Afternoon | Tuesday | 2015 | 12
2245 | 2015-12-15 16:47 | 2015-12-15 16:47 | 13.8KV BANGKO GFPC | Cloudy and Lightning | Lightning | 0 | Bangko GFPC T/R 1x. Ground fault alarm on Bangko fdr #3 & #4. (No load dropped at any feeders) Not checked yet. | 3150433 | 1 | 16:47 | Afternoon | Tuesday | 2015 | 12
2246 | 2015-12-15 16:47 | 2015-12-17 14:47 | 13.8KV BANGKO GFPC | Cloudy and Lightning | Lightning | 0 | Checked & found, Bangko GFPC T/R 1x Ctr: 482-483 R/F: 51N/G. Patrolled Bangko fdr #3 & found, b/o fuse for 3x50Kva Tx at Bangko Camp. Cause: Lightning. | 3150433 | 1 | 16:47 | Afternoon | Tuesday | 2015 | 12
2247 | 2015-12-16 10:40 | 2015-12-16 10:40 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified (Fuse) | 31 | 10:40 It was reported spark on fuse holder for Tx at Well KB #132. 15:30 Checked & found, @1 b/o 2.1SF fuse for 100Kva Tx at Well KB #132. Replaced the b/o fuse with same size, then energized the Tx. 15:35 Found @1 b/o fuse again while starting the Pump. Not checked & replaced yet. | 3150434 | 1 | 10:40 | Morning | Wednesday | 2015 | 12
2248 | 2015-12-16 10:40 | 2015-12-17 11:22 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified (Fuse) | 31 | 11:22 Replaced the b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3150434 | 1 | 10:40 | Morning | Wednesday | 2015 | 12
2249 | 2015-12-16 14:15 | 2015-12-16 14:15 | 13.8KV BEKASAP FEEDER #6 | Cloudy | Powerline - Conductor | 529 | 14:15 Bekasap VCB fdr #6 T/LO. Ctr: 333-337 R/F: 51N. 14:23 It was reported broken conductor o/p near Well Bekasap #22. 15:18 Checked & found, @3 broken conductor between poles #37BE-05 and #37BE-06. (on HLC connection) 16:19 Racked out Bekasap VCB fdr #6. 18:44 Repaired broken conductor above. 18:47 Racked in Bekasap VCB fdr #6. 18:50 Blocked & closed Bekasap VCB fdr #6 from DSC, but failed. 19:03 Blocked & closed Bekasap VCB fdr #6 from local, Ok. Then released the block. Cause: Broken Conductor. | 3150433 | 1 | 14:15 | Afternoon | Wednesday | 2015 | 12
2250 | 2015-12-16 14:16 | 2015-12-16 14:16 | 13.8KV BANGKO FEEDER #1 | Fair | Unidentified (Fuse) | 37 | 14:16 It was reported b/o fuse for Tx at Well Bangko #233. (Bangko fdr #1) 16:35 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Bangko #233. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3150433 | 1 | 14:16 | Afternoon | Wednesday | 2015 | 12
2251 | 2015-12-16 14:34 | 2015-12-16 14:34 | 13.8KV BANGKO FEEDER #3 | Fair | Main breaker | - | 14:34 It was reported b/o fuse for Tx for Tool House office at Bangko Camp. Checked & found, @3 b/o 3.5SF fuse for 3x50Kva Tx, also found, spark at Main breaker. Replaced b/o fuse above with the same size then energized the Tx. (After Electrician replaced Main Breaker) Cause: Main Breaker. | 3150433 | 1 | 14:34 | Afternoon | Wednesday | 2015 | 12
2252 | 2015-12-16 15:29 | 2015-12-16 15:29 | 13.8KV 4D FEEDER #5 | Fair | Transformer Failure | 19 | 15:29 It was reported b/o fuse for Tx at Well #4D-57. (4D fdr #5) 16:30 Checked & found, @1, @3 b/o 7.0SF fuses for 225Kva Tx at Well #4D-57. Performed TTR, Megger Test the Tx & found, Zero Megger Tx. Cause: Transformer Failure. (The Tx is not replaced yet) | 3150434 | 1 | 15:29 | Afternoon | Wednesday | 2015 | 12
2253 | 2015-12-16 15:29 | 2015-12-17 11:38 | 13.8KV 4D FEEDER #5 | Fair | Transformer Failure | 19 | 11:38 Replaced the failure 225 KVA Tx with same size at Well #4D-57 & energized the Tx. Cause: Transformer failure. | 3150434 | 1 | 15:29 | Afternoon | Wednesday | 2015 | 12
2254 | 2015-12-16 15:37 | 2015-12-16 15:37 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 21 | 15:37 It was reported b/o fuse for Tx at Well So.Menggala #01. (Sintong fdr #1) 17:23 Checked & found, @2, @3 b/o 3.5SF fuse for 150Kva Tx at Well So.Menggala #01. Replaced b/o fuse above with the same size then energized the Tx. Cause: Anima (Monkey). 18:27 It was reported b/o fuses at well So.Menggala #01 again. 21:00 Checked & found, @2 b/o 3.5SF fuse for 150Kva Tx. Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced the b/o fuse with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3150433 | 1 | 15:37 | Afternoon | Wednesday | 2015 | 12
2255 | 2015-12-16 21:00 | 2015-12-16 21:00 | 13.8KV 5B FEEDER #2 | Fair | Unidentified (Fuse) | 18 | 21:00 It was reported b/o fuse for Tx at Well #4D-81E. (5B fdr #2) Not checked yet. | 3150434 | 1 | 21:00 | Night | Wednesday | 2015 | 12
2256 | 2015-12-16 21:00 | 2015-12-17 10:47 | 13.8KV 5B FEEDER #2 | Fair | Unidentified (Fuse) | 18 | 10:47 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well #4D-81E. Performed TTR, Megger test the Tx & found, good reading. Replaced b/o fuse with the same size & Energized the Tx. Cause: Unidentified (fuse). | 3150434 | 1 | 21:00 | Night | Wednesday | 2015 | 12
2257 | 2015-12-17 15:36 | 2015-12-17 15:36 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 31 | Pinang OCB fdr #1 T/R 1x. Not checked yet. | 3150433 | 1 | 15:36 | Afternoon | Thursday | 2015 | 12
2258 | 2015-12-17 15:36 | 2015-12-18 16:04 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 31 | Checked & found, Pinang OCB fdr #1 T/R 1x Ctr: 365-366 R/F: 51N. Patrolled the line & found, @2 broken L/A o/p #11C-03. Cause: Lightning. | 3150433 | 1 | 15:36 | Afternoon | Thursday | 2015 | 12
2259 | 2015-12-17 17:50 | 2015-12-17 17:50 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 6 | 17:50 It was reported b/o fuse for Tx at Well Benar #48. 20:11 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Benar #48. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3150433 | 1 | 17:50 | Afternoon | Thursday | 2015 | 12
2260 | 2015-12-18 11:43 | 2015-12-18 11:43 | 13.8KV SINTONG FEEDER #2 | Cloudy | Others | 171 | 11:43 Sintong fdr #2 load dropped 72A (80-8A). Sintong fdr #1 Load dropped 152A (223-71A). Sintong GFPC T/R 1x. (Fault alarm on Sintong fdr #2) 13:05 Checked & found, Recl. 28AF-17 (Sintong fdr #2) T/LO. Ctr: 424-428. 13:33 Patrolled the line & found, a piece of wood hung on @1 & @2 conductors. (between poles #28AL-21 and 28AL-22) Then takingdown its wood from the Powerline. 13:51 Blocked & closed Recl. 28AF-17, Ok. Then released the block. Cause: Others. (a piece of wood thrown by someone to power line) Prod. loss reported by Bangko-GS: Prod. loss = 125 Bbls / 24 Wells. (Sintong fdr #2 / Recl. 28AF-17 T/LO) Prod. loss = 114 Bbls / 23 Wells. (Sintong fdr #1 dropped 152A, due to voltage dip) Grand Total Prod. loss = 239 Bbls / 47 Wells. | 3150433 | 1 | 11:43 | Morning | Friday | 2015 | 12
2261 | 2015-12-19 07:53 | 2015-12-19 07:53 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 1 | 07:53 It was reported b/o fuse for Tx o/p #08-M3-07. 10:53 Checked & found, @2 b/o 2.1SF fuse for 112.5Kva Tx o/p #08-M3-07. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3150433 | 1 | 7:53 | Morning | Saturday | 2015 | 12
2262 | 2015-12-19 17:15 | 2015-12-19 17:15 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Broken Fuse Cut Out | - | 17:15 It was reported b/o fuse for Tx at CGS-1 o/p #01-5-19. 19:00 Checked & found, @2 broken FCO for 112.5kva Tx o/p #01-5-19. (C.Duri fdr #6) 20:21 Blocked C.Duri fdr #6, to replacing broken FCO above. 21:05 Energized the Tx and released block to normal. Cause: Broken Fuse Cut Out. | 3150433 | 1 | 17:15 | Afternoon | Saturday | 2015 | 12
2263 | 2015-12-19 18:10 | 2015-12-19 18:10 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 33 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3150433 | 1 | 18:10 | Afternoon | Saturday | 2015 | 12
2264 | 2015-12-19 18:10 | 2015-12-23 08:57 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 33 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 164-165 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3150433 | 1 | 18:10 | Afternoon | Saturday | 2015 | 12
2265 | 2015-12-19 20:29 | 2015-12-19 20:29 | 13.8KV MENGGALA FEEDER #2 | Rain and Lightning | Lightning | 0 | Menggala fdr #2 load dropped 42A (96-54A). Menggala GFPC in block position. Not checked yet. | 3150433 | 1 | 20:29 | Night | Saturday | 2015 | 12
2266 | 2015-12-19 20:29 | 2015-12-21 07:29 | 13.8KV MENGGALA FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 22AL-21 (Sintong fdr #2) T/R 1x Ctr: 112-113. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 20:29 | Night | Saturday | 2015 | 12
2267 | 2015-12-19 20:54 | 2015-12-19 20:54 | 13.8KV PETANI FEEDER #2 | Rain | Lightning | 30 | Petani OCB fdr #2 T/R 1x. Petani fdr #1 dropped 132A (189-57A). Not checked yet. | 3150433 | 1 | 20:54 | Night | Saturday | 2015 | 12
2268 | 2015-12-19 20:54 | 2015-12-23 08:54 | 13.8KV PETANI FEEDER #2 | Rain | Lightning | 30 | Checked & found, Petani OCB fdr #2 T/R 1x Ctr: 175-176 R/F: 51@2. Patrolled the line & found, @2 F/O Dead end Insulator o/p #NN. (Near Well Petani #35) Cause: Lightning. | 3150433 | 1 | 20:54 | Night | Saturday | 2015 | 12
2269 | 2015-12-19 21:56 | 2015-12-19 21:56 | 13.8KV MENGGALA FEEDER #2 | Fair | Unidentified (Fuse) | 1 | 21:56 It was reported b/o fuse for Tx at Well Sikladi #18. (Menggala fdr #2) 23:57 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Sikladi #18. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3150433 | 1 | 21:56 | Night | Saturday | 2015 | 12
2270 | 2015-12-20 10:30 | 2015-12-20 10:30 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 0 | 10:30-11:25 Open/Close HLC o/p #35CX-20 to replaced @3 broken HLC at TP of Well KB #404. (1 Well was S/D during this job) Cause: Planned Maintenance. | 123 | 1 | 10:30 | Morning | Sunday | 2015 | 12
2271 | 2015-12-20 17:02 | 2015-12-20 17:02 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified | 0 | C.Duri VCB fdr #13 T/R 1x Ctr: 182-183 R/F: 51N(@1,@2). Not Patrolled yet. | 3150433 | 1 | 17:02 | Afternoon | Sunday | 2015 | 12
2272 | 2015-12-20 17:02 | 2015-12-21 15:00 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3150433 | 1 | 17:02 | Afternoon | Sunday | 2015 | 12
2273 | 2015-12-21 23:59 | 2015-12-21 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power System normal condition. |  | 1 | 23:59 | Night | Monday | 2015 | 12
2274 | 2015-12-22 23:59 | 2015-12-22 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power System Normal Condition. |  | 1 | 23:59 | Night | Tuesday | 2015 | 12
2275 | 2015-12-23 07:21 | 2015-12-23 07:21 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | No.Duri VCB fdr #7 T/R 1x. Ground fault alarm at No.Duri fdr #7. Not checked yet. | 3150433 | 1 | 7:21 | Morning | Wednesday | 2015 | 12
2276 | 2015-12-23 07:21 | 2015-12-30 09:21 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | Checked & found, No.Duri VCB fdr #7 T/R 1x Ctr: Did not change. R/F: 50/51N & 51@1,@2. Patrolled the line, but found nothing. Cause: Unidentified. | 3150433 | 1 | 7:21 | Morning | Wednesday | 2015 | 12
2277 | 2015-12-23 09:21 | 2015-12-23 09:21 | 115KV CENTRAL DURI - BATANG LINE | Fair | Tree | 47 | 09:21 115KV CDSY OCB #31 T/R 1x. 115KV CDSY OCB #33 T/SO. 115KV Batang GCB #1 T/R 1x. 115KV Sintong GCB #25 T/R 1x Ctr: 287-288 R/F: 87L-@1 & 67N(Instan). (115KV CDSY - Batang/Sintong line T/R) Batang Substation no power at the time. 09:55 Closed 115KV CDSY OCB #33, Ok. Not checked yet. | 3150433 | 1 | 9:21 | Morning | Wednesday | 2015 | 12
2278 | 2015-12-23 09:21 | 2015-12-30 09:21 | 115KV CENTRAL DURI - BATANG LINE | Fair | Tree | 47 | Checked & found: 115KV CDSY GCB #31 T/R 1x Ctr: 27-28 R/F: 67N (Instan) 115KV CDSY GCB #33 T/SO. Ctr: 586-587. 115KV Batang OCB #1 T/R 1x Ctr: Not reported yet. 115KV Sintong GCB #25 T/R 1x Ctr: 287-288 R/F: 87L-@1 & 67N(Instan). (115KV CDSY - Batang/Sintong line) Patrolled & found, high Trees touching power line at near pole #BTG-05 & #BTG-19. Cause: Tree. | 3150433 | 1 | 9:21 | Morning | Wednesday | 2015 | 12
2279 | 2015-12-23 14:10 | 2015-12-23 14:10 | 13.8KV 6D FEEDER #3 | Fair | Recloser - Control Recloser | 19 | 14:10 It was reported no power at Wells #6D-62, #6D-62N, #6D-72 & #6D-61. 14:35 Checked & found Recl. 6D-03 (6D fdr #3) T/SO. Ctr: 54-55. Blocked & closed Recl. 6D03, but failed. Transfer part load of 6D fdr #3 to 6D fdr #2. 15:15 Open Visual opening of Recl. 6D-03. Closed LBS #6D-68 (fed from 6D fdr #2) Cause: Control Recloser problem. | 3150434 | 1 | 14:10 | Afternoon | Wednesday | 2015 | 12
2280 | 2015-12-23 18:11 | 2015-12-23 18:11 | 13.8KV 4D FEEDER #4 | Fair | Unidentified | 100 | 4D OCB fdr #4 T/R 1x. Not checked yet. | 3150434 | 1 | 18:11 | Afternoon | Wednesday | 2015 | 12
2281 | 2015-12-23 18:11 | 2015-12-30 09:11 | 13.8KV 4D FEEDER #4 | Fair | Unidentified | 100 | Checked & found, 4D OCB fdr #4 T/R 1x Ctr: 256-257 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3150434 | 1 | 18:11 | Afternoon | Wednesday | 2015 | 12
2282 | 2015-12-23 22:45 | 2015-12-23 22:45 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Transformer Failure | 25 | 22:45 It was repoted b/o fuse for Tx at Well KB #351. Not checked yet. | 3150434 | 1 | 22:45 | Night | Wednesday | 2015 | 12
2283 | 2015-12-23 22:45 | 2015-12-24 15:30 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Transformer Failure | 25 | 10:30 Checked & found, @3 b/o 2.1SF fuse for 100Kva Tx at Well KB #351. (CKBS fdr #5) Performed TTR, Megger test the Tx & found, Low Megger reading. Cause: Tx failure. (Low megger reading) 15:30 Replaced 100Kva Tx failure with 300Kva Tx, then energized the Tx. | 3150434 | 1 | 22:45 | Night | Wednesday | 2015 | 12
2284 | 2015-12-24 09:41 | 2015-12-24 09:41 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 12 | CKBS VCB fdr #5 T/R 1x. Not checked yet. | 3150434 | 1 | 9:41 | Morning | Thursday | 2015 | 12
2285 | 2015-12-24 09:41 | 2015-12-25 10:41 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 12 | Checked & found, CKBS VCB fdr #5 T/R 1x Ctr: 130-131 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3150434 | 1 | 9:41 | Morning | Thursday | 2015 | 12
2286 | 2015-12-24 19:00 | 2015-12-24 19:00 | 5 BRAVO SUBSTATION | Fair | Equipment Failure | 247 | 19:00 115KV 5B OCB #23 T/O. 115KV 5B OCB #24 T/O. (115KV For 5B Power Tx #1) Also found, 13.8KV 5B OCB fdr #3 T/O. (5B RTU failed at this time) 20:00 Checked & found, 115KV 5B OCB #23 T/O Ctr: 1022-1023. 115KV 5B OCB #24 T/O Ctr: 305-306 R/F: 51G. Checked 13.8KV breakers & found: -13.8KV OCB fdr #1, in Closed position. -13.8KV OCB fdr #2 T/O. Ctr: 333-334. -13.8KV OCB fdr #3 T/O. Ctr: 356-357 R/F: 51N. -13.8KV OCB fdr #6, in Closed position. Checked & found 5B power Tx #1, normal condition. (R/F: 51G) 20:24 Manually opened 13.8KV OCB fdr #1 Ctr: 204-206. Manually opened 13.8KV OCB fdr #6 Ctr: 243-244. 20:36 Closed 115KV 5B OCB #24, Ok. 20:38 Closed 115KV 5B OCB #23, Ok. (5B Power Transformer-1 energized) 20:40 Blocked & Closed 13.8KV 5B OCB fdr #6, Ok. Then released the block. 20:44 Blocked & Closed 13.8KV 5B OCB fdr #1, Ok. Then released the block. 20:46 Blocked & Closed 13.8KV 5B OCB fdr #2, Ok. Then released the block. 20:50 Opened both side isolation Sw of 5B OCB fdr #3. Blocked & Closed 13.8KV 5B OCB fdr #3, but there is problem in the OCB control box. Then Manually opened 13.8KV 5B OCB fdr #3. Cause: Equipment failure. (Breaker control problem) 21:00 Patrolled the line at downstream of 5B OCB fdr #3, but found nothing. 22:24 Transfer load 5B fdr #3 to 5B fdr #2, by closed LBS #4C-50. Cause: Equipment failure. | 3150434 | 1 | 19:00 | Night | Thursday | 2015 | 12
2287 | 2015-12-25 06:52 | 2015-12-25 06:52 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Dead End Insulator | 0 | C.Duri ACB fdr #4 T/R 1x Ctr: 463-464 R/F: 51N. The line is not Patrolled yet. | 3150433 | 1 | 6:52 | Morning | Friday | 2015 | 12
2288 | 2015-12-25 06:52 | 2015-12-30 09:52 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Dead End Insulator | 0 | Patrolled the line & found, @3 F/O Dead end Insulator o/p #09-08-06. Cause: Dead end Insulator. | 3150433 | 1 | 6:52 | Morning | Friday | 2015 | 12
2289 | 2015-12-25 10:11 | 2015-12-25 10:11 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 90 | Sintong OCB fdr #1 T/R 1x. Sintong fdr #2 Load dropped 12A (78-66A). (Ground fault Alarm at sintong fdr #1) Not checked yet. | 3150433 | 1 | 10:11 | Morning | Friday | 2015 | 12
2290 | 2015-12-25 10:11 | 2015-12-31 16:11 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 90 | Checked & found, Sintong OCB fdr #1 T/R 1x Ctr: 378-379 R/F: 51N. Also found, Sintong GFPC T/R 2x Ctr: 815-817. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 10:11 | Morning | Friday | 2015 | 12
2291 | 2015-12-25 14:15 | 2015-12-25 14:15 | 13.8KV MENGGALA FEEDER #2 | Fair | Planned Maintenance | 19 | 14:15-15:15 S/D well Ubi #26, and Blocked Recl. 26AL-2. (Menggala fdr #2) (to repair Spark at HLC on TP of Well Ubi #26. Cause: Planed Maintenance | 123 | 1 | 14:15 | Afternoon | Friday | 2015 | 12
2292 | 2015-12-25 15:20 | 2015-12-25 15:20 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 45 | Minas fdr #1 Load dropped 128A (128-0A). Not checked yet. | 3150434 | 1 | 15:20 | Afternoon | Friday | 2015 | 12
2293 | 2015-12-25 15:20 | 2015-12-31 10:20 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 45 | Checked & found, Recl. 7D-20 (Minas fdr #1) T/R 1x Ctr: 145-146. Patrolled the line & found, @3 flashed over Dead end Insulator o/p #7C-31. Cause: Lightning. | 3150434 | 1 | 15:20 | Afternoon | Friday | 2015 | 12
2294 | 2015-12-25 15:31 | 2015-12-25 15:31 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 41 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3150433 | 1 | 15:31 | Afternoon | Friday | 2015 | 12
2295 | 2015-12-25 15:31 | 2015-12-30 09:31 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 41 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 165-166 R/F: 51N. Patrolled the line, but found nothing. Also found, Recl. 32AK-16 (Ketigul VCB fdr #1) T/R 1x Ctr: 117-118. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 15:31 | Afternoon | Friday | 2015 | 12
2296 | 2015-12-25 16:52 | 2015-12-25 16:52 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Recloser - Control Recloser | 62 | 16:52 C.Duri fdr #7 load dropped 30A (189-159A). 18:30 Checked & found Recl. 03-07-24 (C.Duri fdr #7) T/SO. Ctr: 42-43. Patrolled the line, but found nothing. 18:45 Blocked & Closed Recl. 03-07-24, but failed. Closed Recl. 03-07-24 by jumpering the terminal connection, Ok. Then unplug this Recloser. Cause: Control recloser. | 3150433 | 1 | 16:52 | Afternoon | Friday | 2015 | 12
2297 | 2015-12-25 23:35 | 2015-12-25 23:35 | 13.8KV NORTH DURI FEEDER #5 | Cloudy and Lightning | Lightning | 0 | 23:35 No.Duri VCB fdr #5 T/O. (In block position due to Rig activity at Well #3F-1009) 23:43 Blocked & Closed No.Duri VCB fdr #5, Ok. (Still In block position). Not checked & Patrolled yet. | 3150433 | 1 | 23:35 | Night | Friday | 2015 | 12
2298 | 2015-12-25 23:35 | 2015-12-30 09:35 | 13.8KV NORTH DURI FEEDER #5 | Cloudy and Lightning | Lightning | 0 | Checked & found, No.Duri VCB fdr #5 T/O. Ctr: 103-104 R/F: 51N(@2). Patrolled the line & found, @2 broken L/A near Well #3H-02. Cause: Lightning. | 3150433 | 1 | 23:35 | Night | Friday | 2015 | 12
2299 | 2015-12-26 09:48 | 2015-12-26 09:48 | 13.8KV MENGGALA FEEDER #2 | Cloudy and Lightning | Lightning | 54 | Menggala OCB fdr #2 T/R 1x. Not checked yet. | 3150433 | 1 | 9:48 | Morning | Saturday | 2015 | 12
2300 | 2015-12-26 09:48 | 2015-12-31 07:48 | 13.8KV MENGGALA FEEDER #2 | Cloudy and Lightning | Lightning | 54 | Checked & found, Menggala OCB fdr #2 T/R 1x Ctr: 527-528 R/F: 51N. Patrolled the line & found: -@3 Broken L/A o/p #26AL-20. -@2 Flashed over Pin Insulator o/p #26AK-01. Cause: Lightning. | 3150433 | 1 | 9:48 | Morning | Saturday | 2015 | 12
2301 | 2015-12-27 12:57 | 2015-12-27 12:57 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 17 | 12:57 It was reported b/o fuse for Tx at Well Gulamo #05. 13:53 Checked & found, @1, @2 b/o 2.1SF fuses for 100Kva Tx at Well Gulamo #05. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Snake) | 3150433 | 1 | 12:57 | Afternoon | Sunday | 2015 | 12
2302 | 2015-12-28 08:47 | 2015-12-28 08:47 | 4.16KV SO RUMBAI FEEDER #1 | Fair | Animal | 0 | 08:47 It was reported b/o fuse for Tx at Rumbai FM Mechanic Building. 14:50 Checked & found, @1, @2, @3 b/o fuse for 3x25Kva Tx at Rumbai FM Building. Performed TTR & Megger Test, found good reading. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Bird) | 3150433 | 1 | 8:47 | Morning | Monday | 2015 | 12
2303 | 2015-12-28 11:55 | 2015-12-28 11:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Powerline - Jumper | - | 11:55 It was reported broken Jumper for Primary Tx at Well Kulin #50. 16:00 Checked & found, @1 broken jumper for 75Kva Tx at Well Kulin #50. Opened all fuses & S/D the Tx, to repair broken jumper above then energized the Tx. Cause: Jumper. (Well Kulin #50 was off under RIG Service status) | 3150433 | 1 | 11:55 | Morning | Monday | 2015 | 12
2304 | 2015-12-28 13:19 | 2015-12-28 13:19 | 13.8KV NELLA FEEDER #2 | Cloudy and Lightning | Lightning | 20 | Nella VCB fdr #2 T/R 1x. Nella fdr #1 load dropped 45A (151-109A). Nella GFPC T/R 1x. (Ground fault alarm on Nella fdr #1) Not checked yet. | 3150433 | 1 | 13:19 | Afternoon | Monday | 2015 | 12
2305 | 2015-12-28 13:19 | 2015-12-31 16:15 | 13.8KV NELLA FEEDER #2 | Cloudy and Lightning | Lightning | 20 | Nella OCB fdr #2 T/R 1x Ctr: 206-207 R/F: 50N(@3). Also found, Nella GFPC Ctr: 683. (Did not operate) Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3150433 | 1 | 13:19 | Afternoon | Monday | 2015 | 12
2306 | 2015-12-29 08:59 | 2015-12-29 08:59 | 115KV KOTABATAK JUNCTION - LIBO LINE | Cloudy | Lightning | 14 | 115KV KBJ GCB #53 T/R 1x. 115KV KBJ GCB #55 T/R 1x. (115KV KBJ - Libo line). (Libo Substation No power at this time) Not Checked yet. | 3150433 | 1 | 8:59 | Morning | Tuesday | 2015 | 12
2307 | 2015-12-29 08:59 | 2015-12-31 09:59 | 115KV KOTABATAK JUNCTION - LIBO LINE | Cloudy | Lightning | 14 | Checked & found: 115KV KBJ GCB #53 T/R 1x Ctr: 212-213. 115KV KBJ GCB #55 T/R 1x Ctr: 311-312 R/F: 67N(Inst.), 21@1-G (Zone-1) (115 KBJ - Libo line T/R) Patrolled the line from KBJ & found: -@1 Broken Dead end Insulator o/p #NN. Patrolled the line from Libo & found: -@2 Broken Suspension Insulator o/p #KW-21. Cause: Lightning. | 3150433 | 1 | 8:59 | Morning | Tuesday | 2015 | 12
2308 | 2015-12-29 16:24 | 2015-12-29 16:24 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 11 | 16:24 It was reported b/o fuse for Tx at Well Sintong #10. (Sintong fdr #2) 17:32 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Sintong #10. Replaced the b/o fuse with the same size, then energized the Tx. Cause: Animal. (Bird) | 3150433 | 1 | 16:24 | Afternoon | Tuesday | 2015 | 12
2309 | 2015-12-30 04:35 | 2015-12-30 04:35 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 114 | 04:35 Batang OCB fdr #3 T/R 1x. 06:14 Batang OCB fdr #3 T/R 1x again. 06:23 Batang OCB fdr #3 T/R 1x again. Not checked yet. | 3150433 | 1 | 4:35 | Morning | Wednesday | 2015 | 12
2310 | 2015-12-30 04:35 | 2016-04-01 15:15 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 114 | Checked & found, Batang OCB fdr #3 T/R 3x Ctr: 299-302 R/F: 50N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3150433 | 1 | 4:35 | Morning | Wednesday | 2015 | 12
2311 | 2015-12-30 10:39 | 2015-12-30 10:39 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified (Fuse) | 21 | 10:39 Replaced @2 b/o 7.8SF fuse for 300Kva Tx at Well KB #273, then energized the Tx. Cause: Unidentified (Fuse). | 3150434 | 1 | 10:39 | Morning | Wednesday | 2015 | 12
2312 | 2015-12-31 07:13 | 2015-12-31 07:13 | 13.8KV BEKASAP FEEDER #2 | Cloudy and Lightning | Lightning | 101 | Bekasap fdr #2 Load dropped 176A (234-58A). Bekasap GFPC T/R 1x. (Ground fault alarm on Bekasap fdr #2) Not checked yet. Production loss reported by EC: Prod. loss = 48 Bbls / 45 Wells. (Pematang-GS) Prod. loss = 53 Bbls / 53 Wells. (Bekasap-GS) Grand Total = 101 Bbls / 98 Wells. 07-Jan-2016. Checked & found, Recl. 35BC-14 (Pematang fdr #1) T/R 1x Ctr: 38-39. Also found, Bekasap Mian GFPC T/R 1x Ctr: 336-337. Patrolled the line & found: -@3 Broken Pin Insulator o/p #35BD-36. -@2 F/O Dead end Insulator o/p #35BD-20. Cause: Lightning. (See report 03-Jan-2016 at 17:07) | 3150433 | 1 | 7:13 | Morning | Thursday | 2015 | 12
2313 | 2015-12-31 08:42 | 2015-12-31 08:42 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Dead End Insulator | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3150433 | 1 | 8:42 | Morning | Thursday | 2015 | 12
2314 | 2015-12-31 08:42 | 2016-04-01 15:42 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Dead End Insulator | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 78-79 R/F: Did not appear. Patrolled the line & found, @1 F/O Dead end Insulator o/p #3DE-41. Cause: Dead end Insulator. | 3150433 | 1 | 8:42 | Morning | Thursday | 2015 | 12
2315 | 2015-12-31 10:40 | 2015-12-31 10:40 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 10:40 It was reported b/o fuse for Tx o/p 01-06-20 (DF fdr #1). 17:45 Checked & found, @2 b/o fuse for 112.5KVA Tx. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3150433 | 1 | 10:40 | Morning | Thursday | 2015 | 12
2316 | 2015-12-31 17:52 | 2015-12-31 17:52 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 9 | 17:52 It was reported by Balam GS, fall down conductor at back side police office Balam . 19:05 Checked & found @1@2@3 B/O fuse for 300Kva at So Balam#132 (So Balam fdr#1). Checked TTR & Megger 300Kva Tx is good condition. 19:23 Replaced @1@2@3 B/O fuse & Energized the Tx. Cause: Animal (Animal). | 3150433 | 1 | 17:52 | Afternoon | Thursday | 2015 | 12
2317 | 2016-01-01 09:00 | 2016-01-01 09:00 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 16 | 09:00 Sintong fdr #1 Load dropped 30A (212-182A). 16:00 Checked & found, Recl. 25AD-26 (Sintong fdr #1) T/R 1x Ctr: 102-103. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3162580 | 1 | 9:00 | Morning | Friday | 2016 | 1
2318 | 2016-01-01 10:07 | 2016-01-01 10:07 | 13.8KV NELLA GFPC | Cloudy | Unidentified | 0 | Nella GFPC T/R 1x. (Ground fault alarm on Nella fdr #1) No Load dropped at any fdrs. Not checked yet. | 3162580 | 1 | 10:07 | Morning | Friday | 2016 | 1
2319 | 2016-01-01 10:07 | 2016-02-01 10:07 | 13.8KV NELLA GFPC | Cloudy | Unidentified | 0 | Checked & found, Nella GFPC T/R 1x Ctr: 683. (Did not operate) R/F: 50N(3). Patrolled Nella fdr #1 line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 10:07 | Morning | Friday | 2016 | 1
2320 | 2016-01-01 10:12 | 2016-01-01 10:12 | 13.8KV 6D FEEDER #3 | Fair | Animal | 41 | 10:12 It was reported b/o fuse for Tx at well 6D-51N. 15:30 Checked and found @3 b/o fuse for 300 Kva Tx. Perform TTR and Megger test --> Good reading. Replace b/o fuse above with the same size and energized the Tx. Cause: Animal (mouse). | 3162581 | 1 | 10:12 | Morning | Friday | 2016 | 1
2321 | 2016-01-01 12:22 | 2016-01-01 12:22 | 13.8KV BANGKO FEEDER #4 | Drizzle | Unidentified (Fuse) | 75 | 12:22 Bangko OCB fdr #4 T/R 1x. Bangko GFPC T/R 1x. 15:12 Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99979-99980 R/F: Did not appear. Also found, Bangko GFPC T/R 1x Ctr: 483-484 R/F: 51N(@2). Patrolled the line & found, @2 b/o 3.5SF fuse for 150Kva Tx for Test Station A at Bangko-GS. Then replaced b/o fuse with the same size & Energized the Tx. Cause: Unidentified (Fuse). | 3162580 | 1 | 12:22 | Afternoon | Friday | 2016 | 1
2322 | 2016-01-01 12:22 | 2016-01-01 12:22 | 13.8KV BANGKO FEEDER #3 | Drizzle | Unidentified | 0 | 12:22 Bangko OCB fdr #3 T/R 1x. Bangko fdr #1 load dropped 32A (271-239A). 15:00 Checked & found, Bangko OCB fdr #3 T/R 1x Ctr: 99934-99935 R/F: Did not appear. Patrolled the line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 12:22 | Afternoon | Friday | 2016 | 1
2323 | 2016-01-01 13:45 | 2016-01-01 13:45 | 13.8KV DURI FIELD FEEDER #4 | Cloudy and Lightning | Lightning | 0 | Duri Field ACB fdr #4 T/R 1x. Not checked yet. | 3162580 | 1 | 13:45 | Afternoon | Friday | 2016 | 1
2324 | 2016-01-01 13:45 | 2016-04-01 16:28 | 13.8KV DURI FIELD FEEDER #4 | Cloudy and Lightning | Lightning | 0 | Checked & found, Duri Field VCB fdr #4 T/R 1x Ctr: 466-467 R/F: 51N(@1,@2). Patrolled the line & found, @2 broken HLC jumper for Cap. Bank o/p #07-V2-01. Cause: Lightning. | 3162580 | 1 | 13:45 | Afternoon | Friday | 2016 | 1
2325 | 2016-01-01 14:29 | 2016-01-01 14:29 | 13.8KV KETIGUL FEEDER#3 | Fair | Animal | 12 | 14:29 It was reported b/o fuse for Tx at Well Gulamo #07. 17:41 Checked & found, @1,@2 b/o 25K fuses for 550Kva Tx at Well Gulamo #07. Performed Test TTR, Megger the Tx & found, normal. (good reading). Replaced b/o fuse above with same size then energized the Tx. Cause: Animal. (Bird) | 3162580 | 1 | 14:29 | Afternoon | Friday | 2016 | 1
2326 | 2016-01-01 22:37 | 2016-01-01 22:37 | 13.8KV BEKASAP FEEDER #3 | Fair | Tree | 6 | 22:37 It was reported b/o fuse for Tx at Well Bekasap #142. Not checked yet. | 3162580 | 1 | 22:37 | Night | Friday | 2016 | 1
2327 | 2016-01-01 22:37 | 2016-02-01 10:18 | 13.8KV BEKASAP FEEDER #3 | Fair | Tree | 6 | Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Bekasap #142. Perform TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Tree. (the Tree fell down & hit primary Tx jumper) | 3162580 | 1 | 22:37 | Night | Friday | 2016 | 1
2328 | 2016-02-01 06:59 | 2016-02-01 06:59 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Animal | 75 | 06:59 CKBS VCB fdr #5 T/R 1x. CKBS fdr #6 Load dropped 15A (194-179A). 18:00 Checked & found, CKBS VCB fdr #5 T/R 1x Ctr: 131-132 R/F: 51N. Patrolled the line and found : -@3 Broken Dead end insulator o/p #36CV-17. -@2 Broken Bushing LBS o/p #36CV-17. -@3 Broken FCO on TP of Well KB #15. Cause: Animal. (Monkey) | 3162581 | 1 | 6:59 | Morning | Monday | 2016 | 2
2329 | 2016-02-01 16:11 | 2016-02-01 16:11 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri Community ACB fdr #2 T/R 1x. Not checked yet. | 3162580 | 1 | 16:11 | Afternoon | Monday | 2016 | 2
2330 | 2016-02-01 16:11 | 2016-03-01 14:11 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #2 T/R 1x Ctr: 65-66 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 16:11 | Afternoon | Monday | 2016 | 2
2331 | 2016-02-01 21:09 | 2016-02-01 21:09 | 13.8KV 3D FEEDER #8 | Cloudy | Animal | 31 | 21:09 3D fdr #8 Load dropped 116A (262-146A). 03-JAN-2016. 00:40 It was reported no power at Well #2F-82N & 2F93. (Will be checked at the morning) | 3162581 | 1 | 21:09 | Night | Monday | 2016 | 2
2332 | 2016-02-01 21:09 | 2016-03-01 09:22 | 13.8KV 3D FEEDER #8 | Cloudy | Animal | 31 | 09:22 Checked & found, Recl. 2F-11 (3D fdr #8) T/LO. Ctr: Not clear. (Display Blur) Also found, a dead Fox at @2 L/A jumper of Recl. 2F-11. Then Removed its animal. 09:30 Blocked & closed Recl. 2F-11, Ok. Then released the block. Cause: Animal. (Fox) | 3162581 | 1 | 21:09 | Night | Monday | 2016 | 2
2333 | 2016-03-01 09:24 | 2016-03-01 09:24 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Duri Community fdr #3 load dropped 34A (100-66A). (It was reported power outage at Talang Camp). Not checked yet. | 3162580 | 1 | 9:24 | Morning | Tuesday | 2016 | 3
2334 | 2016-03-01 09:24 | 2016-06-01 15:24 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Checked & found, Recl. 06F-07 (Duri Community fdr #3) T/R 1x Ctr: 1830-1831. Patrolled the line & found, @1 broken Pin Insulator o/p #2DG-19. (Near hose Talang-73) Cause: Pin Insulator. | 3162580 | 1 | 9:24 | Morning | Tuesday | 2016 | 3
2335 | 2016-03-01 14:10 | 2016-03-01 14:10 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 14:10 It was reported b/o fuse for Tx o/p #08-M3-35. Not checked yet. | 3162580 | 1 | 14:10 | Afternoon | Tuesday | 2016 | 3
2336 | 2016-03-01 14:10 | 2016-04-01 17:38 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | Replaced @2 b/o fuse for 112.5KVA Tx o/p 08-M3-35 then energized the Tx. Cause: Unidentified (Fuse). | 3162580 | 1 | 14:10 | Afternoon | Tuesday | 2016 | 3
2337 | 2016-03-01 14:11 | 2016-03-01 14:11 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Animal | 0 | 14:11 Duri Community ACB fdr #2 T/R 1x Ctr: 66-67 R/F: 51@1 & 51N. 16:32 Patrolled & found, @2 flash over L/A o/p #2F-157 & a Dead Squirrel under pole above. Cause: Animal. (Squirrel) | 3162580 | 1 | 14:11 | Afternoon | Tuesday | 2016 | 3
2338 | 2016-03-01 16:04 | 2016-03-01 16:04 | 13.8KV BATANG FEEDER #2 | Heavy Rain | Lightning | 0 | Batang OCB fdr #2 T/R 1x. Not checked yet. | 3162580 | 1 | 16:04 | Afternoon | Tuesday | 2016 | 3
2339 | 2016-03-01 16:04 | 2016-06-01 15:15 | 13.8KV BATANG FEEDER #2 | Heavy Rain | Lightning | 0 | Checked & found, Batang OCB fdr #2 T/R 1x Ctr: 110-111 R/F: 51@1. Patrolled the line & found, @1 broken Dead end Insulator o/p #35A-24. Cause: Lightning. | 3162580 | 1 | 16:04 | Afternoon | Tuesday | 2016 | 3
2340 | 2016-03-01 17:07 | 2016-03-01 17:07 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 44 | Bekasap Main fdr #2 load dropped 141A (230-89A). Bekasap Main GFPC-TX #C T/R 1x. (Ground fault alarm on Bekasap Main fdr #2) Not checked yet. Note: Pematang fdr #1 & fdr #2 are transferred to Bekasap Main fdr #2. (Since 07-Dec-2015) | 3162580 | 1 | 17:07 | Afternoon | Tuesday | 2016 | 3
2341 | 2016-03-01 17:07 | 2016-07-01 16:40 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 44 | Checked & found, Recl. 35BC-14 (Pematang fdr #1) T/R 1x Ctr: 38-39. Also found, Bekasap Mian GFPC T/R 1x Ctr: 336-337. Patrolled the line & found: -@3 Broken Pin Insulator o/p #35BD-36. -@2 F/O Dead end Insulator o/p #35BD-20. Cause: Lightning. | 3162580 | 1 | 17:07 | Afternoon | Tuesday | 2016 | 3
2342 | 2016-04-01 07:11 | 2016-04-01 07:11 | BANGKO SUBSTATION | Fair | Under investigation | 1651 | 07:11 115KV STG-BKO line load dropped 162A (252-90A). (Bangko RTU failed at this time) It was reported no power at Bangko-GS. 07:28 Checked & found, 115KV Bangko C/S T/O. Ctr: 219. (not change) R/F: 51P (W1). Visual checked all equipment at Bangko SS & found, normal. (To anticipate Spill at Bangko-GS & Bangko-EOR) 07:36 Manual opened Nella VCB fdr #1, then closed at: 08:53. Manual opened Nella VCB fdr #2, then closed at: 08:44. 07:44 Manual opened Bangko OCB fdr #1, #2, #3, #4. 07:54 Manual closed 115KV Bangko C/S, Ok. 07:57 Manual closed Bangko OCB fdr #3. 08:08 Bangko RTU online. 08:32 Manual closed Bangko OCB fdr #2. 08:48 Manual closed Bangko OCB fdr #4. 08:53 Manual closed Bangko OCB fdr #1. Cause: Under Investigation. | 3162580 | 1 | 7:11 | Morning | Friday | 2016 | 4
2343 | 2016-04-01 10:51 | 2016-04-01 10:51 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 4 | 10:51 It was reported b/o fuse for Tx o/p #06-S3-19. (DF fdr #4) 11:56 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #06-S3-19. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Monkey) | 3162580 | 1 | 10:51 | Morning | Friday | 2016 | 4
2344 | 2016-04-01 11:12 | 2016-04-01 11:12 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 12 | 11:12 It was reported b/o fuse for Tx at Well Bangko #153. 14:11 Checked & found, @2 b/o 2.1SF fuse for 100Kva Tx at Well Bangko #153. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3162580 | 1 | 11:12 | Morning | Friday | 2016 | 4
2345 | 2016-04-01 11:18 | 2016-04-01 11:18 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 11:18 Replaced @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T1-08, then energized the Tx. Cause: Unidentified (Fuse). | 3162580 | 1 | 11:18 | Morning | Friday | 2016 | 4
2346 | 2016-04-01 16:50 | 2016-04-01 16:50 | 13.8KV 4D FEEDER #5 | Fair | Transformer Failure | 74 | 16:50 It was reported b/o fuse for Tx at Well #4D-68. 18:34 Checked & found, @1, @2, @3 b/o 14.0SF fuse for 600Kva Tx (F/P). Also found b/o at primary Tx. Cause: Transfomer Failure. (The Tx is not replaced yet) | 3162581 | 1 | 16:50 | Afternoon | Friday | 2016 | 4
2347 | 2016-04-01 16:50 | 2016-11-01 15:00 | 13.8KV 4D FEEDER #5 | Fair | Transformer Failure | 74 | Replaced 600Kva Tx with 450Kva Tx & energized the Tx at Well #4D-68. Cause: Tx failure. (Low megger reading) | 3162581 | 1 | 16:50 | Afternoon | Friday | 2016 | 4
2348 | 2016-05-01 07:08 | 2016-05-01 07:08 | 13.8KV CENTRAL DURI FEEDER #9 | Cloudy and Lightning | Lightning | 0 | C.Duri ACB fdr #9 T/R 1x Ctr: 341-342 R/F: 51N. Not patrolled yet. | 3162580 | 1 | 7:08 | Morning | Sunday | 2016 | 5
2349 | 2016-05-01 07:08 | 2016-07-01 07:30 | 13.8KV CENTRAL DURI FEEDER #9 | Cloudy and Lightning | Lightning | 0 | Patrolled the line & found: -@1 Flashed over Dead end Insulator o/p #04-8-31. -@1 Flashed over Dead end Insulator o/p #04-7-09. Cause: Lightning. | 3162580 | 1 | 7:08 | Morning | Sunday | 2016 | 5
2350 | 2016-05-01 11:10 | 2016-05-01 11:10 | 13.8KV BANGKO FEEDER #1 | Fair | Main breaker | 10 | 11:10 It was reported b/o fuse for Tx at Well Bangko #231. 11:45 Checked & found, @3 b/o 3.5SF fuse for 150KVA Tx at Well Bangko #231. Replaced the b/o fuse with same size then energized the Tx. 14:30 It was reported Unbalance voltage at Well Bangko #231. 15:20 Checked & found, @1 b/o 3.5SF fuse for 150KVA Tx at Well Bangko #231. Replaced the b/o fuse with same size then energized the Tx. 15:40 It was reported b/o fuse for Tx again at Well Bangko #231. 17:45 Checked & found, @2 b/o 3.5SF fuse for 150KVA Tx. Performed TTR, Megger test the TX & found, normal. (good reading) Replaced the b/o fuse above with same size, then energized the Tx. Cause: Main Breaker. | 3162580 | 1 | 11:10 | Morning | Sunday | 2016 | 5
2351 | 2016-05-01 15:45 | 2016-05-01 15:45 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 73 | Bangko fdr #4 load dropped 159A (287-128A). Ground fault alarm on Bangko fdr #4. Not checked yet. | 3162580 | 1 | 15:45 | Afternoon | Sunday | 2016 | 5
2352 | 2016-05-01 15:45 | 14/01/2016 15:55 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 73 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 2x Ctr: 76-78. Also found, Bangko GFPC T/R 1x Ctr: 486-487. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3162580 | 1 | 15:45 | Afternoon | Sunday | 2016 | 5
2353 | 2016-05-01 15:50 | 2016-05-01 15:50 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 111 | 15:50 115KV Sintong-Bangko line load dropped 134A (239-105A). (Bangko RTU, Balam RTU, Nella RTU & Pinang RTU failed at the time) 15:51 Nella 13.8KV Recloser for Cap. Bank T/O, then closed at 17:00. 15:55 Bangko RTU, Balam RTU, Nella RTU & Pinang RTU are back to normal. Bangko fdr #1 load dropped 145A (267-122A). Bangko fdr #2 load dropped 240A (260-20A). Bangko fdr #3 load dropped 54A (217-163A). Bangko fdr #4 load dropped 165A (287-122A). Nella fdr #1 load dropped 23A (147-124A). Pinang fdr #1 load dropped 18A (83-65A). So.Balam fdr #1 load dropped 7A (95-88A). So.Balam fdr #4 load dropped 9A (163-159A). 16:20 Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99981-99982 R/F: 51@1,@2. Bangko 13.8Kv Recloser for CAP. Bank T/O, then close at 16:21. Not patrolled yet. | 3162580 | 1 | 15:50 | Afternoon | Sunday | 2016 | 5
2354 | 2016-05-01 15:50 | 14/01/2016 15:56 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 111 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3162580 | 1 | 15:50 | Afternoon | Sunday | 2016 | 5
2355 | 2016-06-01 14:52 | 2016-06-01 14:52 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 0 | 14:52 Manually open LBS o/p #27Y-13. (Sintong fdr #2) (Switching to transfer part load of Bangko fdr #4 to Sintong fdr #2) 15:05 Closed LBS o/p #27Y-13. (Failed to close Recl. 28AF-02) Cause: Plan Maintenance. | 123 | 1 | 14:52 | Afternoon | Wednesday | 2016 | 6
2356 | 2016-06-01 15:26 | 2016-06-01 15:26 | 13.8KV 8C FEEDER #3 | Heavy Rain | Low mega-ohm reading | 10 | 15:26 It was reported b/o fuse for Tx at Well #7C-88. Checked & found, @1, @2 b/o 7.8SF fuse for 300KVA Tx at Well #7C-88. Performed TTR, Megger test the Tx & found, Low Megger reading. Cause: Tx Failure. (Low Mega Ohm reading Tx) (The Tx is not replaced yet) | 3162581 | 1 | 15:26 | Afternoon | Wednesday | 2016 | 6
2357 | 2016-06-01 15:26 | 14/01/2016 10:00 | 13.8KV 8C FEEDER #3 | Heavy Rain | Low mega-ohm reading | 10 | Replaced 300Kva Tx failure with 150Kva Tx & energized the Tx at Well #7C-88. Cause: Tx failure. (Low megger reading) | 3162581 | 1 | 15:26 | Afternoon | Wednesday | 2016 | 6
2358 | 2016-06-01 18:35 | 2016-06-01 18:35 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Transformer Failure | 47 | 18:35 It was reported b/o fuse for Tx at Well Ampuh #02. Checked & found, @1, @2 b/o 7.0SF fuses for 225Kva Tx at Well Ampuh #02. Performed TTR, Megger test the Tx & found, Unbalance TTR. Cause: Tx Failure. (Burnt out Tx winding) (The Tx is not replaced yet) | 3162580 | 1 | 18:35 | Afternoon | Wednesday | 2016 | 6
2359 | 2016-06-01 18:35 | 2016-07-01 10:35 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Transformer Failure | 47 | Replaced 225Kva Tx failure with 300Kva Tx & energized the Tx at Well Ampuh #02. Cause: Tx failure. (Low megger reading) | 3162580 | 1 | 18:35 | Afternoon | Wednesday | 2016 | 6
2360 | 2016-06-01 20:20 | 2016-06-01 20:20 | 115KV CENTRAL DURI - BATANG LINE | Fair | Lightning Arrester | 0 | 20:20 115KV CDSY OCB #31 T/R 1x. 115KV CDSY OCB #33 T/SO. 115KV Sintong GCB #25 T/R 1x R/F: 87L, 67N(Inst.) & 21G (Zone-1) Ctr: Not reported yet. (115KV CDSY - Batng/Sintong line) (Batang Substation no power at that time) 20:24 Manually Closed 115kV OCB #33, Ok. (Found low air pressure alarm can not be reset) Not checked yet. | 3162580 | 1 | 20:20 | Night | Wednesday | 2016 | 6
2361 | 2016-06-01 20:20 | 2016-12-01 15:43 | 115KV CENTRAL DURI - BATANG LINE | Fair | Lightning Arrester | 0 | Checked & found: 115KV CDSY GCB #31 T/R 1x Ctr: 28-29. 115KV CDSY GCB #33 T/SO 1x Ctr: 586-587 R/F: Not checked yet. 115KV Sintong GCB #25 T/R 1x Ctr: Not checked yet. R/F: 87L, 67N(Inst.) & 21G (Zone-1). (115KV CDSY - Batang/Sintong line) Patrolled the line & found, @1 broken L/A jumper o/p #BTG-85A. Cause: Lightning Arrester. | 3162580 | 1 | 20:20 | Night | Wednesday | 2016 | 6
2362 | 2016-07-01 07:56 | 2016-07-01 07:56 | 13.8KV BEKASAP MAIN GFPC | Cloudy | Unidentified | 0 | Bekasap Main GFPC T/R 1x. Ground fault alarm on Bekasap fdr #2. (No load dropped at any feeders) Not checked yet. | 3162580 | 1 | 7:56 | Morning | Friday | 2016 | 7
2363 | 2016-07-01 07:56 | 14/01/2016 15:15 | 13.8KV BEKASAP MAIN GFPC | Cloudy | Unidentified | 0 | Checked & found, Bekasap GFPC T/R 1x Ctr: 337-338. Patrolled Bekasap fdr #2 line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 7:56 | Morning | Friday | 2016 | 7
2364 | 2016-07-01 08:18 | 2016-07-01 08:18 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 08:18 It was reported b/o fuse for Tx o/p #06-Q5-04B. 16:48 Checked & found: -@2,@3 b/o 2.1SF fuse & F/O FCO for 112.5 KVA Tx, and -@2,@3 broken L/As o/p #06-Q5-04B. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse, L/A & FCO above & energized the Tx. Cause: Lightning. | 3162580 | 1 | 8:18 | Morning | Friday | 2016 | 7
2365 | 2016-07-01 14:20 | 2016-07-01 14:20 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Broken Fuse Cut Out | 0 | 14:20 It was reported b/o fuse & FCO o/p #04-07-17. 17:20 Checked & found, @1 broken FCO for 112.5KVA Tx o/p #04-07-17. Then replaced broken FCO & fuse above, then energized the Tx. Cause: Fuse Cut Out. | 3162580 | 1 | 14:20 | Afternoon | Friday | 2016 | 7
2366 | 2016-07-01 15:58 | 2016-07-01 15:58 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 15:58 It was reported b/o fuse for Tx o/p #01-08-26. 16:21 Checked & found, @2 b/o 2.1SF fuse for 112.5KVA Tx o/p #01-08-26. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3162580 | 1 | 15:58 | Afternoon | Friday | 2016 | 7
2367 | 2016-07-01 19:44 | 2016-07-01 19:44 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Bangko fdr #4 load dropped 137A (266-129) (Ground fault alarm on Bangko fdr #4) Not checked yet. | 3162580 | 1 | 19:44 | Night | Friday | 2016 | 7
2368 | 2016-07-01 19:44 | 14/01/2016 15:44 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Recl. 25Y-07 (Bangko fdr #4) T/R 1x Ctr: 78-79. Patrolled the line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 19:44 | Night | Friday | 2016 | 7
2369 | 2016-08-01 08:50 | 2016-08-01 08:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 8 | 08:50 It was reported b/o fuse for Tx at Well Kulin #82. 11:45 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx at Well Kulin #82. Perform TTR & Megger test found, normal. (Good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Bat) | 3162580 | 1 | 8:50 | Morning | Monday | 2016 | 8
2370 | 2016-08-01 13:09 | 2016-08-01 13:09 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Recloser - Control Recloser | 152 | 13:09 C.Duri fdr #1 Load dropped 51A (219-168A). 13:25 It was reported no power at Puncak-GS. 15:03 Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/SO. Ctr: 226-228. Checked Recloser control & found, Malfunction. 15:10 Blocked & closed Recl. 38AS-09, Ok. Then released the Block. Patrolled the line, but found nothing. Cause: Control Recloser. (Malfunction) | 3162580 | 1 | 13:09 | Afternoon | Monday | 2016 | 8
2371 | 2016-08-01 15:00 | 2016-08-01 15:00 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 15:00 It was reported b/o fuse for Tx o/p #01-07-02. 16:04 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-07-02. Perform TTR, Megger test the Tx & found, normal. (Good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3162580 | 1 | 15:00 | Afternoon | Monday | 2016 | 8
2372 | 2016-08-01 16:34 | 2016-08-01 16:34 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 3 | 16:34 It was reported b/o fuse for Tx at Well Puncak #32. 17:20 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Puncak #32. Perform TTR, Megger test the Tx & found, normal. (Good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3162580 | 1 | 16:34 | Afternoon | Monday | 2016 | 8
2373 | 2016-08-01 18:28 | 2016-08-01 18:28 | 13.8KV S. BALAM GFPC | Fair | Unidentified | 0 | So.Balam GFPC T/R 1x. Fault alarm on So.Balam fdr #1. (No load dropped at any feeders) Not checked yet. | 3162580 | 1 | 18:28 | Afternoon | Monday | 2016 | 8
2374 | 2016-08-01 18:28 | 2016-12-01 07:53 | 13.8KV S. BALAM GFPC | Fair | Unidentified | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 198-199. Patrolled So.Balam fdr #1 line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 18:28 | Afternoon | Monday | 2016 | 8
2375 | 2016-09-01 07:21 | 2016-09-01 07:21 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | No.Duri VCB fdr #2 T/R 1x. Not checked yet. | 3162580 | 1 | 7:21 | Morning | Thursday | 2016 | 9
2376 | 2016-09-01 07:21 | 2016-12-01 16:21 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | Checked & found, No.Duri VCB fdr #2 T/R 1x Ctr: 259-260 R/F: 51N(@2). Patrolled the line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 7:21 | Morning | Thursday | 2016 | 9
2377 | 2016-10-01 20:03 | 2016-10-01 20:03 | 13.8KV BANGKO FEEDER #1 | Fair | Transformer Failure | 14 | 20:03 It was reported b/o fuse for Tx at Well BKO #146. 22:42 Checked & found, @1, @2 b/o 3.5SF fuses for 150KVA Tx at Well BKO #146. Performed TTR & Megger test, found Low Mega-ohm Reading Tx. Cause: Tx failure. (Low Mega-ohm Reading Tx) (The Tx is not replaced yet) | 3162580 | 1 | 20:03 | Night | Saturday | 2016 | 10
2378 | 2016-10-01 20:03 | 2016-11-01 09:30 | 13.8KV BANGKO FEEDER #1 | Fair | Transformer Failure | 14 | Replaced 150Kva Tx with the same size & energized the Tx. Cause: Tx failure. (Tx Low Megger reading) | 3162580 | 1 | 20:03 | Night | Saturday | 2016 | 10
2379 | 2016-11-01 14:53 | 2016-11-01 14:53 | 13.8KV MINAS FEEDER #1 | Cloudy and Lightning | Lightning | 40 | Minas ACB fdr #1 T/R 1x Ctr: 49-50 R/F: 51@1@2. Not Patrolled yet. | 3162581 | 1 | 14:53 | Afternoon | Tuesday | 2016 | 11
2380 | 2016-11-01 14:53 | 14/01/2016 08:53 | 13.8KV MINAS FEEDER #1 | Cloudy and Lightning | Lightning | 40 | Patrolled the line & found, @1,@2 broken Pin Insulators o/p #7D-18. Cause: Lightning. | 3162581 | 1 | 14:53 | Afternoon | Tuesday | 2016 | 11
2381 | 2016-12-01 10:25 | 2016-12-01 10:25 | 13.8KV DURI FIELD FEEDER #3 | Fair | Animal | 0 | 10:25 It was reported no power at Test Station-1 SW DSF Area-1. 15:00 Checked & found, @2 b/o 7.8SF fuse for 300KvaTx o/p #01-07-25. (DF fdr #3) Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3162580 | 1 | 10:25 | Morning | Thursday | 2016 | 12
2382 | 2016-12-01 16:12 | 2016-12-01 16:12 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 0 | So.Balam fdr #4 Load dropped 87A (163-75A). Ground fault Alarm at fdr #1 & fdr #4. Not checked yet. | 3162580 | 1 | 16:12 | Afternoon | Thursday | 2016 | 12
2383 | 2016-12-01 16:12 | 14/01/2016 08:15 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 17AA-43 (So.Balam fdr #4) T/R 1x Ctr: 20-21. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3162580 | 1 | 16:12 | Afternoon | Thursday | 2016 | 12
2384 | 2016-01-13 06:25 | 2016-01-13 06:25 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 06:25 It was reported b/o fuse for Tx o/p #07-T1-08. 08:50 checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T1-08. (DF fdr #2) Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (fuse). | 3162580 | 1 | 6:25 | Morning | Wednesday | 2016 | 1
2385 | 2016-01-13 09:37 | 2016-01-13 09:37 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3162580 | 1 | 9:37 | Morning | Wednesday | 2016 | 1
2386 | 2016-01-13 09:37 | 2016-01-15 16:20 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 79-80 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 9:37 | Morning | Wednesday | 2016 | 1
2387 | 2016-01-13 12:22 | 2016-01-13 12:22 | 13.8KV PINANG FEEDER #1 | Fair | Planned Maintenance | 58 | 12:22 Manually Open Pinang 13.8KV OCB fdr #1. 13:00 Manually Closed MSU 13.8KV VCB fdr #1. Transferred Load of Pinang fdr #1 to MSU fdr #1. According for Planned Maintenance of Pinang Substation. Cause: Planned Maintenance. | 123 | 1 | 12:22 | Afternoon | Wednesday | 2016 | 1
2388 | 2016-01-13 19:04 | 2016-01-13 19:04 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 416 | 19:04 Ketigul VCB fdr #2 T/SO. Ketigul GFPC in block position. 21:15 Checked & found, Ketigul VCB fdr #2 T/SO. Ctr: 192-193 R/F: 51@1,@2. 21:20 Patrolled part of line d/s of Ketigul fdr #2 (Ex Menggala fdr #2), but found nothing. 21:30 Blocked & closed Ketigul VCB fdr #2, Ok. Then released the block. Not patrolled yet. | 3162580 | 1 | 19:04 | Night | Wednesday | 2016 | 1
2389 | 2016-01-13 19:04 | 2016-01-15 16:24 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 416 | Patrolled the line & found, a dead Eagle under pole #29AM-32. Cause: Animal. (Eagle) | 3162580 | 1 | 19:04 | Night | Wednesday | 2016 | 1
2390 | 2016-01-14 14:46 | 2016-01-14 14:46 | 13.8KV 5B FEEDER #2 | Fair | Unidentified | 39 | 5B fdr #2 load dropped 169A (297-128A) Not checked yet. | 3162581 | 1 | 14:46 | Afternoon | Thursday | 2016 | 1
2391 | 2016-01-14 14:46 | 2016-01-20 07:13 | 13.8KV 5B FEEDER #2 | Fair | Unidentified | 39 | Checked & found, Recl. 5C-47 (5B fdr #2) T/R 1x Ctr: 46-47. Patrolled the line, but nothing found. Cause: Unidentified. | 3162581 | 1 | 14:46 | Afternoon | Thursday | 2016 | 1
2392 | 2016-01-14 17:25 | 2016-01-14 17:25 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Unidentified | 0 | C.Duri ACB fdr #11 T/R 1x Ctr: 251-252 R/F: 51N. Not patrolled yet. | 3162580 | 1 | 17:25 | Afternoon | Thursday | 2016 | 1
2393 | 2016-01-14 17:25 | 2016-01-16 17:25 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 17:25 | Afternoon | Thursday | 2016 | 1
2394 | 2016-01-14 17:50 | 2016-01-14 17:50 | 13.8KV SURAM FEEDER #1 | Fair | Guy Wire | 0 | 17:50 Suram OCB fdr #1 T/LO. 19:15 Checked & found, Suram OCB fdr #1 T/LO. Ctr: 89-93 R/F: 51N. Patrolled the line & found, broken Guy Wire & touching @1 jumper of metering o/p #SK-02. 19:55 Then dismantled Guy Wire o/p #SK-02. (After opening both side Isolation switches of Suram OCB fdr #1) 20:00 Closed both side isolation switches of Suram OCB fdr #1. 20:09 Blocked & closed Suram OCB fdr #1, Ok. Then release the block. Cause: Broken Guy Wire. | 3162581 | 1 | 17:50 | Afternoon | Thursday | 2016 | 1
2395 | 2016-01-14 21:21 | 2016-01-14 21:21 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 28 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3162581 | 1 | 21:21 | Night | Thursday | 2016 | 1
2396 | 2016-01-14 21:21 | 2016-01-16 19:21 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 28 | Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1254-1255 R/F: 51N. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3162581 | 1 | 21:21 | Night | Thursday | 2016 | 1
2397 | 2016-01-14 21:37 | 2016-01-14 21:37 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 57 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3162580 | 1 | 21:37 | Night | Thursday | 2016 | 1
2398 | 2016-01-14 21:37 | 2016-01-21 09:19 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 57 | Checked & found, Batang OCB fdr #3 T/R 2x Ctr: 302-304 R/F: 51N(@1). Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3162580 | 1 | 21:37 | Night | Thursday | 2016 | 1
2399 | 2016-01-14 21:54 | 2016-01-14 21:54 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | 21:54 Duri Community fdr #3 Load dropped 37A (112-75A). 22:15 Checked & found, 4160V Recloser at Singgalang Mini Subst. T/O. Ctr: 218-219. Also found: -@3 Broken Bushing of 4160V Reloser at Singgalang Mini Subst. -a dead Civet on the 4160V Recloser at Singgalang Mini Subst. 22:22 Blocked & closed 4160V Recloser, Ok. Then release the block. (After removing a dead Civet above) Cause: Animal. (Civet) | 3162580 | 1 | 21:54 | Night | Thursday | 2016 | 1
2400 | 2016-01-15 10:53 | 2016-01-15 10:53 | 13.8KV 6DN FEEDER #5 | Fair | Others | - | 10:54 6D fdr #3 Load dropped 207A (318-111A). T/O Some WIPs at Minas GS-3. 6DN fdr #3 Load dropped 198A (200-2A). T/O Some WIPs at Minas GS-3. (Minas GS-3 failed to Re-S/U the WIPs above) Cause: 4.16KV Breaker control for WIP problem. To Anticipate Spill at Minas GS-3: 13:37 Minas GS-3 asked DSC to S/D some wells at downstream of 6DN fdr #5 & fdr #6. (Load of 6DN fdr #5 were transferred to Minas fdr #5), and (Load of 6DN fdr #6 were transferred to 4D fdr #5) 14:25 Manually open Recl. 6D-16A & Open LBS #6D-16. (Minas fdr #5) 18:30 Manually open LBS #36DN-32B (4D fdr #5). Minas GS-3 asked DSC to normalize load of 6DN fdr #5 & 6DN fdr #6. (After EQR team, solving the problem of Breaker control for the WIP) 21:15 Closed LBS #36DN-32B (4D fdr #5) 21:30 Closed LBS #6D-16. (Minas fdr #5) 16-Jan-2016. 09:21 Closed Recl. 6D-16A. (Minas fdr #5) (No Production loss charged to PGT) | 3162581 | 1 | 10:53 | Morning | Friday | 2016 | 1
2401 | 2016-01-15 21:14 | 2016-01-15 21:14 | 13.8KV 5B FEEDER #8 | Rain and Lightning | Lightning | 0 | 5B OCB fdr #8 T/R 1x. Not checked yet. | 3162581 | 1 | 21:14 | Night | Friday | 2016 | 1
2402 | 2016-01-15 21:14 | 2016-01-20 07:13 | 13.8KV 5B FEEDER #8 | Rain and Lightning | Lightning | 0 | Checked & found 5B OCB fdr #8 T/R 1x Ctr: 99950-99951 R/F: 51@1. Patrolled the line & found, @1,@2 broken Dead end Insulators o/p #M5B-30. Cause: Lightning. | 3162581 | 1 | 21:14 | Night | Friday | 2016 | 1
2403 | 2016-01-15 21:14 | 2016-01-15 21:14 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 12 | 5B fdr #4 Load dropped 236A (259-23A). 5B fdr #5 Load dropped 18A (18-0A). Not checked yet. | 3162581 | 1 | 21:14 | Night | Friday | 2016 | 1
2404 | 2016-01-15 21:14 | 2016-01-21 10:41 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 12 | Checked & found, Recl. 4B-73 (5B fdr #4) T/R 1x Ctr: 48-49. Patrolled the line & found, @1 broken jumper of Cap. Bank near OBS Well #4C-21. Cause: Lightning. | 3162581 | 1 | 21:14 | Night | Friday | 2016 | 1
2405 | 2016-01-16 06:27 | 2016-01-16 06:27 | 13.8KV KETIGUL FEEDER#2 | Fair | Broken Fuse Holder | 100 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3162580 | 1 | 6:27 | Morning | Saturday | 2016 | 1
2406 | 2016-01-16 06:27 | 2016-01-21 13:56 | 13.8KV KETIGUL FEEDER#2 | Fair | Broken Fuse Holder | 100 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 197-198 R/F: 51N. Patrolled the line & found, @1 broken Fuse holder for Tx at Well Pagar #35. Cause: Broken Fuse Holder. | 3162580 | 1 | 6:27 | Morning | Saturday | 2016 | 1
2407 | 2016-01-16 22:03 | 2016-01-16 22:03 | 13.8KV S. BALAM FEEDER #4 | Fair | Dead End Insulator | 0 | So.Balam fdr #4 Load dropped 42A (161-119A). So.Balam GFPC T/R 1x. Not checked yet. | 3162580 | 1 | 22:03 | Night | Saturday | 2016 | 1
2408 | 2016-01-16 22:03 | 2016-01-18 15:36 | 13.8KV S. BALAM FEEDER #4 | Fair | Dead End Insulator | 0 | Checked & found, Recl. 17AA-43 (So.Balam fdr #4) T/R 1x Ctr: 20-21. Also found, So.Balam GFPC T/R 2x Ctr: 199-201. Patrolled the line & found, @3 broken Pin Insulator o/p #17AA-47. Cause: Broken Dead end insulator. | 3162580 | 1 | 22:03 | Night | Saturday | 2016 | 1
2409 | 2016-01-17 08:25 | 2016-01-17 08:25 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified | 168 | 08:25 C.Duri fdr #1 load dropped 56A (223-167A). 10:17 Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/O. Ctr: 228-229. (In block position) Patrolled the line (near resident village), but found nothing. 10:56 Blocked & closed Recl. 38AS-09, Ok. Then released the block. (need to re-patrolled all power line d/s this Recloser) | 3162580 | 1 | 8:25 | Morning | Sunday | 2016 | 1
2410 | 2016-01-17 08:25 | 2016-01-19 13:17 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified | 168 | Completed Patrolling the line at downstream of Recl. 39AS-09, but nothing found. Cause: Unidentified. | 3162580 | 1 | 8:25 | Morning | Sunday | 2016 | 1
2411 | 2016-01-17 15:10 | 2016-01-17 15:10 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain | Unidentified (Fuse) | 24 | 15:10 It was reported b/o fuse for Tx at Well KB #226. Checked & found, @1 b/o 7.8SF fuse for 300KVA Tx at Well KB #226. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3162581 | 1 | 15:10 | Afternoon | Sunday | 2016 | 1
2412 | 2016-01-18 08:51 | 2016-01-18 08:51 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 47 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3162580 | 1 | 8:51 | Morning | Monday | 2016 | 1
2413 | 2016-01-18 08:51 | 2016-01-21 10:52 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 47 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 303-304 R/F: 50N. Patrolled the line, but nothing found. Cause: Unidentified. | 3162580 | 1 | 8:51 | Morning | Monday | 2016 | 1
2414 | 2016-01-18 11:38 | 2016-01-18 11:38 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 2 | 11:38 It was reported b/o fuse of TX o/p #09-R2-04 (CD fdr#4). 14:02 Checked and found, @1, @2 b/o fuse for 112.5KVA TX. Performed TTR & Megger Test the TX, found good reading. Replaced b/o fuse above with same size then energized the TX. Cause: Unidentified (fuse). | 3162580 | 1 | 11:38 | Morning | Monday | 2016 | 1
2415 | 2016-01-18 11:39 | 2016-01-18 11:39 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 6 | 11:39 It was reported b/o fuse for Tx at Well Kulin # 49 & #91. 16:00 Checked & found, @2 b/o 1.4SF fuse for 75Kva Tx at Well Kulin #49 & #91. Performed TTR, Megger test the Tx & found, good reading. Replaced b/o fuse above with same size then energized the Tx. Cause: Animal. (Bird) | 3162580 | 1 | 11:39 | Morning | Monday | 2016 | 1
2416 | 2016-01-18 16:07 | 2016-01-18 16:07 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 1 | 16:07 It was reported b/o fuse o/p 03-0-13 (d/s CD fdr#6). 18:23 Checked and found, @2 b/o fuse for 112.5KVA TX. Performed TTR & Megger Test the Tx, found good reading. Replaced b/o fuse above with same size then energized the tx. Cause: Unidentified (fuse). | 3162580 | 1 | 16:07 | Afternoon | Monday | 2016 | 1
2417 | 2016-01-18 22:55 | 2016-01-18 22:55 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 0 | 22:55 It was reported b/o fuse at well Pagar#35. Not checked yet. | 3162580 | 1 | 22:55 | Night | Monday | 2016 | 1
2418 | 2016-01-18 22:55 | 2016-01-19 16:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 0 | Checked & found, @1, @2, @3 b/o fuse for 225KVA Tx at well Pagar #35. Performed TTR & Megger Test the Tx, found Zero-Meg Tx. Cause: Transformer Failure. (Will be replaced tomorrow). | 3162580 | 1 | 22:55 | Night | Monday | 2016 | 1
2419 | 2016-01-19 04:56 | 2016-01-19 04:56 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 42 | So.Bekasap fdr #1 load dropped 151A (177-26A). Not checked yet. | 3162580 | 1 | 4:56 | Morning | Tuesday | 2016 | 1
2420 | 2016-01-19 04:56 | 2016-01-21 09:24 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 42 | Checked & found, Recl. 36BI-04 (So.Bekasap fdr #1) T/R 2x Ctr: 732-734. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3162580 | 1 | 4:56 | Morning | Tuesday | 2016 | 1
2421 | 2016-01-19 08:23 | 2016-01-19 08:23 | 13.8KV KETIGUL FEEDER#2 | Rain | Unidentified | 681 | 08:23 Ketigul VCB fdr#2 T/LO. 10:41 Checked and found, Ketigul VCB fdr#2 T/LO Ctr:193-198 R/F: 51N. Patrol the line and found nothing. 11:30 Opened LBS #24AL-05 to separated load. 11:43 Blocked and closed Ketigul VCB fdr#2. ok. 11:46 Closed LBS #24AL-05 and then Normalized block of Ketigul fdr#2. Cause: Unidentified. | 3162580 | 1 | 8:23 | Morning | Tuesday | 2016 | 1
2422 | 2016-01-19 09:05 | 2016-01-19 09:05 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 95 | 09:05 It was reported no power at one road, nearest pole #08-L3-02. (d/s CD fdr#1) 10:20 Checked and found, Recl. 08-L3-32 T/SO Ctr:493-494. Patrolled the line & found nothing. 11:03 Blocked & closed Recl. 08-L3-32, ok, then released the block. Cause: Unidentified. | 3162580 | 1 | 9:05 | Morning | Tuesday | 2016 | 1
2423 | 2016-01-19 13:17 | 2016-01-19 13:17 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Lightning | 0 | Duri Community ACB fdr #1 T/R 1x Ctr: 80-81 R/F: 51@3. Not patrolled yet. | 3162580 | 1 | 13:17 | Afternoon | Tuesday | 2016 | 1
2424 | 2016-01-19 13:17 | 2016-01-21 09:05 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Lightning | 0 | Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3162580 | 1 | 13:17 | Afternoon | Tuesday | 2016 | 1
2425 | 2016-01-19 13:17 | 2016-01-19 13:17 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Lightning | 0 | Duri Community ACB fdr #3 T/R 1x Ctr: 48-49 R/F: 51N. Not patrolled yet. | 3162580 | 1 | 13:17 | Afternoon | Tuesday | 2016 | 1
2426 | 2016-01-19 13:17 | 2016-01-21 09:20 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Lightning | 0 | Patrolled the line & found, @1 broken L/A o/p #6F-10. (at Komplek Guru) Cause: Lightning. | 3162580 | 1 | 13:17 | Afternoon | Tuesday | 2016 | 1
2427 | 2016-01-19 14:27 | 2016-01-19 14:27 | MOBILE SUBSTATION 2 | Heavy Rain | Under investigation | 178 | 14:27 115KV MSU #2 C/S (to Pinang SS) T/O. 16:10 Checked and found, 115KV MSU#2 C/S (to Pinang SS) T/O Ctr:290-291 R/F: 86T and 51N (W2). Reset all R/F and opened MSU #2 VCB #1 (to Pinang fdr #1). 16:29 Closed MSU #2 C/S. ok. 16:30 Closed MSU #2 VCB #1 (to Pinang fdr #1). Cause: Under Investigation. | 3162580 | 1 | 14:27 | Afternoon | Tuesday | 2016 | 1
2428 | 2016-01-19 21:22 | 2016-01-19 21:22 | 13.8KV NORTH DURI FEEDER #7 | Fair | Animal | 0 | 21:22 It was reported b/o fuse for Tx at Area 10 SE Test Station. 23:50 Checked & found, @1 b/o fuse for 1000KVA Tx. Performed TTR & Megger Test the Tx, found good reading. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal (Monkey). | 3162580 | 1 | 21:22 | Night | Tuesday | 2016 | 1
2429 | 2016-01-20 16:28 | 2016-01-20 16:28 | 13.8KV 5B FEEDER #5 | Fair | Transformer Failure | 13 | 16:28 It was reported b/o fuse for TX at Well #4B-75. (5B fdr #5) 18:10 Checked & found, @1,@2,@3 b/o 14.0SF fuses for 550Kva Tx at Well #4B-75. Tested the Tx & found, zero megger reading. Cause: Tx failure. (Zero megger reading) (The Tx is not replaced yet, due to Lifting equipment problem) | 3162581 | 1 | 16:28 | Afternoon | Wednesday | 2016 | 1
2430 | 2016-01-20 16:28 | 2016-01-02 10:00 | 13.8KV 5B FEEDER #5 | Fair | Transformer Failure | 13 | Replaced 550Kva Tx failure with the same size then energized the Tx at Well #4B-75. Cause: Tx failure. (Zero megger reading) | 3162581 | 1 | 16:28 | Afternoon | Wednesday | 2016 | 1
2431 | 2016-01-21 02:33 | 2016-01-21 02:33 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 144 | 02:23 Sintong OCB fdr#1 T/O. Sintong GFPC T/R 1x Ground fault Alarm on Sintong fdr#1 04:16 Checked & found Sintong OCB fdr#1 T/O Ctr: 379-380 R/F: 51N. Patrolled the Line and found Dead Animal (Civet) at Bushing OCB. Removed the civet from bushing OCB fdr #1. Blocked & Closed Sintong OCB # fdr#1 and then Released the Block Cause : Animal (Civet). | 3162580 | 1 | 2:33 | Night | Thursday | 2016 | 1
2432 | 2016-01-21 10:39 | 2016-01-21 10:39 | 13.8KV LIBO FEEDER #1 | Cloudy | Unidentified | 8 | Libo OCB fdr #1 T/R 1x Ctr: 361-362 R/F: 51N. Patrol the line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 10:39 | Morning | Thursday | 2016 | 1
2433 | 2016-01-21 12:51 | 2016-01-21 12:51 | DARLING SUBSTATION | Fair | Under investigation | - | 12:51 Darling 115 kv GCB#2 T/O. Darling 115 kv GCB#24T/O. 13:03 Darling GFPC TX#1 T/O. 13:28 Checked and found Indokomas (under Project team) crew upgrading relay Firmware causes Darling GCB#2, Darling GCB#4 and Darling GFPC TX#1 T/O. Reset all relay. 14:16 Closed Darling 115 kv GCB#2 14:18 Closed Darling 115 kv GCB#4 14:20 Closed Darling GFPC TX#1 Cause: Under Investigation. | 3162580 | 1 | 12:51 | Afternoon | Thursday | 2016 | 1
2434 | 2016-01-22 09:14 | 2016-01-22 09:14 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning Arrester | 0 | Menggala fdr #1 load dropped 36A (159-123A). Menggala GFPC. (in block posisiton) Ground fault alarm on Menggala fdr #1. Not checked yet. | 3162580 | 1 | 9:14 | Morning | Friday | 2016 | 1
2435 | 2016-01-22 09:14 | 2016-01-23 14:12 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning Arrester | 0 | Checked & found, Recl. 19AO-01 (Menggala fdr #1) T/R 1x Ctr: 450-451. Patrolled the line & found, @3 broken L/A on TP of Well Meso #01. Cause: Lightning Arrester. | 3162580 | 1 | 9:14 | Morning | Friday | 2016 | 1
2436 | 2016-01-22 14:00 | 2016-01-22 14:00 | 13.8KV MINAS FEEDER #5 | Fair | Transformer Failure | 35 | 14:00 It was reported b/o fuse for Tx at Well #6D-48E. 15:25 Checked & found, @2 b/o 7.8SF fuse for 300KVa Tx at Well #6D-48E. Performed TTR, Megger test the Tx & found, Low Mega-ohm Reading Tx. Cause: Tx failure. (Low Mega-ohm Reading Tx) (The Tx is not replaced yet) | 3162581 | 1 | 14:00 | Afternoon | Friday | 2016 | 1
2437 | 2016-01-22 14:00 | 2016-01-27 14:00 | 13.8KV MINAS FEEDER #5 | Fair | Transformer Failure | 35 | Replaced 300Kva Tx failure with the same size & energized the Tx at Well #6D-48E. Cause: Tx failure. (Low megger reading) | 3162581 | 1 | 14:00 | Afternoon | Friday | 2016 | 1
2438 | 2016-01-22 16:05 | 2016-01-22 16:05 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Recloser | 0 | 16:04 Duri Community RTU failed. (It was reported no power at IT Tower, Beta, REM & Kutilang Office) 16:35 Checked & found, 13.8KV Recl. SMN at Singgalang Mini Subst. T/O Ctr: 218-219. (Also found, @1, @2, @3 broken Recloser bushing) 16:47 Checked all 13.8KV VCB at Duri Community & found, normal. (All Breaker are close position, No counter changed & no R/F appear) 18:25 Closed 13.8KV Recl. SMN at Singgalang Mini SS, Ok. (After replacing broken Recloser Bushing above) Cause: Broken Recloser bushing. | 3162580 | 1 | 16:05 | Afternoon | Friday | 2016 | 1
2439 | 2016-01-22 19:30 | 2016-01-22 19:30 | 13.8KV S. BALAM FEEDER #1 | Fair | Lightning Arrester | 0 | So.Balam fdr #1 Load dropped 64A (98-34A). So.Balam GFPC T/R 1x. Not checked yet. | 3162580 | 1 | 19:30 | Night | Friday | 2016 | 1
2440 | 2016-01-22 19:30 | 2016-01-23 15:37 | 13.8KV S. BALAM FEEDER #1 | Fair | Lightning Arrester | 0 | Checked & found, Recl. 16Z-25 (So.Balam fdr #1) T/R 1x Ctr: 20-21. Patrolled the line & found, @3 broken L/A on TP of Well So.Balam #136. Cause: Lightning Arrester. | 3162580 | 1 | 19:30 | Night | Friday | 2016 | 1
2441 | 2016-01-23 15:25 | 2016-01-23 15:25 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 15:25 It was reported b/o fuse for Tx o/p 13-H5-07. 17:09 Checked & found, @2 b/o fuse for 112.5KVa Tx. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3162580 | 1 | 15:25 | Afternoon | Saturday | 2016 | 1
2442 | 2016-01-23 18:00 | 2016-01-23 18:00 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified | 0 | N.Duri VCB fdr #8 T/R 1x. N.Duri GFPC-TX #12. (did not operate) Not checked yet. | 3162580 | 1 | 18:00 | Afternoon | Saturday | 2016 | 1
2443 | 2016-01-23 18:00 | 2016-01-25 16:40 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified | 0 | Checked & found, N.Duri VCB fdr #8 T/R 1x Ctr: 57-58 R/F: 51N. Patrolled the line, but nothing found. Cause: Unidentified. | 3162580 | 1 | 18:00 | Afternoon | Saturday | 2016 | 1
2444 | 2016-01-23 18:54 | 2016-01-23 18:54 | 13.8KV 5B FEEDER #2 | Fair | Dead End Insulator | 38 | 5B OCB fdr #2 T/R 1x. Not checked yet. | 3162581 | 1 | 18:54 | Afternoon | Saturday | 2016 | 1
2445 | 2016-01-23 18:54 | 2016-01-24 15:21 | 13.8KV 5B FEEDER #2 | Fair | Dead End Insulator | 38 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 334-335 R/F: 51N. Patrolled the line & found, @1, @3 broken Dead end Insulators o/p #4C-59. Cause: Dead end insulator. | 3162581 | 1 | 18:54 | Afternoon | Saturday | 2016 | 1
2446 | 2016-01-24 04:16 | 2016-01-24 04:16 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 141 | 04:05 Bekasap Main fdr #2 load dropped 187A (240-53A). Not checked yet. 04:16 Bekasap Main OCB fdr #2 T/R 1x. Bekasap Main GFPC-TX #C T/R 1x. Not checked yet. | 3162580 | 1 | 4:16 | Morning | Sunday | 2016 | 1
2447 | 2016-01-24 04:16 | 2016-01-27 18:19 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 141 | Checked & found, Bekasap OCB fdr #2 T/R 1x Ctr: 871-872 R/F: 51@2,@3. Patrolled the line & found, @2,@3 broken L/A on TP of Well Pematang #15. Cause: Lightning. | 3162580 | 1 | 4:16 | Morning | Sunday | 2016 | 1
2448 | 2016-01-24 06:57 | 2016-01-24 06:57 | MOBILE SUBSTATION 2 | Rain | Lightning Arrester | 237 | 06:57 115KV MSU-Pinang C/S T/O. 09:16 Checked & found, 115KV MSU-Pinang C/S T/O Ctr: 291-292 R/F: 86T, 87T @1,@2,@3. Also found, 13.8KV MSU-Pinang VCB fdr #1 T/R 1x Ctr: 201-202 R/F: 50@1,@2,@3. Visual checked all equipment at MSU & found, normal. 09:25 Manual Opened 13.8KV MSU-Pinang VCB fdr #1. 09:26 Closed 115KV MSU-Pinang C/S, Ok. 09:29 Blocked & closed 13.8KV MSU-Pinang VCB fdr #1, Ok. Then released the block. Cause: Under Investigation. (Pinang VCB fdr #1 is not patrolled yet) | 3162580 | 1 | 6:57 | Morning | Sunday | 2016 | 1
2449 | 2016-01-24 06:57 | 2016-01-25 10:57 | MOBILE SUBSTATION 2 | Rain | Lightning Arrester | 237 | Patrolled Pinang fdr #1 line & found, @2 broken L/A on TP of Well Pinang #12. Cause: Lightning Arrester. | 3162580 | 1 | 6:57 | Morning | Sunday | 2016 | 1
2450 | 2016-01-24 09:09 | 2016-01-24 09:09 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 0 | C.Duri fdr #1 load dropped 49A (229-180A). Not checked yet. | 3162580 | 1 | 9:09 | Morning | Sunday | 2016 | 1
2451 | 2016-01-24 09:09 | 2016-01-25 16:41 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 2x Ctr: 203-205. Patrolled the line & found, @3 broken Lightning Arrester o/p #41AW-54. Cause: Lightning. | 3162580 | 1 | 9:09 | Morning | Sunday | 2016 | 1
2452 | 2016-01-24 09:32 | 2016-01-24 09:32 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 48 | 09:32 It was reported b/o fuse for Tx at Well Pagar #31. (Ketigul fdr #2) 15:00 Checked & found, @1, @2 b/o 3.1SF fuses for 225KVA Tx at Well Pagar #31. Performed TTR, Megger Test the Tx & found, Low Mega-ohm Reading. Cause: Tx failure. (Low Mega-ohm Reading) (The Tx is not replaced yet) | 3162580 | 1 | 9:32 | Morning | Sunday | 2016 | 1
2453 | 2016-01-24 09:32 | 2016-01-27 14:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 48 | Replaced 225Kva Tx failure with 250Kva Tx & energized the Tx at Well Pagar #31. Cause: Tx failure. (Low megger reading) | 3162580 | 1 | 9:32 | Morning | Sunday | 2016 | 1
2454 | 2016-01-24 17:42 | 2016-01-24 17:42 | MINAS SWITCH YARD | Fair | Substation Failure (CT) | 0 | 17:42 Mns switch yard 13.8/115KV TX #9 Trip Off. MGT#9 Open Gen. Breaker by Alarm Bus Under Voltage Frequency 59.84 Hz, No Load shedding. Also Trip Off : 115kv Minas GCB # 61 T/o. Connecting to Mns TX #9 115kv Minas GCB # 63 T/o. Connecting to Mns TX #9 115kv Minas GCB # 10 T/o. Tie Line 2 Bus #3 & Bus #4 115kv Minas GCB # 71 T/o. Connecting to Mns TX #10, Bus #3 & Bus #4 115kv Minas GCB # 65 T/o. Connecting to 6D substation & Bus #4 115kv Minas GCB # 51 T/o. Connecting to 5B substation & Bus #3 115kv Minas GCB # 41 T/o. Connecting to Mns TX #7 & Bus #3 18:30 MGT #9 S/D for Not S/B. 19:00 Checked & found 13.8/115KV TX #9 Mns Switch Yard was Trip Off. Liquid Temp 50/85, Winding Temp 60/60. R/F 87T, 86T and 50P. No Relay Flag at Bus #3, Bus #4, 6D Line, and 5B Line. 19:10 Open Isolation Switch Mns TX #9 Reset 87T and 86T 19:28 Closed 115kv Minas GCB # 10 (Ctr: 45-46) Closed 115kv Minas GCB # 71 (Ctr: 134-135) Closed 115kv Minas GCB # 61 (Ctr: 109-110) Closed 115kv Minas GCB # 63 (Ctr: 257-258) Closed 115kv Minas GCB # 65 (Ctr: 240-241) Closed 115kv Minas GCB # 51 (Ctr: 177-178) Closed 115kv Minas GCB # 41 (Ctr: 93-94) Cause : Under Investigation | 3162581 | 1 | 17:42 | Afternoon | Sunday | 2016 | 1
2455 | 2016-01-25 08:55 | 2016-01-25 08:55 | MINAS POWER PLANT | Fair |  | - | 08:55 S/U MGT #1, then online the Unit at 09:12. 09:20 Opened ACB #25. (Tie Breaker) |  | 1 | 8:55 | Morning | Monday | 2016 | 1
2456 | 2016-01-25 09:03 | 2016-01-25 09:03 | 6 DELTA NEW SUBSTATION | Fair | Others | 0 | 115KV 6DN C/S-2 T/O. Ctr: 513-514 R/F: Not reported yet . (Tx under monitoring after service, no load under this Tx) Cause: Under Investigation. | 3162581 | 1 | 9:03 | Morning | Monday | 2016 | 1
2457 | 2016-01-25 09:03 | 2016-03-02 16:00 | 6 DELTA NEW SUBSTATION | Fair | Others | 0 | Checked & found, Air Trapped at the Bucholz relay. Cause: Others. (Accumulation Air Trapped when the Tx energized for warming after servicing) | 3162581 | 1 | 9:03 | Morning | Monday | 2016 | 1
2458 | 2016-01-25 11:12 | 2016-01-25 11:12 | 44KV NORTH DURI - DUMAI LINE | Fair | Unidentified | 0 | 11:12 Dumai RTU failed at this time. (ND RTU Failed since Jan, 24th, 2016 at 09:29 AM). It was reported power outage at Industrial feeder Dumai. 13:30 Checked & found, no R/F & no counter changed for all breaker at Dumai SS. 15:25 Checked & found, 44KV No.Duri GCB #1 (Line to Dumai) T/R 1x Ctr: 103-104 R/F: 51@2,@3. Not patrolled yet. | 3162580 | 1 | 11:12 | Morning | Monday | 2016 | 1
2459 | 2016-01-25 11:12 | 2016-01-27 09:16 | 44KV NORTH DURI - DUMAI LINE | Fair | Unidentified | 0 | Patrolled the line, but nothing found. Cause: Unidentified. | 3162580 | 1 | 11:12 | Morning | Monday | 2016 | 1
2460 | 2016-01-25 15:43 | 2016-01-25 15:43 | 13.8KV 3D FEEDER #3 | Fair | Transformer Failure | 35 | 15:43 It was reported b/o fuse for Tx at Well #4C-38N. (3D fdr #3) 18:00 Checked & found, @1, @2 b/o 3.5SF fuses for 150Kva Tx at Well #4C-38N. Performed TTR, Megger Test the Tx & found, Zero Megger Reading. Cause: Transformer Failure. (The Tx is not replaced yet) | 3162581 | 1 | 15:43 | Afternoon | Monday | 2016 | 1
2461 | 2016-01-25 15:43 | 2016-01-27 16:25 | 13.8KV 3D FEEDER #3 | Fair | Transformer Failure | 35 | Replaced 150Kva Tx failure with the same size & energized the Tx at Well #4C-38N. Cause: Tx failure. (Low megger reading) | 3162581 | 1 | 15:43 | Afternoon | Monday | 2016 | 1
2462 | 2016-01-25 18:21 | 2016-01-25 18:21 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified (Fuse) | 25 | Rangau fdr #2 load dropped 77A (88-11A). Not checked yet. | 3162580 | 1 | 18:21 | Afternoon | Monday | 2016 | 1
2463 | 2016-01-25 18:21 | 2016-01-26 17:59 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified (Fuse) | 25 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: 125-126. Patrolled the line & found, @1,@2 b/o fuse for 150Kva Tx at Well Jurong #01. Cause: Unidentified (Fuse). | 3162580 | 1 | 18:21 | Afternoon | Monday | 2016 | 1
2464 | 2016-01-26 14:54 | 2016-01-26 14:54 | 13.8KV NORTH DURI FEEDER #10 | Fair | Planned Maintenance | 0 | 14:54 S/D 1500KVA Tx at AWT Area-11, then opened HLC o/p #11-H5-10. to repairing @1 hotspot of FCO. 16:15 Closed HLC, then energized the Tx. Cause: Planned Maintenance. | 123 | 1 | 14:54 | Afternoon | Tuesday | 2016 | 1
2465 | 2016-01-26 17:54 | 2016-01-26 17:54 | 13.8KV LIBO FEEDER #2 | Cloudy and Lightning | Lightning | 7 | Libo fdr #2 load dropped 29A (49-20A). Not checked yet. | 3162580 | 1 | 17:54 | Afternoon | Tuesday | 2016 | 1
2466 | 2016-01-26 17:54 | 2016-01-27 10:54 | 13.8KV LIBO FEEDER #2 | Cloudy and Lightning | Lightning | 7 | Checked & found, Recl. 23BW-02 (Libo fdr #2) T/R 1x Ctr: 226-227. Patrolled the line & found: -@2 Burnt out fuse for 150Kva Tx at Well Waduk #14. -@2 Broken Pin Insulator o/p #22BV-09. -@2,@3 Broken Pin Insulators o/p #21BU-09. -@3 Broken Pin Insualtor o/p #21BV-06. -@1 Broken Pin Insulators o/p #22BV-11, 21BV-02 & 21BV-05. Cause: Lightning. | 3162580 | 1 | 17:54 | Afternoon | Tuesday | 2016 | 1
2467 | 2016-01-26 18:13 | 2016-01-26 18:13 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 45 | Batang OCB fdr #3 T/R 1x. (Batang GFPC in block position) Not checked yet. | 3162580 | 1 | 18:13 | Afternoon | Tuesday | 2016 | 1
2468 | 2016-01-26 18:13 | 2016-01-27 15:00 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 45 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 304-305 R/F: 50N. Patrolled the line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 18:13 | Afternoon | Tuesday | 2016 | 1
2469 | 2016-01-27 09:50 | 2016-01-27 09:50 | DURI POWER PLANT |  |  | - | 09:50 S/U DGT #7, then Online the Unit at 10:25. |  | 1 | 9:50 | Morning | Wednesday | 2016 | 1
2470 | 2016-01-27 13:45 | 2016-01-27 13:45 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Recloser - Control Recloser | 0 | So.Bekasap fdr #1 Load dropped 10A (180-170A). 13:45 It was reported no power at So.Bekasap-GS. 15:22 Checked & found, Recl. 37BG-48 (So.Bekasap fdr #1) T/SO. Ctr: 33. (Did not change) Blocked & closed Recl. 37BG-48, but failed. Checked the Recloser control & patroled the line, but nothing found. 16:42 Closed Recl. 37BG-48 by jumpering closing circuit of the Recloser control, Ok. (Then bypassing the Recloser by unplugging Recloser control cable) Cause: Recloser Control Problem. | 3162580 | 1 | 13:45 | Afternoon | Wednesday | 2016 | 1
2471 | 2016-01-27 17:45 | 2016-01-27 17:45 | MINAS SWITCH YARD | Drizzle | Substation Failure (CT) | 195 | 115 KV GCB # 10 T/O. Ctr: 46-47 Closed at: 21:23 (115KV Tie Bus#3 & Bus#4) 115 KV GCB # 41 T/O. Ctr: 94-95 Closed at: 21:21 115 KV GCB # 51 T/O. Ctr: 178-179 Closed at: 21:19 115 KV GCB # 61 T/O. Ctr: 210-212 115 KV GCB # 63 T/O. Ctr: 258-260 115 KV GCB # 65 T/O. Ctr: 241-242 Closed at: 21:12 (115KV line to 6D) 115 KV GCB # 71 T/O. Ctr: 130-131 Closed at: 21:16 Checked & found: Minas SWY Tx-9 Tripped by Relay: 87 Tx #9-@1 & 86 Tx #9. 86 - 61 (GCB) & 86 - 63 (GCB). And found, 115KV Minas SWY Bus-3 no power. (Breaker failure pickup) Cause: Under Investigation. 27 Jan 2016 Production loss: Planned to S/D NDC-2 for Off line wash. GS #1 : 15 Bbls 12 wells. GS #2 : 58 Bbls 22 wells. GS #3 : 22 Bbls 9 wells. GS #4 : 7 Bbls 3 wells. GS #5 : 41 Bbls 19 wells. GS #6 : 47 Bbls 26 wells. ------------------------------------------ Total : 190 Bbls 91 wells. | 3162581 | 1 | 17:45 | Afternoon | Wednesday | 2016 | 1
2472 | 2016-01-27 20:18 | 2016-01-27 20:18 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 5 | Sintiong fdr #2 load dropped 95A (194-99A). Sintong GFPC T/R 1x. Not checked yet. | 3162580 | 1 | 20:18 | Night | Wednesday | 2016 | 1
2473 | 2016-01-27 20:18 | 2016-01-30 10:00 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 5 | Checked & found, Recl. 28AF-17 (Sintong fdr #2) T/R 1x Ctr: 248-249. Sintong GFPC T/R 1x. Ctr: Is not reported yet. Patrolled the line & found, @3 broken Dead end Insulator o/p #28AF-28. Cause: Lightning. | 3162580 | 1 | 20:18 | Night | Wednesday | 2016 | 1
2474 | 2016-01-28 16:14 | 2016-01-28 16:14 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Lightning Arrester | 0 | C.Duri ACB fdr #15 T/R 1x Ctr: 360-361 R/F: 50@1,@2,@3. Not patrolled yet. | 3162580 | 1 | 16:14 | Afternoon | Thursday | 2016 | 1
2475 | 2016-01-28 16:14 | 2016-01-02 17:14 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Lightning Arrester | 0 | Patrolled the line & found, @3 broken L/A o/p #05-Q5-11A. Cause: Lightning Arrester. Also found, Recl. 06-P7-24 (C.duri fdr #15) T/R 1x Ctr: 61-62. Patrolled the line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 16:14 | Afternoon | Thursday | 2016 | 1
2476 | 2016-01-28 17:43 | 2016-01-28 17:43 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 15 | Libo fdr #2 Load dropped 27A (48-21A). Not checked yet. | 3162580 | 1 | 17:43 | Afternoon | Thursday | 2016 | 1
2477 | 2016-01-28 17:43 | 2016-01-31 15:43 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 15 | Checked & found, Recl. 23BW-02 (Libo fdr #2) T/R 2x Ctr: 227-229. Patrolled the line & found: -@2 Burnt out fuse for 150Kva Tx at Well Waduk #14. -@2 Broken Pin Insulator o/p #22BV-09. -@2,@3 Broken Pin Insulators o/p #21BU-09. -@3 Broken Pin Insualtor o/p #21BV-06. -@1 Broken Pin Insulators o/p #22BV-11, 21BV-02 & 21BV-05. Cause: Lightning. | 3162580 | 1 | 17:43 | Afternoon | Thursday | 2016 | 1
2478 | 2016-01-28 18:01 | 2016-01-28 18:01 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 3954 | 18:01 Off line NDC-CT #2, then S/D the Unit at 18:04. (For S/B-Prior to Off line washing program) Informed Minas GS #6 to reduce load total = 50 MW. Production loss reported by Minas-GS: GS #1 : 199 Bbls / 47 wells & 3 WIPs. GS #2 : 262 Bbls / 46 wells & 3 WIPs. GS #3 : 229 Bbls / 39 wells & 3 WIPs. GS #4 : 92 Bbls / 23 wells & 2 WIPs. GS #5 : 334 Bbls / 38 wells & 7 WIPs. GS #6 : 167 Bbls / 28 wells & 3 WIPs. ------------------------------------------ Total : 1283 Bbls / 221 wells & 21 WIPs. | 123 | 1 | 18:01 | Afternoon | Thursday | 2016 | 1
2479 | 2016-01-28 18:01 | 2016-01-29 17:06 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 3954 | 09:09 CGT #5 Tripped. By alarm: 125V DC gone & High Vibration. 10:46 4D OCB fdr #3 & 3D OCB fdr #5 T/O. By Under Frequency relay, then closed at 15:23. Cause: Auto Load shedding (Level-1). (CGT #5 Tripped, during NDC-2 in progress off line wash program) Informed Minas GS #6 to add reducing load total = 60 MW. Production loss reported by Minas-GS: GS #1 : 521 Bbls / 54 wells. (50 wells re-S/U & 4 wells are still off) & 2 WIPs. GS #2 : 828 Bbls / 51 wells. (46 wells re-S/U & 5 wells are still off ) & 2 WIPs. GS #3 : 742 Bbls / 47 wells. (26 wells re-S/U & 21 wells are still off) & 1 WIP. GS #4 : 410 Bbls / 44 wells. (44 wells re-S/U ). GS #5 : 1019 Bbls / 55 wells. (51 wells re-S/U & 4 wells are still off ) GS #6 : 756 Bbls / 56 wells. (49 wells Re-S/U & 7 wells are still off) --------------------------------------------------------------------------------------------------------------- Total : 4276 Bbls / 307 wells. (366 wells re-S/U & 41 wells are still off) & 5 WIPs are still off) Prod. loss reported by MInas GS-6: Prod loss yesterday (28-Jan-2016) : 1283 Bbls / 221 wells & 21 WIPs. Prod. loss additional (29-Jan-2016) : 4276 Bbls / 307 Wells & 5 WIPs. Grand Total prod. loss : 5559 Bbls / 528 Wells & 26 WIPs. Prod. Loss reported by System-EC: Total Prod. loss (28, 29 & 30 Jan 2016) = 3954 Bbls & 319 Wells. 17:06 S/U NDC-CT #2, then online the Unit at 17:36. (After off line washing program) 17:44 S/U CGT #5, then on line the Unit at: 18:03. (After fixing the DC voltage ground above) 19:00 Off line DGT #7, then S/D the Unit for S/B. | 123 | 1 | 18:01 | Afternoon | Thursday | 2016 | 1
2480 | 2016-01-28 21:26 | 2016-01-28 21:26 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 18 | It was reported b/o fuse for Tx at Well Bangko #235. Not checked yet. | 3162580 | 1 | 21:26 | Night | Thursday | 2016 | 1
2481 | 2016-01-28 21:26 | 2016-01-29 10:10 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 18 | Checked & found, @1 b/o 2.1SF fuse for 100Kva Tx at Well BKO #235. (Nella fdr #1) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3162580 | 1 | 21:26 | Night | Thursday | 2016 | 1
2482 | 2016-01-29 09:09 | 2016-01-29 09:09 | CENTRAL DURI POWER PLANT | Fair | Others | - | 09:00 CGT #5 Tripped. By alarm: 125V DC gone & High Vibration. Cause: DC voltage ground. 17:44 S/U CGT #5, then on line the Unit at: 18:03. (After fixing the DC voltage ground above) | 123 | 1 | 9:09 | Morning | Friday | 2016 | 1
2483 | 2016-01-29 10:46 | 2016-01-29 10:46 | 13.8KV 4D FEEDER #3 | Fair | Load Shedding | - | 4D OCB fdr #3 T/O. By Under Frequency relay, then closed at 15:23. Cause: Auto Load shedding (Level-1). (When CGT #5 Tripped, during NDC-2 off line wash progressing) | 3162581 | 1 | 10:46 | Morning | Friday | 2016 | 1
2484 | 2016-01-29 10:46 | 2016-01-29 10:46 | 13.8KV 3D FEEDER #5 | Fair | Load Shedding | - | 3D OCB fdr #5 T/O. By Under Frequency relay, then closed at 15:24. Cause: Auto Load shedding (Level-1). (When CGT #5 Tripped, during NDC-2 off line wash progressing) | 3162581 | 1 | 10:46 | Morning | Friday | 2016 | 1
2485 | 2016-01-29 16:28 | 2016-01-29 16:28 | MINAS POWER PLANT | Fair | Others | - | 16:28 S/U MGT #9, then online the Unit at at 17:01. (After energizing MInas SWY power TX-9 for trouble shooting Relay 87T-@1) 18:25 Off line MGT #9, then S/D the Unit for S/B. (Continued trouble shooting Current CT of Relay 87T-@1 of TX #9) Checked & found Mismatch, when TX #9 loaded by 5 Mw & 5 Mvar: -@1: 2.22 A, @2: 2.20 A, @3: 0.4 A good. -@2 CT current reading for 87T relay terminal 6 is zero reading. Cause: Others. (@1,@2 broken wire of current CT to Generator Breaker Relay panel) | 123 | 1 | 16:28 | Afternoon | Friday | 2016 | 1
2486 | 2016-01-29 17:06 | 2016-01-29 17:06 | NORTH DURI POWER PLANT |  |  | - | 17:06 S/U NDC-CT #2, then online the Unit at 17:36. (After off line washing program) (Also see report 28-Jan-2016 at 18:01) 09:09 CGT #5 Tripped. By alarm: 125V DC gone & High Vibration. 10:46 4D OCB fdr #3 & 3D OCB fdr #5 T/O. By Under Frequency relay, then closed at 15:23. Cause: Auto Load shedding (Level-1). (CGT #5 Tripped, during NDC-2 in progress off line wash program) Informed Minas GS #6 to add reducing load total = 60 MW. Production loss reported by Minas-GS: GS #1 : 521 Bbls / 54 wells. (50 wells re-S/U & 4 wells are still off) & 2 WIPs. GS #2 : 828 Bbls / 51 wells. (46 wells re-S/U & 5 wells are still off ) & 2 WIPs. GS #3 : 742 Bbls / 47 wells. (26 wells re-S/U & 21 wells are still off) & 1 WIP. GS #4 : 410 Bbls / 44 wells. (44 wells re-S/U ). GS #5 : 1019 Bbls / 55 wells. (51 wells re-S/U & 4 wells are still off ) GS #6 : 756 Bbls / 56 wells. (49 wells Re-S/U & 7 wells are still off) --------------------------------------------------------------------------------------------------------------- Total : 4276 Bbls / 307 wells. (366 wells re-S/U & 41 wells are still off) & 5 WIPs are still off) Prod. loss reported by MInas GS-6: Prod loss yesterday (28-Jan-2016) : 1283 Bbls / 221 wells & 21 WIPs. Prod. loss additional (29-Jan-2016) : 4276 Bbls / 307 Wells & 5 WIPs. Grand Total prod. loss : 5559 Bbls / 528 Wells & 26 WIPs. Prod. Loss reported by EC sytem: Total Prod. loss (28 & 29 Jan 2016) = 3954 Bbls & 319 Wells. 17:06 S/U NDC-CT #2, then online the Unit at 17:36. (After off line washing program) 17:44 S/U CGT #5, then on line the Unit at: 18:03. (After fixing the DC voltage ground above) 19:00 Off line DGT #7, then S/D the Unit for S/B. |  | 1 | 17:06 | Afternoon | Friday | 2016 | 1
2487 | 2016-01-29 17:10 | 2016-01-29 17:10 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 41 | CKBS VCB fdr #1 T/R 1x. CKBS #2 Load dropped 249A (259-10A). CKBS #3 Load dropped 63A (71-8A). CKBS #5 Load dropped 218A (348-130A). CKBS #6 Load dropped 16A (193-177A). NKBS #3 Load dropped 34A (370-336A). NKBS #5 Load dropped 194A (230-36A). Petapahan #2 Load dropped 49A (161-112A). Not checked yet. | 3162581 | 1 | 17:10 | Afternoon | Friday | 2016 | 1
2488 | 2016-01-29 17:10 | 2016-01-30 16:26 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 41 | Checked & found, CKBS VCB fdr #1 T/R 1x Ctr: 201-202 R/F: 51@1,@2,@3. Patrolled the line & found, @2 broken L/A o/p #36CW-08. Cause: Lightning. | 3162581 | 1 | 17:10 | Afternoon | Friday | 2016 | 1
2489 | 2016-01-29 18:18 | 2016-01-29 18:18 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 0 | Bangko fdr #4 Load dropped 59A (190-131A). Bangko GFPC T/R 1x. Not checked yet. | 3162580 | 1 | 18:18 | Afternoon | Friday | 2016 | 1
2490 | 2016-01-29 18:18 | 2016-01-02 07:40 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 0 | Checked all Reclosers at downstream of Bangko fdr #4 & found, normal. (Counter did not change) Checked & found, Bangko GFPC T/R 3x Ctr: 488-491. Patrolled Bangko fdr #4 line, but found nothing. Cause: Unidentified. | 3162580 | 1 | 18:18 | Afternoon | Friday | 2016 | 1
2491 | 2016-01-29 19:00 | 2016-01-29 19:00 | DURI POWER PLANT |  |  | - | 19:00 Off line DGT #7, then S/D the Unit for S/B. | 123 | 1 | 19:00 | Night | Friday | 2016 | 1
2492 | 2016-01-29 23:29 | 2016-01-29 23:29 | 13.8KV BATANG FEEDER #3 | Cloudy and Lightning | Lightning | 44 | Batang OCB fdr #3 T/R 1x. Not checked yet. 01-Feb-2016 Checked & found, Batang OCB fdr #3 T/R 2x Ctr: 305-307 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Suspected by Lightning. (Also see report 30-Jan-2016 at 14:43) | 3162580 | 1 | 23:29 | Night | Friday | 2016 | 1
2493 | 2016-01-30 01:12 | 2016-01-30 01:12 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 39 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3162580 | 1 | 1:12 | Night | Saturday | 2016 | 1
2494 | 2016-01-30 01:12 | 2016-02-02 15:12 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 39 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 166-167 R/F: 51N. Patrolled the line & found, @1,@3 F/O Dead end Insulators o/p #32AK-38. Cause: Lightning. | 3162580 | 1 | 1:12 | Night | Saturday | 2016 | 1
2495 | 2016-01-30 06:52 | 2016-01-30 06:52 | 13.8KV RANGAU FEEDER #2 | Cloudy and Lightning | Lightning | 34 | Rangau fdr #2 load dropped 70A (85-15A). Not checked yet. | 3162580 | 1 | 6:52 | Morning | Saturday | 2016 | 1
2496 | 2016-01-30 06:52 | 2016-03-02 14:00 | 13.8KV RANGAU FEEDER #2 | Cloudy and Lightning | Lightning | 34 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: 126-127. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3162580 | 1 | 6:52 | Morning | Saturday | 2016 | 1
2497 | 2016-01-30 11:54 | 2016-01-30 11:54 | 13.8KV BEKASAP FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Bekasap fdr #2 Load dropped 166A (240-74A). Bekasap GFPC-TX #C T/R 1x. (Ground fault alarm at Bekasap fdr #2) Not checked yet | 3162580 | 1 | 11:54 | Morning | Saturday | 2016 | 1
2498 | 2016-01-30 11:54 | 2016-02-02 15:10 | 13.8KV BEKASAP FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 37BD-40 (Bekasap fdr #2) T/R 1x Ctr: 71-72. Patrolled the line & found, @3 F/O Dead end Insulator o/p #37BD-92. Cause: Lightning. | 3162580 | 1 | 11:54 | Morning | Saturday | 2016 | 1
2499 | 2016-01-30 13:48 | 2016-01-30 13:48 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 16 | 13:50 It was reported by Libo-GS, that some Motor pumps were off. (Scada for Libo Substation failed at that time) 13:48 Suspected Libo OCB fdr #2 T/R 1x. Not checked yet. | 3162580 | 1 | 13:48 | Afternoon | Saturday | 2016 | 1
2500 | 2016-01-30 13:48 | 2016-01-31 14:58 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 16 | Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 409-410 R/F: 50N. Patrolled the line & found, @3 broken Pin Insulator o/p #29BV-07. Cause: Lightning. | 3162580 | 1 | 13:48 | Afternoon | Saturday | 2016 | 1
2501 | 2016-01-30 14:43 | 2016-01-30 14:43 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 44 | Batang OCB fdr #3 T/R 1x. Not checked yet | 3162580 | 1 | 14:43 | Afternoon | Saturday | 2016 | 1
2502 | 2016-01-30 14:43 | 2016-01-02 16:43 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 44 | Checked & found, Batang OCB fdr #3 T/R 2x Ctr: 305-307 R/F: 51N(@1). Patrolled the line, but found nothing. Cause: Suspected by Lightning. (Also see report 29-Jan-2016 at 23:29) | 3162580 | 1 | 14:43 | Afternoon | Saturday | 2016 | 1
2503 | 2016-01-30 16:08 | 2016-01-30 16:08 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 77 | 16:08 So.Bekasap OCB fdr #1 T/SO. 17:00 Checked & found, So.Bekasap OCB fdr #1 T/SO. Ctr: 342-343 R/F: 51N. Patrolled the line, but found nothing. 17:20 Blocked & closed Bekasap OCB fdr #1, Ok. Then released the Block. Cause: Suspected by Lightning. | 3162580 | 1 | 16:08 | Afternoon | Saturday | 2016 | 1
2504 | 2016-01-31 23:38 | 2016-01-31 23:38 | 13.8KV KETIGUL FEEDER#1 | Fair | Transformer Failure | 107 | It was reported b/o fuse for Tx at Well Tilan #23. Not checked yet. | 3162580 | 1 | 23:38 | Night | Sunday | 2016 | 1
2505 | 2016-01-31 23:38 | 2016-01-02 16:30 | 13.8KV KETIGUL FEEDER#1 | Fair | Transformer Failure | 107 | 16:30 Checked & found, @1, @3 b/o 7.8SF fuses for 250Kva Tx at Well Tilan #23. (Ketigul fdr #1) Performed TTR, Megger test the Tx & found, Low Megger reading. Cause: Tx failure. (Low megger reading) (The Tx is not replaced yet) | 3162580 | 1 | 23:38 | Night | Sunday | 2016 | 1
2506 | 2016-01-02 23:59 | 2016-01-02 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system normal condition. |  | 1 | 23:59 | Night | Saturday | 2016 | 1
2507 | 2016-02-02 14:17 | 2016-02-02 14:17 | 13.8KV 8D FEEDER #1 | Fair | Broken Fuse Cut Out | 60 | 14:17 It was reported no power at Well #8E-89. 15:30 Checked & found, @3 broken jumper & FCO for 300Kva Tx at Well #8E-89. Manually opened Recl. 8F-05, to replacing FCO & Jumper. 16:00 Closed Recl. 8F-05. Cause: Broken FCO. | 3176057 | 1 | 14:17 | Afternoon | Tuesday | 2016 | 2
2508 | 2016-02-02 17:49 | 2016-02-02 17:49 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Duri Field VCB fdr #3 T/R 1x. Not checked yet. | 3176054 | 1 | 17:49 | Afternoon | Tuesday | 2016 | 2
2509 | 2016-02-02 17:49 | 2016-03-02 13:49 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Checked & found, Duri Field VCB fdr #3 T/R 1x Ctr: 205. (Did not change) R/F: 50N(@1). Patrolled the line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 17:49 | Afternoon | Tuesday | 2016 | 2
2510 | 2016-02-02 19:40 | 2016-02-02 19:40 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified (Fuse) | 9 | It was reported b/o fuse at Well KB #108. Not checked yet | 3176057 | 1 | 19:40 | Night | Tuesday | 2016 | 2
2511 | 2016-02-02 19:40 | 2016-03-02 14:20 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified (Fuse) | 9 | Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well KB #108. Tested the Tx & found, normal. (Good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3176057 | 1 | 19:40 | Night | Tuesday | 2016 | 2
2512 | 2016-02-02 23:30 | 2016-02-02 23:30 | 13.8KV 3D FEEDER #4 | Fair | Unidentified (Fuse) | 9 | It was reported b/o fuse for Tx at Well #2D-73N. Not checked yet. | 3176057 | 1 | 23:30 | Night | Tuesday | 2016 | 2
2513 | 2016-02-02 23:30 | 2016-03-02 18:00 | 13.8KV 3D FEEDER #4 | Fair | Unidentified (Fuse) | 9 | 18:00 Checked & found, @3 b/o 7.8SF fuse for 300Kva Tx at Well #2D-73N. (3D fdr #4) Replaced the b/o fuse above with same size, then energized the Tx. Cause: Unidentified (fuse). | 3176057 | 1 | 23:30 | Night | Tuesday | 2016 | 2
2514 | 2016-03-02 05:28 | 2016-03-02 05:28 | PINANG SUBSTATION | Fair | Others | 860 | 05:28 It was reported no power at Pinang field. 07:20 Checked & found, 115Kv Pinang MSU-C/S T/O. R/F: 87@1,@2,@3 & 86T. Manual open 13.8Kv Pinang MSU VCB fdr #1. 07:35 Closed 115Kv Pinang MSU-C/S. 07:36 Blocked & close 13.8Kv Pinang MSU VCB fdr #1. But, 115Kv Pinang MSU-C/S T/O again. (By Relay: 87@1,@2,@3 & 86T) 07:38 Manual open 13.8Kv Pinang MSU VCB fdr #1. 11:58 Manual open 115Kv Nella GCB #27. (Line to Pinang) 12:30 Checked 115Kv Pinang MSU-C/S & found, loose connection of C/S Control cable. (Also found, 87T Primary current was zero reading) 12:35 Closed 115Kv Nella GCB #27. (Line to Pinang) 12:36 Closed 115Kv Pinang MSU-C/S. (After disabling Differential Relay of the Tx) 12:40 Blocked & closed 13.8Kv Pinang MSU VCB fdr #1, Ok. Then released the Block. Cause: Others. (Circuit Switcher Loose connection control cable) | 3176054 | 1 | 5:28 | Morning | Wednesday | 2016 | 3
2515 | 2016-03-02 08:50 | 2016-03-02 08:50 | MINAS POWER PLANT |  |  | - | 08:50 S/U MGT #9, then On Line the Unit at 09:45. (After troubleshoot & resolve the problem) |  | 1 | 8:50 | Morning | Wednesday | 2016 | 3
2516 | 2016-03-02 15:41 | 2016-03-02 15:41 | 13.8KV 5B FEEDER #4 | Heavy Rain | Lightning | 2 | 5B fdr #4 load dropped 206A (9246-40A). Not checked yet. | 3176057 | 1 | 15:41 | Afternoon | Wednesday | 2016 | 3
2517 | 2016-03-02 15:41 | 2016-04-02 17:05 | 13.8KV 5B FEEDER #4 | Heavy Rain | Lightning | 2 | Checked & found, Recl. 4B-73 (5B fdr #4) T/R 1x Ctr: 49-50. Patrolled the line & found, @2 broken L/A o/p #3B-40F. Cause: Lightning. | 3176057 | 1 | 15:41 | Afternoon | Wednesday | 2016 | 3
2518 | 2016-03-02 16:08 | 2016-03-02 16:08 | CENTRAL DURI POWER PLANT |  |  | - | 16:08 Off line CGT #1, the S/D the Unit for S/B at 16:10 16:09 Close ACB #19. (Tie Breaker) (Prior to fixing the leaking crossfire tube at Turbine compartment) 13-Feb-2016 10:49 S/U CGT #1, then On Line the Unit at 11:37. (After fixing the leaking crossfire tube at Turbine compartment & Replacing F/N set) |  | 1 | 16:08 | Afternoon | Wednesday | 2016 | 3
2519 | 2016-03-02 18:47 | 2016-03-02 18:47 | 13.8KV KETIGUL FEEDER#1 | Fair | Pin Insulator | 0 | Ketigul fdr #1 load dropped 57A (132-75A). Not checked yet. | 3176054 | 1 | 18:47 | Afternoon | Wednesday | 2016 | 3
2520 | 2016-03-02 18:47 | 2016-06-02 08:27 | 13.8KV KETIGUL FEEDER#1 | Fair | Pin Insulator | 0 | Checked & found, Recl. 32AK-16 (Ketigul fdr #1) T/R 1x Ctr: 432-433. Patrolled the line & found, @2 F/O Pin Insulator o/p #33AL-01. Cause: Pin Insulator. | 3176054 | 1 | 18:47 | Afternoon | Wednesday | 2016 | 3
2521 | 2016-03-02 19:15 | 2016-03-02 19:15 | 13.8KV LIBO FEEDER #1 | Fair | Animal | 13 | 19:15 It was reported b/o fuse for Tx at Well SE.Libo #06. (Libo fdr #1) 21:50 Checked & found, @1 b/o 7.8SF fuse for 300kva Tx at Well SE.Libo #06. Tested the Tx & found, normal. Replaced b/o fuse above with same size then energized the TX. Cause: Animal. | 3176054 | 1 | 19:15 | Night | Wednesday | 2016 | 3
2522 | 2016-04-02 14:30 | 2016-04-02 14:30 | 13.8KV KOTABATAK FEEDER #2 | Fair | Transformer Failure | 19 | It was reported b/o fuse for Tx at Well KB #45. Checked & found, @1,@3 b/o 7.8SF fuses for 300Kva Tx at Well KB #45. Performed TTR, Megger test the Tx & found, unbalance TTR. Cause: Tx Failure. (The Tx is not replaced yet) | 3176057 | 1 | 14:30 | Afternoon | Saturday | 2016 | 4
2523 | 2016-04-02 14:30 | 2016-06-02 11:00 | 13.8KV KOTABATAK FEEDER #2 | Fair | Transformer Failure | 19 | Replaced 300Kva Tx failure with the same size & energized the Tx at Well KB #45. Cause: Tx failure. (Unbalance TTR) | 3176057 | 1 | 14:30 | Afternoon | Saturday | 2016 | 4
2524 | 2016-04-02 14:33 | 2016-04-02 14:33 | MINAS POWER PLANT |  |  | - | 14:33 Off line MGT #5, then S/D the Unit for S/B. |  | 1 | 14:33 | Afternoon | Saturday | 2016 | 4
2525 | 2016-05-02 06:43 | 2016-05-02 06:43 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 36 | Bangko fdr #4 Load dropped 112A (192-80A). Bangko fdr #1 Load dropped 18A (207-189A). Bangko GFPC T/R 1x. (Ground fault alarm on Bangko fdr #4) Not checked yet. | 3176054 | 1 | 6:43 | Morning | Monday | 2016 | 5
2526 | 2016-05-02 06:43 | 2016-07-02 10:30 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 36 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 80-81. Also, Bangko GFPC T/R 1x Ctr: 491-492 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 6:43 | Morning | Monday | 2016 | 5
2527 | 2016-05-02 09:59 | 2016-05-02 09:59 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 0 | 09:59 C.Duri fdr #1 Load dropped 52A (225-173A). 17:40 C.Duri fdr #1 Load dropped 55A again (225-170A). Not checked yet. | 3176054 | 1 | 9:59 | Morning | Monday | 2016 | 5
2528 | 2016-05-02 09:59 | 2016-09-02 16:10 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 40AW-17 (C.Duri fdr #1) T/R 2x Ctr: 205-207. Patrolled the line & found, @2 F/O Dead end Insulator o/p #40AW-20. Cause: Lightning. | 3176054 | 1 | 9:59 | Morning | Monday | 2016 | 5
2529 | 2016-05-02 17:35 | 2016-05-02 17:35 | 13.8KV ROKAN FEEDER #2 | Cloudy and Lightning | Lightning | 19 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3176054 | 1 | 17:35 | Afternoon | Monday | 2016 | 5
2530 | 2016-05-02 17:35 | 2016-09-02 16:15 | 13.8KV ROKAN FEEDER #2 | Cloudy and Lightning | Lightning | 19 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 990-991 R/F: 51N. Patrolled the line, but found nothing. Cause: Suepected by Lightning. | 3176054 | 1 | 17:35 | Afternoon | Monday | 2016 | 5
2531 | 2016-06-02 23:59 | 2016-06-02 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system is normal condition. |  | 1 | 23:59 | Night | Thursday | 2016 | 6
2532 | 2016-07-02 06:02 | 2016-07-02 06:02 | 13.8KV 4B FEEDER #2 | Fair | Lightning Arrester | 32 | 06:02 4B OCB fdr #2 T/LO. 07:00 Checked & found, 4B OCB fdr #2 T/LO. Ctr: 219-223 R/F: 51N. Patrolled the line & found, @2 Broken L/A & the jumper touching to cross arm o/p #4B-86. 07:46 Blocked & closed 4B OCB fdr #2, Ok. Then released the block. (After dismantling broken L/A above) Cause: Broken Lightning Arrester. | 3176057 | 1 | 6:02 | Morning | Saturday | 2016 | 7
2533 | 2016-08-02 08:12 | 2016-08-02 08:12 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 44 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3176054 | 1 | 8:12 | Morning | Tuesday | 2016 | 8
2534 | 2016-08-02 08:12 | 2016-10-02 08:42 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 44 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 307-308 R/F: 50N. Patrolled the line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 8:12 | Morning | Tuesday | 2016 | 8
2535 | 2016-08-02 11:09 | 2016-08-02 11:09 | MINAS POWER PLANT |  |  | - | 11:09 S/U MGT #5, then Online the unit at 11:22. |  | 1 | 11:09 | Morning | Tuesday | 2016 | 8
2536 | 2016-08-02 11:56 | 2016-08-02 11:56 | 13.8KV KETIGUL FEEDER#3 | Fair | Animal | 9 | 11:56 It was reported that b/o fuse for Tx at Well GULAMO #03. 14:30 Checked & found, @1 b/o 7.8SF fuse for 300KVA Tx at Well GULAMO #03. Performed TTR, Megger test the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3176054 | 1 | 11:56 | Morning | Tuesday | 2016 | 8
2537 | 2016-08-02 13:55 | 2016-08-02 13:55 | MINAS POWER PLANT |  |  | - | 13:55 Off line MGT #8, then S/D the Unit for S/B at 13:57. (Prior to repairing Gas Speed Ratio Valve leak) 12-Feb-2016. 10:32 S/U MGT #8, then on line the Unit at 10:56. (After repairing Gas Speed Ratio Valve leak) |  | 1 | 13:55 | Afternoon | Tuesday | 2016 | 8
2538 | 2016-08-02 14:30 | 2016-08-02 14:30 | 13.8KV 8C FEEDER #3 | Fair | Transformer Failure | 99 | 14:30 It was reported that b/o fuse for Tx at Well #8D-39E. 15:30 Checked & found, @1,@2 b/o 7.8SF fuse for 300KVA Tx at Well #8D-39E. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx failure. (low megger reading) (The Tx is not replaced yet) | 3176057 | 1 | 14:30 | Afternoon | Tuesday | 2016 | 8
2539 | 2016-08-02 14:30 | 2016-11-02 10:00 | 13.8KV 8C FEEDER #3 | Fair | Transformer Failure | 99 | Replaced 300Kva Tx failure with the same size & energized the Tx at Well #8D-39E. Cause: Tx Failure. (Low megger reading) | 3176057 | 1 | 14:30 | Afternoon | Tuesday | 2016 | 8
2540 | 2016-08-02 14:31 | 2016-08-02 14:31 | 13.8KV 8D FEEDER #11 | Fair | Transformer Failure | 47 | 14:30 It was reported that b/o fuse for Tx at Well #8D-89EP1. 16:20 Checked & found, @1,@2 b/o 7.8SF fuse for 300KVA Tx at Well #8D-89EP1. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx failure. (low megger reading) (The Tx is not replaced yet) | 3176057 | 1 | 14:31 | Afternoon | Tuesday | 2016 | 8
2541 | 2016-08-02 14:31 | 2016-11-02 11:00 | 13.8KV 8D FEEDER #11 | Fair | Transformer Failure | 47 | Replaced 300Kva Tx failure with the same size & energized the Tx at Well #8D-89EP1. Cause: Tx Failure. (Low megger reading) | 3176057 | 1 | 14:31 | Afternoon | Tuesday | 2016 | 8
2542 | 2016-08-02 14:40 | 2016-08-02 14:40 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 14:40 It was reported that b/o fuse for Tx o/p #09-R6-08. 16:30 Checked & found, @1 b/o 2.1SF fuse for 112.5KVA Tx o/p #09-R6-08. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3176054 | 1 | 14:40 | Afternoon | Tuesday | 2016 | 8
2543 | 2016-09-02 06:40 | 2016-09-02 06:40 | 13.8KV LIBO FEEDER #1 | Fair | Animal | 51 | 06:40 Libo OCB fdr #1 T/R 1x. 07:15 Libo OCB fdr #1 T/R 2x again. 08:58 Checked & found, LIBO OCB fdr #1 T/R 3x Ctr: 262-265 R/F: 51N. Patrolled the line & found, a Dead Monkey hung on the Powerline at infront of LIBO-GS. Then Manually opened LIBO OCB fdr #1, to take down its Monkey. (Last Ctr: 266) 09:28 Blocked & closed LIBO OCB fdr #1, Ok. Then released the block. Cause: Animal. (Monkey) | 3176054 | 1 | 6:40 | Morning | Friday | 2016 | 9
2544 | 2016-09-02 06:40 | 2016-10-02 09:55 | 13.8KV LIBO FEEDER #1 | Fair | Animal | 51 | 09:55 Also found, Recl. 34CA-04 (Libo fdr #1) T/SO. Ctr: 26-27. (No wells actived at d/s of this Recloser) Patrolled the line, but found nothing. 09:58 Blocked & closed Recl. 34CA-04, Ok. Then released the block. Cause: Animal. | 3176054 | 1 | 6:40 | Morning | Friday | 2016 | 9
2545 | 2016-09-02 10:17 | 2016-09-02 10:17 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 214 | 10:17 Manually Opened Recl. 23BD-01. (Rangau fdr #2) To repairing hot spot on TOP of Well Jurong #08, and modification the jumper. 13:32 Blocked & closed Recl. 23BD-01, then released the block. Cause: Plan Maintenance. | 123 | 1 | 10:17 | Morning | Friday | 2016 | 9
2546 | 2016-10-02 09:41 | 2016-10-02 09:41 | MINAS SWITCH YARD | Fair | Relay Failure | - | 09:10 Switching to function test of 115KV MSY GCB #31 & #33. (115KV MSY - Lukut line) 09:41 115KV Minas GCB #10 T/O. 115KV Minas GCB #21 T/O. 115KV Minas GCB #25 T/O. (115KV Bus-4 Minas Switchyard no power) (Breaker failure relay Pick up, When Manually opened of 115KV Minas GCB #31) 09:47 Closed 115KV Minas GCB #10. Closed 115KV Minas GCB #21. Closed 115KV Minas GCB #25. 10:10 Closed 115KV Minas GCB #31 & #33. Cause: Under Investigation. | 3176057 | 1 | 9:41 | Morning | Sunday | 2016 | 10
2547 | 2016-10-02 09:41 | 2016-12-02 11:18 | MINAS SWITCH YARD | Fair | Relay Failure | - | Checked & found, Relay 50S Breaker failure timer of 115KV MSY GCB #31 failure. Cause: Relay Failure. (Relay Breaker failure timer failure) | 3176057 | 1 | 9:41 | Morning | Sunday | 2016 | 10
2548 | 2016-10-02 10:41 | 2016-10-02 10:41 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Planned Maintenance | 0 | 10:41-10:46 Manually Opened fuse to S/D 112.5Kva Tx o/p #05-M5-06. (C.Duri fdr #4) To repaire @2 Hot spot Secondary bushing of 112.5Kva Tx o/p above. (4 wells were off during the job) Cause: Maintenance Job. | 123 | 1 | 10:41 | Morning | Sunday | 2016 | 10
2549 | 2016-11-02 09:00 | 2016-11-02 09:00 | 13.8KV MINAS FEEDER #6 | Cloudy and Lightning | Lightning | 74 | 09:00 Minas fdr #6 Load dropped 88A (184-96A). 09:30 Checked & found, Recl. 6E-23A (Minas fdr #6) T/SO. Ctr: 16-17. Blocked & Closed the Recloser above, Ok. Then Released the Block. Cause: The line is not patrolled yet. | 3176057 | 1 | 9:00 | Morning | Wednesday | 2016 | 11
2550 | 2016-11-02 09:00 | 13/02/2016 13:37 | 13.8KV MINAS FEEDER #6 | Cloudy and Lightning | Lightning | 74 | Patrolled the line & found, @1 broken L/A o/p #6E-51. Cause: Lightning. | 3176057 | 1 | 9:00 | Morning | Wednesday | 2016 | 11
2551 | 2016-11-02 10:15 | 2016-11-02 10:15 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Planned Maintenance | 0 | 10:15-10:30 Shutted Off 112.5Kva Tx o/p #06-Q3-03. (C.Duri fdr #14) To repairing Hot spot at Tx secondary bushing o/p above. (5 Wells were off during the Job) Cause: Planned Maintenance. | 123 | 1 | 10:15 | Morning | Wednesday | 2016 | 11
2552 | 2016-11-02 11:44 | 2016-11-02 11:44 | 13.8KV 6D FEEDER #1 | Fair | Unidentified | 28 | 6D fdr #1 load dropped 149A (276-127A). 6D fdr #2 load dropped 123A (217-94A). Not checked yet. | 3176057 | 1 | 11:44 | Morning | Wednesday | 2016 | 11
2553 | 2016-11-02 11:44 | 13/02/2016 13:44 | 13.8KV 6D FEEDER #1 | Fair | Unidentified | 28 | Checked & found, Recl. 5C-42 (6D fdr #1) T/R 1x Ctr: 16-17. Patrolled the line, but found nothing. Cause: Unidentified. Also Checked Recl. 6D-78 & Recl. 6D-298 (6D fdr #2) & found, normal. Ctr: Did not operate. Patrolled the line, but found nothing. Cause: Unidentified. | 3176057 | 1 | 11:44 | Morning | Wednesday | 2016 | 11
2554 | 2016-11-02 15:15 | 2016-11-02 15:15 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 55 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3176054 | 1 | 15:15 | Afternoon | Wednesday | 2016 | 11
2555 | 2016-11-02 15:15 | 15/02/2016 07:28 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 55 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 308-309 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 15:15 | Afternoon | Wednesday | 2016 | 11
2556 | 2016-11-02 21:19 | 2016-11-02 21:19 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Cloudy and Lightning | Lightning | 0 | 4.16KV Dumai (INDS. FDR) VCB fdr #5 T/R 1x. Not checked yet. | 3176054 | 1 | 21:19 | Night | Wednesday | 2016 | 11
2557 | 2016-11-02 21:19 | 2016-12-02 14:00 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Cloudy and Lightning | Lightning | 0 | Checked & found, 4.16KV Dumai (IND. FDR) VCB fdr #5 T/R 1x Ctr: 276-277 R/F: 50@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3176054 | 1 | 21:19 | Night | Wednesday | 2016 | 11
2558 | 2016-12-02 10:32 | 2016-12-02 10:32 | MINAS POWER PLANT |  |  | - | 10:32 S/U MGT #8, then on line the Unit at 10:56. (After repairing Gas Speed Ratio Valve leak) |  | 1 | 10:32 | Morning | Friday | 2016 | 12
2559 | 2016-12-02 10:49 | 2016-12-02 10:49 | CENTRAL DURI POWER PLANT | Fair |  | - | 10:49 S/U CGT #1, then on line The Unit at 11:37. (After finishing problem & replacing F/N set) 11:33 Open 13.8Kv ABC #19. (Tie Breaker) |  | 1 | 10:49 | Morning | Friday | 2016 | 12
2560 | 2016-12-02 14:42 | 2016-12-02 14:42 | MINAS SWITCH YARD | Fair | Others | - | Switching to Re-energize 115KV MSY-LUKUT line. (By CPI team) 16:52 Closed 115KV MSY GCB #31 & GCB #33 (115KV LUKUT SS is energized) (KWH meter opening 913727296 at LUKUT SS is recorded at 16:31 on 12-Feb-2016) Continued Switching to Re-energize 115KV LUKUT - BERUK line. (By BOB Team) 16:58 Closed 115KV LUKUT GCB. (115KV LUKUT - BERUK line is energized) 17:01 115KV LUKUT GCB (Line to BERUK) T/O. 18:40 Manually Opened 115KV Line Switch at BUATAN. (to isolate 115KV Line toward BERUK) 18:44 Closed 115KV LUKUT GCB. (to energize 115KV Line to BUATAN only), Ok. Cause: UR Relay failed. 14-Feb-2016. Continued switching done by BOB Team. 11:15 Manually opened 115KV LUKUT GCB, to close 115KV line Switch at BUATAN. (line toward BERUK) 12:03 Closed 115KV LUKUT GCB. (To energize 115KV LUKUT - BERUK line) (After resetting Relay-21 / Distance Relay, by BOB Team) -Closed 13.8KV Beruk OCB fdr #1 & fdr #2. Note: LUKUT meter reading, Bus Voltage = 103.5KV & Load = 22A. (Read By BOB Team) | 123 | 1 | 14:42 | Afternoon | Friday | 2016 | 12
2561 | 2016-12-02 17:32 | 2016-12-02 17:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Dead End Insulator | 19 | C.Duri fdr #1 Load dropped 60A (214-154A). Not checked yet. | 3176054 | 1 | 17:32 | Afternoon | Friday | 2016 | 12
2562 | 2016-12-02 17:32 | 15/02/2016 14:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Dead End Insulator | 19 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 3x Ctr: 05-208. Patrolled the line & found, @2 broken Dead end Insulator o/p #40AW-20. Cause: Dead end Insulator. | 3176054 | 1 | 17:32 | Afternoon | Friday | 2016 | 12
2563 | 2016-02-13 01:47 | 2016-02-13 01:47 | 115KV MINAS - LUKUT LINE | Fair | Lightning Arrester | 0 | 01:47 115KV Minas GCB #33 T/R 1x. 115KV Minas GCB #31 T/R 1x. (115KV Minas-Lukut Line) 08:00 Checked & found, R/F: 67N. (Trip, Ground Over current) 09:00 Patrolled the Line & found, Broken L/A on @1 load side at Lukut Substation. Cause: Lightning Arrester. | 3176057 | 1 | 1:47 | Night | Saturday | 2016 | 2
2564 | 2016-02-13 07:48 | 2016-02-13 07:48 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 50 | Bekasap Main VCB fdr #6 T/R 1x. Not checked yet. | 3176054 | 1 | 7:48 | Morning | Saturday | 2016 | 2
2565 | 2016-02-13 07:48 | 2016-02-15 15:10 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 50 | Checked & found, Bekasap Main VCB fdr #6 T/R 1x Ctr: 337-338 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 7:48 | Morning | Saturday | 2016 | 2
2566 | 2016-02-13 10:49 | 2016-02-13 10:49 | CENTRAL DURI POWER PLANT | Fair |  | - | 10:49 S/U CGT #1, then On Line the Unit at 11:37. (After fixing the leaking crossfire tube at Turbine compartment & Replacing F/N set) | 123 | 1 | 10:49 | Morning | Saturday | 2016 | 2
2567 | 2016-02-13 12:10 | 2016-02-13 12:10 | MINAS POWER PLANT | Fair |  | - | 12:10 Off line MGT #5, then S/D the Unit for S/B. |  | 1 | 12:10 | Afternoon | Saturday | 2016 | 2
2568 | 2016-02-13 12:50 | 2016-02-13 12:50 | MINAS POWER PLANT | Fair |  | - | 12:50 Off line MGT #2, then S/D the Unit for S/B. |  | 1 | 12:50 | Afternoon | Saturday | 2016 | 2
2569 | 2016-02-13 13:18 | 2016-02-13 13:18 | 13.8KV 5B FEEDER #1 | Fair | Unidentified (Fuse) | 13 | 13:18 It was reported b/o fuse for Tx at Well #5B-87. (5B fdr #1) 15:04 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well #5B-87. Replaced b/o fuse with the same size, then Energized the TX. Cause: Unidentified (fuse). | 3176057 | 1 | 13:18 | Afternoon | Saturday | 2016 | 2
2570 | 2016-02-13 15:47 | 2016-02-13 15:47 | CENTRAL DURI POWER PLANT | Rain | Under investigation | - | 15:47 CGT #2 T/O by Alarm: Fire Detected, but not real. Frequency dropped to 59.70 Hz. (No Load shedding) Cause: Under investigation. |  | 1 | 15:47 | Afternoon | Saturday | 2016 | 2
2571 | 2016-02-13 16:00 | 2016-02-13 16:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Animal | 0 | 16:00 It was reported b/o fuse for Tx o/p #13-J2-03. (N.Duri fdr #2) 17:15 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #13-J2-03. Replaced b/o fuse with the same size, then Energized the TX. Cause: Animal. (Monkey) | 3176054 | 1 | 16:00 | Afternoon | Saturday | 2016 | 2
2572 | 2016-02-13 20:04 | 2016-02-13 20:04 | MINAS POWER PLANT |  |  | - | 20:04 S/U MGT #5, then On line the Unit at 20:14. |  | 1 | 20:04 | Night | Saturday | 2016 | 2
2573 | 2016-02-14 23:59 | 2016-02-14 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system normal condition. |  | 1 | 23:59 | Night | Sunday | 2016 | 2
2574 | 2016-02-15 08:12 | 2016-02-15 08:12 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 92 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3176057 | 1 | 8:12 | Morning | Monday | 2016 | 2
2575 | 2016-02-15 08:12 | 2016-02-16 14:55 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 92 | Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1255-1256 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3176057 | 1 | 8:12 | Morning | Monday | 2016 | 2
2576 | 2016-02-15 09:54 | 2016-02-15 09:54 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #1 | Fair | Unidentified | 27 | Switching procedure to Transfer load 8C fdr #4 to 8D fdr #5. 09:54 MSU #1 VCB fdr #1 (8C fdr #5) T/R 1x (while transferring part of load 8C fdr #4 to MSU #1 VCB fdr #1) Cause: Under Investigation. | 3176057 | 1 | 9:54 | Morning | Monday | 2016 | 2
2577 | 2016-02-16 03:33 | 2016-02-16 03:33 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Duri Community fdr #1 Load dropped 114A (195-81A). Not checked yet. | 3176054 | 1 | 3:33 | Night | Tuesday | 2016 | 2
2578 | 2016-02-16 03:33 | 22/02/2016 14:45 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. KT-74 (Duri Community fdr #1) T/R 1x Ctr: 113-114. Patrolled the line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 3:33 | Night | Tuesday | 2016 | 2
2579 | 2016-02-16 06:16 | 2016-02-16 06:16 | 13.8KV 4D FEEDER #5 | Fair | Pin Insulator | 16 | 4D OCB fdr #5 T/R 1x. Not checked yet. | 3176057 | 1 | 6:16 | Morning | Tuesday | 2016 | 2
2580 | 2016-02-16 06:16 | 2016-02-18 14:15 | 13.8KV 4D FEEDER #5 | Fair | Pin Insulator | 16 | Checked & found, 4D OCB fdr #5 T/R 1x Ctr: 258-259 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator o/p #NN. (Near Well #4D-19) Cause: Pin Insulator. | 3176057 | 1 | 6:16 | Morning | Tuesday | 2016 | 2
2581 | 2016-02-16 10:49 | 2016-02-16 10:49 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | 0 | 10:49 It was reported b/o fuse for Tx o/p #05-P3-11. (C.Duri fdr #15) 11:15 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #05-P3-11. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3176054 | 1 | 10:49 | Morning | Tuesday | 2016 | 2
2582 | 2016-02-16 12:02 | 2016-02-16 12:02 | 13.8KV 3D FEEDER #4 | Fair | Accident | 68 | 09:42 Blocked 3D OCB fdr #4, continued finishing to install new Cap. Bank o/p #3D-230. 12:01 It was requested by TDO team, to manual open 3D OCB fdr #4. 12:02 Manual opened 3D OCB fdr #4. (from DSC) 12:12 Manual closed 3D OCB fdr #4, then normalized the block. Cause: Under Investigation. | 3176057 | 1 | 12:02 | Afternoon | Tuesday | 2016 | 2
2583 | 2016-02-16 21:39 | 2016-02-16 21:39 | 13.8KV MINAS FEEDER #6 | Rain | Animal | 30 | Minas fdr #6 Load dropped 94A (200-106A). Not checked yet. 17-Feb-2016 at 12:45. Checked & found, Recl. 6E-23A (Minas fdr #6) T/LO. Ctr: 17-21. Patrolled the line & found, a death Animal (Bat Fruit) at @2 L/A on TP of Well #6E-85E. Then removed the animal above. Blocked & closed Recl. 6E-23A, Ok. Then released the block. Cause: Animal. (Bat) (See report 17-Feb 2016 at 12:45) | 3176057 | 1 | 21:39 | Night | Tuesday | 2016 | 2
2584 | 2016-02-17 12:45 | 2016-02-17 12:45 | 13.8KV MINAS FEEDER #6 | Fair | Animal | 218 | 12:45 Minas fdr #6 load dropped 101A (204-103A). 13:15 It was reported no power at Angsa Camp & Landscaping Office. 13:55 Checked & found, Recl. 6E-23A (Minas fdr #6) T/LO. Ctr: 17-21. 14:31 Patrolled the line & found, a death Animal (Bat Fruit) at @2 L/A on TP of Well #6E-85E. Then removed the animal above. 14:37 Blocked & closed Recl. 6E-23A, Ok. Then released the block. Cause: Animal. (Bat fruit) (Also see report 16-Feb 2016 at 21:39) | 3176057 | 1 | 12:45 | Afternoon | Wednesday | 2016 | 2
2585 | 2016-02-17 14:04 | 2016-02-17 14:04 | 13.8KV MINAS FEEDER #5 | Fair | Planned Maintenance | 6 | 14:04 Manual Opened Recl. 7E-148 (Minas fdr #5), to opened T-Tap o/p #7D-150. HCT Team doing Hot Tap Job & Installing Stopless Plugging Flare Stack. (at under power line between Recl. 7E-148 & pole #7D-150 above) 14:43 Transferred part of load Minas fdr #5 to Minas fdr #6, to energize FM building & 7 wells. 2 spans are still de-energize, from Recl. 7E-148 toward pole #7D-150. (for HCT job plan above) Cause: Planned Maintenance. | 123 | 1 | 14:04 | Afternoon | Wednesday | 2016 | 2
2586 | 2016-02-17 15:34 | 2016-02-17 15:34 | 13.8KV NORTH DURI FEEDER #1 | Fair | Secondary Cable | 0 | It was reported b/o fuse for Tx o/p #10-J6-21. (N.Duri fdr #1) Not checked yet. | 3176054 | 1 | 15:34 | Afternoon | Wednesday | 2016 | 2
2587 | 2016-02-17 15:34 | 2016-02-19 10:21 | 13.8KV NORTH DURI FEEDER #1 | Fair | Secondary Cable | 0 | 10:21 Checked & found, @2 b/o fuse for 112.5KVA Tx. Replaced b/o fuse above with the same size, but b/o again. Checked & found sparks at Secondary Cable. Replaced Sec. Cable above. 18:05 Replaced b/o fuse above with the same size then energized the Tx. Cause: Sec. Cable. | 3176054 | 1 | 15:34 | Afternoon | Wednesday | 2016 | 2
2588 | 2016-02-17 15:38 | 2016-02-17 15:38 | 13.8KV 6D FEEDER #5 | Fair | Unidentified | 78 | 6D fdr #5 load dropped 180A (235-55A). 6D fdr #6 load dropped 55A (231-176A). Pump Off. Not checked yet. | 3176057 | 1 | 15:38 | Afternoon | Wednesday | 2016 | 2
2589 | 2016-02-17 15:38 | 2016-02-18 13:45 | 13.8KV 6D FEEDER #5 | Fair | Unidentified | 78 | Checked & found, Recl. 5D-10 (6D fdr #5) T/R 1x Ctr: 09-10. Patrolled the line, but found nothing. Cause: Unidentified. | 3176057 | 1 | 15:38 | Afternoon | Wednesday | 2016 | 2
2590 | 2016-02-18 05:28 | 2016-02-18 05:28 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Dead End Insulator | 0 | C.Duri ACB fdr #9 T/R 1x Ctr: 342-343 R/F: 51N. Not patrolled yet. | 3176054 | 1 | 5:28 | Morning | Thursday | 2016 | 2
2591 | 2016-02-18 05:28 | 2016-02-20 10:10 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Dead End Insulator | 0 | Patrolled the line & found, @1 F/O Dead end Insulator o/p #04-7-04. Cause: Dead end Insulator. | 3176054 | 1 | 5:28 | Morning | Thursday | 2016 | 2
2592 | 2016-02-18 11:34 | 2016-02-18 11:34 | 13.8KV CENTRAL DURI FEEDER #12 | Fair | Voltage regulator failure | 0 | 11:34 C.Duri ACB fdr #12 T/R 3x. 11:40 C.Duri ACB fdr #12 T/R 2x again. 12:10 C.Duri ACB fdr #12 T/R 1x again. It was reported fire at Tx o/p #05-SDDB-25. 12:57 Checked & found, C.Duri ACB fdr #12 T/R 6x Ctr: 472-478 R/F: 51@2. 13:18 Checked & found, @2 broken source & load side bushing of 1MVA VR at pole #05-SDDB-25. 13:47 Manual opened C.Duri ACB fdr #12. 13:54 By passed VR above & isolated it by opening all VR Jumpers. 14:14 Manual Closed C.Duri ACB fdr #12, Ok. Cause: Voltage Regulator Failure. | 3176054 | 1 | 11:34 | Morning | Thursday | 2016 | 2
2593 | 2016-02-19 07:14 | 2016-02-19 07:14 | SINABUNG MINI SUBSTATION | Fair | Unidentified | 0 | 07:14 Bangko Area RTU, Bekasap Area RTU, Duri Comm. RTU Failed. 07:20 It was reported power outage (T/R) at security office & Beta Office. Suspected 4.16KV Recl. for Sinabung Mini SS T/R 1x. Not checked yet. | 3176054 | 1 | 7:14 | Morning | Friday | 2016 | 2
2594 | 2016-02-19 07:14 | 22/02/2016 15:10 | SINABUNG MINI SUBSTATION | Fair | Unidentified | 0 | Checked & found, 4.16KV Sinabung Mini Subst. Recloser T/R 1x Ctr: 58. (Did not change) Patrolled the line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 7:14 | Morning | Friday | 2016 | 2
2595 | 2016-02-19 07:40 | 2016-02-19 07:40 | 13.8KV 6D FEEDER #1 | Fair | Unidentified | 39 | 07:40 6D OCB fdr #1 T/R 1x. 11:08 Checked & found, 6D OCB fdr #1 T/R 2x Ctr: 301-303 R/F: 51@1 & 51N. Patrolled the line, but nothing found. Cause: Unidentified. | 3176057 | 1 | 7:40 | Morning | Friday | 2016 | 2
2596 | 2016-02-20 10:40 | 2016-02-20 10:40 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx o/p #10-J6-21. Not checked yet. | 3176054 | 1 | 10:40 | Morning | Saturday | 2016 | 2
2597 | 2016-02-20 10:40 | 22/02/2016 15:00 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #10-J6-21. Performed TTR, megger test the Tx & found, normal. (good reading) Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (fuse). | 3176054 | 1 | 10:40 | Morning | Saturday | 2016 | 2
2598 | 2016-02-20 10:40 | 26/02/2016 16:30 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 16:30 It was reported no Power o/p #10-J6-21. (N.Duri fdr #1) 18:10 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #10-J6-21. Perform TTR, Megger test the Tx also Secondary cable & found, good reading. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3176054 | 1 | 10:40 | Morning | Saturday | 2016 | 2
2599 | 2016-02-20 12:28 | 2016-02-20 12:28 | CENTRAL DURI POWER PLANT |  |  | - | 12:28 S/U CGT #2, then online the Unit at 13:13. |  | 1 | 12:28 | Afternoon | Saturday | 2016 | 2
2600 | 2016-02-20 14:52 | 2016-02-20 14:52 | MINAS POWER PLANT |  |  | - | 14:52 Offline MGT #8, then S/D the Unit for S/B. |  | 1 | 14:52 | Afternoon | Saturday | 2016 | 2
2601 | 2016-02-21 13:00 | 2016-02-21 13:00 | 13.8KV S. BALAM GFPC | Fair | Unidentified | 0 | So.Balam GFPC T/R 1x. Fault alarm on So.Balam fdr #4. (No load dropped at any feeders) Not checked yet. | 3176054 | 1 | 13:00 | Afternoon | Sunday | 2016 | 2
2602 | 2016-02-21 13:00 | 2016-02-24 07:25 | 13.8KV S. BALAM GFPC | Fair | Unidentified | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 201-202. Patrolled So.Balam fdr #4 line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 13:00 | Afternoon | Sunday | 2016 | 2
2603 | 2016-02-21 14:00 | 2016-02-21 14:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Planned Maintenance | 0 | 14:00 Manually opened Duri Community ACB fdr #1. To repairing spark at HLC o/p #SB-05. (infront of Gate-1) Cause: Maintenance Job. 14:20 Manually closed Duri Community ACB fdr #1. (Ctr: 0081-0082) | 123 | 1 | 14:00 | Afternoon | Sunday | 2016 | 2
2604 | 2016-02-22 03:47 | 2016-02-22 03:47 | 13.8KV 5B FEEDER #2 | Fair | Dead End Insulator | 37 | 5B OCB fdr #2 T/R 1x. Not checked yet. | 3176057 | 1 | 3:47 | Night | Monday | 2016 | 2
2605 | 2016-02-22 03:47 | 2016-02-23 10:45 | 13.8KV 5B FEEDER #2 | Fair | Dead End Insulator | 37 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 335-336 R/F: 51N. Patrolled the line & found, @3 broken Dead end Insulator o/p #4C-59. Cause: Dead end Insulator. | 3176057 | 1 | 3:47 | Night | Monday | 2016 | 2
2606 | 2016-02-22 11:26 | 2016-02-22 11:26 | 13.8KV 8C FEEDER #6 | Fair | Planned Maintenance | 38 | 11:26 Manually opened Recl. 8C-94. (8C fdr #6) (To reduce load during refill SF-6 gas into C/S interupter of MSU #1) 12:09 Manually closed Recl. 8C-94. Cause: Planned maintenance. | 123 | 1 | 11:26 | Morning | Monday | 2016 | 2
2607 | 2016-02-22 17:18 | 2016-02-22 17:18 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 3 | It was reported b/o fuse for 150Kva Tx at Well Pagar #08. Not checked yet. | 3176054 | 1 | 17:18 | Afternoon | Monday | 2016 | 2
2608 | 2016-02-22 17:18 | 2016-02-23 16:23 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 3 | Checked & found, @1, @3 b/o 3.5SF fuses for 150Kva Tx at Well Pagar #08. Performed TTR, Megger tested the Tx & found, Low megger reading. Cause: Tx failure. (Low megger reading) (The Tx is not replaced yet) | 3176054 | 1 | 17:18 | Afternoon | Monday | 2016 | 2
2609 | 2016-02-22 17:18 | 2016-02-28 17:18 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 3 | Replaced 150Kva Tx failure with the same size & energized the Tx. Cause: Tx failure. (Low megger reading) | 3176054 | 1 | 17:18 | Afternoon | Monday | 2016 | 2
2610 | 2016-02-22 21:15 | 2016-02-22 21:15 | 13.8KV KETIGUL FEEDER#3 | Fair | ESP Failure | 0 | 21:15 It was reported b/o fuse for Tx at Well Gulamo #05. 23-February-2016. 00:45 Checked & found, @2 b/o 2.1SF fuse for 100Kva Tx at Well Gulamo #05. Performed TTR, Megger test the Tx & found, normal. (Good reading) Replaced the b/o fuse above with same size, then energized the Tx. Cause: Reda motor failure. (zero Megger reading) | 3176054 | 1 | 21:15 | Night | Monday | 2016 | 2
2611 | 2016-02-23 07:30 | 2016-02-23 07:30 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified (Fuse) | 23 | 07:30 It was reported b/o fuse for Tx at Well #7D-97N. 10:05 Checked & found, @1 b/o 14.0K fuse for 550Kva Tx at Well #7D-97N. Performed Test TTR, Megger the Tx & found, normal. (good reading) Replaced b/o fuse above with same size then energized the Tx. Cause: Unidentified. | 3176057 | 1 | 7:30 | Morning | Tuesday | 2016 | 2
2612 | 2016-02-23 10:30 | 2016-02-23 10:30 | 13.8KV S. BALAM FEEDER #4 | Fair | Animal | 14 | 10:30 It was reported b/o fuse for Tx at Well So.Balam #366. 15:25 Checked & found, @2 b/o 3.5SF fuse for 150kva Tx at Well So.Balam #366. Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced the b/o fuse above with same size then energized Tx. Cause: Animal. (Squirrel) | 3176054 | 1 | 10:30 | Morning | Tuesday | 2016 | 2
2613 | 2016-02-24 08:15 | 2016-02-24 08:15 | 13.8KV BATANG FEEDER #2 | Fair | Unidentified (Fuse) | 42 | 08:15 It was reported b/o fuse for Tx at Well Rantau Bais #35. (Batang fdr #2) 15:30 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Rantau Bais #35. Replaced the b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3176054 | 1 | 8:15 | Morning | Wednesday | 2016 | 2
2614 | 2016-02-24 08:54 | 2016-02-24 08:54 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 29 | Sintong OCB fdr #1 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. | 3176054 | 1 | 8:54 | Morning | Wednesday | 2016 | 2
2615 | 2016-02-24 08:54 | 2016-02-25 13:50 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 29 | Checked & found, Sintong OCB fdr #1 T/R 1x Ctr: 380-381 R/F: 51N. Also found, Sintong GFPC T/R 1x Ctr: 822. (Did not change) Patrolled the line & found, @1 broken Dead end Insulator o/p #25AD-05. Cause: Lightning. | 3176054 | 1 | 8:54 | Morning | Wednesday | 2016 | 2
2616 | 2016-02-24 09:08 | 2016-02-24 09:08 | CENTRAL DURI POWER PLANT |  |  | - | 09:08 Off line CGT #3, then S/D the unit for S/B. 09:10 Closed ACB #39. (Tie Breaker) 15:10 Re-S/U CGT #3, then On line the Unit at 15:30. (Due to CGT #4 Tripped) |  | 1 | 9:08 | Morning | Wednesday | 2016 | 2
2617 | 2016-02-24 11:35 | 2016-02-24 11:35 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 0 | To anticipate Spill at Minas GS-5, due to 3 Unit WIPs were Trip. 11:35 Manually Opened 3D OCB fdr #4. (Requested by Operator Minas GS-5) ( 3 Unit pumps were off, due to air compressor problem) 16:07 Blocked & closed 3D OCB fdr #4, then release the block. Cause: Maintenance Job. (No production loss charging to PGT) | 123 | 1 | 11:35 | Morning | Wednesday | 2016 | 2
2618 | 2016-02-24 12:26 | 2016-02-24 12:26 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Others | 47 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3176054 | 1 | 12:26 | Afternoon | Wednesday | 2016 | 2
2619 | 2016-02-24 12:26 | 2016-02-26 07:19 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Others | 47 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 309-310 R/F: 51@1. Patrolled the line & found, a Kites hung on TP of Well Pemburu #02. Cause: Others. (a Kites hung on TP of Well Pemburu #02) | 3176054 | 1 | 12:26 | Afternoon | Wednesday | 2016 | 2
2620 | 2016-02-24 12:27 | 2016-02-24 12:27 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 60 | Bekasap VCB fdr #3 T/R 1x. Not checked yet. | 3176054 | 1 | 12:27 | Afternoon | Wednesday | 2016 | 2
2621 | 2016-02-24 12:27 | 2016-02-29 08:15 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 60 | Checked & found, Bekasap Main fdr #3 T/R 1x Ctr: 99481-99482 R/F: 51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3176054 | 1 | 12:27 | Afternoon | Wednesday | 2016 | 2
2622 | 2016-02-24 12:32 | 2016-02-24 12:32 | CENTRAL DURI POWER PLANT | Cloudy | Under investigation | - | CGT #4 Tripped by alarm: Fire Detective Trip. (Not real) Cause: Under Investigation. C.Duri ACB #39 (Tie Breaker), is still in close position. (When S/D CGT #3 for S/B-Prior to PSV Gas Scruber sertification) |  | 1 | 12:32 | Afternoon | Wednesday | 2016 | 2
2623 | 2016-02-24 12:35 | 2016-02-24 12:35 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Others | 0 | Batang OCB fdr #2 T/R 1x. Not checked yet. | 3176054 | 1 | 12:35 | Afternoon | Wednesday | 2016 | 2
2624 | 2016-02-24 12:35 | 2016-02-26 08:35 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Others | 0 | Checked & found, Batang OCB fdr #2 T/R 3x Ctr: 118-121 R/F: 51@1. Patrolled the line & found, a Kites hung on TP of Well Rantaubais #10. Cause: Others. (a Kites hung on TP of Well Rantaubais #10) | 3176054 | 1 | 12:35 | Afternoon | Wednesday | 2016 | 2
2625 | 2016-02-24 12:44 | 2016-02-24 12:44 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | C.Duri fdr #1 Load dropped 49A (218-169A). Not checked yet. | 3176054 | 1 | 12:44 | Afternoon | Wednesday | 2016 | 2
2626 | 2016-02-24 12:44 | 2016-02-25 15:10 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/R 1x Ctr: 170-171. Patrolled the line & found, @3 broken L/A on TP of Well Kulin #55. Cause: Lightning. | 3176054 | 1 | 12:44 | Afternoon | Wednesday | 2016 | 2
2627 | 2016-02-25 09:55 | 2016-02-25 09:55 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 0 | 09:55 It was reported b/o fuse for Tx o/p #09-N6-05. (C.Duri fdr #8) 11:25 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #09-N6-05. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3176054 | 1 | 9:55 | Morning | Thursday | 2016 | 2
2628 | 2016-02-25 10:59 | 2016-02-25 10:59 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 46 | Sintong OCB fdr #2 T/R 1x. Not checked yet. | 3176054 | 1 | 10:59 | Morning | Thursday | 2016 | 2
2629 | 2016-02-25 10:59 | 2016-02-26 16:15 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 46 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 406-407 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 10:59 | Morning | Thursday | 2016 | 2
2630 | 2016-02-25 16:41 | 2016-02-25 16:41 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 86 | CKBS VCB fdr #5 T/R 1x. Not checked yet. | 3176057 | 1 | 16:41 | Afternoon | Thursday | 2016 | 2
2631 | 2016-02-25 16:41 | 2016-02-26 16:21 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 86 | Checked & found, CKBS VCB fdr #5 T/R 1x Ctr: 132-133 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3176057 | 1 | 16:41 | Afternoon | Thursday | 2016 | 2
2632 | 2016-02-26 12:00 | 2016-02-26 12:00 | 13.8KV MINAS FEEDER #2 | Fair | Animal | 33 | 12:00 It was reported b/o fuse for Tx at Well #7D-12. (Minas fdr #2) 15:08 Checked & found, @1 b/o 7.8SF fuse for 250Kva Tx at Well #7D-12. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Squirrel) | 3176057 | 1 | 12:00 | Afternoon | Friday | 2016 | 2
2633 | 2016-02-27 08:44 | 2016-02-27 08:44 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 32 | C.Duri fdr #1 load dropped 48A (222-174A). Not checked yet. | 3176054 | 1 | 8:44 | Morning | Saturday | 2016 | 2
2634 | 2016-02-27 08:44 | 2016-01-03 16:44 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 32 | Checked All Reclosers at downstream of C.Duri fdr #1, but found normal. (Counter did not change) Patrolled the line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 8:44 | Morning | Saturday | 2016 | 2
2635 | 2016-02-27 18:01 | 2016-02-27 18:01 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | 18:01 Recl. 06-Q3-02 (C.Duri fdr #15) T/O. (in block for PT. MS Job) 18:40 Checked & found Recl 06-Q3-02 (C.Duri fdr #15) T/O. Ctr: Patrolled the line, but found nothing. Blocked & closed the Recl. 06-Q3-02, Ok. (Recloser is still in block for PT. MS job) Cause: Unidentified. | 3176054 | 1 | 18:01 | Afternoon | Saturday | 2016 | 2
2636 | 2016-02-27 23:45 | 2016-02-27 23:45 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 0 | 23:45 Pematang fdr #1 load dropped 26A (114-88A). 28-Feb-2016. 00:39 It was reported Recloser for TX-BWM at Pematang-GS T/O. 01:37 Checked & found Recl. 38BC-43 (Pematang fdr #1) T/O. Ctr: 32-33. 01:45 Manually closed Recl. 38BC-43, Ok. Cause: Unidentified. | 3176054 | 1 | 23:45 | Night | Saturday | 2016 | 2
2637 | 2016-02-28 00:04 | 2016-02-28 00:04 | 13.8KV SINTONG FEEDER #2 | Drizzle | Pin Insulator | 0 | 00:04 Sintong fdr #2 load dropped 9A (217-208). (Ground fault alarm at Sintong fdr #2) 00:14 It was reported No Power at Pagar-GS. 29-Feb-2016. 01:39 Checked & found, Recl. 26AK-24 (Sintong fdr #2) T/LO. Ctr: 212-219. 01:42 Blocked & closed Recl. 26AK-24, but T/O again. Ctr: 219-220. It was reported by Pagar-GS operator, spark on power pole inside Pagar-GS. Patrolled the line, but found nothing. 02:00 Blocked & closed Recl. 26Ak-24, Ok. 02:07 Recl. 26AK-24 T/O again. Ctr: 220-221. Patolled the line & found, @3 broken Pin Insulator o/p #29AK-29. (Then replaced its broken Pin Insulator above) 03:04 Blocked & closed Recl. 26AK-24, Ok. Then released the Block. Cause: Broken pin insulator. | 3176054 | 1 | 0:04 | Night | Sunday | 2016 | 2
2638 | 2016-02-28 06:22 | 2016-02-28 06:22 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx o/p #07-T1-06 and o/p #07-T1-08. (No wells were Off at d/s of Duri Field fdr #2) Not checked yet. | 3176054 | 1 | 6:22 | Morning | Sunday | 2016 | 2
2639 | 2016-02-28 06:22 | 2016-02-29 09:00 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 09:00 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T1-08. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (fuse). | 3176054 | 1 | 6:22 | Morning | Sunday | 2016 | 2
2640 | 2016-02-28 08:40 | 2016-02-28 08:40 | CENTRAL DURI POWER PLANT |  |  | - | 08:40 S/U CGT #4, then on line at 09:30. (for Running on test after Fixing the Problem due to Trip by Alarm: Fire detected) 11:10 CGT #4 T/O. By alarm: Fire Detected. (but Not Real, same as before) Note: Gas CO2 released. Cause: Under Investigation. | 123 | 1 | 8:40 | Morning | Sunday | 2016 | 2
2641 | 2016-02-28 16:56 | 2016-02-28 16:56 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 967 | 16:56 C.Duri fdr #1 Load dropped 92A (246-154A). 18:30 Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/LO. Ctr: 208-215. Patrolled the line, but found nothing. 21:39 Blocked & closed Recl. 41AW-62, but trip again. Ctr: 215-216. Re-patrolled the line downstream of Recl. 41AW-62, but found nothing. 21:56 Blocked & closed Recl. 41AW-62, but trip again. Ctr: 216-217. Re-patrolled & isolated VR, Capacitor Bank, Cathodic protection. and also Manually opened Recl. 39AV-36 and Recl. 40AW-17. 23:34 Blocked & closed Recl. 41AW-62, but trip again. Ctr: 217-218. Re-patrolled line at d/s of Recl. 41AW-62, but found nothing. 00:33 Blocked & closed Recl. 41AW-62, but trip again. Ctr: 218-219. Re-patrolled the line & installed 2 set fault locators o/p #40AW-01 and o/p #40AW17. 00:46 Blocked & closed Recl. 41AW-62, but trip again. Ctr: 219-220. Found, a Dead Monkey & broken Pin Insulator also broken L/A o/p #40AU-12. (as Terminal pole of Well Kulim #83) 29-Feb-2016. 01:35 Blocked & closed Recl. 41AW-62, Ok. Last Ctr: 220-221. (after isolating broken Pin Insulator, L/A & tookdown its the Monkey) 01:37 Blocked & closed Recl. 39AV-36, Ok. Then normalized the block. 01:39 Blocked & closed Recl. 40AW-17, Ok. Then normalized the block. Cause: Animal. (Monkey) Prod. loss Reported by EC system: Kulin Area (HO) Prod. loss = 458 Bbls / 63 Wells. Balam-GS (SLO) Prod. loss = 509 Bbls / 21 Wells. Grand Total Prod. loss. = 967 Bbls / 84 Wells. | 3176054 | 1 | 16:56 | Afternoon | Sunday | 2016 | 2
2642 | 2016-02-28 21:13 | 2016-02-28 21:13 | KOTABATAK JUNCTION SW STA | Drizzle | Unidentified | 26 | 21:13 115KV KBJ Bus #2 and Bus #4 Trip Off. Frequency raise up to 60.27Hz. (Lost of load at Minas north Area about 30MW) 115kv KBJ GCB # 10 T/O. (Tie BUS #3 & BUS #4) 115kv KBJ GCB # 20 T/O. (Tie BUS #1 & BUS #2) 115kv KBJ GCB # 21 T/O. (Line to 5B Substation) 115kv KBJ GCB # 22 T/O. (Line to 230KV N.Duri TX #2) 115kv KBJ GCB # 27 T/O. (Line to 3D Substation) 115kv KBJ GCB # 28 T/O. (Line to 4D Substation) 23:35 Checked & found, 115KV GCB #10, #20, #21, #22, #27 & #28 T/O. By R/F: 87B & 86B (BUS #4) R/F: 87B & 86B (BUS #2) :50S @2 (Breaker failure) of GCB #10,20,21,22,27,28. Then Reset its relay. (87B, 86B and 50S relay) 29-Feb-2016. 00:44 Manually closed 115kv KBJ GCB # 10. (Ctr: 92-93) Manually closed 115kv KBJ GCB # 20. (Ctr: 89-90) Manually closed 115kv KBJ GCB # 21. (Ctr: 192-193) Manually closed 115kv KBJ GCB # 22. (Ctr: 168-169) Manually closed 115kv KBJ GCB # 27. (Ctr: 64-65) Manually closed 115kv KBJ GCB # 28. (Ctr: 311-312) Cause: Under Investigation. Prod. loss due to Voltage dropped: Reported by Minas-GS = 12 Unit WIPs T/O. Reported by Kopet-GS = 11 Bbls / 12 Wells off. Reported by Libo-GS = 15 Bbls / 13 Wells off. Grand Total = 26 Bbls / 25 Wells off + 12 Unit WIP off. | 3176057 | 1 | 21:13 | Night | Sunday | 2016 | 2
2643 | 2016-02-29 13:21 | 2016-02-29 13:21 | 13.8KV NELLA GFPC | Fair | Unidentified | 0 | Nella GFPC T/R 1x. Ground fault alarm on Nella fdr #1. (No load dropped at any fdrs) Not checked yet. | 3176054 | 1 | 13:21 | Afternoon | Monday | 2016 | 2
2644 | 2016-02-29 13:21 | 2016-04-03 09:24 | 13.8KV NELLA GFPC | Fair | Unidentified | 0 | Checked & found, Nella GFPC T/R 1x Ctr: 683-684. Patrolled Nella fdr #1 line, but found nothing. Cause: Unidentified. | 3176054 | 1 | 13:21 | Afternoon | Monday | 2016 | 2
2645 | 2016-02-29 16:00 | 2016-02-29 16:00 | 13.8KV MINAS FEEDER #6 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx at Well #7E-33. Checked & found, @1 b/o 3.5SF fuse for 3x50Kva Tx at Well #7E-33. Replaced the b/o fuse with same size, then energized the Tx. Cause: Unidentified (fuse). | 3176057 | 1 | 16:00 | Afternoon | Monday | 2016 | 2
2646 | 2016-02-29 22:27 | 2016-02-29 22:27 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 27 | C.Duri fdr #1 load dropped 96A (247-151A). Not checked yet. | 3176054 | 1 | 22:27 | Night | Monday | 2016 | 2
2647 | 2016-02-29 22:27 | 2016-01-03 16:27 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 27 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 231-232. Patrolled the line & found, @3 F/O Pin Insulator on TP of Well Kulin #12. Cause: Pin Insulator. | 3176054 | 1 | 22:27 | Night | Monday | 2016 | 2
2648 | 2016-01-03 09:35 | 2016-01-03 09:35 | DURI POWER PLANT |  |  | - | 09:35 S/U DGT #7, then On line at 10:00. |  | 1 | 9:35 | Morning | Sunday | 2016 | 1
2649 | 2016-01-03 09:45 | 2016-01-03 09:45 | 13.8KV 5B FEEDER #4 | Fair | Planned Maintenance | 0 | 09:45 Open LBS #KN-36. (5B fdr #4), to Tie in new Well #3C-42. (Some wells were off during the Job done) 14:30 Closed LBS #KN-36. Cause: Planned Maintenance. (No Prod. loss charged to PGT, due to It is requested by Prod. Team for Tie in new Well #3C-42) | 123 | 1 | 9:45 | Morning | Sunday | 2016 | 1
2650 | 2016-01-03 13:38 | 2016-01-03 13:38 | CENTRAL DURI POWER PLANT |  |  | - | 13:38 S/U CGT #4, then On line the Unit at 13:57. |  | 1 | 13:38 | Afternoon | Sunday | 2016 | 1
2651 | 2016-01-03 14:25 | 2016-01-03 14:25 | CENTRAL DURI POWER PLANT |  |  | - | 14:25 Off line CGT #3, then S/D the Unit at 14:26. (For S/B - Prior to replacing PSV) |  | 1 | 14:25 | Afternoon | Sunday | 2016 | 1
2652 | 2016-01-03 16:15 | 2016-01-03 16:15 | 13.8KV DURI FIELD FEEDER #2 | Fair | Planned Maintenance | 0 | 16:15 De energized 112.5Kva Tx o/p #06-S1-15. (To repairing Hot Spot at Scondary Bushing of the Tx) 17:00 Energized 112.5Kva Tx o/p #06-S1-15. Cause: Planned Maintenance. | 123 | 1 | 16:15 | Afternoon | Sunday | 2016 | 1
2653 | 2016-02-03 14:19 | 2016-02-03 14:19 | CENTRAL DURI POWER PLANT |  |  | - | 14:19 S/U CGT #3, then on line the Unit at 14:34. |  | 1 | 14:19 | Afternoon | Wednesday | 2016 | 2
2654 | 2016-02-03 16:27 | 2016-02-03 16:27 | MINAS POWER PLANT |  |  | - | 16:27 S/U MGT #2, then on line the Unit at 16:57. |  | 1 | 16:27 | Afternoon | Wednesday | 2016 | 2
2655 | 2016-02-03 17:30 | 2016-02-03 17:30 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Transformer Failure | 7 | It was reported b/o fuse for Tx at Well Ampuh #22. Not checked yet. | 3187850 | 1 | 17:30 | Afternoon | Wednesday | 2016 | 2
2656 | 2016-02-03 17:30 | 2016-03-03 15:26 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Transformer Failure | 7 | 15:26 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Ampuh #22. Replaced b/o fuse above with the same size & energized the Tx, but @1, @3 b/o again. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx Failure. (Low megger reading) (The Tx is not replaced yet) | 3187850 | 1 | 17:30 | Afternoon | Wednesday | 2016 | 2
2657 | 2016-02-03 17:30 | 2016-08-03 15:30 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Transformer Failure | 7 | Replaced 150Kva Tx failure with the same size & energized the Tx at Well Ampuh #22. Cause: Tx Failure. (Low megger reading) | 3187850 | 1 | 17:30 | Afternoon | Wednesday | 2016 | 2
2658 | 2016-02-03 17:57 | 2016-02-03 17:57 | 13.8KV 8C FEEDER #3 | Fair | Unidentified | 0 | 8C VCB fdr #3 T/R 1x. 8C fdr #1 load dropped 152A (166-14A). 8C fdr #4 load dropped 43A (70-27A). Not checked yet. | 3187856 | 1 | 17:57 | Afternoon | Wednesday | 2016 | 2
2659 | 2016-02-03 17:57 | 2016-03-03 11:10 | 13.8KV 8C FEEDER #3 | Fair | Unidentified | 0 | Checked & found, 8C VCB fdr #3 T/R 1x Ctr: 481-482 R/F: 51N & 51@1,@2. Patrolled the line, but found nothing. Cause: Unidentified. | 3187856 | 1 | 17:57 | Afternoon | Wednesday | 2016 | 2
2660 | 2016-02-03 18:08 | 2016-02-03 18:08 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 411 | Off line NDC-CT #1, then S/D the Unit for S/B. (Prior to Off line washing program) Manually load shedding at SLS= 20 MW. Prod. Loss reported by GS: GS-1= 68 Bbls/ 23 Wells & 3 WIPs. GS-2= 47 Bbls/ 11 Wells & 2 WIPs. GS-3= 0 Bbls/ 0 Wells & 0 WIPs. GS-4= 74 Bbls/ 16 Wells & 2 WIPs. GS-5= 114 Bbls/ 29 Wells & 4 WIPs. GS-6= 161 Bbls/ 32 Wells & 2 WIPs. TOTAL Prod. Loss= 464 Bbls/ 111 Wells & 13 WIPs. Prod. loss reported by EC system: SLS (All Minas-GS)= 411 Bbls / 112 Wells. 03-Mar-2016. 14:02 S/U NDC-CT #1, then On Line the Unit at 14:37. (After off line wash program) | 123 | 1 | 18:08 | Afternoon | Wednesday | 2016 | 2
2661 | 2016-03-03 10:08 | 2016-03-03 10:08 | 13.8KV NORTH DURI FEEDER #1 | Fair | Transformer Failure | 26 | It was reported b/o fuse fot Tx o/p #10-J6-21. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx Failure. (Low megger reading) (The Tx is not replaced yet) | 3187850 | 1 | 10:08 | Morning | Thursday | 2016 | 3
2662 | 2016-03-03 10:08 | 14/03/2016 09:38 | 13.8KV NORTH DURI FEEDER #1 | Fair | Transformer Failure | 26 | Checked & found @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #10-J6-21. Re-Megger & TTR test the Tx, found Low megger reading. Cause: Tx failure. (Low megger reading) (The Tx failure is not replaced yet) | 3187850 | 1 | 10:08 | Morning | Thursday | 2016 | 3
2663 | 2016-03-03 10:08 | 19/03/2016 10:08 | 13.8KV NORTH DURI FEEDER #1 | Fair | Transformer Failure | 26 | Replaced 112.5Kva Tx failure with the same size, then energized the Tx o/p #10-J6-21. Cause: Tx failure. (Low megger reading) | 3187850 | 1 | 10:08 | Morning | Thursday | 2016 | 3
2664 | 2016-03-03 10:40 | 2016-03-03 10:40 | 13.8KV BEKASAP FEEDER #3 | Fair | Planned Maintenance | 25 | Performed Switching to normalize Load Bekasap fdr #2 & Bekasap fdr #3. 10:40 Manually Opened LBS #36BD-36. (Bekasap fdr #3) (29 Wells were Off) 10:50 Closed Recl. 37BD-12 (Bekasap #2) (29 Wells were ON & fed by Bekasap fdr #2) Cause: Plan Maintanance. Production loss reported by Bekasap-GS: 38 Bbls / 29 Wells. | 123 | 1 | 10:40 | Morning | Thursday | 2016 | 3
2665 | 2016-03-03 14:02 | 2016-03-03 14:02 | NORTH DURI POWER PLANT | Fair |  | - | 14:02 S/U NDC-CT #1, then On Line the Unit at 14:37. (After off line wash program) |  | 1 | 14:02 | Afternoon | Thursday | 2016 | 3
2666 | 2016-03-03 18:29 | 2016-03-03 18:29 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 2526 | 18:29 Off Line NDC-CT #2, then S/D the Unit at 18:32. (For S/B - Prior to Replacing Generator Rotor) Continued Manually load shedding at SLS= 20 MW. Prod. Loss reported by GS: GS-1= 326 Bbls/ 23 Wells & 3 WIPs. GS-2= 122 Bbls/ 11 Wells & 2 WIPs. GS-3= 0 Bbls/ 0 Wells & 0 WIPs. GS-4= 195 Bbls/ 16 Wells & 2 WIPs. GS-5= 306 Bbls/ 29 Wells & 4 WIPs. GS-6= 433 Bbls/ 32 Wells & 2 WIPs. TOTAL Prod. Loss= 1382 Bbls/ 111 Wells & 13 WIPs. Prod. loss reported by EC system: SLS (All Minas-GS)= 1238 Bbls / 134 Wells. | 123 | 1 | 18:29 | Afternoon | Thursday | 2016 | 3
2667 | 2016-03-03 18:29 | 2016-04-03 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 2526 | Continued Manually load shedding at SLS= 15 MW. Prod. Loss reported by GS: GS-1= 274 Bbls/ 18 Wells & 4 WIPs. GS-2= 79 Bbls/ 6 Wells & 1 WIPs. GS-3= 0 Bbls/ 0 Wells & 0 WIPs. GS-4= 164 Bbls/ 12 Wells & 1 WIPs. GS-5= 262 Bbls/ 21 Wells & 2 WIPs. GS-6= 391 Bbls/ 25 Wells & 1 WIPs. TOTAL Prod. Loss= 1170 Bbls/ 82 Wells & 9 WIPs. Prod. loss reported by EC system: SLS (All Minas-GS)= 1014 Bbls / 110 Wells. | 123 | 1 | 18:29 | Afternoon | Thursday | 2016 | 3
2668 | 2016-03-03 18:29 | 2016-05-03 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 2526 | Continued Manually load shedding at SLS= 5 MW. Prod. Loss reported by GS: GS-1= 83 Bbls/ 18 Wells & 4 WIPs. GS-2= 0 Bbls/ 6 Wells & 1 WIPs. GS-3= 0 Bbls/ 0 Wells & 0 WIPs. GS-4= 52 Bbls/ 12 Wells & 1 WIPs. GS-5= 103 Bbls/ 21 Wells & 2 WIPs. GS-6= 148 Bbls/ 25 Wells & 1 WIPs. ------------------------------------------- TOTAL Prod. Loss= 386 Bbls/ 82 Wells & 9 WIPs. GRAND TOTAL Prod. Loss= 1382 Bbls + 1170 Bbls + 386 Bbls= 2938 Bbls. (111 Wells & 13 WIPs) Prod. loss reported by EC system: SLS (All Minas-GS)= 274 Bbls / 72 Wells. | 123 | 1 | 18:29 | Afternoon | Thursday | 2016 | 3
2669 | 2016-03-03 18:29 | 2016-06-03 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 2526 | Manually load shedding at SLS= 0 MW. (All Manually load shedding were S/U, after S/U MGT #11) Prod. Loss reported by GS: No Manually Load shedding. GRAND TOTAL Prod. Loss= 1382 + 1170 + 386 = 2938 Bbls. (111 Wells & 13 WIPs) (Prod. loss Manually from 03-05 Mar 2016) Prod. loss reported by EC system (From 03-05 Mar 2016): SLS (All Minas-GS)= 0 Bbls / 0 Wells. Grand Total Prod. loss Reported by EC system = 1238 + 1014 + 274 = 2526 Bbls. (134 Wells) | 123 | 1 | 18:29 | Afternoon | Thursday | 2016 | 3
2670 | 2016-04-03 21:05 | 2016-04-03 21:05 | MINAS POWER PLANT |  |  | - | 21:05 S/U MGT #11, then Online the Unit at 22:08. (Major Inspection after Tripped) | 123 | 1 | 21:05 | Night | Sunday | 2016 | 4
2671 | 2016-05-03 01:55 | 2016-05-03 01:55 | SOUTH RUMBAI SUBSTATION | Fair | Pin Insulator | 0 | 01:55 44KV So.Rumbai OCB #1 T/O. (So.Rumbai Substation Black out) 02:59 Checked & found, 44KV So.Rumbai OCB #1 T/O. R/F: 87T-@1 & 86T Ctr: 30-31. Checked the Tx & found, normal. (Good condition) 03:38 Manually open 4.16KV So.Rumbai fdr #1, So.Rumbai fdr #4 & So.Rumbai fdr #2. 03:40 Closed 44KV So.Rumbai OCB #1. (So.Rumbai Substation energized) (After resetting Relay flag & checked the Tx) 03:42 Blocked & closed, 4.16KV So.Rumbai fdr #1. (then released the Block) 03:44 Blocked & closed, 4.16KV So.Rumbai fdr #4. (then released the Block) Blocked & closed 4.16KV So.Rumbai fdr #2, but Re-opened the feeder. (Due to there was spark at the line) 04:03 Blocked & closed 4.16KV So.Rumbai fdr #2, Ok. Then released the Block. (After patrolled the line, but found nothing) 10:19 Re-patrolled So.Rumbai fdr #2 line & found, @1 broken Pin Insulator o/p #4RH-02. Cause: Pin Insulator. | 3187856 | 1 | 1:55 | Night | Tuesday | 2016 | 5
2672 | 2016-06-03 02:26 | 2016-06-03 02:26 | 13.8KV 4B FEEDER #1 | Fair | Recloser | 94 | 02:26 4B OCB fdr #1 T/R 1x. 4B fdr #2 load dropped 70A (121-51A). 4B fdr #3 load dropped 128 (130-2A). 03:51 It was reported by Security that no power at KBJ Switching Sta & Loc. at Area #2A & #3A. 06:45 Checked Recl. 3A-28 (4B fdr #1) & found, normal. Checked Recl. 4B-101 (4B fdr #1) & found, @1 Opened bypass Switch. 07:54 Manually opened 4B OCB fdr #1, to closed @1 Bypass Switch of Recl. 4B-101. 07:57 Manually closed 4B OCB fdr #1. Cause: Recloser By Pass switch. (@1 Opened bypass switch of Recl. 4B-101) Note: Normally Recl. 4B-101 in Bypassed position. | 3187856 | 1 | 2:26 | Night | Friday | 2016 | 6
2673 | 2016-06-03 06:07 | 2016-06-03 06:07 | 13.8KV PUNGUT FEEDER #1 | Fair | Unidentified | 16 | Pungut OCB fdr #1 T/R 1x. Not checked yet. | 3187850 | 1 | 6:07 | Morning | Friday | 2016 | 6
2674 | 2016-06-03 06:07 | 2016-08-03 09:30 | 13.8KV PUNGUT FEEDER #1 | Fair | Unidentified | 16 | Checked & found, Pungut OCB fdr #1 T/R 1x Ctr: 346-347 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3187850 | 1 | 6:07 | Morning | Friday | 2016 | 6
2675 | 2016-06-03 19:38 | 2016-06-03 19:38 | 13.8KV SINTONG GFPC | Fair | Unidentified | 0 | Sintong GFPC T/R 1x. Ground fault alarm on Sintong fdr #1. (No load drop at any fdrs.) Not checked yet. | 3187850 | 1 | 19:38 | Night | Friday | 2016 | 6
2676 | 2016-06-03 19:38 | 2016-07-03 10:00 | 13.8KV SINTONG GFPC | Fair | Unidentified | 0 | Checked & found, Sintong GFPC T/R 2x Ctr: 822-824 R/F: 50N. Patrolled Sintong fdr #1 line, but found nothing. Cause: Unidentified. | 3187850 | 1 | 19:38 | Night | Friday | 2016 | 6
2677 | 2016-07-03 08:51 | 2016-07-03 08:51 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 372 | 08:51 Manually opened Recl. 41AW-62 (C.Duri fdr #1) for Planned Maintenance to: -Tie in Well Kulin #83 -Replaced 30 pcs broken Dead end insulators. -Replaced 12 pcs flash over Pin to Post Insulators. -Replaced 12 pcs broken Lightning arresters. 11:49 Manually closed Recl. 41AW-62, Ok. Cause: Planned maintenance. | 123 | 1 | 8:51 | Morning | Sunday | 2016 | 7
2678 | 2016-07-03 10:30 | 2016-07-03 10:30 | 13.8KV 3D FEEDER #2 | Fair | Transformer Failure | 40 | 10:30 It was reported b/o fuse for Tx at Well #4E-42. (3D fdr #2) 12:35 Checked & found @1,@2 b/o 14.0SF fuses for 550kva TX at Well #4E-42. Test TTR and megger the Tx, found Zerro Megger. Cause: Transformer failure. (zero megger) (The Tx is not replaced yet) | 3187856 | 1 | 10:30 | Morning | Sunday | 2016 | 7
2679 | 2016-07-03 10:30 | 22/03/2016 11:40 | 13.8KV 3D FEEDER #2 | Fair | Transformer Failure | 40 | Replaced 550 Kva Tx with the same size at well 4E-42. Cause: Tx Failure. | 3187856 | 1 | 10:30 | Morning | Sunday | 2016 | 7
2680 | 2016-07-03 18:00 | 2016-07-03 18:00 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 58 | 18:00 It was reported no power at Well #9D-99, 10D-14, 10D-16, 10D-24. (8C fdr #1) 18:50 Checked & found, Recl. 9D-111 (8C fdr #1) T/SO. Ctr: 1231-1232. 18:52 Blocked & closed Recl. 9D-111, Ok. Then released the block. Not Patrolled yet. | 3187856 | 1 | 18:00 | Afternoon | Sunday | 2016 | 7
2681 | 2016-07-03 18:00 | 2016-08-03 07:30 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 58 | Patrolled the line, but found nothing. Cause: Unidentified. | 3187856 | 1 | 18:00 | Afternoon | Sunday | 2016 | 7
2682 | 2016-07-03 19:31 | 2016-07-03 19:31 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 116 | 19:31 Bangko VCB fdr #4 T/O. (in Block Position) Bangko fdr #1 load dropped 31A (204-173A). 19:46 Closed Bangko VCB fdr #4, Ok. 22:25 It was reported no power at 7 wells & Benar-GS. 23:00 Checked & found, Recl. 25Z-07 (Bangko fdr #1) T/SO. Ctr: 81-82. 23:11 Blocked & closed Recl. 25Z-07, Ok. Then released the block. Patrolled the line, but found nothing. Cause: Unidentified. | 3187850 | 1 | 19:31 | Night | Sunday | 2016 | 7
2683 | 2016-07-03 19:31 | 2016-11-03 07:57 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 116 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99982-99983 R/F: 51@1. Patrolled the line & found, @1 broken Pin Insulator o/p #25Z-12. Cause: Pin Insulator. | 3187850 | 1 | 19:31 | Night | Sunday | 2016 | 7
2684 | 2016-08-03 03:50 | 2016-08-03 03:50 | 13.8KV NELLA FEEDER #1 | Rain | Lightning | 0 | Nella fdr #1 load dropped 41A (235-194A). Nella GFPC did not operate. Not checked yet. | 3187850 | 1 | 3:50 | Night | Wednesday | 2016 | 8
2685 | 2016-08-03 03:50 | 2016-11-03 07:55 | 13.8KV NELLA FEEDER #1 | Rain | Lightning | 0 | Checked & found, Recl. 22V-06 (Nella fdr #1) T/R 1x Ctr: 72-73. Patrolled the line & found, @2 broken FCO on TP of Well Bangko #287. Cause: Lightning. | 3187850 | 1 | 3:50 | Night | Wednesday | 2016 | 8
2686 | 2016-08-03 08:08 | 2016-08-03 08:08 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | N.Duri VCB fdr #7 T/R 1x. N.Duri GFPC-Tx #12 T/R 1x. Not checked yet. | 318750 | 1 | 8:08 | Morning | Wednesday | 2016 | 8
2687 | 2016-08-03 08:08 | 2016-11-03 08:00 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | Checked & found, N.Duri VCB fdr #7 T/R 1x Ctr: 183 (Did not change) R/F: 51@1. Patrolled the line, but found nothing. Cause: Unidentified. | 318750 | 1 | 8:08 | Morning | Wednesday | 2016 | 8
2688 | 2016-08-03 11:07 | 2016-08-03 11:07 | 13.8KV BATANG FEEDER #3 | Cloudy and Lightning | Lightning | 7 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3187850 | 1 | 11:07 | Morning | Wednesday | 2016 | 8
2689 | 2016-08-03 11:07 | 2016-11-03 14:42 | 13.8KV BATANG FEEDER #3 | Cloudy and Lightning | Lightning | 7 | Batang OCB fdr #3 T/R 1x Ctr: 310-311 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3187850 | 1 | 11:07 | Morning | Wednesday | 2016 | 8
2690 | 2016-08-03 16:10 | 2016-08-03 16:10 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Lightning | 28 | Pungut fdr #1 Load dropped 54A (78-24A). Pungut fdr #2 Load dropped 20A (87-67A). Not checked yet. | 3187850 | 1 | 16:10 | Afternoon | Wednesday | 2016 | 8
2691 | 2016-08-03 16:10 | 2016-10-03 16:10 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Lightning | 28 | Checked & found, Recl. 45BP-09 (Pungut fdr #1) T/R 1x Ctr: 129-130. Patrolled the line & found: -@3 F/O Pin Insulator o/p #45BO-15 -@2 F/O Pin Insulator o/p #45BO-16. Cause: Lightning. | 3187850 | 1 | 16:10 | Afternoon | Wednesday | 2016 | 8
2692 | 2016-09-03 06:44 | 2016-09-03 06:44 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | Sintong fdr #1 load dropped 10A (56-46A). Ground fault alarm on Sintong fdr #1. Not checked yet. | 3187850 | 1 | 6:44 | Morning | Saturday | 2016 | 9
2693 | 2016-09-03 06:44 | 2016-11-03 07:50 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 26AE-22 (Sintong fdr #1) T/R 2x 153-155. Patrolled the line, but found nothing. Cause: Unidentified. | 3187850 | 1 | 6:44 | Morning | Saturday | 2016 | 9
2694 | 2016-09-03 09:13 | 2016-09-03 09:13 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 2 | 09:13 It was reported b/o fuse for Tx o/p #07-T5-09 (D.Field fdr #2) 11:45 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T5-09. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Squirrel) | 3187850 | 1 | 9:13 | Morning | Saturday | 2016 | 9
2695 | 2016-09-03 16:51 | 2016-09-03 16:51 | 13.8KV MENGGALA FEEDER #1 | Fair | Pin Insulator | 0 | Menggala fdr #1 Load dropped 133A (175-42A). Not checked yet. | 3187850 | 1 | 16:51 | Afternoon | Saturday | 2016 | 9
2696 | 2016-09-03 16:51 | 2016-11-03 08:10 | 13.8KV MENGGALA FEEDER #1 | Fair | Pin Insulator | 0 | Checked & found, Recl. 19AN-04 (Menggala fdr #1) T/R 1x Ctr: 319-320 Patrolled the line & found, @1 broken Pin Insulator o/p #19AK-01 & o/p #19AK-02. Cause: Pin Insulator. | 3187850 | 1 | 16:51 | Afternoon | Saturday | 2016 | 9
2697 | 2016-09-03 18:31 | 2016-09-03 18:31 | 13.8KV 3D FEEDER #4 | Cloudy and Lightning | Lightning | 60 | 3D fdr #4 Load dropped 150A (227-77A). 3D GFPC-Tx #1 T/R 1x. Not checked yet. | 3187856 | 1 | 18:31 | Afternoon | Saturday | 2016 | 9
2698 | 2016-09-03 18:31 | 2016-10-03 15:51 | 13.8KV 3D FEEDER #4 | Cloudy and Lightning | Lightning | 60 | Checked & found, 3D OCB fdr #4 T/R 1x Ctr: 4068-4069 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3187856 | 1 | 18:31 | Afternoon | Saturday | 2016 | 9
2699 | 2016-10-03 14:45 | 2016-10-03 14:45 | 13.8KV KETIGUL FEEDER#3 | Cloudy and Lightning | Lightning | 2 | Ketigul VCB fdr #3 T/R 1x. Not checked yet. | 3187850 | 1 | 14:45 | Afternoon | Monday | 2016 | 10
2700 | 2016-10-03 14:45 | 2016-11-03 14:45 | 13.8KV KETIGUL FEEDER#3 | Cloudy and Lightning | Lightning | 2 | Checked & found, Ketigul VCB fdr #3 T/R 1x Ctr: 168-169 R/F: 51N. Patrolled the line & found, @2 broken L/A o/p #31AR-03. Cause: Lightning. | 3187850 | 1 | 14:45 | Afternoon | Monday | 2016 | 10
2701 | 2016-10-03 15:03 | 2016-10-03 15:03 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 74 | Nella fdr #1 Load dropped 135A (232-97A). Nella GFPC T/R 1x. Not checked yet. | 3187850 | 1 | 15:03 | Afternoon | Monday | 2016 | 10
2702 | 2016-10-03 15:03 | 2016-11-03 14:27 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 74 | Checked & found, Recl. 21V-01 (Nella fdr #1) T/R 1x Ctr: 94-95. Patrolled the line & found, @1 broken L/A on TP of Well Bangko #67. Cause: Lightning. | 3187850 | 1 | 15:03 | Afternoon | Monday | 2016 | 10
2703 | 2016-10-03 17:48 | 2016-10-03 17:48 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 6 | 4D OCB fdr #3 T/R 1x. Not checked yet. | 3187856 | 1 | 17:48 | Afternoon | Monday | 2016 | 10
2704 | 2016-10-03 17:48 | 2016-11-03 11:22 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 6 | Checked & found, 4D OCB fdr #3 T/R 1x Ctr: 357-358 R/F: 51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3187856 | 1 | 17:48 | Afternoon | Monday | 2016 | 10
2705 | 2016-10-03 17:50 | 2016-10-03 17:50 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 3 | 3D OCB fdr #8 T/R 2x. Not checked yet. | 3187856 | 1 | 17:50 | Afternoon | Monday | 2016 | 10
2706 | 2016-10-03 17:50 | 13/03/2016 07:50 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 3 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 172-173 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #3E-04. Cause: Lightning. | 3187856 | 1 | 17:50 | Afternoon | Monday | 2016 | 10
2707 | 2016-10-03 17:52 | 2016-10-03 17:52 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 85 | 4B OCB fdr #1 T/R 1x. 4B fdr #2 load dropped 75A (120-45A). Not checked yet. | 3187856 | 1 | 17:52 | Afternoon | Monday | 2016 | 10
2708 | 2016-10-03 17:52 | 13/03/2016 07:52 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 85 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 262-263 R/F: 51@2. Patrolled the line & found, @2 broken Dead end Insulator o/p #4B-26. Cause: Lightning. | 3187856 | 1 | 17:52 | Afternoon | Monday | 2016 | 10
2709 | 2016-10-03 18:00 | 2016-10-03 18:00 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 49 | 4D fdr #4 Load dropped 198A (232-34A). Not Checked Yet. | 3187856 | 1 | 18:00 | Afternoon | Monday | 2016 | 10
2710 | 2016-10-03 18:00 | 15/03/2016 10:52 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 49 | Checked & found, 4D OCB fdr #4 T/R 1x Ctr: 1613-1614. Patrolled the line & found, @1 broken Pin Insulator o/p #NN. (Near Well #5D-12) Cause: Lightning. | 3187856 | 1 | 18:00 | Afternoon | Monday | 2016 | 10
2711 | 2016-11-03 14:27 | 2016-11-03 14:27 | 13.8KV S. BALAM FEEDER #4 | Fair | Transformer Failure | 5 | 14:27 It was reported b/o fuse for Tx at Well SE.Balam #10. (S.Balam fdr #4) 15:25 Checked & found, @1 b/o 1.0SF fuse for 50Kva Tx at Well SE.Balam #10. Measure TTR & Megger the Tx, found Low megger reading. Cause: Tx failure. | 3187850 | 1 | 14:27 | Afternoon | Thursday | 2016 | 11
2712 | 2016-11-03 14:27 | 2016-12-03 15:10 | 13.8KV S. BALAM FEEDER #4 | Fair | Transformer Failure | 5 | Replaced 50Kva Tx failure with 150Kva Tx at Well SE.Balam #10. (S.Balam fdr #4) Cause: Transformer failure. | 3187850 | 1 | 14:27 | Afternoon | Thursday | 2016 | 11
2713 | 2016-12-03 00:25 | 2016-12-03 00:25 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 37 | 4D fdr #2 load dropped 116 A(161-45A). Not checked yet. | 3187856 | 1 | 0:25 | Night | Saturday | 2016 | 12
2714 | 2016-12-03 00:25 | 15/03/2016 11:30 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 37 | Checked & found, Recl. 2D-204 (4D fdr #2) T/R 1x Ctr: 15-16. Patrolled the line & found, @3 broken L/A o/p #3D-155. Cause: Lightning. | 3187856 | 1 | 0:25 | Night | Saturday | 2016 | 12
2715 | 2016-12-03 03:09 | 2016-12-03 03:09 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Powerline - Jumper | 487 | 03:09 4B fdr #1 load dropped 279 A (285-6A). 11:36 Checked & found, @1 broken jumper of bypass SW of Recl. 4B-101. 17:25 Open LBS #4B-90. 17:32 Open LBS #4A-70. -Replaced @1 broken Bypass jumper of Recl. 4B-101. -Replaced @1 broken Dead end insulators. 20:04 Closed LBS #4A-70. 20:06 Closed LBS #4B-90. Cause: Broken jumper. | 3187856 | 1 | 3:09 | Night | Saturday | 2016 | 12
2716 | 2016-12-03 08:50 | 2016-12-03 08:50 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 33 | 08:50 It was reported b/o fuse for Tx o/p #08-M2-B02. (C.Duri fdr #14) 10:30 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #08-M2-B02. Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal. (Monkey) | 3187850 | 1 | 8:50 | Morning | Saturday | 2016 | 12
2717 | 2016-12-03 09:30 | 2016-12-03 09:30 | 13.8KV NORTH DURI FEEDER #6 | Fair | Animal | 27 | 09:30 It was reported b/o fuse for Tx o/p #12-G2-05. 13:10 Checked & found, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #12-G2-05. Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal. (Snake) | 3187850 | 1 | 9:30 | Morning | Saturday | 2016 | 12
2718 | 2016-12-03 15:00 | 2016-12-03 15:00 | 13.8KV MINAS FEEDER #4 | Fair | Switchboard Problem | - | It was reported unbalance voltage at Well #8D-26. Not checked yet. | 3187856 | 1 | 15:00 | Afternoon | Saturday | 2016 | 12
2719 | 2016-12-03 15:00 | 13/03/2016 11:24 | 13.8KV MINAS FEEDER #4 | Fair | Switchboard Problem | - | Checked & found, @1 b/o 7.0SF fuse for 225Kva Tx at Well #8D-26. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Burnt out fuse of Switchboard. (No Prod. loss charged to PGT) | 3187856 | 1 | 15:00 | Afternoon | Saturday | 2016 | 12
2720 | 2016-12-03 15:10 | 2016-12-03 15:10 | 13.8KV KOTABATAK FEEDER #2 | Fair | Transformer Failure | 35 | It was reported b/o fuse for Tx at Well KB #133. Checked & found, @3 b/o 14.0SF fuse for 550Kva Tx at Well KB #133. Performed TTR & Megger Test the Tx, found Zero Megger reading. Cause: Transformer Failure. (The Tx failure is not replaced yet) | 3187856 | 1 | 15:10 | Afternoon | Saturday | 2016 | 12
2721 | 2016-12-03 15:10 | 13/03/2016 11:45 | 13.8KV KOTABATAK FEEDER #2 | Fair | Transformer Failure | 35 | Replaced 550Kva Tx with the same size at Well KB #133, then energized the Tx. Cause: Transformer Failure. | 3187856 | 1 | 15:10 | Afternoon | Saturday | 2016 | 12
2722 | 2016-12-03 17:50 | 2016-12-03 17:50 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 17:50 It was reported b/o fuses for Tx o/p #03-05-06. (C.Duri fdr #7) 18:45 Checked & found, @1,@2 b/o 3.1Sf fuses for 112.5Kva Tx o/p #03-05-06. Replaced b/o fuses above with the same size, then energized the Tx. Cause: Unidentified (fuse). | 3187850 | 1 | 17:50 | Afternoon | Saturday | 2016 | 12
2723 | 2016-03-13 02:36 | 2016-03-13 02:36 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Duri Community ACB fdr #3 T/R 1x. Not checked yet. | 3187850 | 1 | 2:36 | Night | Sunday | 2016 | 3
2724 | 2016-03-13 02:36 | 2016-03-14 16:15 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Checked & found, Duri Community ACB fdr #3 T/R 1x Ctr: 50-51 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator o/p #2DG-24. Cause: Pin Insulator. | 3187850 | 1 | 2:36 | Night | Sunday | 2016 | 3
2725 | 2016-03-13 08:35 | 2016-03-13 08:35 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 96 | Ketigul VCB fdr #1 T/R 1x. (Ketigul GFPC was in block position for Rig Job) Not checked yet. | 3187850 | 1 | 8:35 | Morning | Sunday | 2016 | 3
2726 | 2016-03-13 08:35 | 2016-03-14 13:45 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 96 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 199-200 R/F: 51N. Patrolled the line & found, @3 F/O Pin Insulator o/p #29AL-22. Cause: Lightning. | 3187850 | 1 | 8:35 | Morning | Sunday | 2016 | 3
2727 | 2016-03-14 17:44 | 2016-03-14 17:44 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 28 | 5B OCB fdr #2 T/R 2x. 5B fdr #1 load dropped 62A (92-30A). Not Checked yet. | 3187856 | 1 | 17:44 | Afternoon | Monday | 2016 | 3
2728 | 2016-03-14 17:44 | 2016-03-15 17:44 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 28 | Checked & found, 5B OCB fdr #2 T/R 2x Ctr: 336-338 R/F: 51N & 51@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3187856 | 1 | 17:44 | Afternoon | Monday | 2016 | 3
2729 | 2016-03-14 17:48 | 2016-03-14 17:48 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 80 | 17:48 6DN OCB fdr #2 T/R 1x 21:56 It was reported no power at some wells downstream of 6DN fdr #2. 23:21 Checked & found, Recl. 6D-50 (6DN fdr #2) T/SO. Ctr: 51-52. 23:24 Blocked & closed Recl. 6D-50A, but failed. (Postponed by hard rain) 15-Mar-2016 at 09:59. Checked & found, 6DN OCB fdr #2 T/R 1x Ctr: 296-297 R/F: 50@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. Also Checked & found, Recl. 6D-50 (6DN fdr #2) T/SO. Ctr: 51-52. (Recloser Control problem / broken Push Button) Then patrolled the line, but found nothing. 10:08 Blocked & closed Recl. 6D-50A, Ok. Then released the block. (After replaced broken Push Button above) | 3187856 | 1 | 17:48 | Afternoon | Monday | 2016 | 3
2730 | 2016-03-14 17:53 | 2016-03-14 17:53 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 42 | Minas fdr #1 load dropped 135A (135-0A). Not checked yet. | 3187856 | 1 | 17:53 | Afternoon | Monday | 2016 | 3
2731 | 2016-03-14 17:53 | 2016-03-15 14:15 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 42 | Checked & found, Recl. 7D-21 (Minas fdr #1) T/R 1x Ctr: 146-147. Patrolled the line & found, @3 broken Pin Insulator o/p #7D-19. Cause: Lightning. | 3187856 | 1 | 17:53 | Afternoon | Monday | 2016 | 3
2732 | 2016-03-14 17:55 | 2016-03-14 17:55 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 98 | 6D OCB fdr #2 T/R 1x. 6D fdr #1 load dropped 179A (254-75A). 6D fdr #5 load dropped 166A (232-66A). Not checked yet. | 3187856 | 1 | 17:55 | Afternoon | Monday | 2016 | 3
2733 | 2016-03-14 17:55 | 2016-03-15 14:20 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 98 | Checked & found, 6D OCB fdr #2 T/R 1x Ctr: 232-233 R/F: 51@2. Patrolled the line & found: -@2 Pin Insulator & @1 F/O Pin Insulator o/p #6D-78A. Cause: Lightning. | 3187856 | 1 | 17:55 | Afternoon | Monday | 2016 | 3
2734 | 2016-03-15 14:43 | 2016-03-15 14:43 | 115KV CENTRAL DURI - BATANG LINE | Rain | Unidentified | 49 | 14:43 115KV C.Duri GCB #31 T/R 1x R/F: 21@1 Ctr: Not checked yet. 115KV C.Duri GCB #33 T/SO. 115KV Sintong GCB #25 T/R 1x. (115KV Batang-Sintong line) (Batang Substation No power at the time) 14:51 Closed 115KV C.Duri GCB #33. Not checked yet. Prod. Loss: Batang fdr #1: 30 Bbls, 19 Wells. Batang fdr #2: 0 Batang fdr #3: 53 Bbls, 19 Wells. | 3187850 | 1 | 14:43 | Afternoon | Tuesday | 2016 | 3
2735 | 2016-03-15 14:43 | 2016-03-18 08:35 | 115KV CENTRAL DURI - BATANG LINE | Rain | Unidentified | 49 | Checked and found : -115KV C.Duri GCB #31 T/R 1x Ctr: 29-30 R/F: 21@3. -115KV C.Duri GCB #33 T/SO Ctr: 586. -115KV Sintong GCB #25 T/R 1x Ctr: 289-290 R/F: 87L-3, 21C-G & 67N (Instan). (115KV Batang-Sintong line). Patrolled the line, but nothing found. Cause: Unidentified. | 3187850 | 1 | 14:43 | Afternoon | Tuesday | 2016 | 3
2736 | 2016-03-16 06:55 | 2016-03-16 06:55 | 13.8KV DURI FIELD FEEDER #2 | Fair | Main breaker | - | 06:55 It was reported b/o fuse for Tx o/p #07-U5-17. (DF fdr #2) 10:21 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-U5-17. Also found spark at Main Breaker (Waiting electrician for replacing The Main Breaker). Cause: Main Breaker. | 3187856 | 1 | 6:55 | Morning | Wednesday | 2016 | 3
2737 | 2016-03-16 10:00 | 2016-03-16 10:00 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 62 | 10:00 Manual opened Recl. 45BR-01 (Pungut fdr #2), for Planning Maintenance: - C/O Pin to Post Type Insulator. - C/O Flash over pin insulator o/p 46BT-12. - C/O obsolete FCO at Tandun #1. - Cut high Trees at Tandun #08. 14:02 Closed Recl. 45BR-01. Cause: Planned Maintenance. | 123 | 1 | 10:00 | Morning | Wednesday | 2016 | 3
2738 | 2016-03-16 10:31 | 2016-03-16 10:31 | CENTRAL DURI POWER PLANT | Fair |  | - | 10:31 Offline CGT #4, then S/D the Unit for S/B. (For troubleshooting DC Ground) 10:35 Closed C.Duri ACB #39. (Tie Breaker) 17-Mar-2016 12:04 S/U CGT #4, then online the Unit at 12:26. (after replacing b/o cable-33CB & replaced Gauge-P1) 12:24 Open C.Duri ACB #39. (Tie Breaker) |  | 1 | 10:31 | Morning | Wednesday | 2016 | 3
2739 | 2016-03-16 15:24 | 2016-03-16 15:24 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 0 | 15:24 It was reported b/o fuse for Tx o/p #09-M1-20. 17:00 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #09-M1-20. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3187850 | 1 | 15:24 | Afternoon | Wednesday | 2016 | 3
2740 | 2016-03-16 15:29 | 2016-03-16 15:29 | SINABUNG MINI SUBSTATION | Fair | Under investigation | 0 | 15:29 It was reported no power at REM & Security Office Building. 16:11 Checked & found, 13.8KV Recl. for 2500KVA Tx at Sinabung Mini SS T/O. Ctr: 223-224. Visual checked the Tx & found, normal condition. 16:14 Manual Opened 4.16KV Recl. at Sinabung Mini SS. Closed 13.8KV Recl. for Tx above, ok. 16:18 Closed 4.16KV Recl. at Sinabung Mini SS, ok. Cause: Under Investigation. | 3187850 | 1 | 15:29 | Afternoon | Wednesday | 2016 | 3
2741 | 2016-03-16 18:16 | 2016-03-16 18:16 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 0 | It was reported b/o fuse for Tx o/p 09-N6-06. Not checked yet. | 3187850 | 1 | 18:16 | Afternoon | Wednesday | 2016 | 3
2742 | 2016-03-16 18:16 | 2016-03-17 09:55 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 0 | Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #09-N6-06. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal (Monkey). | 3187850 | 1 | 18:16 | Afternoon | Wednesday | 2016 | 3
2743 | 2016-03-17 06:02 | 2016-03-17 06:02 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning Arrester | 0 | Sintong fdr #2 Load dropped 9A (211-202A). Sintong GFPC T/R 1x. Not checked yet. | 3187850 | 1 | 6:02 | Morning | Thursday | 2016 | 3
2744 | 2016-03-17 06:02 | 2016-03-19 07:48 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning Arrester | 0 | Checked & found Recl. 29Z-13A (Sintong fdr #2) T/R 1x Ctr: 85-86. Also found, Sintong GFPC T/R 1x Ctr: 827-828. Patrolled the line & found, @3 broken L/A on TP of Well Perkebunan #01. Cause: Lightning Arrester. | 3187850 | 1 | 6:02 | Morning | Thursday | 2016 | 3
2745 | 2016-03-17 06:05 | 2016-03-17 06:05 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 10 | C.Duri ACB fdr #7 T/R 1x Ctr: 460-461 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3187850 | 1 | 6:05 | Morning | Thursday | 2016 | 3
2746 | 2016-03-17 09:40 | 2016-03-17 09:40 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Planned Maintenance | 0 | 09:40 Manual Opened Recl. 29CX-05 (Petapahan fdr #2), to Tie in new Well Petapahan #123. 10:40 Closed Recl. 29CX-05. Cause: Planned Maintenance. | 123 | 1 | 9:40 | Morning | Thursday | 2016 | 3
2747 | 2016-03-17 11:20 | 2016-03-17 11:20 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Broken Fuse Holder | 2 | 11:20 It was reported b/o fuse for Tx o/p #03-05-06. 14:45 Checked & found, @2, @3 broken fuse holders for 112.5Kva Tx o/p #03-05-06. Replaced broken fuse holders above then energized the Tx. Cause: Broken Fuse Holder. | 3187850 | 1 | 11:20 | Morning | Thursday | 2016 | 3
2748 | 2016-03-17 12:04 | 2016-03-17 12:04 | CENTRAL DURI POWER PLANT | Fair |  | - | 12:04 S/U CGT #4, then online the Unit at 12:26. 12:24 Opened C.Duri ACB #39. (Tie Breaker) |  | 1 | 12:04 | Afternoon | Thursday | 2016 | 3
2749 | 2016-03-17 14:24 | 2016-03-17 14:24 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Animal | 0 | 14:24 It was reported b/o fuse for Tx at 3SC Test Station. 15:41 Checked & found, @1 b/o 14.0SF fuse for 750Kva Tx at 3SC Test Station. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Squirrel) | 3187850 | 1 | 14:24 | Afternoon | Thursday | 2016 | 3
2750 | 2016-03-17 15:00 | 2016-03-17 15:00 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified (Fuse) | 0 | 15:00 It was reported b/o fuse for Tx at Well #2P-77B & 2P-77C. (C.Duri fdr #13) 16:10 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx at Well #2P-77B & 77C. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3187850 | 1 | 15:00 | Afternoon | Thursday | 2016 | 3
2751 | 2016-03-17 16:34 | 2016-03-17 16:34 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 71 | Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #1 load dropped 26A (158-132A). Not checked yet. | 3187850 | 1 | 16:34 | Afternoon | Thursday | 2016 | 3
2752 | 2016-03-17 16:34 | 2016-03-19 14:52 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 71 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 200-201 R/F: 51N. Patrolled the line, but nothing found. Cause: Unidentified. | 3187850 | 1 | 16:34 | Afternoon | Thursday | 2016 | 3
2753 | 2016-03-18 09:30 | 2016-03-18 09:30 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 09:30 It was reported b/o fuse for Tx o/p #01-06-20. 10:30 Checked & found, @2 b/o 3.1SF fuse for 112.5kva Tx o/p #01-06-20. Performed TTR & Megger test the Tx & found, normal. (good reading) Replaced b/o fuse above with same size then energized the Tx. Cause: Unidentified (Fuse). | 3187850 | 1 | 9:30 | Morning | Friday | 2016 | 3
2754 | 2016-03-19 06:06 | 2016-03-19 06:06 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | 06:06 C.Duri ACB fdr #5 T/R 1x Ctr: 226-227 R/F: 51N. 08:53 C.Duri ACB fdr #5 T/R 1x again. Ctr: 227-228 R/F: 51N. The line is not patrolled yet. | 3187850 | 1 | 6:06 | Morning | Saturday | 2016 | 3
2755 | 2016-03-19 06:06 | 2016-03-22 07:06 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | Patrolled the line, but nothing found. Cause: Unidentified. | 3187850 | 1 | 6:06 | Morning | Saturday | 2016 | 3
2756 | 2016-03-19 06:28 | 2016-03-19 06:28 | 13.8KV BATANG FEEDER #3 | Fair | Pin Insulator | 47 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3187850 | 1 | 6:28 | Morning | Saturday | 2016 | 3
2757 | 2016-03-19 06:28 | 2016-03-23 09:13 | 13.8KV BATANG FEEDER #3 | Fair | Pin Insulator | 47 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 311-312 R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator o/p #37AL-17. Cause: Pin Insulator. | 3187850 | 1 | 6:28 | Morning | Saturday | 2016 | 3
2758 | 2016-03-19 08:36 | 2016-03-19 08:36 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 08:36 It was reported b/o fuse for Tx o/p #01-03-08. 13:22 Checked & found, @2 b/o 3.1SF fuse for 112.5kva Tx o/p #01-03-08. Performed TTR, Megger test the Tx & found, normal. (Good reading) Replaced b/o fuse above with same size then energized the Tx. Cause: Unidentified (Fuse). | 3187850 | 1 | 8:36 | Morning | Saturday | 2016 | 3
2759 | 2016-03-19 17:16 | 2016-03-19 17:16 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 26 | C.Duri fdr #1 Load dropped 102A (257-155A). Not checked yet | 3187850 | 1 | 17:16 | Afternoon | Saturday | 2016 | 3
2760 | 2016-03-19 17:16 | 2016-03-21 16:06 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 26 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 233-234. Patrolled the line, but nothing found. Cause: Unidentified. | 3187850 | 1 | 17:16 | Afternoon | Saturday | 2016 | 3
2761 | 2016-03-20 03:58 | 2016-03-20 03:58 | 13.8KV S. BALAM GFPC | Rain and Lightning | Lightning | 0 | So.Balam GFPC T/R 1x. Ground fault alarm on So.Balam fdr #1. (No load drop at any fdr) Not checked yet. | 3187850 | 1 | 3:58 | Night | Sunday | 2016 | 3
2762 | 2016-03-20 03:58 | 2016-03-21 07:57 | 13.8KV S. BALAM GFPC | Rain and Lightning | Lightning | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 203-204. Patrolled So.Balam fdr #1 line, nothing found. Cause: Suspected by Lightning. | 3187850 | 1 | 3:58 | Night | Sunday | 2016 | 3
2763 | 2016-03-20 07:55 | 2016-03-20 07:55 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Duri Community ACB fdr #3 T/R 1x. Not checked yet. | 3187850 | 1 | 7:55 | Morning | Sunday | 2016 | 3
2764 | 2016-03-20 07:55 | 2016-03-24 08:05 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #3 T/R 1x Ctr: 51-52 R/F: 51N. Patrolled the line, but nothing found. Cause: Unidentified. | 3187850 | 1 | 7:55 | Morning | Sunday | 2016 | 3
2765 | 2016-03-20 07:57 | 2016-03-20 07:57 | 13.8KV CENTRAL DURI FEEDER #12 | Fair | Unidentified | 0 | C.Duri ACB fdr #12 T/R 1x Ctr: 479-480 R/F: 51N & 51@1. The line is not patrolled yet. | 3187850 | 1 | 7:57 | Morning | Sunday | 2016 | 3
2766 | 2016-03-20 07:57 | 2016-03-22 16:31 | 13.8KV CENTRAL DURI FEEDER #12 | Fair | Unidentified | 0 | Patrolled the line, but nothing found. Cause: Unidentified. | 3187850 | 1 | 7:57 | Morning | Sunday | 2016 | 3
2767 | 2016-03-20 08:19 | 2016-03-20 08:19 | 13.8KV BANGKO FEEDER #3 | Cloudy and Lightning | Lightning | 30 | Bangko VCB fdr #3 T/R 1x. Bangko fdr #4 load dropped 90A (223-133A). Bangko fdr #2 load dropped 53A (224-171A). Not checked yet. | 3187850 | 1 | 8:19 | Morning | Sunday | 2016 | 3
2768 | 2016-03-20 08:19 | 2016-03-21 14:19 | 13.8KV BANGKO FEEDER #3 | Cloudy and Lightning | Lightning | 30 | Checxked & found, Bangko OCB fdr #3 T/R 1x Ctr: 99936-99937 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3187850 | 1 | 8:19 | Morning | Sunday | 2016 | 3
2769 | 2016-03-20 08:32 | 2016-03-20 08:32 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 2 | 08:32 It was reported b/o fuse for Tx o/p #03-8A-02. 09:52 Checked & found, @1 b/o 3.5SF fuse for 112.5Kva Tx o/p #03-8A-02. Performed TTR and Megger Test the Tx, found good reading. Replaced b/o fuse above with same size then energized the Tx. Cause: Unidentified (Fuse). | 3187850 | 1 | 8:32 | Morning | Sunday | 2016 | 3
2770 | 2016-03-20 08:49 | 2016-03-20 08:49 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 3 | 08:49 It was reported b/o fuse for Tx o/p 09-M1-11. 10:12 Checked and found, @1 b/o fuse for 112.5 kva TX. Performed TTR and Megger Test the TX, found good reading. Replaced b/o fuse above with same size then energized the TX. Cause: Animal (monkey). | 3187850 | 1 | 8:49 | Morning | Sunday | 2016 | 3
2771 | 2016-03-20 13:50 | 2016-03-20 13:50 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 13:50 It was reported b/o fuse for Tx at Well Pematang Bow #27. 16:00 Checked & found, @1 b/o 7.8SF fuse for 300kva Tx at Well Pematang Bow #27. Performed TTR & Megger Test the Tx, found good reading. Replaced b/o fuse above with same size then energized the Tx. Cause: Unidentified (fuse). | 3187850 | 1 | 13:50 | Afternoon | Sunday | 2016 | 3
2772 | 2016-03-20 13:55 | 2016-03-20 13:55 | NORTH DURI POWER PLANT |  |  | - | 13:56 S/U NDC-CT #2, then online the Unit at 15:08. (Running on test after replacing Generator Rotor) |  | 1 | 13:55 | Afternoon | Sunday | 2016 | 3
2773 | 2016-03-20 15:08 | 2016-03-20 15:08 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Animal | 12 | 15:08 It was reported b/o fuse for Tx o/p #04-05-12. 16:27 Checked & found, @1 b/o 3.1SF fuse for 112.5kva Tx o/p #04-05-12. Performed TTR & Megger Test the Tx, found good reading. Replaced b/o fuse above with same size then energized the Tx. Cause: Animal. (Squirrel) | 3187850 | 1 | 15:08 | Afternoon | Sunday | 2016 | 3
2774 | 2016-03-21 | 2016-03-21 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Pin Insulator | 231 | 00:00 5B fdr #4 load dropped 189A (251-62A). (The weather was still rain) 02:37 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO. Ctr: 50-51. 02:39 Blocked & closed Recl. 4B-73, Ok. Then released the block. 07:03 5B fdr #4 load dropped again 142A (208-66A). 09:08 Checked & found, Recl. 4B-73 95B fdr #4) T/LO. Ctr: 51-55. Patrolled line & found, @2 broken Pin Insulator o/p #3B-30. (Jumper touched to steel pin) 09:50 Opened LBS #3B-22, to isolated line toward Pole #3B-30. 10:00 Blocked & closed Recl. 4B-73, Ok. Then normalize the block. (Then replaced broken Pin Insulator o/p #3B-30) 11:20 Closed LBS #3B-22. Cause: Pin insulator. | 3187856 | 1 | 0:00 | Night | Monday | 2016 | 3
2775 | 2016-03-21 00:02 | 2016-03-21 00:02 | 115KV KOTABATAK JUNCTION - 4D LINE | Rain and Lightning | Lightning | 77 | 115KV 4D GCB #22 T/R 1x. 115KV 4D GCB #24 T/R 1x. 115KV KBJ GCB #28 & GCB #24 (No Alarm Tripped et DSC) (115KV KBJ - 4D Line) Respectively load dropped: 4D fdr #4 load dropped 24A (235-211A). 3D fdr #7 load dropped 113A (231-118A). 3D fdr #8 load dropped 9A (260-251A). 6DN fdr #3 load dropped 129A (194-65A). T/O WIP at GS-3. 6DN fdr #4 load dropped 131A (208-77A). T/O WIP at GS-3. Not checked yet. | 3187856 | 1 | 0:02 | Night | Monday | 2016 | 3
2776 | 2016-03-21 00:02 | 2016-03-22 07:22 | 115KV KOTABATAK JUNCTION - 4D LINE | Rain and Lightning | Lightning | 77 | Checked & found : -115KV 4D GCB #22 T/R 1x Ctr: 169 (Did not change) -115KV 4D GCB #24 T/R 1x Ctr: 415-416 R/F: 87L@3. -115KV KBJ GCB #28 T/R 1x Ctr: 312-313 R/F: 87L@3 & 21BC-G. -115KV KBJ GCB #24 T/SO. Ctr: Not reported yet. (115KV KBJ - 4D Line) Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3187856 | 1 | 0:02 | Night | Monday | 2016 | 3
2777 | 2016-03-21 01:28 | 2016-03-21 01:28 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Unidentified (Fuse) | 47 | 01:28 It was reported b/o fuse for Tx at Well Petapahan #88. 08:30 Checked & found, @2 b/o 3.5SF fuse for 150kva Tx at Well Petapahan #88. Performed TTR & Megger Test the Tx, found good reading. Replaced b/o fuse above with same size then energized the Tx. Cause: Unidentified (Fuse). | 3187856 | 1 | 1:28 | Night | Monday | 2016 | 3
2778 | 2016-03-21 01:57 | 2016-03-21 01:57 | MINAS POWER PLANT | Fair | Under investigation | - | MGT #8 Tripped by Alarm: -High Pressure Mag Pickup Fault. -Computer-S Problem. (No load shedding) Cause: Under Investigation. | 3187856 | 1 | 1:57 | Night | Monday | 2016 | 3
2779 | 2016-03-21 08:48 | 2016-03-21 08:48 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 48 | 08:48 It was reported no power at along one road. (near pole #09-M3-02) 09:10 Checked & found, Recl. 09-M3-01 (C.Duri fdr #1) T/SO. Ctr: 42-43. Patrolled the line & found, b/o fuse for Tx o/p #09-M3-04. (Then replaced b/o fuse with same size o/p above) 09:28 Blocked & closed Recl. 09-M3-01, Ok. Then normalized the block. 18:15 It was reported no power at along one road. (near pole #09-M3-02) 19:45 Checked & found, Recl. 09-M3-01 T/SO again. Ctr: 43-44. Patrolled the line, but found nothing. 20:18 Blocked & closed Recl. 09-M3-01, Ok. Then released the block. Cause: Unidentified. | 3187850 | 1 | 8:48 | Morning | Monday | 2016 | 3
2780 | 2016-03-21 16:51 | 2016-03-21 16:51 | 13.8KV CENTRAL DURI FEEDER #16 | Heavy Rain | Lightning | 0 | C.Duri ACB fdr #16 T/R 1x Ctr: 285-286 R/F: 51@1,@2. The line is not patrolled yet. | 3187850 | 1 | 16:51 | Afternoon | Monday | 2016 | 3
2781 | 2016-03-21 16:51 | 2016-03-22 16:28 | 13.8KV CENTRAL DURI FEEDER #16 | Heavy Rain | Lightning | 0 | Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3187850 | 1 | 16:51 | Afternoon | Monday | 2016 | 3
2782 | 2016-03-21 16:55 | 2016-03-21 16:55 | 13.8KV CENTRAL DURI FEEDER #3 | Heavy Rain | Lightning | 0 | C.Duri ACB fdr #3 T/R 1x Ctr: 182-183 R/F: 51N(@3). The line is not patrolled yet. | 3187850 | 1 | 16:55 | Afternoon | Monday | 2016 | 3
2783 | 2016-03-21 16:55 | 2016-03-22 16:30 | 13.8KV CENTRAL DURI FEEDER #3 | Heavy Rain | Lightning | 0 | Patrolled the line & found, @3 broken Pin Insulator o/p #03-08-13. Cause: Lightning. | 3187850 | 1 | 16:55 | Afternoon | Monday | 2016 | 3
2784 | 2016-03-21 17:13 | 2016-03-21 17:13 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Rangau fdr #2 load dropped 70A (81-11A). Not checked yet. | 3187850 | 1 | 17:13 | Afternoon | Monday | 2016 | 3
2785 | 2016-03-21 17:13 | 2016-03-24 07:22 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: 158-159. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3187850 | 1 | 17:13 | Afternoon | Monday | 2016 | 3
2786 | 2016-03-21 17:16 | 2016-03-21 17:16 | MINAS POWER PLANT |  |  | - | 17:16 S/U MGT #10, then online the Unit at 18:00. (Running on test) |  | 1 | 17:16 | Afternoon | Monday | 2016 | 3
2787 | 2016-03-21 17:29 | 2016-03-21 17:29 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 26 | C.Duri ACB fdr #1 T/R 1x Ctr: 183-184 R/F: 51@1. The line is not patrolled yet. | 3187850 | 1 | 17:29 | Afternoon | Monday | 2016 | 3
2788 | 2016-03-21 17:29 | 2016-03-22 16:25 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 26 | Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3187850 | 1 | 17:29 | Afternoon | Monday | 2016 | 3
2789 | 2016-03-21 19:45 | 2016-03-21 19:45 | MINAS POWER PLANT |  |  | - | 19:45 Offline MGT #3, then S/D the Unit for S/B. |  | 1 | 19:45 | Night | Monday | 2016 | 3
2790 | 2016-03-22 01:41 | 2016-03-22 01:41 | 13.8KV 8D FEEDER #1 | Fair | Pin Insulator | 50 | 01:41 8D OCB fdr #1 T/R 2X. 8D fdr #2 load dropped 18A (117-99A). 8D fdr #3 load dropped 15A (188-173A). 11:03 Checked & found, 8D OCB fdr #1 T/R 2x Ctr: 1982-1984 R/F: 51@2. Patrolled the line & found, @2 broken Pin insulator o/p #MB-12. Cause: Pin Insulator. | 3187856 | 1 | 1:41 | Night | Tuesday | 2016 | 3
2791 | 2016-03-22 01:46 | 2016-03-22 01:46 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 35 | 6D fdr #2 load dropped 155A (216-61A). 6D fdr #5 load dropped 8A (188-173A). Not checked yet. | 3187856 | 1 | 1:46 | Night | Tuesday | 2016 | 3
2792 | 2016-03-22 01:46 | 2016-03-23 13:36 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 35 | Checked & found, Recl. 6D-298 (6D fdr #2) T/R 2x Ctr: 35-37. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3187856 | 1 | 1:46 | Night | Tuesday | 2016 | 3
2793 | 2016-03-22 01:54 | 2016-03-22 01:54 | 13.8KV MINAS FEEDER #5 | Rain and Lightning | Lightning | 3 | 01:54 Minas ACB fdr #5 T/R 1x. Minas fdr #6 load dropped 95A (205-110A). 13:28 Checked & found, Minas ACB fdr #5 T/R 1x Ctr: 76-77 R/F: 51@2. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3187856 | 1 | 1:54 | Night | Tuesday | 2016 | 3
2794 | 2016-03-22 05:51 | 2016-03-22 05:51 | CENTRAL DURI POWER PLANT | Rain | Under investigation | - | 05:51 CGT #4 Tripped by Alarm: DC Ground. (No load shedding) 05:57 Closed Tie Breaker ACB #39. Cause: Under Investigation. | 3187850 | 1 | 5:51 | Morning | Tuesday | 2016 | 3
2795 | 2016-03-22 06:33 | 2016-03-22 06:33 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 9 | 06:33 It was reported b/o fuse for Tx o/p #01-2-16. (C.Duri fdr #3) 15:20 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-2-16. Tested the Tx & found, low megger reading. Cause: Transformer Failure. (Low megger reading) (The Tx failure is not replaced yet) | 3187850 | 1 | 6:33 | Morning | Tuesday | 2016 | 3
2796 | 2016-03-22 06:33 | 26/04/2016 11:00 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 9 | Replaced 112.5Kva TX with the same size & energized the Tx o/p #01-02-16. Cause: Transformer failure. | 3187850 | 1 | 6:33 | Morning | Tuesday | 2016 | 3
2797 | 2016-03-22 09:27 | 2016-03-22 09:27 | 13.8KV KETIGUL FEEDER#3 | Cloudy and Lightning | Lightning | 3 | Ketigul VCB fdr #3 T/R 1x. Ketigul fdr #1 Load dropped 60A (158-98A). Ketigul fdr #2 Load dropped 12A (197-185A). Not checked yet. | 3187850 | 1 | 9:27 | Morning | Tuesday | 2016 | 3
2798 | 2016-03-22 09:27 | 2016-03-24 07:38 | 13.8KV KETIGUL FEEDER#3 | Cloudy and Lightning | Lightning | 3 | Checked & found, Ketigul VCB fdr #3 T/R 1x Ctr: 169-170 R/F: 51N. Patrolled the line & found, @3 broken L/A o/p #31AR-03. Cause: Lightning. | 3187850 | 1 | 9:27 | Morning | Tuesday | 2016 | 3
2799 | 2016-03-22 10:29 | 2016-03-22 10:29 | MINAS POWER PLANT |  |  | - | 10:29 MGT #10 Tripped by Alarm: Fire In Turbin Compartment. (While Running on Test after replacing Generator Rotor) Cause: Under Investigation. |  | 1 | 10:29 | Morning | Tuesday | 2016 | 3
2800 | 2016-03-22 10:55 | 2016-03-22 10:55 | 13.8KV 8D FEEDER #11 | Fair | Transformer Failure | 358 | 10:55 It was reported b/o fuse for Tx at Well #8E-74A. (8D fdr #11) 18:15 Checked & found, @2, @3 b/o 14.0SF fuses for 550Kva Tx at Well #8E-74A. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Transformer Failure. (Low megger reading) (The Tx failure is not replaced yet) | 3187856 | 1 | 10:55 | Morning | Tuesday | 2016 | 3
2801 | 2016-03-22 10:55 | 2016-01-04 16:00 | 13.8KV 8D FEEDER #11 | Fair | Transformer Failure | 358 | Replaced 550 KVa Tx with same size at well 8E 74A. and then Energized the Tx. Cause: Tx failure (Low megger reading). Due to Tx no available and Foco Truck license. | 3187856 | 1 | 10:55 | Morning | Tuesday | 2016 | 3
2802 | 2016-03-22 13:30 | 2016-03-22 13:30 | 13.8KV 6DN FEEDER #2 | Fair | Unidentified (Fuse) | 16 | 13:30 It was reported b/o fuse for Tx at Well #6D-13. (6DN fdr #2) 16:20 Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well #6D-13. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3187856 | 1 | 13:30 | Afternoon | Tuesday | 2016 | 3
2803 | 2016-03-22 19:50 | 2016-03-22 19:50 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Dead End Insulator | 0 | C.Duri ACB fdr #9 T/R 1x Ctr: 343-344 R/F: 51@1 & 51N. The line is not Patrolled Yet. | 3187850 | 1 | 19:50 | Night | Tuesday | 2016 | 3
2804 | 2016-03-22 19:50 | 2016-03-25 08:35 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Dead End Insulator | 0 | Patrolled the line & found, @1 F/O Dead end Insulator o/p #04-07-10. Cause: Dead end Insulator. | 3187850 | 1 | 19:50 | Night | Tuesday | 2016 | 3
2805 | 2016-03-23 06:33 | 2016-03-23 06:33 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri Community ACB fdr #2 T/R 1x. Not checked yet. | 3187850 | 1 | 6:33 | Morning | Wednesday | 2016 | 3
2806 | 2016-03-23 06:33 | 2016-03-28 10:41 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 67-68 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3187850 | 1 | 6:33 | Morning | Wednesday | 2016 | 3
2807 | 2016-03-23 09:21 | 2016-03-23 09:21 | MINAS POWER PLANT |  |  | - | 09:21 S/U MGT #8, then online the Unit at 09:38. |  | 1 | 9:21 | Morning | Wednesday | 2016 | 3
2808 | 2016-03-23 09:28 | 2016-03-23 09:28 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 35 | 09:28 Manually opened Recl. 22V-06 (Neela fdr #1), to replaced broken FCO at TP of Well BKO #287. 09:58 Energized Recl. 22V-06. Cause: Planned Maintenance. | 123 | 1 | 9:28 | Morning | Wednesday | 2016 | 3
2809 | 2016-03-23 09:30 | 2016-03-23 09:30 | SINABUNG MINI SUBSTATION | Fair | Under investigation | 0 | 09:30 It was reported no power at Kutilang & Security Camp Office. 10:00 Checked & found, 13.8KV Recl. for 2500KVA Tx at Sinabung Mini SS T/O. Ctr: 224-225. (Then Opened 4.16KV Recl. at Sinabung Mini SS) Visual checked 2500Kva Tx & found normal. Closed 13.8Kv Recl. for energizing 2500Kva Tx at Sinabung SS. Closed 4.16Kv Recl. at Sinabung Mini SS, to energize Kutilang & Security Office. Cause: Under Investigation. | 3187850 | 1 | 9:30 | Morning | Wednesday | 2016 | 3
2810 | 2016-03-23 10:30 | 2016-03-23 10:30 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 19 | 10:30 Manual Opened Recl. 34BI-18 So.Bekasap fdr #1). (to install & close HLC Jumper for reactive Well Cucut #03) 10:47 Closed Recl. 34BI-18. Cause: Planned Maintenance. | 123 | 1 | 10:30 | Morning | Wednesday | 2016 | 3
2811 | 2016-03-23 11:45 | 2016-03-23 11:45 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 34 | 11:45 It was reported b/o fuse for Tx o/p #04-3-23A. (C.Duri fdr #8) 15:30 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-3-23A. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3187850 | 1 | 11:45 | Morning | Wednesday | 2016 | 3
2812 | 2016-03-23 15:00 | 2016-03-23 15:00 | CENTRAL DURI POWER PLANT |  |  | - | 15:00 S/U CGT #4, then on line the Unit at 15:36. |  | 1 | 15:00 | Afternoon | Wednesday | 2016 | 3
2813 | 2016-03-23 16:58 | 2016-03-23 16:58 | MINAS POWER PLANT |  |  | - | 16:58 S/U MGT #10, then on line the Unit at 17:12. (Running on Test with load 8 MW, after replacing Rotor Generator) |  | 1 | 16:58 | Afternoon | Wednesday | 2016 | 3
2814 | 2016-03-23 23:02 | 2016-03-23 23:02 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain | Unidentified | 109 | NKBS VCB fdr #3 T/R 1x. NKBS GFPC-TX #1 did not operate. NKBS fdr #4 load dropped 38A (80-42A). Not checked yet. | 3187856 | 1 | 23:02 | Night | Wednesday | 2016 | 3
2815 | 2016-03-23 23:02 | 2016-03-24 16:43 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain | Unidentified | 109 | Checked & found NKBS VCB fdr #3 T/R 1x Ctr: 270-271 R/F: 51N. Patrolled the line, but nothing found. Cause: Unidentified. | 3187856 | 1 | 23:02 | Night | Wednesday | 2016 | 3
2816 | 2016-03-24 07:53 | 2016-03-24 07:53 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | C.Duri ACB fdr #2 T/R 1x Ctr: 362-363 R/F: 51@2 & 51N. The line is not patrolled yet. | 3187850 | 1 | 7:53 | Morning | Thursday | 2016 | 3
2817 | 2016-03-24 07:53 | 2016-03-28 16:17 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3187850 | 1 | 7:53 | Morning | Thursday | 2016 | 3
2818 | 2016-03-24 09:00 | 2016-03-24 09:00 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 09:00 It was reported b/o fuse for Tx o/p #04-6-02. (C.Duri fdr #9) 10:10 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-6-02. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3187850 | 1 | 9:00 | Morning | Thursday | 2016 | 3
2819 | 2016-03-24 20:37 | 2016-03-24 20:37 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified (Fuse) | 3 | 20:37 It was reported b/o fuse for Tx at Well Genting #4. 22:00 Checked & found, @1,@2 b/o 1.4SF fuses for 75kva Tx at Well Genting #04. Performed TTR, Megger the Tx & found, normal. (good reading) Replaced b/o fuse above with same size, then energized Tx. Cause: Unidentified (Fuse). | 3187850 | 1 | 20:37 | Night | Thursday | 2016 | 3
2820 | 2016-03-25 07:48 | 2016-03-25 07:48 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 88 | 07:48 Pungut fdr #2 Load dropped 65A (92-27A). 11:53 It was reported No power at Okasam Fields. 15:10 Checked & found, Recl. 44BX-06 (Pungut fdr #2) T/SO. Ctr: 349-350. Patrolled the Line, but found Nothing. Blocked & Closed Recl. 44BX-06, Ok. Then released the block. Cause: Unidentified. | 3187850 | 1 | 7:48 | Morning | Friday | 2016 | 3
2821 | 2016-03-25 07:48 | 2016-03-27 14:27 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 88 | Re-patrolled the line & found: -@1 Broken Pin insulator o/p #43BY-16 -@1 Broken Dead end insulator o/p #43BY-1 Cause: Lightning. | 3187850 | 1 | 7:48 | Morning | Friday | 2016 | 3
2822 | 2016-03-25 15:54 | 2016-03-25 15:54 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 50 | Bangko fdr #4 Load dropped 88A (231-143A). Bangko GFPC T/R 2x. Bangko fdr #4 Ground fault Alarm. Not checked yet. | 3187850 | 1 | 15:54 | Afternoon | Friday | 2016 | 3
2823 | 2016-03-25 15:54 | 2016-03-28 11:08 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 50 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 83-84. Patrolled the line, but found nothing. Cause: Unidentified. | 3187850 | 1 | 15:54 | Afternoon | Friday | 2016 | 3
2824 | 2016-03-25 18:49 | 2016-03-25 18:49 | NORTH DURI POWER PLANT |  |  | - | 18:49 S/U NDC-CT #3, then Online the Unit at 19:16. (Running in simple cycle) |  | 1 | 18:49 | Afternoon | Friday | 2016 | 3
2825 | 2016-03-25 20:00 | 2016-03-25 20:00 | MINAS POWER PLANT |  |  | - | 20:00 Offline MGT #10, then S/D the Unit at 20:02. (To repair oil breather line) |  | 1 | 20:00 | Night | Friday | 2016 | 3
2826 | 2016-03-25 20:25 | 2016-03-25 20:25 | MINAS POWER PLANT |  |  | - | 20:25 Offline MGT #5, then S/D the Unit for S/B. |  | 1 | 20:25 | Night | Friday | 2016 | 3
2827 | 2016-03-26 06:36 | 2016-03-26 06:36 | DURI POWER PLANT |  |  | - | 06:36 Off line DGT#7, then S/D the Unit for S/B. | 123 | 1 | 6:36 | Morning | Saturday | 2016 | 3
2828 | 2016-03-26 06:55 | 2016-03-26 06:55 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 0 | 06:55 It was reported b/o fuse for Tx o/p #08-M3-15. (C.Duri fdr #2) 10:25 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #08-M3-15. Replaced b/o fuse above with the same size, then Energized the Tx. Cause: Animal. (Bird) | 3187850 | 1 | 6:55 | Morning | Saturday | 2016 | 3
2829 | 2016-03-26 07:02 | 2016-03-26 07:02 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Unidentified | 100 | Petapahan fdr #1 Load dropped 53A (91-38A). Petapahan fdr #2 Load dropped 58A (148-90A). Not checked yet. | 3187856 | 1 | 7:02 | Morning | Saturday | 2016 | 3
2830 | 2016-03-26 07:02 | 2016-03-28 14:29 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Unidentified | 100 | Checked & found, Recl. 30CZ-01 (Petapahan fdr #1) T/R 1x Ctr: 99-100. Patrolled the line, but found nothing. Cause: Unidentified. | 3187856 | 1 | 7:02 | Morning | Saturday | 2016 | 3
2831 | 2016-03-27 01:29 | 2016-03-27 01:29 | 13.8KV PEMATANG FEEDER #1 | Fair | Lightning Arrester | 21 | Pematang OCB fdr #1 T/R 1x. Pematang fdr #2 load dropped 18A (55-37A). Not checked yet. | 3187850 | 1 | 1:29 | Night | Sunday | 2016 | 3
2832 | 2016-03-27 01:29 | 2016-03-28 15:35 | 13.8KV PEMATANG FEEDER #1 | Fair | Lightning Arrester | 21 | Checked & found, Pematang OCB fdr #1 T/R 1x Ctr: 125-126 R/F: 51N. Patrolled the line & found, @2 broken L/A on TP of Well Pematnag #67. Cause: Lightning Arrester. | 3187850 | 1 | 1:29 | Night | Sunday | 2016 | 3
2833 | 2016-03-27 06:00 | 2016-03-27 06:00 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 118 | 06:00 Minas ACB fdr #1 T/LO. Ctr: 50-52 R/F: 51@1,@2. It was reported an explosion at Well #6D-99. 07:05 Patrolled the line, but found nothing. 07:07 Blocked & closed Minas ACB fdr #1, Ok. Then released the block. Cause: Unidentified. | 3187856 | 1 | 6:00 | Morning | Sunday | 2016 | 3
2834 | 2016-03-27 09:46 | 2016-03-27 09:46 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Secondary Cable | 0 | 09:45 It was reported b/o fuse for Tx o/p #05-P3-16. 11:45 Checked & found, loss connection at Secondary X0 Terminal of 112.5Kva Tx. Then manual opened all fuses holder. 12:00 Repaired the loss connection, then energized the Tx. Cause: Secondary Cable. (X0 loss connection) | 3187850 | 1 | 9:46 | Morning | Sunday | 2016 | 3
2835 | 2016-03-27 15:00 | 2016-03-27 15:00 | 13.8KV 3D FEEDER #3 | Rain | Lightning | 16 | 3D OCB fdr #3 T/R 1x. 3D GFPC-TX #1 did not operate. 3D fdr #4 load dropped 87A (239-152A). 3D fdr #5 load dropped 49A (196-147A). Not checked yet. | 3187856 | 1 | 15:00 | Afternoon | Sunday | 2016 | 3
2836 | 2016-03-27 15:00 | 2016-03-29 11:30 | 13.8KV 3D FEEDER #3 | Rain | Lightning | 16 | Checked & found, 3D OCB fdr #3 T/R 1x Ctr: 434-435 R/F: 51N. Patrolled the line & found, @1 broken Pin Insulator o/p #3C-29. Cause: Lightning. | 3187856 | 1 | 15:00 | Afternoon | Sunday | 2016 | 3
2837 | 2016-03-28 11:10 | 2016-03-28 11:10 | MINAS POWER PLANT | Fair |  | - | 11:10 Offline MGT #9, then S/D the Unit for S/B. (Due to replacing F/N Set) |  | 1 | 11:10 | Morning | Monday | 2016 | 3
2838 | 2016-03-29 06:53 | 2016-03-29 06:53 | 13.8KV S. BALAM GFPC | Fair | Pin Insulator | 0 | So.Balam GFPC T/R 1x. Ground fault alarm on So.Balam fdr #1. No load drop at any feeder. Not checked yet. | 3187850 | 1 | 6:53 | Morning | Tuesday | 2016 | 3
2839 | 2016-03-29 06:53 | 2016-03-31 11:12 | 13.8KV S. BALAM GFPC | Fair | Pin Insulator | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 205-206 R/F: 50N. Patrolled So.Balam fdr #1 & found, @3 broken Pin Insulator o/p #15Y-09. Cause: Pin Insulator. | 3187850 | 1 | 6:53 | Morning | Tuesday | 2016 | 3
2840 | 2016-03-29 09:00 | 2016-03-29 09:00 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 0 | 09:00 It was reported b/o fuse for Tx o/p #05-P3-16. 14:29 Checked & found, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #05-P3-16. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3187850 | 1 | 9:00 | Morning | Tuesday | 2016 | 3
2841 | 2016-03-29 11:04 | 2016-03-29 11:04 | 13.8KV 4B FEEDER #1 | Fair | Unidentified (Fuse) | 3 | 11:04 It was reported b/o fuse for Tx at Well #4B-36. (4B fdr #1) Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well #4B-36. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3187856 | 1 | 11:04 | Morning | Tuesday | 2016 | 3
2842 | 2016-03-31 07:51 | 2016-03-31 07:51 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Animal | 0 | 07:51 It was reported b/o fuse for Tx o/p #SL-120. (Near Seulawah Camp #37) 09:29 Checked & found, @1 b/o 1.0SF fuse for 50Kva Tx o/p #SL-120. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Squirrel) | 3187850 | 1 | 7:51 | Morning | Thursday | 2016 | 3
2843 | 2016-03-31 12:14 | 2016-03-31 12:14 | 13.8KV SINTONG GFPC | Fair | Equipment Failure | 0 | 12:14 Sintong GFPC T/SO. Ctr: 828-832. Ground fault alarm on Sintong fdr #2. No load dropped at any fdrs. 12:21 Manual closed Sintong GFPC, Ok. Not checked yet. | 3187850 | 1 | 12:14 | Afternoon | Thursday | 2016 | 3
2844 | 2016-03-31 12:14 | 2016-01-04 12:14 | 13.8KV SINTONG GFPC | Fair | Equipment Failure | 0 | Checked & found, Sintong GFPC T/R 4x Ctr: 828-832 R/F: 50N. Found, GFPC Recloser control failed operation. Patrolled Sintong fdr #1 line, but found nothing. Cause: Equipmen failure. | 3187850 | 1 | 12:14 | Afternoon | Thursday | 2016 | 3
2845 | 2016-03-31 14:15 | 2016-03-31 14:15 | 13.8KV PEMATANG FEEDER #2 | Fair | Transformer Failure | 57 | 14:15 It was reported b/o fuse for Tx at Well Pematang #81. 17:20 Checked & found, @2, @3 b/o 3.5SF fuses for 150Kva Tx at Well Pematang #81. Performed TTR & Megger Test, found @3 TTR test failed. Cause: Transformer Failure. (The Tx is not replaced yet) | 3187850 | 1 | 14:15 | Afternoon | Thursday | 2016 | 3
2846 | 2016-03-31 14:15 | 2016-06-04 11:15 | 13.8KV PEMATANG FEEDER #2 | Fair | Transformer Failure | 57 | Replaced 150Kva Tx failure with the same size & energized the Tx at Well Pematang #81. Cause: Tx Failure. | 3187850 | 1 | 14:15 | Afternoon | Thursday | 2016 | 3
2847 | 2016-03-31 18:48 | 2016-03-31 18:48 | 13.8KV BATANG FEEDER #2 | Fair | Pin Insulator | 0 | Batang OCB fdr #2 T/R 1x. Batang fdr #3 load dropped 13A (47-34A). Batang GFPC was in block position. Not checked yet. | 3187850 | 1 | 18:48 | Afternoon | Thursday | 2016 | 3
2848 | 2016-03-31 18:48 | 2016-01-04 10:48 | 13.8KV BATANG FEEDER #2 | Fair | Pin Insulator | 0 | Checked & found, Batang OCB fdr #2 T/R 1x Ctr: 121-122 R/F: 51N. Patrolled the line & found, @1 F/O Pin Insulator o/p #NN. (Near 115KV Pole #STG-03) Cause: Pin Insulator. | 3187850 | 1 | 18:48 | Afternoon | Thursday | 2016 | 3
2849 | 2016-03-31 08:02 | 2016-03-31 08:02 | MINAS POWER PLANT |  |  | - | 08:02 S/U MGT #10, then online the Unit at 08:30. |  | 1 | 8:02 | Morning | Thursday | 2016 | 3
2850 | 2016-03-31 08:40 | 2016-03-31 08:40 | MINAS POWER PLANT |  |  | - | 08:40 Offline MGT #6, then S/D the Unit for S/B. |  | 1 | 8:40 | Morning | Thursday | 2016 | 3
2851 | 2016-03-31 20:12 | 2016-03-31 20:12 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 20:12 It was reported b/o fuse for Tx at Petani Gas Compressor. (Petani fdr #1) 23:24 Checked & found, @2 b/o 14.0SF fuse for 750Kva Tx at Petani Gas Compressor. Test TTR & Megger of 750Kva Tx, found good condition. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3187850 | 1 | 20:12 | Night | Thursday | 2016 | 3
2852 | 2016-01-04 14:13 | 2016-01-04 14:13 | MINAS POWER PLANT |  |  | - | 14:13 S/U MGT#5 and then online the unit at 14:29. |  | 1 | 14:13 | Afternoon | Monday | 2016 | 1
2853 | 2016-01-04 17:56 | 2016-01-04 17:56 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | C.Duri ACB fdr #15 T/R 1x Ctr: 361-362 R/F: 51@1. Not patrolled yet. | 3198862 | 1 | 17:56 | Afternoon | Monday | 2016 | 1
2854 | 2016-01-04 17:56 | 2016-04-04 16:10 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 17:56 | Afternoon | Monday | 2016 | 1
2855 | 2016-02-04 06:02 | 2016-02-04 06:02 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 33 | Sintong OCB fdr #1 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. | 3198862 | 1 | 6:02 | Morning | Thursday | 2016 | 2
2856 | 2016-02-04 06:02 | 2016-03-04 07:52 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 33 | Checked & found, Sintong OCB fdr #1 T/R 1x Ctr: 381-382 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 6:02 | Morning | Thursday | 2016 | 2
2857 | 2016-02-04 08:38 | 2016-02-04 08:38 | 13.8KV MINAS FEEDER #6 | Fair | Dead End Insulator | 54 | Minas ACB fdr #6 T/R 1x Ctr: 158-159 R/F: 51N. Not patrolled yet. | 3198864 | 1 | 8:38 | Morning | Thursday | 2016 | 2
2858 | 2016-02-04 08:38 | 2016-04-04 11:00 | 13.8KV MINAS FEEDER #6 | Fair | Dead End Insulator | 54 | Patrolled the line & found, @3 broken Dead end Insulator o/p #7E-54. Cause: Dead end Insulator. | 3198864 | 1 | 8:38 | Morning | Thursday | 2016 | 2
2859 | 2016-02-04 11:04 | 2016-02-04 11:04 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified (Fuse) | 12 | 11:04 It was reported b/o fuse for Tx at Well Kelok #15. 11:20 Checked & found, @1 b/o 7.8SF fuse for 300kva Tx at Well #Kelok #15. Test TTR and megger found, normal. (good reading) Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 11:04 | Morning | Thursday | 2016 | 2
2860 | 2016-02-04 14:48 | 2016-02-04 14:48 | MINAS POWER PLANT |  |  | - | 14:48 S/U MGT #9, then Online the Unit at 15:08. |  | 1 | 14:48 | Afternoon | Thursday | 2016 | 2
2861 | 2016-02-04 17:15 | 2016-02-04 17:15 | NORTH DURI POWER PLANT |  |  | - | 17:15 Off line, NDC-CT #3, then S/D the Unit for S/B. (Prior to remove Blanking plate) |  | 1 | 17:15 | Afternoon | Thursday | 2016 | 2
2862 | 2016-02-04 17:45 | 2016-02-04 17:45 | MINAS POWER PLANT |  |  | - | 17:45 S/U MGT #6, then ON line the Unit at 18:15. |  | 1 | 17:45 | Afternoon | Thursday | 2016 | 2
2863 | 2016-03-04 08:54 | 2016-03-04 08:54 | 13.8KV 6D FEEDER #2 | Fair | Unidentified | 36 | 6D fdr #2 load dropped 142A (216-74A). Not checked yet. | 3198864 | 1 | 8:54 | Morning | Friday | 2016 | 3
2864 | 2016-03-04 08:54 | 2016-04-04 10:52 | 13.8KV 6D FEEDER #2 | Fair | Unidentified | 36 | Checked & found, Recl. 6D-298 (6D fdr #2) T/R 1x Ctr: 37-38 R/F: 51@3. Patrolled the line, but found nothing. Cause: Unidentified. | 3198864 | 1 | 8:54 | Morning | Friday | 2016 | 3
2865 | 2016-03-04 08:57 | 2016-03-04 08:57 | 13.8KV PETANI FEEDER #2 | Fair | Animal | 18 | 08:57 It was reported b/o fuse for Tx at Well Petani #124. 12:27 Checked & found, @1 b/o 14.0SF fuse for 500kva Tx at Well Petani #124. Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuse with same size, then energized the Tx. Cause: Animal. (Civet) | 3198862 | 1 | 8:57 | Morning | Friday | 2016 | 3
2866 | 2016-03-04 09:48 | 2016-03-04 09:48 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 3 | 09:48 It was reported b/o fuse for Tx o/p #11-H1-18. 11:50 Checked & found, @2 b/o 3.1SF fuse for 112.5kva Tx o/p #11-H1-18. Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal. (Bird) | 3198862 | 1 | 9:48 | Morning | Friday | 2016 | 3
2867 | 2016-03-04 16:45 | 2016-03-04 16:45 | NORTH DURI POWER PLANT |  |  | - | 16:45 S/U NDC#3 and then online the unit at 18:10. |  | 1 | 16:45 | Afternoon | Friday | 2016 | 3
2868 | 2016-03-04 20:14 | 2016-03-04 20:14 | 13.8KV 8C FEEDER #3 | Fair | Unidentified | 12 | 8C VCB fdr #3 T/R 2x. Not checked yet. | 3198864 | 1 | 20:14 | Night | Friday | 2016 | 3
2869 | 2016-03-04 20:14 | 2016-04-04 11:45 | 13.8KV 8C FEEDER #3 | Fair | Unidentified | 12 | Checked & found, 8C VCB fdr #3 T/R 2x Ctr: 482-484 R/F: 51N(@3). Patrolled the line, but found nothing. Cause: Unidentified. | 3198864 | 1 | 20:14 | Night | Friday | 2016 | 3
2870 | 2016-03-04 20:14 | 2016-03-04 20:14 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 64 | 8C VCB fdr #1 T/R 1x. Not checked yet. | 3198864 | 1 | 20:14 | Night | Friday | 2016 | 3
2871 | 2016-03-04 20:14 | 2016-04-04 11:50 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 64 | Checked & found, 8C VCB fdr #1 T/R 1x Ctr: 635-636 R/F: 50@1. Patrolled the line, but found nothing. Cause: Unidentified. | 3198864 | 1 | 20:14 | Night | Friday | 2016 | 3
2872 | 2016-04-04 14:09 | 2016-04-04 14:09 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 30 | Rangau fdr #2 load dropped 60A (75-15A). Not checked yet. | 3198862 | 1 | 14:09 | Afternoon | Monday | 2016 | 4
2873 | 2016-04-04 14:09 | 2016-06-04 08:15 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 30 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: 129-130 R/F: 51N. Patrolled the line & found, @3 broken L/A o/p #26BF-18. Cause: Lightning. | 3198862 | 1 | 14:09 | Afternoon | Monday | 2016 | 4
2874 | 2016-04-04 14:30 | 2016-04-04 14:30 | MINAS POWER PLANT |  |  | - | 14:30 S/U MGT #3, then Online the Unit at 15:17. |  | 1 | 14:30 | Afternoon | Monday | 2016 | 4
2875 | 2016-04-04 15:38 | 2016-04-04 15:38 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 46 | 15:38 Libo OCB fdr #2 T/LO. 16:45 Checked & found, Libo OCB fdr #2 T/LO. Ctr: 410-415 R/F: 50/51N. 16:50 Patrolled the line, but found nothing. Blocked & Closed Libo OCB fdr #2, but T/O again. 17:50 Re-Patrolled the line & found, @2 broken Pin Support Insulator o/p #KW-161. Then replaced the broken Pin Support Insulator above. 18:14 Blocked & Closed Libo OCB fdr #2, Ok. Then normalized the block. Cause: Lightning. | 3198862 | 1 | 15:38 | Afternoon | Monday | 2016 | 4
2876 | 2016-04-04 16:04 | 2016-04-04 16:04 | 13.8KV MINAS FEEDER #1 | Fair | Transformer Failure | 45 | 16:04 It was reported b/o fuse for Tx at Well #7D-63A. 16:57 Checked & found, @1, @2 b/o 7.8SF fuses for 250kva Tx at Well #7D-63A. Performed TTR, Megger Test the Tx & found, Low Mega-ohm Reading Tx. Cause: Transformer failure. (Low Mega-ohm Tx) (The Tx is not replaced yet) | 3198864 | 1 | 16:04 | Afternoon | Monday | 2016 | 4
2877 | 2016-04-04 16:04 | 2016-05-04 11:22 | 13.8KV MINAS FEEDER #1 | Fair | Transformer Failure | 45 | Replaced 250Kva Tx low megger with the same size & energized the Tx at Well #7D-63A. Cause: Tx failure. (Tx Low Megger) | 3198864 | 1 | 16:04 | Afternoon | Monday | 2016 | 4
2878 | 2016-04-04 16:48 | 2016-04-04 16:48 | MINAS POWER PLANT |  |  | - | 16:48 Offline MGT #2, then S/D the Unit for S/B. |  | 1 | 16:48 | Afternoon | Monday | 2016 | 4
2879 | 2016-04-04 17:06 | 2016-04-04 17:06 | NORTH DURI POWER PLANT |  |  | - | 17:06 Offline NDC-CT #1, then S/D the Unit at 17:09. (For S/B-Prior to HGPI, HRSG-1 Pigging & Repair) 20-Apr-2016 08:21 S/U NDC-CT #1, then Online the Unit at 08:53. (After HGPI Inspection program) 20:47 Off Line NDC-CT #1, then S/D at 20:50. (For S/B - Prior to repairing Gas leak at Stage-C of Fuel Nozzle #10) |  | 1 | 17:06 | Afternoon | Monday | 2016 | 4
2880 | 2016-04-04 21:36 | 2016-04-04 21:36 | 13.8KV 4B FEEDER #1 | Fair | Equipment Failure | 627 | 21:04 4B OCB fdr #1 T/R 1x. 4B fdr #2 load dropped 66A (110-44A). 21:36 4B OCB fdr #1 T/LO. 23:26 Checked & found, 4B OCB fdr #1 T/LO. Ctr: 264-273 R/F: 50/51@2, 51 @3 & 50N. | 3198864 | 1 | 21:36 | Night | Monday | 2016 | 4
2881 | 2016-04-04 21:36 | 2016-05-04 00:26 | 13.8KV 4B FEEDER #1 | Fair | Equipment Failure | 627 | 00:26 Checked & found, @2, @3 broken Bypass Switch of Recl. 4B-101. (The Recloser unit was failure before, then bypassed it) 00:42 Opened LBS #4B-90, to isolated broken Bypass Switch above. 00:43 Blocked & closed 4B OCB fdr #1, Ok. Then released the block. (Will be repaired in the morning, approx. 50 wells were still off). 10:00 Opened LBS #4A-70. To replacing broken By-pass Switch of Recl. 4B-101. 11:53 Closed LBS #4A-70. 11:57 Closed LBS #4B-90. Cause: Equipment failure. (Broken Bypass Switch of Recloser) | 3198864 | 1 | 21:36 | Night | Monday | 2016 | 4
2882 | 2016-05-04 12:39 | 2016-05-04 12:39 | 13.8KV 4D FEEDER #5 | Fair | Unidentified | 14 | 12:39 4D fdr #5 Load dropped 23A (121-98A). 14:25 It was reported no power at Well #3E-82, 3E-83, 3E-91, 3E-91N & #3E-93. 15:00 Checked & found, Recl. 4D-14A (4D fdr #5) T/SO. Ctr: 45-46. Patrolled the line, but found nothing. 15:26 Blocked & closed Recl. 4D-14A, Ok. Then release the block. Cause: Unidentified. | 3198864 | 1 | 12:39 | Afternoon | Wednesday | 2016 | 5
2883 | 2016-05-04 16:10 | 2016-05-04 16:10 | 13.8KV 4B FEEDER #1 | Fair | Transformer Failure | 28 | 16:10 It was reported b/o fuse for Tx at Well #3A-75. (4B fdr #1) 18:15 Checked & found, @1, @2 b/o 7.8SF fuses for 300Kva Tx at Well #3A-75. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx failure. (Tx Low Megger reading) (The Tx isn not replaced yet) | 3198864 | 1 | 16:10 | Afternoon | Wednesday | 2016 | 5
2884 | 2016-05-04 16:10 | 2016-07-04 11:23 | 13.8KV 4B FEEDER #1 | Fair | Transformer Failure | 28 | Replaced 150Kva Tx failure with the same size & energized the Tx at Well #3A-75. Cause: Tx failure. (Tx Low Megger reading) | 3198864 | 1 | 16:10 | Afternoon | Wednesday | 2016 | 5
2885 | 2016-06-04 01:22 | 2016-06-04 01:22 | 13.8KV 6DN FEEDER #1 | Fair | Unidentified (Fuse) | 22 | 01:22 It was reported b/o fuse for Tx at Well #5E-51. (6DN fdr #1) 11:00 Checked & found, @1, @2 b/o 14.0SF fuses for 550Kva Tx at Well #5E-51. Performed TTR & Megger test the Tx, found good reading. Replaced b/o fuse above with the same size then Energized the Tx. Cause : Unidentified (Fuse). | 3198864 | 1 | 1:22 | Night | Saturday | 2016 | 6
2886 | 2016-06-04 09:22 | 2016-06-04 09:22 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 373 | 09:22 Performed Switching Procedure to S/D Sintong fdr #2. To repair Bypass Switch of Recl. 28AF-17. 11:38 Re-Energized Recl. 28AF-17. (after finishing the jobs) Then Manually Closed Sintong OCB fdr #2. Cause: Planned Maintenance. | 123 | 1 | 9:22 | Morning | Saturday | 2016 | 6
2887 | 2016-06-04 15:22 | 2016-06-04 15:22 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 248 | 15:22 3D OCB fdr #8 T/R 4x. 3D GFPC T/R 1x. (Ground fault alarm at 3D fdr #8) 15:33 3D OCB fdr #8 T/LO. 16:50 Checked & found, 3D OCB fdr #8 T/LO. Ctr: 173-182 R/F: 51@1 & 51N. Patrolled the line, but found nothing. 18:45 Blocked & closed 3D OCB fdr #8, Ok. Then release the block. Not Re-patrolled yet. | 3198864 | 1 | 15:22 | Afternoon | Saturday | 2016 | 6
2888 | 2016-06-04 15:22 | 2016-07-04 12:54 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 248 | Re-patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 15:22 | Afternoon | Saturday | 2016 | 6
2889 | 2016-06-04 15:32 | 2016-06-04 15:32 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 83 | 6D OCB fdr #2 T/R 2x. 6D fdr #1 Load dropped 151A (200-49A). 6D fdr #3 Load dropped 72A (85-13A). Not checked yet. | 3198864 | 1 | 15:32 | Afternoon | Saturday | 2016 | 6
2890 | 2016-06-04 15:32 | 2016-07-04 12:15 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 83 | Checked & found, 6D OCB fdr #2 T/R 2x Ctr: 233-235 R/F: 51@1,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 15:32 | Afternoon | Saturday | 2016 | 6
2891 | 2016-06-04 15:42 | 2016-06-04 15:42 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 37 | 4B OCB fdr #1 T/R 2x. 4B fdr #2 Load dropped 19A (105-86A). Not checked yet. | 3198864 | 1 | 15:42 | Afternoon | Saturday | 2016 | 6
2892 | 2016-06-04 15:42 | 2016-07-04 12:45 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 37 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 275-276 R/F: 51@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 15:42 | Afternoon | Saturday | 2016 | 6
2893 | 2016-06-04 21:30 | 2016-06-04 21:30 | 13.8KV SINTONG FEEDER #2 | Fair | ESP Failure | 0 | 21:30 It was reported b/o fuse for Tx at Well Mutiara #03. 22:30 Checked & found, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx at Well Mutiara #03. Performed TTR & Megger test The Tx, found good reading. Replaced b/o fuse above with the same size then energized the Tx. Cause: ESP Failure. | 3198862 | 1 | 21:30 | Night | Saturday | 2016 | 6
2894 | 2016-06-04 22:25 | 2016-06-04 22:25 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Powerline - Hot Line Clamp | 0 | 22:25 It was reported a spark at HLC o/p #04-06-20A. 23:20 Checked & found, @3 spark at HLC for 112.5Kva Tx o/p #04-06-20A. S/D the Tx by opening all Fuses. (After Operator turn off Main Breaker) Cause: Others. (Loss connection at HLC) (Not repaired yet) | 3198862 | 1 | 22:25 | Night | Saturday | 2016 | 6
2895 | 2016-06-04 22:25 | 2016-04-05 10:20 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Powerline - Hot Line Clamp | 0 | 10:20-11:20 Repaired @3 Broken Hot Line Clamp o/p 04-6-20A. Energized 112.5 Kva Tx, ok. Cause: Hot line clamp. | 3198862 | 1 | 22:25 | Night | Saturday | 2016 | 6
2896 | 2016-06-04 23:45 | 2016-06-04 23:45 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 82 | 23:45 It was reported no power at Wells #6D-56, 6D-56N, 6D-34E, 6D-35, 6D-45 & #6D-54N. 01:01 Checked & found, Recl. 6D-50 (6DN fdr #2) T/SO. Ctr: Error. Blocked & closed Recl. 6D-50, Ok. Then released the block. Not Patrolled yet. | 3198864 | 1 | 23:45 | Night | Saturday | 2016 | 6
2897 | 2016-06-04 23:45 | 2016-07-04 12:13 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 82 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 23:45 | Night | Saturday | 2016 | 6
2898 | 2016-07-04 08:00 | 2016-07-04 08:00 | 13.8KV 5B FEEDER #2 | Fair | Powerline - Hot Line Clamp | 17 | 08:00 It was reported Unbalance voltage of Tx at Well #4D-46. (5B fdr #2) 15:30 Checked & found, @1 Loose connection HLC for 300Kva Tx on TP of Well above. Cause: Hot Line Clamp. (Loose connection) (The HLC is not Repaired yet) 14-Apr-2016. 10:22 Manually opened Recl. 4C-65A (5B fdr #2) To repairing @1 broken jumper Hot Line Clamp on TOP of Well #4D-46. (14 wells were off) 10:55 Manually closed Recl. 4C-65A. Cause: Broken Hot Line Clamp. | 3198864 | 1 | 8:00 | Morning | Monday | 2016 | 7
2899 | 2016-07-04 10:43 | 2016-07-04 10:43 | PUNGUT SUBSTATION | Fair | Under investigation | 327 | 10:43 It was reported No power at Pungut Field. 12:10 Checked & found, 115KV Pungut C/S. T/O. R/F: 87T-@1 & 86T Last Ctr: 162. (When re-installing @1 Diff. Relay unit on the Relay case after calibration) Manually opened 13.8KV Pungut OCB fdr #1 . Manually opened 13.8KV Pungut OCB fdr #2. Functioning test of the 115KV Pungut C/S above & found normal. 13:08 Manually Closed 115KV Pungut C/S, Ok. (Pungut Power TX energized) 13:16 Blocked & closed 13.8KV Pungut OCB fdr #1, Ok. Then released the block. 13:18 Blocked & closed 13.8KV Pungut OCB fdr #2, Ok. Then released the block. Cause: Under Investigsaion. | 3198862 | 1 | 10:43 | Morning | Monday | 2016 | 7
2900 | 2016-07-04 17:38 | 2016-07-04 17:38 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 0 | 17:38 It was reported b/o fuse for Tx o/p #06-Q5-28. 20:30 Checked & found, @1 b/o 14.0SF fuse for 500kva Tx o/p #06-Q5-28. Test TTR and Megger the Tx, found normal. (good reading) Replaced b/o fuse with same size then energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 17:38 | Afternoon | Monday | 2016 | 7
2901 | 2016-08-04 23:59 | 2016-08-04 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI power system normal condition. |  | 1 | 23:59 | Night | Thursday | 2016 | 8
2902 | 2016-09-04 05:21 | 2016-09-04 05:21 | 13.8KV 6DN FEEDER #6 | Drizzle | Lightning | 49 | 6DN fdr #6 Load dropped 182A (199-17A). 6DN fdr #5 Load dropped 43A (130-87A). 6DN fdr #4 Load dropped 137A (211-73A) T/O WIP at GS-3 Not checked yet. 05:21 6DN fdr #6 Load dropped 182A again (199-17A). 07:30 Checked & found, Recl. 6E-64 (6DN fdr #6) T/SO. Ctr: 34-35. Blocked & closed, Recl. 6E-64, Ok. Then released the Block. Continued Patrolling the Line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 5:21 | Morning | Sunday | 2016 | 9
2903 | 2016-09-04 05:32 | 2016-09-04 05:32 | 13.8KV 6D FEEDER #6 | Drizzle | Lightning | 15 | 6D OCB fdr #6 T/R 1x. 6D fdr #5 Load dropped 177A (234-57A). 6D fdr #4 Load dropped 191A (191-0A) T/O WIP at GS-4. Not checked yet. | 3198864 | 1 | 5:32 | Morning | Sunday | 2016 | 9
2904 | 2016-09-04 05:32 | 2016-12-04 13:05 | 13.8KV 6D FEEDER #6 | Drizzle | Lightning | 15 | Checked & found, 6D OCB fdr #6 T/R 1x Ctr: 570-571 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 5:32 | Morning | Sunday | 2016 | 9
2905 | 2016-09-04 05:34 | 2016-09-04 05:34 | 13.8KV 3D FEEDER #8 | Drizzle | Lightning | 16 | 05:34 3D OCB fdr #8 T/R 1x. 3D fdr #7 load dropped 172A (221-49A) T/O WIP at GS-5. 05:39 3D OCB fdr #8 T/R 1x again. 14:56 Checked & found, 3D OCB fdr #8 T/R 2x Ctr: 182-184 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 5:34 | Morning | Sunday | 2016 | 9
2906 | 2016-09-04 05:36 | 2016-09-04 05:36 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 26 | 05:36 4D fdr #5 load dropped 111 A (127-16A) 4D fdr #4 Load dropped 85A (247-162A). Not checked yet. 16:00 Checked & found Recl. 4D.16A T/SO. Ctr: 46-47 R/F: 50N. Blocked & Closed the Recloser, Ok. Then released the block. Patrolled the Line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 5:36 | Morning | Sunday | 2016 | 9
2907 | 2016-09-04 05:37 | 2016-09-04 05:37 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 60 | 05:37 5B fdr #4 Load dropped 184A (239-55A). 10:45 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO. Ctr: 55-56. Patrolled the Line & found, @1 broken Jumper of 300KVAR Cap. Bank o/p #4C-85. 11:00 Blocked & closed, Recl. 4B-73, Ok. Then released the Block. Cause: Lightning. | 3198864 | 1 | 5:37 | Morning | Sunday | 2016 | 9
2908 | 2016-09-04 05:55 | 2016-09-04 05:55 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 25 | 05:55 5B OCB fdr #4 T/R 1x. 10:45 Checked & found, 5B OCB fdr #4 T/R 1x Ctr: 323-324 R/F: 51@2,@3. Patrolled the line, but found nothing. Cause: Suepected by Lightning. | 3198864 | 1 | 5:55 | Morning | Sunday | 2016 | 9
2909 | 2016-09-04 06:07 | 2016-09-04 06:07 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 0 | 06:07 It was reported b/o fuse for Tx at Well Pagar #30. (Ketigul fdr #2) 11:33 Checked & found, @2, @3 b/o 7.8SF fuses for 300Kva Tx at Well Pagar #30. Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal. (Monkey) | 3198862 | 1 | 6:07 | Morning | Sunday | 2016 | 9
2910 | 2016-09-04 06:17 | 2016-09-04 06:17 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 245 | 06:17 3D fdr #4 Load dropped 90A (239-149A). 18:30 It was reported no power at some wells d/s of Recl. 2D-38. (3D fdr #4) (3D fdr #4 Load still dropped 53A) 21:49 Checked & found, Recl. 2D-38 (3D fdr #4) T/LO. Ctr: 242-246. Patrolled the line & found, @1 broken Pin Insulator o/p #2D-71. (Then replaced broken Pin Insulator above) 22:36 Blocked & Closed Recl. 2D-38, Ok. Then released the block. Cause: Lightning. | 3198864 | 1 | 6:17 | Morning | Sunday | 2016 | 9
2911 | 2016-09-04 07:02 | 2016-09-04 07:02 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Others | 0 | 07:02 It was reported unbalance voltage for Tx o/p #03-01-37. 10:30 Checked & found, Loss connection X0 of 112.5Kva Tx o/p #03-01-37. Opened FCO, then repairing the loose connection X0 of 112.5Kva Tx above. Re-energized 112.5Kva Tx o/p 03-01-37 & S/U all the wells. Cause: Others. (loose connection X0 of Tx) | 3198862 | 1 | 7:02 | Morning | Sunday | 2016 | 9
2912 | 2016-09-04 07:05 | 2016-09-04 07:05 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Lightning Arrester | 0 | 07:05 C.Duri ACB fdr #9 T/R 2x Ctr: 344-346 R/F: 51N. 07:32 C.Duri ACB fdr #9 T/R 1x Ctr: 346-347 R/F: 51N. 07:48 C.Duri ACB fdr #9 T/R 1x Ctr: 347-348 R/F: 51N. 07:52 C.Duri ACB fdr #9 T/R 1x Ctr: 348-349 R/F: 51N. 07:56 C.Duri ACB fdr #9 T/R 3x Ctr: 349-352 R/F: 51N. 11:30 Patrolled the line & found, @2 broken Jumper of L/A o/p #04-07-26A. 13:43 Manually opened C.Duri ACB fdr #9. To dismantling @2 broken jumper of L/A o/p #04-07-26A. 13:47 Manually closed C.Duri ACB fdr #9. Last Ctr: 352-353. Cause: Broken Lightning Arrester. | 3198862 | 1 | 7:05 | Morning | Sunday | 2016 | 9
2913 | 2016-09-04 09:20 | 2016-09-04 09:20 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 896 | 09:20 Manually opened So.Balam VCB fdr #4, to stringing new line toward new Well So.Balam #420. 11:49 Manually closed So.Balam VCB fdr #4 . Cause: Planned Maintenance. | 123 | 1 | 9:20 | Morning | Sunday | 2016 | 9
2914 | 2016-09-04 10:10 | 2016-09-04 10:10 | 13.8KV 6DN FEEDER #6 | Fair | Transformer Failure | 14 | 10:10 It was reported b/o fuse for Tx at Well #6E-43. 15:30 Checked & found, @1, @3 b/o 7.8SF fuses for 300Kva Tx at Well #6E-43. Perforfmed Megger, TTR test the Tx & found, Low meg ohm reading Tx. Cause: Tx Failure. (Low Mega ohm reading) (The Tx is not replaced yet) | 3198864 | 1 | 10:10 | Morning | Sunday | 2016 | 9
2915 | 2016-09-04 10:10 | 2016-11-04 17:50 | 13.8KV 6DN FEEDER #6 | Fair | Transformer Failure | 14 | Replaced 150Kva Tx with the same size at Well #6E-43, then energized the Tx. Cause: Tx Failure. (Low Mega-Ohm reading) | 3198864 | 1 | 10:10 | Morning | Sunday | 2016 | 9
2916 | 2016-09-04 16:46 | 2016-09-04 16:46 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 45 | 16:46 Sintong fdr #2 load dropped 53A (208-155A). 17:06 Sintong fdr #2 load dropped 93A again (208-115A). Not checked yet. | 3198862 | 1 | 16:46 | Afternoon | Sunday | 2016 | 9
2917 | 2016-09-04 16:46 | 2016-10-04 15:45 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 45 | Checked & found, Recl. 29Z-13A (Sintong fdr #2) T/R 2x Ctr: 86-88 R/F: 51N. Patrolled the line & found, @3 broken L/A on TP of Well Perkebunan #01. Cause: Lightning. | 3198862 | 1 | 16:46 | Afternoon | Sunday | 2016 | 9
2918 | 2016-09-04 23:35 | 2016-09-04 23:35 | 13.8KV 4B FEEDER #1 | Fair | Transformer Failure | 312 | It was reported b/o fuse for Tx at Well #4B-28. Not checked yet. | 3198864 | 1 | 23:35 | Night | Sunday | 2016 | 9
2919 | 2016-09-04 23:35 | 2016-10-04 10:10 | 13.8KV 4B FEEDER #1 | Fair | Transformer Failure | 312 | 10:10 Checked & found, @1, @2 b/o 7.8SF fuses for 300Kva Tx at Well #4B-28. (4B fdr #1) Performed megger, TTR test the Tx & found, Low Mega Ohm Reading Tx. Cause: Tx Failure. (Low Megger reading Tx) (The Tx failure is not replaced yet) | 3198864 | 1 | 23:35 | Night | Sunday | 2016 | 9
2920 | 2016-09-04 23:35 | 2016-11-04 16:18 | 13.8KV 4B FEEDER #1 | Fair | Transformer Failure | 312 | Replaced 300Kva Tx failure with the same size at Well #4B-28, then energized the Tx. Cause: Tx Failure. (Low Mega-ohm Reading) | 3198864 | 1 | 23:35 | Night | Sunday | 2016 | 9
2921 | 2016-10-04 22:01 | 2016-10-04 22:01 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Rain and Lightning | Lightning | 56 | CKBS VCB fdr #6 T/R 1x. Not checked yet. | 3198864 | 1 | 22:01 | Night | Tuesday | 2016 | 10
2922 | 2016-10-04 22:01 | 13/04/2016 15:30 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Rain and Lightning | Lightning | 56 | CKBS VCB fdr #6 T/R 1x Ctr: 129-130 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 22:01 | Night | Tuesday | 2016 | 10
2923 | 2016-11-04 00:27 | 2016-11-04 00:27 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 48 | 00:27 6DN fdr #6 Load dropped 146A (193-47A). 6DN fdr #4 Load dropped 74A (221-148A). 11:15 Checked & found, Recl. 6E-64 (6DN fdr #6) T/R 1x Ctr: 35-36. Patrolled the line & found, @3 broken Dead end Insulator o/p #5E-44. Cause: Lightning. | 3198864 | 1 | 0:27 | Night | Friday | 2016 | 11
2924 | 2016-11-04 00:34 | 2016-11-04 00:34 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 41 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3198864 | 1 | 0:34 | Night | Friday | 2016 | 11
2925 | 2016-11-04 00:34 | 13/04/2016 08:15 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 41 | Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1257-1258 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #38CW-07. Cause: Lightning. | 3198864 | 1 | 0:34 | Night | Friday | 2016 | 11
2926 | 2016-11-04 02:14 | 2016-11-04 02:14 | MINAS POWER PLANT |  |  | - | 02:14 MGT #5 Tripped by: Fire detected alarm. Cause: Under Investigation. |  | 1 | 2:14 | Night | Friday | 2016 | 11
2927 | 2016-11-04 04:28 | 2016-11-04 04:28 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 115 | 44KV Pematang Main OCB #1 (Line to Petani) T/R 1x. Not checked yet. | 3198862 | 1 | 4:28 | Morning | Friday | 2016 | 11
2928 | 2016-11-04 04:28 | 2016-12-04 09:28 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 115 | Checked & found, 44KV Pematang Main OCB #1 (Line to Petani) T/R 1x Ctr: 449-450 R/F: 50N. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 4:28 | Morning | Friday | 2016 | 11
2929 | 2016-11-04 15:30 | 2016-11-04 15:30 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Transformer Failure | 5 | 17:55 It was reported b/o fuse for Tx at Well KB #409. 16:36 Checked & found, @2 b/o 7.8SF fuse for 250Kva Tx at Well KB #409. Performed TTR, Megger Test the Tx & found unbalance Tx. Cause: Transformer Failure. (Unbalance TTR) (The Tx failure is not replaced yet) | 3198864 | 1 | 15:30 | Afternoon | Friday | 2016 | 11
2930 | 2016-11-04 15:30 | 2016-12-04 14:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Transformer Failure | 5 | Replaced 250KVA Tx with the same size at well KB-409 then energized the Tx. Cause: Transformer Failure. | 3198864 | 1 | 15:30 | Afternoon | Friday | 2016 | 11
2931 | 2016-11-04 17:23 | 2016-11-04 17:23 | 13.8KV PETANI FEEDER #1 | Fair | Recloser - Control Recloser | 515 | 17:23 Petani fdr #1 Load dropped 92A (209-117A). 18:03 It was reported no power at some wells d/s of Petani fdr #1. 20:21 Checked & found Recl. 33AY-47 (Petani fdr #1) T/SO. Ctr: 130-131. Blocked & closed Recl. 33AY-47, but failed to close. 21:32 Manually opened Petani OCB fdr #1. Closed Bypass Switch of Recl. 33AY-47. 21:40 Blocked & closed Petani OCB fdr #1, Ok. Then released the block. Cause: Control Recloser problem. | 3198862 | 1 | 17:23 | Afternoon | Friday | 2016 | 11
2932 | 2016-12-04 04:44 | 2016-12-04 04:44 | MINAS POWER PLANT |  |  | - | MGT #6 Tripped By alarm: Fire in Turbine or Accecories Area. Cause: Under Investigtion. |  | 1 | 4:44 | Morning | Sunday | 2016 | 12
2933 | 2016-12-04 05:30 | 2016-12-04 05:30 | 13.8KV S. BALAM FEEDER #4 | Fair | Powerline - Jumper | 12 | 05:30 It was reported broken primary Jumper for Tx at Well So.Balam #53. 07:08 Checked & found, @2 broken primary Jumper for 150Kva Tx at Well So.Balam #53. Manual opened all Fuses, to S/D the Tx. 08:07 Repaired broken Jumper above then energized the Tx. Cause: Jumper. | 3198862 | 1 | 5:30 | Morning | Sunday | 2016 | 12
2934 | 2016-12-04 08:08 | 2016-12-04 08:08 | MINAS POWER PLANT |  |  | - | 08:08 S/U MGT #2, then online the Unit at 08:23. 08:25 Opened Minas ACB #25. (Tie Breaker) |  | 1 | 8:08 | Morning | Sunday | 2016 | 12
2935 | 2016-12-04 08:18 | 2016-12-04 08:18 | DURI POWER PLANT |  |  | - | 08:18 S/U DGT #7, then online the Unit at 08:38. |  | 1 | 8:18 | Morning | Sunday | 2016 | 12
2936 | 2016-12-04 09:17 | 2016-12-04 09:17 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 114 | 09:17 Bangko OCB fdr #4 T/SO. Ctr: 99983-99984 R/F: 50N. Bangko GFPC T/SO. Ctr: 495-497 R/F: 50N. 09:21 Manual Closed Bangko GFPC, Ok. 09:40 Blocked & By Passed Bangko GFPC. 09:45 Blocked & closed Bangko OCB fdr #4, Ok. Then released the block. 09:55 It was reported no Power at Benar Fields. 10:08 Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/SO. Ctr: 84-85. 10:10 Blocked & closed Recl. 25Z-07, Ok. Then released the block. Not patrolled yet. | 3198862 | 1 | 9:17 | Morning | Sunday | 2016 | 12
2937 | 2016-12-04 09:17 | 14/04/2016 07:45 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 114 | Patrolled the line & found, @1 broken Pin Insulator o/p #25Z-12. Cause" Pin Insulator. | 3198862 | 1 | 9:17 | Morning | Sunday | 2016 | 12
2938 | 2016-12-04 11:30 | 2016-12-04 11:30 | MINAS POWER PLANT |  |  | - | 11:30 S/U MGT #5, then online the Unit at 11:42. |  | 1 | 11:30 | Morning | Sunday | 2016 | 12
2939 | 2016-12-04 11:55 | 2016-12-04 11:55 | MINAS POWER PLANT |  |  | - | 11:55 Offline MGT #1, then S/D the Unit for S/B. (Prior to repairing Lube Oil leakage at Bearing-2) |  | 1 | 11:55 | Morning | Sunday | 2016 | 12
2940 | 2016-12-04 14:49 | 2016-12-04 14:49 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 31 | 14:49 It was reported b/o fuse for Tx o/p #09-R4-01. 17:32 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx o/p #09-R4-01. Not replaced yet. (The Tx will be tested, need equipment bucket Truck) | 3198862 | 1 | 14:49 | Afternoon | Sunday | 2016 | 12
2941 | 2016-12-04 14:49 | 13/04/2016 15:30 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 31 | Performed TTR & Megger Test 112.5KVA Tx o/p 09-R4-01, found good reading. Replaced @1, @2 b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 14:49 | Afternoon | Sunday | 2016 | 12
2942 | 2016-12-04 17:51 | 2016-12-04 17:51 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 20 | It was reported power outage (T/R) at Pematang GS. Pematang RTU Failed at this time. Suspected Pematang OCB fdr #1 T/R 1x. Not checked yet. | 3198862 | 1 | 17:51 | Afternoon | Sunday | 2016 | 12
2943 | 2016-12-04 17:51 | 13/04/2016 15:10 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 20 | Checked & found, Pematang OCB fdr #1 T/R 1x Ctr: 126-127 R/F: Did not appear. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 17:51 | Afternoon | Sunday | 2016 | 12
2944 | 2016-04-13 12:00 | 2016-04-13 12:00 | 13.8KV 4B FEEDER #1 | Fair | Transformer Failure | 9 | 12:00 It was reported b/o fuse for Tx at Well #4A-34. 15:12 Checked & found, @1, @2 b/o 7.8SF fuses for 300Kva Tx at Well #4A-34. Performed TTR & Megger Test, found Low Mega-ohm Reading Tx. 17:24 Replaced 300Kva Tx above with the same size then energized the Tx. Cause: Tx Failure. (Low Mega-ohm Reading Tx) | 3198864 | 1 | 12:00 | Afternoon | Wednesday | 2016 | 4
2945 | 2016-04-13 14:30 | 2016-04-13 14:30 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Transformer Failure | 4 | 14:30 It was reported b/o fuse for Tx at Well Petapahan #78. 16:00 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Petapahan #78. Performed TTR, Megger Test the Tx & found, low Mega-ohm Reading Tx. Cause: Tx Failure. (Low Mega-ohm reading Tx) (The Tx is not replaced yet) | 3198864 | 1 | 14:30 | Afternoon | Wednesday | 2016 | 4
2946 | 2016-04-13 14:30 | 2016-04-14 14:00 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Transformer Failure | 4 | Replaced 300kva Tx failure with same size then energized the Tx at Well #4A-34. Cause: Tx Failure. | 3198864 | 1 | 14:30 | Afternoon | Wednesday | 2016 | 4
2947 | 2016-04-13 14:38 | 2016-04-13 14:38 | MINAS POWER PLANT |  |  | - | 14:38 S/U MGT #6, then online the Unit at 14:50. |  | 1 | 14:38 | Afternoon | Wednesday | 2016 | 4
2948 | 2016-04-13 15:37 | 2016-04-13 15:37 | 13.8KV MENGGALA FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Menggala fdr #1 Load dropped 35A (185-150A). Menggala GFPC in block position. Not checked yet. | 3198862 | 1 | 15:37 | Afternoon | Wednesday | 2016 | 4
2949 | 2016-04-13 15:37 | 2016-04-16 07:45 | 13.8KV MENGGALA FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 19AO-01 (Menggala fdr #1) T/R 1x Ctr: 451-452 R/F: 51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 15:37 | Afternoon | Wednesday | 2016 | 4
2950 | 2016-04-13 16:35 | 2016-04-13 16:35 | 13.8KV BATANG FEEDER #3 | Rain | Lightning | 48 | Batang OCB fdr #3 T/R 1x. Not checked yet. | 3198862 | 1 | 16:35 | Afternoon | Wednesday | 2016 | 4
2951 | 2016-04-13 16:35 | 2016-04-14 15:45 | 13.8KV BATANG FEEDER #3 | Rain | Lightning | 48 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 312-313 R/F: 50N. Patrolled the line & found: -@1 Burnt out fuse for Tx on TP of Well Candi #04. -@1 Broken L/A & @2 Broken Fuse Holder on TP of Well Candi #01. Cause: Lightning. | 3198862 | 1 | 16:35 | Afternoon | Wednesday | 2016 | 4
2952 | 2016-04-13 17:20 | 2016-04-13 17:20 | DURI POWER PLANT |  |  | - | 17:20 Offline DGT #7, then S/D the Unit for S/B. |  | 1 | 17:20 | Afternoon | Wednesday | 2016 | 4
2953 | 2016-04-14 06:53 | 2016-04-14 06:53 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr #1 Load dropped 60A (236-176A). Not checked yet. | 3198862 | 1 | 6:53 | Morning | Thursday | 2016 | 4
2954 | 2016-04-14 06:53 | 2016-04-19 11:26 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 234-235. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 6:53 | Morning | Thursday | 2016 | 4
2955 | 2016-04-14 10:02 | 2016-04-14 10:02 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | 5 | 10:02 It was reported b/o for Tx o/p #06-Q5-04B. 10:30 Checked & found, @2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #06-Q5-04B. Perform TTR and Megger tested & found, normal. (Good reading) Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 10:02 | Morning | Thursday | 2016 | 4
2956 | 2016-04-14 10:22 | 2016-04-14 10:22 | 13.8KV 5B FEEDER #2 | Fair | Planned Maintenance | 0 | 10:22 Manually opened Recl. 4C-65A (5B fdr #2) To repairing @1 broken jumper Hot Line Clamp on TOP of Well #4D-46. (14 wells were off) 10:55 Manually closed Recl. 4C-65A. Cause: Planned Maintenace. (Repair broken HLC) | 123 | 1 | 10:22 | Morning | Thursday | 2016 | 4
2957 | 2016-04-14 14:53 | 2016-04-14 14:53 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 9 | 14:53 It was reported b/o fuse for Tx o/p #01-08-28. 16:08 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-08-28. Performed TTR and Megger test the Tx & found, normal. (Good reading) Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 14:53 | Afternoon | Thursday | 2016 | 4
2958 | 2016-04-14 16:12 | 2016-04-14 16:12 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 16:12 It was reported @1, @2 b/o fuses for 150Kva Tx at Well Candi #01. Not replaced yet. | 3198862 | 1 | 16:12 | Afternoon | Thursday | 2016 | 4
2959 | 2016-04-14 16:12 | 2016-04-18 16:00 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Candi #01. Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuses above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 16:12 | Afternoon | Thursday | 2016 | 4
2960 | 2016-04-14 16:12 | 2016-04-14 16:12 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 16:12 It was reported @1 b/o 3.5SF fuse for 150Kva Tx at Well Candi #04. Not replaced yet. | 3198862 | 1 | 16:12 | Afternoon | Thursday | 2016 | 4
2961 | 2016-04-14 16:12 | 2016-04-18 16:15 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1,@2 b/o 3.5SF fuse for 150Kva Tx at Well Candi #04. Tested the Tx & found, normal. (good reading) The Tx would be dismanthled, due to Well Candi #01 is a Idle Well. Cause: Unidentified (Fuse). | 3198862 | 1 | 16:12 | Afternoon | Thursday | 2016 | 4
2962 | 2016-04-14 19:58 | 2016-04-14 19:58 | 13.8KV 5B FEEDER #4 | Fair | Transformer Failure | 8 | 19:58 5B OCB fdr #4 T/R 2x. 20:06 5B OCB fdr #4 T/R 2x again. 20:08 5B OCB fdr #4 T/R 1x again. 20:35 It was reported there was spark at Well #4B-54. 21:53 Checked & found, 5B OCB fdr #4 T/R 5x Ctr: 324-329 R/F: 51N. 22:38 Checked & found, @1,@2,@3 b/o 7.8SF fuses for 250Kva Tx. Tested the Tx & found, 250Kva Tx oil leaks. Cause: Tx failure. (The Tx failure is not replaced yet) | 3198864 | 1 | 19:58 | Night | Thursday | 2016 | 4
2963 | 2016-04-14 19:58 | 2016-04-15 17:10 | 13.8KV 5B FEEDER #4 | Fair | Transformer Failure | 8 | Replace 250Kva Tx failure with 300Kva Tx & energized the Tx at Well #4B-54. Cause: Tx Failure. | 3198864 | 1 | 19:58 | Night | Thursday | 2016 | 4
2964 | 2016-04-15 01:49 | 2016-04-15 01:49 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 19 | 01:49 3D OCB fdr #8 T/R 2x. 3D fdr #7 Load dropped 176A (216-40A). 14:45 Checked & found, 3D OCB fdr #8 T/R 3x Ctr: 184-187 R/F: 51N. Patrolled the line & found, @1 broken L/A o/p #3D-46. Cause: Lightning. | 3198864 | 1 | 1:49 | Night | Friday | 2016 | 4
2965 | 2016-04-15 02:07 | 2016-04-15 02:07 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 5 | 02:07 3D fdr #4 Load dropped 72A (239-167A). 14:57 Checked & found, Recl. 2D-14 (3D fdr #4) T/R 1x Ctr: 34-35. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 2:07 | Night | Friday | 2016 | 4
2966 | 2016-04-15 06:18 | 2016-04-15 06:18 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Lightning | 0 | So.Balam fdr #1 Load dropped 14A (90-76A). So.Balam fdr #4 Load dropped 16A (163-147A). So.Balam GFPC T/R 1x. (Ground fault alarm on So.Balam fdr #1) Not checked yet. | 3198862 | 1 | 6:18 | Morning | Friday | 2016 | 4
2967 | 2016-04-15 06:18 | 2016-04-17 17:15 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 209-210 R/F: 51N. Checked Recloser at downstream of So.Balam fdr #1 & fdr #4 are normal. (Ctr; Did not change) Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 6:18 | Morning | Friday | 2016 | 4
2968 | 2016-04-15 11:25 | 2016-04-15 11:25 | 13.8KV BANGKO FEEDER #4 | Drizzle | Powerline - Conductor | 694 | 11:25 Bangko OCB fdr #4 T/O. (In blocked position for RIG HPS #09 Job at Well BKO #31) 11:48 It was reported fallen conductor towards Test Sta-A. 11:55 Checked & found, @3 broken conductor o/p #24Y-05. 12:10 Opened LBS-02. (To isolate Power line & Installed personal ground at the spot) (To Repairing broken conductor & jumpers, also replacing broken Pin Insulator) 16:00 Removed personal ground, then Closed LBS #02. 16:33 Blocked & closed Bangko OCB fdr #4, Ok. (Bangko OCB fdr #4 is still in blocked position for RIG HPS #09 Job at Well BKO #31) 16:40 It was reported that Benar-Gs is still no power. 17:10 Checked & found Recl. 25Z-07 (Bangko fdr #4) T/SO. Ctr: 85-86. 17:18 Blocked & closed Recl. 25Z-07, Ok. Then released the blocked. Cause: Broken Conductor. | 3198862 | 1 | 11:25 | Morning | Friday | 2016 | 4
2969 | 2016-04-15 14:54 | 2016-04-15 14:54 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Transformer Failure | 0 | It was reported b/o fuse for Tx o/p #03-06-25. Checked & found, @1 ,@2 b/o 3.1SF fuses and also oil leakage, on secondary bushing for 112.5Kva Tx o/p #03-06-25. Replaced b/o fuse above with the same size but b/o again. Cause: Tx failure. (The Tx is not tested yet) | 3198862 | 1 | 14:54 | Afternoon | Friday | 2016 | 4
2970 | 2016-04-15 14:54 | 2016-04-16 11:30 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Transformer Failure | 0 | Performed TTR, Megger test the Tx o/p #03-06-25 & found, Low megger reading. Cause: Tx failure. (Low megger reading) (This Tx is not replaced yet) | 3198862 | 1 | 14:54 | Afternoon | Friday | 2016 | 4
2971 | 2016-04-15 14:54 | 2016-04-30 11:02 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Transformer Failure | 0 | Replaced 112.5Kva Tx failure with the same size and Energized the Tx o/p #03-06-25. Cause: Tx Failure. | 3198862 | 1 | 14:54 | Afternoon | Friday | 2016 | 4
2972 | 2016-04-15 15:29 | 2016-04-15 15:29 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 0 | Ketigul fdr #1 Load dropped 73A (134-61A). Not checked yet. | 3198862 | 1 | 15:29 | Afternoon | Friday | 2016 | 4
2973 | 2016-04-15 15:29 | 2016-04-19 11:03 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 0 | Checked & found, Recl. 32AK-16 (Ketigul fdr #1) T/R 1x Ctr: 119-120. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 15:29 | Afternoon | Friday | 2016 | 4
2974 | 2016-04-16 11:50 | 2016-04-16 11:50 | 13.8KV 4D FEEDER #5 | Fair | Unidentified (Fuse) | 1 | 11:50 It was reported b/o fuse for Tx at Well #4D-46A. 15:40 Checked & found, @2 b/o 3.5SF fuse for 150kva Tx at Well #4D-46A. Replaced b/o fuse with same size then energized the Tx. Cause: Unidentified (Fuse). | 3198864 | 1 | 11:50 | Morning | Saturday | 2016 | 4
2975 | 2016-04-16 16:40 | 2016-04-16 16:40 | 13.8KV 4D FEEDER #5 | Fair | Transformer Failure | 34 | 16:40 It was reported b/o fuse for Tx at Well #4D-68. 18:14 Checked & found, @2,@3 b/o 14.0SF fuses for 450Kva Tx at Well #4D-68. Performed TTR, Megger test the Tx & found, Unbalance TTR. Cause: Tx Failure. (Unbalance TTR) (The Tx failure is not replaced yet) | 3198864 | 1 | 16:40 | Afternoon | Saturday | 2016 | 4
2976 | 2016-04-16 16:40 | 26/05/2016 16:40 | 13.8KV 4D FEEDER #5 | Fair | Transformer Failure | 34 | Replaced 550Kva Tx failure with the same size & energized the Tx at Well #4D-68. Cause: Tx Failure. | 3198864 | 1 | 16:40 | Afternoon | Saturday | 2016 | 4
2977 | 2016-04-16 18:12 | 2016-04-16 18:12 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr #1 Load dropped 33A (240-207A). Not checked yet. | 3198862 | 1 | 18:12 | Afternoon | Saturday | 2016 | 4
2978 | 2016-04-16 18:12 | 2016-04-19 11:25 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/R 1x Ctr: 173-174. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 18:12 | Afternoon | Saturday | 2016 | 4
2979 | 2016-04-17 02:16 | 2016-04-17 02:16 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 25 | 02:16 Libo OCB fdr #1 T/R 1x. 03:46 Libo OCB fdr #1 T/R 1x again. Not checked yet. | 3198862 | 1 | 2:16 | Night | Sunday | 2016 | 4
2980 | 2016-04-17 02:16 | 2016-04-19 12:35 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 25 | Checked & found, Libo OCB fdr #1 T/R 2x Ctr: 366-368 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. Also found, Recl. 34CA-04 (Libo fdr #1) T/R 1x Ctr: 39-40. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 2:16 | Night | Sunday | 2016 | 4
2981 | 2016-04-17 04:11 | 2016-04-17 04:11 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 31 | CKBS VCB fdr #1 T/R 1x. CKBS fdr #2 load dropped 251A ( 258-7A). CKBS fdr #3 load dropped 54A ( 62-8A). Not checked yet. | 3198864 | 1 | 4:11 | Morning | Sunday | 2016 | 4
2982 | 2016-04-17 04:11 | 2016-04-20 08:45 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 31 | Checked & found, CKBS VCB fdr #1 T/R 1x Ctr: 215-216 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 4:11 | Morning | Sunday | 2016 | 4
2983 | 2016-04-17 04:11 | 2016-04-17 04:11 | 13.8KV PETAPAHAN FEEDER #2 | Rain and Lightning | Lightning | 0 | 04:11 Petapahan fdr #2 Load dropped 37A (157-120A). 15:40 Checked & found, Recl. 38CW-01 (Petapahan fdr #2) T/R 1x Ctr: 43-44. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 4:11 | Morning | Sunday | 2016 | 4
2984 | 2016-04-17 04:13 | 2016-04-17 04:13 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 310 | CKBS VCB fdr #5 T/R 1x. CKBS fdr #6 load dropped 140A (176-36A). Not checked yet. | 3198864 | 1 | 4:13 | Morning | Sunday | 2016 | 4
2985 | 2016-04-17 04:13 | 2016-04-18 07:50 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 310 | Checked & found, CKBS VCB fdr #5 T/R 1x Ctr: 141-142 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #36CU-27. Cause: Lightning. | 3198864 | 1 | 4:13 | Morning | Sunday | 2016 | 4
2986 | 2016-04-17 04:25 | 2016-04-17 04:25 | 115KV KOTABATAK - PETAPAHAN LINE | Rain and Lightning | Lightning | 527 | 115KV CKB GCB #1 (115KV Line to Petapahan) T/R 1x. (Petapahan & Suram Substations are no power at the time) No checked yet. | 3198864 | 1 | 4:25 | Morning | Sunday | 2016 | 4
2987 | 2016-04-17 04:25 | 2016-04-18 09:30 | 115KV KOTABATAK - PETAPAHAN LINE | Rain and Lightning | Lightning | 527 | Checked & found, 115KV CKB GCB #1 (115KV line to Petapahan) T/R 1x Ctr: 34-35 R/F: 21@1,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 4:25 | Morning | Sunday | 2016 | 4
2988 | 2016-04-17 05:08 | 2016-04-17 05:08 | 13.8KV BATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Batang OCB fdr #1 T/R 1x. Not checked yet. | 3198862 | 1 | 5:08 | Morning | Sunday | 2016 | 4
2989 | 2016-04-17 05:08 | 2016-04-21 08:20 | 13.8KV BATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Batang OCB fdr #1 T/R 1x Ctr: 110-111 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 5:08 | Morning | Sunday | 2016 | 4
2990 | 2016-04-17 05:34 | 2016-04-17 05:34 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 15 | Pungut fdr #2 Load dropped 71A (82-11A). Pungut fdr #1 Load dropped 32A (82-50A). Not checked yet. | 3198862 | 1 | 5:34 | Morning | Sunday | 2016 | 4
2991 | 2016-04-17 05:34 | 2016-04-19 11:05 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 15 | Checked & found, Recl. 45BR-01 (Pungut fdr #2) T/R 1x Ctr: 490-491. Patrolled the line & found, @1,@3 broken Pin Insulators o/p #46BT-12. Cause: Lightning. | 3198862 | 1 | 5:34 | Morning | Sunday | 2016 | 4
2992 | 2016-04-17 07:08 | 2016-04-17 07:08 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Heavy Rain | Others | 0 | 07:08 Manually opened CKBS VCB fdr #6. (Request by Kt.Batak-GS) (To anticipate spills at Kt.Batak-GS, due to failed to S/U some WIPs) 08:17 Manually closed CKBS VCB fdr #6. Cause: Others. (Production lost is not charged to PGT) | 3198864 | 1 | 7:08 | Morning | Sunday | 2016 | 4
2993 | 2016-04-17 08:32 | 2016-04-17 08:32 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | - | Pematang fdr #1 Load dropped 74A (147-73A). Not checked yet. | 3198862 | 1 | 8:32 | Morning | Sunday | 2016 | 4
2994 | 2016-04-17 08:32 | 2016-04-21 08:15 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | - | Checked & found, Pematang OCB fdr #1 T/R 1x Ctr: 126-127 R/F: Did not appear. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 8:32 | Morning | Sunday | 2016 | 4
2995 | 2016-04-17 08:36 | 2016-04-17 08:36 | 13.8KV PETANI FEEDER #1 | Fair | Animal | 15 | 08:36 It was reported b/o fuse for Tx at Well Petani #124. 13:30 Checked & found, @1,@2 b/o 14.0SF fuses for 500kva Tx at Well Petani #124. Performed test TTR, Megger the Tx & found, normal. (good reading) Replaced b/o fuse with same size then energized the Tx. Cause: Animal. (Rat) | 3198862 | 1 | 8:36 | Morning | Sunday | 2016 | 4
2996 | 2016-04-17 18:48 | 2016-04-17 18:48 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 18:48 C.Duri fdr #7 load dropped 111A (172-71A). 20:00 It was reported b/o fuse for 1000Kva Tx at CGS-3. (Some motor pumps/loads of the Tx at CGS-3 were off) 21:00 Checked & found, @3 b/o 14.0SF fuse for 1000Kva Tx at CGS-3. Performed Megger and TTR test the Tx, found Normal. Replaced the b/o fuse with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 18:48 | Afternoon | Sunday | 2016 | 4
2997 | 2016-04-18 06:57 | 2016-04-18 06:57 | 13.8KV 6D FEEDER #4 | Fair | Unidentified | 0 | 6D OCB fdr #4 T/R 1x. Not checked yet. | 3198864 | 1 | 6:57 | Morning | Monday | 2016 | 4
2998 | 2016-04-18 06:57 | 2016-04-19 16:57 | 13.8KV 6D FEEDER #4 | Fair | Unidentified | 0 | Checked & found, 6D OCB fdr #4 T/R 1x Ctr: 536-537 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3198864 | 1 | 6:57 | Morning | Monday | 2016 | 4
2999 | 2016-04-18 09:35 | 2016-04-18 09:35 | 13.8KV RANGAU FEEDER #2 | Fair | Lightning Arrester | 31 | Rangau fdr #2 Load dropped 67A (83-16A). Not checked yet. | 3198862 | 1 | 9:35 | Morning | Monday | 2016 | 4
3000 | 2016-04-18 09:35 | 2016-04-20 16:15 | 13.8KV RANGAU FEEDER #2 | Fair | Lightning Arrester | 31 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: 130-131. Patrolled the line & found, @3 broken L/A o/p #21BD-01. Cause: Lightning Arrester. | 3198862 | 1 | 9:35 | Morning | Monday | 2016 | 4
3001 | 2016-04-18 10:45 | 2016-04-18 10:45 | 13.8KV NORTH DURI FEEDER #7 | Fair | Animal | 0 | 10:45 It was reported b/o fuse for Tx o/p #10-K4-40. 16:28 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #10-K4-40. Performed TTR & Megger Test the Tx, found good reading. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. | 3198862 | 1 | 10:45 | Morning | Monday | 2016 | 4
3002 | 2016-04-18 14:28 | 2016-04-18 14:28 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 14 | 14:28 CGT #5 Tripped. By Alarm: Generator electrical protection problem. Frequency dropped to 59,62 Hz. (Load shedding level-1) 4D fdr #3 T/O. Closed at: 15:29. 3D fdr #5 T/O. Closed at: 15:28. 15:53 S/U CGT #5, then online the Unit at 16:22. Cause: Under Investigation. | 3198862 | 1 | 14:28 | Afternoon | Monday | 2016 | 4
3003 | 2016-04-18 15:55 | 2016-04-18 15:55 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 62 | 15:55 OKB fdr #2 Load dropped 175A (249-74A). 17:35 Checked & found, Recl. 38CW-01 (OKB fdr #2) T/SO. Ctr: 27-28. 17:36 Blocked & closed Recl. 38CW-01, Ok. Then release the blocked. Not Patrolled yet. | 3198864 | 1 | 15:55 | Afternoon | Monday | 2016 | 4
3004 | 2016-04-18 15:55 | 2016-04-20 08:50 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 62 | Patrolled line at downstream of Recl. 38CW-01, but found nothing. Cause: Unidentified. | 3198864 | 1 | 15:55 | Afternoon | Monday | 2016 | 4
3005 | 2016-04-18 16:19 | 2016-04-18 16:19 | 3 DELTA SUBSTATION | Fair | Voltage regulator failure | 108 | 16:19 115KV 3D C/S-TX #1 T/O. 17:20 Checked & found, 115KV 3D C/S-TX #1 T/O. Ctr: 108-109 R/F: 87@3 & 86T. Also found, @2 VR bushing Oil Leakage. (VR can not be Energized) 17:22 Reset all R/F and By Passing VR of 3D TX #1. 17:25 Open 3D OCB fdr #3, then Closed at 17:55. 17:25 Open 3D OCB fdr #4, then Closed at 17:56. 17:26 Open 3D OCB fdr #5, then Closed at 17:53. 17:52 Closed 115KV 3D C/S-TX #1, Ok. Transferred load 3D fdr #5 to 3D fdr #6. (Due to 3D Bus voltage of TX #1 low) 18:20 Closed LBS #3D-223. (3D fdr #5 paralled with 3D fdr #6) 18:21 Opened 3D OCB fdr #5. Cause: Voltage Regulator Failure. | 3198864 | 1 | 16:19 | Afternoon | Monday | 2016 | 4
3006 | 2016-04-18 18:57 | 2016-04-18 18:57 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 32 | Bekasap VCB fdr #6 T/R 1x. Bekasap fdr #5 load dropped 79A (272-193A). T/O WIP at Bekasap GS. Not checked yet. | 3198862 | 1 | 18:57 | Afternoon | Monday | 2016 | 4
3007 | 2016-04-18 18:57 | 2016-04-20 13:50 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 32 | Checked & found, Bekasap VCB fdr #6 T/R 1x Ctr: 338-339 R/F: 51N. Patrolled the line & found, @2 broken Dead end Insulator o/p #38BE-05. Cause: Lightning. | 3198862 | 1 | 18:57 | Afternoon | Monday | 2016 | 4
3008 | 2016-04-18 21:58 | 2016-04-18 21:58 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | 21:58 It was reported b/o fuses for Tx at AWT Area-1. 00:30 Checked & found, @2 b/o 14.0SF fuse for 500Kva Tx at AWT Area-1. Performed Megger and TTR test the Tx, found good reading. Replaced the b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 21:58 | Night | Monday | 2016 | 4
3009 | 2016-04-19 10:25 | 2016-04-19 10:25 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 35 | 10:25 It was reported b/o fuse for Tx o/p #01-2-27. (C.Duri fdr #6) 11:50 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-2-27. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 10:25 | Morning | Tuesday | 2016 | 4
3010 | 2016-04-19 16:08 | 2016-04-19 16:08 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | CGT #5 Tripped. By Alarm: Generator Electricel Protection Trouble. Cause: Under Investigation. | 3198862 | 1 | 16:08 | Afternoon | Tuesday | 2016 | 4
3011 | 2016-04-20 08:21 | 2016-04-20 08:21 | NORTH DURI POWER PLANT |  |  | - | 08:21 S/U NDC-CT #1, then Online the Unit at 08:53. (After HGPI Inspection program) 20:47 Off Line NDC-CT #1, then S/D at 20:50. (For S/B - Prior to repairing Gas leak at Stage-C of Fuel Nozzle #10) | 123 | 1 | 8:21 | Morning | Wednesday | 2016 | 4
3012 | 2016-04-20 20:47 | 2016-04-20 20:47 | NORTH DURI POWER PLANT |  |  | - | 20:47 Off Line NDC-CT #1, then S/D at 20:50. (For S/B - Prior to repairing gas leak at Stage-C of Fuel Nozzle #10) |  | 1 | 20:47 | Night | Wednesday | 2016 | 4
3013 | 2016-04-21 06:24 | 2016-04-21 06:24 | NORTH DURI POWER PLANT |  |  | - | 06:24 S/U NDC-CT #1, then On Line Unit at at 06:51. (After fixing Gas Leak at Stage-C Fuel Nozzle #10 & hot spot on CT Insulation) |  | 1 | 6:24 | Morning | Thursday | 2016 | 4
3014 | 2016-04-21 09:10 | 2016-04-21 09:10 | 13.8KV 8C FEEDER #4 | Fair | Planned Maintenance | 15 | 09:10-16:00 Switching to S/D 8C Bus-2, due to re-install Bus conduit & 112.5Kva Sta. service. Transfered Load of 8C fdr #4 to MSU-1 fdr #1. (8C fdr #5) (10 Wells were Off during the Job) Cause: Maintenance Job. | 123 | 1 | 9:10 | Morning | Thursday | 2016 | 4
3015 | 2016-04-21 09:41 | 2016-04-21 09:41 | 13.8KV MINAS FEEDER #6 | Fair | Others | - | 09:41 Minas fdr #6 Load dropped 133A (204-71A). Minas GS-3 found, 12" Production line leakage at near Well #6E-65. Minas GS-1 & & GS-3 manually S/D 31 Wells at downstream of Minas fdr #6. 17:45 Re-S/U all the Wells, after repairing the leaking 12" Production line above. Cause: Others. (No Prod. loss charged to PGT) | 123 | 1 | 9:41 | Morning | Thursday | 2016 | 4
3016 | 2016-04-21 15:38 | 2016-04-21 15:38 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 13 | 3D OCB fdr #8 T/R 1x. 3D fdr #6 Load dropped 261A (269-8A). 3D fdr #7 Load dropped 210A (218-8A). Not checked yet. 24-Apr-2016 Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 187-188 R/F: 50N. Patrolled the line & found, @2 broken Dead end Insulator o/p #3E-03. Cause: Lightning. (See at 16:32 on 22-apr-2016 report) | 3198864 | 1 | 15:38 | Afternoon | Thursday | 2016 | 4
3017 | 2016-04-21 15:44 | 2016-04-21 15:44 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 20 | 3D OCB fdr #3 T/R 1x. Not checked yet. | 3198864 | 1 | 15:44 | Afternoon | Thursday | 2016 | 4
3018 | 2016-04-21 15:44 | 2016-04-24 07:45 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 20 | Checked & found, 3D OCB fdr #3 T/R 1x Ctr: 434-435 R/F: 50N(@2). Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 15:44 | Afternoon | Thursday | 2016 | 4
3019 | 2016-04-21 15:53 | 2016-04-21 15:53 | 4 DELTA SUBSTATION | Rain and Lightning | Unidentified | 433 | 15:53 Found, 4D, 3D, 4B, KBJ RTU failed. 16:27 3D, 4B, KBJ RTU back to normal, but 4D RTU is still failed. 20:19 It was reported no power for starting WIP at GS-5. 20:26 Manual Open 3D OCB fdr #4. (GS-5 Requested, to anticipate Spill), then Closed at: 21:50. 20:33 Checked & found, 115KV 4D C/S-TX #1 T/O. Ctr: 1766-1767 R/F: 51G. Visual checked the TX #1 & VR #1 & found, normal. 20:52 Manual opened 13.8KV 4D OCB fdr #1, #2, #3. Manual opened Isolation Switches for All OCB above. 21:01 Closed 115KV 4D C/S-TX #1, Ok. (4D RTU back to normal). Closed Isolation Switches for 4D OCB fdr #1, #2, #3. 21:06 Blocked & closed 4D OCB fdr #1, Ok. Then released the block. 21:13 Blocked & closed 4D OCB fdr #2, Ok. Then released the block. 21:17 Blocked & closed 4D OCB fdr #3, Ok. Then released the block. Cause: Under Investigation. | 3198864 | 1 | 15:53 | Afternoon | Thursday | 2016 | 4
3020 | 2016-04-21 17:40 | 2016-04-21 17:40 | MINAS POWER PLANT |  |  | - | 17:40 Off line MGT #10, then S/D the Unit for S/B. (Prior to Fix the leaking of Atomazing Air compressor) |  | 1 | 17:40 | Afternoon | Thursday | 2016 | 4
3021 | 2016-04-22 06:24 | 2016-04-22 06:24 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 134 | So.Balam VCB fdr #4 T/R 1x. Not checked yet. | 3198862 | 1 | 6:24 | Morning | Friday | 2016 | 4
3022 | 2016-04-22 06:24 | 2016-04-28 08:51 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 134 | Checked & found, So.Balam VCB fdr #4 T/R 4x Ctr: 210-214 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 6:24 | Morning | Friday | 2016 | 4
3023 | 2016-04-22 06:45 | 2016-04-22 06:45 | 13.8KV 8C FEEDER #1 | Fair | Powerline - Jumper | 101 | 06:45 8C VCB fdr #1 T/R 1x. 8C fdr #3 load dropped 169A (218-49A). 11:45 Checked & found, 8C VCB fdr #1 T/R 3x Ctr: 636-639 R/F: 51N. Patrolled the line & found, @2 broken Jumper o/p #9D-45. Cause: Jumper. | 3198864 | 1 | 6:45 | Morning | Friday | 2016 | 4
3024 | 2016-04-22 06:45 | 2016-04-25 11:41 | 13.8KV 8C FEEDER #1 | Fair | Powerline - Jumper | 101 | 11:41 Repair @2 broken jumper o/p# 9D-45. (wells #9D-53 and #9D54 back on running). Cause: Jumper (broken). | 3198864 | 1 | 6:45 | Morning | Friday | 2016 | 4
3025 | 2016-04-22 09:32 | 2016-04-22 09:32 | 13.8KV SINTONG FEEDER #1 | Fair | Planned Maintenance | 226 | 09:32-10:57 Performed Switching to Shutdown Recl. 25AD-26 (Sintong fdr #1). Relocated power line for Well Seruni #37. (1 Span =/+ 50Meters). All Production losses are charged to Project. Cause: Planned Maintenance. | 123 | 1 | 9:32 | Morning | Friday | 2016 | 4
3026 | 2016-04-22 11:23 | 2016-04-22 11:23 | 13.8KV BATANG FEEDER #2 | Fair | Pin Insulator | 0 | Batang OCB fdr #2 T/R 1x. Not checked yet. | 3198862 | 1 | 11:23 | Morning | Friday | 2016 | 4
3027 | 2016-04-22 11:23 | 2016-04-28 15:55 | 13.8KV BATANG FEEDER #2 | Fair | Pin Insulator | 0 | Checked & found, Batang OCB fdr #2 T/R 1x Ctr: 122-123 R/F: 51N. Patrolled the line & found, @1 F/O Pin Insulator o/p #35AE-02. Cause: Pin Insulator. | 3198862 | 1 | 11:23 | Morning | Friday | 2016 | 4
3028 | 2016-04-22 16:32 | 2016-04-22 16:32 | 13.8KV 3D FEEDER #8 | Fair | Dead End Insulator | 12 | 3D OCB fdr #8 T/R 1x. Not checked yet. | 3198864 | 1 | 16:32 | Afternoon | Friday | 2016 | 4
3029 | 2016-04-22 16:32 | 2016-04-24 07:30 | 13.8KV 3D FEEDER #8 | Fair | Dead End Insulator | 12 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 188-189 R/F: 50N. Patrolled the line & found, @2 broken Dead end Insulator o/p #3E-03. Cause: Dead end Insulator. (Also see report at 15:38 on 21-Apr-2016) | 3198864 | 1 | 16:32 | Afternoon | Friday | 2016 | 4
3030 | 2016-04-22 18:13 | 2016-04-22 18:13 | CENTRAL DURI POWER PLANT |  |  | - | 18:13 S/U CGT #5, then On Line the Unit at 18:35. |  | 1 | 18:13 | Afternoon | Friday | 2016 | 4
3031 | 2016-04-22 18:32 | 2016-04-22 18:32 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 62 | Sintong OCB fdr #2 T/R 1x. Not checked yet. | 3198862 | 1 | 18:32 | Afternoon | Friday | 2016 | 4
3032 | 2016-04-22 18:32 | 2016-04-29 16:30 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 62 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 409-410 R/F: 51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 18:32 | Afternoon | Friday | 2016 | 4
3033 | 2016-04-22 19:20 | 2016-04-22 19:20 | MINAS POWER PLANT |  |  | - | 19:20 Off line MGT #5, then S/D the Unit for S/B. |  | 1 | 19:20 | Night | Friday | 2016 | 4
3034 | 2016-04-22 23:12 | 2016-04-22 23:12 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Unidentified (Fuse) | 49 | 23:12 It was reported b/o fuse for Tx at Well Petapahan #123. 23:55 Checked & found, @1 b/o 14.0SF fuse for 400Kva Tx at Well Petapahan #123. Performed TTR and Megger test the Tx found, normal. (good reading) Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (Fuse). | 3198864 | 1 | 23:12 | Night | Friday | 2016 | 4
3035 | 2016-04-22 23:14 | 2016-04-22 23:14 | 115KV SINTONG - BANGKO LINE | Rain and Lightning | Lightning | 40275 | 23:14 115KV Sintong OCB #22 (Line to Bangko) T/LO. 23:22 Blocked & closed, 115KV Sintong OCB #22, but failed. (Requested by Mr Winarto) 23:29 It was reported broken 115KV Power line at Batang ibul. (It was reported by Bangko Security to secure scene) 23:49 Patrolled 115KV Sintong-Bangko line & found, @3 broken conductor o/p #BKO-30. 23-April-2016. 00:13 Manually opened 13.8KV Sintong OCB fdr #2. (It is requested by Bangko-GS, to avoid spill at Benar-GS) 00:40 Checked & found, 115KV Sintong OCB #22 (Line to Bangko) T/LO. Ctr: 611-615 R/F: 21G @C. -Opened Line Switch of 115KV Sintong OCB # 22. -Closed Grounding Switch of 115KV Sintong-Bangko Line. 01:09 Manually opened Recl. 28AF-02 (Sintong fdr #2), to isolate Benar-GS. 01:11 Manually closed 13.8KV Sintong OCB fdr #2. 03:46 Manually closed Recl. 28AF-02 (Sintong fdr #2). 05:02 Manually opened 115KV Bangko OCB fdr #24. (Bangko-Nella line) Manually opened 115KV Bangko Circuit Switcher. (Then Repairing @3 broken 115KV Sintong-Bangko line between poles BKO #30 and #31) 13:02 Manually opened Nella OCB fdr #1 Manually opened Nella OCB fdr #2. 13:03 Manually opened Bangko OCB fdr #1 Manually opened Bangko OCB fdr #2, and closed at 13:31 13:04 Manually opened Bangko OCB fdr #3, and closed at 13:31 Manually opened Bangko OCB fdr #4 13:05 Opened 115KV Grounding Switch at Bangko Switching station. 13:10 Closed Line switch of OCB #22 at Sintong SS. 13:18 Closed 115KV Sintong OCB #22, but T/O again. Ctr: 615-616 & R/F: Did not appear. (115KV Sintong-Bangko line energized) 13:33 Closed 115KV Bangko OCB #24. (115KV Bangko-Nella line energized) 13:35 Closed 115KV Bangko Circuit Switcher. (To energized Bangko SS) 14:10 Found Bangko Bus Voltage dropped to 12.33KV, then energized Bangko Cap. Bank & Raise up VR. 15:00 Checked & found unbalance Voltage at 13.8KV Bangko Bus. 15:27 Re-Opened 115KV Sintong OCB #22, to exercise 115KV Sintong Line Sw. (Line to Bangko) (3X Patrolling 115KV Sintong-Bangko line, but found nothing) 20:29 Manually opened 115KV Batang OCB #1 20:30 Manually opened 115KV Sintong OCB #25. (Line to Batang) 20:30 Manually opened 115KV Sintong OCB #23. (Line to Menggala) 20:31 Manually opened 115KV Menggala OCB #28. (Line to Sintong) 20:40 Opened 115KV Line Switch of Sintong OCB #25. Opened 115KV Line Switch of Sintong OCB #23. Then installed personal ground on load & source side of Sintong OCB #22. 21:00 Repaired & closed Bypass Switch of 115KV Sintong OCB #22. Repaired & opened both side Isolation switches of 115KV Sintong OCB #22. Tested contactor of 115KV Sintong OCB #22 & found, @3 no Contact 23:30 Closed 115KV Line Switch of Sintong OCB #25 and #23. (after removing personal ground of 115KV Sintong OCB #22) Resetting Distance Reflay D-60 of 115KV Batang OCB #1 and 115KV Menggala OCB #28. 24-April-2016. 00:06 Closed 115KV Batang OCB #1. 00:12 Closed 115KV Sintong OCB#25. 00:13 Closed 115KV Sintong OCB #23. 00:18 Opened 13.8KV Bangko OCB fdr #2 and fdr #3. 00:20 Closed 115KV Bangko Circuit Switcher. (Bangko SS energized) 00:21 Closed 13.8KV Bangko OCB fdr #2 and fdr #3. 00:22 Closed 115KV Menggala OCB #28. (115KV C.Duri-Batang-Bangko & Pematang line back to loop) 00:26 Closed 115KV Bangko OCB #24. (115KV Bangko-Nella line energized) 02:30 Adjusted VR of Bangko SS. at Neutral position. 02:35 It was reported no power at Pinang field. 03:04 Closed 13.8KV Bangko OCB fdr #4. 03:26 Closed 13.8KV Bangko OCB fdr #1. 03:30 Closed 13.8KV Nella OCB fdr #1. 03:33 Closed 13.8KV Nella OCB fdr #2. 03:52 Checked & found, 115KV MSU-2 C/S. T/O. R/F:.... 03:54 Opened 13.8KV MSU-2 fdr #1. (Pinang fdr #1) 03:58 Closed 115KV MSU-2 C/S, Ok. 03:59 Closed 13.8KV MSU-2 fdr #1 (Pinang fdr #1), Ok. Cause: Lightning. | 3198862 | 1 | 23:14 | Night | Friday | 2016 | 4
3036 | 2016-04-23 00:15 | 2016-04-23 00:15 | CENTRAL DURI POWER PLANT |  |  | - | 00:15 Off Line CGT #2, then S/D the Unit for S/B. (Prior to C/I program) |  | 1 | 0:15 | Night | Saturday | 2016 | 4
3037 | 2016-04-23 01:05 | 2016-04-23 01:05 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 113 | 01:05 Petani OCB fdr #2 T/R 1x. Petani fdr #1 Load dropped 100A (206-106A). 01:46 Petani OCB fdr #2 T/R 1x again. Not checked yet. | 3198862 | 1 | 1:05 | Night | Saturday | 2016 | 4
3038 | 2016-04-23 01:05 | 2016-04-27 07:15 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 113 | Checked & found, Petani OCB fdr #2 T/R 2x Ctr: 183-185 R/F: 51N & 50@2,@3. Patrolled the line & found: -@3 Broken L/A on TP of Well Petani #48. -@3 Flashed over Pin Insulator o/p #32AW-37. Cause: Lightning. | 3198862 | 1 | 1:05 | Night | Saturday | 2016 | 4
3039 | 2016-04-23 01:53 | 2016-04-23 01:53 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 579 | Rangau OCB fdr #2 T/R 1x. Not checked yet. | 3198862 | 1 | 1:53 | Night | Saturday | 2016 | 4
3040 | 2016-04-23 01:53 | 2016-04-28 15:37 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 579 | Checked & found, Rangau OCB fdr #2 T/R 2x Ctr: 306-308 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 1:53 | Night | Saturday | 2016 | 4
3041 | 2016-04-23 01:54 | 2016-04-23 01:54 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 92 | 01:54 Pematang OCB fdr #1 T/O. (In blocked for RIG BMS #09 job at Well Pematang #54) (Call RIG-BMS #09 and Normal condition) 02:00 Blocked & Closed Pematang OCB fdr #1, Ok. (Still in blocked due to RIG Activity) Not checked yet. | 3198862 | 1 | 1:54 | Night | Saturday | 2016 | 4
3042 | 2016-04-23 01:54 | 2016-04-27 07:00 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 92 | Checked & found, Pematang OCB fdr #1 T/O. Ctr: 127-128 R/F: 51N. (In Block position) Patrolled the line & found: -@3 Flashed over Dead end Insulator o/p #NN. (Near Well Pematang #64) -@1,@2 Flashed over Pin Insulator o/p #34BC-35. Cause: Lightning. | 3198862 | 1 | 1:54 | Night | Saturday | 2016 | 4
3043 | 2016-04-23 01:55 | 2016-04-23 01:55 | 13.8KV RANGAU FEEDER #1 | Rain and Lightning | Lightning | 156 | Rangau OCB fdr #1 T/R 1x. Not checked yet. | 3198862 | 1 | 1:55 | Night | Saturday | 2016 | 4
3044 | 2016-04-23 01:55 | 2016-04-28 15:35 | 13.8KV RANGAU FEEDER #1 | Rain and Lightning | Lightning | 156 | Checked & found, Rangau OCB fdr #1 T/R 1x Ctr: 007-008 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 1:55 | Night | Saturday | 2016 | 4
3045 | 2016-04-23 01:56 | 2016-04-23 01:56 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 0 | 44KV Pematang Main OCB #2 (Line to Rangau) T/R 1x. Not checked yet. | 3198862 | 1 | 1:56 | Night | Saturday | 2016 | 4
3046 | 2016-04-23 01:56 | 2016-04-27 07:45 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 0 | Found, 44KV Pematang Main OCB #2 (line to Rangau) T/R 1x Ctr: 11115-11116 R/F: 50@3. Patrolled the line & found, @3 F/O Dead end Insulator o/p #RGU-39 & RGU-29. Cause: Lightning. | 3198862 | 1 | 1:56 | Night | Saturday | 2016 | 4
3047 | 2016-04-23 03:34 | 2016-04-23 03:34 | 13.8KV LIBO FEEDER #1 | Fair | Lightning Arrester | 7 | Libo OCB fdr #1 T/R 1x. Not checked yet. | 3198862 | 1 | 3:34 | Night | Saturday | 2016 | 4
3048 | 2016-04-23 03:34 | 2016-04-27 13:35 | 13.8KV LIBO FEEDER #1 | Fair | Lightning Arrester | 7 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 368-369 R/F: 50N. Patrolled the line & found, @2 broken L/A on TP of Well S.E Libo #08. Cause: Lightning Arrester. | 3198862 | 1 | 3:34 | Night | Saturday | 2016 | 4
3049 | 2016-04-23 07:06 | 2016-04-23 07:06 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Post Pin Insulator | 0 | Duri Community ACB fdr #2 T/R 1x. Not checked yet. | 3198862 | 1 | 7:06 | Morning | Saturday | 2016 | 4
3050 | 2016-04-23 07:06 | 2016-04-28 15:15 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Post Pin Insulator | 0 | Checked & found, Duri Community ACB fdr #2 T/R 1x Ctr: 068-069 R/F: 51N. Patrolled the line & found, @1 broken Insulator of Bypass Sw o/p #2F-14. Cause: Post Insulator of Bypass SW. | 3198862 | 1 | 7:06 | Morning | Saturday | 2016 | 4
3051 | 2016-04-23 08:48 | 2016-04-23 08:48 | MINAS POWER PLANT |  |  | - | 08:48 Off line MGT #6, then S/D the Unit for S/B. |  | 1 | 8:48 | Morning | Saturday | 2016 | 4
3052 | 2016-04-23 11:37 | 2016-04-23 11:37 | 13.8KV PETANI FEEDER #1 | Fair | Animal | 166 | 11:37 It was reported b/o fuse for Tx at Well Peteni #09. 15:00 Checked & found, @1, @2 & @3 b/o 3.1SF fuses for 100Kva Tx at Well Petani #09. Replaced b/o fuses above with same size, then energized the Tx. Cause: Animal. (Mice) | 3198862 | 1 | 11:37 | Morning | Saturday | 2016 | 4
3053 | 2016-04-23 12:30 | 2016-04-23 12:30 | CENTRAL DURI POWER PLANT |  |  | - | CGT #5 Tripped. By Alarm: High Vibration. Cause: Under investigation. |  | 1 | 12:30 | Afternoon | Saturday | 2016 | 4
3054 | 2016-04-23 12:42 | 2016-04-23 12:42 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 255 | 12:42 6DN OCB fdr #6 T/SO. 6DN fdr #5 Load dropped 119A (130-11A). 6DN fdr #4 Load dropped 137A (210-73A). 14:00 Checked & found 6DN OCB fdr #6 T/SO. Crt: Can not be read. R/F: 51@1,@3. 14:48 Patrolled the line, but found nothing. 15:54 Blocked & closed 6DN OCB fdr #6, Ok. Then released the block. Cause: Suspected by Lightning. | 3198864 | 1 | 12:42 | Afternoon | Saturday | 2016 | 4
3055 | 2016-04-23 13:00 | 2016-04-23 13:00 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 35 | 8D OCB fdr #10 T/R 1x. Not checked yet. | 3198864 | 1 | 13:00 | Afternoon | Saturday | 2016 | 4
3056 | 2016-04-23 13:00 | 2016-04-29 15:30 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 35 | Checked & found, 8D OCB fdr #10 T/R 1x Ctr: 214-215 R/F: 50N. Patrolled the line & found, @1 broken FCO of Cap. Bank o/p #7E-94. Cause: Lightning. | 3198864 | 1 | 13:00 | Afternoon | Saturday | 2016 | 4
3057 | 2016-04-23 14:53 | 2016-04-23 14:53 | 13.8KV BATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Batang OCB fdr #1 T/R 2x. Not checked yet. | 3198862 | 1 | 14:53 | Afternoon | Saturday | 2016 | 4
3058 | 2016-04-23 14:53 | 2016-04-28 15:50 | 13.8KV BATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Batang OCB fdr #1 T/R 2x Ctr: 111-113 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 14:53 | Afternoon | Saturday | 2016 | 4
3059 | 2016-04-24 06:16 | 2016-04-24 06:16 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Lightning | 67 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3198862 | 1 | 6:16 | Morning | Sunday | 2016 | 4
3060 | 2016-04-24 06:16 | 2016-04-28 15:20 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Lightning | 67 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 201-202 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #29AM-28. Cause: Lightning. | 3198862 | 1 | 6:16 | Morning | Sunday | 2016 | 4
3061 | 2016-04-24 07:27 | 2016-04-24 07:27 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | C.Duri ACB fdr #7 T/R 1x Ctr: 461-462 R/F: 51N & 51@1. Not patrolled yet. | 3198862 | 1 | 7:27 | Morning | Sunday | 2016 | 4
3062 | 2016-04-24 07:27 | 2016-04-26 16:30 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 7:27 | Morning | Sunday | 2016 | 4
3063 | 2016-04-24 08:00 | 2016-04-24 08:00 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Transformer Failure | 33 | 08:00 It was reported b/o fuse for Tx o/p #08-M3-36. 11:00 Checked & found, @1, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #08-M3-36. Performed Megger, TTR test The Tx & found, Low Megger reading) Cause: Tx failure. (Low Megger treading) (The Tx is not replaced yet) | 3198862 | 1 | 8:00 | Morning | Sunday | 2016 | 4
3064 | 2016-04-24 08:00 | 2016-04-26 11:59 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Transformer Failure | 33 | Replaced 112.5Kva Tx with same size, then energized the Tx o/p #08-M3-36. Cause: Transformer failure. | 3198862 | 1 | 8:00 | Morning | Sunday | 2016 | 4
3065 | 2016-04-24 08:40 | 2016-04-24 08:40 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 279 | 08:40 It was reported no power at Benar fields (Seroja). 10:10 Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/SO. Blocked & closed the Recl. 25Z-07, Ok. Then released the Block The line is not patrolled yet. | 3198862 | 1 | 8:40 | Morning | Sunday | 2016 | 4
3066 | 2016-04-24 08:40 | 2016-04-29 16:40 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 279 | Checked & found, Bangko OCB fdr #4 T/R ix Ctr: 99988-99989 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 8:40 | Morning | Sunday | 2016 | 4
3067 | 2016-04-24 09:45 | 2016-04-24 09:45 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified (Fuse) | 11 | 09:45 It was reported b/o fuse for Tx o/p #11-J2-19B. 11:30 Checked & found, @1, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #11-J2-19B. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 9:45 | Morning | Sunday | 2016 | 4
3068 | 2016-04-24 11:17 | 2016-04-24 11:17 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Cloudy | Lightning | 19 | MSU-2 VCB fdr #1 (Pinang fdr #1) T/R 1x. Not checked yet. | 3198862 | 1 | 11:17 | Morning | Sunday | 2016 | 4
3069 | 2016-04-24 11:17 | 2016-04-28 08:58 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Cloudy | Lightning | 19 | MSU-2 VCB fdr #1 (Pinang fdr #1) T/R 1x 208-209 R/F: 51@1,@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 11:17 | Morning | Sunday | 2016 | 4
3070 | 2016-04-24 11:25 | 2016-04-24 11:25 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx at Bangko Test Sta-A. Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Bangko Test Sta-A. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 11:25 | Morning | Sunday | 2016 | 4
3071 | 2016-04-24 13:55 | 2016-04-24 13:55 | 13.8KV MENGGALA FEEDER #1 | Fair | Transformer Failure | 24 | 13:55 It was reported b/o fuse for Tx at Well Menggala North #40 16:00 Checked & found, @1,@3 b/o 7.8SF fuses for 300kva Tx at Well Menggala North #40. Performed TTR, Megger test the Tx & found, low megger reading. Cause: Tx failure. (Low megger reading) (The Tx is not replaced yet) | 3198862 | 1 | 13:55 | Afternoon | Sunday | 2016 | 4
3072 | 2016-04-24 13:55 | 2016-04-29 16:07 | 13.8KV MENGGALA FEEDER #1 | Fair | Transformer Failure | 24 | Replaced 300KVA Tx with the same size then energized the Tx. Cause: Transformer Failure. | 3198862 | 1 | 13:55 | Afternoon | Sunday | 2016 | 4
3073 | 2016-04-24 21:20 | 2016-04-24 21:20 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 21:20 It was reported b/o fuse for Tx o/p #NN. 23:10 Checked & found, @1 b/o 1.4SF fuse for 75Kva Tx o/p #NN. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 21:20 | Night | Sunday | 2016 | 4
3074 | 2016-04-24 22:20 | 2016-04-24 22:20 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified (Fuse) | 5 | 22:20 It was reported b/o fuse for Tx at Well So.Balam #343. 23:31 Checked & found, @2 b/o 3.5SF fuse for 150Kva Tx at Well So.Balam #343. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 22:20 | Night | Sunday | 2016 | 4
3075 | 2016-04-25 06:35 | 2016-04-25 06:35 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Post Pin Insulator | 0 | C.Duri ACB fdr #5 T/R 1x Ctr: 228-229 R/F: 51N. Patrolled the line & found, @1 broken Pin Post Insulator o/p #03-07-01A. Cause: Pin Post Insulator. | 3198862 | 1 | 6:35 | Morning | Monday | 2016 | 4
3076 | 2016-04-25 07:00 | 2016-04-25 07:00 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 07:00 It was reported b/o fuse for Tx o/p #10-K6-17. 10:15 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #10-K6-17. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 7:00 | Morning | Monday | 2016 | 4
3077 | 2016-04-25 10:53 | 2016-04-25 10:53 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 196 | 10:53 Batang fdr #3 load dropped 48A (48-0A). 11:29 Batang OCB fdr #3 T/R 1x. (Batang GFPC was in block position) Not checked yet. | 3198862 | 1 | 10:53 | Morning | Monday | 2016 | 4
3078 | 2016-04-25 10:53 | 2016-03-05 07:05 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 196 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 313-314 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 10:53 | Morning | Monday | 2016 | 4
3079 | 2016-04-25 12:11 | 2016-04-25 12:11 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 7 | 3D OCB fdr #8 T/R 1x. 3D GFPC-TX #2 did not operate. Not checked yet. | 3198864 | 1 | 12:11 | Afternoon | Monday | 2016 | 4
3080 | 2016-04-25 12:11 | 2016-04-30 08:30 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 7 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 187-188 R/F: 51N. Patrolled the line & found, @2 broken L/A o/p #2F-11C. Cause: Lightning. | 3198864 | 1 | 12:11 | Afternoon | Monday | 2016 | 4
3081 | 2016-04-25 12:13 | 2016-04-25 12:13 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 50 | 3D OCB fdr #4 T/R 1x. 3D fdr #4 load dropped 19A (148-129A). 3D GFPC-TX #1 did not operate. Not checked yet. | 3198864 | 1 | 12:13 | Afternoon | Monday | 2016 | 4
3082 | 2016-04-25 12:13 | 2016-04-29 15:55 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 50 | Checked & found, 3D OCB fdr #4 T/R 1x Ctr: 547-548 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 12:13 | Afternoon | Monday | 2016 | 4
3083 | 2016-04-25 19:18 | 2016-04-25 19:18 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 50 | 19:18 It was reported no power at Well Candi #2, #11, #12. (Batang fdr #3) 22:30 Checked & found, Recl. 36AL-13 (Batang fdr #3) T/O. Ctr: 118-119. 22:34 Blocked & closed Recl. 36AL-13, Ok. Then release the block. Not patrolled yet. | 3198862 | 1 | 19:18 | Night | Monday | 2016 | 4
3084 | 2016-04-25 19:18 | 2016-03-05 07:00 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 50 | Patrolled the line at downstream of Recl. 36AL-13, but found nothing. Cause: Unidentified. | 3198862 | 1 | 19:18 | Night | Monday | 2016 | 4
3085 | 2016-04-26 09:30 | 2016-04-26 09:30 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 0 | 09:30 It was reported b/o fuse for Tx o/p #06-S1-12A. (S.E Test Sta Area-6) 10:45 Checked & found, @2 b/o 14.0SF fuse for 500Kva Tx o/p #06-S1-12A. Performed TTR & Megger Test the Tx, found good reading. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Monkey) | 3198862 | 1 | 9:30 | Morning | Tuesday | 2016 | 4
3086 | 2016-04-26 10:18 | 2016-04-26 10:18 | 8 DELTA SUBSTATION | Fair | Planned Maintenance | 47 | Shutdown 115KV 8D Substation Power TX #3, to replace Interrupter of 115KV 8D C/S-TX #3. (after switching to transfer & shutdown some load) 10:18-12:48 Manually opened Recl. 9E-02. (8D fdr #11). 12:48-12:32 Manually Opened 8D OCB fdr #9. (S/D Some WIPs at GS-1) Cause: Planned Maintenance. | 123 | 1 | 10:18 | Morning | Tuesday | 2016 | 4
3087 | 2016-04-26 10:37 | 2016-04-26 10:37 | CENTRAL DURI POWER PLANT |  |  | - | 10:37 S/U CGT #5, then on line to Unit at 10:56. |  | 1 | 10:37 | Morning | Tuesday | 2016 | 4
3088 | 2016-04-26 17:28 | 2016-04-26 17:28 | 13.8KV LIBO FEEDER #2 | Fair | Unidentified | 5 | Libo OCB fdr #2 T/R 1x. Not checked yet. | 3198862 | 1 | 17:28 | Afternoon | Tuesday | 2016 | 4
3089 | 2016-04-26 17:28 | 2016-04-27 13:40 | 13.8KV LIBO FEEDER #2 | Fair | Unidentified | 5 | Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 417-418 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 17:28 | Afternoon | Tuesday | 2016 | 4
3090 | 2016-04-26 18:01 | 2016-04-26 18:01 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Planned Maintenance | - | 26-Apr-2016. 18:01 Manually Opened CKBS VCB fdr #6. It was requested by KB-GS operator, to S/D some wells at downstream of CKBS VCB fdr #6 (for anticipating spill, due to WIP problem & need to repairing it) 27-Apr-2016. 01:55 Closed CKBS VCB fdr #6. (After repairing the WIP) Cause: Planned Maintenance. | 123 | 1 | 18:01 | Afternoon | Tuesday | 2016 | 4
3091 | 2016-04-27 12:12 | 2016-04-27 12:12 | CENTRAL DURI POWER PLANT |  |  | - | 12:12 Offline CGT #5, then S/D the Unit for S/B. (Priot to troubleshooting Computer-S Problem) |  | 1 | 12:12 | Afternoon | Wednesday | 2016 | 4
3092 | 2016-04-27 17:50 | 2016-04-27 17:50 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 41 | Menggala fdr #1 load dropped 132A (195-63A). Menggala GFPC was in block position. Not checked yet. | 3198862 | 1 | 17:50 | Afternoon | Wednesday | 2016 | 4
3093 | 2016-04-27 17:50 | 2016-04-30 08:35 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 41 | Checked & found, Recl. 19AO-01 (Menggala fdr #1) T/R 1x 452-453. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 17:50 | Afternoon | Wednesday | 2016 | 4
3094 | 2016-04-28 07:56 | 2016-04-28 07:56 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | No.Duri VCB fdr #1 T/R 1x. Not checked yet. | 3198862 | 1 | 7:56 | Morning | Thursday | 2016 | 4
3095 | 2016-04-28 07:56 | 2016-01-05 15:45 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, No.Duri VCB fdr #1 T/R 1x Ctr: 272-273 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 7:56 | Morning | Thursday | 2016 | 4
3096 | 2016-04-28 12:00 | 2016-04-28 12:00 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 15 | 12:00 It was reported b/o fuse for Tx at Well So.Balam #350. 14:49 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well So.Balam #350. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal. (Squirrel) | 3198862 | 1 | 12:00 | Afternoon | Thursday | 2016 | 4
3097 | 2016-04-28 14:15 | 2016-04-28 14:15 | CENTRAL DURI POWER PLANT |  |  | - | 14:15 S/U CGT #5, then online the Unit at 15:40. |  | 1 | 14:15 | Afternoon | Thursday | 2016 | 4
3098 | 2016-04-28 15:18 | 2016-04-28 15:18 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 35 | 4B OCB fdr #1 T/R 1x. Not checked yet. | 3198864 | 1 | 15:18 | Afternoon | Thursday | 2016 | 4
3099 | 2016-04-28 15:18 | 2016-04-30 14:10 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 35 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 278-279 R/F: 51N. Patrolled the line & found, @3 broken Dead end Insulator o/p #3A-13. Cause: Lightning. | 3198864 | 1 | 15:18 | Afternoon | Thursday | 2016 | 4
3100 | 2016-04-28 15:30 | 2016-04-28 15:30 | 13.8KV 3D FEEDER #7 | Rain and Lightning | Lightning | 70 | 3D OCB fdr #7 T/R 1x. 3D fdr #8 load dropped 48A (269-221A). 3D GFPC-TX #2 T/R 1x. Not checked yet. | 3198864 | 1 | 15:30 | Afternoon | Thursday | 2016 | 4
3101 | 2016-04-28 15:30 | 2016-04-30 14:05 | 13.8KV 3D FEEDER #7 | Rain and Lightning | Lightning | 70 | Checked & found, 3D OCB fdr #7 T/R 1x Ctr: 206-207 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #2D-29. Cause: Lightning. | 3198864 | 1 | 15:30 | Afternoon | Thursday | 2016 | 4
3102 | 2016-04-28 15:33 | 2016-04-28 15:33 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | 5B fdr #1 Load dropped 83A (91-8A). Not checked yet. | 3198864 | 1 | 15:33 | Afternoon | Thursday | 2016 | 4
3103 | 2016-04-28 15:33 | 2016-04-30 14:15 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, 5B OCB fdr #1 T/R 1x Ctr: 206-207 R/F: 51N. Patrolled the line & found, @3 broken Dead end Insulator o/p #6B-5B #18. Cause: Lightning. | 3198864 | 1 | 15:33 | Afternoon | Thursday | 2016 | 4
3104 | 2016-04-28 15:41 | 2016-04-28 15:41 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 0 | 15:41 5B fdr #4 Load dropped 177A (246-69A). 17:29 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO. Ctr: 56-57. 17:33 Blocked & closed Recl. 4B-73, Ok. Then released the block. Not patrolled yet. | 3198864 | 1 | 15:41 | Afternoon | Thursday | 2016 | 4
3105 | 2016-04-28 15:41 | 2016-04-29 14:00 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 0 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 15:41 | Afternoon | Thursday | 2016 | 4
3106 | 2016-04-28 15:47 | 2016-04-28 15:47 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 39 | 15:47 It was reported b/o fuse for Tx o/p 04-03-23A. Not checked yet. | 3198862 | 1 | 15:47 | Afternoon | Thursday | 2016 | 4
3107 | 2016-04-28 15:47 | 2016-04-29 09:11 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 39 | 09:11 Checked & found, @3 b/o fuse for 112.5KVA Tx. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 15:47 | Afternoon | Thursday | 2016 | 4
3108 | 2016-04-28 15:48 | 2016-04-28 15:48 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 27 | 4D OCB fdr #2 T/R 1x. 4D fdr #3 Load dropped 56A (73-17A). Not checked yet. | 3198864 | 1 | 15:48 | Afternoon | Thursday | 2016 | 4
3109 | 2016-04-28 15:48 | 2016-04-29 16:05 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 27 | Checked & found, 4D OCB fdr #2 T/R 1x Ctr: 212-213 R/F: 51@1,@2. Patrolled the line, but found nothing. Also found, Recl. 4D-204 (4D fdr #2) T/R 1x Ctr: 16-17. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 15:48 | Afternoon | Thursday | 2016 | 4
3110 | 2016-04-28 15:56 | 2016-04-28 15:56 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 58 | 4D OCB fdr #3 T/R 1x. Not checked yet. | 3198864 | 1 | 15:56 | Afternoon | Thursday | 2016 | 4
3111 | 2016-04-28 15:56 | 2016-04-29 16:10 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 58 | Checked & found, 4D OCB fdr #3 T/R 1x Ctr: 356-367 R/F: 51@2,@3. Patrolled the line & found, @2 broken Pin Insulator o/p #4D-69. Cause: Lightning. | 3198864 | 1 | 15:56 | Afternoon | Thursday | 2016 | 4
3112 | 2016-04-28 15:57 | 2016-04-28 15:57 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 20 | 5B OCB fdr #1 T/R 1x. 5B fdr #2 Load dropped 200A (261-61A). Not checked yet. | 3198864 | 1 | 15:57 | Afternoon | Thursday | 2016 | 4
3113 | 2016-04-28 15:57 | 2016-02-05 08:15 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 20 | Checked & found, 5B OCB fdr #1 T/R 1x Ctr: 206-207 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #6D5B-18. Cause: Lightning. | 3198864 | 1 | 15:57 | Afternoon | Thursday | 2016 | 4
3114 | 2016-04-28 16:09 | 2016-04-28 16:09 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 0 | 6D OCB fdr #4 T/R 1x. Not checked yet. | 3198864 | 1 | 16:09 | Afternoon | Thursday | 2016 | 4
3115 | 2016-04-28 16:09 | 2016-04-29 15:55 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, 6D OCB fdr #4 T/R 1x Ctr: 537-538 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 16:09 | Afternoon | Thursday | 2016 | 4
3116 | 2016-04-28 16:19 | 2016-04-28 16:19 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 16 | 6D fdr #5 Load dropped 61A (227-166A). Not checked yet. | 3198864 | 1 | 16:19 | Afternoon | Thursday | 2016 | 4
3117 | 2016-04-28 16:19 | 2016-04-29 16:00 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 16 | Checked & found, Recl. 5D-10 (6D fdr #5) T/R 1x Ctr: 09-10. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198864 | 1 | 16:19 | Afternoon | Thursday | 2016 | 4
3118 | 2016-04-28 19:12 | 2016-04-28 19:12 | 13.8KV 4B FEEDER #1 | Fair | Others | - | 19:12 GS #6 requested to Open 4B fdr #1. (To anticipate Spill at Minas GS-6, due to failed to S/U Shipping Pump) 19:14 Opened OCB 4B fdr #2, then closed at 19:14. (Power to supply GS-6) 19:36 Closed 4B OCB fdr #1 (Power to supply NBS & IT at KBJ) Cause: Others. (No Prod. loss charged to PGT) |  | 1 | 19:12 | Night | Thursday | 2016 | 4
3119 | 2016-04-29 02:00 | 2016-04-29 02:00 | 13.8KV BEKASAP FEEDER #3 | Fair | Others | 41 | 02:00 It was reported b/o fuse for Tx at Well Bekasap #159. 12:06 Checked & found, @1, @2, @3 M/O fuses for 150Kva Tx by outsider. Then Energized the Tx. Cause: Other. (Vandalism) | 3198862 | 1 | 2:00 | Night | Friday | 2016 | 4
3120 | 2016-04-29 06:24 | 2016-04-29 06:24 | 13.8KV BEKASAP MAIN GFPC | Fair | Unidentified | 0 | Bekasap Main GFPC-TX #C T/R 1x. Ground fault alarm on Bekasap Main fdr #2. (No load dropped at any fdrs.) Not checked yet. | 3198862 | 1 | 6:24 | Morning | Friday | 2016 | 4
3121 | 2016-04-29 06:24 | 2016-01-05 17:25 | 13.8KV BEKASAP MAIN GFPC | Fair | Unidentified | 0 | Checked & found, Bekasap Main GFPC-TX #C T/R 1x Ctr: 342-343. Patrolled Bekasap fdr #2 line, but found nothing. Cause: Unidentified. | 3198862 | 1 | 6:24 | Morning | Friday | 2016 | 4
3122 | 2016-04-29 10:47 | 2016-04-29 10:47 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 10:47 It was reported b/o fuse for Tx o/p #13-F3-32. 14:46 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #13-F3-32. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3198862 | 1 | 10:47 | Morning | Friday | 2016 | 4
3123 | 2016-04-29 13:09 | 2016-04-29 13:09 | 13.8KV BATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Batang OCB fdr #1 T/R 6x. Batang fdr #3 Load dropped 42A (47-5A). Not checked yet. | 3198862 | 1 | 13:09 | Afternoon | Friday | 2016 | 4
3124 | 2016-04-29 13:09 | 2016-02-05 13:50 | 13.8KV BATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Batang OCB fdr #1 T/R 6x Ctr: 113-119 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3198862 | 1 | 13:09 | Afternoon | Friday | 2016 | 4
3125 | 2016-04-29 21:24 | 2016-04-29 21:24 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Cloudy | Lightning | 0 | MSU-2 VCB fdr #1 (Pinang fdr #1) T/R 1x. Not checked yet. | 3198862 | 1 | 21:24 | Night | Friday | 2016 | 4
3126 | 2016-04-29 21:24 | 2016-01-05 08:20 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Cloudy | Lightning | 0 | Checked & found, MSU-2 VCB fdr #1 (Pinang fdr #1) T/R 1x Ctr: 209-210 R/F: 51N. Patrolled the line & found, @1,@3 broken Pin Insulators on TP of Well Pinang #10. Cause: Lightning. | 3198862 | 1 | 21:24 | Night | Friday | 2016 | 4
3127 | 2016-04-30 07:04 | 2016-04-30 07:04 | 13.8KV 4D FEEDER #5 | Fair | Pin Insulator | 0 | 4D OCB fdr #5 T/R 1x. Not checked yet. | 3198862 | 1 | 7:04 | Morning | Saturday | 2016 | 4
3128 | 2016-04-30 07:04 | 2016-03-05 16:39 | 13.8KV 4D FEEDER #5 | Fair | Pin Insulator | 0 | Checked & found 4D OCB fdr #5 T/R 1x Ctr: 259-260 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator o/p #NN. (Near Well #4D-19) Cause: Pin Insulator. | 3198862 | 1 | 7:04 | Morning | Saturday | 2016 | 4
3129 | 2016-04-30 13:51 | 2016-04-30 13:51 | 13.8KV PEMATANG FEEDER #1 | Fair | Lightning Arrester | 21 | Pematang OCB fdr #1 T/R 1x. Pematang fdr #2 load dropped 47A (57-10A). Not checked yet. | 3198862 | 1 | 13:51 | Afternoon | Saturday | 2016 | 4
3130 | 2016-04-30 13:51 | 2016-01-05 16:50 | 13.8KV PEMATANG FEEDER #1 | Fair | Lightning Arrester | 21 | Checked & found, Pematang OCB fdr #1 T/R 1x Ctr: 128-129 R/F: 51N. Patrolled the line & found, @2 broken L/A on TP of Well Pematang #67. Cause: Lightning Arrester. | 3198862 | 1 | 13:51 | Afternoon | Saturday | 2016 | 4
3131 | 2016-04-30 16:34 | 2016-04-30 16:34 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Recloser - Control Recloser | 109 | 16:34 So.Balam fdr #4 Load dropped 22A (156-134A). So.Balam fdr #3 Load dropped 66A (135-69A). T/O WIP. So.Balam fdr #2 Load dropped 28A (31-3A). T/O WIP. So.Balam GFPC T/R 1x. 21:30 It was reported no power at Well S.E Balam #02,16,19 and 23. 22:20 Checked & found, Recl. 19AA-07 (So.Balam fdr #4) T/SO. Ctr: 140-141. 22:30 Blocked & closed Recl. 19AA-07, but failed. Patrol the line & found, a Kite hang on TP of Well S.E Balam #03, then removed it. 00:59 Manually opened So.Balam VCB fdr #4. Closed Bypass Switch of Recl. 19AA-07. 01:08 Blocked & closed So.Balam VCB fdr #4, but found spark on @1 source side of HLC jumper. (Bypass Switch jumper of Recl. 19AA-07) 01:19 Manually opened So.Balam VCB fdr #4, to tighten all HLC of Bypass jumpers. 01:30 Blocked & closed So.Balam VCB fdr #4, Ok. Then release the block. Cause: Recloser control. | 3198862 | 1 | 16:34 | Afternoon | Saturday | 2016 | 4
3132 | 2016-04-30 22:59 | 2016-04-30 22:59 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Transformer Failure | 1 | It was reported b/o fuse for Tx o/p #01-01-06. Not checked yet. | 3198862 | 1 | 22:59 | Night | Saturday | 2016 | 4
3133 | 2016-04-30 22:59 | 2016-05-05 08:58 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Transformer Failure | 1 | Checked & found, b/o fuses for 112.5Kva Tx o/p #01-6-01. Tested the Tx & found, Low megger reading. Cause: Tx Failure. (Low megger reading) 08:58-10:15 Replaced 112.5Kva Tx failure with the same size & Energized the Tx o/p #01-6-01. Cause: Transformer Failure. | 3198862 | 1 | 22:59 | Night | Saturday | 2016 | 4
3134 | 2016-01-05 00:44 | 2016-01-05 00:44 | 13.8KV BATANG FEEDER #3 | Fair | Transformer Failure | 137 | 00:44 It was reported b/o fuse for Tx at Well Pemburu #16. 03:00 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Pemburu #16. Perfored TTR, Megger test the Tx & found, Unbalance TTR & Low megger reading. 15:34 Replaced Tx failure with the same size & energized the Tx at Well Pemburu #16. Cause: Transformer failure. | 3211045 | 1 | 0:44 | Night | Tuesday | 2016 | 1
3135 | 2016-01-05 00:56 | 2016-01-05 00:56 | 13.8KV KOTABATAK FEEDER #2 | Rain | Lightning | 0 | 00:44 OKB fdr #2 Load dropped 170A (242-72A). 03:40 Checked & found, Recl. 38CW-08 (OKB fdr #2) T/SO. Ctr: 28-29. 03:45 Blocked & closed Recl. 38CW-08, Ok. Then released the block. 17:12 Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211046 | 1 | 0:56 | Night | Tuesday | 2016 | 1
3136 | 2016-01-05 07:47 | 2016-01-05 07:47 | 13.8KV CENTRAL DURI FEEDER #12 | Fair | Unidentified | 0 | C.Duri ACB fdr #12 T/R 1x Ctr: 480-481 R/F: 51N. Not patrolled yet. | 3211045 | 1 | 7:47 | Morning | Tuesday | 2016 | 1
3137 | 2016-01-05 07:47 | 2016-03-05 07:10 | 13.8KV CENTRAL DURI FEEDER #12 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3211045 | 1 | 7:47 | Morning | Tuesday | 2016 | 1
3138 | 2016-01-05 14:10 | 2016-01-05 14:10 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy and Lightning | Lightning | 36 | So.Bekasap OCB fdr #1 T/R 1x. Not checked yet. | 3211045 | 1 | 14:10 | Afternoon | Tuesday | 2016 | 1
3139 | 2016-01-05 14:10 | 2016-02-05 18:00 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy and Lightning | Lightning | 36 | Checked & found, So.Bekasap OCB fdr #1 T/R 1x Ctr: 343-344 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 14:10 | Afternoon | Tuesday | 2016 | 1
3140 | 2016-01-05 14:49 | 2016-01-05 14:49 | 13.8KV RANGAU FEEDER #1 | Rain and Lightning | Lightning | 9 | Rangau OCB fdr #1 T/R 1x. Rangau fdr #2 load dropped 22A (84-62A). Not checked yet. | 3211045 | 1 | 14:49 | Afternoon | Tuesday | 2016 | 1
3141 | 2016-01-05 14:49 | 2016-03-05 17:50 | 13.8KV RANGAU FEEDER #1 | Rain and Lightning | Lightning | 9 | Checked & found, Rangau OCB fdr #1 T/R 1x Ctr: 008-009 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 14:49 | Afternoon | Tuesday | 2016 | 1
3142 | 2016-01-05 15:21 | 2016-01-05 15:21 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 26 | 3D fdr #4 load dropped 150A (221-71A). 3D GFPC-TX #1 T/R 1x. (Ground fault alarm on 3D fdr #4) Not checked yet. | 3211046 | 1 | 15:21 | Afternoon | Tuesday | 2016 | 1
3143 | 2016-01-05 15:21 | 2016-03-05 17:32 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 26 | Checked & found, Recl. 2D-204 (3D fdr #4) T/R 1x Ctr: 35-36. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3211046 | 1 | 15:21 | Afternoon | Tuesday | 2016 | 1
3144 | 2016-01-05 15:37 | 2016-01-05 15:37 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 146 | 3D OCB fdr #8 T/LO. Ctr: 91-95 R/F: 50@1. 20:30 Patrolled the line & found, @1,@2,@3 broken Dead end Insulators o/p #3E-03. 20:40 Open LBS #3E-64, to isolate broken Dead end Insulator above. 20:45 Blocked & closed 3D fdr #8, Ok. Then released the block. Cause: Lightning. | 3211046 | 1 | 15:37 | Afternoon | Tuesday | 2016 | 1
3145 | 2016-01-05 15:37 | 2016-02-05 13:14 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 146 | Replaced @1,@2,@3 broken Pin insulators o/p #3E-03. Opened L/A Jumpers, to dismantling the L/A o/p #3E-07. Closed LBS #3E-64. (3D fdr #8 Back to normal) | 3211046 | 1 | 15:37 | Afternoon | Tuesday | 2016 | 1
3146 | 2016-01-05 16:01 | 2016-01-05 16:01 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 37 | 16:01 6D OCB fdr #1 T/R 1x. 16:17 6D OCB fdr #1 T/R 1x. Not checked yet. | 3211046 | 1 | 16:01 | Afternoon | Tuesday | 2016 | 1
3147 | 2016-01-05 16:01 | 2016-03-05 17:18 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 37 | Checked & found, 6D OCB fdr #1 T/R 2x Ctr: 303-305 R/F: 51N. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3211046 | 1 | 16:01 | Afternoon | Tuesday | 2016 | 1
3148 | 2016-01-05 16:08 | 2016-01-05 16:08 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Powerline - Conductor | 160 | 16:08 Minas ACB fdr #3 T/LO. Ctr: 56-58 R/F: 50@2,@3. Patrolled the line & found, @2,@3 conductors twisted. (at beside switch yard) 19:04 Blocked & closed Minas ACB fdr #3, Ok. Then released the block. (After releasing the Twisted conductors above) Cause: Conductor. | 3211046 | 1 | 16:08 | Afternoon | Tuesday | 2016 | 1
3149 | 2016-01-05 16:10 | 2016-01-05 16:10 | 13.8KV MINAS FEEDER #5 | Rain and Lightning | Lightning | 0 | Minas ACB fdr #5 T/R 1x Ctr: 77-78 R/F: 50N. Not checked yet. | 3211046 | 1 | 16:10 | Afternoon | Tuesday | 2016 | 1
3150 | 2016-01-05 16:10 | 2016-02-05 16:00 | 13.8KV MINAS FEEDER #5 | Rain and Lightning | Lightning | 0 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211046 | 1 | 16:10 | Afternoon | Tuesday | 2016 | 1
3151 | 2016-01-05 16:10 | 2016-01-05 16:10 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Powerline - Conductor | 126 | 16:10 Minas ACB fdr #2 T/LO. Ctr: 884-886 R/F: 51N. Found, @1,@2 conductors twisted at beside of Switch Yard. 18:58 Blocked & closed Minas ACB fdr #2, Ok. Then released the block. (After releasing the Twisted conductors above) Cause: Conductor. | 3211046 | 1 | 16:10 | Afternoon | Tuesday | 2016 | 1
3152 | 2016-01-05 16:12 | 2016-01-05 16:12 | MINAS POWER PLANT |  |  | - | 16:12 MGT #4 Tripped. By alarm: Emergency Trip. Cause: Under investigation. |  | 1 | 16:12 | Afternoon | Tuesday | 2016 | 1
3153 | 2016-01-05 16:17 | 2016-01-05 16:17 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 57 | 8D OCB fdr #10 T/R 1x. 8D fdr #11 load dropped 60A (233-173A). Not checked yet. | 3211046 | 1 | 16:17 | Afternoon | Tuesday | 2016 | 1
3154 | 2016-01-05 16:17 | 2016-02-05 17:20 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 57 | Checked & found, 8D OCB fdr #10 T/R 1x Ctr: 216-217 R/F: 50@2,@3. Patrolled the line & found: -@2 Broken Dead end Insulator o/p #MB-10 -@3 Flashed over Dead end Insulator o/p #7E-103. Cause: Lightning. | 3211046 | 1 | 16:17 | Afternoon | Tuesday | 2016 | 1
3155 | 2016-02-05 06:32 | 2016-02-05 06:32 | 13.8KV PETANI FEEDER #1 | Fair | Lightning Arrester | 79 | Petani OCB fdr #1 T/R 1x. Petani fdr #2 Load dropped 8A (36-28A). 18:30 Checked & found, Petani OCB fdr #1 T/R 1x Ctr: 23-24 R/F: 51N. Patrolled the line & found, @3 broken L/A on TP of Well Petani #25. Cause: Lightning Arrester. | 3211045 | 1 | 6:32 | Morning | Friday | 2016 | 2
3156 | 2016-02-05 07:20 | 2016-02-05 07:20 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | 07:20 It was reported b/o fuse for Tx at SMGG building. (Duro Community fdr #3) 09:10 Checked & found, @1 b/o 1.0SF fuse for 50Kva Tx at SMGG building. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Squirrel) | 3211045 | 1 | 7:20 | Morning | Friday | 2016 | 2
3157 | 2016-02-05 08:40 | 2016-02-05 08:40 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | 08:40 It was reported no power at Talang #50 & Talang#45 housing. (DC fdr #3) 09:45 Checked & found, @1 b/o 1.0SF fuse for 50Kva Tx o/p #NN. (at Talang #45 & #50) Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Squirrel) | 3211045 | 1 | 8:40 | Morning | Friday | 2016 | 2
3158 | 2016-02-05 14:09 | 2016-02-05 14:09 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Equipment Failure | 279 | 14:09 Nella OCB fdr #2 T/R 1x. 14:16 Nella OCB fdr #2 T/LO. 15:27 Checked & found, Nella VCB fdr #2 T/SO. Ctr: 209-211 R/F: 51@1,@2. Patrolled the line, but found nothing. 17:00 Blocked & closed Nella VCB fdr #2, but failed. Checked VCB Nella fdr #2 & found, the VCB Spring discharge. 17:17 Blocked & closed Nella VCB fdr#2, Ok. Then release the block. (After manual charge the Spring of Nella VCB fdr #2) Cause: Equipment Failure. (Motor spring charge problem) | 3211045 | 1 | 14:09 | Afternoon | Friday | 2016 | 2
3159 | 2016-02-05 14:16 | 2016-02-05 14:16 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 71 | 14:09 Nella fdr #1 Load dropped 86A (238-152A). 14:16 Nella OCB fdr #1 T/R 1x. Nella GFPC in block position. Not checked yet. | 3211045 | 1 | 14:16 | Afternoon | Friday | 2016 | 2
3160 | 2016-02-05 14:16 | 2016-03-05 08:45 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 71 | Checked & found, Nella VCB fdr #1 T/R 1x Ctr: 275-276 R/F: 51@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 14:16 | Afternoon | Friday | 2016 | 2
3161 | 2016-02-05 14:35 | 2016-02-05 14:35 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Powerline - Conductor | 489 | 14:35 So.Balam VCB fdr #4 T/LO. Ctr: 287. R/F: 51@1,@2,@#3. So.Balam fdr #1 load dropped 70A (95-25A). So.Balam GFPC T/R 1x. 15:00 Patrolled the line & found, @2,@3 broken conductors o/p #19AA-07. Opened Bypass Switch o/p #BN-202. (ex Recloser), to isolate the broken conductors. (and to repairing is broken conductor) 17:43 Blocked & closed So.Balam fdr #4, then release the block. (to energize & S/U some wells part load of So.Balam fdr #4) 21:33 Manually open So.Balam VCB fdr #4 and close Bypass Switch o/p #BN-202. 21:40 Blocked & closed So.Balam fdr #4, Ok. Then released the block. Cause: Conductor. | 3211045 | 1 | 14:35 | Afternoon | Friday | 2016 | 2
3162 | 2016-02-05 16:56 | 2016-02-05 16:56 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 16:56 C.Duri fdr #1 Load dropped 55A (239-184A). 17:40 Checked & found, Recl. 39AS-09 (C.Duri fdr #1) T/SO. Ctr: 230-231. 17:43 Blocked & closed Recl. 39AS-09, Ok. Then release the block. The line is not patrolled yet. | 3211045 | 1 | 16:56 | Afternoon | Friday | 2016 | 2
3163 | 2016-02-05 16:56 | 2016-07-05 08:56 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. | 3211045 | 1 | 16:56 | Afternoon | Friday | 2016 | 2
3164 | 2016-02-05 18:16 | 2016-02-05 18:16 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Planned Maintenance | 0 | 18:00 It was reported there was sparked o/p #06-JY-01. Checked & found, Sparked at HLC jumper o/p #06-JY-01. 18:16 Blocked C.Duri ACB fdr #14. 18:30 Manally Opened Recl. 06-JY-02. (Load junk yard / CMTF) To repairing the HLC connection jumper o/p #06-JY-01. 18:38 Closed Recl. 06-JY-02, then release block of C.Duri fdr #14. Cause: Plant Maintenance. (Lost Connection HLC jumper) | 123 | 1 | 18:16 | Afternoon | Friday | 2016 | 2
3165 | 2016-03-05 09:49 | 2016-03-05 09:49 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Planned Maintenance | 0 | 09:49-10:52 Manually S/D 112.5Kva Tx, then open HLC o/p #01-01-14. (C.Duri fdr #6) To replacing @1,@2,@3 broken L/As o/p #.... (Oil well involved :4S-19A,19B,29A and 4S-29B) Cause: Planned Maintenance. | 123 | 1 | 9:49 | Morning | Saturday | 2016 | 3
3166 | 2016-03-05 10:00 | 2016-03-05 10:00 | 13.8KV PINANG FEEDER #1 | Fair | Animal | 15 | 10:00 It was reported b/o fuse for Tx at Well Pinang #27. 11:15 Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well Pinang #27. Performed TTR, Megger tested the Tx found, normal. (good reading) Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal. (Monkey) | 3211045 | 1 | 10:00 | Morning | Saturday | 2016 | 3
3167 | 2016-03-05 11:05 | 2016-03-05 11:05 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Planned Maintenance | 0 | 11:05-11:55 Manually S/D 112.5Kva Tx, then open HLC o/p #6Q-05-11. (C.Duri fdr #15) To replacing @1,@2,@3 broken L/As o/p above. (Oil well involved :7Q-50B,6Q-59A,6Q-69A) Cause: Planned Maintenance. | 123 | 1 | 11:05 | Morning | Saturday | 2016 | 3
3168 | 2016-03-05 11:15 | 2016-03-05 11:15 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified | 160 | 11:15 Nella OCB fdr #1 T/SO. 11:22 Blocked & closed Nella OCB fdr #1, Ok. Then released the block. Not checked & patrolled yet. | 3211045 | 1 | 11:15 | Morning | Saturday | 2016 | 3
3169 | 2016-03-05 11:15 | 2016-04-05 07:15 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified | 160 | Checked & found, Nella VCB fdr #1 T/SO. Ctr: 476-477 R/F: 50N. Patrolled the line, but found nothing. Cause: Unidentified. | 3211045 | 1 | 11:15 | Morning | Saturday | 2016 | 3
3170 | 2016-03-05 14:17 | 2016-03-05 14:17 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning Arrester | 100 | Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #1 load dropped 15A (119-104A). Not checked yet. | 3211045 | 1 | 14:17 | Afternoon | Saturday | 2016 | 3
3171 | 2016-03-05 14:17 | 2016-07-05 08:17 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning Arrester | 100 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 00-01 R/F: 51N. Patrolled the line & found, @1 broken L/A o/p #26AL-20 & o/p #31N-06. Cause: Lightning Arrester. | 3211045 | 1 | 14:17 | Afternoon | Saturday | 2016 | 3
3172 | 2016-03-05 14:35 | 2016-03-05 14:35 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Planned Maintenance | 0 | 14:35-15:10 Manually S/D 112.5Kva Tx, then open HLC o/p #05-P3-09. To replacing @1,@2,@3 broken L/As o/p above. (Oil well involved: P7-35A,P7-35C and P&-36A) Cause: Planned Maintenance. | 123 | 1 | 14:35 | Afternoon | Saturday | 2016 | 3
3173 | 2016-03-05 16:29 | 2016-03-05 16:29 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Lightning | 32 | Pematang OCB fdr #2 T/R 1x. Not checked yet. | 3211045 | 1 | 16:29 | Afternoon | Saturday | 2016 | 3
3174 | 2016-03-05 16:29 | 2016-04-05 13:45 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Lightning | 32 | Checked & found, Pematang OCB fdr #2 T/R 1x Ctr: 00-01 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator o/p #34BC-80. Cause: Lightning. | 3211045 | 1 | 16:29 | Afternoon | Saturday | 2016 | 3
3175 | 2016-03-05 16:29 | 2016-03-05 16:29 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning Arrester | 35 | Pematang OCB fdr #1 T/R 1x. Not checked yet. | 3211045 | 1 | 16:29 | Afternoon | Saturday | 2016 | 3
3176 | 2016-03-05 16:29 | 2016-07-05 07:29 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning Arrester | 35 | Checked & found Pematang VCB fdr#1 T/R 1x Ctr:129-130 R/F:None. Patrolled the line & Found @2 Broken LA on T/P Pematang#67. Cause : Lightning Arrester | 3211045 | 1 | 16:29 | Afternoon | Saturday | 2016 | 3
3177 | 2016-03-05 16:29 | 2016-03-05 16:29 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 28 | Rangau fdr #2 Load dropped 32A (82-50A). Checked & found nothing, the Recloser was not working. Patrolled the Line, also found nothing. Cause : Unidentified. | 3211045 | 1 | 16:29 | Afternoon | Saturday | 2016 | 3
3178 | 2016-03-05 16:29 | 2016-05-05 15:30 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 28 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: Did not change. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 16:29 | Afternoon | Saturday | 2016 | 3
3179 | 2016-03-05 16:32 | 2016-03-05 16:32 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 67 | Bekasap OCB fdr #2 T/R 1x. Not checked yet. | 3211045 | 1 | 16:32 | Afternoon | Saturday | 2016 | 3
3180 | 2016-03-05 16:32 | 2016-05-05 21:00 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 67 | Checked & found, Bekasap Main OCB fdr #2 T/R 1x Ctr: 872-873 R/F: 51@1. Patrolled the line & found, @1 F/O Dead end Insulator o/p #37BD-13. Cause: Lightning. | 3211045 | 1 | 16:32 | Afternoon | Saturday | 2016 | 3
3181 | 2016-03-05 16:45 | 2016-03-05 16:45 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 42 | So.Bekasap fdr #1 Load dropped 94A (157-63A). Not checked yet. | 3211045 | 1 | 16:45 | Afternoon | Saturday | 2016 | 3
3182 | 2016-03-05 16:45 | 2016-05-05 13:40 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 42 | Checked & found, Recl. 34BI-18 (So.Bekasap fdr #1) T/R 1x Ctr: 151-152. Patrolled the line & found, @1 broken Pin Insulator o/p #31BD-21. Cause: Lightning. | 3211045 | 1 | 16:45 | Afternoon | Saturday | 2016 | 3
3183 | 2016-03-05 17:16 | 2016-03-05 17:16 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 23 | 3D OCB fdr #8 T/R 1x. Not checked yet. | 3211046 | 1 | 17:16 | Afternoon | Saturday | 2016 | 3
3184 | 2016-03-05 17:16 | 2016-09-05 06:15 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 23 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 195-196 R/F: 51@1. Patrolled the line & found, @1 broken Dead end Insulator o/p #3E-58. Cause: Lightning. | 3211046 | 1 | 17:16 | Afternoon | Saturday | 2016 | 3
3185 | 2016-04-05 05:03 | 2016-04-05 05:03 | 13.8KV 8D FEEDER #1 | Fair | Planned Maintenance | 0 | 05:39 Manual open 8D OCB fdr #1. (as per GS-1 requested) (High level Tank due to two (2) WIPs failed to start up) 10:24 Blocked & closed 8D OCB fdr#1, then release the block. Cause: Planned maintenance. (No Prod. loss charge to PGT) | 3211046 | 1 | 5:03 | Morning | Tuesday | 2016 | 4
3186 | 2016-04-05 15:30 | 2016-04-05 15:30 | 13.8KV 6D FEEDER #2 | Fair | Animal | 0 | 15:30 It was reported b/o fuse for Tx at Well #7C-27. (6D fdr #2) 17:00 Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well #7C-27. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Squirrel) | 3211046 | 1 | 15:30 | Afternoon | Tuesday | 2016 | 4
3187 | 2016-04-05 15:35 | 2016-04-05 15:35 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Rain and Lightning | Lightning | 42 | MSU-2 VCB fdr #1 (Pinang fdr #1) T/R 1x. Not checked yet. | 3211045 | 1 | 15:35 | Afternoon | Tuesday | 2016 | 4
3188 | 2016-04-05 15:35 | 2016-12-05 09:45 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Rain and Lightning | Lightning | 42 | Checked & found, MSU-2 VCB fdr #1 (Pinang fdr #1) T/R 1x Ctr: 211-212 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 15:35 | Afternoon | Tuesday | 2016 | 4
3189 | 2016-05-05 06:40 | 2016-05-05 06:40 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Pin Insulator | 0 | Duri Community ACB fdr #2 T/R 1x Ctr: 69-70 R/F: 51N. Patrolled the line & found, @3 F/O Pin Insulator o/p #SLI-1B-06. Cause: Pin Insulator. | 3211045 | 1 | 6:40 | Morning | Thursday | 2016 | 5
3190 | 2016-05-05 12:18 | 2016-05-05 12:18 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Lightning | 0 | 12:18 44KV No.DURI GCB #44 (Line to Dumai) T/R 1x. 13:12 44KV No.DURI GCB #44 (Line to Dumai) T/R 1x again. Not checked yet. | 3211045 | 1 | 12:18 | Afternoon | Thursday | 2016 | 5
3191 | 2016-05-05 12:18 | 2016-07-05 08:18 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Lightning | 0 | Checked & found, 44KV No.Duri GCB #44 (Line to Dumai) T/R 2x Ctr: 104-106 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 12:18 | Afternoon | Thursday | 2016 | 5
3192 | 2016-05-05 13:37 | 2016-05-05 13:37 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 87 | Bangko VCB fdr#4 T/R 1x. Bangko fdr #1 Load dropped 116A (200-84A). Not checked yet. | 3211045 | 1 | 13:37 | Afternoon | Thursday | 2016 | 5
3193 | 2016-05-05 13:37 | 2016-08-05 08:37 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 87 | Checked & found, Bangko VCB fdr #4 T/R 1x Ctr: 992-993 R/F: 50N. Patrolled the line & found, @1 broken L/A on TP of Well Bangko #179. Cause: Lightning. | 3211045 | 1 | 13:37 | Afternoon | Thursday | 2016 | 5
3194 | 2016-05-05 13:59 | 2016-05-05 13:59 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 37 | Nella VCB fdr #2 T/R 1x. Not checked yet. | 3211045 | 1 | 13:59 | Afternoon | Thursday | 2016 | 5
3195 | 2016-05-05 13:59 | 2016-07-05 08:59 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 37 | Checked & found, Nella VCB fdr #2 T/R 1x Ctr: 216-217 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 13:59 | Afternoon | Thursday | 2016 | 5
3196 | 2016-05-05 14:03 | 2016-05-05 14:03 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Rain and Lightning | Lightning | 45 | 14:03 MSU-2 VCB fdr #1 (Pinang fdr #1) T/R 1x. 14:14 MSU-2 VCB fdr #1 (Pinang fdr #1) T/R 1x again. Not checked yet. | 3211045 | 1 | 14:03 | Afternoon | Thursday | 2016 | 5
3197 | 2016-05-05 14:03 | 2016-12-05 09:45 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Rain and Lightning | Lightning | 45 | Checked & found, MSU-2 VCB fdr #1 (Pinang fdr #1) T/R 1x Ctr: 212-214 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator o/p #11D-36. Cause: Lightning. | 3211045 | 1 | 14:03 | Afternoon | Thursday | 2016 | 5
3198 | 2016-05-05 14:33 | 2016-05-05 14:33 | 13.8KV RANGAU FEEDER #2 | Fair | Transformer Failure | 40 | 14:33 It was reported b/o fuse for Tx at Well Jurong #13. (Rangau fdr #2) 16:00 Checked & found, @1,@3 b/o 3.5SF fuses for 150Kva Tx at Well Jurong #13. Test TTR & Megger 150Kva Tx found, Unbalance TTR. Cause: Tx failure. (The Tx is not replaced yet) | 3211045 | 1 | 14:33 | Afternoon | Thursday | 2016 | 5
3199 | 2016-05-05 14:33 | 2016-06-05 15:45 | 13.8KV RANGAU FEEDER #2 | Fair | Transformer Failure | 40 | Replaced 150Kva Tx failure with the same size & Energized the Tx. Cause Tx Failure. | 3211045 | 1 | 14:33 | Afternoon | Thursday | 2016 | 5
3200 | 2016-05-05 14:53 | 2016-05-05 14:53 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 30 | 6D OCB fdr #5 T/R 1x. Not checked yet. | 3211046 | 1 | 14:53 | Afternoon | Thursday | 2016 | 5
3201 | 2016-05-05 14:53 | 2016-10-05 16:40 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 30 | Checked & found, 6D OCB fdr #5 T/R 2x Ctr: 727-729 R/F: 51N. Patrolled the line & found, @1 broken Pin Insulator o/p #6D-504. Cause: Lightning. | 3211046 | 1 | 14:53 | Afternoon | Thursday | 2016 | 5
3202 | 2016-05-05 15:29 | 2016-05-05 15:29 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 21 | 15:29 6D OCB fdr #1 T/R 1x. 15:48 6D OCB fdr #1 T/R 1x again. Not checked yet. | 3211046 | 1 | 15:29 | Afternoon | Thursday | 2016 | 5
3203 | 2016-05-05 15:29 | 2016-10-05 16:50 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 21 | Checked & found, 6D OCB fdr #1 T/R 2x Ctr: 305-307 R/F: 51N. Patrolled the line & found: -@3 Broken Dead end Insulator o/p #5B-69. -@2 Broken Dead end Insulator o/p #5B-57. Cause: Lightning. | 3211046 | 1 | 15:29 | Afternoon | Thursday | 2016 | 5
3204 | 2016-05-05 15:29 | 2016-05-05 15:29 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 51 | 6D OCB fdr #2 T/R 1x. Not checked yet. | 3211046 | 1 | 15:29 | Afternoon | Thursday | 2016 | 5
3205 | 2016-05-05 15:29 | 2016-10-05 16:55 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 51 | Checked & found, 6D OCB fdr #2 T/R 1x Ctr: 235-236 R/F: 50N. Patrolled the line & found, @2 broken Pin Insulator o/p #6D-78A. Cause: Lightning. | 3211046 | 1 | 15:29 | Afternoon | Thursday | 2016 | 5
3206 | 2016-05-05 15:31 | 2016-05-05 15:31 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 123 | 15:31 6DN OCB fdr #6 T/O. 16:23 Checked & found, 6DN OCB fdr #6 T/O. Blocked & closed 6DN OCB fdr #6, Ok. Then release the block. Not checked & Patrolled yet. | 3211046 | 1 | 15:31 | Afternoon | Thursday | 2016 | 5
3207 | 2016-05-05 15:31 | 2016-08-05 08:31 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 123 | Checked & found, 6DN OCB fdr #6 T/SO. Ctr: 327-328 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211046 | 1 | 15:31 | Afternoon | Thursday | 2016 | 5
3208 | 2016-05-05 15:33 | 2016-05-05 15:33 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 412 | 15:33 3D OCB fdr #8 T/LO. 3D fdr #7 load dropped 212A (229-17A). 16:47 Checked & found, 3D OCB fdr #8 T/LO. Ctr: 196-201 R/F: 51@1,@2,@3. 3D GFPC Tx-2 T/R 4x Ctr: 620-624. Patrolled the line & found, seriously broken Dead end Insulators o/p #3E-03 & 3E-04. 18:00 Then Opened LBS #3E-64. (To isolate the broken Dead end Insulators above) 18:03 Blocked & closed 3D OCB fdr #8, Ok. Then release the block. (The LBS #3E-64 is still in open position & some wells were off) Cause: Lightning. | 3211046 | 1 | 15:33 | Afternoon | Thursday | 2016 | 5
3209 | 2016-05-05 15:33 | 2016-06-05 16:30 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 412 | Replaced, @1,@2 broken Dead End Insulators o/p #3E-03 & #3E-04. Manually clesed LBS #3E-64. Cause: Lightning. Prod. loss: 362Bbls / 13 wells. | 3211046 | 1 | 15:33 | Afternoon | Thursday | 2016 | 5
3210 | 2016-05-05 15:40 | 2016-05-05 15:40 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 22 | 4D OCB fdr #4 T/R 1x. 4D fdr #5 Load dropped 91A (103-12A). Not checked yet. | 3211046 | 1 | 15:40 | Afternoon | Thursday | 2016 | 5
3211 | 2016-05-05 15:40 | 2016-10-05 16:35 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 22 | Checked & found, 4D OCB fdr #4 T/R 1x Ctr: 257-258 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator o/p #36DN-38. Cause: Lightning. | 3211046 | 1 | 15:40 | Afternoon | Thursday | 2016 | 5
3212 | 2016-05-05 15:40 | 2016-05-05 15:40 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 0 | Menggala fdr #1 Load dropped 53A (191-148A). Not checked yet. | 3211046 | 1 | 15:40 | Afternoon | Thursday | 2016 | 5
3213 | 2016-05-05 15:40 | 2016-07-05 17:40 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 19AN-04 (Menggala fdr #1) T/R 1x Ctr: 320-321. Patrolled the line & found, @3 broken Pin Insulator o/p #19AK-11. Cause: Lightning. | 3211046 | 1 | 15:40 | Afternoon | Thursday | 2016 | 5
3214 | 2016-05-05 15:45 | 2016-05-05 15:45 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 42 | 3D fdr #3 Load dropped 143A (154-11A). 3D fdr #4 Load dropped 74A (226-152A). Not checked yet. | 3211046 | 1 | 15:45 | Afternoon | Thursday | 2016 | 5
3215 | 2016-05-05 15:45 | 2016-08-05 09:45 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 42 | Checked & found, 3D OCB fdr #3 T/R 1x Ctr: Did not change. R/F: 50N. Patrolled the line & found, @1 broken Dead end insulator o/p #4C-15. Cause: Lightning. | 3211046 | 1 | 15:45 | Afternoon | Thursday | 2016 | 5
3216 | 2016-05-05 15:46 | 2016-05-05 15:46 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 73 | 15:46 5B fdr #2 Load dropped 116A (274-158A). 16:15 It was reported no power at Well #4D-53E & #4D-46. (5B fdr #2) 17:20 Checked & found, Recl. 4C-65A (5B fdr #2) T/SO. Ctr: 135-136. Blocked & Closed Recl. 4C-65A, Ok. Then release the block. Not patrolled yet. | 3211046 | 1 | 15:46 | Afternoon | Thursday | 2016 | 5
3217 | 2016-05-05 15:46 | 2016-06-05 16:15 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 73 | Patrolled the line at downstream of Recl. 4C-65A (5B fdr #2), but found nothing. Cause: Suspected by Lightning. Also found, Recl. 5C-07 (5B fdr #2) T/R 1x Ctr: 47-48. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211046 | 1 | 15:46 | Afternoon | Thursday | 2016 | 5
3218 | 2016-05-05 15:50 | 2016-05-05 15:50 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 66 | 15:50 Minas fdr #6 Load dropped 120A (194-74). 17:26 Checked & found, Recl. 6E-23A (Minas fdr #6) T/SO. Ctr: 20-21. Blocked & closed Recl. 6E-23A, Ok. Then release the block. Not Patrolled yet. | 3211046 | 1 | 15:50 | Afternoon | Thursday | 2016 | 5
3219 | 2016-05-05 15:50 | 2016-08-05 08:50 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 66 | Patrolled the line, but found nothing. Cause: Lightning. | 3211046 | 1 | 15:50 | Afternoon | Thursday | 2016 | 5
3220 | 2016-05-05 16:05 | 2016-05-05 16:05 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 38 | 4B OCB fdr #1 T/R 1x. Not checked yet. | 3211046 | 1 | 16:05 | Afternoon | Thursday | 2016 | 5
3221 | 2016-05-05 16:05 | 2016-10-05 17:00 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 38 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 279-280 R/F: 51N. Patrolled the line & found, @1 broken L/A of LBS #4B-150. Cause: Lightning. | 3211046 | 1 | 16:05 | Afternoon | Thursday | 2016 | 5
3222 | 2016-05-05 16:05 | 2016-05-05 16:05 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 0 | 4B OCB fdr#2 Load dropped 53A (96-43A). Not checked yet. | 3211046 | 1 | 16:05 | Afternoon | Thursday | 2016 | 5
3223 | 2016-05-05 16:05 | 2016-07-05 15:00 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 5B-93 (4B fdr #2) T/R 1x Ctr: 00 (Did not change). Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211046 | 1 | 16:05 | Afternoon | Thursday | 2016 | 5
3224 | 2016-06-05 01:43 | 2016-06-05 01:43 | 13.8KV 5B FEEDER #2 | Cloudy | Lightning | 34 | 5B fdr #2 Load dropped 141A (274-133A). Not checked yet. | 3211046 | 1 | 1:43 | Night | Sunday | 2016 | 6
3225 | 2016-06-05 01:43 | 2016-10-05 16:45 | 13.8KV 5B FEEDER #2 | Cloudy | Lightning | 34 | Checked & found, Recl. 5C-07 (5B fdr #2) T/R 1x Ctr: 47-48. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211046 | 1 | 1:43 | Night | Sunday | 2016 | 6
3226 | 2016-06-05 17:32 | 2016-06-05 17:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr #1 Load dropped 46A (237-191A). Not checked yet. | 3211045 | 1 | 17:32 | Afternoon | Sunday | 2016 | 6
3227 | 2016-06-05 17:32 | 2016-07-05 17:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/R 1x Ctr: 176-177. Patrolled the line, but found nothing. Cause: Unidentified. | 3211045 | 1 | 17:32 | Afternoon | Sunday | 2016 | 6
3228 | 2016-06-05 19:21 | 2016-06-05 19:21 | 13.8KV BATANG FEEDER #1 | Fair | Unidentified | 0 | 19:21 Batang OCB fdr #1 T/R 1x. 19:25 Batang OCB fdr #1 T/R 1x. 19:27 Batang OCB fdr #1 T/R 1x again. Checked & found, Batang OCB fdr #1 T/R 3x Ctr: 122-125 R/F: 51N & 51@1,@2,@3. Patrolled the line, but found nothing. Cause: Unidentified. | 3211045 | 1 | 19:21 | Night | Sunday | 2016 | 6
3229 | 2016-06-05 19:24 | 2016-06-05 19:24 | 13.8KV BATANG FEEDER #2 | Cloudy | Lightning | 0 | Batang OCB fdr #2 T/R 1x Ctr: 123-124 R/F: 51N & 51@1,@2,@3. Found, @2,@3 seriously broken L/As on Structure at Batang Substation. Cause: Lightning. | 3211045 | 1 | 19:24 | Night | Sunday | 2016 | 6
3230 | 2016-06-05 19:27 | 2016-06-05 19:27 | 13.8KV BATANG FEEDER #3 | Cloudy | Lightning | 464 | 19:25 Batang OCB fdr #3 T/R 1x. 19:27 Batang OCB fdr #3 T/LO. 22:34 Checked & found, Batang OCB fdr #3 T/LO. Ctr: 318-322 R/F: 50@3 & 50N. Patrolled the line & found, @3 broken L/A on Recl. 36AL-13 (source side). 22:37 Blocked & closed Batang OCB fdr #3, Ok. Then released the block. Cause: Lightning. 22:47 It was reported that no power at downstream of Recl. 36AL-13 (Batang fdr #3). 07-May-2016. 02:28 Checked & found Recl. 36AL-13 (Batang fdr #3) T/SO. Ctr: 119-120. Patrolled the line, but nothing found. 02:50 Blocked & closed Recl. 36AL-13, Ok. Then released the block. Cause: Lightning. | 3211045 | 1 | 19:27 | Night | Sunday | 2016 | 6
3231 | 2016-06-05 22:47 | 2016-06-05 22:47 | 13.8KV BATANG FEEDER #2 | Fair | Lightning Arrester | 26 | 22:47 Batang OCB fdr #2 T/LO. Ctr: 124-128 R/F: 51@2. 07-May-2016. 01:55 Patrolled the line & found: -@2 broken L/A o/p #35AF-29. -@3 broken L/A on TP of Well Rantau Bais #27. 01:57 Blocked & closed Batang OCB fdr #2, Ok. Then released the block. 02:00 Batang OCB fdr #2 T/O again. (in block) Ctr: 128-129 R/F: 50@2. 03:15 Open Bypass SW of Recl. 39AG-11. 03:16 Blocked & closed Batang OCB fdr #2, but T/O again. 03:39 Checked & found: -@2 broken L/A on the structure of Batang fdr #2. -@1 broken L/A on the structure of Batang fdr #3. 04:09 Manually open 13.8KV Batang OCB fdr #1. Manually open 13.8KV Batang OCB fdr #3. 04:11 Manually open 115KV Batang C/S, but failed from DSC. Manually open 115KV Batang C/S from Batang Subtation. 04:16 Installed personal ground. Cut jumper of 6Pcs L/As on the structure Batang Subtation. (Batang fdr #2 & fdr #3) (Then removed Personal Ground) 04:56 Closed Bypass SW of Recl. 36AG-11. 04:58 Manually closed 115KV Batang C/S. (Power Tx at Batang Substation energized) 04:59 Blocked & closed 13.8KV Batang OCB fdr #1, Ok. Then released the block. 05:00 Blocked & closed 13.8KV Batang OCB fdr #2, Ok. Then released the block. 05:01 Blocked & closed 13.8KV Batang OCB fdr #3, Ok. Then released the block. Cause: Lightning Arrester. | 3211045 | 1 | 22:47 | Night | Sunday | 2016 | 6
3232 | 2016-07-05 05:00 | 2016-07-05 05:00 | 13.8KV BATANG FEEDER #3 | Fair | Lightning Arrester | 0 | 05:00 It was reported b/o fuse for Tx at Pemburu-GS. (Batang fdr #3) 08:00 Checked & found: -@1,@2,@3 b/o 7.8SF fuses for 300Kva Tx at Pemburu-GS. -@1 Broken L/A of 300Kva Tx above. 09:00 Dismantle @1,@2,@3 broken L/As of 300Kva Tx at Pemburu-GS. Replaced @1,@2,@3 b/o fuse above with the same size & Energized Tx. Cause: Lightning Arester. | 3211405 | 1 | 5:00 | Morning | Tuesday | 2016 | 7
3233 | 2016-07-05 08:15 | 2016-07-05 08:15 | 13.8KV 5B FEEDER #2 | Fair | Transformer Failure | 93 | 08:15 It was reported b/o fuse for Tx at Well #5D-82. (5B fdr #2) 12:30 Checked & found, @2,@3 b/o 7.8SF fuses for 300Kva Tx at Well #5D-82. Performed TTR, Megger test the Tx & found, Low Megger reading. Cause: Tx Failure. (Low Megger reading) (The Tx is not replaced yet) | 3211046 | 1 | 8:15 | Morning | Tuesday | 2016 | 7
3234 | 2016-07-05 08:15 | 22/05/2016 08:37 | 13.8KV 5B FEEDER #2 | Fair | Transformer Failure | 93 | Replaced 300Kva Tx failure with same size and energized the Tx. Cause: Transformer failure. | 3211046 | 1 | 8:15 | Morning | Tuesday | 2016 | 7
3235 | 2016-07-05 08:15 | 2016-07-05 08:15 | 13.8KV 5B FEEDER #2 | Fair | Unidentified (Fuse) | 9 | 08:15 It was reported b/o fuse for Tx at Well #4E-93. (4D fdr #4) 12:35 Checked & found, @2,@3 b/o 14.0SF fuses for 550Kva Tx at Well #4E-93. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3211046 | 1 | 8:15 | Morning | Tuesday | 2016 | 7
3236 | 2016-07-05 13:01 | 2016-07-05 13:01 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 10 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3211045 | 1 | 13:01 | Afternoon | Tuesday | 2016 | 7
3237 | 2016-07-05 13:01 | 2016-10-05 19:21 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 10 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 991-992 R/F: 51N. Patrolled the line & found, @1 broken Dead End Insulator o/p #29AV-22. Cause: Lightning. | 3211045 | 1 | 13:01 | Afternoon | Tuesday | 2016 | 7
3238 | 2016-07-05 13:30 | 2016-07-05 13:30 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 187 | So.Balam fdr #4 Load dropped 60A (158-98A). Not checked yet | 3211045 | 1 | 13:30 | Afternoon | Tuesday | 2016 | 7
3239 | 2016-07-05 13:30 | 2016-08-05 17:30 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 187 | Checked & found, Recl. 16AB-02 (So.Balam fdr #4) T/R 2x Ctr: 435-437. Patrolled the line & found, @1 broken L/A on TP of Test Station-E. Cause: Lightning. | 3211045 | 1 | 13:30 | Afternoon | Tuesday | 2016 | 7
3240 | 2016-07-05 13:39 | 2016-07-05 13:39 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Lightning | 83 | Pematang OCB fdr #2 T/R 1x. Pematang fdr #1 Load dropped 132A (150-18A). Not checked yet. | 3211045 | 1 | 13:39 | Afternoon | Tuesday | 2016 | 7
3241 | 2016-07-05 13:39 | 2016-10-05 19:39 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Lightning | 83 | Checked & found, Pematang OCB fdr #2 T/R 1x Ctr: 454-455 R/F: 50N. Patrolled the line & found, @1 F/O Dead end Insulator o/p #34BC-53. Cause: Lightning. | 3211045 | 1 | 13:39 | Afternoon | Tuesday | 2016 | 7
3242 | 2016-07-05 13:56 | 2016-07-05 13:56 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 0 | Menggala fdr #1 Load dropped 160A (190-30A). Not checked yet. | 3211046 | 1 | 13:56 | Afternoon | Tuesday | 2016 | 7
3243 | 2016-07-05 13:56 | 2016-08-05 17:26 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 19AO-01 (Menggala fdr #1) T/R 1x Ctr: 453-454. Patrolled the line & found, @1 broken L/A on TP of Well So.Menggala #01. Cause: Lightning. | 3211046 | 1 | 13:56 | Afternoon | Tuesday | 2016 | 7
3244 | 2016-07-05 15:18 | 2016-07-05 15:18 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 65 | 3D OCB fdr #8 T/R 1x. 3D GFPC-Tx #2 T/R 3x. Not checked yet. | 3211046 | 1 | 15:18 | Afternoon | Tuesday | 2016 | 7
3245 | 2016-07-05 15:18 | 2016-08-05 19:39 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 65 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 201 (Did not change). R/F: 51N. Patrolled the line & found: -@1 Broken suspension Insulator o/p #3E-59. -@1 Broken Dead end Insulator o/p #4D-49. Cause: Lightning. | 3211046 | 1 | 15:18 | Afternoon | Tuesday | 2016 | 7
3246 | 2016-07-05 15:36 | 2016-07-05 15:36 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 25 | 4D OCB fdr #5 T/R 1x. 4D fdr #4 Load dropped 155A (198-43A). Not checked yet. | 3211046 | 1 | 15:36 | Afternoon | Tuesday | 2016 | 7
3247 | 2016-07-05 15:36 | 2016-08-05 07:52 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 25 | Checked & found 4D OCB fdr #5 T/R 2x Ctr: 260-262 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #4D-75. Cause: Lightning. | 3211046 | 1 | 15:36 | Afternoon | Tuesday | 2016 | 7
3248 | 2016-07-05 15:36 | 2016-07-05 15:36 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 26 | 4D fdr #4 load dropped 155A (198-43A). Not checked yet. | 3211046 | 1 | 15:36 | Afternoon | Tuesday | 2016 | 7
3249 | 2016-07-05 15:36 | 2016-08-05 08:12 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 26 | Checked & found, 4D OCB fdr #4 T/R 1x Ctr: 257-258 R/F: 51N. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3211046 | 1 | 15:36 | Afternoon | Tuesday | 2016 | 7
3250 | 2016-07-05 15:39 | 2016-07-05 15:39 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 16 | 3D OCB fdr #3 T/R 1x. Not checked yet. | 3211046 | 1 | 15:39 | Afternoon | Tuesday | 2016 | 7
3251 | 2016-07-05 15:39 | 2016-08-05 08:05 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 16 | Checked & found, 3D OCB fdr #3 T/R 1x Ctr: 434-435 R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator o/p #3C-29. Cause: Lightning. | 3211046 | 1 | 15:39 | Afternoon | Tuesday | 2016 | 7
3252 | 2016-08-05 21:34 | 2016-08-05 21:34 | NORTH DURI SUBSTATION | Fair | Under investigation | 0 | 23:34 No.Duri 115KV C/S-Tx #11 T/O. No Power at : 1. 44KV Power Tx. (44KV line to Dumai) 2. 13.8KV No.Duri OCB fdr #1. (to No.Duri Field) 3. 13.8KV No.Duri OCB fdr #2. (to No.Duri Field & CIF) 4. 13.8KV No.Duri OCB fdr #3. (to CGS #10) 22:58 Checked & found, 115KV No.Duri C/S-TX #11 T/O. Ctr: 763-764 R/F: 86T & 87T(@A,@C). Manually opened 13.8KV No.Duri VCB #14. (Power Tx-14 / 44KV Line to Dumai). Manually opened 13.8KV No.Duri VCB fdr #1. Manually opened 13.8KV No.Duri VCB fdr #2. Manually opened 13.8KV No.Duri VCB fdr #3. Then released Relay-86T. 23:03 Manually closed No.Duri C/S-TX #11. (115Kv Power Tx #11 energized) Closed 13.8KV VCB #14. (44KV Power Tx energized) 23:12 Closed 44KV No.Duri GCB #44. (44KV No.Duri-Dumai line energized) Last Ctr: 147-148. 23:17 Blocked & closed No.Duri VCB fdr #3, Ok. Then released the Block. Last Ctr: 169-170. 23:20 Blocked & closed No.Duri VCB fdr #2, Ok. Then released the Block. Last Ctr: 260-261. 23:32 Blocked & closed No.Duri VCB fdr #1, Ok. Then released the Block. Last Ctr: 273-274. Cause: Under investigation. | 3211045 | 1 | 21:34 | Night | Friday | 2016 | 8
3253 | 2016-09-05 02:38 | 2016-09-05 02:38 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Animal | 0 | 02:38 Duri Community ACB fdr #5 T/R 1x Ctr: 101-102 R/F: 51N. 02:48 It was reported there was spark o/p #1SG-01. (by Security) 15:37 Patrolled the line & found, @2 F/O Dead end Insulator o/p #1SG-01. (And found a Dead civet under pole #1SG-01 at infront of Drilling Building) Cause: Animal. (Civet) | 3211045 | 1 | 2:38 | Night | Monday | 2016 | 9
3254 | 2016-09-05 02:38 | 2016-09-05 02:38 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Dead End Insulator | 0 | Duri Community ACB fdr #3 T/R 1x Ctr: 52-53 R/F: 51N. Patrolled the line & found, @2 broken Dead end Insulator o/p #4DD-55. Cause: Dead end Insulator. | 3211045 | 1 | 2:38 | Night | Monday | 2016 | 9
3255 | 2016-09-05 15:00 | 2016-09-05 15:00 | 13.8KV NORTH DURI FEEDER #1 | Fair | Secondary Cable | 0 | 15:00 It was reported b/o fuse for Tx at o/p #10-J6-22. (ND fdr #1) 15:55 Checked & found, @1 b/o 3.1SF fuse for 112.5Kv Tx o/p #10-J6-22 Replaced b/o fuse above with the same saze, then energized the Tx. Cause: Secondary Cable. (Under ground cable zero meg) | 3211045 | 1 | 15:00 | Afternoon | Monday | 2016 | 9
3256 | 2016-09-05 15:47 | 2016-09-05 15:47 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 55 | 6DN OCB fdr #2 T/R 1x. Not checked yet. | 3211046 | 1 | 15:47 | Afternoon | Monday | 2016 | 9
3257 | 2016-09-05 15:47 | 2016-12-05 23:30 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 55 | Checked & found, So.Rumbai Recl. fdr #2 T/R 1x Ctr: 297-298 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211046 | 1 | 15:47 | Afternoon | Monday | 2016 | 9
3258 | 2016-09-05 16:06 | 2016-09-05 16:06 | 4.16KV NO RUMBAI FEEDER #1 | Rain and Lightning | Lightning | 0 | No.Rumbai VCB fdr #1 T/R 2x. Not checked yet. | 3211046 | 1 | 16:06 | Afternoon | Monday | 2016 | 9
3259 | 2016-09-05 16:06 | 2016-12-05 23:40 | 4.16KV NO RUMBAI FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, No.Rumbai VCB fdr #1 T/R 2x Ctr: 386-388 R/F: 50/51@1. Patrolled the line & found: -@1 Broken Pin Insulator o/p #2RB-03. -@1 Broken Jumper of L/A o/p #2RE-03. Cause: Lightning. | 3211046 | 1 | 16:06 | Afternoon | Monday | 2016 | 9
3260 | 2016-09-05 16:12 | 2016-09-05 16:12 | 4.16KV SO RUMBAI FEEDER #1 | Rain and Lightning | Lightning | 0 | So.Rumbai Recl. fdr #1 T/R 1x. Not checked yet. | 3211046 | 1 | 16:12 | Afternoon | Monday | 2016 | 9
3261 | 2016-09-05 16:12 | 2016-12-05 23:35 | 4.16KV SO RUMBAI FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, So.Rumbai Recl. fdr #1 T/R 1x Ctr: 472-473 R/F: 50@2. Patrolled the line & found, @2 broken line Jumper o/p #4RH-02A. Cause: Lightning. | 3211046 | 1 | 16:12 | Afternoon | Monday | 2016 | 9
3262 | 2016-09-05 17:05 | 2016-09-05 17:05 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 45 | So.Bekasap OCB fdr #1 T/R 1x. Not checked yet. | 3211045 | 1 | 17:05 | Afternoon | Monday | 2016 | 9
3263 | 2016-09-05 17:05 | 2016-10-05 19:05 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 45 | Checked & found, So.Bekasap OCB fdr #1 T/R 1x Ctr: 344-345 R/F: 51N. Patrolled the line & found, @1 F/O Dead end Insulator o/p #37BH-04. Cause: Lightning. | 3211045 | 1 | 17:05 | Afternoon | Monday | 2016 | 9
3264 | 2016-09-05 17:17 | 2016-09-05 17:17 | 4.16KV EAST RUMBAI FEEDER #2 | Rain and Lightning | Lightning | 0 | E.Rumbai VCB fdr #2 T/R 1x. Not checked yet. | 3211046 | 1 | 17:17 | Afternoon | Monday | 2016 | 9
3265 | 2016-09-05 17:17 | 2016-12-05 23:45 | 4.16KV EAST RUMBAI FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, E.Rumbai VCB fdr #2 T/R 1x Ctr: 510-511 R/F: 51N. Patrolled the line & found, @2 broken jumper of L/A o/p #4RF-15. Cause: Lightning. | 3211046 | 1 | 17:17 | Afternoon | Monday | 2016 | 9
3266 | 2016-09-05 17:59 | 2016-09-05 17:59 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 18 | 17:59 Libo OCB fdr #2 T/R 1x. 18:01 Libo OCB fdr #2 T/R 1x. 18:02 Libo OCB fdr #2 T/R 1x. 18:03 Libo OCB fdr #2 T/R 1x. 18:06 Libo OCB fdr #2 T/R 1x. 18:09 Libo OCB Fdr #2 T/R 1x. Libo fdr #1 load dropped 40A (88-48A). Not checked yet. | 3211045 | 1 | 17:59 | Afternoon | Monday | 2016 | 9
3267 | 2016-09-05 17:59 | 2016-10-05 13:00 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 18 | Checked & found, Libo OCB fdr #2 T/R 6x Ctr: 418-424 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 17:59 | Afternoon | Monday | 2016 | 9
3268 | 2016-09-05 18:18 | 2016-09-05 18:18 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Lightning | 5 | Menggala fdr #1 Load dropped 127A (183-56A). Ground fault alarm on Menggala fdr #1. Not checked yet. | 3211045 | 1 | 18:18 | Afternoon | Monday | 2016 | 9
3269 | 2016-09-05 18:18 | 15/05/2016 17:18 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Lightning | 5 | Checked & found, Recl. 19AN-04 (Menggala fdr #1) T/R 1x Ctr: 321-322. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 18:18 | Afternoon | Monday | 2016 | 9
3270 | 2016-10-05 08:20 | 2016-10-05 08:20 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 08:20 It was reported no power at Duri field Area #3 Road #5. (One road was no power) Checked & found, Recl. 03-05-27 (C.Duri fdr #7) T/SO. Ctr: 1354-1358 (Found b/o fuse control of Recl. 03-05-27, then replaced it) 08:45 Blocked & closed Recl. 03-05-27, Ok. Then released the Block. Patrolled the Line & found, @2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #03-05-23. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3211045 | 1 | 8:20 | Morning | Wednesday | 2016 | 10
3271 | 2016-10-05 13:55 | 2016-10-05 13:55 | MINAS POWER PLANT |  |  | - | 13:55 S/U MGT #10, then On Line the Unit at 14:20. |  | 1 | 13:55 | Afternoon | Wednesday | 2016 | 10
3272 | 2016-10-05 14:24 | 2016-10-05 14:24 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Planned Maintenance | 0 | 14:24-14:57 S/D Wells #4S-33A & #4S-33B, then open fuse for 112.5Kva Tx o/p #01-02-24. To replace broken L/A of Tx o/p above. Cause: Planned Maintenance. | 123 | 1 | 14:24 | Afternoon | Wednesday | 2016 | 10
3273 | 2016-10-05 14:42 | 2016-10-05 14:42 | MINAS POWER PLANT |  |  | - | Off line MGT #7, then S/D the Unit for S/B. |  | 1 | 14:42 | Afternoon | Wednesday | 2016 | 10
3274 | 2016-10-05 14:53 | 2016-10-05 14:53 | MINAS POWER PLANT |  |  | - | Off line MGT #8, then S/D the Unit for S/B. |  | 1 | 14:53 | Afternoon | Wednesday | 2016 | 10
3275 | 2016-10-05 20:53 | 2016-10-05 20:53 | 4.16KV SO RUMBAI FEEDER #1 | Fair | Planned Maintenance | 0 | 20:53-21:13 Manually opened So.Rumbai Recl. fdr #1. To Repairing @3 broken jumper o/p #4RH-2A. Cause: Planned Maintenance. | 3211045 | 1 | 20:53 | Night | Wednesday | 2016 | 10
3276 | 2016-11-05 09:52 | 2016-11-05 09:52 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Planned Maintenance | 0 | 09:52-11:40 Blocked Recl. 04-06-40. (C.Duri fdr #8) To change out broken L/A o/p #04-06-39. (4 Wells #3P-35A, #3P-36A, #3P-36B & #3P-44B were off) Cause: Planned Maintenance. | 3211045 | 1 | 9:52 | Morning | Saturday | 2016 | 11
3277 | 2016-11-05 13:08 | 2016-11-05 13:08 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Lightning | 0 | 13:08 44KV No.Duri VCB #1 (Line to Dumai) T/O. (in Block status / PT. MS works under Power Line) 13:56 Blocked & closed No.Duri VCB #1, Ok. (44KV No.Duri-Dumai line energized) (After got clearance from job site & normal) Not checked & patrolled yet. | 3211045 | 1 | 13:08 | Afternoon | Saturday | 2016 | 11
3278 | 2016-11-05 13:08 | 13/05/2016 16:20 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Lightning | 0 | Checked & found, 44KV No.Duri VCB #44 (Line to Dumai) T/R 1x Ctr: 106-107 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 13:08 | Afternoon | Saturday | 2016 | 11
3279 | 2016-11-05 13:27 | 2016-11-05 13:27 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Lightning | 213 | 13:27 No.Duri VCB fdr #2 T/O. (in Blocked status for construction jobs) 14:29 Blocked & Closed No.Duri VCB fdr #2, Ok. (after got clearance from job site) Not checked & patrolled yet. | 3211045 | 1 | 13:27 | Afternoon | Saturday | 2016 | 11
3280 | 2016-11-05 13:27 | 13/05/2016 16:15 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Lightning | 213 | Checked & found, No.Duri VCB fdr #2 T/O. Ctr: 261-262 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 13:27 | Afternoon | Saturday | 2016 | 11
3281 | 2016-11-05 13:37 | 2016-11-05 13:37 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 61 | 13:37 Sintong OCB fdr #2 T/R 1x. (Ground fault alarm at Sintong fdr #2) It was reported no power at Pagar-GS. 14:50 Checked & found, Recl. 28AF-17 (Sintong fdr #2) T/SO. Ctr: not reported yet. Blocked & Closed, Recl. 28AF-17, Ok. Then released the Block. Not checked & patrolled yet. | 3211045 | 1 | 13:37 | Afternoon | Saturday | 2016 | 11
3282 | 2016-11-05 13:37 | 2016-12-05 14:45 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 61 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 410-411 R/F: 51N. Patrolled the line, but found nothing. Also found, Recl. 28AF-07 (Sintong fdr #3) T/R 1x Ctr: 429-430. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 13:37 | Afternoon | Saturday | 2016 | 11
3283 | 2016-11-05 14:40 | 2016-11-05 14:40 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Transformer Failure | 0 | 14:40 It was reported b/o fuse for Tx o/p #03-07-20. (C.Duri fdr #7) 18:30 Checked & found, @1,@3 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-07-20. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx Failure. (Low megger reading) (The Tx failure is not replaced yet) | 3211045 | 1 | 14:40 | Afternoon | Saturday | 2016 | 11
3284 | 2016-11-05 14:40 | 24/05/2016 15:10 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Transformer Failure | 0 | Replaced 112.5Kva Tx failure with same size & enegized the Tx. Cause: Transformer Failure. | 3211045 | 1 | 14:40 | Afternoon | Saturday | 2016 | 11
3285 | 2016-11-05 15:02 | 2016-11-05 15:02 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Lightning | 0 | No.Duri VCB fdr #8 T/R 1x. Not checked yet. | 3211045 | 1 | 15:02 | Afternoon | Saturday | 2016 | 11
3286 | 2016-11-05 15:02 | 16/05/2016 12:50 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Lightning | 0 | Checked & found, No.Duri VCB fdr #8 T/R 1x Ctr: 58-59 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 15:02 | Afternoon | Saturday | 2016 | 11
3287 | 2016-11-05 18:46 | 2016-11-05 18:46 | 13.8KV PEMATANG FEEDER #2 | Fair | Animal | 71 | 18:46 It was reported b/o fuse for Tx at Well Pematang #97. (Pematang fdr #2) 21:00 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Pematang #97. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3211045 | 1 | 18:46 | Afternoon | Saturday | 2016 | 11
3288 | 2016-11-05 20:28 | 2016-11-05 20:28 | 13.8KV ROKAN FEEDER #2 | Fair | Pin Insulator | 10 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3211045 | 1 | 20:28 | Night | Saturday | 2016 | 11
3289 | 2016-11-05 20:28 | 13/05/2016 14:50 | 13.8KV ROKAN FEEDER #2 | Fair | Pin Insulator | 10 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 992-993 R/F: 51@3. Patrolled the line & found, @3 broken Pin Insulator o/p #30AV-24. Cause: Pin Insulator. | 3211045 | 1 | 20:28 | Night | Saturday | 2016 | 11
3290 | 2016-12-05 10:42 | 2016-12-05 10:42 | MINAS POWER PLANT |  |  | - | 10:42 S/U MGT #1, then On Line the Unit at 11:14. |  | 1 | 10:42 | Morning | Monday | 2016 | 12
3291 | 2016-12-05 11:30 | 2016-12-05 11:30 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Fair | Planned Maintenance | 9 | 11:30-13:00 Blocked MSU-2 VCB fdr #1 (Pinang fdr #1) For Replacing broken Pin Insulator & broken HLC jumper o/p #11D-35. (Wells Pinang #16, #37 & #39 were off during the job done) Cause: Planned Maintenance. | 3211045 | 1 | 11:30 | Morning | Monday | 2016 | 12
3292 | 2016-12-05 11:40 | 2016-12-05 11:40 | MINAS POWER PLANT |  |  | - | 11:40 Off line MGT #3, then S/D the Unit for S/B. (Prior to replacing Fuel Nozzle set) |  | 1 | 11:40 | Morning | Monday | 2016 | 12
3293 | 2016-12-05 15:52 | 2016-12-05 15:52 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Unidentified | 162 | 15:52 C.Duri fdr #1 Load dropped 51A (239-186A). 18:12 Checked & found, Recl. 38AS-09 T/SO. Ctr: 231-232. Patrolled the Line, but found nothing. Blocked & Closed Recl. 38AS-09, Ok. The released the block. Cause: Unidentified. | 3211045 | 1 | 15:52 | Afternoon | Monday | 2016 | 12
3294 | 2016-12-05 16:00 | 2016-12-05 16:00 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 167 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3211045 | 1 | 16:00 | Afternoon | Monday | 2016 | 12
3295 | 2016-12-05 16:00 | 14/05/2016 17:00 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 167 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr. R/F are not reported yet. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 16:00 | Afternoon | Monday | 2016 | 12
3296 | 2016-12-05 17:11 | 2016-12-05 17:11 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 31 | 17:11 Bekasap VCB fdr #6 T/R 1x. 17:28 Beaksap VCB fdr #6 T/R 1x again. Not checked yet. | 3211045 | 1 | 17:11 | Afternoon | Monday | 2016 | 12
3297 | 2016-12-05 17:11 | 14/05/2016 17:10 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 31 | Checked & found, Bekasap Main OCB fdr #6 T/R 2x Ctr: 339-341 R/F: 51N & 51@1. Patrolled the line & found: -@1 Broken Pin Insulator o/p #38BE-05. -@2 Broken Dead end Insulator o/p #38BE-05. -@2 Broken Pin Insulator o/p #39BE-12. -@3 Broken L/A on TP of Well Aman #03. -@1 Broken Pin Insulator o/p #39BH-09. Cause: Lightning. | 3211045 | 1 | 17:11 | Afternoon | Monday | 2016 | 12
3298 | 2016-05-13 01:04 | 2016-05-13 01:04 | CENTRAL DURI POWER PLANT | Fair | Equipment Failure | - | 01:04 CGT #5 Tripped by alarm: Computer T Communication Link in Cooperative. Cause: Equipment failure. (Power supply Computer-T problem) Frequency dropped to 59.83HZ. (No load shedding) 09:25 S/U CGT #5, then online the Unit at 09:40. (After replacing power supply for Computer-T) |  | 1 | 1:04 | Night | Friday | 2016 | 5
3299 | 2016-05-13 09:09 | 2016-05-13 09:09 | 13.8KV PETAPAHAN FEEDER #1 | Rain | Recloser | 176 | 09;09 Petapahan OCB Fdr#1 load droped 27A (82-55A). 10:00 It was reported some wells no power ( PTH#07, PTH#20, PTH#23 ,PTH#25, PTH#30 PTH#32,PTH#37,PTH#46,PTH#49) 11:40 Checked & found Recl. 30CZ-01 T/SO. ctr:100 - 101. Blocked & closed, but fail,control problem, continued to troble shoot. 15:42 Manual Opened Petapahan OCB fdr#1, (after got Clearance by TL Petapahan GS) Closed bypass Recl. 30CZ-01. OK. 15:44 Manual Closed Petapahan OCB Fdr#1, OK. Cause : Recloser | 3211046 | 1 | 9:09 | Morning | Friday | 2016 | 5
3300 | 2016-05-13 09:25 | 2016-05-13 09:25 | CENTRAL DURI POWER PLANT |  |  | - | 09:25 CDGT #5 S/U then online the unit at 09:40 after replaced computer T power supplay module. | 3211046 | 1 | 9:25 | Morning | Friday | 2016 | 5
3301 | 2016-05-13 15:30 | 2016-05-13 15:30 | 13.8KV CENTRAL DURI FEEDER #1 | Lightning | Lightning | 108 | 15:30 CD fdr#1 Load dropped 70A(239-169). 17:09 Checked & found Recl. 39.AV.36 T/SO, Ctr: 178-179. Patrolled the Line but found nothing. Blocked & Closed the Recl. 39.AV.36, OK, then released the block. Cause : Suspected Lightning. | 3211045 | 1 | 15:30 | Afternoon | Friday | 2016 | 5
3302 | 2016-05-13 16:16 | 2016-05-13 16:16 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 23 | Petani OCB fdr#2 T/R 1x. Petani fdr#1 Load dropped 141A (218-77A). Not checked yet. | 3211045 | 1 | 16:16 | Afternoon | Friday | 2016 | 5
3303 | 2016-05-13 16:16 | 2016-05-16 18:15 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 23 | Checked & found, Petani OCB fdr #2 T/R 1x Ctr: Not reported yet. R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 16:16 | Afternoon | Friday | 2016 | 5
3304 | 2016-05-13 17:10 | 2016-05-13 17:10 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified (Fuse) | 1 | 17:10 It was reported b/o fuse for Tx o/p #01-06-17. (D.Field fdr #1) 17:40 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #01-06-17. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3211045 | 1 | 17:10 | Afternoon | Friday | 2016 | 5
3305 | 2016-05-13 18:47 | 2016-05-13 18:47 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 160 | 18:47 8D fdr #10 Load dropped 118A (139-21A). 18:55 8D OCB fdr #10 T/LO. 19:52 Checked & found, 8D OCB fdr #10 T/LO. Ctr: 217-222 R/F: 51N. 21:40 Patrolled the line & found, @2 broken Pin Insulator o/p #N8D-17A. (Then replaced @2 broken Pin Insulator o/p #N8D-17A) 23:20 Blocked & Closed 8D OCB fdr #10, Ok. Then release the block. Cause: Lightning. | 3211046 | 1 | 18:47 | Afternoon | Friday | 2016 | 5
3306 | 2016-05-14 05:28 | 2016-05-14 05:28 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Lightning Arrester | 0 | 05:28 Duri Community fdr#3 Load dropped 39A (73-34A). 06:00 Checked & found Recl. 6F-07 T/LO Ctr:1835-1838. 06:05 Blocked and closed Recl.6F-07 but tripped again. 06:42 Patrolled the line & found @1 Broken LA o/p 2DG-14. Isolated @1 Broken LA o/p 2DG-14. 07:20 Blocked & Closed Recl. 6F-07, ok, then release the block. Cause: lightning Arrester. | 3211045 | 1 | 5:28 | Morning | Saturday | 2016 | 5
3307 | 2016-05-14 09:14 | 2016-05-14 09:14 | 115KV MINAS - LUKUT LINE | Fair | Construction Job | - | 09:14 115KV MSY-Lukut line Load dropped 12A (100%) Switching to Manually open 115KV Lukut GCB (to Beruk-Zamrud / BOB) To Tie in / Re-coonected 115KV Beruk-Zamrud system with CPI Power system. (As per 1.2 PSA Reconnection, to add Load Max 10MW from 6MW Max / No.190/SOM/IV/2016) Date: 18 april 2016 Cause: Planned Construction. (Additional Load Max 10MW) 12:27 Manually Close 115KV Lukut GCB (to Beruk-Zamrud / BOB) 115KV MSY Load 42A. (9MW) Cause: Planned Construction. (Additional Load Max 10MW) |  | 1 | 9:14 | Morning | Saturday | 2016 | 5
3308 | 2016-05-14 09:44 | 2016-05-14 09:44 | 13.8KV NORTH DURI FEEDER #2 | Fair | Transformer Failure | 46 | 09:44 It was reported b/o fuse for Tx o/p #10-J8-12. (No.Duri fdr #2) 12:00 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #10-J8-12. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx Failure. (Low Megger reading) (The Tx failure is not replaced yet) | 3211045 | 1 | 9:44 | Morning | Saturday | 2016 | 5
3309 | 2016-05-14 09:44 | 2016-05-21 11:09 | 13.8KV NORTH DURI FEEDER #2 | Fair | Transformer Failure | 46 | Replaced 112.5 Kva Tx failure with same size and energized the Tx. Cause: Transformer Failure. | 3211045 | 1 | 9:44 | Morning | Saturday | 2016 | 5
3310 | 2016-05-14 11:36 | 2016-05-14 11:36 | 13.8KV S. BALAM FEEDER #4 | Fair | Transformer Failure | 37 | 11:36 It was reported b/o fuse for Tx at Well So.Balam #55. (Balam fdr #4) 14:30 Checked & found, @1,@3 b/o 3.5SF fuses for 150Kva Tx at Well So.Balam #55. Performed TTR, Megger Test the Tx & found, Low megger reading. Cause: Tx Failure. (Low megger reading) (The Tx failure is not replaced yet) | 3211045 | 1 | 11:36 | Morning | Saturday | 2016 | 5
3311 | 2016-05-14 11:36 | 2016-05-18 11:00 | 13.8KV S. BALAM FEEDER #4 | Fair | Transformer Failure | 37 | Replaced 100Kva Tx failure with the same size & energized the Tx at Well So.Balam #555. Cause: Tx Failure. (Low megger reading) | 3211045 | 1 | 11:36 | Morning | Saturday | 2016 | 5
3312 | 2016-05-14 16:12 | 2016-05-14 16:12 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 46 | Bangko fdr #1 Load dropped 67A (205-138A). Not checked yet. | 3211045 | 1 | 16:12 | Afternoon | Saturday | 2016 | 5
3313 | 2016-05-14 16:12 | 2016-05-15 17:10 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 46 | Checked & found, Recl. 23W-12 (Bangko fdr #1) T/R 1x Ctr: 238-239. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 16:12 | Afternoon | Saturday | 2016 | 5
3314 | 2016-05-14 16:12 | 2016-05-14 16:12 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 38 | Bangko fdr #4 Load dropped 90A (226-136A). Not checked yet. | 3211045 | 1 | 16:12 | Afternoon | Saturday | 2016 | 5
3315 | 2016-05-14 16:12 | 2016-05-15 17:12 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 38 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 96-97. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 16:12 | Afternoon | Saturday | 2016 | 5
3316 | 2016-05-14 16:14 | 2016-05-14 16:14 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 75 | Nella fdr #1 Load dropped 137A (253-116A). Not checked yet. | 3211045 | 1 | 16:14 | Afternoon | Saturday | 2016 | 5
3317 | 2016-05-14 16:14 | 2016-05-15 17:15 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 75 | Checked & found, Recl. 21V-01 (Nella fdr #1) T/R 1x Ctr: 95-96. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 16:14 | Afternoon | Saturday | 2016 | 5
3318 | 2016-05-14 17:00 | 2016-05-14 17:00 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 35 | So.Bekasap fdr #1 Load dropped 104A (155-51). Not checked yet. | 3211045 | 1 | 17:00 | Afternoon | Saturday | 2016 | 5
3319 | 2016-05-14 17:00 | 2016-05-17 17:00 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 35 | Checked & found, Recl. 34BI-18 (So.Bekasap fdr #1) T/R 1x Ctr: 152-153. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 17:00 | Afternoon | Saturday | 2016 | 5
3320 | 2016-05-15 04:38 | 2016-05-15 04:38 | 115KV DURI - KOTABATAK JUNCTION LINE | Fair | Accident | 831 | 04:38 115KV DRB GCB #26 T/O. 115KV DRB GCB #28 T/O. 115KV KBJ GCB #43 T/O. 115KV KBJ GCB #45 T/O. (115KV DRB- KBJ line Tripped) 05:43 Checked & found: 115KV DRB GCB #26 T/LO. Last Ctr: 899. (Not change) 115KV DRB GCB #28 T/LO. Last Ctr: 152. 115KV KBJ GCB #43 T/LO. Last Ctr: 417. 115KV KBJ GCB #45 T/LO. Last Ctr: 302. R/F: 21@2,@3 & 86L. (115KV DRB - KBJ line) 06:43 Patrolled & found: -@1,@2,@3 Broken 115KV conductor o/p #DK-69 & #DK-70. -@1,@2,@3 Broken 13.8KV conductor / under build. (Pungut fdr #2) (115KV DRB-KBJ line broken conductor & Pungut fdr #2 line) Cause: Accident. (Fire under power line due to Publick Truck hit CPI Gas line at near Intan crossing road) 07:08 Open 115KV Line Switch KBJ-DRB. (MOD 410-73-003) 07:10 Closed 115KV Grounding Switch KBJ-DRB line. 08:22 Open 115KV Line Switch DRB-KBJ. (10-73-14). 08:30 Closed 115KV Grounding Switch DRB-KBJ line. 08:10 Opened 13.8KV Isolation Switch of Pungut OCB fdr #2. 11:48 Manual Closed 115KV DRB GCB #26 & GCB #28. (to normalize Ring Bus of DRB) 14:20 Cut Jumper o/p #45BR-06 of 13.8KV Pungut fdr #2, to isolate line toward Intan Fields. (Tandun Fields are still Energize) 14:30 Block & Closed, 13.8KV Pungut OCB fdr #2, Ok. Then released the Block. 17:10 Manual Closed 115KV KBJ GCB #43 & GCB #45. (to normalize Ring Bus of KBJ) Cause: Accident. (Broken 115KV conductor DRB-KBJ line due to fire) Production loss Reported by EC: Prod. loss 14 May 2016 = 429 Bbls / 8 Wells. Prod. loss 15 May 2016 = 402 Bbls / 20 Wells. Grand Total = 831 Bbls / 28 Wells. | 3211045 | 1 | 4:38 | Morning | Sunday | 2016 | 5
3321 | 2016-05-15 07:01 | 2016-05-15 07:01 | DARLING SUBSTATION | Fair | Unidentified | 0 | 07:01 Darling 115KV GCB #1 T/O. Ctr: not reported yet. R/F: 87T-@1,@2 & 86T. Darling 115KV GCB #3 T/O. (Darling Substation TX-2 no power) 08:30 Checked Darling TX-2, but found nothing. (Normal) 08:47 Manually open 13.8KV Darling VCB fdr #5, #6, #7 & #8. Then resetting Relay 87T & 86T. 08:52 Closed Darling 115KV GCB #1 (SC). Closed Darling 115KV GCB #3 (SC). 08:57 Blocked & closed, 13.8KV Darling VCB fdr #6, Ok. Then released the block. Blocked & closed, 13.8KV Darling VCB fdr #7, Ok. Then released the block. Blocked & closed, 13.8KV Darling VCB fdr #5, Ok. Then released the block. Blocked & closed, 13.8KV Darling VCB fdr #8, Ok. Then released the block. Caused: Unidentified. | 3211045 | 1 | 7:01 | Morning | Sunday | 2016 | 5
3322 | 2016-05-16 06:10 | 2016-05-16 06:10 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 9 | 06:10 It was reported b/o fuse for Tx at Well Kulim #07. (C.Duri fdr #1) 11:00 Checked & found, @1 b/o 1.0SF fuse for 45Kva Tx at Well Kulim #07. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3211045 | 1 | 6:10 | Morning | Monday | 2016 | 5
3323 | 2016-05-16 06:47 | 2016-05-16 06:47 | 13.8KV S. BALAM GFPC | Rain and Lightning | Lightning | 0 | So.Balam GFPC T/R 1x. Ground fault alarm at So.Balam fdr #4. (No load dropped at any fdrs.) Not checked yet. | 3211045 | 1 | 6:47 | Morning | Monday | 2016 | 5
3324 | 2016-05-16 06:47 | 2016-05-18 16:45 | 13.8KV S. BALAM GFPC | Rain and Lightning | Lightning | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 215-216 R/F: 51N. Patrolled So.Balam fdr #4 line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 6:47 | Morning | Monday | 2016 | 5
3325 | 2016-05-16 11:10 | 2016-05-16 11:10 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified (Fuse) | 96 | 11:10 It was reported b/o fuse for Tx at Well Pematang #97. 13:45 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Pematang #97. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3211045 | 1 | 11:10 | Morning | Monday | 2016 | 5
3326 | 2016-05-16 14:30 | 2016-05-16 14:30 | 13.8KV DURI FIELD FEEDER #4 | Fair | Theft | - | It was reported no power o/p #07-V5-15. Also reported lost of secondary cable of Tx o/p #07-V5-15. Not checked yet. | 3211045 | 1 | 14:30 | Afternoon | Monday | 2016 | 5
3327 | 2016-05-16 14:30 | 2016-05-17 14:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Theft | - | 14:00 Checked & found, lost of secondary cable of 112.5Kva Tx o/p #07-V5-15. (D.Field fdr #4) 17:00 Replaced secondary cable above, the energized the Tx o/p #07-V5-15. Cause: Theft. | 3211045 | 1 | 14:30 | Afternoon | Monday | 2016 | 5
3328 | 2016-05-17 09:10 | 2016-05-17 09:10 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 43 | 09:10-14:50 Blocked So.Balam fdr #4, then open HLC o/p #16AA-113. To tie in new Wells #So.Balam #421, #422 & #423. (Well #So.Balam #332 was off during the Job done) Cause: Planned to Construction. (No production loss charge to PGT) | 123 | 1 | 9:10 | Morning | Tuesday | 2016 | 5
3329 | 2016-05-17 10:00 | 2016-05-17 10:00 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 10:00 It was reported b/o fuse for Tx o/p #04-3-11. 15:45 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #04-3-11. Performed TTR, megger test the tx & found, Normal. (Good reading). Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3211045 | 1 | 10:00 | Morning | Tuesday | 2016 | 5
3330 | 2016-05-17 18:45 | 2016-05-17 18:45 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 7 | It was reported b/o fuse for Tx o/p #02-04-08. (C.Duri fdr #6). Not checked yet. | 3211045 | 1 | 18:45 | Afternoon | Tuesday | 2016 | 5
3331 | 2016-05-17 18:45 | 2016-05-18 14:40 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 7 | Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #02-04-08. Replaced b/o fuse above with the same size & energized the Tx, but b/o again. Cause: Tx Failure. (The Tx failure is not replaced yet) | 3211045 | 1 | 18:45 | Afternoon | Tuesday | 2016 | 5
3332 | 2016-05-17 18:45 | 2016-01-06 15:00 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 7 | Replaced 112.5Kva Tx failure with the same size, then energized the Tx o/p #02-04-08. Cause: Tx Failure. | 3211045 | 1 | 18:45 | Afternoon | Tuesday | 2016 | 5
3333 | 2016-05-18 02:34 | 2016-05-18 02:34 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 57 | Minas ACB fdr #6 T/R 1x Ctr: 159-160 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211046 | 1 | 2:34 | Night | Wednesday | 2016 | 5
3334 | 2016-05-18 05:45 | 2016-05-18 05:45 | 13.8KV 8C FEEDER #1 | Rain and Lightning | Lightning | 12 | 8C VCB fdr #1 T/R 1x. 8C fdr #3 Load dropped 64A (222-158A). 8C fdr #4 Load dropped 244A (282-38A). Not checked yet. | 3211046 | 1 | 5:45 | Morning | Wednesday | 2016 | 5
3335 | 2016-05-18 05:45 | 2016-05-20 10:00 | 13.8KV 8C FEEDER #1 | Rain and Lightning | Lightning | 12 | Checked & found, 8C VCB fdr #1 T/R 1x Ctr: 639-640 R/F: 50@2,@3. Patrolled the line & found, @3 broken Dead end Insulator o/p #9C-12. Cause: Lightning. | 3211046 | 1 | 5:45 | Morning | Wednesday | 2016 | 5
3336 | 2016-05-18 06:19 | 2016-05-18 06:19 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 34 | 4B OCB fdr #1 T/R 1x. Not checked yet. | 3211046 | 1 | 6:19 | Morning | Wednesday | 2016 | 5
3337 | 2016-05-18 06:19 | 2016-05-21 13:59 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 34 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 280-281 R/F: 51N. Patrolled the line & found: -@3 Broken L/A on TP of Well #4A-53. -@1 Broken Dead End Insulator o/p #3A-27. -@1 Broken Dead End Insulator o/p #3A-09. Cause: Lightning. | 3211046 | 1 | 6:19 | Morning | Wednesday | 2016 | 5
3338 | 2016-05-18 15:25 | 2016-05-18 15:25 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Animal | 2 | 15:25 It was reported b/o fuse for Tx o/p #03-02-17. (C.Duri fdr #6) 16:48 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-02-17. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal. (Bird) | 3211045 | 1 | 15:25 | Afternoon | Wednesday | 2016 | 5
3339 | 2016-05-18 15:42 | 2016-05-18 15:42 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 50 | 6DN OCB fdr #6 T/R 1x. 6DN fdr #5 Load dropped 8A (126-118A). Not checked yet. | 3211046 | 1 | 15:42 | Afternoon | Wednesday | 2016 | 5
3340 | 2016-05-18 15:42 | 2016-05-22 18:26 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 50 | Checked & found, 6DN OCB fdr #6 T/R 1x Ctr: 344-345 R/F: 50@3. Patrolled the line & found, @3 broken L/A o/p #6E-64. Cause: Lightning. | 3211046 | 1 | 15:42 | Afternoon | Wednesday | 2016 | 5
3341 | 2016-05-18 16:49 | 2016-05-18 16:49 | 13.8KV CENTRAL DURI FEEDER #1 | Drizzle | Lightning | 0 | 16:49 C.Duri fdr #1 Load dropped 90A (240-150A). 17:36 Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/O. Ctr: 236-237. (In blocked position due to Rig activity at Loc Kulim #01) Blocked & closed Recl. 41AW-62, Ok. Then released the blocked. The line is not Patrolled yet. | 3211045 | 1 | 16:49 | Afternoon | Wednesday | 2016 | 5
3342 | 2016-05-18 16:49 | 2016-05-19 17:15 | 13.8KV CENTRAL DURI FEEDER #1 | Drizzle | Lightning | 0 | Patrolled the line downstream of Recl. 41AW-62, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 16:49 | Afternoon | Wednesday | 2016 | 5
3343 | 2016-05-19 17:35 | 2016-05-19 17:35 | 13.8KV NORTH DURI FEEDER #9 | Cloudy and Lightning | Lightning | 0 | N.Duri VCB fdr #9 T/R 1x. Not checked yet. | 3211045 | 1 | 17:35 | Afternoon | Thursday | 2016 | 5
3344 | 2016-05-19 17:35 | 2016-05-22 07:09 | 13.8KV NORTH DURI FEEDER #9 | Cloudy and Lightning | Lightning | 0 | Checked & found, No.Duri VCB fdr #9 T/R 1x Ctr: 40-41 R/F: 51@1,@2,@3. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3211045 | 1 | 17:35 | Afternoon | Thursday | 2016 | 5
3345 | 2016-05-19 18:30 | 2016-05-19 18:30 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 59 | Nella VCB fdr #2 T/R 1x. Nella fdr #1 load dropped 70A (260-190A). Nella Capacitor Bank Recloser T/O. (Nella GFPC on By Passed) Not checked yet. | 3211045 | 1 | 18:30 | Afternoon | Thursday | 2016 | 5
3346 | 2016-05-19 18:30 | 2016-05-23 08:30 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 59 | Checked & found, Nella VCB fdr #2 T/R 1x Ctr: 217-218 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 18:30 | Afternoon | Thursday | 2016 | 5
3347 | 2016-05-20 14:48 | 2016-05-20 14:48 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | No.Duri VCB fdr #2 T/R 1x. Not checked yet. | 3211045 | 1 | 14:48 | Afternoon | Friday | 2016 | 5
3348 | 2016-05-20 14:48 | 2016-05-22 07:07 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | Checked & found, No.Duri VCB fdr #2 T/R 1x Ctr: 260-261 R/F: 51@2. Patrolled the line, but nothing found. Cause: Unidentified. | 3211045 | 1 | 14:48 | Afternoon | Friday | 2016 | 5
3349 | 2016-05-20 15:05 | 2016-05-20 15:05 | 13.8KV 3D FEEDER #8 | Fair | Planned Maintenance | 38 | 15:05 Switching to transfer load 3D fdr #2 to 3D fdr #8, then Opened LBS #3E-64. To replaced @1,@3 broken Dead end Insulator o/p #3E-58 and o/p #3E-59. (22 Wells were off during the job done / GS-4 = 12Wells & GS-5 = 10Wells) 16:20 Closed LBS #3E-64. Production loss GS #4 = 25 Bbls / 12 wells. Production loss GS #5 = 33 Bbls / 10 wells. Cause: Planned Maintenance. | 123 | 1 | 15:05 | Afternoon | Friday | 2016 | 5
3350 | 2016-05-20 18:14 | 2016-05-20 18:14 | 13.8KV DURI FIELD FEEDER #4 | Heavy Rain | Lightning | 7 | 18:14 It was reported no power at Road-7. (No.Duri fdr #4) 18:47 Checked & found, Recl. 06-S7-19 (No.Duri fdr #14) T/SO. Ctr: 494-495. Blocked & closed Recl. 06-S7-19, Ok. Then released the block. The line is not patrolled yet. | 3211045 | 1 | 18:14 | Afternoon | Friday | 2016 | 5
3351 | 2016-05-20 18:14 | 2016-05-22 07:02 | 13.8KV DURI FIELD FEEDER #4 | Heavy Rain | Lightning | 7 | Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3211045 | 1 | 18:14 | Afternoon | Friday | 2016 | 5
3352 | 2016-05-20 19:14 | 2016-05-20 19:14 | 13.8KV 4B FEEDER #2 | Cloudy and Lightning | Lightning | 32 | 4B VCB fdr#2 T/R 1x. 4B fdr#1 Load dropped 145A(290-145A). Not checked yet. | 3211046 | 1 | 19:14 | Night | Friday | 2016 | 5
3353 | 2016-05-20 19:14 | 2016-05-22 17:51 | 13.8KV 4B FEEDER #2 | Cloudy and Lightning | Lightning | 32 | Checked and found 4B OCB fdr #2 T/R 2x Ctr: 224-226 R/F: 51@3. Patrolled the line nothing found. Cause: Unidentified. | 3211046 | 1 | 19:14 | Night | Friday | 2016 | 5
3354 | 2016-05-21 15:00 | 2016-05-21 15:00 | CENTRAL DURI POWER PLANT | Fair |  | - | 15:00 S/U CGT #2, then On Line the Unit at 16:15. |  | 1 | 15:00 | Afternoon | Saturday | 2016 | 5
3355 | 2016-05-21 16:06 | 2016-05-21 16:06 | 13.8KV MENGGALA FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Menggala fdr #1 Load dropped 44A (180-136A). Mengggala GFPC T/R 1x. (Ground fault alarm on Menggala fdr #1) Not checked yet. | 3211045 | 1 | 16:06 | Afternoon | Saturday | 2016 | 5
3356 | 2016-05-21 16:06 | 2016-05-23 08:35 | 13.8KV MENGGALA FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 19AO-01 (Menggala fdr #1) T/R 1x Ctr: 454-455 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 16:06 | Afternoon | Saturday | 2016 | 5
3357 | 2016-05-22 00:15 | 2016-05-22 00:15 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 34 | 00:15 It was reported no Power at Well Hitam #01. (Libo fdr #2) 16:25 Checked & found, Spark at secondary cable. Opened FCO for replacing Secondary cable above. Cause: Maintenance Job. | 3211046 | 1 | 0:15 | Night | Sunday | 2016 | 5
3358 | 2016-05-22 08:40 | 2016-05-22 08:40 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 12 | 08:40 It was reported b/o fuse for Tx o/p #04-05-10. (C.Duri fdr #9) 09:48 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-05-10. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (fuse). | 3211045 | 1 | 8:40 | Morning | Sunday | 2016 | 5
3359 | 2016-05-22 22:50 | 2016-05-22 22:50 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 22:50 It was reported b/o fuse for Tx o/p #01-04-19 (for CGS-1 Facility) 23:26 Checked & found, @2 b/o 10.4SF fuse for 400Kva Tx o/p #01-04-19. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3211045 | 1 | 22:50 | Night | Sunday | 2016 | 5
3360 | 2016-05-23 17:00 | 2016-05-23 17:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Duri Field ACB fdr #4 T/R 1x. Not checked yet. | 3211045 | 1 | 17:00 | Afternoon | Monday | 2016 | 5
3361 | 2016-05-23 17:00 | 2016-05-25 18:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Duri Field ACB fdr #4 T/R 1x Ctr: 467-468 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3211045 | 1 | 17:00 | Afternoon | Monday | 2016 | 5
3362 | 2016-05-24 11:01 | 2016-05-24 11:01 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | CDGT #4 Tripped By Alarm: Fire detective trip (45 FT). Frequency dropped to 59.86Hz. (No Load shedding) Cause: Under Investigation. | 3211045 | 1 | 11:01 | Morning | Tuesday | 2016 | 5
3363 | 2016-05-24 11:45 | 2016-05-24 11:45 | MINAS POWER PLANT | Fair |  | - | 11:45 S/U MGT #6, Then On Line the Unit at 12:03. |  | 1 | 11:45 | Morning | Tuesday | 2016 | 5
3364 | 2016-05-24 16:52 | 2016-05-24 16:52 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 210 | CKBS VCB fdr #5 T/R 1x. Not checked yet. | 3211046 | 1 | 16:52 | Afternoon | Tuesday | 2016 | 5
3365 | 2016-05-24 16:52 | 2016-05-25 14:30 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 210 | Checked & found, CKBS VCB fdr #5 T/R 1x Ctr: 142-143 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3211046 | 1 | 16:52 | Afternoon | Tuesday | 2016 | 5
3366 | 2016-05-24 16:55 | 2016-05-24 16:55 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 0 | So.Bekasap fdr #1 Load dropped 92A ( 170-78A ). Not checked yet. | 3211045 | 1 | 16:55 | Afternoon | Tuesday | 2016 | 5
3367 | 2016-05-24 16:55 | 2016-05-28 16:55 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 34BI-18 (So.Bekasap fdr #1) T/R 2x Ctr: 153-155. Patrolled the line & found, @2 broken L/A o/p #33BG-05. Cause: Lightning. | 3211045 | 1 | 16:55 | Afternoon | Tuesday | 2016 | 5
3368 | 2016-05-25 08:25 | 2016-05-25 08:25 | DURI POWER PLANT |  |  | - | 08:25 S/U DGT #7, then Online the Unit at 08:52. |  | 1 | 8:25 | Morning | Wednesday | 2016 | 5
3369 | 2016-05-25 08:30 | 2016-05-25 08:30 | 13.8KV PUNGUT FEEDER #2 | Fair | Low mega-ohm reading | 0 | 08:30 It was reported b/o fuse for Tx at Well Asih #05. (Pungut fdr #2) 10:25 Checked & found, @1,@3 b/o 3.5SF fuses for 150Kva Tx at Well Asih #05. Performed TTR, Megger test the Tx & found, low megger reading. Cause: Tx Failure. (Low megger reading) (The Tx failure is not replaced yet) | 3211045 | 1 | 8:30 | Morning | Wednesday | 2016 | 5
3370 | 2016-05-25 08:30 | 2016-05-28 12:20 | 13.8KV PUNGUT FEEDER #2 | Fair | Low mega-ohm reading | 0 | Replaced 150Kva Tx with the same size at well Asih#05, then energized Tx. Cause: Transformer Low Megger. | 3211045 | 1 | 8:30 | Morning | Wednesday | 2016 | 5
3371 | 2016-05-25 09:10 | 2016-05-25 09:10 | CENTRAL DURI POWER PLANT |  |  | - | 09:10 S/U CGT #4, then online the Unit at 09:46. |  | 1 | 9:10 | Morning | Wednesday | 2016 | 5
3372 | 2016-05-25 10:17 | 2016-05-25 10:17 | MINAS POWER PLANT |  |  | - | Off line MGT #6, then S/D the Unit for S/B. |  | 1 | 10:17 | Morning | Wednesday | 2016 | 5
3373 | 2016-05-25 14:15 | 2016-05-25 14:15 | 13.8KV ROKAN FEEDER #2 | Fair | Planned Maintenance | 54 | 14:15 Manually opened and rack out Rokan VCB fdr #2. To repairing broken jumpers near pole of LBS #RT-01. 16:20 Closed LBS #RT-01. (Transfered all load of Rokan fdr #2 to Rokan fdr #4 for PM service) (After repairing jumper above) Cause: Planned Maintenance. | 123 | 1 | 14:15 | Afternoon | Wednesday | 2016 | 5
3374 | 2016-05-25 17:10 | 2016-05-25 17:10 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | 17:10 It was reported b/o fuse for Tx o/p #01-3-26. (C.Duri fdr #6) 17:45 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-3-26 Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3211045 | 1 | 17:10 | Afternoon | Wednesday | 2016 | 5
3375 | 2016-05-26 | 2016-05-26 | 13.8KV DURI FIELD FEEDER #4 | Rain | Animal | 0 | Duri Field ACB fdr #4 T/R 1x Ctr: 468-469 R/F: 51N. Patrolled the line & found, a Dead Monkey under pole #07-V1-04. Cause: Animal. | 3211045 | 1 | 0:00 | Night | Thursday | 2016 | 5
3376 | 2016-05-26 06:14 | 2016-05-26 06:14 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Duri Field ACB fdr #1 T/R 1x Ctr: 630-631 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3211045 | 1 | 6:14 | Morning | Thursday | 2016 | 5
3377 | 2016-05-26 07:00 | 2016-05-26 07:00 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Low mega-ohm reading | 25 | 07:00 It was reported b/o fuse for Tx at Well Petapahan #52. 15:00 Checked & found, @1, @2 b/o 3.5SF fuses for 150Kva Tx at Well Petapahan #52. TTR tested & megger the Tx, found Low mega ohm reading Tx. Replaced 150Kva Tx with 400Kva Tx VSD at well Petapahan#52 & Energized the Tx. Cause: Transformer Failure. (Low Megga ohm reading) | 3211046 | 1 | 7:00 | Morning | Thursday | 2016 | 5
3378 | 2016-05-26 09:55 | 2016-05-26 09:55 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Secondary Cable | 0 | 09:55 It was reported b/o fuse for Tx o/p #05-P1-12. (C.Duri fdr #15) 10:30 Checked & found, @1 b/o fuse for 112.5Kva Tx o/p #05-P1-12. Cause: Broken Secondary Cable. (The broken Secondary cable is not replaced yet) | 3211045 | 1 | 9:55 | Morning | Thursday | 2016 | 5
3379 | 2016-05-26 09:55 | 2016-05-27 11:55 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Secondary Cable | 0 | Replaced Sec Cable 112.5 Kva Tx , then energized the Tx. | 3211045 | 1 | 9:55 | Morning | Thursday | 2016 | 5
3380 | 2016-05-26 15:08 | 2016-05-26 15:08 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 30 | C.Duri fdr #1 Load dropped 63A (242-179A). Not checked yet. | 3211045 | 1 | 15:08 | Afternoon | Thursday | 2016 | 5
3381 | 2016-05-26 15:08 | 2016-05-30 19:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 30 | Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/R 1x Ctr: 176-177. Patrolled the line, but found nothing. Cause: Unidentified. | 3211045 | 1 | 15:08 | Afternoon | Thursday | 2016 | 5
3382 | 2016-05-26 15:44 | 2016-05-26 15:44 | DURI POWER PLANT |  |  | - | Off Line DGT #7, then S/D the Unit for S/B. |  | 1 | 15:44 | Afternoon | Thursday | 2016 | 5
3383 | 2016-05-27 08:03 | 2016-05-27 08:03 | 13.8KV S. BALAM FEEDER #1 | Fair | Pin Insulator | 0 | SO.Balam fdr #1 Load dropped 66A (95-29A). So.Balam GFPC T/R 1x. Not checked yet. | 3211045 | 1 | 8:03 | Morning | Friday | 2016 | 5
3384 | 2016-05-27 08:03 | 2016-05-28 14:31 | 13.8KV S. BALAM FEEDER #1 | Fair | Pin Insulator | 0 | Checked & found, Recl. 16Z-25 (So.Balam fdr #1) T/R 1x Ctr: 22-23. Patrolled the line & found, @1 broken Pin insulator o/p #15Y-26. Cause: Pin Insulator. | 3211045 | 1 | 8:03 | Morning | Friday | 2016 | 5
3385 | 2016-05-27 09:25 | 2016-05-27 09:25 | 13.8KV PUNGUT FEEDER #1 | Fair | Transformer Failure | 35 | 09:25 It was reported b/o fuse for Tx at Well Pungut #35. (Pungut fdr #2) 14:50 Checked & found, @2,@3 b/o 7.8SF fuses for 225Kva Tx at Well Pungut #35. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Transformer Failure. (Low Megger reading) (The Tx Failure is not replaced yet) | 3211045 | 1 | 9:25 | Morning | Friday | 2016 | 5
3386 | 2016-05-27 09:25 | 2016-05-28 11:00 | 13.8KV PUNGUT FEEDER #1 | Fair | Transformer Failure | 35 | Replaced 225Kva Tx failure with 100Kva Tx at Well Pungut #35, then energized the Tx. Cause: Transformer Failure. | 3211045 | 1 | 9:25 | Morning | Friday | 2016 | 5
3387 | 2016-05-27 19:08 | 2016-05-27 19:08 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr #1 load dropped 49A (246-197A). Not checked yet. | 3211045 | 1 | 19:08 | Night | Friday | 2016 | 5
3388 | 2016-05-27 19:08 | 2016-05-28 19:13 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 08-L3-32 (C.Duri fdr #1) T/R 2x Ctr: 504-506. Patrolled the line, but nothing found. Cause: Unidentified. | 3211045 | 1 | 19:08 | Night | Friday | 2016 | 5
3389 | 2016-05-27 21:42 | 2016-05-27 21:42 | 13.8KV S. BALAM FEEDER #1 | Fair | Transformer Failure | 2 | It was reported b/o fuse for Tx at Well So.Balam #354. Not checked yet. | 3211045 | 1 | 21:42 | Night | Friday | 2016 | 5
3390 | 2016-05-27 21:42 | 2016-05-28 10:30 | 13.8KV S. BALAM FEEDER #1 | Fair | Transformer Failure | 2 | Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well So.Balam #354. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Transformer Failure. (Low megger reading) (The Tx failure is not replaced yet) | 3211045 | 1 | 21:42 | Night | Friday | 2016 | 5
3391 | 2016-05-27 21:42 | 2016-05-29 11:25 | 13.8KV S. BALAM FEEDER #1 | Fair | Transformer Failure | 2 | Replaced 150Kva Tx with the same size at well So.Balam#354. Cause: Transformer Failure. | 3211045 | 1 | 21:42 | Night | Friday | 2016 | 5
3392 | 2016-05-28 06:47 | 2016-05-28 06:47 | 13.8KV PUNGUT FEEDER #1 | Fair | Pin Insulator | 52 | 06:47 Pungut OCB fdr #1 T/O. (On block for RIG APS #3516 at Pungut #11) 06:58 Blocked & closed Pungut OCB fdr #1, Ok. 08:30 Checked & found, Pungut OCB fdr #1 T/O. Ctr: 348-349 R/F: 51N. Patrolled the line & found, @1 F/O Pin Insulator o/p #45BP-48. Cause: Pin Insulator. | 3211045 | 1 | 6:47 | Morning | Saturday | 2016 | 5
3393 | 2016-05-28 07:40 | 2016-05-28 07:40 | 13.8KV 6DN FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 07:40 It was reported b/o fuse for Tx at Well #5D-85. (6DN fdr #2) 15:45 Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well #5D-85. Performed Test TTR, Megger the Tx & found, normal. (Good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3211046 | 1 | 7:40 | Morning | Saturday | 2016 | 5
3394 | 2016-05-28 15:03 | 2016-05-28 15:03 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning | 8 | Ketigul VCB fdr#3 T/R 1x. Not checked yet. | 3211045 | 1 | 15:03 | Afternoon | Saturday | 2016 | 5
3395 | 2016-05-28 15:03 | 2016-05-29 18:00 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning | 8 | Checked & found, Ketigul VBC fdr #3 T/R 1x Ctr: 170-171 R/F: 51N. Patrolled the line & found, @1,@2 broken L/As o/p #31AR-03. Cause: Lightning. | 3211045 | 1 | 15:03 | Afternoon | Saturday | 2016 | 5
3396 | 2016-05-29 09:44 | 2016-05-29 09:44 | MINAS POWER PLANT |  |  | - | 09:44 S/U MGT #5, then on line the Unit at 10:02. |  | 1 | 9:44 | Morning | Sunday | 2016 | 5
3397 | 2016-05-29 14:14 | 2016-05-29 14:14 | MINAS POWER PLANT |  |  | - | 14:14 S/U MGT #3, then on line the Unit at 14:36. |  | 1 | 14:14 | Afternoon | Sunday | 2016 | 5
3398 | 2016-05-29 15:19 | 2016-05-29 15:19 | MINAS POWER PLANT |  |  | - | 15:19 S/U MGT #4, then on line the Unit at 15:40. |  | 1 | 15:19 | Afternoon | Sunday | 2016 | 5
3399 | 2016-05-29 18:45 | 2016-05-29 18:45 | 13.8KV BEKASAP FEEDER #3 | Heavy Rain | Lightning | 64 | Bekasap fdr #3 Load dropped 97A (156-59A). Not checked yet. | 3211045 | 1 | 18:45 | Afternoon | Sunday | 2016 | 5
3400 | 2016-05-29 18:45 | 2016-05-31 13:50 | 13.8KV BEKASAP FEEDER #3 | Heavy Rain | Lightning | 64 | Checked & found, Recl.38BD-18 (Bekasap fdr #3) T/R 1x Ctr: 79-80. Patrolled the line & found, @2 broken L/A on TP of Well Bekasap #58. Cause: Lightning. | 3211045 | 1 | 18:45 | Afternoon | Sunday | 2016 | 5
3401 | 2016-05-29 18:52 | 2016-05-29 18:52 | 13.8KV CENTRAL DURI FEEDER #1 | Heavy Rain | Lightning | 269 | 18:52 C.Duri fdr #1 Load dropped 55A (245-190A). 22:06 Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/SO. Ctr: 232-233. 22:09 Blocked & closed Recl. 38AS-09, Ok. Then released the block. The line is not patrolled yet. | 3211045 | 1 | 18:52 | Afternoon | Sunday | 2016 | 5
3402 | 2016-05-29 18:52 | 2016-05-30 07:10 | 13.8KV CENTRAL DURI FEEDER #1 | Heavy Rain | Lightning | 269 | Patrolled the line at downstream of Recl. 38AS-09, but found nothing. Cause: Suspected by Lightning. | 3211045 | 1 | 18:52 | Afternoon | Sunday | 2016 | 5
3403 | 2016-05-29 19:09 | 2016-05-29 19:09 | CENTRAL DURI POWER PLANT | Heavy Rain | Under investigation | 0 | CDGT #4 Tripped By Alarm: 125V DC-Ground. (Status - NSB) Cause: Under Investigation. | 3211045 | 1 | 19:09 | Night | Sunday | 2016 | 5
3404 | 2016-05-30 04:59 | 2016-05-30 04:59 | 13.8KV 6D FEEDER #1 | Fair | Unidentified | 38 | 6D OCB fdr #1 T/R 1x. Not checked yet. | 3211046 | 1 | 4:59 | Morning | Monday | 2016 | 5
3405 | 2016-05-30 04:59 | 2016-02-06 13:30 | 13.8KV 6D FEEDER #1 | Fair | Unidentified | 38 | Checked & found, 6D OCB fdr #1 T/R 1x Ctr: 307-308 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3211046 | 1 | 4:59 | Morning | Monday | 2016 | 5
3406 | 2016-05-30 09:42 | 2016-05-30 09:42 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 6 | 09:42 It was reported b/o fuse for Tx o/p #07-V5-23. (D.Field fdr #4) 11:30 Checked & found, @1,@2 b/o 3.1Sf fuses for 112.5Kva Tx o/p #07-V5-23 Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3211045 | 1 | 9:42 | Morning | Monday | 2016 | 5
3407 | 2016-05-30 10:38 | 2016-05-30 10:38 | 13.8KV PUNGUT FEEDER #2 | Fair | Animal | 15 | 10:38 It was reported b/o fuse for Tx at Well Tandun #04. (Pungut fdr #2) 14:00 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Tandun #04. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Squirrel) | 3211045 | 1 | 10:38 | Morning | Monday | 2016 | 5
3408 | 2016-05-30 13:17 | 2016-05-30 13:17 | MINAS POWER PLANT |  |  | - | 13:17 S/U MGT #8, then online the Unit at 13:34. |  | 1 | 13:17 | Afternoon | Monday | 2016 | 5
3409 | 2016-05-30 13:45 | 2016-05-30 13:45 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 13:45 It was reported b/o fuse for Tx o/p #10-J8-12. (N.Duri fdr #2) 15:03 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #10-J8-12 Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3211045 | 1 | 13:45 | Afternoon | Monday | 2016 | 5
3410 | 2016-05-30 14:20 | 2016-05-30 14:20 | MINAS POWER PLANT |  |  | - | 14:20 S/U MGT #7, then online the Unit at 14:37. |  | 1 | 14:20 | Afternoon | Monday | 2016 | 5
3411 | 2016-05-30 14:21 | 2016-05-30 14:21 | 8 CHARLIE SUBSTATION | Fair | Planned Maintenance | 244 | 13:17 Perform Switching to Manual S/D 28MVA TX-2 8C Substation: -To dismantling transition plate on Tx terminal connection. -To transferring Load MSU-1 to 8C TX-2. (Normailze load of 8C Tx-2) 14:21 GS-2 S/D 2 unit WIPs & S/D some wells under feeders below: 8D fdr #3 Load dropped 30A (173-143A). 8C fdr #3 Load dropped 34A (239-205A). 8C fdr #2 Load dropped 13A (189-176A). 17:17 Energized 8C 28MVA TX-2 at 8C Substation, and S/D 28MVA MSU TX-1. Cause: Planned Maintenance. | 123 | 1 | 14:21 | Afternoon | Monday | 2016 | 5
3412 | 2016-05-30 16:50 | 2016-05-30 16:50 | MINAS POWER PLANT |  |  | - | 16:50 S/U MGT #6, then On line the Unit at 17:10. |  | 1 | 16:50 | Afternoon | Monday | 2016 | 5
3413 | 2016-05-30 17:15 | 2016-05-30 17:15 | CENTRAL DURI POWER PLANT |  |  | - | 17:15 S/U CGT #4, then On line the Unit at 17:34. |  | 1 | 17:15 | Afternoon | Monday | 2016 | 5
3414 | 2016-05-30 18:00 | 2016-05-30 18:00 | NORTH DURI POWER PLANT |  |  | - | 18:00 Off line NDC-CT #2, then S/D the Unit for S/B. (Prior to Turbine off line Washing program) 31-May-2016. 15:50 S/U NDC-CT #2, then online the Unit at 16:19. (After Performed off line washing program) |  | 1 | 18:00 | Afternoon | Monday | 2016 | 5
3415 | 2016-05-31 07:53 | 2016-05-31 07:53 | MINAS POWER PLANT |  |  | - | 07:53 Offline MGT #2, then S/D the Unit for S/B. |  | 1 | 7:53 | Morning | Tuesday | 2016 | 5
3416 | 2016-05-31 07:58 | 2016-05-31 07:58 | MINAS POWER PLANT |  |  | - | 07:58 Offline MGT #5, then S/D the Unit for S/B. |  | 1 | 7:58 | Morning | Tuesday | 2016 | 5
3417 | 2016-05-31 10:09 | 2016-05-31 10:09 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Unidentified | 24 | Petapahan OCB fdr #1 T/R 1x. Not checked yet. | 3211046 | 1 | 10:09 | Morning | Tuesday | 2016 | 5
3418 | 2016-05-31 10:09 | 2016-01-06 07:30 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Unidentified | 24 | Checked & found, Petapahan OCB fdr #1 T/R 1x Ctr: 211-212 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3211046 | 1 | 10:09 | Morning | Tuesday | 2016 | 5
3419 | 2016-05-31 15:50 | 2016-05-31 15:50 | NORTH DURI POWER PLANT |  |  | - | 15:50 S/U NDC-CT #2, then online the Unit at 16:19. (After Performed off line washing program) |  | 1 | 15:50 | Afternoon | Tuesday | 2016 | 5
3420 | 2016-05-31 20:39 | 2016-05-31 20:39 | NORTH DURI POWER PLANT |  |  | - | 20:39 Offline NDC-CT #3, then S/D the Unit for offline wash. 01-June-2016. 16:05 S/U NDC-CT #3, then Online the Unit at 17:24. (After Perform Off Line washing program) 19:10 Offline NDC-CT #3, then S/D the Unit due to high vibration. (Prepare for Fast Load Start) 20:24 S/U NDC-CT #3, then online the Unit at 20:50. |  | 1 | 20:39 | Night | Tuesday | 2016 | 5
3421 | 2016-01-06 03:54 | 2016-01-06 03:54 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 0 | 03:54 C.Duri ACB fdr #15 T/LO. Ctr: 362-366 R/F: 50@2,@3. 05:19 Patrolled the line, but found nothing. 05:22 Blocked & closed C.Duri ACB fdr #15, but tripped again. Ctr: 366-367 R/F: 50@2,@3. 06:13 Re-patrolled the line & found: -a Dead Bird (Hornbill) touched @2,@3 source & load side of Recl. 06-R1-02. -Also found @2,@3 broken Recloser Bushings of Recloser above. Then isolated the Recloser by opening its visual opening switches. 06:19 Blocked & closed C.Duri ACB fdr #15, Ok. Then released the block. 10:00 Opened HLC of load side jumpers of Recl. 06-R1-02 to isolate the Recloser. 10:34 Closed LBS #06-R1-21, (load under Recl. 06-R1-02) transferred to C.Duri fdr #14. Cause: Animal. (Hornbill) | 3227452 | 1 | 3:54 | Night | Wednesday | 2016 | 1
3422 | 2016-01-06 10:04 | 2016-01-06 10:04 | 13.8KV 3D FEEDER #4 | Fair | Tree | 126 | 10:04 3D OCB fdr #4 T/LO. 3D fdr #3 Load dropped 91A (148-57A). 11:40 Checked & found, 3D OCB #4 T/LO. Ctr: 548-552 R/F: 50/51@2 & 50@3. Also found Oil Leak around OCB, but the bushing is good. 11:50 Blocked & Closed OCB fdr #4. Ok. Then Released the Block Patrolled the line, but found nothing. 14:05 Found, Recl. 2D-14 (3D fdr #4) T/LO. Ctr: 36-40. Blocked & closed Recl. 2D-14, Ok. Then released the Block. Patrolled the line, but found nothing. 17:00 It was checked the load of 3D fdr #4, but 63A more to normal load (223A) Checked & found, Recl. 2D-33 (D/S of Recl. 2D-14) T/LO. Ctr: 23-27. Patrolled the line & found, fall down Tree & hit to @3 conductor between poles #NN. 17:30 Blocked & closed Recl. 2D-33, Ok. Then released the Block. (After clearing the Tree above) Cause: Tree. (Touching to @3 conductor) | 3227455 | 1 | 10:04 | Morning | Wednesday | 2016 | 1
3423 | 2016-01-06 16:05 | 2016-01-06 16:05 | NORTH DURI POWER PLANT |  |  | - | 16:05 S/U NDC-CT #3, then Online the Unit at 17:24. (After Performing Off Line wash program) 19:10 Offline NDC-CT #3, then S/D the Unit due to high vibration. (Prepare for Fast Load Start) 20:24 S/U NDC-CT #3, then online the Unit at 20:50. |  | 1 | 16:05 | Afternoon | Wednesday | 2016 | 1
3424 | 2016-01-06 17:48 | 2016-01-06 17:48 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Others | 0 | 17:48 NKBS fdr #5 Load dropped 87A (147-60A). KB-GS reported 3 unit WIPs tripped & could not be started. 18:36 Manual opened CKBS VCB fdr #6, then Closed at: 19:49. (Its requested by KB-GS to anticipate spills) No Prod. loss charged to PGT. Cause: Others. (WIP Problem) | 3227455 | 1 | 17:48 | Afternoon | Wednesday | 2016 | 1
3425 | 2016-02-06 | 2016-02-06 | NORTH DURI POWER PLANT |  |  | - | 00:00 Offline NDC-CT #1, then S/D the Unit for offline wash. 17:49 S/U NDC CT#1, then On Line the Unit at 18:00 (After perform On Line Washing program) |  | 1 | 0:00 | Night | Saturday | 2016 | 2
3426 | 2016-02-06 17:49 | 2016-02-06 17:49 | NORTH DURI POWER PLANT |  |  | - | 17:49 NDC CT#1 S/U , On Line the Unit at 18:00 After perform On Line Wash. |  | 1 | 17:49 | Afternoon | Saturday | 2016 | 2
3427 | 2016-02-06 23:35 | 2016-02-06 23:35 | 13.8KV 6D FEEDER #2 | Fair | Unidentified | 31 | 6D fdr #2 Load dropped 142A (219-77A). Not checked yet. | 3227455 | 1 | 23:35 | Night | Saturday | 2016 | 2
3428 | 2016-02-06 23:35 | 2016-03-06 16:15 | 13.8KV 6D FEEDER #2 | Fair | Unidentified | 31 | Checked & found, Recl. 6D-298 (6D fdr #2) T/R 1x Ctr: 39-40. Patrolled the line, but found nothing. Cause: Unidentified. | 3227455 | 1 | 23:35 | Night | Saturday | 2016 | 2
3429 | 2016-03-06 06:38 | 2016-03-06 06:38 | 13.8KV BATANG FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 06:38 It was reported b/o fuse for Tx at Well Rantaubais #22. (Batang fdr #2) 14:24 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Rantaubais #22. Replaced b/o fuse above with the same size, the energized the Tx. Cause: Unidentified (Fuse). | 3227452 | 1 | 6:38 | Morning | Sunday | 2016 | 3
3430 | 2016-03-06 10:20 | 2016-03-06 10:20 | CENTRAL DURI POWER PLANT |  |  | - | 10:20 Offline CGT#1, then S/D the Unit for S/B. (Prior to Fixing the failure flame Scanner) 05-June-2016. 08:30 S/U CGT #1, then On line the Unit at 08:58. (After Fixing Flame scanner Failure) |  | 1 | 10:20 | Morning | Sunday | 2016 | 3
3431 | 2016-03-06 10:30 | 2016-03-06 10:30 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 6 | 10:30 It was reported No power at Well #10D-14, #9D-99, #10D-16 & #10D-24. (8C fdr #1) 11:50 Checked & found, Recl. 9D-111 (8C fdr #1) T/SO. Ctr: 1232-1233. Patrolled the Line, but found nothing. Blocked & Closed the Recl. 9D-111, Ok. Then released the block. Cause: Unidentified. | 3227455 | 1 | 10:30 | Morning | Sunday | 2016 | 3
3432 | 2016-03-06 10:30 | 2016-03-06 10:30 | MINAS POWER PLANT |  |  | - | 10:30 Offline MGT #4, then S/D the Unit for S/B. |  | 1 | 10:30 | Morning | Sunday | 2016 | 3
3433 | 2016-03-06 10:32 | 2016-03-06 10:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 2 | C.Duri fdr #1 Load ropped 69A (244-175A). Not checked yet. | 3227452 | 1 | 10:32 | Morning | Sunday | 2016 | 3
3434 | 2016-03-06 10:32 | 2016-07-06 17:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 2 | Checked & found, Recl. 09-L7-01 (C.Duri fdr #1) T/R 3x Ctr: 440-443. Patrolled the line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 10:32 | Morning | Sunday | 2016 | 3
3435 | 2016-03-06 11:00 | 2016-03-06 11:00 | MINAS POWER PLANT |  |  | - | 11:00 Offline MGT #6, then S/D the Unit for S/B. |  | 1 | 11:00 | Morning | Sunday | 2016 | 3
3436 | 2016-03-06 11:10 | 2016-03-06 11:10 | MINAS POWER PLANT |  |  | - | 11:10 Offline MGT#7, then S/D the Unit for S/B. |  | 1 | 11:10 | Morning | Sunday | 2016 | 3
3437 | 2016-03-06 13:30 | 2016-03-06 13:30 | MINAS POWER PLANT |  |  | - | 13:30 Offline MGT #8, then S/D the Unit for S/B. |  | 1 | 13:30 | Afternoon | Sunday | 2016 | 3
3438 | 2016-03-06 23:14 | 2016-03-06 23:14 | 13.8KV BEKASAP FEEDER #2 | Fair | Unidentified | 32 | Bekasap fdr #2 Load dropped 83A (138-57A). Not checked yet. | 3227452 | 1 | 23:14 | Night | Sunday | 2016 | 3
3439 | 2016-03-06 23:14 | 2016-06-06 08:30 | 13.8KV BEKASAP FEEDER #2 | Fair | Unidentified | 32 | Checked & found, Recl. 37BD-12 (Bekasap fdr #2) T/R 1x Ctr: 170-171. Patrolled the line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 23:14 | Night | Sunday | 2016 | 3
3440 | 2016-04-06 00:48 | 2016-04-06 00:48 | 13.8KV 4D FEEDER #2 | Fair | Unidentified | 35 | 00:48 4D OCB fdr #2 T/R 1x. 4D fdr #3 Load dropped 44A (71-27A). (4D Substation RTU failed at this time) 16:42 Checked & found, 4D OCB fdr #2 T/R 1x Ctr: 213-214 R/F: 50@2,@3. Patriolled the line, but nothing found. Cause: Unidentified. | 3227455 | 1 | 0:48 | Night | Wednesday | 2016 | 4
3441 | 2016-04-06 07:03 | 2016-04-06 07:03 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 0 | 07:03 Sintong fdr #2 Load dropped 107A (220-113A). 14:00 Checked & found, Recl. 28AF-17 (Sintong fdr #2) T/R 1x Ctr: 430-431 R/F: 50@1,@2. Patrolled the line & found, a Dead monkey under TP of Well Mutiara #1. Cause: Animal. (Monkey) | 3227452 | 1 | 7:03 | Morning | Wednesday | 2016 | 4
3442 | 2016-04-06 10:42 | 2016-04-06 10:42 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 10:42 It was reported b/o fuse for Tx o/p #39AU-01. (C.Duri fdr #1) 15:30 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #39AU-01. Replaced b/o fuse above with the same size & Energized the Tx. Cause: Unidentified (Fuse). | 3227452 | 1 | 10:42 | Morning | Wednesday | 2016 | 4
3443 | 2016-04-06 16:20 | 2016-04-06 16:20 | 13.8KV 4D FEEDER #3 | Fair | Dead End Insulator | 7 | 4D OCB fdr #3 T/R 1x. Not checked yet. | 3227455 | 1 | 16:20 | Afternoon | Wednesday | 2016 | 4
3444 | 2016-04-06 16:20 | 2016-05-06 17:03 | 13.8KV 4D FEEDER #3 | Fair | Dead End Insulator | 7 | Checked & found, 4D OCB fdr #3 T/R 1x Ctr: 357-358 R/F: 51N. Patrolled the line & found, @3 broken Dead end Insulator o/p #3D-26. Cause: Dead end Insulator. | 3227455 | 1 | 16:20 | Afternoon | Wednesday | 2016 | 4
3445 | 2016-04-06 20:13 | 2016-04-06 01:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Tree | 1095 | 20:13 C.Duri fdr #1 Load dropped 148A (245-97A) 21:45 Checked & found, Recl. SBB-07-R1 (C.Duri fdr #1) T/SO. Ctr: 528-529. Then Blocked & closed Recl. SBB-07-R1, but failed to close. Patrolled the line, but found nothing. 23:00 Opened LBS o/p #08-L8-09. 23:03 Blocked & closed Recl. SBB-07-R1, Ok. 23:50 Manually opened Recl. 09-L7-01, but failed. (Control problem) Manually opened Recl. 08-L3-32B, then closed at 00:28. Manually opened Recl. 08-L5-35, then closed at 00:22. Manually opened Recl. 08-L7-38. 23:59 Closed LBS o/p #08-L8-09. Patrolled & found, high danger Trees touching power line between poles #08-L7-20 & 21. 05-June-2016. 01:00 Cut high danger Trees beetwen poles #08-L7-20 & #08-L7-21. 01:30 Open visual opening of Recl. 08-L7-38. 01:34 Closed LBS o/p #08-L7-06. (to Transferring load C.Duri fdr #1 to C.Duri fdr #2) 01:35 Patrolled the line under Recl. 09-L7-01. (C.Duri fdr #1), but found nothing. (Patrolled the line would be continued in the morning) 08:00 Re-patrolled the line under Recl. 09-L7-01, but found nothing. Checked & trouble shoot Recl. 09-L7-01 & found, closing Switch problem, then Fixed it. 09:00 Blocked & Closed Recl. 09-L7-01, Ok. (After functioning test close & open the Recloser) Cause: Tree. | 3227452 | 1 | 20:13 | Night | Wednesday | 2016 | 4
3446 | 2016-05-06 08:30 | 2016-05-06 08:30 | CENTRAL DURI POWER PLANT |  |  | - | 08:30 S/U CGT #1, then On line the Unit at 08:58. (After Fixing Flame scanner Failure) |  | 1 | 8:30 | Morning | Friday | 2016 | 5
3447 | 2016-05-06 23:41 | 2016-06-06 00:03 | 13.8KV MINAS FEEDER #2 | Fair | Others | 6 | 23:41 Minas ACB fdr #2 T/SO. Ctr: 58-59 R/F: 50@1,@2. Patrolled the line, but found nothing. 06-June-2016. 00:03 Blocked & closed Minas ACB fdr #2, but failed. Re-patrolled the line, but found nothing. Open Isolation switch for 2500Kva Tx at Minas Mini Substation. (Minas ACB fdr #2) 01:32 Blocked & Closed Minas ACB fdr #2, Ok. 02:00 Open Disconnecting Switch for 2500Kva Tx at 4160V Mini Substation. (Minas fdr #2) (Transferred load Minas Housing / Minas fdr #2 to Minas fdr #6) 02:15 Closed Line Switch o/p #HGU-3a. (Warehouse, Commisary, Akasia, Al-Fatah are still off) Cause: Other (Dirty 4.16kV panel of housing feeder and industrial feeder of Mini Substation). | 3227455 | 1 | 23:41 | Night | Friday | 2016 | 5
3448 | 2016-06-06 00:03 | 2016-06-06 00:03 | MINAS SWITCH YARD | Fair | Unidentified | 0 | 00:03 115KV Minas SWY OCB #23 T/O. 00:09 Closed 115KV Minas SWY OCB #23. Not checked yet. | 3227455 | 1 | 0:03 | Night | Monday | 2016 | 6
3449 | 2016-06-06 00:03 | 2016-12-06 17:43 | MINAS SWITCH YARD | Fair | Unidentified | 0 | Checked & found, 115KV MSWY OCB #23 T/SO. Ctr: 99944-99945 R/F: Not Appeare. Patrolled the line nothing found. Cause: Unidentified. | 3227455 | 1 | 0:03 | Night | Monday | 2016 | 6
3450 | 2016-06-06 01:36 | 2016-06-06 01:36 | 13.8KV 8C FEEDER #4 | Fair | Unidentified | 23 | 8C VCB fdr #4 T/R 1x. Not checked yet. | 3227455 | 1 | 1:36 | Night | Monday | 2016 | 6
3451 | 2016-06-06 01:36 | 2016-08-06 15:10 | 13.8KV 8C FEEDER #4 | Fair | Unidentified | 23 | Checked & found, 8C VCB fdr #4 T/R 1x Ctr: 578-579 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3227455 | 1 | 1:36 | Night | Monday | 2016 | 6
3452 | 2016-06-06 09:25 | 2016-06-06 09:25 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 0 | 09:25 It was reported b/o fuse for Tx at CSS Area-6. 11:05 Checked & found, @2,@3 b/o 100K fuses for 1500Kva Tx at CSS Area-6. 15:00 Performed TTR, Megger test the Tx & found, normal. (good reading) Replaced b/o fuse above with same size & energize the Tx. Cause: Unindentified (Fuse). | 3227452 | 1 | 9:25 | Morning | Monday | 2016 | 6
3453 | 2016-06-06 09:48 | 2016-06-06 09:48 | MINAS POWER PLANT |  |  | - | 09:48 S/U MGT #8, then Online the Unit at 10:06. 15:00 Off line MGT #8, then S/D the Unit for S/B. |  | 1 | 9:48 | Morning | Monday | 2016 | 6
3454 | 2016-06-06 10:15 | 2016-06-06 10:15 | MINAS POWER PLANT |  |  | - | 10:15 Off line MGT #9, then S/D the Unit for S/B. (Prior to replacing Generator Rotor) |  | 1 | 10:15 | Morning | Monday | 2016 | 6
3455 | 2016-06-06 10:20 | 2016-06-06 10:20 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 10:20 It was reported b/o fuse for Tx o/p #04-03-08. 18:00 Checked & found, @2,@3 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-03-08. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3227452 | 1 | 10:20 | Morning | Monday | 2016 | 6
3456 | 2016-06-06 23:41 | 2016-06-06 23:41 | 13.8KV MINAS FEEDER #2 | Fair | Dead End Insulator | 0 | 23:41 Minas ACB fdr #2 T/SO. Ctr: 58-59 R/F: 51@1,@2. Patrolled the line, but found nothing. 07-June-2016. 00:03 Blocked & closed Minas ACB fdr #2, but T/O again. Re-patrolled the line, but found nothing. Then isolated Minas Mini Substation by opening fuses for 2500Kva Tx 01:32 Blocked & closed Minas ACB fdr #2, Ok. 02:00 Dismanthled 2500Kva Tx at Minas Mini Substation. (Load 4.16KV Minas Ind. & Hsg fdrs) Transferred 4.16KV Minas Ind. & Hsg. to 4.16KV Minas CEWA Substation. 02:15 Closed LBS #HGU-3A. 04:20 Closed LBS #1-JT-1. (4.16KV Minas Ind. & Hsg. fdrs fed by Minas CEWA Substation) 09:10 Patrolled the line & found, @1,@2,@3 broken Dead end Insulators o/p #1IZ-07. Cause: Dead end Insulator. | 3227455 | 1 | 23:41 | Night | Monday | 2016 | 6
3457 | 2016-07-06 10:52 | 2016-07-06 10:52 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 38 | 10:52 It was reported b/o fuse for Tx at Well Ubi #24. 16:45 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Ubi #24. Performed TTR, Megger test the Tx & found, Low mega ohm reading Tx. Cause: Tx Failure. (Low megger reading) (The Tx failure is not replaced yet) | 3227452 | 1 | 10:52 | Morning | Wednesday | 2016 | 7
3458 | 2016-07-06 10:52 | 2016-08-06 11:28 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 38 | Replaced 150Kva Tx failure with same size and energized the Tx. Cause: Tx Failure. | 3227452 | 1 | 10:52 | Morning | Wednesday | 2016 | 7
3459 | 2016-07-06 11:16 | 2016-07-06 11:16 | 115KV NELLA SW. STA - PINANG LINE | Fair | Planned Maintenance | 114 | 11:16-12:44 Manually opened 115KV Nella GCB #27. (115KV Nella - Pinang line) Switching to energizing Pinang Substation, after general servicing Power Tx. Cause: Planned Maintanance. | 123 | 1 | 11:16 | Morning | Wednesday | 2016 | 7
3460 | 2016-07-06 13:36 | 2016-07-06 13:36 | 3 DELTA SUBSTATION | Fair | Planned Maintenance | 203 | 13:36-16:29 Switching to Open 13.8KV 3D OCB fdr #4. (20 wells were off) And also transferred load of 3D fdr #3 & fdr #4 to other fdrs. 13:40-16:19 Manually opened 115KV 3D C/S-TX #1. To replacing Interrupter of 115KV C/S-TX #1 at 3D Substation. Cause: Planned Maintanance. | 123 | 1 | 13:36 | Afternoon | Wednesday | 2016 | 7
3461 | 2016-07-06 14:24 | 2016-07-06 14:24 | MINI CENDRAWASIH SUBSTATION | Fair | Dead End Insulator | 0 | Minas fdr #6 Load dropped 93A (272-179A). Not checked yet. | 3227455 | 1 | 14:24 | Afternoon | Wednesday | 2016 | 7
3462 | 2016-07-06 14:24 | 2016-09-06 09:10 | MINI CENDRAWASIH SUBSTATION | Fair | Dead End Insulator | 0 | Checked & found, 4.16KV Minas CEWA Substation T/R 1x Ctr: 694-695 R/F: 51G. Patrolled the line & found, @1,@2,@3 broken Dead end Insulators o/p #1IZ-07. Cause: Dead end Insulator. | 3227455 | 1 | 14:24 | Afternoon | Wednesday | 2016 | 7
3463 | 2016-07-06 22:20 | 2016-07-06 22:20 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Rangau fdr #2 Load dropped 80A (91-11A). Not checked yet. | 3227452 | 1 | 22:20 | Night | Wednesday | 2016 | 7
3464 | 2016-07-06 22:20 | 2016-08-06 17:15 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 4x Ctr: 130-134. Patrolled the line & found, @1 broken L/A o/p #23BD-01. Cause: Lightning. | 3227452 | 1 | 22:20 | Night | Wednesday | 2016 | 7
3465 | 2016-07-06 23:16 | 2016-07-06 23:16 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 22 | Libo OCB fdr #1 T/R 1x. Not checked yet. | 4337452 | 1 | 23:16 | Night | Wednesday | 2016 | 7
3466 | 2016-07-06 23:16 | 2016-08-06 16:15 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 22 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 369-370 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 4337452 | 1 | 23:16 | Night | Wednesday | 2016 | 7
3467 | 2016-07-06 23:22 | 2016-07-06 23:22 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Lightning | 0 | So.Balam VCB fdr #1 T/R 1x. Not checked yet. | 3227452 | 1 | 23:22 | Night | Wednesday | 2016 | 7
3468 | 2016-07-06 23:22 | 2016-09-06 08:20 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, So.Balam VCB fdr #1 T/R 1x Ctr: 342-343 R/F: 51N. Patrolled the line & found, @2 broken line jumper o/p #25AD-09. Cause: Lightning. | 3227452 | 1 | 23:22 | Night | Wednesday | 2016 | 7
3469 | 2016-07-06 23:26 | 2016-07-06 23:26 | 13.8KV 8C FEEDER #1 | Rain and Lightning | Lightning | 0 | 8C VCB fdr #1 T/R 1x. Not checked yet. | 3227455 | 1 | 23:26 | Night | Wednesday | 2016 | 7
3470 | 2016-07-06 23:26 | 2016-08-06 15:15 | 13.8KV 8C FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, 8C VCB fdr #1 T/R 1x Ctr: 640-641 R/F: 51@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3227455 | 1 | 23:26 | Night | Wednesday | 2016 | 7
3471 | 2016-08-06 14:57 | 2016-08-06 14:57 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 0 | 14:57 C.Duri fdr #1 Load dropped 55A (193-138 A). 15:56 Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/SO. Ctr: 249-250. Blocked & Closed Recl. 38AS-09, Ok. Then released the blocked. Patrolled the line & found, a Kite hang on @1,@2,@3 power line o/p #38AS-28. Cause: Others. (a Kite hang on power line) | 3227452 | 1 | 14:57 | Afternoon | Saturday | 2016 | 8
3472 | 2016-09-06 01:48 | 2016-09-06 01:48 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Transformer Failure | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3227452 | 1 | 1:48 | Night | Tuesday | 2016 | 9
3473 | 2016-09-06 01:48 | 2016-11-06 07:48 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Transformer Failure | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 82-83 R/F: 51N. Patrolled & found: -@1,@2,@3 b/o 7.8SF fuses for 300Kva Tx at HCT Office. -@2 broken Tx bushing. Cause: Tx failure. (This Tx is not replaced yet) | 3227452 | 1 | 1:48 | Night | Tuesday | 2016 | 9
3474 | 2016-09-06 01:48 | 2016-12-06 10:30 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Transformer Failure | 0 | Replaced 300Kva Tx failure with same size and energized the Tx. Cause: Tx failure. | 3227452 | 1 | 1:48 | Night | Tuesday | 2016 | 9
3475 | 2016-09-06 07:03 | 2016-09-06 07:03 | 13.8KV 8C FEEDER #1 | Fair | Powerline - Jumper | 65 | 07:03 8C fdr #1 Load dropped 13A ( 182-169A). 11:00 Checked & found, Recl. 9D-111 (8C fdr #1) T/SO. Ctr: 1233-1234. Patrolled the Line & found, @2 broken Jumper of L/A on TP of Well #10D-24. 11:02 Blocked & Closed Recl. 9D-111, Ok. Then released the Block. (After dismanthling broken L/A jumper above) Cause: Jumper | 3227455 | 1 | 7:03 | Morning | Tuesday | 2016 | 9
3476 | 2016-09-06 11:08 | 2016-09-06 11:08 | MINI CENDRAWASIH SUBSTATION | Fair | Dead End Insulator | 0 | 11:08 Minas fdr #6 Load Drop 61A (247-186A). Checked & found, 4.16KV Minas CEWA Substation feeder. T/R 1x Ctr: Not reported yet. Suspected caused by broken Dead end Insulator o/p #IZS-03. 15:25 Manually Opened LBS #HGU-3A. To replacing broken Dead end Insulator o/p #IZS-03. Normalized 4.16KV MInas Mini Substation fed by Minas fdr #2 from Minas fdr #6. 17:00 Manually open LBS #HGU-3A & Open LBS #1-JT-1. Closed 4.16KV Minas (Industrial) fdr #2. Last Ctr: 635. Closed 4.16KV Minas (Housing) fdr #2. Last Ctr: 720. Cause: Dead end Insulator. | 3227455 | 1 | 11:08 | Morning | Tuesday | 2016 | 9
3477 | 2016-09-06 18:00 | 2016-09-06 18:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Recloser | 0 | 18:00 Duri Field VCB fdr #4 T/LO. 18:20 Checked & found, Duri Field VCB fdr #4 T/LO. Ctr: 464-473 R/F: 51@1,@2,@3. Patrolled the Line & found, burnt out Bushing of Recl. 07-U3-02. Also found broken Visual Opening of Recloser above. 19:04 Bypassed Recl. 07-U3-02. (After opening HLC Source & Load side of the Recloser) 19:05 Blocked & Closed Duri Field VCB fdr #4, Ok. Then released the block. Cause: Recloser. (Bushing & Visual Opening) | 3227452 | 1 | 18:00 | Afternoon | Tuesday | 2016 | 9
3478 | 2016-10-06 13:40 | 2016-10-06 13:40 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Transformer Failure | 27 | 13:40 It was reported b/o fuse for Tx o/p #01-01-12. 14:50 Checked & found, @1,@2 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-01-12. Replaced @2 b/o fuse above with same size & energized the Tx, but b/o again. Cause: Tx Failure. (Low Megger Reading) (This Tx failure is not replaced yet) | 3227452 | 1 | 13:40 | Afternoon | Thursday | 2016 | 10
3479 | 2016-10-06 13:40 | 15/06/2016 14:00 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Transformer Failure | 27 | Replaced 112.5Kva Tx failure with the same size & energized the Tx o/p #01-1-12. Cause: Transformer failure. | 3227452 | 1 | 13:40 | Afternoon | Thursday | 2016 | 10
3480 | 2016-11-06 00:07 | 2016-11-06 00:07 | 13.8KV RANGAU FEEDER #1 | Fair | Unidentified (Fuse) | 176 | 00:07 Rangau OCB fdr #1 T/R 1x. 01:05 It was reported some Wells & Booster pumps were off at Rangau-GS. Cause: Not checked yet. To Maintain Liquid level Tank at Rangau-GS. 01:30 Manually open Rangau OCB fdr #2. 02:19 Checked & found, @2 b/o 14K fuse for 750Kva Tx at Rangau-GS. 03:25 Manually close Rangau OCB fdr #2 (After replacing b/o fuse above & energized the Tx) Cause: Unidentified (Fuse). | 3227452 | 1 | 0:07 | Night | Sunday | 2016 | 11
3481 | 2016-11-06 00:07 | 13/06/2016 17:37 | 13.8KV RANGAU FEEDER #1 | Fair | Unidentified (Fuse) | 176 | Checked & found, Rangau OCB fdr #1 T/R 1x Ctr: 09-10 R/F: 51GN. Patrolled the line & found, @2 b/o 14K fuse for 750Kva Tx at Rangau-GS. Cause: Unidentified (Fuse). | 3227452 | 1 | 0:07 | Night | Sunday | 2016 | 11
3482 | 2016-11-06 01:30 | 2016-11-06 01:30 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 0 | 01:30 Manually open Rangau OCB fdr #2. (To Maintain Liquid level Tank at Rangau-GS) 02:19 Checked & found, @2 b/o 14K fuse for 750Kva Tx at Rangau-GS. 03:25 Manually close Rangau OCB fdr #2 (After replacing b/o fuse above & energized the Tx) Cause: Unidentified (Fuse). (See report 11-June-2016 at 00:07) | 123 | 1 | 1:30 | Night | Sunday | 2016 | 11
3483 | 2016-11-06 07:17 | 2016-11-06 07:17 | 13.8KV 8C FEEDER #4 | Fair | Unidentified | 24 | 8C VCB fdr #4 T/R 1x. Not checked yet. | 3227455 | 1 | 7:17 | Morning | Sunday | 2016 | 11
3484 | 2016-11-06 07:17 | 2016-12-06 17:29 | 13.8KV 8C FEEDER #4 | Fair | Unidentified | 24 | Checked & found, 8C VCB fdr #4 T/R 1x Ctr: 579-580 R/F: 51N. Patrolled the line, but nothing found. Cause: Unidentified. | 3227455 | 1 | 7:17 | Morning | Sunday | 2016 | 11
3485 | 2016-11-06 09:10 | 2016-11-06 09:10 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Planned Maintenance | 131 | 08:26-11:42 Blocked Petapahan OCB fdr #1. 09:10-17:30 Cut jumpers on pole #30DA-11, to cut down trees under power line. (Wells PTH #07, 25, 23, 46 & #46 were off during this job done) Cause: Plan Maintenance. | 123 | 1 | 9:10 | Morning | Sunday | 2016 | 11
3486 | 2016-12-06 17:10 | 2016-12-06 17:10 | 13.8KV 3D FEEDER #8 | Drizzle | Unidentified | 52 | 3D OCB fdr #8 T/R 1x. Not checked yet. | 3227455 | 1 | 17:10 | Afternoon | Tuesday | 2016 | 12
3487 | 2016-12-06 17:10 | 16/06/2016 08:10 | 13.8KV 3D FEEDER #8 | Drizzle | Unidentified | 52 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 298-299 R/F: 50@1. Patrolled the line, but found nothing. Cause: Unidentified. | 3227455 | 1 | 17:10 | Afternoon | Tuesday | 2016 | 12
3488 | 2016-06-13 03:57 | 2016-06-13 03:57 | 13.8KV PEMATANG FEEDER #2 | Fair | Pin Insulator | 26 | 03:57 Pematang OCB fdr #2 T/R 1x ctr: 455-456 R/F 51N. Pematang fdr #1 Load Dropped 103A (150-47A). 17:45 Patrolled the line & found, @1 broken Pin insulator o/p #34BG-62. Cause: Pin Insulator. (Broken) | 3227452 | 1 | 3:57 | Night | Monday | 2016 | 6
3489 | 2016-06-14 14:26 | 2016-06-14 14:26 | 13.8KV 8C FEEDER #5 | Fair | Lightning Arrester | 0 | 8C VCB fdr #5 T/R 2x. Not checked yet. | 3227455 | 1 | 14:26 | Afternoon | Tuesday | 2016 | 6
3490 | 2016-06-14 14:26 | 2016-06-19 16:20 | 13.8KV 8C FEEDER #5 | Fair | Lightning Arrester | 0 | Checked & found, 8C VCB fdr #5 T/R 3x Ctr: 91-94 R/F: 51N. Patrolled the line & found, @2 broken L/A o/p #8C-247. Cause: Lightning Arrester. | 3227455 | 1 | 14:26 | Afternoon | Tuesday | 2016 | 6
3491 | 2016-06-14 14:26 | 2016-06-14 14:26 | 13.8KV 8C FEEDER #3 | Fair | Lightning Arrester | 45 | 14:26:01 8C fdr #3 Load dropped 118A (224-106A). Found, Recl. 8D-18A (8C fdr #3) T/LO. Ctr: Not reported yet. 14:30 Blocked & Closed Recl. 8D-18A (8C fdr #3), Ok. Then released the Block. The line is not patrolled yet. | 3227455 | 1 | 14:26 | Afternoon | Tuesday | 2016 | 6
3492 | 2016-06-14 14:26 | 2016-06-18 17:45 | 13.8KV 8C FEEDER #3 | Fair | Lightning Arrester | 45 | Checked & found, Recl. 8D-18A (8C fdr #3) T/LO. Ctr: 25-29. Patrolled the line & found, @2 broken L/A o/p #8C-247. Cause: Lightning Arrester. | 3227455 | 1 | 14:26 | Afternoon | Tuesday | 2016 | 6
3493 | 2016-06-14 15:20 | 2016-06-14 15:20 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 36 | 15:20 Generator Breaker CGT #4 Tripped. By: MCC under voltage. Cause: 480V Breaker Trip. (no cooling system for Excitation) Frequency system dropped to 59.70Hz. (Load shedding level-1) 3D OCB fdr #6 Tripped, then closed at 15:25. 4D OCB fdr #4 Tripped, then closed at 15:26. 4D OCB fdr #5 Tripped, then Closed at 15:26. 15:40 Closed Generator Breaker CGT #4. (After closing 480V Breaker) Cause: Under investigation. Prod. loss: GS #4 => 4D fdr #4: 24 Bbls/ 18 Wells. 4D fdr #5: 14 Bbls/ 20 Wells. GS #5 => 3D fdr #6: 0 Bbls - 0 Wells. (T/O WIP) Total: 39 Bbls/ 38 Wells. | 3227452 | 1 | 15:20 | Afternoon | Tuesday | 2016 | 6
3494 | 2016-06-14 22:36 | 2016-06-14 22:36 | 13.8KV MINAS FEEDER #1 | Fair | Pin Insulator | 31 | Minas ACB fdr #1 T/R 1x Ctr:52-53 R/F:51N. Not patrolled yet. | 3227455 | 1 | 22:36 | Night | Tuesday | 2016 | 6
3495 | 2016-06-14 22:36 | 2016-06-18 17:40 | 13.8KV MINAS FEEDER #1 | Fair | Pin Insulator | 31 | Checked & found, Minas ACB fdr #1 T/R 1x Ctr: 52-53 R/F: 51N. Patrolled the line & found, @1 broken Pin Insulator o/p #7D-19. Cause: Pin Insulator. | 3227455 | 1 | 22:36 | Night | Tuesday | 2016 | 6
3496 | 2016-06-14 23:37 | 2016-06-14 23:37 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 13 | 3D fdr #4 load dropped 118A (189-71A). (Ground fault alarm on 3D fdr #4) Not checked yet. | 3227455 | 1 | 23:37 | Night | Tuesday | 2016 | 6
3497 | 2016-06-14 23:37 | 2016-06-18 16:00 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 13 | Checked & found, Recl. 2D-14 (3D fdr #4) T/R 1x Ctr: 40-41. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3227455 | 1 | 23:37 | Night | Tuesday | 2016 | 6
3498 | 2016-06-15 00:05 | 2016-06-15 00:05 | 13.8KV NORTH DURI FEEDER #7 | Fair | Animal | 753 | 00:05 No.Duri VCB fdr #7 T/LO. No.Duri fdr #4 Load dropped 26A (103-77A). 02:00 Checked & found, No.Duri VCB fdr #7 T/SO. Ctr: 62-64 R/F: 51@1,@2 & 51N. Patrolled the line, but found nothing. 03:03 Open Recl. 10-L1-02. (ex No.Duri fdr #8) 03:38 Blocked & closed No.Duri VCB fdr #7, but failed. 03:39 Closed both side of isolation switch of No.Duri VCB fdr #8. 03:47 Blocked & closed No.Duri VCB fdr #8, Ok. Then released the block. Open both isolation switch of No.Duri VCB fdr #7. (to function test the breaker, but failed from DSC & Local) 04:18 Manuall open No.Duri VCB fdr #8, to closing Bypass SW of Recl.10-L1-02. 04:32 Blocked & closed No.Duri VCB fdr #8, but T/O again. (By R/F: 51@1,@2 & 51N) Re-Open Bypass SW of Recl. 10-L1-02. 04:34 Blocked & closed No.Duri VCB fdr #8, Ok. Then released the block. 05:20 Patrolled the line & found, leaks for 112.5Kva Tx o/p #10-K8-24. 05:30 Closed LBS #10-K4-14 (No.Duri fdr #7 supply from No.Duri fdr #8) Checked & found, Recl. 10-L1-02 T/O. Ctr: not reported yet. Unplug & close Recl. 10-L1-02. 06:19 Open disconnect switch o/p #10-J4-01. Open No.Duri fdr #8 and close LBS #10-K4-14. Blocked & closed No.Duri fdr #8, but failed. Re-Open LBS #10-K4-14. Isolated Recl. 10-L1-17 & Recl. 10-J5-02. (D/S of No.Duri fdr #7) 07:06 Blocked & closed No.Duri fdr #8, Ok. Then released the block. 07:20 Close LBS #10-L1-30. 07:40 Checked & found, An animal (Bird) on @1, @2 Bushing of Recl. 10-K2-18 Also found, @1,@2 broken bushing of Recl. 10-K2-18. 10:35 Closed LBS #10-K4-14. (after Bypassing Recl. 10-K2-18) Cause: Animal. (Bird) | 3227452 | 1 | 0:05 | Night | Wednesday | 2016 | 6
3499 | 2016-06-15 03:22 | 2016-06-15 03:22 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Powerline - Conductor | 0 | 03:22 4.16KV Dumai VCB fdr #1 T/LO. 04:30 Check & found, 4.16KV Dumai VCB fdr #1 T/LO. Ctr: 247-249 R/F: 50@2,@3 & 50N. 05:30 Patrolled the line & found, @3 broken conductor o/p #W92-12. (ex Pelindo) 06:50 Opened FCO o/p #W92-12. (to isolate broken conductor above) 07:00 Blocked & closed 4.16KV Dumai VCB fdr #1, Ok. Then released the block. Cause: Broken conductor. | 3227452 | 1 | 3:22 | Night | Wednesday | 2016 | 6
3500 | 2016-06-16 08:20 | 2016-06-16 08:20 | MINAS POWER PLANT |  |  | - | 08:20 S/U MGT #4, then on line the Unit at 09:00. |  | 1 | 8:20 | Morning | Thursday | 2016 | 6
3501 | 2016-06-16 13:50 | 2016-06-16 13:50 | MINAS POWER PLANT |  |  | - | Off line MGT #1, then S/D the Unit for S/B. |  | 1 | 13:50 | Afternoon | Thursday | 2016 | 6
3502 | 2016-06-16 17:07 | 2016-06-16 17:07 | 8 CHARLIE SUBSTATION | Fair | Substation Failure (CT) | 73 | 17:07 115KV 8C C/S-TX #2 T/O. Ctr: 494-495 R/F: 51T @3. (Due to Switching transfer load 8C fdr #3 to 8C fdr #6) 8C VCB fdr #3 T/O, then closed at 17:08. 17:09 Open 8C VCB fdr #4, then closed at 17:16. (Last Ctr: 581) 17:09 Open 8C VCB fdr #5, then closed at 17:16. (Last Ctr: 95) 17:10 Open 8C VCB fdr #6, then closed at 17:24. (Last Ctr: 595) 17:15 Closed 115KV 8C C/S-TX #2. (after resetting the Relay flag) 17:31 Manually Open Minas ACB fdr #3, then Closed at 20:03. (Requested by GS #2) Production Loss: 1. 8C VCB fdr #3 = 156 Barrels / 35 wells. 2. 8C VCB fdr #4 = 35 Barrels / 11 wells. 3. 8C VCB fdr #6 = 53 Barrels / 17 wells. --------------------------------------------------- + Total = 244 Barrels / 63 wells. Cause: Under investigation. Investigation Result: Wrong tap CT during over current protection setting, picked tap not as engineering recommendation. | 3227455 | 1 | 17:07 | Afternoon | Thursday | 2016 | 6
3503 | 2016-06-17 01:23 | 2016-06-17 01:23 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Tree | 0 | 01:23 Duri Community ACB fdr #5 T/LO. Ctr: 102-104 R/F: 51N. 02:06 Checked & found, falling down trees & touching to the power line at near PE Lab. (Dismantle the trees above from power line) 02:41 Blocked & Closed Duri Community ACB fdr #5, Ok. Then released the block. Cause: Tree. | 3227452 | 1 | 1:23 | Night | Friday | 2016 | 6
3504 | 2016-06-17 02:47 | 2016-06-17 02:47 | 13.8KV 6D FEEDER #2 | Rain | Unidentified | 0 | 6D fdr #2 load dropped 89A (218-129A). Not checked yet. | 3227455 | 1 | 2:47 | Night | Friday | 2016 | 6
3505 | 2016-06-17 02:47 | 2016-06-18 15:47 | 13.8KV 6D FEEDER #2 | Rain | Unidentified | 0 | Checked & found, Recl. 6D-87 (6D fdr #2) T/R 1x Ctr: 48-49. Patrolled the line, but nothing found. Cause: Unidentified. | 3227455 | 1 | 2:47 | Night | Friday | 2016 | 6
3506 | 2016-06-18 15:55 | 2016-06-18 15:55 | 13.8KV DURI FIELD FEEDER #3 | Fair | Animal | 0 | 15:55 It was reported b/o fuse for Tx o/p #01-7-02. (D.Field fdr #3) 16:40 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-07-02. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Bird) | 3227452 | 1 | 15:55 | Afternoon | Saturday | 2016 | 6
3507 | 2016-06-18 17:35 | 2016-06-18 17:35 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 55 | 17:35 CGT #3 Open Generator Breaker, By Alarm: Not Apprear. (When performed test 88CW-2 & selected 88CW-1 to Standby mode) Frequency system dropped to :59.70Hz. (Load shedding level-1) 3D OCB fdr #6 T/O, then closed at 17:37. 4D OCB fdr #4 T/O, then closed at 17:38. 4D OCB fdr #5 T/O, then closed at 17:39. 17:42 Closed Generator Breaker ACB #36. (CGT #3 back to online) 17:52 CGT #3 Open Generator Breaker again. (Load shedding level-1) 3D OCB fdr #6 T/O, then closed at 17:53. 4D OCB fdr #4 T/O, then closed at 17:53. 4D OCB fdr #5 T/O, then closed at 17:53. 17:55 Closed Generator Breaker ACB #36. (CGT #3 back to online to the system) Production loss: 1. 3D OCB fdr #6 = WIP GS #5. 2. 4D OCB fdr #4 = 24 Barrels / 18 wells. (GS #4). 4D OCB fdr #4 = 39 Barrels / 24 wells. (GS #3). 3. 4D OCB fdr #5 = 13 Barrels / 12 wells. (GS #5). 4D OCB fdr #5 = 1 Barrels / 1 wells. (GS #4). ------------------------------------------------------- + Total = 77 Barrels / 55 wells. | 3227455 | 1 | 17:35 | Afternoon | Saturday | 2016 | 6
3508 | 2016-06-18 18:13 | 2016-06-18 18:13 | 13.8KV BANGKO FEEDER #1 | Fair | Switchboard Problem | 0 | 18:13 It was reported b/o fuse for Tx at Well Bangko #70. Checked & found, @1,@2,@3 b/o 3.5SF fuses for 150Kva Tx at Well Bangko #70. Tested the Tx & found, Low megger reading. Cause: Tx failure. (Low megger reading) (The Tx failure is not replaced yet) | 3227452 | 1 | 18:13 | Afternoon | Saturday | 2016 | 6
3509 | 2016-06-18 18:13 | 2016-06-21 14:16 | 13.8KV BANGKO FEEDER #1 | Fair | Switchboard Problem | 0 | Checked & found, b/o fuses for 150Kva Tx at Well Bangko #70. Also found, burnt out Switch board at well above. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Switch board Problem. (Vacuum contactor) | 3227452 | 1 | 18:13 | Afternoon | Saturday | 2016 | 6
3510 | 2016-06-18 19:50 | 2016-06-18 19:50 | MINAS POWER PLANT |  |  | - | 19:50 S/U MGT #7, then On line the Unit at 20:16. |  | 1 | 19:50 | Night | Saturday | 2016 | 6
3511 | 2016-06-18 22:30 | 2016-06-18 22:30 | CENTRAL DURI POWER PLANT |  |  | - | 22:30 Off Line CGT #3, then S/D the Unit for Stand By. (Prior to Troubleshooting, after open Generator breaker event of this unit) 22:31 Closed C.Duri ACB #39. (Tie Breaker) |  | 1 | 22:30 | Night | Saturday | 2016 | 6
3512 | 2016-06-19 05:59 | 2016-06-19 05:59 | 13.8KV DARLING GFPC-TX#2 | Fair | Unidentified | 0 | Darling GFPC-TX #2 T/R 1x. Not load dropped on any feeders. (Ground fault alarm on Darling fdr #6) Not checked yet. | 3227452 | 1 | 5:59 | Morning | Sunday | 2016 | 6
3513 | 2016-06-19 05:59 | 2016-06-24 07:59 | 13.8KV DARLING GFPC-TX#2 | Fair | Unidentified | 0 | Checked & found, Darling GFPC-TX #2 T/R 1x Ctr: 201-202. Patrolled Darling fdr #6 line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 5:59 | Morning | Sunday | 2016 | 6
3514 | 2016-06-19 08:40 | 2016-06-19 08:40 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 51 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3227452 | 1 | 8:40 | Morning | Sunday | 2016 | 6
3515 | 2016-06-19 08:40 | 2016-06-22 17:15 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 51 | Checked & found, Ketigul VCB fdr #1 T/R 2x Ctr: 171-173 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #32AK-38. Cause: Dead end Insulator. | 3227452 | 1 | 8:40 | Morning | Sunday | 2016 | 6
3516 | 2016-06-19 10:12 | 2016-06-19 10:12 | MINAS POWER PLANT |  |  | - | 10:12 S/U MGT #8, then on line the Unit at 10:38. |  | 1 | 10:12 | Morning | Sunday | 2016 | 6
3517 | 2016-06-19 13:21 | 2016-06-19 13:21 | MINAS POWER PLANT |  |  | - | 13:21 S/U MGT #6, then on line the Unit at 13:34. |  | 1 | 13:21 | Afternoon | Sunday | 2016 | 6
3518 | 2016-06-19 14:03 | 2016-06-19 14:03 | MINAS POWER PLANT |  |  | - | Off line MGT #10, then S/D the Unit for S/B. (Prior to replacing Fuel Nozzle set) 21-Jun-2016. 10:50 S/U MGT #10, then On Line the Unit at 11:06. (After replacing Fuel Nozzle set) |  | 1 | 14:03 | Afternoon | Sunday | 2016 | 6
3519 | 2016-06-19 14:48 | 2016-06-19 14:48 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 25 | 14:48 It was reported b/o fuse for Tx at Well No.Menggala #38. (Menggala fdr #1) 16:25 Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well No.Menggala #38. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3227452 | 1 | 14:48 | Afternoon | Sunday | 2016 | 6
3520 | 2016-06-19 15:21 | 2016-06-19 15:21 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 70 | Petani OCB fdr #1 T/R 1x. Petani fdr #2 Load dropped 20A (42-22A). Not checked yet. | 3227452 | 1 | 15:21 | Afternoon | Sunday | 2016 | 6
3521 | 2016-06-19 15:21 | 2016-06-20 17:30 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 70 | Petani OCB fdr #1 T/R 1x Ctr: 24-25 R/F: 51N. Patrolled the line & found, transformer failure at Well Petani #09. Cause: Transformer failure. | 3227452 | 1 | 15:21 | Afternoon | Sunday | 2016 | 6
3522 | 2016-06-19 22:10 | 2016-06-19 22:10 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 31 | 22:10 It was reported b/o fuse for Tx at Well Petani #09. 23:50 Checked & found, @1,@2 b/o 3.1SF fuses for 100Kva Tx at Well Petani #09. Performed TTR, Megger test the Tx & found, Zero Meg Ohm reading Tx. Cause: TX failure. (Zero megger reading) (This Tx is not replaced yet) | 3227452 | 1 | 22:10 | Night | Sunday | 2016 | 6
3523 | 2016-06-19 22:10 | 2016-06-20 10:30 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 31 | Replaced 100Kva Tx failure with 150Kva Tx at Well Petani #09, then energized the Tx. Cause: Tx failure. | 3227452 | 1 | 22:10 | Night | Sunday | 2016 | 6
3524 | 2016-06-20 05:27 | 2016-06-20 05:27 | 13.8KV BANGKO FEEDER #4 | Drizzle | Lightning | 121 | 05:27 Bangko fdr #4 Load dropped 158A (218-60A). (Bangko GFPC in By Pass position due to GFPC Problem) 06:50 Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/LO. Ctr: 97-102. 07:30 Patrolled the line & found, @3 broken Pin Insulator o/p #27Y-12. 09:40 Blocked & closed Recl. 25Z-07, Ok. Then released the Block. (After replacing broken Pin Insulator above) Cause: Lightning. | 3227452 | 1 | 5:27 | Morning | Monday | 2016 | 6
3525 | 2016-06-20 11:00 | 2016-06-20 11:00 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 45 | LIbo fdr #2 Load dropped 28A (47-19A). 11:00-14:00 Manually opened Line Switches o/p #23BW-41. (After shutdown 4Wells at downstream) To Replacing broken & flashed over Pin Insulators. (21Pcs on 7 electric poles) Cause: Maintenance Job. | 123 | 1 | 11:00 | Morning | Monday | 2016 | 6
3526 | 2016-06-21 07:44 | 2016-06-21 07:44 | 13.8KV SURAM FEEDER #1 | Fair | Animal | 0 | Suram fdr #1 Load dropped 56A (76-20A). Not checked yet. | 3227455 | 1 | 7:44 | Morning | Tuesday | 2016 | 6
3527 | 2016-06-21 07:44 | 2016-06-22 08:30 | 13.8KV SURAM FEEDER #1 | Fair | Animal | 0 | Checked & found, Recl. 14CY-01 (Suram fdr #1) T/R 1x Ctr: 289-290. Patrolled the line & found, a Dead Monkey under pole #14CY-10. Cause: Animal. (Monkey) | 3227455 | 1 | 7:44 | Morning | Tuesday | 2016 | 6
3528 | 2016-06-21 08:11 | 2016-06-21 08:11 | 13.8KV ROKAN FEEDER #2 | Fair | Dead End Insulator | 7 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3227452 | 1 | 8:11 | Morning | Tuesday | 2016 | 6
3529 | 2016-06-21 08:11 | 2016-06-26 07:15 | 13.8KV ROKAN FEEDER #2 | Fair | Dead End Insulator | 7 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 1236-1237 R/F: 51@1. Patrolled the line & found, @1 F/O Dead end Insulator o/p #31AV-23. Cause: Dead end Insulator. | 3227452 | 1 | 8:11 | Morning | Tuesday | 2016 | 6
3530 | 2016-06-21 10:50 | 2016-06-21 10:50 | MINAS POWER PLANT |  |  | - | 10:50 S/U MGT #10, then On Line the Unit at 11:06. (After replacing Fuel Nozzle set) |  | 1 | 10:50 | Morning | Tuesday | 2016 | 6
3531 | 2016-06-21 12:09 | 2016-06-21 12:09 | 13.8KV DURI FIELD FEEDER #4 | Cloudy and Lightning | Lightning | 0 | Duri Field ACB fdr #4 T/R 1x. Not checked yet. | 3227452 | 1 | 12:09 | Afternoon | Tuesday | 2016 | 6
3532 | 2016-06-21 12:09 | 2016-06-25 10:10 | 13.8KV DURI FIELD FEEDER #4 | Cloudy and Lightning | Lightning | 0 | Checked & found, D.Field ACB fdr #4 T/R 1x Ctr: 473-474 R/F: 51N. Patrolled the line & found, @2 broken bushing of LBS o/p #07-U2-02. Cause: Lightning. | 3227452 | 1 | 12:09 | Afternoon | Tuesday | 2016 | 6
3533 | 2016-06-21 12:12 | 2016-06-21 12:12 | MENGGALA SUBSTATION | Fair | Others | - | When PT SDI Install PQM Relay at Menggala Substation, then Closed it. (Bangko Substation Bus voltage dropped to 13.2KV, but no wells off) Cause: Others. | 3227452 | 1 | 12:12 | Afternoon | Tuesday | 2016 | 6
3534 | 2016-06-21 13:16 | 2016-06-21 13:16 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 26 | 13:16 C.Duri fdr #1 Load dropped 55A (191-146A). 19:14 C.Duri fdr #1 Load dropped 55A again (191-146A). Not checked yet. | 3227352 | 1 | 13:16 | Afternoon | Tuesday | 2016 | 6
3535 | 2016-06-21 13:16 | 2016-06-30 16:10 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 26 | Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/R 1x Ctr: 186-187. Patrolled the line, but found nothing. Cause: Unidentified. | 3227352 | 1 | 13:16 | Afternoon | Tuesday | 2016 | 6
3536 | 2016-06-21 14:05 | 2016-06-21 14:05 | MINAS POWER PLANT |  |  | - | Off line MGT #6, then S/D Unit for S/B. |  | 1 | 14:05 | Afternoon | Tuesday | 2016 | 6
3537 | 2016-06-21 14:27 | 2016-06-21 14:27 | MINAS POWER PLANT |  |  | - | Off line MGT #7, then S/D the Unit for S/B. |  | 1 | 14:27 | Afternoon | Tuesday | 2016 | 6
3538 | 2016-06-21 15:39 | 2016-06-21 15:39 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 37 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3227452 | 1 | 15:39 | Afternoon | Tuesday | 2016 | 6
3539 | 2016-06-21 15:39 | 2016-06-25 16:30 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 37 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 172-173 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #32AK-38. Cause: Dead end Insulator. | 3227452 | 1 | 15:39 | Afternoon | Tuesday | 2016 | 6
3540 | 2016-06-21 19:00 | 2016-06-21 19:00 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 35 | 19:00 It was reported b/o fuse for Tx at Well Bangko #267. 20:10 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Bangko #267. Perform TTR, Megger test the Tx & found, good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal. (Monkey) | 3227452 | 1 | 19:00 | Night | Tuesday | 2016 | 6
3541 | 2016-06-22 07:01 | 2016-06-22 07:01 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 120 | 07:01 Sintong OCB fdr #2 T/O. (in block position) 07:03 Close Sintong OCB fdr #2, Ok. Then Released the Block. 16:21 Sintong OCB fdr #2 T/R 1x again. Not checked yet. | 3227452 | 1 | 7:01 | Morning | Wednesday | 2016 | 6
3542 | 2016-06-22 07:01 | 2016-06-25 08:13 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 120 | Checked & found, Sintong VCB fdr #2 T/SO. Ctr: 411-413 R/F: 51N. Patrolled the Line, but found nothing. Cause: Suspected by Lightning. | 3227452 | 1 | 7:01 | Morning | Wednesday | 2016 | 6
3543 | 2016-06-22 09:30 | 2016-06-22 09:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 5 | 09:30 It was reported b/o fuse for Tx at Well Pagar #30. (Ketigul fdr #2) 16:50 Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well Pagar #30. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3227452 | 1 | 9:30 | Morning | Wednesday | 2016 | 6
3544 | 2016-06-22 13:46 | 2016-06-22 07:45 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified | 9 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 1237-1238 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 13:46 | Afternoon | Wednesday | 2016 | 6
3545 | 2016-06-22 13:46 | 2016-06-22 13:46 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified | 9 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3227452 | 1 | 13:46 | Afternoon | Wednesday | 2016 | 6
3546 | 2016-06-22 15:50 | 2016-06-22 15:50 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 116 | 15:50 It Was reported b/o fuse for Tx at Well So.Balam #132. (So.Balam fdr #1) 19:30 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well So.Balam #132. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Squirrel) | 3227452 | 1 | 15:50 | Afternoon | Wednesday | 2016 | 6
3547 | 2016-06-22 17:18 | 2016-06-22 17:18 | 13.8KV SURAM FEEDER #1 | Fair | Animal | 0 | Suram fdr #1 Load dropped 52A (71-19A). Not checked yet. | 3227455 | 1 | 17:18 | Afternoon | Wednesday | 2016 | 6
3548 | 2016-06-22 17:18 | 2016-06-23 08:15 | 13.8KV SURAM FEEDER #1 | Fair | Animal | 0 | Checked & found, Recl. 14Y-01 (Suram fdr #1) T/R 1x Ctr: 290-291. Patrolled the line & found, a Dead Mokey under TP of Well Kasikan #20. Cause: Animal. (Monkey) | 3227455 | 1 | 17:18 | Afternoon | Wednesday | 2016 | 6
3549 | 2016-06-23 16:00 | 2016-06-23 16:00 | MINAS POWER PLANT |  |  | - | 16:00 S/U MGT #5, then On line the Unit at 16:10. |  | 1 | 16:00 | Afternoon | Thursday | 2016 | 6
3550 | 2016-06-23 16:10 | 2016-06-23 16:10 | CENTRAL DURI POWER PLANT |  |  | - | 16:10 S/U CGT #3, then On line the Unit at 16:40. |  | 1 | 16:10 | Afternoon | Thursday | 2016 | 6
3551 | 2016-06-23 16:13 | 2016-06-23 16:13 | MINAS POWER PLANT |  |  | - | Off line MGT #4, then S/D the Unit for S/B. |  | 1 | 16:13 | Afternoon | Thursday | 2016 | 6
3552 | 2016-06-23 23:57 | 2016-06-23 23:57 | 13.8KV CENTRAL DURI FEEDER #6 | Cloudy and Lightning | Lightning | 0 | C.Duri ACB fdr #6 T/R 1x Ctr: 441-442 R/F: 51N. Not patrolled yet. | 3227452 | 1 | 23:57 | Night | Thursday | 2016 | 6
3553 | 2016-06-23 23:57 | 2016-06-25 10:25 | 13.8KV CENTRAL DURI FEEDER #6 | Cloudy and Lightning | Lightning | 0 | Patrolled the line & found, @1 broken Pin Insulator o/p #01-01-11. Cause: Lightning. | 3227452 | 1 | 23:57 | Night | Thursday | 2016 | 6
3554 | 2016-06-24 05:16 | 2016-06-24 05:16 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 05:16 CGT #3 Generator Breaker Tripped. By Alarm: No alarm appear. Frequency system dropped to 59.92Hz. (No load shedding) 05:27 Closed Generator Breaker CGT #3, Ok. Cause: Under Investigation. | 3227452 | 1 | 5:16 | Morning | Friday | 2016 | 6
3555 | 2016-06-24 07:09 | 2016-06-24 07:09 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 95 | Bangko OCB fdr #4 T/R 1x. Bangko GFPC T/R 1x. (Ground fault alarm at Bangko fdr #4) Not checked yet. | 3227452 | 1 | 7:09 | Morning | Friday | 2016 | 6
3556 | 2016-06-24 07:09 | 2016-06-25 10:00 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 95 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 993-994 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. Also found, Recl. 25Z-07 (Bangko fdr #4) T/SO. Ctr: 102-103. Patrolled the line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 7:09 | Morning | Friday | 2016 | 6
3557 | 2016-06-24 14:56 | 2016-06-24 14:56 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | 14:56 Duri Community ACB fdr #1 T/SO. 15:31 Checked & found, Duri Community ACB fdr #1 T/SO. Ctr: 83-84 R/F: Did not appear. Blocked & Close Duri Community ACB fdr #1, Ok. Then released the Block. Patrolled the line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 14:56 | Afternoon | Friday | 2016 | 6
3558 | 2016-06-24 15:33 | 2016-06-24 15:33 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr #1 Load drop 50A (196-146A). Not Checked yet. | 3227452 | 1 | 15:33 | Afternoon | Friday | 2016 | 6
3559 | 2016-06-24 15:33 | 2016-06-30 16:05 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/R 1x Ctr: 187-188. Patrolled the line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 15:33 | Afternoon | Friday | 2016 | 6
3560 | 2016-06-25 01:30 | 2016-06-25 01:30 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 397 | 01:30 No.Duri fdr #11 Load dropped 141A (151-10A). 02:24 It was reported no power at CIF area-10. 04:18 Checked & found, Recl. 13-F11-03R (No.Duri fdr #11) T/O. Ctr: 10-11. Blocked & closed Recl. 13-F11-03R, but T/O again. Patrolled the line, but found nothing. Transferred part Load of No.Duri fdr #11 to No.Duri fdr #2. 05:05 Closed Isolation switch of N.Duri VCB fdr #2. 05:15 Unplug Recl. 13-F11-03R. 05:19 Blocked & closed No.Duri VCB fdr #2, Ok. Then release the block. Re-Patrolled the line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 1:30 | Night | Saturday | 2016 | 6
3561 | 2016-06-25 03:13 | 2016-06-25 03:13 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified (Fuse) | 4 | 03:13 It was reported b/o fuse for Tx o/p #01-9-13. (D.Field fdr #3) 09:00 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #01-9-13. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3227452 | 1 | 3:13 | Night | Saturday | 2016 | 6
3562 | 2016-06-25 16:54 | 2016-06-25 16:54 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | C.DURI ACB fdr #6 T/R 1x. Not checked yet. | 3227452 | 1 | 16:54 | Afternoon | Saturday | 2016 | 6
3563 | 2016-06-25 16:54 | 2016-06-27 15:30 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | Checked & found, C.Duri ACB fdr #6 T/R 1x Ctr: 442-443 R/F: 50@2,@3. Patrolled the line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 16:54 | Afternoon | Saturday | 2016 | 6
3564 | 2016-06-25 17:05 | 2016-06-25 17:05 | 13.8KV 6DN FEEDER #6 | Fair | Lightning Arrester | 39 | 6DN OCB fdr #6 T/R 1x. 6DN fdr #1 Load dropped 66A (2-9-153A). Not checked yet. | 3227455 | 1 | 17:05 | Afternoon | Saturday | 2016 | 6
3565 | 2016-06-25 17:05 | 2016-06-29 08:45 | 13.8KV 6DN FEEDER #6 | Fair | Lightning Arrester | 39 | Checked & found, 6DN OCB fdr #6 T/R 1x Ctr: 345-346 R/F: 50@1. Patrolled the line & found, @1 broken L/A on TP of Well #6E-11. Cause: Lightning Arrester. | 3227455 | 1 | 17:05 | Afternoon | Saturday | 2016 | 6
3566 | 2016-06-26 13:13 | 2016-06-26 13:13 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 19 | 13:13 CGT #3 Generator breaker Tripped. By Alarm: L30A68. (Reverse Power) Frequency system found at Scada Alarm dropped to 59.95Hz. (Load shedding level-1): 3D OCB fdr #6 T/O, then closed at 13:30. 4D OCB fdr #4 T/O, then closed at 13:30. 4D OCB fdr #5 T/O, then closed at 13:31. 13:19 Closed CGT #3 Generator Breaker, but Trip again. (Tried to Close & trip 3x) 13:55 Closed CGT #3 Generator Breaker, Ok. (The load keep at 10MW) Cause: Under Investigation. | 3227452 | 1 | 13:13 | Afternoon | Sunday | 2016 | 6
3567 | 2016-06-27 02:30 | 2016-06-27 02:30 | MINI CENDRAWASIH SUBSTATION | Fair | Unidentified | 0 | 02:30 It was reported no power at Cermai Komplek. 03:10 Checked & found, 13.8Kv Recl. for 2.5Mva Tx at Minas Cewa Subst. T/O. Also 4.16Kv Recl. for CEWA housing feeder T/O. Ctr: 698-700 Blocked & closed, 13.8Kv Recl. for 2.5Mva Tx, Ok. 03:15 Blocked & closed, 4.16Kv Recl. for CEWA Housing feeder, but failed. Checked & found, 4.16Kv Recl. Control Batteray, Low DC Voltage. (Then replaced Battery above) 03:50 Blokced & closed, 4.16Kv Recl. for CEWA housing feeder, Ok. Then released the block. The line is not patrolled yet. | 3227455 | 1 | 2:30 | Night | Monday | 2016 | 6
3568 | 2016-06-27 02:30 | 2016-06-29 09:15 | MINI CENDRAWASIH SUBSTATION | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3227455 | 1 | 2:30 | Night | Monday | 2016 | 6
3569 | 2016-06-27 09:30 | 2016-06-27 09:30 | CENTRAL DURI POWER PLANT |  |  | - | 09:30 Off line CGT #3, then S/D the Unit for S/B at 09:32. (Prior to troubleshooting after Generator Breaker Tripped) |  | 1 | 9:30 | Morning | Monday | 2016 | 6
3570 | 2016-06-28 06:38 | 2016-06-28 06:38 | 13.8KV 5B FEEDER #4 | Cloudy and Lightning | Lightning | 46 | 06:38 5B fdr #4 Load dropped 182A (250-68A). 09:40 Checked & found, Recl. 4B-73 T/SO. Ctr: 57-58. R/F: 51N 09:50 Blocked & closed Recl. 4B-73, Ok. Then released the Block. Patrolled the Line, but Found nothing. Cause: Lightning | 3227455 | 1 | 6:38 | Morning | Tuesday | 2016 | 6
3571 | 2016-06-28 10:14 | 2016-06-28 10:14 | 13.8KV DURI FIELD FEEDER #1 | Fair | Animal | 0 | 10:14 It was reported b/o fuse for Tx o/p #01-06-20. 10:40 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-06-20. Replaced b/o fuse above with same size & energize the Tx. Cause: Animal. (Monkey) | 3227452 | 1 | 10:14 | Morning | Tuesday | 2016 | 6
3572 | 2016-06-28 14:45 | 2016-06-28 14:45 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified (L/A) | 0 | No.Duri VCB fdr #1 T/R 1x. Not checked yet. | 327452 | 1 | 14:45 | Afternoon | Tuesday | 2016 | 6
3573 | 2016-06-28 14:45 | 2016-06-30 15:45 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified (L/A) | 0 | Checked & found, No.Duri VCB fdr #1 T/R 1x Ctr: 275-276 R/F: 51@2. Patrolled the line, but found nothing. Cause: Unidentified. | 327452 | 1 | 14:45 | Afternoon | Tuesday | 2016 | 6
3574 | 2016-06-29 07:04 | 2016-06-29 07:04 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | 07:04 Duri Community ACB fdr #1 T/R 1x Ctr: 84-85 R/F: 51N. 18:00 Patrolled the Line, but found nothing. Cause: Unidentified | 3227452 | 1 | 7:04 | Morning | Wednesday | 2016 | 6
3575 | 2016-06-29 09:27 | 2016-06-29 09:27 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 7 | 09:27 C.Duri fdr #1 Load dropped 50A (192-142A). 18:27 C.Duri fdr #1 Load dropped 63A (192-129A). 21:42 C.Duri fdr #1 Load dropped 42A (192-146A). Not checked yet. | 3227452 | 1 | 9:27 | Morning | Wednesday | 2016 | 6
3576 | 2016-06-29 09:27 | 2016-06-30 16:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 7 | Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/R 1x Ctr: 188-189. Patrolled the line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 9:27 | Morning | Wednesday | 2016 | 6
3577 | 2016-06-29 18:30 | 2016-06-29 18:30 | 13.8KV 5B FEEDER #4 | Fair | Unidentified | 45 | 18:30 5B fdr #4 Load dropped 161A (229-68A). 20:15 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO. Ctr: 58-59. Blocked & Closed Recl. 4B-73, Ok. Then released the block. The line is not patrolled yet. | 3227455 | 1 | 18:30 | Afternoon | Wednesday | 2016 | 6
3578 | 2016-06-29 18:30 | 2016-06-30 16:45 | 13.8KV 5B FEEDER #4 | Fair | Unidentified | 45 | Patrolled the line, but found nothing. Cause: Unidentified. | 3227455 | 1 | 18:30 | Afternoon | Wednesday | 2016 | 6
3579 | 2016-06-30 15:14 | 2016-06-30 15:14 | CENTRAL DURI POWER PLANT |  |  | - | 15:14 S/U CGT #3, then On line the unit at 16:30. (Running on test / Keep load = 10 MW) |  | 1 | 15:14 | Afternoon | Thursday | 2016 | 6
3580 | 2016-06-30 17:22 | 2016-06-30 17:22 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 0 | Ketigul fdr #1 Load dropped 66A (120-54A). Not checked yet. | 3227452 | 1 | 17:22 | Afternoon | Thursday | 2016 | 6
3581 | 2016-06-30 17:22 | 2016-01-07 17:22 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 0 | Checked & found, Recl. 32AK-16 (Ketigul fdr #1) T/R 1x Ctr: 121-122 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3227452 | 1 | 17:22 | Afternoon | Thursday | 2016 | 6
3582 | 2016-01-07 15:16 | 2016-01-07 15:16 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 0 | No.Duri VCB fdr #1 T/R 1x. Not checked yet. | 3239052 | 1 | 15:16 | Afternoon | Thursday | 2016 | 1
3583 | 2016-01-07 15:16 | 2016-02-07 16:30 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 0 | Checked & found, No.Duri VCB fdr #1 T/R 1x Ctr: 276-277 R/F: 51@2. Patrolled the line & found, a Dead Monkey under pole #12-F3-38. Cause: Animal. (Monkey) | 3239052 | 1 | 15:16 | Afternoon | Thursday | 2016 | 1
3584 | 2016-01-07 17:36 | 2016-01-07 17:36 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | CGT #3 Tripped by Alarm Revers Power and Computer R Link In operative. (The unit running on test after troubleshooting on load 14.5MW.) Cause: Under investigation. | 3239052 | 1 | 17:36 | Afternoon | Thursday | 2016 | 1
3585 | 2016-02-07 10:58 | 2016-02-07 10:58 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 0 | 10:58 It was reported that b/o fuse for Tx o/p #09-P3-06. 11:36 Checked & found, @3 b/o 3.1SF fuse for for 112.5Kva Tx o/p #09-P3-06. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3239052 | 1 | 10:58 | Morning | Sunday | 2016 | 2
3586 | 2016-02-07 15:15 | 2016-02-07 15:15 | CENTRAL DURI POWER PLANT |  |  | - | 15:15 S/U CGT #3, then On line the Unit at 15:40. (Status: Running on test & Keep load = 8.0 MW) 17:16 CGT #3 Generator Breaker Tripped. By Alarm: Not reported yet. (On load 15 MW & No load shedding) 17:32 CGT #3 Closed Generator Breaker. (After replacing HSAA card) |  | 1 | 15:15 | Afternoon | Sunday | 2016 | 2
3587 | 2016-02-07 18:24 | 2016-02-07 18:24 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 105 | 18:24 CD FDR #1 Load drop 72A (194-122A) 20:27 CD FDR #1 Load drop 74A (194-120A) 21:22 CD FDR #1 Load drop 72A (194-122A) 23:42 CD FDR #1 Load drop 72A (194-122A) Not checked yet | 3239052 | 1 | 18:24 | Afternoon | Sunday | 2016 | 2
3588 | 2016-02-07 18:24 | 2016-03-07 10:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 105 | Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/R 10x Ctr: 189-199. Patrolled the line & found, a Kite hang on @1,@2 conductor near pole #38AS-30. Cause: Others. (a Kite hang on @1,@2 conductors) | 3239052 | 1 | 18:24 | Afternoon | Sunday | 2016 | 2
3589 | 2016-02-07 22:05 | 2016-02-07 22:05 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 22:05 It was reported b/o fuse for Tx o/p #07-T1-08. (C.Duri fdr #2) 23:10 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T1-08. Perform TTR & Megger test the Tx & found, normal. (good reading). Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3239052 | 1 | 22:05 | Night | Sunday | 2016 | 2
3590 | 2016-03-07 01:30 | 2016-03-07 01:30 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Lightning Arrester | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3239052 | 1 | 1:30 | Night | Monday | 2016 | 3
3591 | 2016-03-07 01:30 | 2016-07-07 12:30 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Lightning Arrester | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 85-86 R/F: 51N. Patrolled the line & found, @1 broken L/A o/p #NN. Cause: Lightning Arrester. | 3239052 | 1 | 1:30 | Night | Monday | 2016 | 3
3592 | 2016-03-07 10:38 | 2016-03-07 10:38 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 23 | 10:38 It was reported that b/o fuse for Tx o/p #08-M3-36. 11:06 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #08-M3-36. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). | 3239052 | 1 | 10:38 | Morning | Monday | 2016 | 3
3593 | 2016-03-07 13:36 | 2016-03-07 13:36 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 0 | 13:36 Manual Open Recl. 40CY-16 (OKB fdr #2). To repairing @1 loose connection of Hot Line Clamp jumper o/p #KB-033. (3 Wells were off during the Job done) 14:08 Manual Closed Recl. 40CY-16. (After repairing HLC above) Cause: Plan Maintenance. | 123 | 1 | 13:36 | Afternoon | Monday | 2016 | 3
3594 | 2016-03-07 14:26 | 2016-03-07 14:26 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Transformer Failure | 0 | 14:26 It was reported that b/o fuse for Tx o/p #03-04-34. 15:00 Checked & found, @2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #03-04-34. Tested the Tx & found, Low megger reading. Cause: Tx failure. (Low megger reading). (This Tx failure is not replaced yet) | 3239052 | 1 | 14:26 | Afternoon | Monday | 2016 | 3
3595 | 2016-03-07 14:26 | 14/07/2016 14:30 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Transformer Failure | 0 | Replaced Failure 112.5Kva Tx with the same size o/p #03-04-34. Then Energized the Tx. Cause Tx Failure. | 3239052 | 1 | 14:26 | Afternoon | Monday | 2016 | 3
3596 | 2016-04-07 05:30 | 2016-04-07 05:30 | 13.8KV BEKASAP FEEDER #3 | Fair | Theft | - | 05:30 It was reported b/o fuse for Tx at Well #Bks-59. (BKS fdr #2) 06:30 Checked & found, Broken and Burn out 150Kva Tx at Well #Bks-59. (Well Off Status) Cause: Thief. (Vandalism) | 3239052 | 1 | 5:30 | Morning | Thursday | 2016 | 4
3597 | 2016-05-07 10:08 | 2016-05-07 10:08 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 52 | 10:08 CGT#3 Open Generator Breaker, then S/D the unit for Investigation. (Load shedding level 1) 3D OCB fdr#6 T/O, then closed at 10:10 Production loss = WIP at GS #5. 4D OCB fdr#4 T/O, then closed at 10:11 Production loss = 63 Bbls / 39 wells. 4D OCB fdr#5 T/O, then closed at 10:11 Production loss = 12 Bbls / 12 wells. --------------------------------------------- + Grand total = 75 Bbls / 51 wells. 10:30 Closed Tie Breaker ACB#39. Cause: Under Investigation. | 3239052 | 1 | 10:08 | Morning | Saturday | 2016 | 5
3598 | 2016-05-07 10:40 | 2016-05-07 10:40 | MINAS POWER PLANT |  |  | - | 10:40 S/U MGT#7, then on line the unit at 11:05. |  | 1 | 10:40 | Morning | Saturday | 2016 | 5
3599 | 2016-05-07 10:50 | 2016-05-07 10:50 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3239052 | 1 | 10:50 | Morning | Saturday | 2016 | 5
3600 | 2016-05-07 10:50 | 2016-07-07 21:47 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 86-87 R/F: 51N. Patrolled the line, but nothing found. Cause: Unidentified. | 3239052 | 1 | 10:50 | Morning | Saturday | 2016 | 5
3601 | 2016-05-07 13:35 | 2016-05-07 13:35 | 4.16KV SO RUMBAI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 13:35 It was reported unbalance voltage at Rumbai Water Well #10. (So.Rumbai fdr #1) 14:40 Checked & found, @3 b/o fuse for 150Kva Tx at Rumbai Water Well #10. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3239054 | 1 | 13:35 | Afternoon | Saturday | 2016 | 5
3602 | 2016-05-07 18:02 | 2016-05-07 18:02 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 312 | 18:02 C.Duri fdr #1 Load dropped 78A (197-119A). 19:49 Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/LO. Ctr: 119-123. Patrolled the line, but nothing found. 20:56 Blocked & closed Recl. 39AV-36, but T/O again. 21:15 Opened LBS #37AQ-08. Blocked & closed Recl. 39AV-36, Ok. Then released the block. Continue Patrolling the line at downstream of LBS #37AQ-08 & found: -a Dead Monkey hang on @3 conductor o/p #35AQ-10, then took down its Monkey. Cause: Animal. (Monkey). 22:06 Closed LBS #37AQ-08. | 3239052 | 1 | 18:02 | Afternoon | Saturday | 2016 | 5
3603 | 2016-06-07 01:39 | 2016-06-07 01:39 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 23 | 01:39 8C VCB fdr #4 T/R 1x. 01:51 8C VCB fdr #4 T/R 1x again. Not checked yet. | 3239054 | 1 | 1:39 | Night | Tuesday | 2016 | 6
3604 | 2016-06-07 01:39 | 2016-07-07 16:39 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 23 | Checked & found, 8C VCB fdr #4 T/R 2x Ctr: 581-583 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 1:39 | Night | Tuesday | 2016 | 6
3605 | 2016-06-07 01:44 | 2016-06-07 01:44 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 59 | 8D OCB fdr #11 T/R 1x. Not checked yet. | 3239054 | 1 | 1:44 | Night | Tuesday | 2016 | 6
3606 | 2016-06-07 01:44 | 2016-07-07 16:44 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 59 | Checked & found, 8D OCB fdr #11 T/R 1x R/F: 99898-99899 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 1:44 | Night | Tuesday | 2016 | 6
3607 | 2016-06-07 01:44 | 2016-06-07 01:44 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 34 | 8D fdr #1 Load dropped 48A (144-96A). Not checked yet. | 3239054 | 1 | 1:44 | Night | Tuesday | 2016 | 6
3608 | 2016-06-07 01:44 | 2016-08-07 13:44 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 34 | Checked & found, Recl. 8F-05 (8D fdr #1) T/R 1x Ctr: 63-64. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 1:44 | Night | Tuesday | 2016 | 6
3609 | 2016-06-07 01:44 | 2016-06-07 01:44 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 23 | 8D fdr #3 Load dropped 92A (149-57A). Not checked yet. | 3239054 | 1 | 1:44 | Night | Tuesday | 2016 | 6
3610 | 2016-06-07 01:44 | 2016-07-07 17:07 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 23 | Checked & found, Recl. 8D-30 (8D fdr #3) T/R 1x Ctr: 12-13. Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3239054 | 1 | 1:44 | Night | Tuesday | 2016 | 6
3611 | 2016-06-07 03:25 | 2016-06-07 03:25 | 13.8KV KETIGUL FEEDER#1 | Fair | Lightning Arrester | 43 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3239052 | 1 | 3:25 | Night | Tuesday | 2016 | 6
3612 | 2016-06-07 03:25 | 2016-07-07 15:25 | 13.8KV KETIGUL FEEDER#1 | Fair | Lightning Arrester | 43 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 173-174 R/F: 51@1. Patrolled the line & found, @1 Broken L/A o/p #NN. Cause: Lightning Arrester. | 3239052 | 1 | 3:25 | Night | Tuesday | 2016 | 6
3613 | 2016-06-07 09:48 | 2016-06-07 09:48 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 219 | 09:48 C.Duri fdr #1 Load dropped 73A (196-123). 11:17 Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/LO. Ctr: 204-208. Patrolled the line, but found nothing. 11:55 Blocked & closed Recl. 39AV36, but T/O again. 11:57 Open LBS #37AQ-08. 11:59 Blocked & closed Recl. 39AV-36, Ok. 12:50 Contnued Patrolling the line at downstream of LBS #37AQ-08 & found: -a Dead Monkey o/p #37AQ-07 & @2 Broken L/A o/p #37AQ-07. (Then isolate @2 broken L/A o/p #37AQ-07 above) 13:03 Closed LBS #37AQ-07, Ok. Cause: Animal. (Monkey) | 3239052 | 1 | 9:48 | Morning | Tuesday | 2016 | 6
3614 | 2016-06-07 13:35 | 2016-06-07 13:35 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Lightning | 0 | C.Duri ACB fdr #7 T/R 1x Ctr: 462-463 R/F: 51N. Not patrolled yet. | 3239052 | 1 | 13:35 | Afternoon | Tuesday | 2016 | 6
3615 | 2016-06-07 13:35 | 2016-07-07 21:49 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Lightning | 0 | Patrolled the line, but nothing found. Cause: Suspected by Lightning. | 3239052 | 1 | 13:35 | Afternoon | Tuesday | 2016 | 6
3616 | 2016-06-07 15:46 | 2016-06-07 15:46 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Lightning | 32 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3239054 | 1 | 15:46 | Afternoon | Tuesday | 2016 | 6
3617 | 2016-06-07 15:46 | 2016-07-07 15:46 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Lightning | 32 | Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1258-1259 R/F: 51N. Patrolled the line & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well #KB-23. Cause: Suspected by Lightning. | 3239054 | 1 | 15:46 | Afternoon | Tuesday | 2016 | 6
3618 | 2016-06-07 17:37 | 2016-06-07 17:37 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | C.Duri fdr #14 Load dropped 183A (257-74A). Not checked yet. | 3239052 | 1 | 17:37 | Afternoon | Tuesday | 2016 | 6
3619 | 2016-06-07 17:37 | 2016-07-07 21:51 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | Checked & found, Recl. 06-P7-02 (C.Duri fdr #14) T/R 1x Ctr: 193-194. Patrolled the line, but nothing found. Cause: Unidentified. | 3239052 | 1 | 17:37 | Afternoon | Tuesday | 2016 | 6
3620 | 2016-06-07 21:46 | 2016-06-07 21:46 | 13.8KV 8D FEEDER #11 | Fair | Transformer Failure | 15 | It was reported b/o fuse for Tx at Well #8D-79. (8D fdr #11) Not checked yet. | 3239054 | 1 | 21:46 | Night | Tuesday | 2016 | 6
3621 | 2016-06-07 21:46 | 2016-07-07 16:30 | 13.8KV 8D FEEDER #11 | Fair | Transformer Failure | 15 | Checked & found, @1,@2,@3 b/o 7.8SF fuses for 300Kva Tx at Well #8D-79. Performed TTR, Megger test the Tx & found, Low megger Reading. Cause: Tx Failure. (Transformer Low Megger reading) (The Tx failure is not replaced yet) | 3239054 | 1 | 21:46 | Night | Tuesday | 2016 | 6
3622 | 2016-06-07 21:46 | 2016-10-07 10:00 | 13.8KV 8D FEEDER #11 | Fair | Transformer Failure | 15 | Replaced Failure 300Kva Tx with the same size at Well #8D-79. Then Energized the Tx. Cause: Tx Failure. | 3239054 | 1 | 21:46 | Night | Tuesday | 2016 | 6
3623 | 2016-07-07 07:13 | 2016-07-07 07:13 | 13.8KV 5B FEEDER #2 | Fair | Tree | 0 | 5B OCB fdr #2 T/R 1x. Not checked yet. | 3239054 | 1 | 7:13 | Morning | Thursday | 2016 | 7
3624 | 2016-07-07 07:13 | 15/07/2016 08:00 | 13.8KV 5B FEEDER #2 | Fair | Tree | 0 | Checked & found, 5B OCB fdr #2 T/R 2x Ctr: 338-340 R/F: 51N. Patrolled the line & found, High Palm Trees & touching to power line near pole #4C-53. Cause: Tree. | 3239054 | 1 | 7:13 | Morning | Thursday | 2016 | 7
3625 | 2016-07-07 08:00 | 2016-07-07 08:00 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified (Fuse) | 11 | 08:00 It was reported b/o fuse for Tx at Well #KB-23. (OKB fdr #2) 09:50 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well KB-23. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (Fuse). | 3239054 | 1 | 8:00 | Morning | Thursday | 2016 | 7
3626 | 2016-07-07 13:19 | 2016-07-07 13:19 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 13:19 It was reported b/o fuse for Tx at 5S-Steam Station. (C.Duri fdr #3) 15:00 Checked & found, @3 b/o 100K fuse for 1000Kva Tx at 5S-Steam Station. 16:30 Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3239052 | 1 | 13:19 | Afternoon | Thursday | 2016 | 7
3627 | 2016-07-07 13:50 | 2016-07-07 13:50 | 13.8KV 8D FEEDER #3 | Fair | Unidentified (Fuse) | 15 | 13:50 It was reported b/o fuse for tx at Well #8D-96N. (8D fdr #3) 15:10 Checked & found, @2 b/o 3.5SF fuse for 150Kva Tx at Well #8D-96N. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (Fuse). | 3239054 | 1 | 13:50 | Afternoon | Thursday | 2016 | 7
3628 | 2016-08-07 00:52 | 2016-08-07 00:52 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | 00:52 D.Fiel fdr #2 Load dropped 62A (142-80A). 01:56 Checked & found, Recl. 07-V3-21 (DF fdr #2) T/SO. Ctr: 124-125. Blocked & closed Recl. 07-V3-21, Ok. Then released the Block. Not Patrolled yet. | 3239052 | 1 | 0:52 | Night | Sunday | 2016 | 8
3629 | 2016-08-07 00:52 | 2016-09-07 21:42 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | Patrolled the line, but nothing found. Cause: Unidentified. | 3239052 | 1 | 0:52 | Night | Sunday | 2016 | 8
3630 | 2016-08-07 06:54 | 2016-08-07 06:54 | 13.8KV LIBO FEEDER #2 | Drizzle | Lightning | 6 | 06:54 Libo OCB fdr #2 T/R 1x. 14:00 Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 425-426 R/F: 51N. Patrolled the line & found, @1 broken Suspension Insulator o/p #KW-153. Cause: Lightning. | 3239052 | 1 | 6:54 | Morning | Sunday | 2016 | 8
3631 | 2016-08-07 07:27 | 2016-08-07 07:27 | 13.8KV 3D FEEDER #3 | Rain | Tree | 20 | 3D OCB fdr #3 T/R 1x. Not checked yet. | 3239054 | 1 | 7:27 | Morning | Sunday | 2016 | 8
3632 | 2016-08-07 07:27 | 15/07/2016 08:05 | 13.8KV 3D FEEDER #3 | Rain | Tree | 20 | Checked & found, 3D OCB fdr #3 T/R 1x Ctr: 436-437 R/F: Did not appear. Patrolled the line & found, High Palm Trees & touching to power line near pole #4C-24B. Cause: Tree. | 3239054 | 1 | 7:27 | Morning | Sunday | 2016 | 8
3633 | 2016-08-07 08:10 | 2016-08-07 08:10 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Lightning Arrester | 0 | 08:10 Duri Community ACB fdr #2 T/LO. 08:30 Checked & found, Duri Community ACB fdr #2 T/LO. Ctr: 70-72 R/F: 51N. Patrolled the line & found, @3 Broken L/A o/p #41BE-08. 08:38 Then isolate @3 Broken L/A o/p #41BE-08. 08:39 Blocked & closed, Duri Community ACB fdr #2, but T/O again. 08:58 Open LBS #KRC-20. (near Kerinci complex) 09:23 Blocked & closed Duri Community ACB fdr #2, Ok. 09:48 Open LBS #KRC-01. 09:50 Closed LBS #KRC-20. Patrolled the line, but found nothing. 10:03 Closed LBS #KRC-01. (Duri Community fdr #2 back to normal) Cause: Lightning Arrester. | 3239052 | 1 | 8:10 | Morning | Sunday | 2016 | 8
3634 | 2016-08-07 10:44 | 2016-08-07 10:44 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 10:44 It was reported b/o fuse for Tx o/p #10-K4-40. (N.Duri fdr #9) 11:45 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #10-K4-40. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (Fuse). | 3239052 | 1 | 10:44 | Morning | Sunday | 2016 | 8
3635 | 2016-08-07 10:53 | 2016-08-07 10:53 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 10 | 10:53 It was reported b/o fuse for Tx o/p #06-R5-17. (D.Field fdr #2) 14:40 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #06-R5-17. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal. | 3239052 | 1 | 10:53 | Morning | Sunday | 2016 | 8
3636 | 2016-08-07 14:40 | 2016-08-07 14:40 | CENTRAL DURI POWER PLANT |  |  | - | 14:40 S/U CGT #3, then on line the Unit at 15:07. (Running on test) |  | 1 | 14:40 | Afternoon | Sunday | 2016 | 8
3637 | 2016-08-07 15:49 | 2016-08-07 15:49 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 9 | 15:49 It was reported b/o fuse for Tx o/p #07-T1-08. (D.Field fdr #2) 18:00 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T1-08. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (Fuse). | 3239052 | 1 | 15:49 | Afternoon | Sunday | 2016 | 8
3638 | 2016-08-07 16:02 | 2016-08-07 16:02 | MINAS POWER PLANT |  |  | - | 16:02 S/U MGT #1, then on line the Unit at 16:23. |  | 1 | 16:02 | Afternoon | Sunday | 2016 | 8
3639 | 2016-08-07 16:37 | 2016-08-07 16:37 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 142 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3239054 | 1 | 16:37 | Afternoon | Sunday | 2016 | 8
3640 | 2016-08-07 16:37 | 2016-10-07 08:37 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 142 | Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1259-1260 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3239054 | 1 | 16:37 | Afternoon | Sunday | 2016 | 8
3641 | 2016-08-07 17:07 | 2016-08-07 17:07 | MINAS POWER PLANT |  |  | - | Off line MGT #3, then S/D the Unit for S/B. |  | 1 | 17:07 | Afternoon | Sunday | 2016 | 8
3642 | 2016-08-07 18:40 | 2016-08-07 18:40 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 76 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3239052 | 1 | 18:40 | Afternoon | Sunday | 2016 | 8
3643 | 2016-08-07 18:40 | 19/07/2016 11:22 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 76 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 204-205 R/F: 51N. Patrolled the line & found, @1 broken L/A o/p #31AN-06. Cause: Lightning. | 3239052 | 1 | 18:40 | Afternoon | Sunday | 2016 | 8
3644 | 2016-08-07 19:01 | 2016-08-07 19:01 | 13.8KV RANGAU FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Rangau fdr #2 Load dropped 79A (91-12A). Not checked yet. | 3239052 | 1 | 19:01 | Night | Sunday | 2016 | 8
3645 | 2016-08-07 19:01 | 17/07/2016 15:00 | 13.8KV RANGAU FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: 134-135. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239052 | 1 | 19:01 | Night | Sunday | 2016 | 8
3646 | 2016-09-07 06:40 | 2016-09-07 06:40 | 13.8KV NELLA FEEDER #1 | Fair | Lightning Arrester | 43 | 06:40 Nella fdr #1 Load dropped 102A (252-150A). Nella GFPC T/R 1x. (Ground fault alarm on Nella fdr #1) 13:47 Checked & found, Recl. 21V-01 (Nella fdr #1) T/R 1x Ctr: 97-98. Patrolled the line & found, @2 broken Lightning Arrester o/p #22W-36. Cause: Lightning Arrester. | 3239052 | 1 | 6:40 | Morning | Wednesday | 2016 | 9
3647 | 2016-09-07 16:45 | 2016-09-07 16:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 36 | C.Duri ACB 11 fdr#1 Load dropped 47A(194-147A). Not checked yet. | 3239052 | 1 | 16:45 | Afternoon | Wednesday | 2016 | 9
3648 | 2016-09-07 16:45 | 2016-11-07 16:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 36 | Checked & found, Recl. 39AV 36 T/R 3x ctr: 208-211. Patrolled the line & found, a Kite hang on @1, @2 conductor near well Kulin #42. Cause: Other (a Kite). | 3239052 | 1 | 16:45 | Afternoon | Wednesday | 2016 | 9
3649 | 2016-09-07 18:07 | 2016-09-07 18:07 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri ACB fdr #16 T/R 1x Ctr: 286-287 R/F: 51@1,@2. Not patrolled yet. | 3239052 | 1 | 18:07 | Afternoon | Wednesday | 2016 | 9
3650 | 2016-09-07 18:07 | 2016-11-07 18:07 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked & found, C.Duri ACB fdr #16 T/R 1x Ctr: 286-287 R/F: 51@1,@2. Patrolled the line, but found nothing. Cause: Unidentified. | 3239052 | 1 | 18:07 | Afternoon | Wednesday | 2016 | 9
3651 | 2016-10-07 06:07 | 2016-10-07 06:07 | 13.8KV NORTH DURI FEEDER #5 | Fair | Lightning Arrester | 0 | N.Duri VCB fdr #5 T/R 1x. N.Duri GFPC T/R 1x. (Fault alarm on N.Duri fdr #5) Not cheked yet. | 3239052 | 1 | 6:07 | Morning | Friday | 2016 | 10
3652 | 2016-10-07 06:07 | 2016-11-07 16:07 | 13.8KV NORTH DURI FEEDER #5 | Fair | Lightning Arrester | 0 | Checked & found, No.Duri VCB fdr #5 T/R 1x Ctr: 107-108 R/F: 51@1. Patrolled the line & found, @1 broken L/A o/p #12-G8.1-01. Cause: Lightning Arrester. | 3239052 | 1 | 6:07 | Morning | Friday | 2016 | 10
3653 | 2016-10-07 07:42 | 2016-10-07 07:42 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri ACB fdr #16 T/R 1x Ctr: 287-288 R/F: 51@1. Not Patrolled yet. | 3239052 | 1 | 7:42 | Morning | Friday | 2016 | 10
3654 | 2016-10-07 07:42 | 2016-11-07 17:42 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked & found, C.Duri ACB fdr #16 T/R 1x Ctr: 287-288 R/F: 51@1. Patrolled the line, but found nothing. Cause: Unidentified. | 3239052 | 1 | 7:42 | Morning | Friday | 2016 | 10
3655 | 2016-10-07 08:10 | 2016-10-07 08:10 | 13.8KV 5B FEEDER #2 | Fair | Tree | 31 | 5B OCB fdr #2 T/R 1x. Not checked yet. | 3239054 | 1 | 8:10 | Morning | Friday | 2016 | 10
3656 | 2016-10-07 08:10 | 16/07/2016 06:37 | 13.8KV 5B FEEDER #2 | Fair | Tree | 31 | Checked & found, 5B OCB fdr #2 T/R 2x Ctr: 338-340 R/F: 50N. Patrolled the Line & found, fall down Tree & hit to power line near pole #4C-53. Cause: Tree. | 3239054 | 1 | 8:10 | Morning | Friday | 2016 | 10
3657 | 2016-10-07 19:44 | 2016-10-07 19:44 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 183 | 19:44 C.Duri fdr #1 Load dropped 74A (194-120A). 20:51 Checked and found Recl. 39-AV-36 T/LO Ctr: 208-215. Patrolled the line found a kite hang on @2 and @3 power line between poles 38-AS-14 and 15. Dismantled a kite from power line. 21:31 Blocked and closed Recl. 39-AV-36 --> OK and then released the block. Cause: Others (A Kite hang on power line). | 3239052 | 1 | 19:44 | Night | Friday | 2016 | 10
3658 | 2016-10-07 21:33 | 2016-10-07 21:33 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 7 | Rangau OCB fdr #2 T/R 1x. Not Checked Yet. | 3239052 | 1 | 21:33 | Night | Friday | 2016 | 10
3659 | 2016-10-07 21:33 | 18/07/2016 16:30 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 7 | Checked & found, Rangau OCB fdr #2 T/R 1x Ctr: 308-309 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239052 | 1 | 21:33 | Night | Friday | 2016 | 10
3660 | 2016-10-07 23:54 | 2016-10-07 23:54 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 45 | 4B OCB fdr #2 T/R 1x. 4B fdr #1 Load dropped 78A (290-212A). Not checked yet. | 3239054 | 1 | 23:54 | Night | Friday | 2016 | 10
3661 | 2016-10-07 23:54 | 16/07/2016 06:31 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 45 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 226-227 R/F: 51N. Patrolled the Line & found, @2 broken bypass switch Insulator o/p #4B-06. Cause: Lightning. | 3239054 | 1 | 23:54 | Night | Friday | 2016 | 10
3662 | 2016-11-07 00:12 | 2016-11-07 00:12 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 18 | 00:12 5B fdr #4 Load dropped 168A (229-61A). 01:19 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO. Ctr: 59-60. Blocked & closed Recl. 4B-73, Ok. Then released the block. The line is not patrolled yet. | 3239054 | 1 | 0:12 | Night | Monday | 2016 | 11
3663 | 2016-11-07 00:12 | 17/07/2016 15:25 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 18 | Patrolled the Line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 0:12 | Night | Monday | 2016 | 11
3664 | 2016-11-07 17:42 | 2016-11-07 17:42 | CENTRAL DURI POWER PLANT |  |  | - | 17:42 CGT #3 Generator Breaker Tripped. (on Load 10Mw) 17:50 Closed CGT #3 Generator Breaker. (after changing computer-T and switched it on) |  | 1 | 17:42 | Afternoon | Monday | 2016 | 11
3665 | 2016-11-07 18:22 | 2016-11-07 18:22 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Others | 0 | C.Duri fdr #1 Load dropped 72A (192-120A). Not checked yet. | 3239052 | 1 | 18:22 | Afternoon | Monday | 2016 | 11
3666 | 2016-11-07 18:22 | 2016-12-07 16:22 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Others | 0 | Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/R 1x Ctr: 215-216. Patrolled the line & found, a Kite hang on @2, @3 Conductors o/p #38-AS-12. Cause: Others. (a Kite) | 3239052 | 1 | 18:22 | Afternoon | Monday | 2016 | 11
3667 | 2016-11-07 18:37 | 2016-11-07 18:37 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 36 | 6DN OCB fdr #5 T/R 1x. 6DN fdr #4 Load dropped 140A ( 215-75 ). T/O WIP at Minas GS-3) Not checked yet . | 3239054 | 1 | 18:37 | Afternoon | Monday | 2016 | 11
3668 | 2016-11-07 18:37 | 15/07/2016 08:15 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 36 | Checked & found, 6DN OCB fdr #5 T/LO. Ctr: Not reported yet. R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator o/p #M5B-12. Cause: Lightning. | 3239054 | 1 | 18:37 | Afternoon | Monday | 2016 | 11
3669 | 2016-11-07 18:37 | 2016-11-07 18:37 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 50 | 6DN fdr #6 Load dropped 184A (194-10A). Not checked yet. | 3239054 | 1 | 18:37 | Afternoon | Monday | 2016 | 11
3670 | 2016-11-07 18:37 | 15/07/2016 08:10 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 50 | Checked & found, Recl. 6E-64 (6DN fdr #6) T/R 1x Ctr: 38-39. Patrolled the line & found, @1 broken Dead end Insulator o/p #5E-44. Cause: Lightning. | 3239054 | 1 | 18:37 | Afternoon | Monday | 2016 | 11
3671 | 2016-12-07 01:12 | 2016-12-07 01:12 | 13.8KV 6DN FEEDER #5 | Fair | Pin Insulator | 445 | 01:12 6DN OCB fdr #5 T/R 1x. 01:13 6DN OCB fdr #5 T/LO. 01:39 Checked & found, 6DN OCB fdr #5 T/LO. Ctr: 202-207 R/F: 51N. Patrolled the line, but found nothing. 03:00 Blocked & closed 6DN OCB fdr #5, but T/O again. Re-Patrolled the line, but found nothing. 05:00 Open Recl. 6D-16A. Blocked & closed 6DN OCB fdr #5, but T/O again. 07:30 Ensure Recl. 6D-16A & Recl. 6D-18 were Open status. 07:40 Blocked & closed 6DN OCB fdr #5 from Local, but Triped again. 07:55 Open LBS #6D-16A. (to trouble shoot 6DN OCB fdr #5) 08:05 Found, Recl. 6D-16A failed to Close, due to Control Problem. (Then byapass Recl. 6D-16A) Transferred part load of 6DN fdr #5 to 6D fdr #3. 08:15 Closed LBS #6D-15. (part load of 6DN fdr #5 fed by 6D fdr #3) Transferred part load of 6DN fdr #5 to Minas fdr #1. 08:30 Closed LBS #6D-26A. (Load 6DN fdr #5 fed by Minas fdr #1) 09:30 Re-patrolled the line 6DN fdr #5 & found @3 Broken Pin Insulator o/p #M5-B12. 10:30 Replaced broken Pin Insulator above. 11:30 Functional tested of Closed 6DN OCB fdr #5. (Ctr: 202-219) Cause: Pin Insulator | 3239054 | 1 | 1:12 | Night | Wednesday | 2016 | 12
3672 | 2016-12-07 06:49 | 2016-12-07 06:49 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 223 | 06:49 C.Duri fdr #1 Load dropped 71A (189-118). 09:30 Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/LO. Patrolled the Line, but found nothing. 10:00 Open LBS #39AQ-08. Blocked & Closed Recl. 39AV-36, then released the block. Re-patrolled the Line under LBS #39AQ-08 & found, a Dead Monkey Under power line. 10:30 Closed LBS #39AQ-08. Cause: Animal. (Monkey) | 3239052 | 1 | 6:49 | Morning | Wednesday | 2016 | 12
3673 | 2016-12-07 10:44 | 2016-12-07 10:44 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 10:44 It was reported b/o fuse for Tx o/p #01-02-10. (C.Duri fdr #3) 13:30 Checked & found, @2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #01-02-10. Replaced b/o fuse above with the same size, then Energized the Tx. Cause: Unidentified (Fuse). | 3239052 | 1 | 10:44 | Morning | Wednesday | 2016 | 12
3674 | 2016-12-07 11:37 | 2016-12-07 11:37 | MINAS POWER PLANT |  |  | - | Off line MGT #8, then S/D Unit for S/B. (as per Unit Capability Commitment program) |  | 1 | 11:37 | Morning | Wednesday | 2016 | 12
3675 | 2016-12-07 11:50 | 2016-12-07 11:50 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 11:50 CGT #3 Automatically Open Generator Breaker (On Load 11MW). (While Perform Simulation Raise & Lower Load, after Installing and Switch On Computer-T) 11:55 Closed Generator Breaker of CGT #3. 16:45 CGT #3 Automatically Open Generator Breaker (On Load 10MW). While Perform Simulation Raise & Lower Load, to trouble shoot Load dropped uncontrollable. (Running with R.S.T) 16:45 Closed Generator Breaker of CGT #3. 20:24 Generator Breaker CGT#3 T/O again. 20:30 S/D the Unit for investigation. 20:36 Closed C.Duri ACB #39. (Tie Breaker) Cause: Under Investigation. | 3239052 | 1 | 11:50 | Morning | Wednesday | 2016 | 12
3676 | 2016-12-07 14:00 | 2016-12-07 14:00 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 16:45 It was reported b/o fuse for Tx at DSF Fabrication shop. (C.Duri fdr #3) 16:49 Checked & found, @1,@2 b/o 2.1SF fuses for 50Kva Tx at DSF Fabrication Shop. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3239052 | 1 | 14:00 | Afternoon | Wednesday | 2016 | 12
3677 | 2016-12-07 20:24 | 2016-12-07 20:24 | CENTRAL DURI POWER PLANT |  |  | - | 20:24 CGT #3 Generator Breaker Tripped. 20:30 Then S/D CGT-3. 20:36 Closed C.Duri ACB #39. (Tie Breaker( Status: Stand By. (For investigation) |  | 1 | 20:24 | Night | Wednesday | 2016 | 12
3678 | 2016-07-13 06:35 | 2016-07-13 06:35 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr #1 Load dropped 72A (172-100A). Not checked yet. | 3239052 | 1 | 6:35 | Morning | Wednesday | 2016 | 7
3679 | 2016-07-13 06:35 | 2016-07-18 07:51 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 08-L3-32 (C.Duri fdr #1) T/R 1x Ctr: 507-508. Patrolled the Line, but found nothing. Cause: Unidentified. | 3239052 | 1 | 6:35 | Morning | Wednesday | 2016 | 7
3680 | 2016-07-13 10:17 | 2016-07-13 10:17 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 10:17 It was reported b/o fuse for Tx o/p #05-P3-05. (C.Duri fdr #14) 10:45 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #05-P3-05. Replaced b/o fuse above with the same size, then Energized the Tx. Cause: Animal. (Monkey) | 3239052 | 1 | 10:17 | Morning | Wednesday | 2016 | 7
3681 | 2016-07-13 11:00 | 2016-07-13 11:00 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified (Fuse) | 0 | 11:00 It was reported b/o fuse for Tx o/p #09-L5-19. (C.Duri fdr #16) 13:30 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3239052 | 1 | 11:00 | Morning | Wednesday | 2016 | 7
3682 | 2016-07-13 11:24 | 2016-07-13 11:24 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | 11:24 Sintong fdr #2 Load dropped 54A (216-162A). Sintong GFPC T/R 1x. (Ground fault alarm at Sintong fdr #2) Not checked yet. 22:49 It was reported b/o fuse at Well Benar #25. (Sintong fdr #2) | 3239052 | 1 | 11:24 | Morning | Wednesday | 2016 | 7
3683 | 2016-07-13 11:24 | 2016-07-14 14:00 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | 00:23 Checked & found, @1,@3 b/o 3.5SF fuses for 150Kva Tx at Well Benar #25. Performed TTR, Megger tested the Tx & found, Low Megger reading. Cause: Tx Failure. (Low Megger reading). 10:00 Replaced failure 150Kva Tx at Well Benar #25 with the same size, then energized the Tx . Cause: Tx Failure. | 3239052 | 1 | 11:24 | Morning | Wednesday | 2016 | 7
3684 | 2016-07-13 11:24 | 2016-07-16 07:28 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recl. 26AK-24 (Sintong fdr #2) T/R 1x Ctr: 221-222. Patrolled the Line, but found nothing. Cause: Unidentified. (Suspected TX failure at Well Benar #25) | 3239052 | 1 | 11:24 | Morning | Wednesday | 2016 | 7
3685 | 2016-07-13 18:14 | 2016-07-13 18:14 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Sintong OCB fdr #2 T/R 1x. Not checked yet. | 3239052 | 1 | 18:14 | Afternoon | Wednesday | 2016 | 7
3686 | 2016-07-13 18:14 | 2016-07-16 15:15 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 413-414 R/F: 51N. Patrolled the Line, but found nothing. Cause: Unidentified. | 3239052 | 1 | 18:14 | Afternoon | Wednesday | 2016 | 7
3687 | 2016-07-14 06:09 | 2016-07-14 06:09 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Pin Insulator | 0 | C.Duri fdr #5 Load dropped 61A (78-17A). Not checked yet. | 3239052 | 1 | 6:09 | Morning | Thursday | 2016 | 7
3688 | 2016-07-14 06:09 | 2016-07-15 07:37 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Pin Insulator | 0 | Checked & found, Recl. 03-04-16 (C.Duri fdr #5) T/R 2x Ctr: 169-171. Patrolled the Line & found, @1 broken Pin Insulator o/p #03-07-01B. Cause: Pin Insulator. | 3239052 | 1 | 6:09 | Morning | Thursday | 2016 | 7
3689 | 2016-07-14 23:35 | 2016-07-14 23:35 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Bangko fdr #4 Load dropped 77A (194-117A). Not checked yet. | 3239052 | 1 | 23:35 | Night | Thursday | 2016 | 7
3690 | 2016-07-14 23:35 | 2016-07-16 14:08 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: Not reported yet. R/F: 51N. Also found, Bangko GFPC T/R 4x Ctr: 86 - 90. Patrolled the Line & found, @1,@2 broken L/As on TP of Well Bangko #80. Cause: Lightning. | 3239052 | 1 | 23:35 | Night | Thursday | 2016 | 7
3691 | 2016-07-15 09:28 | 2016-07-15 09:28 | MINAS POWER PLANT |  |  | - | 09:28 S/U MGT #6, then On Line the Unit at 09:50. (S/D MGT #7 for S/B-Prior to Cleaning Inlet House Louver) |  | 1 | 9:28 | Morning | Friday | 2016 | 7
3692 | 2016-07-15 09:35 | 2016-07-15 09:35 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 38 | Minas ACB fdr #2 T/R 1x Ctr: 60-61 R/F: 51N. Not Patrolled yet | 3239054 | 1 | 9:35 | Morning | Friday | 2016 | 7
3693 | 2016-07-15 09:35 | 2016-07-17 15:20 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 38 | Patrolled the Line, but found nothing. Cause: Unidentified. | 3239054 | 1 | 9:35 | Morning | Friday | 2016 | 7
3694 | 2016-07-15 10:30 | 2016-07-15 10:30 | 13.8KV MINAS FEEDER #1 | Fair | Tree | 443 | 10:30 It was reported no Power at some Wells #6D-88, #7D-13, #7D-13N, #7D-22, #7D-23 & #7D-33. Checked & found, Recl. 7D-20 (Minas fdr #1) T/LO. Ctr: 149-153. Patrolled the Line & found, fall down Tree & touching to conductor between poles# & # . 14:30 Blocked & closed Recl. 7D-20, Ok. Then released the Block. (after removing the above Tree) Cause: Tree. | 3239054 | 1 | 10:30 | Morning | Friday | 2016 | 7
3695 | 2016-07-15 10:35 | 2016-07-15 10:35 | 13.8KV BATANG FEEDER #2 | Fair | Unidentified (Fuse) | 1 | 10:35 It was reported b/o fuse for Tx at Well Rantaubais #57. (Batang fdr #2) 16:25 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Rantaubais #57. Replaced b/o fuse above with the same size, then Energized the Tx. Cause: Unidentified (Fuse). | 3239052 | 1 | 10:35 | Morning | Friday | 2016 | 7
3696 | 2016-07-15 11:07 | 2016-07-15 11:07 | MINAS POWER PLANT |  |  | - | Off line MGT #7, then S/D the Unit for S/B. (Prior to Cleaning up Inlet House Louver) |  | 1 | 11:07 | Morning | Friday | 2016 | 7
3697 | 2016-07-15 21:24 | 2016-07-15 21:24 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning Arrester | 52 | Bangko OCB fdr #4 T/R 1x. Bangko fdr #1 Load dropped 83A (202-119A). Bangko GFPC T/R 1x. Not checked yet. | 3239052 | 1 | 21:24 | Night | Friday | 2016 | 7
3698 | 2016-07-15 21:24 | 2016-07-16 14:03 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning Arrester | 52 | Checked & found, Bangko OCB fdr #4 T/R 1x Ctr: 99994 - 99995 R/F: 51N. Patrolled the line & found, @1,@2 Broken L/As on TP of Well Bangko #80. Cause: Lightning Arrester. | 3239052 | 1 | 21:24 | Night | Friday | 2016 | 7
3699 | 2016-07-16 13:13 | 2016-07-16 13:13 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Bangko fdr #4 Load dropped 69A(191-130A). Not checked yet. | 3239052 | 1 | 13:13 | Afternoon | Saturday | 2016 | 7
3700 | 2016-07-16 13:13 | 2016-07-17 10:15 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 105-106. Also found, Bangko GFPC T/R 1x Ctr: 90-91 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239052 | 1 | 13:13 | Afternoon | Saturday | 2016 | 7
3701 | 2016-07-16 13:49 | 2016-07-16 13:49 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Unidentified | 68 | So.Balam fdr #1 Load dropped 81A (109-28A). So.Balam fdr #4 Load dropped 39A (168-129A). Ground fault alarm at So.Balam fdr #1. (So.Balam GFPC TX on Block status) Not checked yet. | 3239052 | 1 | 13:49 | Afternoon | Saturday | 2016 | 7
3702 | 2016-07-16 13:49 | 2016-07-19 15:14 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Unidentified | 68 | Checked All Reclosers Under So.Balam fdr #1 & found, All Normal condition. Patrolled the Line, but found nothing. Cause: Unidentified. (Normal Condition) | 3239052 | 1 | 13:49 | Afternoon | Saturday | 2016 | 7
3703 | 2016-07-16 14:59 | 2016-07-16 14:59 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 0 | C.Duri fdr #1 Load dropped 50A (170-20A). Not checked yet. | 3239052 | 1 | 14:59 | Afternoon | Saturday | 2016 | 7
3704 | 2016-07-16 14:59 | 2016-07-20 20:43 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/R 1x Ctr: 220-221. Patrolled the line & found, @3 broken L/A on T/P of Well Kulin #64. Cause: Lightning. | 3239052 | 1 | 14:59 | Afternoon | Saturday | 2016 | 7
3705 | 2016-07-16 21:56 | 2016-07-16 21:56 | 13.8KV NORTH DURI FEEDER #2 | Fair | Planned Maintenance | 0 | 16-Jul-2016. 21:56 It was reported Sparked o/p #10-J6-09. (No.Duri fdr #2) 23:30 Checked & found, @3 broken FCO for 1000Kva Tx at 10NC-Test Station. 17-Jul-2016. 01:15 Manually opened Recl. 10-J8-16A, to Replacing FCO above. 02:00 Closed Recl. 10-J8-16A, Ok. Cause: Fuse Cut Out. | 123 | 1 | 21:56 | Night | Saturday | 2016 | 7
3706 | 2016-07-16 22:25 | 2016-07-16 22:25 | 13.8KV S. BALAM FEEDER #1 | Fair | Transformer Failure | 3 | It was reported b/o fuse for Tx at Well So.Balam #83. (So.Balam fdr #1) Not checked yet. | 3239052 | 1 | 22:25 | Night | Saturday | 2016 | 7
3707 | 2016-07-16 22:25 | 2016-07-17 14:25 | 13.8KV S. BALAM FEEDER #1 | Fair | Transformer Failure | 3 | Checked & found, @1,@2,@3 b/o 2.1SF fuses for 100Kva Tx at Well So.Balam #83. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx Failure. (Low megger reading) (The Tx failure is not replaced yet) | 3239052 | 1 | 22:25 | Night | Saturday | 2016 | 7
3708 | 2016-07-16 22:25 | 2016-07-18 10:30 | 13.8KV S. BALAM FEEDER #1 | Fair | Transformer Failure | 3 | Replaced 100Kva Tx failure with the same size at Well So.Balam #83, then energized the Tx. Cause: Tx Failure. (Low megger reading) | 3239052 | 1 | 22:25 | Night | Saturday | 2016 | 7
3709 | 2016-07-17 01:21 | 2016-07-17 01:21 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 78 | 01:21 It was repored b/o fuse for Tx at Well N.Menggala #15. (Menggala fdr#1). 11:00 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well N.Menggala #15. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3239052 | 1 | 1:21 | Night | Sunday | 2016 | 7
3710 | 2016-07-17 07:35 | 2016-07-17 07:35 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 0 | 07:35 It was reported b/o fuse for Tx o/p #11-H5-08. (N.Duri fdr #9) 11:25 Checked & found, @2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #11-H5-08. Perform TTR, Megger test the Tx & found, good reading. Replaced b/o fuses above with the same size, then Energized the Tx. Cause: Animal. (Monkey) | 3239052 | 1 | 7:35 | Morning | Sunday | 2016 | 7
3711 | 2016-07-17 08:23 | 2016-07-17 08:23 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 10 | 08:23 It was reported b/o fuse for Tx o/p #06-Q5-04B. (C.Duri fdr #15) 10:45 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #06-Q5-04B. Perform TTR, Megger test the Tx & found, good reading. Replaced b/o fuses above with the same size, then Energized the Tx. Cause: Animal. (Monkey) | 3239052 | 1 | 8:23 | Morning | Sunday | 2016 | 7
3712 | 2016-07-17 15:00 | 2016-07-17 15:00 | CENTRAL DURI POWER PLANT |  |  | - | 15:00 S/U CGT #3, then On line the Unit at 15:17. (Running on Test with Load 7.0MW) After Replaced HSAA Card & Adjust LVD of Gas control Valve. Also Running with Computer R & S. |  | 1 | 15:00 | Afternoon | Sunday | 2016 | 7
3713 | 2016-07-17 16:25 | 2016-07-17 16:25 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 15 | 16:19 Libo fdr #1 Load dropped 94A (103-9A). 16:25 Libo OCB fdr #1 T/R 2x. Not checked yet. | 3239052 | 1 | 16:25 | Afternoon | Sunday | 2016 | 7
3714 | 2016-07-17 16:25 | 2016-07-18 17:22 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 15 | Checked & found, Libo OCB fdr #1 T/R 2x Ctr: 370-372 R/F: 51@2. Patrolled the Line & found, @2 broken Pin Insulator o/p #KW-90. Cause: Lightning. | 3239052 | 1 | 16:25 | Afternoon | Sunday | 2016 | 7
3715 | 2016-07-17 16:30 | 2016-07-17 16:30 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 5 | Libo OCB fdr #2 T/R 1x. Not checked yet. | 3239052 | 1 | 16:30 | Afternoon | Sunday | 2016 | 7
3716 | 2016-07-17 16:30 | 2016-07-18 17:29 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 5 | Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 426-427 R/F: 51N. Patrolled the Line, but found nothing. Cause: Suspected by Lightning. | 3239052 | 1 | 16:30 | Afternoon | Sunday | 2016 | 7
3717 | 2016-07-17 16:32 | 2016-07-17 16:32 | 13.8KV CENTRAL DURI FEEDER #2 | Cloudy and Lightning | Lightning | 232 | 16:32 C.Duri fdr #2 Load dropped 54A (226-172A). 17:30 Checked & found, Recl. 08-M3-38 (C.Duri fdr #2) T/LO. Ctr: 130-134. Patrolled the line, but found nothing. 19:18 Blocked & closed Recl. 08-M3-38, but Tripped again. 19:35 Open LBS #08-M3-24. 19:44 Blocked & closed Recl. 08-M3-38, Ok. 19:57 Open LBS #08-M3-20. 20:00 Closed LBS #08-M3-24. 20:22 Open LBS #08-M3-01. 20:25 Closed LBS #08-M3-20. Then normalized block of Recl. 08-M3-38. Patrolled the line & found, @2 Broken L/A o/p #08-M2-01. Cause: Lightning. | 3239052 | 1 | 16:32 | Afternoon | Sunday | 2016 | 7
3718 | 2016-07-17 20:18 | 2016-07-17 20:18 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 26 | C.Duri fdr #1 Load dropped 47A (169-122A). Not checked yet. | 3239052 | 1 | 20:18 | Night | Sunday | 2016 | 7
3719 | 2016-07-17 20:18 | 2016-07-20 20:44 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 26 | Checked & found, Recl. 39AV-36 (C.Duri fdr #1) T/R 2x Ctr: 221-223. Patrolled the line & found, @1 broken L/A o/p #37AP-04A. Cause: Lightning. | 3239052 | 1 | 20:18 | Night | Sunday | 2016 | 7
3720 | 2016-07-18 13:52 | 2016-07-18 13:52 | MINAS SWITCH YARD | Fair | Unidentified | 192 | 13:52 Minas 115Kv GCB #20 T/O. Ctr: 75-76 R/F: 87B@2 & 86B. Minas 115Kv OCB #23 T/O. Ctr: 94-95. Minas 115Kv OCB #26 T/O. Ctr: 184-185. Minas 115Kv GCB #35 T/O. Ctr: 111-112. Minas 115Kv GCB #85 T/O. Ctr: 200-201. (No power to 115Kv Minas SWY BUS-2) Minas fdr #1 load dropped 16A (207-191A). . . . . . . . . . . . . . .GS1 Prod. loss: 0 Minas fdr #2 load dropped 10A (143-133A). . . . . . . . . . . . . . .GS1 Prod. loss: 0 Minas fdr #3 load dropped 33A (160-127A). . . . . . . . . . . . .. . GS2 Prod. loss: 85 Bbls, 34 Wells. Minas fdr #4 load dropped 78A (303-255A). . . . . . . . . . . . . . .GS2 Prod. loss: 49 Bbls, 19 Wells. MSU fdr #1 load dropped 220A (230-10A) -----Ex 8C fdr #3..GS1 Prod. loss: 0 MSU fdr #2 load dropped 168A (178-10A) -----Ex 8C fdr #1..GS1 Prod. loss: 62 Bbls, 39 Wells. ...GS2 Prod. loss: 17 Bbls, 8 Wells. ------------------------------------------- TOTAL Prod. loss: 213 Bbls,100 Wells. 8C fdr #4 load dropped 46A (234-188A) -----WIP. 8C fdr #5 load dropped 199A (199-0A) -----WIP. 8C fdr #6 load dropped 162A (179-17A) -----WIP. 8D fdr #6 load dropped 58A (190-132A) -----WIP. 14:30 Checked and found: Minas 115Kv GCB #20 T/O. and closed at:15:12. Minas 115Kv OCB #23 T/O. and closed at:17:04. Minas 115Kv OCB #26 T/O. and closed at:15:13. Minas 115Kv GCB #35 T/O. and closed at:15:16. Minas 115Kv GCB #85 T/O. and closed at:15:15. Patrolled the line, but found nothing. 15:09 Manually open Minas fdr #3, and closed at :15:36. (Due to GS-1 WIP problem / late to Re-S/U) Cause: Unidentified. | 3239054 | 1 | 13:52 | Afternoon | Monday | 2016 | 7
3721 | 2016-07-19 06:15 | 2016-07-19 06:15 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | 06:15 It was reported b/o fuse for Tx o/p #02-04-08. 09:20 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #02-04-08. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3239052 | 1 | 6:15 | Morning | Tuesday | 2016 | 7
3722 | 2016-07-19 15:17 | 2016-07-19 15:17 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 24 | Bangko fdr #1 Load dropped 67A (209-132A). Not Checked yet. | 3239052 | 1 | 15:17 | Afternoon | Tuesday | 2016 | 7
3723 | 2016-07-19 15:17 | 2016-07-22 08:30 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 24 | Checked & found, Recl. 29Y-21 (Bangko fdr #1) T/R 1x Ctr: 100-101. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239052 | 1 | 15:17 | Afternoon | Tuesday | 2016 | 7
3724 | 2016-07-19 18:25 | 2016-07-19 18:25 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Animal | 68 | 18:25 Menggala fdr #1 load dropped 93A (191-98A). (Ground fault alarm on Menggala fdr #1) 21:40 Checked & found, Recl. 19AO-01 (Menggala fdr #1) T/LO. Ctr: 455-459 R/F: 51@B. Patrolled the line & found, a Dead Monkey hang on the conductor o/p #20AP-01. 22:00 Blocked & Closed Recl. 19AO-01, Ok. Then released the block. Cause: Animal. (Monkey) | 3239052 | 1 | 18:25 | Afternoon | Tuesday | 2016 | 7
3725 | 2016-07-20 12:00 | 2016-07-20 12:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx at Well KB #065. Checked & found, @2 b/o 2.1SF fuse for 100Kva Tx at Well KB #065. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3239054 | 1 | 12:00 | Afternoon | Wednesday | 2016 | 7
3726 | 2016-07-20 15:45 | 2016-07-20 15:45 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 58 | 15:45 It was reported b/o fuse for Tx o/p #08-M1-22. (C.Duri fdr #2) 17:00 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #08-M1-22. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3239052 | 1 | 15:45 | Afternoon | Wednesday | 2016 | 7
3727 | 2016-07-20 16:49 | 2016-07-20 16:49 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 0 | So.Bekasap fdr #1 Load dropped 147A (164-17A). Not checked yet. | 3239052 | 1 | 16:49 | Afternoon | Wednesday | 2016 | 7
3728 | 2016-07-20 16:49 | 2016-07-28 07:45 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 36BI-04 (So.Bekasap fdr #1) T/R 1x Ctr: 734-735. Patrolled the line & found: -@3 Broken Pin Insulator o/p #35BK-09. -@3 Broken Pin Insulator o/p #35BK-19. -@3 Broken Pin Insulator o/p #35BL-02. -@1,@2 Broken Dead end Insulator o/p #34BI-20. -@1 Broken Dead end Insulator o/p #34BJ-08. Cause: Lightning. | 3239052 | 1 | 16:49 | Afternoon | Wednesday | 2016 | 7
3729 | 2016-07-20 18:31 | 2016-07-20 18:31 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 36 | 8D OCB fdr #5 T/R 1x. 8D fdr #1 load dropped 59A (144-85A). 8D fdr #2 load dropped 44A (113-69A). 8D fdr #3 load dropped 32A (140-108A). 8D fdr #4 load dropped 47A (175-128A). Not checked yet. | 3239054 | 1 | 18:31 | Afternoon | Wednesday | 2016 | 7
3730 | 2016-07-20 18:31 | 2016-07-24 15:30 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 36 | Checked & found, 8D OCB fdr #5 T/R 1x Ctr: 498-499 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 18:31 | Afternoon | Wednesday | 2016 | 7
3731 | 2016-07-21 09:30 | 2016-07-21 09:30 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 14 | 09:30 Shutdown Well #6E-96 & #7E-11, then Open HLC o/p #7E-125. To cutting trees under power line. 16:00 Closed HLC o/p #7E-125 & Re-S/U the wells. Cause: Plan Maintenance. | 123 | 1 | 9:30 | Morning | Thursday | 2016 | 7
3732 | 2016-07-21 09:53 | 2016-07-21 09:53 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 703 | 09:53 Manually open Recl. 39AV-36 (C.Duri fdr #1). To Replacing Recl. 38AS-09 and Some Pin insulator to Post type Insulator. 15:53 Closed Recl. 39AV-36. Cause: Plan maintenance. Prod. loss reported by EC: Puncak/Lincak = 456 Bbls / 20 Wells. Kulin = 247 Bbls / 30 Wells. Total Prod. loss= 703 Bbls / 50 Wells. | 123 | 1 | 9:53 | Morning | Thursday | 2016 | 7
3733 | 2016-07-21 10:00 | 2016-07-21 10:00 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Broken Fuse Cut Out | 0 | 10:00 It was reported b/o fuse for Tx o/p #04-03-10. 16:15 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-03-10. Also found @3 b/o FCO o/p above. Replaced @3 b/o FCO and @3 b/o fuse with same size, then energized the Tx. Cause: Broke FCO. | 3239052 | 1 | 10:00 | Morning | Thursday | 2016 | 7
3734 | 2016-07-21 14:35 | 2016-07-21 14:35 | 13.8KV 8D FEEDER #5 | Fair | Transformer Failure | 40 | It was reported b/o fuse for Tx at Well #8D-29E. Checked & found, @1,@2,@3 b/o 7.8SF fuses for 300Kva Tx at Well #8D-29E. Performed TTR, Megger test the Tx & found, Low Megger reading. Cause: Tx failure. (The Tx failure is not replaced yet) | 3239054 | 1 | 14:35 | Afternoon | Thursday | 2016 | 7
3735 | 2016-07-21 14:35 | 2016-07-22 15:20 | 13.8KV 8D FEEDER #5 | Fair | Transformer Failure | 40 | Replaced 300Kva Tx failure with the same size at Well #8D-29E & energized the Tx. Cause: Tx failure. | 3239054 | 1 | 14:35 | Afternoon | Thursday | 2016 | 7
3736 | 2016-07-22 00:25 | 2016-07-22 00:25 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 31 | Bekasap main VCB fdr #6 T/R 1x. Not checked yet | 3239052 | 1 | 0:25 | Night | Friday | 2016 | 7
3737 | 2016-07-22 00:25 | 2016-07-27 15:25 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 31 | Checkd & found, Bekasap main VCB fdr #6 T/R 2x Ctr: 342-344 R/F: 51N. Patrolled the line & found, @1 broken L/A on TP of Well Aman #03. Cause: Lightning. | 3239052 | 1 | 0:25 | Night | Friday | 2016 | 7
3738 | 2016-07-22 00:52 | 2016-07-22 00:52 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 42 | 00:52 Libo OCB fdr #2 T/R 1x. 14:45 Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 247-248 R/F: 51N. Patrolled the line & found, @3 F/O Pin Insulator o/p #KW-125B. Cause: Lightning. | 3239052 | 1 | 0:52 | Night | Friday | 2016 | 7
3739 | 2016-07-22 01:37 | 2016-07-22 01:37 | 115KV KOTABATAK - PETAPAHAN LINE | Rain and Lightning | Lightning | 1270 | 01:37 115KV KOTABATAK OCB #1 (Line to Petapahan) T/R 1x. (Petapahan & Suram Substations are no power) OKB fdr#2 Load dropped 210A (249-39A),.....................Prod.Loss: 70 Bbls,64 Wells NKB fdr #3 Load dropped 155A (379-224A)...................Prod.Loss: 161 Bbls,72 Wells NKB fdr #4 Load dropped 30A (73-43A). T/O WIP. NKB fdr #5 Load dropped 196A (229-33A). T/O WIP. CKB fdr #1 Load dropped 57A (90-33A)........................Prod.Loss: 33 Bbls,18 Wells CKB fdr #2 Load dropped 232A (238-6A). T/O WIP. CKB fdr #3 Load dropped 11A (69-58A)........................Prod.Loss: 23 Bbls,13 Wells CKB fdr #5 Load dropped 274A (317-43A)....................Prod.Loss: 107 Bbls,70 Wells CKB fdr #6 Load dropped 138A (192-54A).....................Prod.Loss: 96 Bbls,61 Wells ---------------------------------- TOTAL KB GS : 490 Bbls,298 Wells PET fdr #1 No Power ...................................................Prod.Loss: 44 Bbls,21 Wells PET fdr #2 No Power ...................................................Prod.Loss:571 Bbls,83 Wells SRM fdr #1 No Power ..................................................Prod.Loss: 5 Bbls,3 Wells SRM fdr #2 No Power ..................................................Prod.Loss: 0 Bbls,0 Wells --------------------------------- TOTAL PET.GS : 620 Bbls,107 Wells 14:10 Checked & found, 115KV KOTABATAK OCB #1 T/R 1x Ctr: 35-36 R/F: 51@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 1:37 | Night | Friday | 2016 | 7
3740 | 2016-07-22 14:00 | 2016-07-22 14:00 | MINAS POWER PLANT |  |  | - | 14:00 Off line MGT #6, then S/D the Unit for S/B. | 123 | 1 | 14:00 | Afternoon | Friday | 2016 | 7
3741 | 2016-07-22 20:21 | 2016-07-22 20:21 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Pin Insulator | 34 | 20:21 6DN fdr #2 Load dropped 26A (88-62A). 24:00 Checked & found, Recl. 6D-50 (6DN fdr #2) T/SO. Ctr: 54-55. Blocked & closed the Recloser, OK. Then Released the block. Patrolled the Line & found, @3 F/O Pin Insulator o/p #..... Cause: Pin Insulator. | 3239054 | 1 | 20:21 | Night | Friday | 2016 | 7
3742 | 2016-07-22 20:21 | 2016-07-23 10:26 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Pin Insulator | 34 | 10:26 It was reported no power at downstream of 6DN fdr #6. (Some wells were off, #6D-34E, #35, #45, #54N & #6D-56) Checked & found, Recl. #6D-50 condition & found, in close but Voltage unbalance. 11:02 Mannually open Recl. #6D-50. Closed LBS #6D-09 to transfer load d/s Rcel. #6D-50 to 6D fdr #3. Cause: Control failure (Recl.). | 3239054 | 1 | 20:21 | Night | Friday | 2016 | 7
3743 | 2016-07-22 21:45 | 2016-07-22 21:45 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 22 | 21:45 It was reported b/o fuse for Tx at Well Bangko #243. (Bangko fdr #4) Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Bangko #243. Performed TTR and megger the Tx, found Low Mega Ohm reading. Cause: Tx Failure. (Low Megger reading) ( The Tx is not replaced yet) | 3239052 | 1 | 21:45 | Night | Friday | 2016 | 7
3744 | 2016-07-22 21:45 | 2016-07-23 11:02 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 22 | 11:02 Replaced 150Kva Tx failure with 300Kva Tx at Well Bangko #243 & energized the Tx. Cause: Tx Failure. (Low megger reading) | 3239052 | 1 | 21:45 | Night | Friday | 2016 | 7
3745 | 2016-07-23 08:45 | 2016-07-23 08:45 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 0 | 08:45 It was reported b/o fuse for Tx o/p #06-R5-15. 10:22 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #06-R5-15. Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal (Monkey). | 3239052 | 1 | 8:45 | Morning | Saturday | 2016 | 7
3746 | 2016-07-23 15:15 | 2016-07-23 15:15 | MINAS POWER PLANT |  |  | - | 15:15 S/U MGT #9, then on line the Unit at 16:13. (Running on test with max load 16.0MW / after replacing Generator rotor) |  | 1 | 15:15 | Afternoon | Saturday | 2016 | 7
3747 | 2016-07-23 22:33 | 2016-07-23 22:33 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 9 | 4D OCB fdr #3 T/R 1x. Not checked yet. | 3239054 | 1 | 22:33 | Night | Saturday | 2016 | 7
3748 | 2016-07-23 22:33 | 2016-07-24 15:45 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 9 | Checked & found, 4D OCB fdr #3 T/R 1x Ctr: 358-359 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 22:33 | Night | Saturday | 2016 | 7
3749 | 2016-07-23 22:40 | 2016-07-23 22:40 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 66 | 4D OCB fdr #2 T/R 1x. Not checked yet. | 3239054 | 1 | 22:40 | Night | Saturday | 2016 | 7
3750 | 2016-07-23 22:40 | 2016-07-24 15:40 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 66 | Checked & found, 4D OCB fdr #2 T/R 1x Ctr: 214-215 R/F: 51N. Patrolled the line & found: -@2 Broken Pin Insulator o/p #4D-102. -@1,@3 Broken Pin Insulators o/p #4D-100. Cause: Lightning. | 3239054 | 1 | 22:40 | Night | Saturday | 2016 | 7
3751 | 2016-07-23 22:45 | 2016-07-23 22:45 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 31 | 3D OCB fdr #3 T/R 1x. 3D fdr #2 Load dropped 100A (211-111A). 3D fdr #4 Load dropped 58A (227-169A). Not checked yet. | 3239054 | 1 | 22:45 | Night | Saturday | 2016 | 7
3752 | 2016-07-23 22:45 | 2016-07-28 14:25 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 31 | Checked & found, 3D OCB fdr #3 T/R 1x Ctr: 437-438 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 22:45 | Night | Saturday | 2016 | 7
3753 | 2016-07-24 06:10 | 2016-07-24 06:10 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Tree | 0 | Duri Community ACB fdr #3 T/R 2x. Not checked yet. | 3239052 | 1 | 6:10 | Morning | Sunday | 2016 | 7
3754 | 2016-07-24 06:10 | 2016-07-28 08:45 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Tree | 0 | Checked & found, Duri Community ACB fdr #3 T/R 2x Ctr: 53-55 R/F: 51N. Patrolled the line & found: -High danger trees near pole #DK-09, #SG-02, #DK-03. -@1 Flashed over Dead end Insulator o/p #6F-06. Cause: Tree. | 3239052 | 1 | 6:10 | Morning | Sunday | 2016 | 7
3755 | 2016-07-24 09:12 | 2016-07-24 09:12 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 0 | 09:12 It was repoted b/o fuse for Tx o/p #07-V1-33. 10:45 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p above. Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal (Bird). | 3239052 | 1 | 9:12 | Morning | Sunday | 2016 | 7
3756 | 2016-07-24 13:37 | 2016-07-24 13:37 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 42 | 4D OCB fdr #4 T/R 1x. Not checked yet. | 3239054 | 1 | 13:37 | Afternoon | Sunday | 2016 | 7
3757 | 2016-07-24 13:37 | 2016-07-26 15:20 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 42 | Checked & found, 4D OCB fdr #4 T/R 1x Ctr: 235-236 R/F: 51N. Patrolled the line & found: -@3 Broken L/A o/p #5D-94. -@1,@2 Broken Pin Insulators o/p #36DN-38. Cause: Lightning. | 3239054 | 1 | 13:37 | Afternoon | Sunday | 2016 | 7
3758 | 2016-07-24 18:09 | 2016-07-24 18:09 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 15 | 4B OCB fdr #2 T/R 1x. Not checked yet. | 3239054 | 1 | 18:09 | Afternoon | Sunday | 2016 | 7
3759 | 2016-07-24 18:09 | 2016-07-30 16:00 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 15 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 227-228 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 18:09 | Afternoon | Sunday | 2016 | 7
3760 | 2016-07-24 18:13 | 2016-07-24 18:13 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 18 | 4B OCB fdr #1 T/R 1x. Not checked yet. | 3239054 | 1 | 18:13 | Afternoon | Sunday | 2016 | 7
3761 | 2016-07-24 18:13 | 2016-07-26 15:10 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 18 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 281-282 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 18:13 | Afternoon | Sunday | 2016 | 7
3762 | 2016-07-24 18:24 | 2016-07-24 18:24 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 6 | 18:24 5B fdr #4 Load dropped 182A (250-68A). 20:50 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO. Ctr: 60-61. Blocked & Closed the Recloser, OK. Then released the block. Not Patrolled yet yet. | 3239054 | 1 | 18:24 | Afternoon | Sunday | 2016 | 7
3763 | 2016-07-24 18:24 | 2016-07-26 15:15 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 6 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 18:24 | Afternoon | Sunday | 2016 | 7
3764 | 2016-07-24 18:58 | 2016-07-24 18:58 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 0 | 6DN fdr #6 Load dropped 130A (196-66A). Not checked yet. | 3239054 | 1 | 18:58 | Afternoon | Sunday | 2016 | 7
3765 | 2016-07-24 18:58 | 2016-07-28 14:20 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 6E-64 (6DN fdr #6) T/R 1x Ctr: 39-40 R/F: 51N. Patrolled the line & found, @2 broken L/A o/p #6E-53. Cause: Lightning. | 3239054 | 1 | 18:58 | Afternoon | Sunday | 2016 | 7
3766 | 2016-07-24 19:11 | 2016-07-24 19:11 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 49 | 6DN OCB fdr #6 T/R 1x. Not checked yet. | 3239054 | 1 | 19:11 | Night | Sunday | 2016 | 7
3767 | 2016-07-24 19:11 | 2016-07-28 14:15 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 49 | Checked & found, 6DN OCB fdr #6 T/R 1x Ctr: 346-347 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 19:11 | Night | Sunday | 2016 | 7
3768 | 2016-07-24 19:24 | 2016-07-24 19:24 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | 3D fdr #4 Load dropped 139A (218-79A). Not checked yet. | 3239054 | 1 | 19:24 | Night | Sunday | 2016 | 7
3769 | 2016-07-24 19:24 | 2016-07-27 15:20 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 2D-33 (3D fdr #4) T/R 1x Ctr: 28-29. Patrolled the line & found, @1 broken L/A on TP of Well #2D-32. Cause: Lightning. | 3239054 | 1 | 19:24 | Night | Sunday | 2016 | 7
3770 | 2016-07-24 20:00 | 2016-07-24 20:00 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT #4, then S/D the Unit for S/B. (Prior to C/I program) 25-July-2016. 01:20 S/U CGT #4, then on line the Unit at 01:44. (Postpone to C/I program, due to CGT #3 Generator breaker Trip) |  | 1 | 20:00 | Night | Sunday | 2016 | 7
3771 | 2016-07-24 23:30 | 2016-07-24 23:30 | CENTRAL DURI POWER PLANT | Drizzle | Under investigation | 0 | CGT #3 Open Generator breaker by Alarm: l68-30. (32 Reverse Power) (Then S/D the Unit due to fail to On Line) Cause: Under Investigation. | 3239052 | 1 | 23:30 | Night | Sunday | 2016 | 7
3772 | 2016-07-25 01:20 | 2016-07-25 01:20 | CENTRAL DURI POWER PLANT |  |  | - | 01:20 S/U CGT #4, then on line the Unit at 01:44. (Postpone to C/I program, due to CGT #3 Generator breaker Trip) |  | 1 | 1:20 | Night | Monday | 2016 | 7
3773 | 2016-07-25 09:27 | 2016-07-25 09:27 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 7 | 09:27 It was reported b/o fuse for Tx o/p #07-V1-15. (D.Field fdr #1) 10:16 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-V1-15. Tested TTR and Megger found, good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unindentified (Fuse). | 3239052 | 1 | 9:27 | Morning | Monday | 2016 | 7
3774 | 2016-07-25 11:17 | 2016-07-25 11:17 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 25 | Sintong fdr #2 load dropped 185A (211-16A). Sintong fdr #1 load dropped 12A (71-59A). Sintong GFPC in By pass and block position. Not checked yet. | 3239052 | 1 | 11:17 | Morning | Monday | 2016 | 7
3775 | 2016-07-25 11:17 | 2016-07-27 09:30 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 25 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 414-415 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3239052 | 1 | 11:17 | Morning | Monday | 2016 | 7
3776 | 2016-07-25 12:31 | 2016-07-25 12:31 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified (Fuse) | 14 | 12:31 It was reported b/o fuse for Tx at Well Pemburu #21. (Batang fdr #3) 15:51 Checked & found, @2 b/o 2.1SF fuse for 100Kva Tx at Well Pemburu #21. Tested TTR and Megger found, good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unindentified (Fuse). | 3239052 | 1 | 12:31 | Afternoon | Monday | 2016 | 7
3777 | 2016-07-25 14:30 | 2016-07-25 14:30 | CENTRAL DURI POWER PLANT |  |  | - | 14:30 S/U CGT #3, then on line the Unit at 14:50. (Running on test) |  | 1 | 14:30 | Afternoon | Monday | 2016 | 7
3778 | 2016-07-25 14:38 | 2016-07-25 14:38 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr #1 Load dropped 40A (162-122A). Not checked yet. | 3239052 | 1 | 14:38 | Afternoon | Monday | 2016 | 7
3779 | 2016-07-25 14:38 | 2016-07-26 15:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/R 3x Ctr: 189-192. Patrolled the line, but found nothing. Cause: Unidentified. | 3239052 | 1 | 14:38 | Afternoon | Monday | 2016 | 7
3780 | 2016-07-26 02:06 | 2016-07-26 02:06 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 41 | 8C VCB fdr #6 T/R 1x. Not checked yet. | 3239054 | 1 | 2:06 | Night | Tuesday | 2016 | 7
3781 | 2016-07-26 02:06 | 2016-07-28 14:00 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 41 | Checked & found, 8C VCB fdr #6 T/R 1x Ctr: 560-561 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 2:06 | Night | Tuesday | 2016 | 7
3782 | 2016-07-26 04:56 | 2016-07-26 04:56 | CENTRAL DURI POWER PLANT |  |  | - | 04:56 CGT #3 Generator Breaker T/O. 05:46 Closed CGT #3 Generator Breaker & T/O again. 05:51 S/D CGT #3, for S/B-Status. (Being Investigated) |  | 1 | 4:56 | Morning | Tuesday | 2016 | 7
3783 | 2016-07-26 13:20 | 2016-07-26 13:20 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 159 | Ketigul fdr #2 load dropped 142A (195-53A). Not checked yet. | 3239052 | 1 | 13:20 | Afternoon | Tuesday | 2016 | 7
3784 | 2016-07-26 13:20 | 2016-07-31 07:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 159 | Checked All Recloser at downstream & found, normal. (Counter: Did not operate.) Patrolled the line, but found nothing. Cause: Unidentigied. Note: The Reclosers at downstream of Ketigul fdr #2 are needed to Functional test. | 3239052 | 1 | 13:20 | Afternoon | Tuesday | 2016 | 7
3785 | 2016-07-26 23:44 | 2016-07-26 23:44 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 33 | Petani OCB fdr #1 T/R 1x. (Petani RTU failed at that time) Not checked yet. | 3239052 | 1 | 23:44 | Night | Tuesday | 2016 | 7
3786 | 2016-07-26 23:44 | 2016-07-28 15:00 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 33 | Checked & found, Petani OCB fdr #1 T/R 1x Ctr: 25-26 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3239052 | 1 | 23:44 | Night | Tuesday | 2016 | 7
3787 | 2016-07-26 23:44 | 2016-07-26 23:44 | 13.8KV RANGAU FEEDER #2 | Fair | Animal | 0 | Rangau fdr #2 Load dropped 26A (71-45A). Not checked yet. | 3239052 | 1 | 23:44 | Night | Tuesday | 2016 | 7
3788 | 2016-07-26 23:44 | 2016-07-27 15:45 | 13.8KV RANGAU FEEDER #2 | Fair | Animal | 0 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 5x Ctr: 135-140. Patrolled the line & found, a dead Monkey under pole #22BC-04. Cause: Animal. (Monkey) | 3239052 | 1 | 23:44 | Night | Tuesday | 2016 | 7
3789 | 2016-07-27 07:00 | 2016-07-27 07:00 | 13.8KV RANGAU FEEDER #2 | Fair | Animal | 0 | 07:00 Rangau fdr #2 Load dropped 56A (71-15A). 07:13 Rangau fdr #2 Load dropped 60A (71-11A). Not checked yet. | 3239052 | 1 | 7:00 | Morning | Wednesday | 2016 | 7
3790 | 2016-07-27 07:00 | 2016-07-28 07:30 | 13.8KV RANGAU FEEDER #2 | Fair | Animal | 0 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 5x Ctr: 135-140. Patrolled the line & found, a dead Monkey under pole #22BC-04. Cause: Animal. (Monkey) | 3239052 | 1 | 7:00 | Morning | Wednesday | 2016 | 7
3791 | 2016-07-27 08:03 | 2016-07-27 08:03 | 13.8KV BEKASAP FEEDER #6 | Cloudy and Lightning | Lightning | 90 | 08:03 Bekasap VCB fdr #6 T/R 1x. 08:21 Bekasap VCB fdr #6 T/R 1x. Not checked yet. | 3239052 | 1 | 8:03 | Morning | Wednesday | 2016 | 7
3792 | 2016-07-27 08:03 | 2016-07-28 14:45 | 13.8KV BEKASAP FEEDER #6 | Cloudy and Lightning | Lightning | 90 | Checked & found, Bekasap main VCB fdr #6 T/R 2x Ctr: 342-344 R/F: 51N. Patrolled the line & found: -@1 Broken L/A on TP of Well Aman #03. -@1 Broken Pin Insulator o/p #39BF-12. Cause: Lightning. | 3239052 | 1 | 8:03 | Morning | Wednesday | 2016 | 7
3793 | 2016-07-27 14:44 | 2016-07-27 14:44 | 13.8KV PUNGUT FEEDER #1 | Fair | Unidentified | 34 | 14:44 Pungut OCB fdr #1 T/O. (In block position due to PT Multi Structure crossing pipe) 14:55 Blocked & closed Pungut OCB fdr #1, Ok. Then released the block. Not checked & patrolled yet. | 3239052 | 1 | 14:44 | Afternoon | Wednesday | 2016 | 7
3794 | 2016-07-27 14:44 | 2016-07-28 14:30 | 13.8KV PUNGUT FEEDER #1 | Fair | Unidentified | 34 | Checked & found, Pungut OCB fdr #1 T/R 1x Ctr: 349-350 R/F: 50N. Patrolled the line, but found nothing. Cause: Unidentified. | 3239052 | 1 | 14:44 | Afternoon | Wednesday | 2016 | 7
3795 | 2016-07-28 10:48 | 2016-07-28 10:48 | 13.8KV 4D FEEDER #5 | Fair | Planned Maintenance | 22 | 10:48 Manually opened 4D OCB fdr #5. To replacing @1, @3 seriously broken Pin Insulator o/p #4D-101. 11:01 Manually closed 4D OCB fdr #5. Cause: Plan Maintenance. | 123 | 1 | 10:48 | Morning | Thursday | 2016 | 7
3796 | 2016-07-29 11:47 | 2016-07-29 11:47 | 13.8KV ROKAN FEEDER #2 | Fair | Dead End Insulator | 13 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3239052 | 1 | 11:47 | Morning | Friday | 2016 | 7
3797 | 2016-07-29 11:47 | 2016-01-08 17:40 | 13.8KV ROKAN FEEDER #2 | Fair | Dead End Insulator | 13 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 1239-1240 R/F: 51@1. Patrolled the line & found, @1 F/O Dead end Insulator o/p #27AV-70. Cause: Dead end Insulator. | 3239052 | 1 | 11:47 | Morning | Friday | 2016 | 7
3798 | 2016-07-29 14:30 | 2016-07-29 14:30 | 13.8KV CENTRAL KOTABATAK FEEDER #2 | Fair | Animal | 27 | 14:30 It was reported b/o fuse for Tx at Well KB #349 & #89. 15:54 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well KB #129. Performed TTR, Megger test the Tx & found, normal. (Good reading) Replaced the b/o fuse above with same size, then energized the Tx. Cause: Animal. (Squirrel) | 3239054 | 1 | 14:30 | Afternoon | Friday | 2016 | 7
3799 | 2016-07-29 15:46 | 2016-07-29 15:46 | CENTRAL DURI POWER PLANT |  |  | - | 15:46 Off line CGT #4, then S/D the Unit at 15:55. (For S/B-Prior to closing Guilotine of HRSG-4 for certification) 30-July-2016. 21:08 S/U CGT #4, then on line the Unit at 21:58. (After closing Guilotine of HRSG-4) |  | 1 | 15:46 | Afternoon | Friday | 2016 | 7
3800 | 2016-07-29 16:00 | 2016-07-29 16:00 | CENTRAL DURI SWITCH YARD | Fair | Substation Failure (Tx SS) | 0 | 16:00 C.Duri 13.8KV ACB #44 T/O. C.Duri 115 KV OCB #63 T/O. C.Duri 115 KV OCB #65 T/O. (When adjusting LTC of Tx-4, due to S/D CGT #4 for repairing 12" gas line leakage ) (115KV C.Duri Power Tx. Tripped & 13.8KV C.Duri Bus-4 no power) C.Duri ACB fdr #9, fdr #10 & fdr #11 are no power. 16:02 Closed C.Duri ACB #39. (Tie Breaker) for energizing C.Duri Bus #4 & the fdrs. Checked & found: R/F: 87@2 & 86T. 16:59 Closed 115KV OCB #63, but T/O again. (with the same Relay flag / 87@2 & 86T) 17:10 Closed 115KV OCB #63, but T/O again. (With the same Relay flag / 87@2 & 86T) (After functional test by adjusting LTC Tx back to Rais-13) Cause: Under Investigation. (Suspected @2 TX #4 LTC contactor problem) | 3239052 | 1 | 16:00 | Afternoon | Friday | 2016 | 7
3801 | 2016-07-30 06:57 | 2016-07-30 06:57 | 115KV NELLA SW. STA - PINANG LINE | Cloudy | Improper Protection | 324 | 06:57 115KV Nella GCB #27 (115KV Nella-Pinang line) Trippep by R/F: 51G & 86T. (Pinang Substation no power) 07:52 Checked & found at Nella Substation : * Nella 115 KV GCB #27 T/O. Ctr: 182-183 R/F: 51G & 86T. (Relay T-60 Pinang operate / Pinang Tx lock out) Also found, Pinang Substation: * Pinang OCB fdr #1 T/SO. Ctr: 407-408 R/F: 51G & 51N. (Then Resetting the UR Relay) 09:42 Blocked & closed 115KV Nella GCB #27, Ok. Then released the block. 09:51 Blocked & closed 13.8KV Pinang OCB fdr #1, Ok. Then released the block. Cause: Under Investigation. | 3239052 | 1 | 6:57 | Morning | Saturday | 2016 | 7
3802 | 2016-07-30 13:03 | 2016-07-30 13:03 | 13.8KV DURI FIELD FEEDER #3 | Fair | Animal | 16 | 13:03 It was reported b/o fuse for Tx o/p #01-05-10. 15:45 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #01-05-10. Replaced b/o fuses above with same size, then energized the Tx. Cause: Animal. (Chivet) | 3239052 | 1 | 13:03 | Afternoon | Saturday | 2016 | 7
3803 | 2016-07-30 14:52 | 2016-07-30 14:52 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain and Lightning | Lightning | 93 | 14:52 NKBS VCB #3 T/R 1X. NKBS VCB #4 load dropped 19A (57-38A). NKBS VCB #5 load dropped 192A (230-38A) To WIP. 14:53 NKBS VCB #3 T/R 1X again. Cause : Not checked yet. | 3239054 | 1 | 14:52 | Afternoon | Saturday | 2016 | 7
3804 | 2016-07-30 14:52 | 2016-07-31 16:20 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain and Lightning | Lightning | 93 | Checked & found, NKBS OCB fdr #3 T/R 2x Ctr: 271-273 R/F: 51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 14:52 | Afternoon | Saturday | 2016 | 7
3805 | 2016-07-30 15:02 | 2016-07-30 15:02 | 13.8KV PUNGUT FEEDER #1 | Cloudy and Lightning | Lightning | 54 | Pungut OCB fdr #1 T/R 1x. Not checked yet. | 3239052 | 1 | 15:02 | Afternoon | Saturday | 2016 | 7
3806 | 2016-07-30 15:02 | 2016-01-08 16:45 | 13.8KV PUNGUT FEEDER #1 | Cloudy and Lightning | Lightning | 54 | Checked & found, Pungut OCB fdr #1 T/R 1x Ctr: 350-351 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239052 | 1 | 15:02 | Afternoon | Saturday | 2016 | 7
3807 | 2016-07-30 15:02 | 2016-07-30 15:02 | 13.8KV PUNGUT FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Pungut OCB fdr #2 T/R 1x. Not checked yet. | 3239052 | 1 | 15:02 | Afternoon | Saturday | 2016 | 7
3808 | 2016-07-30 15:02 | 2016-01-08 17:00 | 13.8KV PUNGUT FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Checked & found, Pungut OCB fdr #2 T/R 1x Ctr: 345-346 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239052 | 1 | 15:02 | Afternoon | Saturday | 2016 | 7
3809 | 2016-07-30 15:22 | 2016-07-30 15:22 | 13.8KV KOTABATAK FEEDER #2 | Cloudy and Lightning | Lightning | 18 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3239054 | 1 | 15:22 | Afternoon | Saturday | 2016 | 7
3810 | 2016-07-30 15:22 | 2016-07-31 14:00 | 13.8KV KOTABATAK FEEDER #2 | Cloudy and Lightning | Lightning | 18 | Checked & found, OKBS OCB fdr #2 T/R 1x Ctr: 1260-1261 R/F: 51@1. Patrolled the line & found, @1 broken Dead end Insulator o/p #38CW-07. Cause: Lightning. | 3239054 | 1 | 15:22 | Afternoon | Saturday | 2016 | 7
3811 | 2016-07-30 16:22 | 2016-07-30 16:22 | 13.8KV LIBO FEEDER #1 | Fair | Animal | 5 | 16:22 It was reported b/o fuse for Tx at Well SE.Libo #06. 17:05 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well SE.Libo #06. Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal. (Bird) | 3239052 | 1 | 16:22 | Afternoon | Saturday | 2016 | 7
3812 | 2016-07-30 16:42 | 2016-07-30 16:42 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 15 | 3D fdr #4 Load dropped 137A (217-80A). 3D GFPC-TX #1 T/R 1x. Not checked yat. | 3239054 | 1 | 16:42 | Afternoon | Saturday | 2016 | 7
3813 | 2016-07-30 16:42 | 2016-06-08 08:46 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 15 | Checked & found, Recl. 2D-33 (3D fdr #4) T/R 1x Ctr: 29-30 R/F: 51N. Patrolled the Line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 16:42 | Afternoon | Saturday | 2016 | 7
3814 | 2016-07-30 17:09 | 2016-07-30 17:09 | 13.8KV 4B FEEDER #1 | Cloudy and Lightning | Lightning | 24 | 4B OCB fdr #1 T/R 1x. Not checked yet. | 3239054 | 1 | 17:09 | Afternoon | Saturday | 2016 | 7
3815 | 2016-07-30 17:09 | 2016-03-08 08:55 | 13.8KV 4B FEEDER #1 | Cloudy and Lightning | Lightning | 24 | Checked & found, 4B OCB fdr #1 T/R 2x Ctr: 282-284 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3239054 | 1 | 17:09 | Afternoon | Saturday | 2016 | 7
3816 | 2016-07-30 21:08 | 2016-07-30 21:08 | CENTRAL DURI POWER PLANT |  |  | - | 21:08 S/U CGT #4, then on line the Unit at 21:58. (After closing Guilotine of HRSG-4) |  | 1 | 21:08 | Night | Saturday | 2016 | 7
3817 | 2016-07-31 08:34 | 2016-07-31 08:34 | NORTH DURI POWER PLANT | Fair | Others | 603 | 08:34 NDC-CT #1 Tripped. By alarm: Lube oil temp high. (Load capability: 87.9 MW) Found: 480V Breaker for cooling Fan system Tripped. - Frequency dropped to 59.2Hz. (Load shedding Level-3) A. Frequency : 59.6. 1. 5B feeder #7 Closed at: 09:51. (Transfer to 3D feeder #3). 2. 5B feeder #5 Closed at: 10:25. 3. 4D feeder #3 Closed at: 09:56. 4. 4D feeder #5 Closed at: 09:47. 5. 3D feeder #5 Closed at: 08:52. (Transfer to 3D feeder #6). 6. 5B feeder #4 Closed at: 10:24. B. Frequency : 59.4. 7. 4D feeder #4 Closed at: 09:47. 8. 4D feeder #2 Closed at: 09:47. (Transfer to 4D feeder #5). 9. 4B feeder #6 Closed at: 09:15. 10.4D feeder #6 Closed at: 09:52. 11.4B feeder #4 Closed at: 08:48. C. Frequency :59.2. 12. Suram feeder #1 Closed at: 09:09. 13. Suram feeder #2 Normal. 14. Rokan feeder #2 Normal. 15. 3D feeder #3 Closed at: 09:53. 16. 8C feeder #2 Closed at: 09:08. 17. 8D feeder #3 Closed at: 09:08. 18. 8D feeder #1 Closed at: 09:08. 19. 8C feeder #5 Normal. @ Minas feeder #3 Closed at : 10:16. (Load shedding level #7). @ 3 Delta feeder #6 Closed at : 08:52. (Load shedding level #8). @ 8 Delta feeder #10 Closed at : 10:20. (Load shedding level #5). 09:05 S/U MGT #6, then On Line the unit at 09:34. 09:56 S/U MGT #7, then On Line the unit at 10:17. 10:50 S/U MGT #8, then On Line the unit at 11:23. 15:09 S/U NDC-CT #1, then online the unit at 15:45. 17:55 Offline MGT #8, then S/D the unit for S/B. 18:08 Offline MGT #9, then S/D the unit for S/B. 20:06 Offline MGT #6, then S/D the unit for S/B. Cause: Others. (Lube oil temperature High / 480V breaker for cooling Fan system Tripped)) Prod Loss: 1. GS #1 : 174 Bbls / 45 Wells. 2. GS #2 : 135 Bbls / 34 Wells. 3. GS #3 : 82 Bbls / 22 Wells. 4. GS #4 : 53 Bbls / 16 Wells. 5. GS #5 : 197 Bbls / 110 Wells. 6. GS #6 : 139 Bbls / 54 Wells. ------------------------------------- Total : 780 Bbls / 281 Wells | 3239052 | 1 | 8:34 | Morning | Sunday | 2016 | 7
3818 | 2016-07-31 09:05 | 2016-07-31 09:05 | MINAS POWER PLANT |  |  | - | 09:05 S/U MGT #6 then online the unit at 09:34. (For replacing NDC #1 Trip) 20:06 Offline MGT #6 then S/D the unit for S/B. |  | 1 | 9:05 | Morning | Sunday | 2016 | 7
3819 | 2016-07-31 09:56 | 2016-07-31 09:56 | MINAS POWER PLANT |  |  | - | 09:56 S/U MGT #7 then online the unit at 10:17. (For replacing NDC #1 Trip). |  | 1 | 9:56 | Morning | Sunday | 2016 | 7
3820 | 2016-07-31 10:50 | 2016-07-31 10:50 | MINAS POWER PLANT |  |  | - | 10:50 S/U MGT #8 then online the unit at 11:23. (For replacing NDC #1 Trip) 17:55 Offline MGT #8, then S/D the unit for S/B. |  | 1 | 10:50 | Morning | Sunday | 2016 | 7
3821 | 2016-07-31 13:09 | 2016-07-31 13:09 | 13.8KV LIBO FEEDER #2 | Fair | Powerline - Conductor | 101 | 13:09 Libo fdr #2 Load dropped 23A (42-19A). 14:08 Checked & found, Recl. 23BW-02 T/LO ctr: 230-234. Patrolled the line & found, @2 broken conductor o/p #23BW-17. 20:10 Blocked & closed Recl. 23BW-02, Ok. Then released the block. (After repairing broken conductor above) Cause: Broken Conductor. | 3239052 | 1 | 13:09 | Afternoon | Sunday | 2016 | 7
3822 | 2016-07-31 18:08 | 2016-07-31 18:08 | MINAS POWER PLANT |  |  | - | 18:08 Offline MGT #9 then S/D the unit for S/B. (After NDC #1 S/U). |  | 1 | 18:08 | Afternoon | Sunday | 2016 | 7
3823 | 2016-01-08 09:45 | 2016-01-08 09:45 | 13.8KV NEW KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 0 | 09:45-10:00 Manually Open Recl. for 6 MVA Tx at KBGS. For repairing Hot Spot at load side of its Recloser. (S/D Pump #B & #C during this job) Cause: Planned Maintenance. | 3253331 | 1 | 9:45 | Morning | Friday | 2016 | 1
3824 | 2016-01-08 11:19 | 2016-01-08 11:19 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 11:19 It was reported b/o fuse for Tx at Well Kulin #55. (C.Duri fdr #1) 15:00 Checked & found, @1 b/o 1.4SF fuse for 75Kva Tx at Well Kulin #55. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3253331 | 1 | 11:19 | Morning | Friday | 2016 | 1
3825 | 2016-01-08 16:38 | 2016-01-08 16:38 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy and Lightning | Lightning | 39 | So.Bekasap OCB fdr #1 T/R 1x. Not checked yet. | 3253331 | 1 | 16:38 | Afternoon | Friday | 2016 | 1
3826 | 2016-01-08 16:38 | 2016-02-08 16:45 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy and Lightning | Lightning | 39 | Checked & found, So.Bekasap OCB fdr #1 T/R 1x Ctr: 345-346 R/F: 51@2. Patrolled the line & found, @2 F/O Dead end Insulator o/p #37BG-30. Cause: Lightning. | 3253331 | 1 | 16:38 | Afternoon | Friday | 2016 | 1
3827 | 2016-02-08 07:52 | 2016-02-08 07:52 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 0 | N.Duri VCB fdr #1 T/R 1x. Not checked yet. | 3253331 | 1 | 7:52 | Morning | Monday | 2016 | 2
3828 | 2016-02-08 07:52 | 2016-05-08 14:45 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 0 | Checked & found, N.Duri VCB fdr #1 T/R 2x Ctr: 277-279 R/F: 51N. Patrolled the line & found, a dead Monkey under pole #12-E3-27. Cause: Animal. (Monkey) | 3253331 | 1 | 7:52 | Morning | Monday | 2016 | 2
3829 | 2016-02-08 09:30 | 2016-02-08 09:30 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 145 | 09:30 It was reported no power at Road-L3/Area-10. Checked & found, Recl. 10-L1-44 (N.Duri fdr #1) T/SO. Ctr: 78-79. Patrolled the line & found, a dead Monkey hang on secondary bushing of Recl. 10-L1-44. 11:08 Blocked & closed Recl. 10-Li-44, Ok. Then released the Block. (After removing the Monkey above) Couse: Animal. (Monkey) | 3253331 | 1 | 9:30 | Morning | Monday | 2016 | 2
3830 | 2016-02-08 09:55 | 2016-02-08 09:55 | 13.8KV PEMATANG FEEDER #1 | Fair | Planned Maintenance | 30 | 09:55-11:30 Manually open Recl. 35BC-14. (Pematang fdr #1) To dismantle Static Wire & Install new Conductor by Project team. (5 Wells were off during this job). Cause: Planned Maintenance. | 123 | 1 | 9:55 | Morning | Monday | 2016 | 2
3831 | 2016-02-08 16:38 | 2016-02-08 16:38 | 13.8KV BATANG FEEDER #1 | Fair | Tree | 0 | Batang OCB fdr # 1 T/R. Not checked Yet. (Got info from PHE operator, cutting tree & touching to conductor at near Well Batang # 09) | 3253331 | 1 | 16:38 | Afternoon | Monday | 2016 | 2
3832 | 2016-02-08 16:38 | 2016-03-08 07:30 | 13.8KV BATANG FEEDER #1 | Fair | Tree | 0 | Checked & found, Batang OCB fdr #1 T/R 1x Ctr: 125-126 R/F: 51N. Patrolled the line & found, cutting high Trees & hit power line at near Well Batang #09. Cause: Tree. | 3253331 | 1 | 16:38 | Afternoon | Monday | 2016 | 2
3833 | 2016-02-08 17:04 | 2016-02-08 17:04 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 36 | 17:04 It was reported b/o fuse for Tx at Well Petani #105. (Petani fdr #1) 21:25 Checked & found, @1, @3 b/o 3.5SF fuses for 150Kva Tx at Well Petani #105. Performed TTR & Megger test, found Low Mega-ohm Reading Tx. Cause: Tx Failure. (Low Mega-ohm Reading) (The Tx failure is not replaced yet) | 3253331 | 1 | 17:04 | Afternoon | Monday | 2016 | 2
3834 | 2016-02-08 17:04 | 2016-03-08 10:30 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 36 | Replaced 150Kva Tx failure with the same size, then energized the Tx at Well Petani #105. Cause: Tx Failure. (Low megger reading) | 3253331 | 1 | 17:04 | Afternoon | Monday | 2016 | 2
3835 | 2016-02-08 22:26 | 2016-02-08 22:26 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 52 | Bekasap OCB fdr #2 T/R 1x. Bekasap GFPC T/R 1x. Not checked yet. | 3253331 | 1 | 22:26 | Night | Monday | 2016 | 2
3836 | 2016-02-08 22:26 | 2016-04-08 16:30 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 52 | Checked & found, Bekasap OCB fdr #2 T/R 1x Ctr: 873-874 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3253331 | 1 | 22:26 | Night | Monday | 2016 | 2
3837 | 2016-02-08 22:26 | 2016-02-08 22:26 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 59 | Pematang OCB fdr #1 T/R 1x. Pematang fdr #2 load dropped 12A (56-44A). Not checked yet. | 3253331 | 1 | 22:26 | Night | Monday | 2016 | 2
3838 | 2016-02-08 22:26 | 2016-04-08 16:35 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 59 | Checked & found, Pematang OCB fdr #1 T/R 1x Ctr: 130-131 R/F: 51N. Patrolled the line,, but found nothing. Cause: Suspected by Lightning. | 3253331 | 1 | 22:26 | Night | Monday | 2016 | 2
3839 | 2016-02-08 22:26 | 2016-02-08 22:26 | 13.8KV PETAPAHAN FEEDER #2 | Rain and Lightning | Lightning | 518 | Petapahan OCB fdr #2 T/R 1x. Petapahan fdr #1 load dropped 58A (86-28A). Not checked yet. | 3253333 | 1 | 22:26 | Night | Monday | 2016 | 2
3840 | 2016-02-08 22:26 | 2016-03-08 14:24 | 13.8KV PETAPAHAN FEEDER #2 | Rain and Lightning | Lightning | 518 | Checked & found, Petapahan OCB fdr #2 T/R 1x Ctr: 355-356 R/F: 51@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3253333 | 1 | 22:26 | Night | Monday | 2016 | 2
3841 | 2016-02-08 22:27 | 2016-02-08 22:27 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 30 | Bekasap VCB fdr #6 T/R 1x. Not checked yet. | 3253331 | 1 | 22:27 | Night | Monday | 2016 | 2
3842 | 2016-02-08 22:27 | 2016-04-08 16:35 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 30 | Checked & found, Bekasap VCB fdr #6 T/R 1x Ctr: 344-345 R/F: 50@1. Patrolled the line & found: -@1 Broken Pin Insualtor o/p #39BH-08. -@2 Broken Pin Insulator o/p #39BF-12. Cause: Lightning. | 3253331 | 1 | 22:27 | Night | Monday | 2016 | 2
3843 | 2016-02-08 22:51 | 2016-02-08 22:51 | 13.8KV NORTH DURI GFPC | Rain and Lightning | Unidentified | 0 | N.Duri GFPC-TX #13 T/R 1x. Ground fault alarm on N.Duri fdr #10. (No load dropped at any fdrs.) Not checked yet. | 3253331 | 1 | 22:51 | Night | Monday | 2016 | 2
3844 | 2016-02-08 22:51 | 2016-07-08 07:39 | 13.8KV NORTH DURI GFPC | Rain and Lightning | Unidentified | 0 | Checked & found, N.Duri GFPC-Tx #13 T/R 1x Ctr: 86-87. Patrolled the Line at downstream of N.Duri fdr #10, but found nothing. Cause: Unidentified. | 3253331 | 1 | 22:51 | Night | Monday | 2016 | 2
3845 | 2016-03-08 00:18 | 2016-03-08 00:18 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 27 | 8D OCB fdr #3 T/R 1x. 8D fdr #2 load dropped 40A (60-20A). 8D fdr #5 load dropped 63A (100-37A). Not checked yet. | 3253331 | 1 | 0:18 | Night | Tuesday | 2016 | 3
3846 | 2016-03-08 00:18 | 2016-04-08 19:25 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 27 | Checked & found, 8D OCB fdr #3 T/R 2x Ctr: 567-569 R/F: 50@1. Patrolled the line & found: -@1 Broken Dead end Insulator o/p #8DC-14. -@1 Broken Pin Insulator o/p #9D-50. Cause: Lightning. | 3253331 | 1 | 0:18 | Night | Tuesday | 2016 | 3
3847 | 2016-03-08 00:18 | 2016-03-08 00:18 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #1 | Rain and Lightning | Lightning | 56 | MSU-1 fdr #1 (8C fdr #3) Load dropped 134A (148-10A). (MSU-1 RTU failed at this time) Not checked yet. | 3253333 | 1 | 0:18 | Night | Tuesday | 2016 | 3
3848 | 2016-03-08 00:18 | 2016-04-08 19:15 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #1 | Rain and Lightning | Lightning | 56 | Checked & found, Recl. 8D-18A (8C fdr #3) T/R 2x Ctr: 30-32. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3253333 | 1 | 0:18 | Night | Tuesday | 2016 | 3
3849 | 2016-03-08 00:18 | 2016-03-08 00:18 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #2 | Rain and Lightning | Lightning | 15 | MSU-1 fdr #2 (8C fdr #1) Load dropped 193A (209-16A). (MSU-1 RTU failed at this time) Not checked yet. | 3253333 | 1 | 0:18 | Night | Tuesday | 2016 | 3
3850 | 2016-03-08 00:18 | 2016-04-08 19:20 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #2 | Rain and Lightning | Lightning | 15 | Checked & found, Recl. 9D-14A (8C fdr #1) T/R 1x Ctr: 000. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3253333 | 1 | 0:18 | Night | Tuesday | 2016 | 3
3851 | 2016-03-08 00:18 | 2016-03-08 00:18 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 0 | 8D fdr #1 Load dropped 84A (140-56A). Not checked yet. | 3253333 | 1 | 0:18 | Night | Tuesday | 2016 | 3
3852 | 2016-03-08 00:18 | 2016-04-08 19:21 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 8F-05 (8D fdr #1) T/R 1x. Ctr: Not reported yet. Patrolled the line, but found nothing. Cause: Suepected by Lightning. | 3253333 | 1 | 0:18 | Night | Tuesday | 2016 | 3
3853 | 2016-03-08 00:24 | 2016-03-08 00:24 | 13.8KV 8C FEEDER #5 | Rain and Lightning | Lightning | 12 | 8C VCB fdr #5 T/R 1x. Not checked yet. | 3253333 | 1 | 0:24 | Night | Tuesday | 2016 | 3
3854 | 2016-03-08 00:24 | 2016-04-08 19:10 | 13.8KV 8C FEEDER #5 | Rain and Lightning | Lightning | 12 | Checked & found, 8C VCB fdr #5 T/R 1x Ctr: 95-96 R/F: 50@3. Patrolled the line & found, @3 F/O Pin Insulator o/p #8D-246. Cause: Lightning. | 3253333 | 1 | 0:24 | Night | Tuesday | 2016 | 3
3855 | 2016-03-08 11:00 | 2016-03-08 11:00 | 13.8KV PUNGUT FEEDER #2 | Fair | Recloser | 55 | 11:00 It was reported no power at Ami & Asih Field. (Pungut fdr #2) Checked & found, Recl. 43BY-25 (Pungut fdr #2) T/SO. Ctr: 170-171. 12:00 Blocked & Closed Recl. 43BY-25, but failed. (Counter did not change) (Trouble shoot the Rcloser & found, Recloser closing coil problem) 12:25 Manually open Recl. 44BX-06 (Upstream), then closed Bypass Sw of Recl. 43BY-25. 14:45 Blocked & Closed Recl. 44BX-06, Ok. The released the block. Patrolled the Line, but Found nothing. Cause: Recloser problem. | 3253333 | 1 | 11:00 | Morning | Tuesday | 2016 | 3
3856 | 2016-03-08 18:27 | 2016-03-08 18:27 | 13.8KV BANGKO FEEDER #4 | Cloudy | Lightning | 0 | Bangko fdr #4 load dropped 88A (235-147A). Bangko GFPC T/R 1x. (Ground fault alarm on Bangko fdr #4) Not checked yet. | 3253331 | 1 | 18:27 | Afternoon | Tuesday | 2016 | 3
3857 | 2016-03-08 18:27 | 2016-05-08 14:00 | 13.8KV BANGKO FEEDER #4 | Cloudy | Lightning | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 91-92. Also found, Bangko GFPC T/R 1x Ctr: 106-107. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3253331 | 1 | 18:27 | Afternoon | Tuesday | 2016 | 3
3858 | 2016-03-08 18:36 | 2016-03-08 18:36 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain and Lightning | Lightning | 133 | NKBS OCB fdr #3 T/R 1x. NKBS GFPC T/R 1x. (Ground fault alarm on NKBS fdr #3) Not checked yet. | 3253333 | 1 | 18:36 | Afternoon | Tuesday | 2016 | 3
3859 | 2016-03-08 18:36 | 2016-04-08 16:26 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain and Lightning | Lightning | 133 | Checked & found, NKBS VCB fdr #3 T/R 1x Ctr: 273-274 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3253333 | 1 | 18:36 | Afternoon | Tuesday | 2016 | 3
3860 | 2016-03-08 20:07 | 2016-03-08 20:07 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 0 | 20:07 It was reported b/o fuse for Tx at Test Station-A Bangko field. 21:15 Checked & found, @1, @3 b/o 3.5SF fuses for 150Kva Tx at Test Sta-A Bangko. Performed TTR & Megger test, found Low Mega-ohm Reading Tx. Cause: Tx Failure. (Low Mega-ohm Reading Tx) (The Tx failure is not replaced yet) | 3253331 | 1 | 20:07 | Night | Tuesday | 2016 | 3
3861 | 2016-03-08 20:07 | 2016-10-08 10:00 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 0 | Replaced 150Kva Tx with 112.5Kva Tx at Test Station-A Bangko field. Cause: Tx Failure. (Low Mega-ohm Reading Tx) | 3253331 | 1 | 20:07 | Night | Tuesday | 2016 | 3
3862 | 2016-04-08 07:15 | 2016-04-08 07:15 | 115KV NELLA SW. STA - PINANG LINE | Fair | Improper Protection | 225 | 07:15 115KV Nella GCB #27 (115KV Nella-Pinang line) T/O. 08:55 Checked & found, 115KV Nella GCB #27 T/O. Ctr: 183-184 R/F: Pinang T60 Transfer Trip & 87T60. 09:00 Also found, Pinang 10.5Mva Tx. (R/F: 51G & 86T) 13.8Kv Pinang OCB fdr #1 T/R 1x Ctr: 409-410 R/F: 51N & 51G. Then Manually opened 13.8Kv Pinang OCB fdr #1. 09:26 Manually closed 115Kv Nella GCB #27. (After resetting all the Ralay flag) Ensure 10.5Mva Tx at Pinang Substation, in normal condition. Blocked & closed, 13.8Kv Pinang OCB fdr #1, Ok. Then released the block. Continued patrolling Pinang fdr #1 line, but found nothing. Cause: Relay problem. (Coordination relay setting) | 3253331 | 1 | 7:15 | Morning | Friday | 2016 | 4
3863 | 2016-04-08 22:26 | 2016-04-08 22:26 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx at well Pagar #29. Not checked yet. | 3253331 | 1 | 22:26 | Night | Friday | 2016 | 4
3864 | 2016-04-08 22:26 | 2016-05-08 15:20 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Pagar #29. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3253331 | 1 | 22:26 | Night | Friday | 2016 | 4
3865 | 2016-04-08 23:22 | 2016-04-08 23:22 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 0 | 23:22 It was reported b/o fuse for Tx at well Pematang #80. 00:36 Checked & found, @1 opened fuse for 150KVA Tx. No b/o fuse was found & all fencing was in good condition. Closed the fuse & energized the Tx. Cause: Unidentified. | 3253331 | 1 | 23:22 | Night | Friday | 2016 | 4
3866 | 2016-04-08 23:22 | 2016-04-08 23:22 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 16 | 23:22 It was reported b/o fuse for Tx at well Pematang #71. 00:36 Checked & found, @3 opened fuse for 150KVA Tx. No b/o fuse was found & all fencing was in good condition. Closed the fuse & energized the Tx. Cause: Unidentified. | 3253331 | 1 | 23:22 | Night | Friday | 2016 | 4
3867 | 2016-05-08 06:09 | 2016-05-08 06:09 | 13.8KV BANGKO FEEDER #3 | Cloudy | Unidentified | 0 | 06:09 Bangko OCB fdr #3 T/R 1x. Bangko GFPC T/R 1x. Ground fault alarm on Bangko fdr #3 14:00 Checked & found, Bangko OCB fdr #3 T/R 1x Ctr: 99940-99941 R/F: N/A. patrolled the Line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 6:09 | Morning | Sunday | 2016 | 5
3868 | 2016-05-08 09:05 | 2016-05-08 09:05 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT #4, then S/D the Unit for NSB. (To Open/Raise Up Blind Plate of HRSG-4) |  | 1 | 9:05 | Morning | Sunday | 2016 | 5
3869 | 2016-05-08 17:30 | 2016-05-08 17:30 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 24 | Pematang fdr #1 Load dropped 32A (147-115A). Not checked yet. | 3253331 | 1 | 17:30 | Afternoon | Sunday | 2016 | 5
3870 | 2016-05-08 17:30 | 2016-09-08 15:05 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 24 | Checked all Reclosers at downstream & found, normal. Ctr: Did not change. Patrolled the line, but found nothing. Cause: Unidentified. (Suspected WIP Tripped at Pematang-GS) | 3253331 | 1 | 17:30 | Afternoon | Sunday | 2016 | 5
3871 | 2016-05-08 18:47 | 2016-05-08 18:47 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 12 | Libo OCB fdr #1 T/R 1x. not checked yet. | 3253331 | 1 | 18:47 | Afternoon | Sunday | 2016 | 5
3872 | 2016-05-08 18:47 | 2016-06-08 14:16 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 12 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 372-373 R/F: 51N. Patrolled the Line, but found nothing Cause: Unidentified. | 3253331 | 1 | 18:47 | Afternoon | Sunday | 2016 | 5
3873 | 2016-06-08 06:38 | 2016-06-08 06:38 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Recloser | 230 | 06:38 C.Duri fdr #8 Load dropped 38A (2017-179A). 08:00 Checked & found, Recl. 04-0-25 (C.Duri fdr #8) T/SO. Ctr: 70-71. 08:30 Blocked & Closed the Recloser, but failed. Troubleshoot by unplugging the Recloser control cable. Blocked & closed the Recloser, but failed. 09:15 Closed the Recloser By Bypassing Recloser control, but Tripped again. Patrolled the Line, but found nothing. Suspected Recloser control Problem. (Open Recl. 04-0-25 & Pulling down the Yellow Handle) 11:15 Transfered Load of Recl. 04-0-25 to C.Duri fdr #9. By Closing LBS #04-01-01A. Cause: Recloser problem. | 3253331 | 1 | 6:38 | Morning | Wednesday | 2016 | 6
3874 | 2016-06-08 13:01 | 2016-06-08 13:01 | 13.8KV PINANG FEEDER #1 | Fair | Planned Maintenance | 21 | 13:01-15:23 Manually Open HLC o/p #11-D2, to replace Pin to Post type Insulators o/p #11-D3, #D4, #E1, #E2, #E3 & #E7. (3 Wells were offs during this job) Cause: Planned Maintenance. | 3253331 | 1 | 13:01 | Afternoon | Wednesday | 2016 | 6
3875 | 2016-06-08 13:09 | 2016-06-08 13:09 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 63 | Sintong OCB fdr #2 T/R 1x. Sintong fdr #1 Load dropped 21A (75-54A). (Ground fault alarm at Sintong fdr #2) Sintong GFPC in blocked position. (GFPC problem) Not checked yet. | 3253331 | 1 | 13:09 | Afternoon | Wednesday | 2016 | 6
3876 | 2016-06-08 13:09 | 2016-08-08 13:50 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 63 | Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 415-416 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 13:09 | Afternoon | Wednesday | 2016 | 6
3877 | 2016-06-08 15:36 | 2016-06-08 15:36 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 24 | Pematang fdr #1 Load dropped 34A (148-114A). Not checked yet. | 3253331 | 1 | 15:36 | Afternoon | Wednesday | 2016 | 6
3878 | 2016-06-08 15:36 | 2016-09-08 15:00 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 24 | Checked all Reclosers at downstream & found, normal. Ctr: Did not change. Patrolled the line, but found nothing. Cause: Unidentified. (Suspected WIP Tripped at Pematang-GS) | 3253331 | 1 | 15:36 | Afternoon | Wednesday | 2016 | 6
3879 | 2016-07-08 02:38 | 2016-07-08 02:38 | 13.8KV MINAS FEEDER #6 | Fair | Powerline - Jumper | 0 | 02:38 It was reported no power at Kenanga #512, #508, #514 & #510 housing. 03:15 Checked & found, @1 broken Jumper of 100Kva Tx o/p #CHW-7. 09:50 Repaired broken jumper above then energized the Tx. Cause: Jumper. | 3253333 | 1 | 2:38 | Night | Friday | 2016 | 7
3880 | 2016-07-08 03:27 | 2016-07-08 03:27 | 13.8KV 3D FEEDER #4 | Fair | Unidentified | 34 | 3D fdr #4 Load dropped 141A (227-86A). Not checked yet. | 3253333 | 1 | 3:27 | Night | Friday | 2016 | 7
3881 | 2016-07-08 03:27 | 2016-11-08 07:48 | 13.8KV 3D FEEDER #4 | Fair | Unidentified | 34 | Checked & found, Recl. 2D-14 (3D fdr #4) T/R 2x Ctr: 42-44 R/F: 51N. Patrolled the Line, but found nothing. Cause: Unidentified. | 3253333 | 1 | 3:27 | Night | Friday | 2016 | 7
3882 | 2016-07-08 08:55 | 2016-07-08 08:55 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 6 | 08:55-15:30 Blocked OKB fdr #2, then Opened HLC o/p #38CW-02. To replacing broken Dead end insulator o/p #38CW-07. (Well KB #73 was off during the Job done) Cause: Planed Maintenance. | 123 | 1 | 8:55 | Morning | Friday | 2016 | 7
3883 | 2016-08-08 06:33 | 2016-08-08 06:33 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Duri Community fdr #3 Load dropped 25A (62-37A). Not checked yet. | 3253331 | 1 | 6:33 | Morning | Monday | 2016 | 8
3884 | 2016-08-08 06:33 | 2016-11-08 08:36 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Checked & found, Recl. 6F-07 (DC fdr #3) T/R 1x Ctr: 1841-1842. Patrolled the Line & found, @2 broken Pin insulator o/p #2DG-24. (Near Talang #60) Cause: Pin Insulator. | 3253331 | 1 | 6:33 | Morning | Monday | 2016 | 8
3885 | 2016-08-08 08:03 | 2016-08-08 08:03 | 13.8KV PUNGUT FEEDER #1 | Fair | Planned Maintenance | 0 | 08:03 Manually open Pungunt OCB fdr #1. 19:15 Block & Closed Pungut OCB fdr#1. (After finishing the Job of Production team Project) (Tied In 10" Prod. line at Well Pungut #21 to Pungut GS). Cause: Plan maintenance. (No Prod. loss charged to PGT) | 123 | 1 | 8:03 | Morning | Monday | 2016 | 8
3886 | 2016-08-08 09:44 | 2016-08-08 09:44 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Unidentified | 539 | 09:44 Petapahan OCB fdr #1 T/R 3x. Petapahan fdr #2 Load dropped 112A (170- 58A). 10:05 Checked & found, Petapahan OCB fdr #1 T/R 3x Ctr: 212-215 R/F: 51@2,@3. Patrolled the line, but found nothing. Cause: Unidentified. (Suspected by animal) | 3253333 | 1 | 9:44 | Morning | Monday | 2016 | 8
3887 | 2016-08-08 14:30 | 2016-08-08 14:30 | 13.8KV 6D FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 14:30 It was reported b/o fuse for Tx at Well #6B-78E. Checked & found, @1,@2 b/o 7.8SF fuses for 250Kva Tx at Well #6B-78E. Performed TTR test & megger the Tx, found Normal. (good reading) Replaced b/o fuse above with same size, then energize the Tx. Cause: Unidentified (Fuse). | 3253333 | 1 | 14:30 | Afternoon | Monday | 2016 | 8
3888 | 2016-08-08 22:58 | 2016-08-08 22:58 | 13.8KV 3D FEEDER #4 | Fair | Unidentified | 92 | 3D OCB fdr #4 T/R 1x. 3D GFPC-TX #1 T/R 1x. (Ground fault alarm at 3D fdr #4) 3D fdr #2 Load dropped 198A (220-22A). 3D fdr #3 Load dropped 117A (159-42A). Not checked Yet. | 3253333 | 1 | 22:58 | Night | Monday | 2016 | 8
3889 | 2016-08-08 22:58 | 2016-11-08 07:53 | 13.8KV 3D FEEDER #4 | Fair | Unidentified | 92 | Checked & found, 3D OCB fdr #4 T/R 1x Ctr: 553-554 R/F: 51N. Patrolled the Line, but found nothing. Cause: Unidentified. | 3253333 | 1 | 22:58 | Night | Monday | 2016 | 8
3890 | 2016-09-08 09:30 | 2016-09-08 09:30 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Unidentified (Fuse) | 46 | 09:30 It was reported b/o fuse for Tx at Well Petapahan #25. 09:35 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Petapahan #25. Performed TTR test & Megger the TX, Good condition. Replaced b/o fuse above with same size, then energize the Tx. Cause: Unidentified (Fuse). | 3253333 | 1 | 9:30 | Morning | Thursday | 2016 | 9
3891 | 2016-09-08 09:55 | 2016-09-08 09:55 | 13.8KV LIBO FEEDER #2 | Fair | Transformer Failure | 7 | 09:55 It was reported b/o fuse for Tx at Well Waduk #14. Checked & found, @1,@3 b/o 3.5SF fuses for 150Kva Tx at Well Waduk #14. Performed TTR, Megger test the Tx & found, Low Megger reading. Cause: Tx Failure. (Low megger reading) (The Tx failure is not replaced yet) | 3253331 | 1 | 9:55 | Morning | Thursday | 2016 | 9
3892 | 2016-09-08 09:55 | 2016-11-08 15:00 | 13.8KV LIBO FEEDER #2 | Fair | Transformer Failure | 7 | 15:00 Replaced 150Kva Tx at Well Waduk #14 and then energized the Tx. Ok. Cause: Tx Failure. | 3253331 | 1 | 9:55 | Morning | Thursday | 2016 | 9
3893 | 2016-09-08 14:35 | 2016-09-08 14:35 | MINAS POWER PLANT |  |  | - | 14:35 S/U MGT #8, then on line the Unit at 14:58. (Due to NDC-CT #3 Shutdown for C/I program) |  | 1 | 14:35 | Afternoon | Thursday | 2016 | 9
3894 | 2016-09-08 16:40 | 2016-09-08 16:40 | 13.8KV NORTH DURI FEEDER #2 | Fair | Animal | 15 | 16:40 It was reported b/o fuse for Tx o/p #13-G51-27. 18:00 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #13-G51-27. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3253331 | 1 | 16:40 | Afternoon | Thursday | 2016 | 9
3895 | 2016-09-08 19:10 | 2016-09-08 19:10 | CENTRAL DURI POWER PLANT |  |  | - | 19:10 S/U CGT #4, then on line the Unit at 19:35. (Due to NDC-CT #3 Shutdown for C/I program) Note: Its Running on test, due to DC Ground problem. |  | 1 | 19:10 | Night | Thursday | 2016 | 9
3896 | 2016-10-08 04:48 | 2016-10-08 04:48 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 0 | Ketigul fdr #3 Load dropped 17A (22-5A). Not checked yet. | 3253331 | 1 | 4:48 | Morning | Saturday | 2016 | 10
3897 | 2016-10-08 04:48 | 13/08/2016 08:26 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 0 | 08:26 Checked & found, no Breaker & Recl. operated. Patrolled the line & found nothing. Cause: Unidentified. | 3253331 | 1 | 4:48 | Morning | Saturday | 2016 | 10
3898 | 2016-10-08 07:30 | 2016-10-08 07:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 14 | 07:30 It was reported b/o fuse for Tx at well Sikaladi #23. 15:30 Checked and found, @1 b/o fuse for 300Kva Tx. Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal (Squirrel). | 3253331 | 1 | 7:30 | Morning | Saturday | 2016 | 10
3899 | 2016-10-08 13:46 | 2016-10-08 13:46 | MINAS POWER PLANT |  |  | - | 13:46 MGT #6 S/U, then On Line at 14:04. to Backed up power, due to NDC CT#3 S/D for Maintenance Inspection. |  | 1 | 13:46 | Afternoon | Saturday | 2016 | 10
3900 | 2016-10-08 16:15 | 2016-10-08 16:15 | MINAS POWER PLANT |  |  | - | 16:15 MGT #9 S/U, then On Line at 16:50. to Backed Up Power due to NDC CT #3 S/D for Maintenance Inspection. |  | 1 | 16:15 | Afternoon | Saturday | 2016 | 10
3901 | 2016-10-08 17:02 | 2016-10-08 17:02 | NORTH DURI POWER PLANT |  |  | - | 17:02 NDC CT#3 Off Line and S/D for Maintenance Combustion Inspection. |  | 1 | 17:02 | Afternoon | Saturday | 2016 | 10
3902 | 2016-10-08 22:15 | 2016-10-08 22:15 | MINAS POWER PLANT |  |  | - | 22:15 MGT #4 S/U, then On line to system at 22:30 to Back up power due to NDC CT#3 S/D for Maintenance Inspection. |  | 1 | 22:15 | Night | Saturday | 2016 | 10
3903 | 2016-11-08 05:44 | 2016-11-08 05:44 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 0 | Pematang fdr#1 Load dropped 20A (151-131A). Not checked yet. | 3253331 | 1 | 5:44 | Morning | Tuesday | 2016 | 11
3904 | 2016-11-08 05:44 | 13/08/2016 18:29 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 35BC-14 (Pematang fdr #1) T/R 1x Ctr: 41 (did not change). Patrolled the Line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 5:44 | Morning | Tuesday | 2016 | 11
3905 | 2016-11-08 09:31 | 2016-11-08 09:31 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 15 | 09:31 It was reported b/o fuse for Tx o/p #04-00-07. 11:30 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #04-00-07. Replaced b/o fuse above above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3253331 | 1 | 9:31 | Morning | Tuesday | 2016 | 11
3906 | 2016-11-08 09:50 | 2016-11-08 09:50 | 13.8KV KOTABATAK FEEDER #2 | Fair | Animal | 18 | 09:50 It was reported b/o fuse for Tx at Well KB #30. Checked & found, @1, @2 b/o 7.8SF fuses for 300Kva Tx at Well KB #30. Replaced b/o fuses above with same size, then energized the Tx. Cause: Animal (Bird). | 3253333 | 1 | 9:50 | Morning | Tuesday | 2016 | 11
3907 | 2016-12-08 06:10 | 2016-12-08 06:10 | 13.8KV KETIGUL FEEDER#2 | Fair | Pin Insulator | 154 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3253331 | 1 | 6:10 | Morning | Thursday | 2016 | 12
3908 | 2016-12-08 06:10 | 14/08/2016 08:34 | 13.8KV KETIGUL FEEDER#2 | Fair | Pin Insulator | 154 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 205-206 R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator o/p #28AL-17. Cause: Pin Insulator. | 3253331 | 1 | 6:10 | Morning | Thursday | 2016 | 12
3909 | 2016-12-08 06:27 | 2016-12-08 06:27 | 4.16KV EAST RUMBAI FEEDER #3 | Fair | Unidentified | 0 | East Rumbai 4160 V VCB fdr#3 Load dropped 20A(52-32A). Not checked yet. | 3253333 | 1 | 6:27 | Morning | Thursday | 2016 | 12
3910 | 2016-12-08 06:27 | 14/08/2016 13:30 | 4.16KV EAST RUMBAI FEEDER #3 | Fair | Unidentified | 0 | 13:30 Checked East Rumbai VCB fdr #3, but nothing found. Patrolled the line, but nothing found. Cause: Unidentified. | 3253333 | 1 | 6:27 | Morning | Thursday | 2016 | 12
3911 | 2016-12-08 09:15 | 2016-12-08 09:15 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 4 | 09:15 Open HLC O/P # 21 U 38 to Install jumper at Bangko 20. (Well Bangko 285 was off during this job). Cause : Planned maintenance. | 123 | 1 | 9:15 | Morning | Thursday | 2016 | 12
3912 | 2016-12-08 14:31 | 2016-12-08 14:31 | 13.8KV ROKAN FEEDER #2 | Fair | Equipment Failure | 16 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3253331 | 1 | 14:31 | Afternoon | Thursday | 2016 | 12
3913 | 2016-12-08 14:31 | 14/08/2016 22:33 | 13.8KV ROKAN FEEDER #2 | Fair | Equipment Failure | 16 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: Not recorded R/F: 51N. Patrolled the Line & found, @2, @3 b/o fuse link for 150Kva Tx at Well Kopar #38. (LTC Well) Performed TTR, Megger test the Tx & found, Low Mega-ohm Reading Tx. (Then dismantled its Tx) Cause: Equipment Failure. (Tx Failure low Mega-ohm reading Tx) | 3253331 | 1 | 14:31 | Afternoon | Thursday | 2016 | 12
3914 | 2016-12-08 17:10 | 2016-12-08 17:10 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | C.Duri fdr #1 Load dropped 52A (152-100A). Not checked yet. | 3253331 | 1 | 17:10 | Afternoon | Thursday | 2016 | 12
3915 | 2016-12-08 17:10 | 13/08/2016 17:19 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 339-340. Patrolled the Line & found, @3 F/O Pin insulator o/p #NN. (near Well Kulin #12) Cause: Pin Insulator. | 3253331 | 1 | 17:10 | Afternoon | Thursday | 2016 | 12
3916 | 2016-12-08 18:23 | 2016-12-08 18:23 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified | 0 | C.Duri ACB fdr #9 T/R 1x. Not checked yet. | 3253331 | 1 | 18:23 | Afternoon | Thursday | 2016 | 12
3917 | 2016-12-08 18:23 | 13/08/2016 17:18 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified | 0 | Checked & found, C.Duri ACB fdr #9 T/R 1x Ctr: 344-345 R/F: 51N. Patrolled the Line, but found nothing. Cause: Unidentified | 3253331 | 1 | 18:23 | Afternoon | Thursday | 2016 | 12
3918 | 2016-08-13 06:31 | 2016-08-13 06:31 | 13.8KV MINAS FEEDER #6 | Fair | Unidentified | 0 | 06:31 Minas fdr #6 Load dropped 150A (196-46 A). 18:27 Checked & found, Recl. 7E-67A (MInas fdr #6) T/R 1x Ctr: 50-51 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 32353333 | 1 | 6:31 | Morning | Saturday | 2016 | 8
3919 | 2016-08-13 07:21 | 2016-08-13 07:21 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri Community ACB fdr #2 T/R 1x. Not checked yet. | 3253331 | 1 | 7:21 | Morning | Saturday | 2016 | 8
3920 | 2016-08-13 07:21 | 2016-08-14 08:30 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #2 T/R 1x Ctr: 73-74 R/F: 51@1. Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 7:21 | Morning | Saturday | 2016 | 8
3921 | 2016-08-13 09:15 | 2016-08-13 09:15 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 09:15 It was reported b/o fuse for Tx o/p #01-06-20. 10:50 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-06-20. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (fuse). | 3253331 | 1 | 9:15 | Morning | Saturday | 2016 | 8
3922 | 2016-08-13 10:30 | 2016-08-13 10:30 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 10:30 It was reported b/o fuse for Tx o/p #04-07-12. 11:02 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-07-12. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (fuse). | 3253331 | 1 | 10:30 | Morning | Saturday | 2016 | 8
3923 | 2016-08-14 07:10 | 2016-08-14 07:10 | 13.8KV 8D FEEDER #5 | Fair | Unidentified | 50 | 8D OCB fdr #5 T/R 1x. Not checked yet. | 3253331 | 1 | 7:10 | Morning | Sunday | 2016 | 8
3924 | 2016-08-14 07:10 | 2016-08-15 07:55 | 13.8KV 8D FEEDER #5 | Fair | Unidentified | 50 | Checked & found, 8D OCB fdr #5 T/R 1x Ctr: 499. (did not change) R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 7:10 | Morning | Sunday | 2016 | 8
3925 | 2016-08-14 10:00 | 2016-08-14 10:00 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 7 | 10:00 It was reported b/o fuse for Tx at Well Petani #16. 15:30 Checked & found, @1, @3 b/o 3.5SF fuses for 150Kva Tx at Well Petani #16. Performed TTR, Megger Test the Tx & found, Low Mega-ohm Reading Tx. Cause: Tx Failure. (Low Mega Ohm Reading Tx) (The Tx failure is not replaced yet) | 3253331 | 1 | 10:00 | Morning | Sunday | 2016 | 8
3926 | 2016-08-14 10:00 | 2016-08-15 11:30 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 7 | Replaced 150Kva Tx with the same size at Well Petani #16, then energized the Tx. Cause: Tx Failure. (Low Mega-ohm Reading Tx) | 3253331 | 1 | 10:00 | Morning | Sunday | 2016 | 8
3927 | 2016-08-15 00:38 | 2016-08-15 00:38 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Pin Insulator | 61 | 00:38 C.Duri fdr #4 Load dropped 22A (122-100A). 01:12 Checked & found, Recl. 09-S6-08 (C.Duri fdr #4) T/SO. Ctr: 106-107. 01:51 Blocked & Closed Recl. 09-S6-08, but tripped again. Patrolled the Line & found, @1 seriously broken Pin Insulator o/p #09-T5-02. (Then replaced broken Pin insulator above) 03:30 Bloked & Closed Recl. 09-S6-08, but triped again. Then transferred load under Recl. 09-S6-08 to DF fdr #1. Open Visual opening of Recl. 09-S6-08. (Last Ctr: 118) 04:30 Closed LBS #09-S6-01. To transfer load under Recl. 09-S6-08 to DF fdr #1. Cause: Pin Insulator. | 3253331 | 1 | 0:38 | Night | Monday | 2016 | 8
3928 | 2016-08-15 06:51 | 2016-08-15 06:51 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 67 | 06:51 Sintong OCB fdr #2 T/R 1x. Sintong fdr #1 load dropped 24A (77-53A). Ground fault alarm at sintong fdr #2. (GFPC was in block position). 14:09 Checked & found, Sintong OCB fdr #2 T/R 1x Ctr: 416-417 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 6:51 | Morning | Monday | 2016 | 8
3929 | 2016-08-15 08:40 | 2016-08-15 08:40 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 08:40 It was reported b/o fuse for Tx o/p #04-7-12. (C.Duri fdr #9) 09:25 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-7-12. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3253331 | 1 | 8:40 | Morning | Monday | 2016 | 8
3930 | 2016-08-15 12:00 | 2016-08-15 12:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Animal | 3 | 12:00 It was reported b/o fuse for Tx at Well KB #313. (CKBS fdr #5. 14:30 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well KB #313. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal (Squirrel). | 3253333 | 1 | 12:00 | Afternoon | Monday | 2016 | 8
3931 | 2016-08-15 19:00 | 2016-08-15 19:00 | 13.8KV PUNGUT FEEDER #1 | Fair | Transformer Failure | 33 | 19:00 It was reported b/o fuse for Tx at Well Pungut #31. 21:00 Checked & found, @1,@3 b/o 3.5SF fuses for 150Kva Tx at Well Pungut #31. Performed TTR, Megger test the Tx & found, Low Mega Ohm reading Tx. Cause: Tx Failure. (Low Mega Ohm Tx) (The Tx failure is not replaced yet) | 3253331 | 1 | 19:00 | Night | Monday | 2016 | 8
3932 | 2016-08-15 19:00 | 2016-08-16 11:00 | 13.8KV PUNGUT FEEDER #1 | Fair | Transformer Failure | 33 | Replaced 150Kva Tx failure with 300Kva Tx at Well Pungut #31. Cause: Tx Failure. (Low Megger reading) | 3253331 | 1 | 19:00 | Night | Monday | 2016 | 8
3933 | 2016-08-15 21:01 | 2016-08-15 21:01 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Animal | 130 | 44Kv Pematang main OCB #1 (Line to Petani) T/R 1x. (No power to Petani Substation) Not checket yet. | 3253331 | 1 | 21:01 | Night | Monday | 2016 | 8
3934 | 2016-08-15 21:01 | 2016-08-16 14:01 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Animal | 130 | Checked & found, 44Kv Pematang Main OCB #1 T/R 1x Ctr: 550-551 R/F: 50N. Patrolled the line & found, a dead Civet at structure 44Kv Pematang Main. Cause: Animal. (Civet) | 3253331 | 1 | 21:01 | Night | Monday | 2016 | 8
3935 | 2016-08-16 14:37 | 2016-08-16 14:37 | MINAS POWER PLANT |  |  | - | 14:37 S/U MGT #3, then on line the Unit at 15:00. |  | 1 | 14:37 | Afternoon | Tuesday | 2016 | 8
3936 | 2016-08-16 15:28 | 2016-08-16 15:28 | MINAS POWER PLANT |  |  | - | Off line MGT #1, then S/D the unit for S/B. |  | 1 | 15:28 | Afternoon | Tuesday | 2016 | 8
3937 | 2016-08-16 17:13 | 2016-08-16 17:13 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 26 | C.Duri fdr #1 Load dropped 73A (152-79A). Not checked yet. | 3253331 | 1 | 17:13 | Afternoon | Tuesday | 2016 | 8
3938 | 2016-08-16 17:13 | 2016-08-21 08:13 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 26 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 2x Ctr: 239-241 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 17:13 | Afternoon | Tuesday | 2016 | 8
3939 | 2016-08-16 18:26 | 2016-08-16 18:26 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 160 | So.Balam VCB fdr #4 T/R 1x. So.Balam GFPC T/R 1x. Not checked yet. | 3253331 | 1 | 18:26 | Afternoon | Tuesday | 2016 | 8
3940 | 2016-08-16 18:26 | 2016-08-17 18:26 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 160 | Checked & found, So.Balam VCB fdr #4 T/R 1x Ctr: 304. (did not operate) R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 18:26 | Afternoon | Tuesday | 2016 | 8
3941 | 2016-08-17 23:59 | 2016-08-17 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI power system was normal operation. |  | 1 | 23:59 | Night | Wednesday | 2016 | 8
3942 | 2016-08-18 06:44 | 2016-08-18 06:44 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3253331 | 1 | 6:44 | Morning | Thursday | 2016 | 8
3943 | 2016-08-18 06:44 | 2016-08-21 16:44 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 87-88 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 6:44 | Morning | Thursday | 2016 | 8
3944 | 2016-08-18 08:25 | 2016-08-18 08:25 | 13.8KV 4D FEEDER #4 | Fair | Unidentified | 45 | 4D fdr #4 Load dropped 202A (240-38A). Not checked yet. | 3253333 | 1 | 8:25 | Morning | Thursday | 2016 | 8
3945 | 2016-08-18 08:25 | 2016-08-21 08:25 | 13.8KV 4D FEEDER #4 | Fair | Unidentified | 45 | Checked & found, No Breaker & Recl. operated. Patrolled the line, but found nothing. Cause: Unidentified. | 3253333 | 1 | 8:25 | Morning | Thursday | 2016 | 8
3946 | 2016-08-18 12:25 | 2016-08-18 12:25 | NORTH DURI POWER PLANT |  |  | - | 12:25 S/U NDC-CT #3, then online the unit at 13:50. 13:53 Closed 230KV GCB #33. (From DSC) |  | 1 | 12:25 | Afternoon | Thursday | 2016 | 8
3947 | 2016-08-18 14:03 | 2016-08-18 14:03 | 13.8KV 6DN FEEDER #6 | Fair | Lightning Arrester | 18 | 6DN OCB fdr #6 Load dropped 127A (181-54A). Not checked yet. | 3253333 | 1 | 14:03 | Afternoon | Thursday | 2016 | 8
3948 | 2016-08-18 14:03 | 2016-08-21 14:03 | 13.8KV 6DN FEEDER #6 | Fair | Lightning Arrester | 18 | Checked & found, Recl. 6E-64 (6DN fdr #6) T/R 1x Ctr: 40-41 R/F: 51N. Patrolled the line & found, @2 broken L/A o/p #2D-08. Cause: Lightning Arrester. | 3253333 | 1 | 14:03 | Afternoon | Thursday | 2016 | 8
3949 | 2016-08-18 17:00 | 2016-08-18 17:00 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 18 | 17:00 It was reported b/o fuse for Tx at Well Bangko #27. (Nella fdr #1) 18:00 Checked & found, @2 b/o 2.1SF fuse for 100Kva Tx at Well Bangko #27. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3253331 | 1 | 17:00 | Afternoon | Thursday | 2016 | 8
3950 | 2016-08-18 20:33 | 2016-08-18 20:33 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 46 | 3D OCB fdr #4 T/R 1x. Not checked yet. | 3253333 | 1 | 20:33 | Night | Thursday | 2016 | 8
3951 | 2016-08-18 20:33 | 2016-08-21 20:33 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 46 | Checked & found, 3D OCB fdr #4 T/R 2x Ctr: 553-555 R/F: 51N. Patrolled the line & found, @1 broken Dead-end Insulator o/p #2D-08. Cause: Lightning. | 3253333 | 1 | 20:33 | Night | Thursday | 2016 | 8
3952 | 2016-08-18 20:33 | 2016-08-18 20:33 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 43 | 3D fdr #2 Load dropped 52A (220-168A). Not checked yet. | 3253333 | 1 | 20:33 | Night | Thursday | 2016 | 8
3953 | 2016-08-18 20:33 | 2016-08-21 20:33 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 43 | Checked & found, 3D OCB fdr #2 T/R 1x Ctr: 220. (did not change) R/F: 51N. Patrolled the line & found, @2 broken Pin insulator o/p #MDB-4. Cause: Lightning. | 3253333 | 1 | 20:33 | Night | Thursday | 2016 | 8
3954 | 2016-08-19 06:28 | 2016-08-19 06:28 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri ACB fdr #16 T/R 1x. Not checked yet. | 3253331 | 1 | 6:28 | Morning | Friday | 2016 | 8
3955 | 2016-08-19 06:28 | 2016-08-20 06:28 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked & found, C.Duri ACB fdr #16 T/R 1x Ctr: 288-289 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 6:28 | Morning | Friday | 2016 | 8
3956 | 2016-08-19 06:55 | 2016-08-19 06:55 | 13.8KV PETANI FEEDER #1 | Fair | Pin Insulator | 68 | Petani OCB fdr #1 T/R 1x. (Petani RTU failed at that time) Rangau fdr #2 Load dropped 21A (71-50A). Not checked yet. 17:40 Checked & found, Petani OCB fdr #1 T/R 2x Ctr: 25-27 R/F: 51@1,@2. Patrolled the line & found, @1,@2 Broken & F/O Pin Insulators o/p #33AX-02. Cause: Pin Insulator. | 3253331 | 1 | 6:55 | Morning | Friday | 2016 | 8
3957 | 2016-08-19 08:20 | 2016-08-19 08:20 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 12 | 08:20 It was reported b/o fuse for Tx o/p #11-J2-19A. (N.Duri fdr #9) 10:18 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #11-J2-19A. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal (Monkey). | 3253331 | 1 | 8:20 | Morning | Friday | 2016 | 8
3958 | 2016-08-19 16:01 | 2016-08-19 16:01 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 27 | C.Duri fdr #1 Load dropped 74A (152-78A). Not checked yet. | 3253331 | 1 | 16:01 | Afternoon | Friday | 2016 | 8
3959 | 2016-08-19 16:01 | 2016-08-22 16:01 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 27 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 2x Ctr: 239-241 R/F: 51N. Patrolled the line & found, a kite hang on power line o/p #NN. (toward Well Kulin #30) Cause: Others. (a Kite) | 3253331 | 1 | 16:01 | Afternoon | Friday | 2016 | 8
3960 | 2016-08-19 19:50 | 2016-08-19 19:50 | NORTH DURI POWER PLANT |  |  | - | 19:50 Off line NDC-CT #2, then S/D the Unit for Off Line wash. 20-Aug-2016. 18:45 S/U NDC-CT #2, then on line the Unit at 19:16. (After Off line wash program) |  | 1 | 19:50 | Night | Friday | 2016 | 8
3961 | 2016-08-20 10:22 | 2016-08-20 10:22 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 10:22 It was reported b/o fuse for Tx o/p #05-P3-05. (C.Duri fdr #14) 10:50 Checked & found, @2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #05-P3-05. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal (Monkey). | 3253331 | 1 | 10:22 | Morning | Saturday | 2016 | 8
3962 | 2016-08-20 18:45 | 2016-08-20 18:45 | NORTH DURI POWER PLANT |  |  | - | 18:45 S/U NDC-CT #2, then on line the Unit at 19:16. (After Off line wash program) |  | 1 | 18:45 | Afternoon | Saturday | 2016 | 8
3963 | 2016-08-20 23:32 | 2016-08-20 23:32 | NORTH DURI POWER PLANT |  |  | - | 23:32 Off line NDC-CT #1, then S/D the Unit for Off Line Wash. 21-Aug-2016. 15:47 S/U NDC-CT #1, then on line the Unit at 16:30. (After Off line wash program) |  | 1 | 23:32 | Night | Saturday | 2016 | 8
3964 | 2016-08-21 06:43 | 2016-08-21 06:43 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | 06:43 C.Duri ACB fdr #6 T/R 1x Ctr: 443-444 R/F: 51N. 16:00 Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 6:43 | Morning | Sunday | 2016 | 8
3965 | 2016-08-21 09:47 | 2016-08-21 09:47 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 2 | 09:47 It was reported b/o fuse for Tx o/p #07-T3-03. (D.Field fdr #2) 11:30 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx o/p #07-T3-03. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal (Bat). | 3253331 | 1 | 9:47 | Morning | Sunday | 2016 | 8
3966 | 2016-08-21 15:47 | 2016-08-21 15:47 | NORTH DURI POWER PLANT |  |  | - | 15:47 S/U NDC-CT #1, then on line the Unit at 16:30. (After Off line wash program) |  | 1 | 15:47 | Afternoon | Sunday | 2016 | 8
3967 | 2016-08-21 21:06 | 2016-08-21 21:06 | CENTRAL DURI POWER PLANT |  |  | - | 21:06 Off line CGT #3, then S/D the Unit at 21:07. (for S/B-Prior to M/O) |  | 1 | 21:06 | Night | Sunday | 2016 | 8
3968 | 2016-08-21 23:28 | 2016-08-21 23:28 | 13.8KV 5B FEEDER #1 | Fair | Unidentified | 6 | 5B OCB fdr #1 T/R 1x. Not checked yet. | 3253333 | 1 | 23:28 | Night | Sunday | 2016 | 8
3969 | 2016-08-21 23:28 | 2016-08-24 19:50 | 13.8KV 5B FEEDER #1 | Fair | Unidentified | 6 | Checked & found, 5B OCB fdr #1 T/R 1x Ctr: 208-209 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3253333 | 1 | 23:28 | Night | Sunday | 2016 | 8
3970 | 2016-08-22 10:22 | 2016-08-22 10:22 | MINAS POWER PLANT |  |  | - | Off line MGT #4, then S/D the Unit for S/B. |  | 1 | 10:22 | Morning | Monday | 2016 | 8
3971 | 2016-08-22 10:34 | 2016-08-22 10:34 | MINAS POWER PLANT |  |  | - | Off line MGT #6, then S/D the Unit for S/B. |  | 1 | 10:34 | Morning | Monday | 2016 | 8
3972 | 2016-08-22 11:39 | 2016-08-22 11:39 | MINAS POWER PLANT |  |  | - | Off line MGT #8, then S/D the Unit for S/B . |  | 1 | 11:39 | Morning | Monday | 2016 | 8
3973 | 2016-08-22 12:26 | 2016-08-22 12:26 | 13.8KV NORTH DURI FEEDER #2 | Fair | Secondary Cable | 0 | 12:26 It was reported b/o fuse for Tx o/p #13-J3-07. (N.Duri fdr #2) 15:55 N.Duri fdr #2 Load dropped 65A (163-78A). 17:15 Checked & found: -@1, @2 b/o fuses for 112.5Kva Tx o/p #13-J3-07. (at CIF area #10) -Broken 480 Volt Secondary Cable. 19:00 Replaced Broken fuses & 480 Volt Secondary Cable above. 20:00 Energized 112.5Kva Tx at CIF Area 10. 20:37 N.Duri VCB fdr #2 Back to normal. Cause: Broken Secondary Cable. | 3253331 | 1 | 12:26 | Afternoon | Monday | 2016 | 8
3974 | 2016-08-22 15:42 | 2016-08-22 15:42 | MINAS POWER PLANT |  |  | - | Off line MGT #9, then S/D the Unit for S/B. |  | 1 | 15:42 | Afternoon | Monday | 2016 | 8
3975 | 2016-08-22 17:15 | 2016-08-22 17:15 | 13.8KV DARLING VCB FEEDER #4 | Fair | Animal | 2 | 17:15 Darling VCB fdr #4 T/LO. Ctr: 121-125 R/F: 51N. 18:18 Blocked & Closed Darling VCB fdr #4, Ok. Then released the Block. 19:00 Patrolled the line & found, a dead Monkey under pole #05-M5-15N. Cause: Animal. (Monkey) | 3253331 | 1 | 17:15 | Afternoon | Monday | 2016 | 8
3976 | 2016-08-22 18:02 | 2016-08-22 18:02 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | 18:02 C.Duri ACB fdr #2 T/LO. Ctr: 263-267 R/F: 51G & 51@2,@3. 18:13 Blocked & Closed C.Duri ACB fdr #2, Ok. Then released the Block. Not Patrolled yet. | 3253331 | 1 | 18:02 | Afternoon | Monday | 2016 | 8
3977 | 2016-08-22 18:02 | 2016-08-23 14:02 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 18:02 | Afternoon | Monday | 2016 | 8
3978 | 2016-08-22 19:33 | 2016-08-22 19:33 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 0 | 19:33 It was reported B/O fuse o/p 40BA35 (C.Duri fdr#1). 21:05 Replaced @1@2 B/O fuse for 112.5Kva Tx with the same size. Cause: Animal (Squirrel). | 3253331 | 1 | 19:33 | Night | Monday | 2016 | 8
3979 | 2016-08-22 22:01 | 2016-08-22 22:01 | 13.8KV 6D FEEDER #2 | Fair | Pin Insulator | 36 | 6D OCB fdr #2 T/R 1x. 6D fdr #1 Load dropped 120A (250-130A). Not checked yet. | 3253333 | 1 | 22:01 | Night | Monday | 2016 | 8
3980 | 2016-08-22 22:01 | 2016-08-24 19:55 | 13.8KV 6D FEEDER #2 | Fair | Pin Insulator | 36 | Checked & found, 6D OCB fdr #2 T/R 1x Ctr: 236-237 R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator o/p #6B-56. Cause: Pin Insulator. | 3253333 | 1 | 22:01 | Night | Monday | 2016 | 8
3981 | 2016-08-23 05:54 | 2016-08-23 05:54 | 13.8KV 8D FEEDER #5 | Fair | Dead End Insulator | 61 | 8D OCB fdr #5 T/R 1x. Not checked yet. | 3253333 | 1 | 5:54 | Morning | Tuesday | 2016 | 8
3982 | 2016-08-23 05:54 | 2016-08-24 20:00 | 13.8KV 8D FEEDER #5 | Fair | Dead End Insulator | 61 | Checked & found, 8D OCB fdr #5 T/R 1x Ctr: 498-499 R/F: 50N. Patrolled the line & found, @1 broken Dead end Insulator o/p #8E-38. Cause: Dead end Insulator. | 3253333 | 1 | 5:54 | Morning | Tuesday | 2016 | 8
3983 | 2016-08-23 07:20 | 2016-08-23 07:20 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 92 | 07:20 C.Duri ACB fdr #3 T/O. (on block status) Ctr: 183-184 R/F: 51G. 07:30 Blocked & Closed C.Duri ACB fdr #3, Ok. then released the block. 07:32 C.Duri ACB fdr #3 T/SO. Ctr: 184-185 R/F: 51G. Checked C.Duri ACB fdr #3 breaker & found, good condition. Patrolled the line until LBS #03-8A-08, but found normal condition. 08:45 Opened LBS #03-8A-08. 09:00 Blocked & Closed C.Duri ACB fdr #3, Ok. (stay on block, due to Rig BN #09 job) Then continue patrolled under LBS #03-8A-08, but found normal condition. 09:30 Close LBS #03-8A-08, Ok. Cause: Unidentified. | 3253331 | 1 | 7:20 | Morning | Tuesday | 2016 | 8
3984 | 2016-08-23 09:45 | 2016-08-23 09:45 | 13.8KV 6DN FEEDER #5 | Fair | Planned Maintenance | 59 | Back to normalize load of 6DN fdr #5. 09:45 LBS #6D-16A (6DN fdr #5) is in open position. Opened LBS #6D-26A (toward Minas fdr #1). Opened LBS #6D-15 (toward 6D fdr #3). (23 wells were shut down) 09:50 Bypassed Recl. 6D-18 and Recl. 6D-16A, due to control problem. (6DN fdr #5) 10:05 Closed LBS #6D-16A (6DN fdr #5), Ok. 6DN fdr #5 Load is back to original load. Cause: Planned Maintenance. | 123 | 1 | 9:45 | Morning | Tuesday | 2016 | 8
3985 | 2016-08-23 17:08 | 2016-08-23 17:08 | 13.8KV 4B FEEDER #1 | Fair | Pin Insulator | 21 | 4B OCB fdr #1 T/R 1x. Not checked yet. | 3253333 | 1 | 17:08 | Afternoon | Tuesday | 2016 | 8
3986 | 2016-08-23 17:08 | 2016-08-26 19:10 | 13.8KV 4B FEEDER #1 | Fair | Pin Insulator | 21 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 284-285 R/F: 51N. Patrolled the line & found, @1 F/O Pin Insulator o/p #4B-99. Cause: Pin Insulator. | 3253333 | 1 | 17:08 | Afternoon | Tuesday | 2016 | 8
3987 | 2016-08-23 17:37 | 2016-08-23 17:37 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 48 | 17:37 Sintong fdr #1 Load dropped 15A (80-65A). 19:45 It was reported no power at Kerang fields. 21:00 Checked & found, Recl. 26AE-22 (Sintong fdr #1) T/SO. Ctr: 157-158 (in Block position). Patrolled the line, but found nothing. 21:38 Blocked & Closed Recl. 26AE-22, Ok. Cause: Unidentified. | 3253331 | 1 | 17:37 | Afternoon | Tuesday | 2016 | 8
3988 | 2016-08-23 17:46 | 2016-08-23 17:46 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Lightning | 197 | So.Balam VCB fdr #4 T/R 1x. Ground fault alarm at So.Balam fdr #4. Not checked yet. | 3253331 | 1 | 17:46 | Afternoon | Tuesday | 2016 | 8
3989 | 2016-08-23 17:46 | 2016-08-24 17:15 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Lightning | 197 | Checked & found, So.Balam VCB fdr #4 T/R 1x Ctr: 303-304 R/F: 51N. Also found, So.Balam GFPC T/R 3x Ctr: Not reported yet. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3253331 | 1 | 17:46 | Afternoon | Tuesday | 2016 | 8
3990 | 2016-08-23 20:26 | 2016-08-23 20:26 | 13.8KV 5B FEEDER #3 | Rain | Animal | 12 | 5B OCB fdr #3 T/R 1x. Not checked yet. | 3253333 | 1 | 20:26 | Night | Tuesday | 2016 | 8
3991 | 2016-08-23 20:26 | 2016-08-25 19:00 | 13.8KV 5B FEEDER #3 | Rain | Animal | 12 | Checked & found, 5B OCB fdr #3 T/R 1x Ctr: 359-360 R/F: 51N. Patrolled the line & found, a dead Squirrel under 5B fdr #3 breaker at 5B Substation. (No Equipment damaged) Cause: Animal. (Squirrel) | 3253333 | 1 | 20:26 | Night | Tuesday | 2016 | 8
3992 | 2016-08-24 23:59 | 2016-08-24 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system is normal condition. |  | 1 | 23:59 | Night | Wednesday | 2016 | 8
3993 | 2016-08-25 11:14 | 2016-08-25 11:14 | MINAS SWITCH YARD | Fair | Relay Failure | 0 | 11:14 115KV MSY TX-3 Tripped. (115KV OCB #23, OCB #24 T/O, & 13.8Kv ACB #23 Indication close position) Also T/SO all 4160V feeders S.Rumbai, E.Rumbai, N.Rumbai. 11:47 Checked & found: -115KV MSY OCB #23 & OCB #24 T/O. By R/F: 51@1, 87T@1 & 86T. -13.8Kv MSG ACB #23 open position. (just Scada indication close) (115KV MSY TX-3 No power) 11:48 Ensure 138KV ACB #23 in open position. 11:49 Manual Opened 13.8KV ACB #21. (44KV line to Rumbai) 11.50 Manual Opened Minas ACB fdr #5. (GS-1 WIP) 11:51 Manual Opened Minas ACB fdr #6. (GS-1 Wells) 11:52 Manual Opened Generator Breaker of MGT #5 & Re-Online at 11:59. 11:52 Checked & found: 44KV E.Rumbai GCB #5 (for E.Rumbai TX) T/O. Ctr: 34-35 R/F: 24. 4160V E.Rumbai fdr #1 T/SO. Ctr: 538-539 R/F: 81. 4160V E.Rumbai fdr #2 T/SO. Ctr: 520-521 R/F: 81. 4160V E.Rumbai fdr #3 T/SO. Ctr: 470-471 R/F: 81. 4160V S.Rumbai fdr #1 Still Closed status 4160V S.Rumbai fdr #2 T/SO. Ctr: 793-794 R/F: 81. 4160V S.Rumbai fdr #3 T/SO. Ctr: 127-128 R/F: 81. 4160V S.Rumbai fdr #4 T/SO. Ctr: 166-167 R/F: 81. 4160V N.Rumbai fdr #1 T/SO. Ctr: 388-389 R/F: 81. 4160V N.Rumbai fdr #2 T/SO. Ctr: 336-337 R/F: 81. 11.55 Manual Closed Tie Breaker ACB #16. (all MSG Busses are connected) 11:58 Manual Closed ACB #21. (44KV line to Rumbai energized) 12:00 Manual Closed 4160V E.Rumbai fdr #1, #2 & #3. 12:04 Manual Closed 4160V N.Rumbai fdr #1 & #2. 12:15 Manual Closed 4160V S.Rumbai fdr #2, #3 & #4. 12:20 Manual Closed Minas ACB fdr #5. (GS-1 WIP) 12:21 Manual Closed Minas ACB fdr #6. (GS-1 Wells) Cause: Under Investigation. 13:33 S/U MGT #4, then online the Unit at 13:49. Open Minas ACB #8. (Tie Breaker) Investigation Result: (Miss-operate of 87T Tx#3 Minas Switchyard due to repeated ON-OFF condition of DC battery, supply to 87T) | 3253333 | 1 | 11:14 | Morning | Thursday | 2016 | 8
3994 | 2016-08-25 13:33 | 2016-08-25 13:33 | MINAS POWER PLANT |  |  | - | 13:33 S/U MGT #4, then online the Unit at 13:49 |  | 1 | 13:33 | Afternoon | Thursday | 2016 | 8
3995 | 2016-08-25 14:40 | 2016-08-25 14:40 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 15 | 14:40 It was reported b/o fuse for Tx at Well Mutiara #01. (Sintong fdr #2) 15:15 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Mutiara #01. Replaced b/o fuse above with the same size, then Energized the Tx. Cause: Animal. (Mokey) | 3253331 | 1 | 14:40 | Afternoon | Thursday | 2016 | 8
3996 | 2016-08-25 15:55 | 2016-08-25 15:55 | 13.8KV NORTH DURI FEEDER #9 | Fair | Transformer Failure | 0 | 15:55 It was reported b/o fuse for Tx o/p #11-G7-10. (N.Duri fdr #9) 18:00 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #11-G7-10. Perform TTR, Megger test the Tx & found, Low Mega Ohm reading. Cause: Tx Failure. (Low Mega Ohm reading) (The Tx failure is not replaced yet) | 3253331 | 1 | 15:55 | Afternoon | Thursday | 2016 | 8
3997 | 2016-08-25 15:55 | 2016-08-26 18:30 | 13.8KV NORTH DURI FEEDER #9 | Fair | Transformer Failure | 0 | Replaced 112.5Kva Tx failure with the same size & energized the Tx o/p #11-G7-10. Cause: Tx failure. | 3253331 | 1 | 15:55 | Afternoon | Thursday | 2016 | 8
3998 | 2016-08-25 17:53 | 2016-08-25 17:53 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 17:52 It was reported b/o fuse for Tx o/p #11-H5-23. (N.Duri fdr #9) 18:40 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #11-H5-23. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3253331 | 1 | 17:53 | Afternoon | Thursday | 2016 | 8
3999 | 2016-08-26 09:40 | 2016-08-26 09:40 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 20 | 09:30 It was reported b/o fuse for Tx o/p #09-R6-03. (C.Duri fdr #4) 10:40 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #09-R6-03. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3253331 | 1 | 9:40 | Morning | Friday | 2016 | 8
4000 | 2016-08-26 21:10 | 2016-08-26 21:10 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 2 | 21:10 It was reported b/o fuse for Tx o/p #07-V3-08. (D.Field fdr #2) 22:20 Checked & found, @2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #07-V3-08. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3253331 | 1 | 21:10 | Night | Friday | 2016 | 8
4001 | 2016-08-27 07:13 | 2016-08-27 07:13 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning Arrester | 14 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3253331 | 1 | 7:13 | Morning | Saturday | 2016 | 8
4002 | 2016-08-27 07:13 | 2016-08-29 17:15 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning Arrester | 14 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 1241-1242 R/F: 51@1. Patrolled the line & found: -@1 broken L/A o/p #28AV-20. -Also found broken Guywire o/p #35BI-13. Cause: Lightning Arrester. | 3253331 | 1 | 7:13 | Morning | Saturday | 2016 | 8
4003 | 2016-08-27 09:10 | 2016-08-27 09:10 | 13.8KV 6DN FEEDER #6 | Fair | Planned Maintenance | 7 | 09:10 Blocked Recl. 6E-64. (6DN fdr #6) Replaced Pin Insulator to Post type on TP of Well #6E-11. (Well #6E-11 was off during the job done) 10:11 Normalized Recl. 6E-64, then S/U Well #6E-11. Cause: Panned Maintenance. | 123 | 1 | 9:10 | Morning | Saturday | 2016 | 8
4004 | 2016-08-28 16:54 | 2016-08-28 16:54 | 13.8KV CENTRAL DURI FEEDER #4 | Foggy and Smoke | Unidentified | 29 | C.Duri ACB fdr #4 T/R 1x Ctr: 464-465 R/F: 51N. Not checked yet. | 3253331 | 1 | 16:54 | Afternoon | Sunday | 2016 | 8
4005 | 2016-08-28 16:54 | 2016-08-31 15:30 | 13.8KV CENTRAL DURI FEEDER #4 | Foggy and Smoke | Unidentified | 29 | Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 16:54 | Afternoon | Sunday | 2016 | 8
4006 | 2016-08-28 17:56 | 2016-08-28 17:56 | 13.8KV CENTRAL DURI FEEDER #4 | Foggy and Smoke | Transformer Failure | 6 | It was reported b/o fuse for Tx o/p #09-R8-04. (C.Duri fdr #4) Not checked yet. | 3253331 | 1 | 17:56 | Afternoon | Sunday | 2016 | 8
4007 | 2016-08-28 17:56 | 2016-08-29 09:20 | 13.8KV CENTRAL DURI FEEDER #4 | Foggy and Smoke | Transformer Failure | 6 | 09:20 Checked and found, @1, @3 b/o fuse for 112.5Kva Tx o/p #09-R8-04 (d/s C. Duri Fdr #4). Also found Lube Oil leak at Tapping of TX. Cause: Transformer failure. | 3253331 | 1 | 17:56 | Afternoon | Sunday | 2016 | 8
4008 | 2016-08-28 17:56 | 2016-02-09 15:50 | 13.8KV CENTRAL DURI FEEDER #4 | Foggy and Smoke | Transformer Failure | 6 | Replaced 112.5 Kva Tx failure with same size and energized the Tx. Cause: Tx failure. | 3253331 | 1 | 17:56 | Afternoon | Sunday | 2016 | 8
4009 | 2016-08-28 18:35 | 2016-08-28 18:35 | 13.8KV RANGAU FEEDER #2 | Foggy and Smoke | Dead End Insulator | 0 | Rangau fdr #2 Load dropped 58A (70-12A). Not checked yet. | 3253331 | 1 | 18:35 | Afternoon | Sunday | 2016 | 8
4010 | 2016-08-28 18:35 | 2016-08-29 17:00 | 13.8KV RANGAU FEEDER #2 | Foggy and Smoke | Dead End Insulator | 0 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 1x Ctr: 140-141. Patrolled the line & found, @2 broken Dead end Insulator o/p #22BD-15. Cause: Dead end Insulator. | 3253331 | 1 | 18:35 | Afternoon | Sunday | 2016 | 8
4011 | 2016-08-29 11:15 | 2016-08-29 11:15 | 13.8KV 8D FEEDER #1 | Fair | Pin Insulator | 41 | 8D OCB fdr #1 T/R 1x. Not checked yet. | 3253333 | 1 | 11:15 | Morning | Monday | 2016 | 8
4012 | 2016-08-29 11:15 | 2016-08-31 21:00 | 13.8KV 8D FEEDER #1 | Fair | Pin Insulator | 41 | Checked & found, 8D OCB fdr #1 T/R 1x Ctr: 1988-1989 R/F: 51@2. Patrolled the line & found, @2 broken Pin Insulator o/p #8E-133. Cause: Pin Insulator. | 3253333 | 1 | 11:15 | Morning | Monday | 2016 | 8
4013 | 2016-08-29 15:00 | 2016-08-29 15:00 | 115KV CENTRAL DURI - BATANG LINE | Fair | Under investigation | 121 | 15:00 115KV C.Duri OCB #31 T/O. (In block position for replacing L/A) 115KV C.Duri OCB #33 T/O. (In block position for replacing L/A) 115KV Sintong GCB #25 T/O. (In Block position for replacing L/A) (115KV C.Duri - Sintong line T/O) (Batang Substation no power / black out) Respectively load drop at: Sintong fdr #2 load dropped 151A (216-65A). Sintong fdr #1 load dropped 23A (74-49A). Menggala fdr #1 load dropped 105A (168-63A). Nella fdr #1 load dropped 86A (266-140A). Bangko Fdr #4 load dropped 36A (236-200A). Balam fdr #4 load dropped 34A (180-146A). 15:01 Manually closed 115KV C.Duri OCB #33. Manually closed 115KV C.Duri OCB #31. Manually closed 115 KV Sintong GCB #25. (115KV C.Duri - Sintong line energized) Not checked yet. Note: Batang fdr #1. (Batang field / PHE Prod. Loss: 6 Bbls, 60 wells) Batang fdr #2. (Rantau Bais, HO prod. loss:........) Batang fdr #3. (Pemburu, candi, Balam-GS / Prod. loss: 49 Bbls, 19 Wells) | 3253331 | 1 | 15:00 | Afternoon | Monday | 2016 | 8
4014 | 2016-08-29 17:23 | 2016-08-29 17:23 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 40 | Minas fdr #1 Load dropped 129A (129-0). Minas fdr #2 load dropped 26A (126-100). Not checked yet. | 3253333 | 1 | 17:23 | Afternoon | Monday | 2016 | 8
4015 | 2016-08-29 17:23 | 2016-08-31 21:03 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 40 | Checked & found, Minas ACB fdr #1 T/R 1x Ctr: Not reported yet. R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3253333 | 1 | 17:23 | Afternoon | Monday | 2016 | 8
4016 | 2016-08-29 18:13 | 2016-08-29 18:13 | MINAS POWER PLANT |  |  | - | Off line MGT #3, then S/D the Unit for S/B. (Due to Excitation problem) |  | 1 | 18:13 | Afternoon | Monday | 2016 | 8
4017 | 2016-08-29 18:31 | 2016-08-29 18:31 | MINAS POWER PLANT |  |  | - | 18:31 S/U MGT #2, then online the Unit at 18:46. |  | 1 | 18:31 | Afternoon | Monday | 2016 | 8
4018 | 2016-08-29 23:39 | 2016-08-29 23:39 | 13.8KV NELLA FEEDER #1 | Fair | Recloser | 2230 | 23:39 Nella VCB fdr #1 T/SO Ctr: 486-495 R/F: 51@1, 51N. Nella GFPC T/R 1x. (Ground fault Alarm at Nella fdr #1) 30-Aug-2016. 00:40 Checked & found, Nella VCB fdr #1 T/SO. Ctr: 486;487 R/F: Not appear. Patrolled the Line & found, broken power Pole #21T-11. (toward Wells BKO #55 & #225) Open HLC o/p #20V-36. (to Isolate broken Pole above) 01:45 Blocked & Closed Nella VCB fdr #1, but Tripped again. 03:00 Open LBS #20V-01 . Blocked & Closed Nella VCB fdr#1, Ok. Re-patrolled the line under LBS #20V-01 & found, seriously broken Pin Insulator o/p #...... (Then replaced its broken Pin Insulator above) Open Nella VCB fdr #1, then Closed LBS #20V-01. 05:30 Blocked & Closed Nella fdr #1, but Tripped again. (by the same Alarm / Ground fault) 05:41 Open Recl. 22V-06. Blocked & Closed Nella VCB fdr #1, but tripped again. Transferred Load of Recl. 22V-06 to Banko fdr #1. 06:15 Closed LBS #23W-01, Ok. (Banko fdr #1 Load to be 306A) Cause: Under investigation. (Continued repatrolling line / Between LBS #20V-01 and Recl. 22V-06) 07:30 Open Recl. #21V-01. Blocked and closed Nella Fdr #1. Ok. 07:42 Mannually open Nella Fdr #1. By Pass Recl. #21V-01. 07:48 Blocked and closed Nella Fdr #1. Ok, then released the block. 08:08 Closed Recl. #22V-01 (Paralel Nella Fdr #1 to Bangko Fdr #1). 08:42 Re open Recl. #22V-01 (LBS #23W-01 failed to open). 14:23 Closed Recl. #22V-01 (Paralel Nella Fdr #1 to Bangko Fdr #1). Open LBS # 23W-01 (Nella Fdr #1 back to normal). (Prod. loss is not reported yet) Cause: Recloser. | 3253331 | 1 | 23:39 | Night | Monday | 2016 | 8
4019 | 2016-08-30 02:00 | 2016-08-30 02:00 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 9 | Libo OCB fdr #1 T/R 1x. Not checked yet. | 3253331 | 1 | 2:00 | Night | Tuesday | 2016 | 8
4020 | 2016-08-30 02:00 | 2016-08-31 14:00 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 9 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 373-374 R/F: 50/51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3253331 | 1 | 2:00 | Night | Tuesday | 2016 | 8
4021 | 2016-08-30 09:39 | 2016-08-30 09:39 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Secondary Cable | 0 | 09:39 It was reported b/o fuse for Tx o/p #05-N7-15. 17:00 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx o/p #05-N7-15. Replaced b/o fuses above with same size, then energized the Tx. Cause: Secondary cable. | 3253331 | 1 | 9:39 | Morning | Tuesday | 2016 | 8
4022 | 2016-08-30 11:30 | 2016-08-30 11:30 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Secondary Cable | 30 | 11:30 It was reported b/o fuse for Tx o/p #08-M1-19. 17:00 Checked & found, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #08-M1-19. Replaced b/o fuses above with same size, then energized the Tx. Cause: Secondary Cable. | 3253331 | 1 | 11:30 | Morning | Tuesday | 2016 | 8
4023 | 2016-08-30 13:24 | 2016-08-30 13:24 | MINAS POWER PLANT |  |  | - | 13:24 MGT #11 Tripped off. By Alarm: Generator Ventilation trouble. Cause: Under investigation. |  | 1 | 13:24 | Afternoon | Tuesday | 2016 | 8
4024 | 2016-08-30 14:10 | 2016-08-30 14:10 | MINAS POWER PLANT |  |  | - | 14:10 S/U MGT #9, then on line the Unit at 14:34. |  | 1 | 14:10 | Afternoon | Tuesday | 2016 | 8
4025 | 2016-08-31 06:26 | 2016-08-31 06:26 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Dead End Insulator | 0 | Duri Community ACB fdr #1 T/R 1x . Not checked yet. | 3253331 | 1 | 6:26 | Morning | Wednesday | 2016 | 8
4026 | 2016-08-31 06:26 | 2016-02-09 14:30 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Dead End Insulator | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 88-89 R/F: 51N. Patrolled the line & found, @1, @3 F/O Dead end Insulators o/p #KT-34. Cause: dead end Insulator. | 3253331 | 1 | 6:26 | Morning | Wednesday | 2016 | 8
4027 | 2016-08-31 06:50 | 2016-08-31 06:50 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Recloser - Control Recloser | 352 | 06:50 C.Duri fdr #6 Load dropped 65A (110-45). 09:20 It was reported no power at #03-02-.. and #03-00-... 10:05 Checked and found : 1. Recl. 03-02-02 Closed position. (at downstream of Recl. 02-01-01) 2. Recl. 03-00-02 Closed position. (at downstream of Recl. 02-01-01) 3. Recl. 02-01-01 T/LO Ctr: ...... 10:15 Patrolled the line at downstream of Recl. 02-01-01, but nothing found. 10:20 Blocked and closed Recl. 02-01-01, but failed. Patrolled the line, but nothing found. Opened Recl. 03-02-02 and Recl. 03-00-02 (downstream of Recl. 02-01-01) (Then functioning test of Recl. 02-01-01, but the Recloser failed to close) Opened 300 KVar Cap Bank o/p #03-02-09. Opened 600 KVar Cap Bank o/p #03-02-14. By pass Recl. 03-02-02. (Suspected Recloser control problem) Transferred load of Recl. 03-00-02 (CD fdr #6) to CD fdr #7. By closing LBS #03-00-27. 13:00 Blocked and closed Recl. 02-01-01, Ok. Then released the block. Cause: Recloser control problem. | 3253331 | 1 | 6:50 | Morning | Wednesday | 2016 | 8
4028 | 2016-08-31 14:54 | 2016-08-31 14:54 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | C.Duri fdr #2 Load dropped 113A (201-88A). Not checked yet. | 3253331 | 1 | 14:54 | Afternoon | Wednesday | 2016 | 8
4029 | 2016-08-31 14:54 | 2016-02-09 14:00 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recl. 08-M1-38 (C.Duri fdr #2) T/R 1x Ctr: 161-162 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3253331 | 1 | 14:54 | Afternoon | Wednesday | 2016 | 8
4030 | 2016-08-31 16:04 | 2016-08-31 16:04 | MINAS POWER PLANT |  |  | - | Off line MGT #4, then S/D the Unit for S/B. |  | 1 | 16:04 | Afternoon | Wednesday | 2016 | 8
4031 | 2016-08-31 16:40 | 2016-08-31 16:40 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 0 | Pungut fdr #2 Load dropped 30A (40-10A). Not checked yet | 3253331 | 1 | 16:40 | Afternoon | Wednesday | 2016 | 8
4032 | 2016-08-31 16:40 | 2016-02-09 07:10 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Pungut OCB fdr #2 T/R 1x Ctr: 352-353. Patrolled the line & found: -@3 Broken Pin Insulator o/p #43BY-05. -@1,@3 Broken Pin Insulators o/p #43BY-16. Cause: Lightning. | 3253331 | 1 | 16:40 | Afternoon | Wednesday | 2016 | 8
4033 | 2016-08-31 17:14 | 2016-08-31 17:14 | 13.8KV NORTH DURI FEEDER #9 | Rain and Lightning | Lightning | 0 | N.Duri VCB fdr #9 T/R 2x. Not checked yet. | 3253331 | 1 | 17:14 | Afternoon | Wednesday | 2016 | 8
4034 | 2016-08-31 17:14 | 2016-01-09 09:27 | 13.8KV NORTH DURI FEEDER #9 | Rain and Lightning | Lightning | 0 | Checked & found, N.Duri VCB fdr #9 T/R 2x Ctr: 41-43 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3253331 | 1 | 17:14 | Afternoon | Wednesday | 2016 | 8
4035 | 2016-08-31 17:14 | 2016-08-31 17:14 | DARLING SUBSTATION | Rain and Lightning | Under investigation | 108 | 17:14 It was reported No Power at CGS-5. (Darling RTU was Failed) 18:20 Checked Darling Substation & found: -115KV Darling-TX #2 Tripped. By R/F:.......... & 86T. -115KV Darling GCB #1 T/O. Ctr: 191-192 -115KV Darling GCB #2 T/O. Ctr: 104-105 Closed 115KV Darling GCB #1, but Failed. (After select 79C/O position on DL, OFF, SC). Open Isolation Switch of VCB Darling fdr #6 & Darling fdr #7. (Transferred all load Darling fdr #6 to C.Duri fdr #11), to anticipate spill at CGS-5 18:47 Closed C.Duri fdr #11. (after opened Isolation Switches of Darling VCB fdr #6) 18:49 Closed Darling 115KV GCB #1 & GCB #3, OK. Closed both Isolation Switch of Darling fdr #7. 19:04 Closed Darling VCB fdr #7. (On Block position), then Released the Block. Cause: Under Investigation. | 3253331 | 1 | 17:14 | Afternoon | Wednesday | 2016 | 8
4036 | 2016-08-31 17:14 | 2016-08-31 17:14 | 13.8KV DURI FIELD FEEDER #2 | Rain and Lightning | Lightning | 325 | 17:14 D.Field fdr #2 Load dropped 64A (148-84A). 19:12 It was reported No Power at Duri Field Area-7, Road-S6. 20:34 Checked & found, Recl. 07-U3-21 (D.Field fdr #2) T/SO. Ctr: 152-153. Blocked & closed Recl. 07-U3-21, Ok. Then released the Block. Patrolled the Line, but found nothing. Cause: Suspected by Lightning. | 3253331 | 1 | 17:14 | Afternoon | Wednesday | 2016 | 8
4037 | 2016-01-09 05:59 | 2016-01-09 05:59 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | 05:59 C.Duri ACB fdr #7 T/R 1x Ctr: 463-464 R/F: 51N (@1). C.Duri fdr #6 Load dropped 42A (91-49A). 14:00 Patrolled the line but found nothing. Cause: Unidentified. | 3267191 | 1 | 5:59 | Morning | Saturday | 2016 | 1
4038 | 2016-01-09 14:05 | 2016-01-09 14:05 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Animal | 0 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3267192 | 1 | 14:05 | Afternoon | Saturday | 2016 | 1
4039 | 2016-01-09 14:05 | 2016-05-09 08:00 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Animal | 0 | Checked and found, OKB OCB fdr #2 T/R 1x Ctr: 1261-1262 R/F: 51N. Patrolled the line and found, a dead Bird on Tx at Well KB #283. Cause: Animal. (Bird) | 3267192 | 1 | 14:05 | Afternoon | Saturday | 2016 | 1
4040 | 2016-01-09 14:10 | 2016-01-09 14:10 | 115KV KOTABATAK JUNCTION-KOTABATAK LINE | Rain and Lightning | Others | 3022 | 14:10 KBJ 115KV GCB #41 T/O. Ctr: 209-210. KBJ 115KV GCB #43 T/O. Ctr: 418-419. (115KV KBJ - Kota Batak line T/O, By R/F: 21P @1,@2.(Zone-2) Patrolled the Line, but found nothing. 14:16 Manually Closed 115KV GCB #41 but Failed. (Continued Patrolling the Line and found, steel Roof of NKBS Substation flying and Touch to the 115KV Conductor at NKBS Substation) 15:40 Manually Opened 115KV NKBS C/S and Bypassing 115KV NKBS OCB #1 (line toward CKBS) 15:43 Closed 115KV KBJ GCB #41, Ok. Closed 115KV KBJ GCB #43, Ok. (115KV KBJ - Kotabatak line energized) 17:14 Closed 115KV NKBS C/S. 17:15 Blocked and Closed NKBS VCB fdr #3, Ok. Then Released the Block. 17:16 Blocked and Closed NKBS VCB fdr #4, Ok. Then Released the Block. 17:17 Blocked and Closed NKBS VCB fdr #5, Ok. Then Released the Block. 18:38 Normalized Bypass of 115KV NKBS OCB #1. Cause: Others. (Extreme Weather / Heavy rain & wind) | 3267192 | 1 | 14:10 | Afternoon | Saturday | 2016 | 1
4041 | 2016-01-09 14:44 | 2016-01-09 14:44 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 56 | 4B OCB fdr #1 T/R 2x. Not checked yet. | 3267192 | 1 | 14:44 | Afternoon | Saturday | 2016 | 1
4042 | 2016-01-09 14:44 | 2016-06-09 11:55 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 56 | Checked and found, 4B OCB fdr #1 T/R 3x Ctr: 285-288 R/F: 51N. Patrolled the line and found, @2 broken L/A on TP of Well #3A-93. Cause: Lightning. | 3267192 | 1 | 14:44 | Afternoon | Saturday | 2016 | 1
4043 | 2016-01-09 15:03 | 2016-01-09 15:03 | 13.8KV 4D FEEDER #6 | Rain and Lightning | Lightning | 0 | 4D OCB fdr #6 T/R 1x Ctr: 181-182 R/F: 51@1,@2,@3. Not Patrolled yet. | 3267192 | 1 | 15:03 | Afternoon | Saturday | 2016 | 1
4044 | 2016-01-09 15:03 | 2016-04-09 07:54 | 13.8KV 4D FEEDER #6 | Rain and Lightning | Lightning | 0 | Patrolled the line, but found Nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 15:03 | Afternoon | Saturday | 2016 | 1
4045 | 2016-01-09 15:06 | 2016-01-09 15:06 | MINAS POWER PLANT |  |  | - | S/U MGT #6, then On line the Unit at 15:27. (Due to S/D NDC-CT #1 for repairing) |  | 1 | 15:06 | Afternoon | Saturday | 2016 | 1
4046 | 2016-01-09 15:08 | 2016-01-09 15:08 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Others | 17 | 15:08 4D OCB fdr #4 T/SO. 16:49 Manually Closed 4D OCB fdr 4. Not checked and patrolled yet. | 3267192 | 1 | 15:08 | Afternoon | Saturday | 2016 | 1
4047 | 2016-01-09 15:08 | 2016-04-09 23:10 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Others | 17 | Checked & found, 4D OCB fdr #4 T/O. Ctr: 237-238 R/F: 81. Patrolled the line, but found nothing. Cause: Others. (When 115KV KBJ-Kotabatak line Tripped and NDC-CT #1 emergency S/D) | 3267192 | 1 | 15:08 | Afternoon | Saturday | 2016 | 1
4048 | 2016-01-09 15:08 | 2016-01-09 15:08 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Others | 30 | 15:08 4D OCB fdr #5 T/SO. 16:51 Manually Closed 4D OCB fdr #5. Not checked and patrolled yet. | 3267192 | 1 | 15:08 | Afternoon | Saturday | 2016 | 1
4049 | 2016-01-09 15:08 | 2016-04-09 07:50 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Others | 30 | Checked & found, 4D OCB fdr #5 T/O. Ctr: 285-286 R/F: 81. Patrolled the line, but found nothing. Cause: Others. (When 115KV KBJ-Kotabatak line tripped and NDC-CT #1 emergency S/D) | 3267192 | 1 | 15:08 | Afternoon | Saturday | 2016 | 1
4050 | 2016-01-09 15:14 | 2016-01-09 15:14 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 0 | 4D OCB fdr #2 T/R 1x. Not checked yet. | 3267192 | 1 | 15:14 | Afternoon | Saturday | 2016 | 1
4051 | 2016-01-09 15:14 | 2016-04-09 23:15 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked and found, 4D OCB fdr #2 T/R 1x Ctr: 234-235 R/F: 51N. Patrolled the line and found, @1 broken L/A o/p #3D-5. Cause: Lightning. | 3267192 | 1 | 15:14 | Afternoon | Saturday | 2016 | 1
4052 | 2016-01-09 15:41 | 2016-01-09 15:41 | MINAS POWER PLANT |  |  | - | S/U MGT #8, then On line the Unit at 15:57. (Due to S/D NDC-CT #1 for repairing) |  | 1 | 15:41 | Afternoon | Saturday | 2016 | 1
4053 | 2016-01-09 16:02 | 2016-01-09 16:02 | NORTH DURI POWER PLANT |  |  | - | Off line NDC-CT #1, then S/D the Unit for NSB at 16:05. (Due to Exciter Diode Failure) |  | 1 | 16:02 | Afternoon | Saturday | 2016 | 1
4054 | 2016-01-09 16:07 | 2016-01-09 16:07 | DARLING SUBSTATION | Rain and Lightning | Lightning | 46 | 16:07 Darling 115KV GCB #2 T/O. Ctr: 173-174 Darling 115KV GCB #4 T/O. Ctr: 83-84 R/F: .... and 86T. (115KV Darling TX-2 no power) 17:00 Checked and found, 115KV Darling TX-2 Tripped Off. By R/F: .... and 86T. Opened 13.8KV Darling VCB fdr #3. Opened 13.8KV Darling VCB Fdr #4. 17:18 Reset the Relay 86T. Closed 115KV Darling GCB #2, Ok. Closed 115KV Darling GCB #4, Ok. (115KV Darling TX-2 Energized) 17:19 Closed 13.8KV Darling VCB fdr #3, Ok. Closed 13.8KV Darling VCB fdr #4, Ok. Cause: Under Investigation | 3267191 | 1 | 16:07 | Afternoon | Saturday | 2016 | 1
4055 | 2016-01-09 16:07 | 2016-03-09 18:02 | DARLING SUBSTATION | Rain and Lightning | Lightning | 46 | Checked and found, 115KV DARLING GCB #2 T/O. Ctr: 124-125 R/F: 86T. 115KV DARLING GCB #4 T/O. Ctr: 163-164 R/F: 86T. Checked Susbstation and the Line, but found nothing. Cause: Suspected by Lightning. | 3267191 | 1 | 16:07 | Afternoon | Saturday | 2016 | 1
4056 | 2016-01-09 16:08 | 2016-01-09 16:08 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 29 | 16:08 Rokan VCB fdr #2 T/O. (On Block Status due to Rig activity) 16:24 Manualy Closed Rokan VCB fdr #2. Not checked and patrolled yet. | 3267191 | 1 | 16:08 | Afternoon | Saturday | 2016 | 1
4057 | 2016-01-09 16:08 | 2016-04-09 16:30 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 29 | Checked and found, Rokan VCB fdr #2 T/R 1x Ctr: 1242-1243 R/F: 51N. Patrolled the line and found: -@1,@3 F/O Dead end Insulators o/p #32AV-23. -@1,@3 F/O Dead end Insukators o/p #30AV-30. -@1,@3 F/O Dead end Insulators o/p #29AV-20. Cause: Lightning. | 3267191 | 1 | 16:08 | Afternoon | Saturday | 2016 | 1
4058 | 2016-01-09 18:13 | 2016-04-09 20:15 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 19 | Checked and found, 3D OCB fdr #3 T/R 1x Ctr: 439-440 R/F: 50@1,@2. Patrolled the line and found, @1,@2 broken L/As on TP of Well #3D-92. Cause: Lightning. | 3267192 | 1 | 18:13 | Afternoon | Saturday | 2016 | 1
4059 | 2016-01-09 18:13 | 2016-04-09 20:15 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 19 | Checked and found, 3D OCB fdr #3 T/R 1x Ctr: 439-440 R/F: 50@1,@2. Patrolled the line and found, @1,@2 broken L/As on TP of Well #3D-92. Cause: Lightning. | 3267192 | 1 | 18:13 | Afternoon | Saturday | 2016 | 1
4060 | 2016-01-09 20:11 | 2016-01-09 20:11 | NEW KOTABATAK SUBSTATION | Rain and Lightning | Unidentified | 0 | 20:11 NKBS 115KV Circuit Switcher T/O. 21:30 Checked and found NKB Circuit Switcher T/O, and NKB TX Off Line, R/F: Not Appear. NKB Fdr#3, #4, #5 No power. Open Isolation Switches of NKB Fdr#3, and Fdr#4. Transfer Load NKB Feeder to CKBS. 21:34 Transfer Load NKB Fdr#3 to CKB Fdr#1 Closed LBS 3.6CU.05, OK. 21:48 Transfer Load NKB Fdr#4 to CKB Fdr#3. (LBS 37.CV.13 Have ben Closed status before, NKB fdr#1 transfer to CKB fdr#3). Closed LBS 37.CV.12, OK. 22:51 Closed 115 KV NKB Circuit Switcher, OK. 22:53 Closed 13.8KV NKB OCB Fdr#5, OK. Cause: Unidentified. | 3267192 | 1 | 20:11 | Night | Saturday | 2016 | 1
4061 | 2016-01-09 20:40 | 2016-01-09 20:40 | MINAS POWER PLANT |  |  | - | S/U MGT #1, then On Line the Unit at 21:45. (Due to emergency S/D NDC-CT #1 for replacing broken Diode) |  | 1 | 20:40 | Night | Saturday | 2016 | 1
4062 | 2016-02-09 08:23 | 2016-02-09 08:23 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Duri Field ACB fdr #4 T/R 1x. Not checked yet. | 3267191 | 1 | 8:23 | Morning | Tuesday | 2016 | 2
4063 | 2016-02-09 08:23 | 2016-04-09 11:40 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Duri Field ACB fdr #4 T/R 1x Ctr: 474-475 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 8:23 | Morning | Tuesday | 2016 | 2
4064 | 2016-02-09 09:00 | 2016-02-09 09:00 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified (Fuse) | 2 | 09:00 It was reported no power at CSS Area-1. (C.Duri fdr #3) 17:08 Checked & found, @2,@3 b/o 100K fuses for 1.2Mva Tx at CSS Area-1. Perform TTR and Megger found, good reading. Replaced b/o fuse above with same size and energized the Tx. Cause: Unidentified (fuse). | 3267191 | 1 | 9:00 | Morning | Tuesday | 2016 | 2
4065 | 2016-02-09 14:05 | 2016-02-09 14:05 | MINAS POWER PLANT |  |  | - | 14:05 S/U MGT #3, then On Line the Unit at 14:28 (Due to S/D NDC-CT#1 for replacing Diode fuse) |  | 1 | 14:05 | Afternoon | Tuesday | 2016 | 2
4066 | 2016-02-09 14:22 | 2016-02-09 14:22 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Transformer Failure | 42 | 14:22 It was reported b/o fuse for Tx at Well KB #123. (CKBS fdr #1) 15:38 Checked & found, @2,@3 b/o 25K fuses for 550Kva Tx at Well KB #123. Tested the Tx & found, Low megger reading. Cause: Tx failure. (Low megger reading) (This Tx is not replaced yet) | 3267192 | 1 | 14:22 | Afternoon | Tuesday | 2016 | 2
4067 | 2016-02-09 14:22 | 2016-11-09 14:10 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Transformer Failure | 42 | Replaced 550Kva Tx failure with the same size at Well KB #123. Cause: Tx failure. (Low megger reading) | 3267192 | 1 | 14:22 | Afternoon | Tuesday | 2016 | 2
4068 | 2016-02-09 14:44 | 2016-02-09 14:44 | 13.8KV 5B FEEDER #4 | Fair | Unidentified | 706 | 5B fdr #4 Load dropped 180A. (.... - .....A) 14:44 It was reported no power at Well #.... 16:31 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO. Ctr: 71-72. Blocked & closed Recl. 4B-73, Ok. Then released the block. The line is not patrolled yet. | 3267192 | 1 | 14:44 | Afternoon | Tuesday | 2016 | 2
4069 | 2016-02-09 14:44 | 2016-06-09 16:00 | 13.8KV 5B FEEDER #4 | Fair | Unidentified | 706 | Patrolled the line, but found nothing. Cause: Unidentified. | 3267192 | 1 | 14:44 | Afternoon | Tuesday | 2016 | 2
4070 | 2016-02-09 15:20 | 2016-02-09 15:20 | 13.8KV 6DN FEEDER #2 | Fair | Planned Maintenance | 70 | 15:20 Manually opened 6DN OCB fdr #2. (For replacing 6DN Voltage Regulator-1 at 6DN Substation) 16:01 Manually closed 6DN OCB fdr #2. Cause: Plan Maintenance. | 123 | 1 | 15:20 | Afternoon | Tuesday | 2016 | 2
4071 | 2016-03-09 10:22 | 2016-03-09 10:22 | 13.8KV 4B FEEDER #1 | Fair | Animal | 40 | 10:22 It was reported no power at Well #3A-64N, #3W-48, #3A-65 & #3A-28. Checked & found, Recl. 3A-28 (4B fdr #1) T/LO. Ctr: 14-17. Patrolled the line & found, a dead Bird hang on load side of Recl. 3A-28. (Then tookdown it) 12:19 Blocked & closed Recl. 3A-28, Ok. Then released the Block. Cause: Animal. (Bird) | 3267192 | 1 | 10:22 | Morning | Wednesday | 2016 | 3
4072 | 2016-03-09 12:30 | 2016-03-09 12:30 | 13.8KV 4D FEEDER #4 | Fair | Transformer Failure | 0 | 12:30 It was reported b/o fuse for Tx at Well #5D-14E. (4D fdr #4) 15:30 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well #5D-14E. Perform TTR and Megger test found, low megger reading. Cause: Tx failure. (Low megger reading) (The Tx failure is not replaced yet) | 3267192 | 1 | 12:30 | Afternoon | Wednesday | 2016 | 3
4073 | 2016-03-09 12:30 | 2016-04-09 10:30 | 13.8KV 4D FEEDER #4 | Fair | Transformer Failure | 0 | Replaced 300 Kva Tx failure with same size and energized the Tx. Cause: Tx failure (low megger reading). | 3267192 | 1 | 12:30 | Afternoon | Wednesday | 2016 | 3
4074 | 2016-03-09 15:51 | 2016-03-09 15:51 | NEW KOTABATAK SUBSTATION | Fair | Relay Failure | 0 | 15:51 115KV NKBS-C/S T/O. Ctr: Did not reported yet. R/F: Not appear. 16:08 Manually opened 13.8KV NKBS VCB fdr #3. 16:15 Manually opened 13.8KV NKBS VCB fdr #5. Transferred all loads of NKBS fdr #3 to NKBS fdr #1. 16:33 Closed LBS #36-CU-35. (After opened both side Isolation switch of NKBS VCB fdr #3) 16:52 Manually closed 115KV NKBS-C/S at NKBS, Ok. 16:56 Manually Closed NKBS VCB fdr #5, Ok. Cause: Under Investigation. Investigation Result: Relay failure -> CT/VT module of T60 is fail. | 3267192 | 1 | 15:51 | Afternoon | Wednesday | 2016 | 3
4075 | 2016-04-09 00:37 | 2016-04-09 00:37 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified (Fuse) | 0 | 00:37 It was Reported b/o fuse for Tx o/p #13-F1-01. (N.Duri fdr #11) 10:31 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #13-F1-01. Perform TTR and Megger found, good reading. Repalced b/o fuse above with same size and energized the Tx. Cause: Unidentified (fuse). | 3267191 | 1 | 0:37 | Night | Saturday | 2016 | 4
4076 | 2016-04-09 14:13 | 2016-04-09 14:13 | MINAS POWER PLANT |  |  | - | 14:13 Off line MGT #4, then S/D the Unit for S/B. |  | 1 | 14:13 | Afternoon | Saturday | 2016 | 4
4077 | 2016-04-09 14:25 | 2016-04-09 14:25 | MINAS POWER PLANT |  |  | - | 14:25 Off line MGT #3, then S/D the Unit for S/B. |  | 1 | 14:25 | Afternoon | Saturday | 2016 | 4
4078 | 2016-04-09 14:30 | 2016-04-09 14:30 | MINAS POWER PLANT |  |  | - | 14:30 Off line MGT #1, then S/D the Unit for S/B. |  | 1 | 14:30 | Afternoon | Saturday | 2016 | 4
4079 | 2016-04-09 15:00 | 2016-04-09 15:00 | MINAS POWER PLANT |  |  | - | 15:00 Off line MGT #7, then S/D the Unit for S/B. |  | 1 | 15:00 | Afternoon | Saturday | 2016 | 4
4080 | 2016-04-09 15:07 | 2016-04-09 15:07 | MINAS POWER PLANT |  |  | - | 15:07 Off line MGT #8, then S/D the Unit for S/B. |  | 1 | 15:07 | Afternoon | Saturday | 2016 | 4
4081 | 2016-04-09 21:47 | 2016-04-09 21:47 | 13.8KV S. BALAM FEEDER #1 | Fair | Transformer Failure | 8 | It was reported b/o fuse for Tx at Well So.Balam #361. (So.Balam fdr #4). Not Checked Yet. | 3267191 | 1 | 21:47 | Night | Saturday | 2016 | 4
4082 | 2016-04-09 21:47 | 2016-05-09 11:25 | 13.8KV S. BALAM FEEDER #1 | Fair | Transformer Failure | 8 | 09:40 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well So.Balam #361. Perform TTR and Megger test the Tx, found low megger reading. Cause: Tx Failure. (Low megger reading) 11:25 Replaced 150Kva Tx failure with same size and energized the Tx. | 3267191 | 1 | 21:47 | Night | Saturday | 2016 | 4
4083 | 2016-05-09 15:30 | 2016-05-09 15:30 | 13.8KV BATANG FEEDER #3 | Fair | Animal | 27 | 15:30 It was reported no power at Candi Fields. (Batang fdr #3) 17:50 Checked & found, Recl. 36AL-13 (Batang fdr #3) T/SO. Ctr: 120-121. Patrolled the line & found, a dead Monkey hang on powerline o/p #35AK-15. (Then tookdown it) Blocked & closed Recl. 36AL-13, Ok. Then released block. Cause: Animal. (Monkey) | 3267191 | 1 | 15:30 | Afternoon | Monday | 2016 | 5
4084 | 2016-06-09 07:00 | 2016-06-09 07:00 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | 07:00 It was reported b/o fuse for 150Kva Tx. (Batang fdr #2) 11:30 Checked & found @2,@3 b/o 3.5SF fuses for 150Kva Tx at Well Rantau Bais #57. Perform TTR and Megger found good reading. Replaced b/o fuse above with same size and energized the Tx. Cause: Animal (Monkey). | 3267191 | 1 | 7:00 | Morning | Thursday | 2016 | 6
4085 | 2016-06-09 07:25 | 2016-06-09 07:25 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 41 | 07:25 OKB OCB fdr #2 T/R 1x. 15:00 Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1262-1263 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3267192 | 1 | 7:25 | Morning | Thursday | 2016 | 6
4086 | 2016-07-09 23:59 | 2016-07-09 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system Normal operation. |  | 1 | 23:59 | Night | Saturday | 2016 | 7
4087 | 2016-08-09 13:28 | 2016-08-09 13:28 | 13.8KV DURI FIELD FEEDER #1 | Fair | Secondary Cable | 0 | 13:28 It was reported b/o fuse for Tx o/p #TL-229. (C.Duri fdr #4) 16:10 Checked & found, broken secondary cable for 112.5Kva Tx o/p #TL-229. 17:54 Replaced broken Secondary cable & @1 b/o fuse with the same size o/p #TL-229, then energized the Tx. Cause: Secondary cable. | 3267191 | 1 | 13:28 | Afternoon | Tuesday | 2016 | 8
4088 | 2016-08-09 14:23 | 2016-08-09 14:23 | MINAS POWER PLANT |  |  | - | 14:23 S/U MGT #3. then on line the Unit at 14:35. |  | 1 | 14:23 | Afternoon | Tuesday | 2016 | 8
4089 | 2016-08-09 15:19 | 2016-08-09 15:19 | MINAS POWER PLANT |  |  | - | Off line MGT #2, the S/D the Unit for S/B. |  | 1 | 15:19 | Afternoon | Tuesday | 2016 | 8
4090 | 2016-08-09 17:33 | 2016-08-09 17:33 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 0 | Bangko fdr #1 Load dropped 19A (205-186). Bangko GFPC T/R 1x. Not checked yet. | 3267191 | 1 | 17:33 | Afternoon | Tuesday | 2016 | 8
4091 | 2016-08-09 17:33 | 2016-10-09 14:33 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 0 | Checked & found, Bangko GFPC T/R 1x Ctr: 94-95. Patrolled the line & found, @1,@2 b/o fuse for Tx at Well Bangko #268. (Bangko fdr #1) Cause: Animal. | 3267191 | 1 | 17:33 | Afternoon | Tuesday | 2016 | 8
4092 | 2016-08-09 20:06 | 2016-08-09 20:06 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 38 | 20:06 It was reported b/o fuse for Tx at Well BKO #268. (Bangko fdr #1) 21:40 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well BKO #268. Perform TTR and Megger found, good reading. Replaced b/o fuse above with same size and energized the Tx. Cause: Animal. (LIzard) | 3267191 | 1 | 20:06 | Night | Tuesday | 2016 | 8
4093 | 2016-09-09 04:37 | 2016-09-09 04:37 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Unidentified | 6 | 04:37 Bekasap fdr #2 Load dropped 49A (90-41A). Bekasap GFPC T/R 1x. 07:30 Checked & found, Recl. 37BD-12 (Bekasap fdr #2) T/SO. (in Block position) Ctr: 172-173. Blocked & closed Recl. 37BD-12, Ok. Then release the block. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 4:37 | Morning | Friday | 2016 | 9
4094 | 2016-09-09 10:45 | 2016-09-09 10:45 | 13.8KV NORTH DURI FEEDER #5 | Fair | Animal | 0 | 10:45 It was reported b/o fuse for Tx o/p #12-F9-07. (N.Duri fdr #5) 15:30 Checked & found, @2 b/o 7.0SF fuse for 225Kva Tx o/p #12-F9-07. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3267191 | 1 | 10:45 | Morning | Friday | 2016 | 9
4095 | 2016-09-09 13:07 | 2016-09-09 13:07 | 13.8KV 5B FEEDER #4 | Cloudy | Recloser - Control Recloser | 54 | 13:07 5B fdr #4 Load dropped 165A (233-68A). 15:00 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO. Ctr: 72-73. 15:30 Blocked & closed Recl. 4B-73, Ok. Then release the block. 15:55 By-pass & opened Recl. 4B-73. Cause: Control Recloser problem. | 3267192 | 1 | 13:07 | Afternoon | Friday | 2016 | 9
4096 | 2016-09-09 22:33 | 2016-09-09 22:33 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 17 | 22:33 It was reported b/o fuse for Tx at Well Petani #105. (Petani fdr #1) 00:00 Checked & found, @2,@3 b/o 3.5SF fuses for 150Kva Tx at Well Petani #105. Perform TTR & Megger test the Tx found, Low megger reading. Cause: Tx failure. (Low megger reading) (This Tx is not replaced yet) | 3267191 | 1 | 22:33 | Night | Friday | 2016 | 9
4097 | 2016-09-09 22:33 | 2016-10-09 14:40 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 17 | 14:40 Replaced 150Kva Tx failure with the same size & energized the Tx at Well Petani #105. Cause: Tx Failure. (Low Megger reading) | 3267191 | 1 | 22:33 | Night | Friday | 2016 | 9
4098 | 2016-10-09 12:00 | 2016-10-09 12:00 | 13.8KV MENGGALA FEEDER #2 | Fair | Transformer Failure | 0 | 12:00 It was reported b/o fuse for Tx at Well Sikladi #09. (Menggala fdr #2) 15:00 Checked & found, @1,@2 b/o 2.1SF fuses for 100Kva Tx at Well Sikladi #09. Perform TTR and Megger found, Low megger reading. Cause: Tx failure. (Low megger reading) (This Tx is not replaced yet) | 3267191 | 1 | 12:00 | Afternoon | Sunday | 2016 | 10
4099 | 2016-10-09 12:00 | 13/09/2016 10:00 | 13.8KV MENGGALA FEEDER #2 | Fair | Transformer Failure | 0 | Replaced 100Kva Tx failure with 150Kva Tx & energized the Tx at Well Sikladi #09. Cause: Tx failure. (Low megger reading) | 3267191 | 1 | 12:00 | Afternoon | Sunday | 2016 | 10
4100 | 2016-10-09 16:32 | 2016-10-09 16:32 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | D.Field ACB fdr #2 T/R 1x. Not checked yet. | 3267191 | 1 | 16:32 | Afternoon | Sunday | 2016 | 10
4101 | 2016-10-09 16:32 | 2016-11-09 13:30 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | Checked & found, D.Field ACB fdr #2 T/R 3x Ctr: 190-193 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 16:32 | Afternoon | Sunday | 2016 | 10
4102 | 2016-10-09 20:18 | 2016-10-09 20:18 | 13.8KV NELLA FEEDER #1 | Fair | Lightning Arrester | 225 | 20:18 Nella VCB fdr #1 T/SO. Ctr. & R/F are not reported yet. 20:44 Blocked & closed Nella VCB fdr #1, Ok. Then released the Block. The line is not patrolled yet. | 3267191 | 1 | 20:18 | Night | Sunday | 2016 | 10
4103 | 2016-10-09 20:18 | 14/09/2016 07:30 | 13.8KV NELLA FEEDER #1 | Fair | Lightning Arrester | 225 | Checked & found, Nella VCB fdr #1 T/SO. Ctr: 495-496 R/F: 51N. Patrolled the line & found, @1,@2 broken L/As on TP of Well Bangko #35. Cause: Lightning Arrester. | 3267191 | 1 | 20:18 | Night | Sunday | 2016 | 10
4104 | 2016-10-09 21:17 | 2016-10-09 21:17 | 13.8KV 5B FEEDER #4 | Fair | Unidentified | 14 | 5B OCB fdr #4 T/R 1x. Not checked yet. | 3267192 | 1 | 21:17 | Night | Sunday | 2016 | 10
4105 | 2016-10-09 21:17 | 2016-11-09 15:17 | 13.8KV 5B FEEDER #4 | Fair | Unidentified | 14 | Checked & found, 5B OCB fdr #4 T/R 1x Ctr: 330-331 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3267192 | 1 | 21:17 | Night | Sunday | 2016 | 10
4106 | 2016-11-09 07:28 | 2016-11-09 07:28 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Sintong fdr #2 Load dropped 71A (216-145A). Sintong GFPC T/R 1x. Not checked yet. | 3267191 | 1 | 7:28 | Morning | Wednesday | 2016 | 11
4107 | 2016-11-09 07:28 | 14/09/2016 07:15 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recl. 28AF-02 (Sintong fdr #2) T/R 1x Last Ctr: 628. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 7:28 | Morning | Wednesday | 2016 | 11
4108 | 2016-11-09 20:15 | 2016-11-09 20:15 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 17 | 20:15 It was reported b/o fuse for Tx at Well Bangko #200. (Nella fdr #1) 21:45 Checked & found, @1 b/o 14.0SF fuse for 500Kva Tx at Well Bangko #200. Performed TTR and Megger found, Good reading. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3267191 | 1 | 20:15 | Night | Wednesday | 2016 | 11
4109 | 2016-11-09 22:08 | 2016-11-09 22:08 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 24 | 5B OCB fdr #3 T/R 1x. Not checked yet. | 3267192 | 1 | 22:08 | Night | Wednesday | 2016 | 11
4110 | 2016-11-09 22:08 | 2016-12-09 07:30 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 24 | 07:30 5B fdr #3 is still dropped 64A (100-36A). 10:44 Checked & found, Recl. 4C-65A (5B fdr #3) T/SO. Ctr: 136-137. Blocked & closed Recl. above, Ok. Then released the block. Patrolled the line & found, @2 broken Pin Insulator o/p #4D-112. Cause: Lightning. | 3267192 | 1 | 22:08 | Night | Wednesday | 2016 | 11
4111 | 2016-11-09 22:08 | 13/09/2016 14:00 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 24 | Checked & found, 5B OCB fdr #3 T/R 1x Ctr: 360-361 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspedted by Lightning. | 3267192 | 1 | 22:08 | Night | Wednesday | 2016 | 11
4112 | 2016-11-09 22:08 | 2016-11-09 22:08 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 39 | 22:08 4D OCB fdr #2 T/R 1x. 4D fdr #3 Load dropped 55A (75-20A). Not checked yet. 22:14 4D OCB fdr #2 T/R 1x. Not checked yet. | 3267192 | 1 | 22:08 | Night | Wednesday | 2016 | 11
4113 | 2016-11-09 22:08 | 15/09/2016 19:00 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 39 | Checked & found, 4D OCB fdr #2 T/R 2x Ctr: 234-236 R/F: 51@1,@2. Patrolled the line & found, @1,@2 F/O Dead end Insulators o/p #4D- .... Cause: Lightning. | 3267192 | 1 | 22:08 | Night | Wednesday | 2016 | 11
4114 | 2016-11-09 22:08 | 2016-11-09 22:08 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 43 | 5B fdr #2 Load dropped 122A (169-47A). 5B fdr #1 Load dropped 71A (91-20A). Not checked yet. | 3267192 | 1 | 22:08 | Night | Wednesday | 2016 | 11
4115 | 2016-11-09 22:08 | 14/09/2016 14:00 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 43 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 340-341 R/F: 51N. Patrolled the line & found, @2 broken Dead end Insulator o/p #4C-75. Cause: Lightning. Also found, Recl. 5C-07 (5B fdr #2) T/R 1x Ctr: 48-49. Patrolled the line, but found nothing. Cause: Suspected by Lightning. Checked all Recloser at downstream of 5B fdr #1 & found, normal. (No Recloser Tripped) Cause: Suspected Voltage dip when 5B OCB fdr #2 T/R. | 3267192 | 1 | 22:08 | Night | Wednesday | 2016 | 11
4116 | 2016-11-09 22:08 | 2016-11-09 22:08 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Animal | 38 | 6D fdr #1 Load dropped 183A (243-60A). Not checked yet. | 3267192 | 1 | 22:08 | Night | Wednesday | 2016 | 11
4117 | 2016-11-09 22:08 | 15/09/2016 13:30 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Animal | 38 | Checked & found, Recl. 5C-42 (6D fdr #1) T/R 1x Ctr: 20-21. Patrolled the line & found, a dead Bird on the Recl. 5C-42. (No equipment damage) Cause: Animal. (Bird) | 3267192 | 1 | 22:08 | Night | Wednesday | 2016 | 11
4118 | 2016-11-09 22:12 | 2016-11-09 22:12 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 24 | 4D OCB fdr #5 T/R 1x. Not checked yet. | 3267192 | 1 | 22:12 | Night | Wednesday | 2016 | 11
4119 | 2016-11-09 22:12 | 15/09/2016 19:10 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 24 | Checked & found, 4D OCB fdr #5 T/R 1x Ctr: 286-287 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 22:12 | Night | Wednesday | 2016 | 11
4120 | 2016-11-09 22:12 | 2016-11-09 22:12 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 24 | 4D fdr #4 Load dropped 194A (233-39A). Not checked yet. | 3267192 | 1 | 22:12 | Night | Wednesday | 2016 | 11
4121 | 2016-11-09 22:12 | 15/09/2016 13:35 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 24 | Checked & found, Recl. 4D-85 (4D fdr #4) T/R 1x Ctr: 1613-1614. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 22:12 | Night | Wednesday | 2016 | 11
4122 | 2016-11-09 22:14 | 2016-11-09 22:14 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 13 | 4B OCB fdr #2 T/R 1x. Not checked yet. | 3267192 | 1 | 22:14 | Night | Wednesday | 2016 | 11
4123 | 2016-11-09 22:14 | 14/09/2016 14:10 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 13 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 229-230 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 22:14 | Night | Wednesday | 2016 | 11
4124 | 2016-11-09 22:24 | 2016-11-09 22:24 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 45 | 5B OCB fdr #2 T/R 1x. Not checked yet. | 3267192 | 1 | 22:24 | Night | Wednesday | 2016 | 11
4125 | 2016-11-09 22:24 | 18/09/2016 22:24 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 45 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 340-341 R/F: 51@2. Patrolled the line & found, @2 broken Dead-end Insulator o/p #4C-75. Cause: Lightning. | 3267192 | 1 | 22:24 | Night | Wednesday | 2016 | 11
4126 | 2016-12-09 10:18 | 2016-12-09 10:18 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 37 | Menggala fdr #1 Load dropped 136A (196-60A). Not checked yet. | 3267191 | 1 | 10:18 | Morning | Friday | 2016 | 12
4127 | 2016-12-09 10:18 | 15/09/2016 16:00 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 37 | Checked & found, Recl. 19AN-04 (Menggala fdr #1) T/R 1x Ctr: 322-323 R/F: 51N. Patrolled the line, but found nothing Cause: Unidentified. | 3267191 | 1 | 10:18 | Morning | Friday | 2016 | 12
4128 | 2016-12-09 16:58 | 2016-12-09 16:58 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | C.Duri ACB fdr #15 T/R 1x Ctr: 369-370 R/F: 51N. Not patrolled yet. | 3267191 | 1 | 16:58 | Afternoon | Friday | 2016 | 12
4129 | 2016-12-09 16:58 | 19/09/2016 16:58 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Caused: Unidentified. | 3267191 | 1 | 16:58 | Afternoon | Friday | 2016 | 12
4130 | 2016-12-09 22:00 | 2016-12-09 22:00 | 13.8KV ROKAN FEEDER #2 | Fair | Animal | 53 | 22:00 It was reported b/o fuse for Tx at Well Kopar #37. (Rokan fdr #2) 24:00 Checked & found, @2,@3 b/o 7.8SF fuses for 300Kva Tx at Well Kopar #37. Replaced b/o fuse above with the same size & energized the Tx, Cause: Animal. (Monkey) | 3267191 | 1 | 22:00 | Night | Friday | 2016 | 12
4131 | 2016-09-13 07:47 | 2016-09-13 07:47 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 65 | Ketigul VCB fdr #2 T/R 1x Ctr: 206-207 R/F: 51@1. Ketigul fdr #3 load dropped 10A (23-13A). Patrolled the line & found, a dead Monkey under pole #27AL-06. Cause: Animal. (Monkey) | 3267191 | 1 | 7:47 | Morning | Tuesday | 2016 | 9
4132 | 2016-09-13 08:19 | 2016-09-13 08:19 | 13.8KV 6D FEEDER #2 | Fair | Dead End Insulator | 12 | 6D fdr #2 Load dropped 90A (242-152A). Not checked yet. | 3267192 | 1 | 8:19 | Morning | Tuesday | 2016 | 9
4133 | 2016-09-13 08:19 | 2016-09-16 11:35 | 13.8KV 6D FEEDER #2 | Fair | Dead End Insulator | 12 | Checked & found, Recl. 6D-87 (6D fdr #2) T/R 1x Ctr: 51-52 R/F: 51N. Patrolled the line & found, @3 broken Dean End insulator o/p #6C-05. Cause: Dead End Insulator. | 3267192 | 1 | 8:19 | Morning | Tuesday | 2016 | 9
4134 | 2016-09-13 11:30 | 2016-09-13 11:30 | 13.8KV 8D FEEDER #3 | Fair | Transformer Failure | 86 | 11:30 It was reported b/o fuse for Tx at Well #8E-45N. 16:30 Checked & found, @2, @3 b/o 14.0SF fuses for 550Kva Tx at Well #8E-45. Performed TTR & Megger test, found TTR reading failed. Cause: Transformer failure. (This Tx is not replaced yet) | 3267192 | 1 | 11:30 | Morning | Tuesday | 2016 | 9
4135 | 2016-09-13 11:30 | 2016-09-18 11:30 | 13.8KV 8D FEEDER #3 | Fair | Transformer Failure | 86 | Replaced 550Kva Tx failure with the same size & energized the Tx at Well #8E-45E. Cause: Tx Failure. | 3267192 | 1 | 11:30 | Morning | Tuesday | 2016 | 9
4136 | 2016-09-13 20:58 | 2016-09-13 20:58 | KOTABATAK SUBSTATION | Cloudy | Under investigation | 180 | 20:58 Old Kotabatak 115KV Circuit Switcher T/O. 22:01 Checked & found, 115KV OKB C/S at OKB Substation T/O. Ctr:.... R/F: 51@1. Manually opened 13.8KV OKB OCB fdr #2. 22:10 Closed 115KV OKB C/S, but failed. (due to b/o fuse control of Circuit Switcher) Transferred load of OKB fdr #2 to CKBS fdr #1. A. Transfer part load CKBS fdr #1 to NKBS fdr #3 by: 1. Closed LBS #36CU-35. (Parallel CKBS fdr #1 and NKBS fdr #3). 2. Opened LBS #36CU-05. ( Part load of CKBS fdr #1 transfer to NKBS fdr #3) - Checked load : CKBS fdr #1 = 63A. - Checked load : NKBS fdr #3 = 378A. B. Transfer Load OKB fdr #2 (258 A) to CKBS fdr #1 by: 1. Closed LBS #37CX-11. -Checked load CKBS fdr #1. (258+63A = 331 A) Cause: Under Investigation. (Suspected Circuit Switcher problem) | 3267192 | 1 | 20:58 | Night | Tuesday | 2016 | 9
4137 | 2016-09-13 22:15 | 2016-09-13 22:15 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 0 | 22:15 It was reported no power at D/S of 8C fdr #4. (8C RTU was failed) 23:57 Checked & found, 8C VCB fdr #4 T/R 1x Ctr: 583-584 R/F: 51@3. Not Patrolled yet. | 3267192 | 1 | 22:15 | Night | Tuesday | 2016 | 9
4138 | 2016-09-13 22:15 | 2016-09-15 19:15 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 0 | Patrolled the line & found: -@3 F/O Dead end Insulator. -@2 Broken Dead end Insulator o/p #8D-39. Cause: Lightning. | 3267192 | 1 | 22:15 | Night | Tuesday | 2016 | 9
4139 | 2016-09-13 22:44 | 2016-09-13 22:44 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 0 | 8D OCB fdr #1 T/R 1x. Not checked yet. | 3267192 | 1 | 22:44 | Night | Tuesday | 2016 | 9
4140 | 2016-09-13 22:44 | 2016-09-15 19:20 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, 8D OCB fdr #1 T/R 1x Ctr: 1989-1090 R/F: 51@2. Patrolled the line & found, @2 broken Pin Insulator o/p #8E-133. Cause: Lightning. | 3267192 | 1 | 22:44 | Night | Tuesday | 2016 | 9
4141 | 2016-09-14 01:45 | 2016-09-14 01:45 | 8 CHARLIE SUBSTATION | Fair | Unidentified | 1140 | 01:45 It was reported no power at D/S of 8C OCB fdr #4. (8C Substation failed) To anticipate spill at Minas GS-2: 01:51 Open 8D OCB fdr #3, Then Closed at 04:28. 01:55 Open Minas ACB fdr #3, Then Closed at 04:27. 01:56 Open Minas ACB fdr #4, Then Closed at 04:28. 02:13 Checked & found, 115KV 8C C/S-Tx #2 T/O. Ctr: 153-154 R/F: 51G. 02:24 Open 8C OCB fdr #4, then Closed at 04:00. Open 8C OCB fdr #5, then Closed at 04:07. Open 8C OCB fdr #6, then Closed at 04:04. 02:25 Closed 115KV 8C C/S-Tx #2, but T/O again. 02:43 Open 8C OCB fdr #3, then Closed at 04:25. 02:45 Open 8C OCB fdr #1, then Closed at 04:11. 02:48 Open 8C OCB fdr #2, then Closed at 04:11. 02:47 Requested NDC plant to lowering load. (Frequency system was high) 03:15 Open Isolation switch 8C fdr #4, #5 & #6. 03:30 Closed 115KV 8C C/S-Tx #2, Ok. Closed Isolation Switch & close 8C VCB fdr #4, #5, #6. (after function test the breaker) 04:28 Power to GS-2 back to normal. Cause: Under Investigation. | 3267192 | 1 | 1:45 | Night | Wednesday | 2016 | 9
4142 | 2016-09-14 07:00 | 2016-09-14 07:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Secondary Cable | 0 | 07:00 It was reported b/o fuse for Tx o/p #07-T3-07. 10:49 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T3-07. Also found broken Secondary Cable. 14:28 Replaced broken secondary cable & b/o fuse above then energized the Tx. Cause: Secondary Cable. | 3267191 | 1 | 7:00 | Morning | Wednesday | 2016 | 9
4143 | 2016-09-14 10:39 | 2016-09-14 10:39 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 1 | 10:39 It was reported b/o fuse for Tx o/p #03-0-19. 15:08 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-0-19. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3267191 | 1 | 10:39 | Morning | Wednesday | 2016 | 9
4144 | 2016-09-14 11:27 | 2016-09-14 11:27 | 13.8KV MINAS FEEDER #1 | Fair | Planned Maintenance | 6 | 11:27-13:00 Blocked Recl. 7D-20 (Minas fdr #1) to opened HLC o/p #6D-280. Replaced Pin to Post Insulator type. (Well #6D-97 was off during this job) Cause: Planned Maintenance. | 123 | 1 | 11:27 | Morning | Wednesday | 2016 | 9
4145 | 2016-09-14 18:30 | 2016-09-14 18:30 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 63 | Sintong fdr #2 Load dropped 120A (215-95A). Not checked yet. | 3267191 | 1 | 18:30 | Afternoon | Wednesday | 2016 | 9
4146 | 2016-09-14 18:30 | 2016-09-15 18:30 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 63 | Checked & found, Recl. 28AF-02 (Sintong fdr #2) T/R 1x Ctr: 628-629 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267191 | 1 | 18:30 | Afternoon | Wednesday | 2016 | 9
4147 | 2016-09-15 08:13 | 2016-09-15 08:13 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 35 | Rangau fdr #2 Load dropped 59A (65-6A). Not checked yet. | 3267191 | 1 | 8:13 | Morning | Thursday | 2016 | 9
4148 | 2016-09-15 08:13 | 2016-09-18 08:13 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 35 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 2x Ctr: 141-143 R/F: 51@2. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 8:13 | Morning | Thursday | 2016 | 9
4149 | 2016-09-15 13:37 | 2016-09-15 13:37 | MINAS POWER PLANT |  |  | - | 13:37 S/U MGT #11, then online the Unit at 14:20. |  | 1 | 13:37 | Afternoon | Thursday | 2016 | 9
4150 | 2016-09-15 15:40 | 2016-09-15 15:40 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 15:40 It was reported b/o fuse for Tx at Well Jurong #37. Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Jurong #37. 19:00 Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3267191 | 1 | 15:40 | Afternoon | Thursday | 2016 | 9
4151 | 2016-09-15 16:22 | 2016-09-15 16:22 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | 2 | 16:22 It was reported b/o fuse for Tx o/p #06-Q5-13. 17:21 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #06-Q5-13. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3267191 | 1 | 16:22 | Afternoon | Thursday | 2016 | 9
4152 | 2016-09-15 16:43 | 2016-09-15 16:43 | MINAS POWER PLANT |  |  | - | 16:43 Offline MGT #9, then S/D the Unit for S/B. |  | 1 | 16:43 | Afternoon | Thursday | 2016 | 9
4153 | 2016-09-15 17:31 | 2016-09-15 17:31 | MINAS POWER PLANT |  |  | - | 17:31 S/U MGT #7, then online the Unit at 18:00 (For certification) 21:00 Off line MGT #7, then S/D the Unit for S/B. |  | 1 | 17:31 | Afternoon | Thursday | 2016 | 9
4154 | 2016-09-15 21:12 | 2016-09-15 21:12 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Lightning | 0 | C.Duri ACB fdr #5 T/R 1x Ctr: 229-230 R/F: 51N. The line is not patrolled yet. | 3267191 | 1 | 21:12 | Night | Thursday | 2016 | 9
4155 | 2016-09-15 21:12 | 2016-09-19 21:12 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Lightning | 0 | Patrolled the line & found, @1 broken L/A o/p #03-8A-10. Cause: Lightning. | 3267191 | 1 | 21:12 | Night | Thursday | 2016 | 9
4156 | 2016-09-15 21:12 | 2016-09-15 21:12 | 13.8KV DURI FIELD FEEDER #1 | Rain and Lightning | Tree | 81 | 21:12 Duri Field ACB fdr #1 T/LO. 22:28 Open Recl. 01-8-31, then close at 23:48. 22:35 Open Recl. 01-6-30. then close at 23:54. 22:35 Blocked & closed, Duri field ACB fdr #1, but T/O again. Patrolled the line & found, fall down tree & hit to power line near pole #.... (Then remove the Tree above) 23:45 Blocked & closed Duri Faied ACB fdr #1, Ok. Then released the block. Cause: Tree. | 3267191 | 1 | 21:12 | Night | Thursday | 2016 | 9
4157 | 2016-09-15 21:17 | 2016-09-15 21:17 | 115KV MINAS - 8C LINE | Rain and Lightning | Lightning | 274 | 115KV Minas SWY GCB #22 T/R 1x. 115KV Minas SWY GCB #26 T/R 1x. (115KV Minas SWY - 8C line) Not checked yet. | 3267192 | 1 | 21:17 | Night | Thursday | 2016 | 9
4158 | 2016-09-15 21:17 | 2016-09-16 21:17 | 115KV MINAS - 8C LINE | Rain and Lightning | Lightning | 274 | Checked & found: 115KV Minas SWY GCB #22 T/R 1x Ctr: 1525-1526. 115KV Minas SWY GCB #26 T/R 1x Ctr: did not change. R/F: Did not reported yet. (115KV Minas SWY - 8C line T/R 1x) Patrolled the line, but found nothing. Cause: Suspected by Ligthning. | 3267192 | 1 | 21:17 | Night | Thursday | 2016 | 9
4159 | 2016-09-15 21:43 | 2016-09-15 21:43 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 154 | 21:43 6DN OCB fdr #5 T/R 1x. 6DN fdr #6 Load dropped 150A (185-35A). 21:54 6DN OCB fdr #5 T/LO. Patrolled the line but found nothing. 16-Sep-2016. 00:20 Opened LBS #6D-16A. 00:30 Blocked & closed 6DN OCB fdr #5, Ok. 00:34 Closed LBS #6D-16A, but 6DN OCB fdr #5 Tripped off again. Re-Open LBS #6D-16A. 00:37 Blocked & closed, 6DN OCB fdr #5, Ok. 01:50 Patrolled the line & found, @2 seriously broken Pin Insulator o/p #6D-87. Then replaced broken Pin supported jumper Insulator above. 03:06 Open 6DN OCB fdr #5, to close LBS #6D-16A. 03:07 Blocked & closed, 6DN OCB fdr #5, but tripped off again. Opened By-pass SW of Recl. 6D-18. 03:39 Blocked & closed, 6DN OCB fdr #5, but tripped off again. 04:00 Patrolled the line & found, @1,@2 broken L/As of the Recl. 6D-18. (Isolated broken L/As above & open source site jumper of Recl. 6D-18) 04:10 Blocked & closed 6DN OCB fdr #5, Ok. Then released the block. Transferred load of Recl. 6D-18 to Minas fdr #1. 04:15 Closed LBS #6D-26A. Cause: Lightning. | 3267192 | 1 | 21:43 | Night | Thursday | 2016 | 9
4160 | 2016-09-15 21:44 | 2016-09-15 21:44 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 35 | 3D fdr #2 Load dropped 181A (204-23A). Not checked yet. | 3267192 | 1 | 21:44 | Night | Thursday | 2016 | 9
4161 | 2016-09-15 21:44 | 2016-09-16 11:44 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 35 | Checked & found, 3D OCB fdr #2 T/R 1x Ctr: 220-221 R/F:51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:44 | Night | Thursday | 2016 | 9
4162 | 2016-09-15 21:44 | 2016-09-15 21:44 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 28 | 21:44 3D fdr #3 Load dropped 127A (151-24A). 22:34 3D OCB fdr #3 T/R 1x. Not checked yet. | 3267192 | 1 | 21:44 | Night | Thursday | 2016 | 9
4163 | 2016-09-15 21:44 | 2016-09-16 11:40 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 28 | Checked & found, 3D OCB fdr #3 T/R 1x Ctr: 440-441 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:44 | Night | Thursday | 2016 | 9
4164 | 2016-09-15 21:44 | 2016-09-15 21:44 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 24 | 3D fdr #4 Load dropped 138A (203-65A). Not checked yet. | 3267192 | 1 | 21:44 | Night | Thursday | 2016 | 9
4165 | 2016-09-15 21:44 | 2016-09-16 21:44 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 24 | Checked & found, Recl. 2D-44 (3D fdr #4) T/R 1x Ctr: 10-11. Patrolled the line & found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:44 | Night | Thursday | 2016 | 9
4166 | 2016-09-15 21:46 | 2016-09-15 21:46 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 15 | 4D OCB fdr #3 T/R 1x. Not checked yet. | 3267192 | 1 | 21:46 | Night | Thursday | 2016 | 9
4167 | 2016-09-15 21:46 | 2016-09-16 11:42 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 15 | Checked & found, 4D OCB fdr #3 T/R 1x Ctr: 229-330 R/F: 51@2. Patrolled the line & found, @2 broken Pin Insulator o/p #4D-69. Cause: Lightning. | 3267192 | 1 | 21:46 | Night | Thursday | 2016 | 9
4168 | 2016-09-15 21:46 | 2016-09-15 21:46 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 20 | 4D fdr #2 Load dropped 109A (145-36A). Not checked yet. | 3267192 | 1 | 21:46 | Night | Thursday | 2016 | 9
4169 | 2016-09-15 21:46 | 2016-09-16 11:46 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 20 | Checked & found, Recl. 3D-119 (4D fdr #2) T/R 1x Ctr: 25-26. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:46 | Night | Thursday | 2016 | 9
4170 | 2016-09-16 06:38 | 2016-09-16 06:38 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | C.Duri ACB fdr #2 T/R 1x Ctr: 367-368 R/F: 51G, 51N. Not Patrolled yet. | 3267191 | 1 | 6:38 | Morning | Friday | 2016 | 9
4171 | 2016-09-16 06:38 | 2016-09-19 06:38 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | Checked & found, C.Duri ACB #2 T/R 1x Ctr: 367-368 R/F: 51N. Patrolled the line and found nothing. Caused: Unidentified. | 3267191 | 1 | 6:38 | Morning | Friday | 2016 | 9
4172 | 2016-09-16 10:07 | 2016-09-16 10:07 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Animal | 9 | 10:07 It was reported b/o fuse for Tx o/p #04-01-19. 13:38 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx o/p #04-01-19. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal (Bird). | 3267191 | 1 | 10:07 | Morning | Friday | 2016 | 9
4173 | 2016-09-16 10:55 | 2016-09-16 10:55 | MINAS POWER PLANT |  |  | - | 10:55 S/U MGT #1 then online the unit at 11:30. (For certification). 16:35 Off line MGT#1, then S/D the unit for S/B. |  | 1 | 10:55 | Morning | Friday | 2016 | 9
4174 | 2016-09-16 13:00 | 2016-09-16 13:00 | 13.8KV 4D FEEDER #5 | Fair | Unidentified (Fuse) | 1 | 13:00 It was reported b/o fuse for Tx at Well #4D-96. 17:16 Checked & found, @2, @3 b/o 3.5SF fuses for 150Kva Tx at Well #4D-96. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3267192 | 1 | 13:00 | Afternoon | Friday | 2016 | 9
4175 | 2016-09-16 13:12 | 2016-09-16 13:12 | 13.8KV DURI FIELD FEEDER #1 | Fair | Animal | 0 | 13:12 It was reported b/o fuse for Tx o/p 42-D-54 (Toman Office). 14:12 Checked & found, @2, @3 b/o fuse for 112.5KVA Tx. Also found broken Sec. Breaker. Replaced broken Sec. breaker above by FM Electrical Team. 15:58 Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal (Squirrel). | 3267191 | 1 | 13:12 | Afternoon | Friday | 2016 | 9
4176 | 2016-09-16 15:30 | 2016-09-16 15:30 | MINAS POWER PLANT |  |  | - | 15:30 S/U MGT#8, then on line the unit at 15:54. (For Certificate). 18:54 Off line MGT#8, then S/D the unit for S/B. |  | 1 | 15:30 | Afternoon | Friday | 2016 | 9
4177 | 2016-09-16 16:23 | 2016-09-16 16:23 | 13.8KV CENTRAL DURI FEEDER #16 | Rain and Lightning | Lightning | 0 | C.Duri ACB fdr #16 T/R 2x Ctr: 290-292 R/F: 51N. Not patrolled yet. | 3267191 | 1 | 16:23 | Afternoon | Friday | 2016 | 9
4178 | 2016-09-16 16:23 | 2016-09-19 | 13.8KV CENTRAL DURI FEEDER #16 | Rain and Lightning | Lightning | 0 | Patrolled the line & found, @1 F/O Deadend Insulator o/p #09-N2-01A. Caused: Lightning. | 3267191 | 1 | 16:23 | Afternoon | Friday | 2016 | 9
4179 | 2016-09-16 18:08 | 2016-09-16 18:08 | 13.8KV S. BALAM GFPC | Cloudy and Lightning | Lightning | 0 | Balam GFPC T/R 1x. Ground fault alarm on So.Balam fdr #2. (No load dropped at any fdrs.) Not checked yet. | 3267191 | 1 | 18:08 | Afternoon | Friday | 2016 | 9
4180 | 2016-09-16 18:08 | 2016-09-19 07:10 | 13.8KV S. BALAM GFPC | Cloudy and Lightning | Lightning | 0 | Checked & found, So.Balam GFPC T/R 1x Ctr: 226-227 R/F: 51N. Patrolled So.Balam fdr #2 line, but found nothing. Cause: Suspected by Lightning. | 3267191 | 1 | 18:08 | Afternoon | Friday | 2016 | 9
4181 | 2016-09-16 21:34 | 2016-09-16 21:34 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 0 | Sintong fdr #1 Load dropped 30A (80-50A). Sintong fdr #2 Load dropped 46A (215-169A). (Oil Pump Off) Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #1) Not checked yet. | 3267191 | 1 | 21:34 | Night | Friday | 2016 | 9
4182 | 2016-09-16 21:34 | 2016-09-18 10:00 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 26AE-22 (Sintong fdr #1) T/SO. Ctr: 158-159. Then closed Recl. 26AE-22, Ok. Then released the block. Patrolled the line & found nothing. Cause: Suspected by Ligthning. | 3267191 | 1 | 21:34 | Night | Friday | 2016 | 9
4183 | 2016-09-17 00:17 | 2016-09-17 00:17 | CENTRAL DURI SWITCH YARD | Rain and Lightning | Equipment Failure | 7001 | 00:17 115KV C.Duri SWY GCB #45 T/R 1x 115KV C.Duri SWY GCB #43 T/O. 115KV C.Duri SWY GCB #41 T/O. 115KV Rokan GCB #12 T/R 1X. (115KV C.Duri-Pematang line T/R & C.Duri Tx-3 Tripped) Respectively: So.Balam fdr #4 Load dropped 156A (250-94A). Nella fdr #1 Load dropped 226A (266-46A). Menggala fdr #1 Load dropped 115A (190-75A). Sintong fdr #1 Load dropped 18A (77-59A). Sintong fdr #2 Load dropped 151A (215-64A). Bekasap fdr #3 Load dropped 30A (150-120A). Pematang fdr #1 Load dropped 101A (150-49A). Pematang fdr #2 Load dropped 49A (50-1A). Rangau fdr #1 Load dropped 18A (26-8A). Rangau fdr #2 Load dropped 60A (70-10A). Petani fdr #1 Load dropped 131A (201-70A). Ketigul fdr #1 Load dropped 23A (113-90A). Ketigul fdr #2 Load dropped 32A (216-184A). To anticipate spill at Bangko-GS. 00:54 Manual opened Bangko VCB fdr #1. Then Closed at: 01:27. 01:14 Checked & found, Recl. 26AE-22 (Sintong fdr #1) T/SO. Blocked & closed Recl. 26AE-22, Ok. Then released the block 03:00 Checked & found, 115KV C.Duri TX-3 T/O. Opened Line Switch for isolating 115KV C.Duri TX-3. 03:47 Closed 115KV C.Duri GCB #41 & #43. 03:43 Transferred load CD fdr #11 to Darling fdr #6. 04:07 CGT #4 T/O. (Affected 13.8KV C.Duri Bus-4 & C.Duri fdr #7, 8, 9 no power) To anticipate Spill at CGS-4. 05:20 Manual opened C.Duri ACB fdr #16, then closed at: 09:31. (Requested by HO Dispacther). 05:45 Opened C.Duri ACB fdr #8 & C.Duri ACB fdr #9. Preparation to transfer load of CGS #4. (to C.Duri fdr #6 & C.Duri #16) 05:50 By passed Recl. 03-7-24. Normalized at: 15:18 06:00 Unplug Recl. 02-1-01. Normalized at: 09:45 07:00 Opened Recl. 03-05-27 (CD fdr #7). Closed at: 10:34 07:20 Opened Recl. 03-01-39 (CD fdr #7). Closed at: 10:40 07:20 Opened Recl. 04-02-22 (CD fdr #8). Closed at: 09:58 07:47 Opened Recl. 04-06-40 (CD fdr #8). Closed at: 10:21 07:39 Opened Recl. 04-01-02 (CD fdr #9). Closed at: 10:32 07:47 Opened Recl. 04-03-02 (CD fdr #9). Closed at: 10:36 07:32 115KV C.Duri OCB #33 T/O. 115KV C.Duri OCB #35 T/O. (115KV C.Duri TX-5 Tripped for CGT #5) 07:56 Closed LBS #03-07-03. (C.Duri fdr #7 energized from C.Duri fdr #5) (Also C.Duri Bus #3 & #4 energized from C.Duri ACB fdr #7) 08:00 Checked 115KV C.Duri TX-3, found normal. 08:08 Manual opened 115KV C.Duri GCB #41 & #43. 08:13 Closed 115KV Line Switch of C.Duri TX-3. 08:15 Closed 115KV C.Duri GCB #41. (115KV C.Duri TX-3 energized) Visual checked the Tx & found, normal. 08:20 Closed 115KV C.Duri GCB #43. 08:27 Opened C.Duri ACB fdr #7. (C.Duri Bus #3 & #4 de-energized) 08:28 Closed 13.8KV C.Duri ACB #34. (13.8KV C.Duri Bus #3 & #4 energized) 08:46 Closed 13.8KV C.Duri ACB fdr #7. (C.Duri fdr #7 parallel with C.Duri fdr #5) 08:55 Opened LBS #03-07-03. (C.Duri fdr #7 & C.Duri fdr #5 are separated) 09:15 Closed 13.8KV C.Duri ACB fdr #8. 09:17 Closed 13.8KV C.Duri ACB fdr #9. 09:31 Closed 13.8KV C.Duri ACB fdr #16. Cause: Under Investigation. Prod. loss Reported by EC: Duri Fiels (HO) = 5607 Bbls / 1226 Wells. Bangko North = 994 Bbls / 145 Wells. Bekasap North = 400 Bbls / 93 Wells. Grand Total = 7001 Bbls / 1464 Wells | 3267191 | 1 | 0:17 | Night | Saturday | 2016 | 9
4184 | 2016-09-17 07:55 | 2016-09-17 07:55 | MINAS POWER PLANT |  |  | - | 07:55 S/U MGT #7, then online the Unit at 08:10 |  | 1 | 7:55 | Morning | Saturday | 2016 | 9
4185 | 2016-09-17 08:00 | 2016-09-17 08:00 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified (Fuse) | 37 | 08:00 It was reported b/o fuse for Tx at Well Pudu #17. 14:55 Checked & found, @1 b/o 7.8SF fuse for 250Kva Tx at Well Pudu #17. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3267191 | 1 | 8:00 | Morning | Saturday | 2016 | 9
4186 | 2016-09-17 08:00 | 2016-09-17 08:00 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified (Fuse) | 210 | 08:00 It was reported b/o fuse for Tx at Well Pematang #57. 16:27 Checked & found, @1 b/o 14.0SF fuse for 500Kva Tx at Well Pematang #57. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3267191 | 1 | 8:00 | Morning | Saturday | 2016 | 9
4187 | 2016-09-17 09:30 | 2016-09-17 09:30 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Main breaker | 0 | 09:30 It was reported b/o fuse for Tx at DIF area #4. 10:30 Checked & found, @2, @3 b/o 100K fuses for 1000Kva Tx-C at DIF area #4. Perform TT and Megger test & found good reading. Replaced b/o fuse above with the same size but not energized due to spark on main breaker. Cause: Main breaker on MCC. | 3267191 | 1 | 9:30 | Morning | Saturday | 2016 | 9
4188 | 2016-09-17 10:33 | 2016-09-17 10:33 | 13.8KV BANGKO FEEDER #1 | Fair | Switchboard Problem | 0 | It was reported @2 b/o fuse for 150KVA Tx at Well BKO #20. Replaced b/o fuse above with the same size then energized the Tx. Cause: Switchboard problem. | 3267191 | 1 | 10:33 | Morning | Saturday | 2016 | 9
4189 | 2016-09-17 14:37 | 2016-09-17 14:37 | MINAS POWER PLANT | Fair |  | - | 14:37 S/U MGT #9, then online the unit at 14:55. 19:25 Off line MGT #9, then S/D the unit for S/B. |  | 1 | 14:37 | Afternoon | Saturday | 2016 | 9
4190 | 2016-09-17 15:15 | 2016-09-17 15:15 | 13.8KV NORTH DURI FEEDER #9 | Fair | Transformer Failure | 0 | 15:15 It was reported b/o fuse for Tx o/p #11-H3-20. Not checked yet. | 3267191 | 1 | 15:15 | Afternoon | Saturday | 2016 | 9
4191 | 2016-09-17 15:15 | 2016-09-19 16:00 | 13.8KV NORTH DURI FEEDER #9 | Fair | Transformer Failure | 0 | 16:00 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #11-H3-20. (N.Duri fdr #9) Performed TTR test and megger the TX and found, Low mega ohm reading TX. Cause: Tx Failure. (Low mega ohm reading TX) (The Tx is not replaced yet) | 3267191 | 1 | 15:15 | Afternoon | Saturday | 2016 | 9
4192 | 2016-09-17 15:15 | 2016-09-28 15:00 | 13.8KV NORTH DURI FEEDER #9 | Fair | Transformer Failure | 0 | Replaced 112.5Kva Tx failure with the same size & energized the Tx o/p #11-H3-20. Cause: Tx Failure. | 3267191 | 1 | 15:15 | Afternoon | Saturday | 2016 | 9
4193 | 2016-09-17 16:54 | 2016-09-17 16:54 | CENTRAL DURI POWER PLANT |  |  | - | 16:54 S/U CGT#4, then on line the Unit at 17:27. |  | 1 | 16:54 | Afternoon | Saturday | 2016 | 9
4194 | 2016-09-17 20:54 | 2016-09-17 20:54 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain and Lightning | Tree | 0 | 20:54 Duri Community fdr #2 Load dropped 40A (125-85A). 22:05 Checked & found, 4.16KV Recl. at IT Mini Subst. T/O. 22:10 Blocked & closed 4.16KV Recl. at IT Mini Subst.,Ok. Then released the block. Not patrolled yet. | 3267191 | 1 | 20:54 | Night | Saturday | 2016 | 9
4195 | 2016-09-17 20:54 | 2016-09-19 20:54 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain and Lightning | Tree | 0 | Checked & found, 4.16KV Recl. at IT Mini SS. T/R 2x Ctr: 70-72. Patrolled the line & found, High tree & touching to power line at near pole #NN. (Duri Garage shop) Cause: Tree. | 3267191 | 1 | 20:54 | Night | Saturday | 2016 | 9
4196 | 2016-09-17 21:51 | 2016-09-17 21:51 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 42 | 6D OCB fdr #1 T/R 1x. Not checked yet. | 3267192 | 1 | 21:51 | Night | Saturday | 2016 | 9
4197 | 2016-09-17 21:51 | 2016-09-18 11:51 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 42 | Checked & found, 6D OCB fdr #1 T/R 1x Ctr: 308-309 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:51 | Night | Saturday | 2016 | 9
4198 | 2016-09-17 21:51 | 2016-09-17 21:51 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 17 | 6D fdr #2 Load dropped 208A (242-34A). Not checked yet. | 3267192 | 1 | 21:51 | Night | Saturday | 2016 | 9
4199 | 2016-09-17 21:51 | 2016-09-18 11:51 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 17 | Checked & found, Recl. 6D-298 (6D fdr #2) T/R 1x Ctr: 43-44. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:51 | Night | Saturday | 2016 | 9
4200 | 2016-09-17 21:54 | 2016-09-17 21:54 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 50 | Minas ACB fdr #6 Load dropped 132A (184-52A). Not checked yet. | 3267192 | 1 | 21:54 | Night | Saturday | 2016 | 9
4201 | 2016-09-17 21:54 | 2016-09-19 17:15 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 50 | Checked & found, Recl. 7E-67A (MInas fdr #6) T/R 1x Ctr: 51-52 F/R: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:54 | Night | Saturday | 2016 | 9
4202 | 2016-09-17 22:43 | 2016-09-17 22:43 | CENTRAL DURI SWITCH YARD | Rain and Lightning | Equipment Failure | 0 | 22:43 115KV C. Duri GCB #41 T/O 115KV C. Duri GCB #43 T/O (115KV C. Duri TX-3 Tripped). Transferred load C. Duri fdr #9 to C. Duri fdr #6. 02:48 Opened C. Duri fdr #9. 02:49 Opened Recl. 02-1-01. 02:51 Closed LBS 04-07-01. 02:52 Closed Recl. 02-01-01. 03:32 CGT #4 Tripped. 03:51 Opened C. Duri ACB fdr #7. Opened C. Duri ACB fdr #8. Transferred load C. Duri fdr #7 to C. Duri fdr #5. 04:00 By passed Recl. 03-07-24. 04:01 Closed LBS 03-07-03. Energized CGS-4. 04:38 Opened Recl. 04-5-32. 04:46 Closed LBS 04-5-25. (CGS #4 energized from C. Duri fdr #9 (C. Duri fdr #6)). Transfer load CD fdr #8 to C. Duri fdr #4. 07:21 Closed LBS 03-01-02. (C. Duri fdr #5 & C. Duri fdr #6 parallel) 07:26 Opened Recl. 03-01-39 (Part load C. Duri fdr #5 transferred to C. Duri fdr #6). 07:43 Opened LBS 03-03-44. 07:58 Closed LBS 04-08-29. 08:03 Unplug Recl. 09-Q1-06. 08:06 Closed LBS 09-Q1-01. Cause: Under Investigation. | 3267191 | 1 | 22:43 | Night | Saturday | 2016 | 9
4203 | 2016-09-18 08:13 | 2016-09-18 08:13 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 52 | Ketigul VCB fdr #1 T/R 1x. Not checked yet. | 3267191 | 1 | 8:13 | Morning | Sunday | 2016 | 9
4204 | 2016-09-18 08:13 | 2016-09-19 08:13 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 52 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 211-212 R/F: 51@1. Patrolled the line & found, @1 broken Dead end Insulator o/p #29AM-28. Cause: Dead end Insulator. | 3267191 | 1 | 8:13 | Morning | Sunday | 2016 | 9
4205 | 2016-09-18 18:22 | 2016-09-18 18:22 | 13.8KV DURI FIELD FEEDER #4 | Fair | Lightning Arrester | 0 | D.Field ACB fdr #4 T/R 1x. Not checked yet. | 3267191 | 1 | 18:22 | Afternoon | Sunday | 2016 | 9
4206 | 2016-09-18 18:22 | 2016-09-19 08:30 | 13.8KV DURI FIELD FEEDER #4 | Fair | Lightning Arrester | 0 | Checked & found, D.Field ACB fdr #4 T/R 1x Ctr: 475-376 R/F: 51N. Patrolled the line & found, @1 broken L/A o/p #07-V5-03. Caused: Lightning Arrester. | 3267191 | 1 | 18:22 | Afternoon | Sunday | 2016 | 9
4207 | 2016-09-18 21:50 | 2016-09-18 21:50 | MINAS POWER PLANT |  |  | - | 21:50 S/U MGT #8, then on line the Unit at 22:04. |  | 1 | 21:50 | Night | Sunday | 2016 | 9
4208 | 2016-09-18 22:10 | 2016-09-18 22:10 | MINAS POWER PLANT |  |  | - | Off line MGT #11, then S/D the Unit for S/B. (Lube oil leak at 63QT) |  | 1 | 22:10 | Night | Sunday | 2016 | 9
4209 | 2016-09-19 06:18 | 2016-09-19 06:18 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Secondary Cable | 0 | 06:18 It was reported b/o fuse for Tx o/p #05-P5-14. 15:00 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #05-P5-14. Also found broken secondary cable. Replaced broken secondary cable & fuse with the same size, then energized the Tx. Cause: Secondary cable (broken). | 3267191 | 1 | 6:18 | Morning | Monday | 2016 | 9
4210 | 2016-09-19 09:00 | 2016-09-19 09:00 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | 09:00 It was reported b/o fuse for Tx o/p #03-02-17. 12:15 Checked & found, @3 b/o 3.1Sf fuse for 112.5Kva Tx o/p #03-02-17. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 3267191 | 1 | 9:00 | Morning | Monday | 2016 | 9
4211 | 2016-09-19 14:52 | 2016-09-19 14:52 | MINAS POWER PLANT |  |  | - | 14:52 S/U MGT #2, then on line the Unit at 15:27. (Foro Re-certification) 17:40 Off line MGT #2, then S/D the Unit for S/B. |  | 1 | 14:52 | Afternoon | Monday | 2016 | 9
4212 | 2016-09-20 10:00 | 2016-09-20 10:00 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 10:00 It was reported b/o fuse for Tx at WTP Minas. 10:30 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at WTP Minas. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 3267192 | 1 | 10:00 | Morning | Tuesday | 2016 | 9
4213 | 2016-09-21 17:13 | 2016-09-21 17:13 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Transformer Failure | 0 | 17:13 Duri Community fdr #3 Load dropped 25A (65-40A). 18:00 Checked & found, Bus Voltage TX #1 Duri Community was 14.4KV. Adjusted voltage to 13.9KV. Patrolled the line & found nothing. 18:55 Checked & found, Recl. 6F-07 (D.Community fdr #3) T/LO. Ctr: 1842-1844. Blocked & closed Recl. 6F-07 above, but tripped again. Patrolled the line & found, failure 3x100Kva Tx o/p #2DG-01. (for SMP Cendana) (found the Fuse Holder is still connected to FCO) Then Isolated the Tx, by open Fuse holder/fuse link. 19:23 Blocked & closed Recl. 6F-07, Ok. Then released the block. Cause: Transformer Failure. | 3267191 | 1 | 17:13 | Afternoon | Wednesday | 2016 | 9
4214 | 2016-09-22 06:17 | 2016-09-22 06:17 | 13.8KV S. BALAM GFPC | Fair | Unidentified | 0 | So.Balam GFPC T/R 1x. Ground fault alarm on So.Balam fdr #2. (No load dropped at any fdrs.) Not checked yet. | 3267191 | 1 | 6:17 | Morning | Thursday | 2016 | 9
4215 | 2016-09-22 06:17 | 2016-09-26 10:17 | 13.8KV S. BALAM GFPC | Fair | Unidentified | 0 | Checked & found, So.Balam GFPC T/R 4x Ctr: 227-231 R/F: 51N. Patrolled So.Balam fdr #2 line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 6:17 | Morning | Thursday | 2016 | 9
4216 | 2016-09-22 09:29 | 2016-09-22 09:29 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified (Fuse) | 20 | 09:29 It was reported b/o fuse for Tx o/p #10-K4-40. 14:58 Checked & found, @3 b/o 3.1SF fuse for 112.5KVA Tx o/p #10-K4-40. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3267191 | 1 | 9:29 | Morning | Thursday | 2016 | 9
4217 | 2016-09-22 13:10 | 2016-09-22 13:10 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 0 | 13:10 Manually Opened LBS #29BY-06. (LIBO fdr #2) For Replacing @2 broken Pin Insulator o/p #29BY-07. and also replacing Hot Line Clamp o/p #29BY-11. 14:18 Closed LBS #29BY-06. Cause: Plan Maintenance | 123 | 1 | 13:10 | Afternoon | Thursday | 2016 | 9
4218 | 2016-09-22 13:25 | 2016-09-22 13:25 | 13.8KV BEKASAP FEEDER #6 | Fair | Planned Maintenance | 9 | 13:25 Opened HLC on Take of Pole of Well Aman #3 & Aman #5. (Bekasap fdr #6) For replacing @1,@2,@3 broken L/As on Take of Pole Well Aman #3 & Aman #5. 15:00 Closed HLC on Take of Pole of Well Aman #3 & Aman #5, then S/U the wells. Cause: Plan Maintenance. | 123 | 1 | 13:25 | Afternoon | Thursday | 2016 | 9
4219 | 2016-09-22 21:34 | 2016-09-22 21:34 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | It was reported b/o fuse for Tx o/p #06-Q5-04B. (C.Duri fdr #14) Not checked yet. | 3267191 | 1 | 21:34 | Night | Thursday | 2016 | 9
4220 | 2016-09-22 21:34 | 2016-09-23 10:10 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 10:10 Checked & found, @2,@3 b/o 3.1SF fuses for for 112.5Kva Tx o/p #06-Q5-04B. Perform TTR and Megger test the Tx found good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (Monkey). | 3267191 | 1 | 21:34 | Night | Thursday | 2016 | 9
4221 | 2016-09-22 22:14 | 2016-09-22 22:14 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Animal | 0 | 22:14 It was reported b/o fuse for Tx o/p #05-N1-17. (NW-Test station A-5) 23:05 Checked & found, @2 b/o 3.1SF fuse for 112.5kva Tx o/p #05-N1-17. Replaced b/o fuse above with the same size then energized the TX. Cause: Animal. (Monkey) | 3267191 | 1 | 22:14 | Night | Thursday | 2016 | 9
4222 | 2016-09-23 07:52 | 2016-09-23 07:52 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 58 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3267191 | 1 | 7:52 | Morning | Friday | 2016 | 9
4223 | 2016-09-23 07:52 | 2016-09-26 11:15 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 58 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 382-383 R/F: Not appear. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 7:52 | Morning | Friday | 2016 | 9
4224 | 2016-09-23 15:50 | 2016-09-23 15:50 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #1 | Fair | Unidentified | 94 | MSU-2 VCB fdr #1 (So.Balam fdr #1 & fdr #2) T/R 1x. Not checked yet. | 3267191 | 1 | 15:50 | Afternoon | Friday | 2016 | 9
4225 | 2016-09-23 15:50 | 2016-09-24 16:38 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #1 | Fair | Unidentified | 94 | Checked & found, MSU-2 VCB fdr #1 T/R 1x Ctr: 239-240 R/F: 51N. Patrolled the line, but nothing found. Cause: Unidentified. | 3267191 | 1 | 15:50 | Afternoon | Friday | 2016 | 9
4226 | 2016-09-23 16:07 | 2016-09-23 16:07 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Planned Maintenance | 0 | 16:07 Manually Opened LBS #1F-273. (S/D power to Talang & Leuser Complexes) Due to modifications 3x100Kva Tx (Three phases) to 2x150Kva Tx (Single phase). 18:25 Closed LBS #1F-273. 20:00 Completed to replacing its Tx, then energized the Tx. Cause: Planned Maintenance. | 123 | 1 | 16:07 | Afternoon | Friday | 2016 | 9
4227 | 2016-09-23 19:20 | 2016-09-23 19:20 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Transformer Failure | 65 | 19:20 It was reported b/o fuse for Tx at Well Pudu #03. 21:55 Checked & found, @3 b/o 7.8SF fuse for 300KVA Tx at Well Pudu #03. Performed TTR & Megger test, found zero-megger reading. Cause: Transformer Failure. | 3267191 | 1 | 19:20 | Night | Friday | 2016 | 9
4228 | 2016-09-23 19:20 | 2016-09-25 11:55 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Transformer Failure | 65 | 11:55 Replaced Transformer failure 300Kva with the same size & energized the Tx. Cause: Tx Failure. (Low megger Reading) | 3267191 | 1 | 19:20 | Night | Friday | 2016 | 9
4229 | 2016-09-23 20:51 | 2016-09-23 20:51 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 3 | Ketigul fdr #2 Load dropped 63A (222-159A). Not checked yet. | 3267191 | 1 | 20:51 | Night | Friday | 2016 | 9
4230 | 2016-09-23 20:51 | 2016-09-27 15:20 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 3 | Checked & found, Ketigul VCB fdr #2 T/R 4x Ctr: 112-116 R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator on TP of Well Sikladi #23. Cause: Lightning. | 3267191 | 1 | 20:51 | Night | Friday | 2016 | 9
4231 | 2016-09-23 21:44 | 2016-09-23 21:44 | 115KV KOTABATAK JUNCTION-KOTABATAK LINE | Rain and Lightning | Lightning | 976 | 115KV KBJ GCB #41 T/R 1x. 115KV KBJ GCB #43 T/R 1x. 115KV NKB GCB #1 T/R 1x. (115KV line KBJ-NKB T/R) NKB SS, CKB SS, OKB SS, Petapahan SS & Suram SS were no power during this outage. Not checked yet. Prod Loss: Kotabatak Area : 438 bbls / 270 wells. Petapahan Suram : 569 bbls / 107 wells. ---------------------------------------------------- + Total : 1007 bbls / 377 wells. | 3267192 | 1 | 21:44 | Night | Friday | 2016 | 9
4232 | 2016-09-23 21:44 | 2016-09-25 07:38 | 115KV KOTABATAK JUNCTION-KOTABATAK LINE | Rain and Lightning | Lightning | 976 | Checked & found: 115KV KBJ GCB #41 T/R 1x Ctr: 210-211 115KV KBJ GCB #43 T/R 2x Ctr: 418-420 R/F: 21@1,@2,@3. (115KV KBJ - NKBS line T/R 1x) Patrolled 115KV KBJ - NKBS line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:44 | Night | Friday | 2016 | 9
4233 | 2016-09-23 21:44 | 2016-09-23 21:44 | 13.8KV NORTH DURI FEEDER #5 | Rain and Lightning | Lightning | 0 | No.Duri fdr #5 Load dropped 28A (49-21A). No.Duri GFPC-TX #12. (did not operate) Not checked yet. | 3267191 | 1 | 21:44 | Night | Friday | 2016 | 9
4234 | 2016-09-23 21:44 | 2016-09-27 16:00 | 13.8KV NORTH DURI FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 12-E11-05 (No.Duri fdr #5) T/R 1x Ctr: 103-104. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267191 | 1 | 21:44 | Night | Friday | 2016 | 9
4235 | 2016-09-23 21:44 | 2016-09-23 21:44 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 0 | 21:44 CKBS VCB fdr #1 T/R 1x. Not checked yet. 24-SEP-16 It was reported that no power at downstream of Recl. 38CX-25. 01:51 Checked & found, Recl. 38CX-25 (CKBS fdr #1) T/SO. Ctr: 92-93. Blocked & closed Recl. 38CX-25, Ok. Then released the block. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:44 | Night | Friday | 2016 | 9
4236 | 2016-09-23 21:44 | 2016-09-26 04:49 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked and found CKBS VCB fdr #1 T/R 1x Ctr: 216-217 R/F: 51@2. Patrolled the line & found, @2 broken L/A on TP of Well KB #357. Cause: Lightning. | 3267192 | 1 | 21:44 | Night | Friday | 2016 | 9
4237 | 2016-09-23 21:44 | 2016-09-23 21:44 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain and Lightning | Lightning | 0 | NKBS VCB fdr #3 T/R 1x. NKBS GFPC T/R 1x. Not checked yet. | 3267192 | 1 | 21:44 | Night | Friday | 2016 | 9
4238 | 2016-09-23 21:44 | 2016-09-25 07:44 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found, NKBS VCB fdr #3 T/R 1x Ctr: 278-279 R/F: 51N. Patrolled the line & found, @1 broken L/A on TP of Well KB #08. Cause: Lightning. | 3267192 | 1 | 21:44 | Night | Friday | 2016 | 9
4239 | 2016-09-23 21:48 | 2016-09-23 21:48 | 13.8KV 8C FEEDER #5 | Rain and Lightning | Lightning | 37 | 8C VCB fdr #5 T/R 1x. 8C fdr #4 Load dropped 241A (292-51A). Not checked yet. | 3267192 | 1 | 21:48 | Night | Friday | 2016 | 9
4240 | 2016-09-23 21:48 | 2016-09-25 16:00 | 13.8KV 8C FEEDER #5 | Rain and Lightning | Lightning | 37 | Checked & found, 8C VCB fdr #5 T/R 1x Ctr: 98-99 R/F: 50N. Patrolled the line & found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:48 | Night | Friday | 2016 | 9
4241 | 2016-09-23 21:48 | 2016-09-23 21:48 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 105 | 8C fdr #3 Load dropped 115A (198-83A). Not checked yet. | 3267192 | 1 | 21:48 | Night | Friday | 2016 | 9
4242 | 2016-09-23 21:48 | 2016-09-25 16:00 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 105 | Checked & found, Recl. 8D-18A (8C fdr #3) T/R 1x Ctr: 33-34. Patrolled the line & found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:48 | Night | Friday | 2016 | 9
4243 | 2016-09-23 21:54 | 2016-09-23 21:54 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 25 | 4B OCB fdr #1 T/R 1x. 4B fdr #2 load dropped 30A (108-78A). 4B fdr #3 load dropped 65A (67-2A). T/O WIP at GS-6. Not checked yet. | 3267192 | 1 | 21:54 | Night | Friday | 2016 | 9
4244 | 2016-09-23 21:54 | 2016-09-24 01:30 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 25 | 01:30 4B fdr #1 still dropped 58A (269-211A). 17:00 Checked & found, Recl. 3A-28 (4B fdr #1) T/SO. Ctr: 17-18. Blocked & closed Recl. 3A-28, Ok. Then released the block. Cause: Recloser Control Problem. | 3267192 | 1 | 21:54 | Night | Friday | 2016 | 9
4245 | 2016-09-23 21:54 | 2016-09-28 06:53 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 25 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 289-290 R/F: 51@1,@2. Patrolled the line & found, @1,@2 broken Dead end Insulators o/p #NN. Cause: Lightning. | 3267192 | 1 | 21:54 | Night | Friday | 2016 | 9
4246 | 2016-09-23 21:57 | 2016-09-23 21:57 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 22 | 6D fdr #1 load dropped 75A (191-116A). Not checked yet. | 3267192 | 1 | 21:57 | Night | Friday | 2016 | 9
4247 | 2016-09-23 21:57 | 2016-09-25 16:00 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 22 | Checked & found, Recl. 5C-42 (6D fdr #1) T/R 1x Ctr: 21-22. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:57 | Night | Friday | 2016 | 9
4248 | 2016-09-23 21:57 | 2016-09-23 21:57 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 30 | 6D fdr #2 Load dropped 157A (229-71A). Not checked yet. | 3267192 | 1 | 21:57 | Night | Friday | 2016 | 9
4249 | 2016-09-23 21:57 | 2016-09-25 16:00 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 30 | Checked & found, Recl. 6D-298 (6D fdr #2) T/R 1x Ctr: 44-46. Patrolled the line & found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:57 | Night | Friday | 2016 | 9
4250 | 2016-09-23 21:57 | 2016-09-23 21:57 | 13.8KV 6D FEEDER #3 | Rain and Lightning | Lightning | 0 | 6D fdr #3 Load dropped 55A (88-32A). Not checked yet. | 3267192 | 1 | 21:57 | Night | Friday | 2016 | 9
4251 | 2016-09-23 21:57 | 2016-09-28 06:57 | 13.8KV 6D FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 6D-298 (6D fdr #3) T/R 2x Ctr: 44-46. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 21:57 | Night | Friday | 2016 | 9
4252 | 2016-09-23 22:09 | 2016-09-23 22:09 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 61 | Minas ACB fdr #1 T/R 1x Ctr: 53-54 R/F: 51N. Not patrolled yet. | 3267192 | 1 | 22:09 | Night | Friday | 2016 | 9
4253 | 2016-09-23 22:09 | 2016-09-27 22:45 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 61 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267192 | 1 | 22:09 | Night | Friday | 2016 | 9
4254 | 2016-09-23 22:22 | 2016-09-23 22:22 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 198 | 8D fdr #11 Load dropped 135A (226-91A). Not checked yet. | 3267192 | 1 | 22:22 | Night | Friday | 2016 | 9
4255 | 2016-09-23 22:22 | 2016-09-25 16:00 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 198 | Checked & found, Recl. 9E-02 (8D fdr #11) T/R 1x Ctr: 1058-1059. Patrolled the line & found nothing. Cause: Suspected by Lighting. | 3267192 | 1 | 22:22 | Night | Friday | 2016 | 9
4256 | 2016-09-23 22:48 | 2016-09-23 22:48 | MINAS POWER PLANT | Rain and Lightning | Under investigation | 0 | MGT #10 T/O. By Alarm: High Vibration Trip. (No load shedding) Cause: Under Investigation. | 3267192 | 1 | 22:48 | Night | Friday | 2016 | 9
4257 | 2016-09-24 10:25 | 2016-09-24 10:25 | 13.8KV MINAS FEEDER #2 | Fair | Planned Maintenance | 8 | 10:25 Blocked Recl. 7D-21 to open HLC o/p #7D-204. (toward Wells #7D-41A & 7D-32) (For repairing hotspot at @3 HLC o/p #7D-204). 15:22 Completed the job & normalized the Recl. (2 well were offs during this job) Cause: Planned Maintenance. | 123 | 1 | 10:25 | Morning | Saturday | 2016 | 9
4258 | 2016-09-24 12:46 | 2016-09-24 12:46 | MINAS POWER PLANT |  |  | - | 12:46 S/U MGT #4, then online the Unit at 13:03. |  | 1 | 12:46 | Afternoon | Saturday | 2016 | 9
4259 | 2016-09-24 20:21 | 2016-09-24 20:21 | 13.8KV NORTH DURI FEEDER #10 | Rain and Lightning | Lightning | 7 | 20:21 No.Duri fdr #10 Load dropped 19A (148-129A). No.Duri GFPC-TX #13 T/R 1x. (Ground fault alarm on No.Duri fdr #10) 21:00 It was reported no power at (1 road) near pole #13-G7.2-07. 23:14 Checked & found, Recl. 13-G7.1-10 (No.Duri fdr #10) T/O. (In block position) Ctr: 02-03. 23:19 Closed Recl. 13-G7.1-10, Ok. Then released the block. Not patrolled yet. | 3267191 | 1 | 20:21 | Night | Saturday | 2016 | 9
4260 | 2016-09-24 20:21 | 2016-09-25 17:00 | 13.8KV NORTH DURI FEEDER #10 | Rain and Lightning | Lightning | 7 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267191 | 1 | 20:21 | Night | Saturday | 2016 | 9
4261 | 2016-09-24 21:00 | 2016-09-24 21:00 | 13.8KV NORTH DURI FEEDER #9 | Fair | Transformer Failure | 3 | 21:00 It was reported bo fuse for Tx o/p #10-J4-26. Not checked yet. | 3267191 | 1 | 21:00 | Night | Saturday | 2016 | 9
4262 | 2016-09-24 21:00 | 2016-09-25 11:30 | 13.8KV NORTH DURI FEEDER #9 | Fair | Transformer Failure | 3 | 11:30 Checked & found, @1,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #10-J4-26. Performed TTR test and Megger the TX and found, TX failure. Cause:Tx Failure. (Low megger reading) (The TX is not replaced yet) | 3267191 | 1 | 21:00 | Night | Saturday | 2016 | 9
4263 | 2016-09-24 21:00 | 2016-09-29 16:30 | 13.8KV NORTH DURI FEEDER #9 | Fair | Transformer Failure | 3 | Replaced 112.5Kva Tx failure with the same size & energized the Tx o/p #10-J4-26. Cause: Tx Failure. | 3267191 | 1 | 21:00 | Night | Saturday | 2016 | 9
4264 | 2016-09-24 21:02 | 2016-09-24 21:02 | MINAS POWER PLANT |  |  | - | 21:02 S/U MGT #1, then online the Unit at 21:12. 21:25 Opened Minas ACB #16. (Tie Breaker) 21:27 Closed Minas ACB #8 (Tie Breaker) |  | 1 | 21:02 | Night | Saturday | 2016 | 9
4265 | 2016-09-24 22:59 | 2016-09-24 22:59 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 21 | 4B OCB fdr #1 T/R 1x. 4B fdr #2 Load dropped 37A (108-71A). 4B fdr #3 Load dropped 60A (63-3A). Not checked yet. | 3267192 | 1 | 22:59 | Night | Saturday | 2016 | 9
4266 | 2016-09-24 22:59 | 2016-09-27 23:00 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 21 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 289-290 R/F: 51@1,@2. Patrolled the line & found, @1,@2 broken Dead end Insulators o/p #NN. Cause: Lightning. | 3267192 | 1 | 22:59 | Night | Saturday | 2016 | 9
4267 | 2016-09-25 00:18 | 2016-09-25 00:18 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Static Wire | 137 | 00:18 5B Substation RTU failed & back to online at 00:19. 5B OCB fdr #3 T/LO. 5B fdr #1 load dropped 72A (92-20A). 5B fdr #2 load dropped 154A (169-15A). 5B fdr #6 load dropped 136A (191-55A). T/O WIP at GS-4. 01:26 Checked & found, 5B OCB fdr #3 T/SO. Ctr: 361-364 R/F: 51@1,@2. 01:34 Blocked & closed 5B OCB fdr #3, but tripped again. 02:45 Patrolled the line & found, broken Static wire & hit to power line o/p #NN. (4 Spans before Recl. 4C-65A) Transferred part load of 5B fdr #3 to 4D fdr #5. 03:00 Opened Recl. 4C-65A & its visual openings. 03:53 Closed LBS #4D-160. 06:29 Blocked & closed 5B OCB fdr #3, Ok. Then released the block. (After isolating broken static wire above) Cause: Broken Static Wire. | 3267192 | 1 | 0:18 | Night | Sunday | 2016 | 9
4268 | 2016-09-25 14:25 | 2016-09-25 14:25 | MINAS POWER PLANT |  |  | - | 14:24 S/U MGT #11, then on line the Unit at 14:46. |  | 1 | 14:25 | Afternoon | Sunday | 2016 | 9
4269 | 2016-09-25 15:30 | 2016-09-25 15:30 | 13.8KV 5B FEEDER #3 | Fair | Unidentified (Fuse) | 1 | 15:30 It was reported b/o fuse for Tx at Well #4D-52N. 16:30 Checked & found @3 b/o 7.8SF fuse for 300Kva Tx at Well #4D-52N. Replaced b/o fuse above with sama size, then energized the Tx. Cause: Unidentified (Fuse). | 3267192 | 1 | 15:30 | Afternoon | Sunday | 2016 | 9
4270 | 2016-09-25 16:16 | 2016-09-25 16:16 | MINAS POWER PLANT |  |  | - | 16:16 Off line MGT #9, then S/D the Unit for S/B at 16:17. (Prior to replacing F/N Set) |  | 1 | 16:16 | Afternoon | Sunday | 2016 | 9
4271 | 2016-09-26 09:13 | 2016-09-26 09:13 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 239 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3267191 | 1 | 9:13 | Morning | Monday | 2016 | 9
4272 | 2016-09-26 09:13 | 2016-09-27 15:15 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 239 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 283-284 R/F: Not appear. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 9:13 | Morning | Monday | 2016 | 9
4273 | 2016-09-26 15:44 | 2016-09-26 15:44 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 4 | 15:44 It was reported b/o fuse for Tx at Well Kulim #79. (C.Duri fdr #1) 16:54 Checked & found, @2 b/o 1.0SF fuse for 45Kva Tx at Well Kulim #79. Perform TTR and Megger found, good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (Fuse). | 3267191 | 1 | 15:44 | Afternoon | Monday | 2016 | 9
4274 | 2016-09-26 19:28 | 2016-09-26 19:28 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Duri field VCB fdr #4 T/R 1x. Not checked yet. | 3267191 | 1 | 19:28 | Night | Monday | 2016 | 9
4275 | 2016-09-26 19:28 | 2016-09-29 19:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Duri Field ACB fdr #4 T/R 3x Ctr: 476-479 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 19:28 | Night | Monday | 2016 | 9
4276 | 2016-09-27 06:49 | 2016-09-27 06:49 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Others | - | 05:02 NKBS VCB fdr #5 Load dropped 190A (229-39A). (Pump Off) 06:49 KB-GS Requested to M/O CKBS VCB fdr #6. (to anticipate spill at KB-GS) (Due to WIP area 3 Problem). 07:29 Manual Closed CKBS VCB fdr #6. 09:58 NKBS VCB fdr #5 Load dropped again 190A (229-39A) (Pump Off). 11:38 NKBS VCB fdr #5 Load dropped again 190A (229-39A) (Pump Off). 12:17 KB-GS Requested to M/O CKBS VCB fdr #6 again. (Due to WIP area 3 Problem). 14:35 Manual Closed CKBS VCB fdr #6. 15:31 NKBS VCB fdr #5 Load dropped again 190A (229-39A) (Pump Off). 19:59 KB-GS Requested to M/O CKBS VCB fdr #6 again. (Due to WIP area 3 Problem). 22:10 Manual Closed CKBS VCB fdr #6. Cause: Other. (WIP / Pump Trouble). Production Loss Reported by EC: 72 Bbls / 63 Well. (Its not charged to PGT) |  | 1 | 6:49 | Morning | Tuesday | 2016 | 9
4277 | 2016-09-27 17:22 | 2016-09-27 17:22 | 13.8KV LIBO FEEDER #1 | Fair | Animal | 3 | 17:22 Libo OCB fdr #1 T/R 1x. 23:04 Libo OCB fdr #1 T/R 1x again. Not checked yet. | 3267191 | 1 | 17:22 | Afternoon | Tuesday | 2016 | 9
4278 | 2016-09-27 17:22 | 2016-09-28 14:10 | 13.8KV LIBO FEEDER #1 | Fair | Animal | 3 | Checked & found, Libo OCB fdr #1 T/R 2x Ctr: 370-372 R/F: 51N. Patrolled the line & found, a Dead Monkey under TP of Libo-GS. Cause: Animal. (Monkey) | 3267191 | 1 | 17:22 | Afternoon | Tuesday | 2016 | 9
4279 | 2016-09-27 17:33 | 2016-09-27 17:33 | MINAS POWER PLANT |  |  | - | 17:33 S/U MGT #9, then on line the Unit at 17:49. |  | 1 | 17:33 | Afternoon | Tuesday | 2016 | 9
4280 | 2016-09-28 05:48 | 2016-09-28 05:48 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Duri Field VCB fdr #1 T/R 1x. Not checked yet. | 3267191 | 1 | 5:48 | Morning | Wednesday | 2016 | 9
4281 | 2016-09-28 05:48 | 2016-09-29 19:10 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Duri Field ACB fdr #1 T/R 1x Ctr: 638-639 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 5:48 | Morning | Wednesday | 2016 | 9
4282 | 2016-09-28 15:40 | 2016-09-28 15:40 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Duri Community ACB fdr #3 T/R 1x. Not checked yet. | 3267191 | 1 | 15:40 | Afternoon | Wednesday | 2016 | 9
4283 | 2016-09-28 15:40 | 2016-09-29 16:00 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #3 T/R 1x Ctr: 55-56 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 15:40 | Afternoon | Wednesday | 2016 | 9
4284 | 2016-09-28 18:08 | 2016-09-28 18:08 | MINAS POWER PLANT |  |  | - | Off line MGT#9, then S/D the Unit for S/B. (Prior to replacing Fuel Nozzle set) |  | 1 | 18:08 | Afternoon | Wednesday | 2016 | 9
4285 | 2016-09-28 18:18 | 2016-09-28 18:18 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Cloudy and Lightning | Lightning | 140 | MSU-2 VCB fdr #1 T/R 1x. MSU-2 fdr #2 Load dropped 102A (250-148A). Not checked yet. | 3267191 | 1 | 18:18 | Afternoon | Wednesday | 2016 | 9
4286 | 2016-09-28 18:18 | 2016-01-10 07:10 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Cloudy and Lightning | Lightning | 140 | Checked & found, MSU-2 VCB fdr #1 T/R 1x Ctr: 240-241 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3267191 | 1 | 18:18 | Afternoon | Wednesday | 2016 | 9
4287 | 2016-09-29 07:48 | 2016-09-29 07:48 | 13.8KV SINTONG FEEDER #1 | Fair | Lightning Arrester | 0 | Sintong fdr #1 Load dropped 13A (76-63A). Sintong GFPC T/R 1x. Not checked yet. | 3267191 | 1 | 7:48 | Morning | Thursday | 2016 | 9
4288 | 2016-09-29 07:48 | 2016-09-30 17:10 | 13.8KV SINTONG FEEDER #1 | Fair | Lightning Arrester | 0 | Checked & found, Recl. 26AE-22 (Sintong fdr #1) T/R 1x Ctr: 351-352. Patrolled the line & found, @3 broken L/A on TP of Well Kerang #13. Cause: Lightning Arrester. | 3267191 | 1 | 7:48 | Morning | Thursday | 2016 | 9
4289 | 2016-09-29 10:17 | 2016-09-29 10:17 | MINAS POWER PLANT |  |  | - | 10:17 S/U MGT #2, then online the Unit at 10:39. |  | 1 | 10:17 | Morning | Thursday | 2016 | 9
4290 | 2016-09-30 06:13 | 2016-09-30 06:13 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 0 | Rangau fdr #2 Load dropped 77A (83-6A). Not checked yet. | 3267191 | 1 | 6:13 | Morning | Friday | 2016 | 9
4291 | 2016-09-30 06:13 | 2016-02-10 06:13 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 0 | Checked & found Recl. 23DB-01 (Rangau fdr #2) T/R 1x Ctr: 173-174. Patrolled the line, but found nothing. Cause: Unidentified. | 3267191 | 1 | 6:13 | Morning | Friday | 2016 | 9
4292 | 2016-09-30 14:13 | 2016-09-30 14:13 | MINAS POWER PLANT |  |  | - | 14:13 S/U MGT #9, then on line the Unit at 14:32. |  | 1 | 14:13 | Afternoon | Friday | 2016 | 9
4293 | 2016-09-30 15:46 | 2016-09-30 15:46 | MINAS POWER PLANT |  |  | - | Off line MGT #11, then S/D the Unit for Maintenance. |  | 1 | 15:46 | Afternoon | Friday | 2016 | 9
4294 | 2016-01-10 17:50 | 2016-01-10 17:50 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | 17:50 It was reported b/o fuse for Tx o/p #NN. (at Talang Complex) (No power at Talang house #46,47,48,49 and #50) 18:59 Checked & found, @1 b/o 1.0SF fuse for 25Kva Tx o/p #NN. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Squirrel) | 3278528 | 1 | 17:50 | Afternoon | Sunday | 2016 | 1
4295 | 2016-02-10 08:42 | 2016-02-10 08:42 | CENTRAL DURI POWER PLANT |  |  | - | 08:42 S/U CGT #5, then on line the Unit at 10:24. (Running on Test) 17:35 CGT #5, Automatic Open generator Breaker. 17:40 Re- Closed Generator Breaker. |  | 1 | 8:42 | Morning | Wednesday | 2016 | 2
4296 | 2016-02-10 09:24 | 2016-02-10 09:24 | MINAS POWER PLANT |  |  | - | 09:24 S/U MGT #11, then on line the Unit at 09:49. |  | 1 | 9:24 | Morning | Wednesday | 2016 | 2
4297 | 2016-02-10 10:42 | 2016-02-10 10:42 | MINAS POWER PLANT |  |  | - | Off line MGT #2, then S/D the Unit for S/B. |  | 1 | 10:42 | Morning | Wednesday | 2016 | 2
4298 | 2016-02-10 11:21 | 2016-02-10 11:21 | MINAS POWER PLANT |  |  | - | Off line MGT #1, then S/D the Unit for S/B. |  | 1 | 11:21 | Morning | Wednesday | 2016 | 2
4299 | 2016-02-10 14:35 | 2016-02-10 14:35 | MINAS POWER PLANT |  |  | - | Off line MGT #4, then S/D the unit for S/B. |  | 1 | 14:35 | Afternoon | Wednesday | 2016 | 2
4300 | 2016-02-10 18:51 | 2016-02-10 18:51 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 182 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3278431 | 1 | 18:51 | Afternoon | Wednesday | 2016 | 2
4301 | 2016-02-10 18:51 | 2016-03-10 16:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 182 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 216-217 R/F: 51N. Patrolled the & found, a Dead Monkey & @2 Flashed over FCO on TP of Well Pager #44. Cause: Animal. (Monkey) | 3278431 | 1 | 18:51 | Afternoon | Wednesday | 2016 | 2
4302 | 2016-02-10 20:30 | 2016-02-10 20:30 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #1 | Fair | Animal | 27 | 20:30 It was reported b/o fuse for Tx at Well So.Balam #132. (So.Balam fdr #1) 21:38 Checked & found,@2,@3 b/o 3.5SF fuses for 300Kva Tx at Well So.Balam #132. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3278449 | 1 | 20:30 | Night | Wednesday | 2016 | 2
4303 | 2016-03-10 06:44 | 2016-03-10 06:44 | 44KV MINAS - RUMBAI LINE | Fair | Animal | 0 | Minas 13.8KV ACB #21 (44KV Minas-Rumbai line) T/R 1x. Not checked yet. | 3278454 | 1 | 6:44 | Morning | Thursday | 2016 | 3
4304 | 2016-03-10 06:44 | 2016-04-10 08:12 | 44KV MINAS - RUMBAI LINE | Fair | Animal | 0 | Checked & found, Minas ACB #21 (44KV line to Rumbai) T/R 2x Ctr: 72-74 R/F: 51G. Patrolled the line & found, @2 broken Dead end Insulator o/p #MR-57. Cause: Animal. (Monkey) | 3278454 | 1 | 6:44 | Morning | Thursday | 2016 | 3
4305 | 2016-03-10 10:34 | 2016-03-10 10:34 | 13.8KV BANGKO FEEDER #1 | Fair | Unidentified | 7 | Bangko fdr #1 Load dropped 22A (216-194A). Not checked yet. | 3278510 | 1 | 10:34 | Morning | Thursday | 2016 | 3
4306 | 2016-03-10 10:34 | 2016-03-10 10:34 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 15 | Bangko fdr #4 Load dropped 148A (245-97A). Not checked yet. | 3278513 | 1 | 10:34 | Morning | Thursday | 2016 | 3
4307 | 2016-03-10 10:34 | 2016-03-10 10:34 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Sintong fdr #2 Load dropped 27A (214-187A). Not checked yet. | 3278514 | 1 | 10:34 | Morning | Thursday | 2016 | 3
4308 | 2016-03-10 11:15 | 2016-03-10 11:15 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 11:15 It was reported b/o fuse for Tx o/p #07-T1-08. (Duri Field #2) 13:40 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T1-08. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3279355 | 1 | 11:15 | Morning | Thursday | 2016 | 3
4309 | 2016-03-10 12:26 | 2016-03-10 12:26 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified (Fuse) | 7 | 12:26 It was reported b/o fuse for Tx at Well Meso #10. (Menggala fdr #1) 15:00 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Meso #10. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3278520 | 1 | 12:26 | Afternoon | Thursday | 2016 | 3
4310 | 2016-03-10 13:46 | 2016-03-10 13:46 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Animal | 275 | 13:46 C.Duri fdr #6 Load dropped 160A (202-42A). 14:25 Checked & found, Recl. 02-01-01 (C.Duri fdr #6) T/LO. Ctr: 204-207. Patrolled the line & found, a dead Monkey under Recl. 03-02-02 (C.Duri fdr #6). 14:57 Manually Closed Recl. 02-01-01, Ok. Repatrolled the line & found, broken FCO for Cap. Bank o/p #04-05-11A. (Then Isolated its Capacitor Bank) Cause: Animal. (Monkey) | 3278523 | 1 | 13:46 | Afternoon | Thursday | 2016 | 3
4311 | 2016-03-10 21:14 | 2016-03-10 21:14 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Duri Community ACB fdr #1 T/R 1x. Not checked yet. | 3278526 | 1 | 21:14 | Night | Thursday | 2016 | 3
4312 | 2016-03-10 21:14 | 2016-08-10 16:50 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 89-90 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3278526 | 1 | 21:14 | Night | Thursday | 2016 | 3
4313 | 2016-04-10 00:29 | 2016-04-10 00:29 | 115KV DURI - PUNGUT LINE | Fair | Unidentified | 0 | 00:29 115Kv DRB OCB #21 T/O. 115Kv DRB OCB #29 T/O. 115Kv Pungut OCB #21 T/O. (115Kv DRB - Pungut line T/O) 00:47 Manually close 115Kv DRB OCB #21. Manually close 115Kv Pungut OCB #21. (115Kv DRB-Pungut line energized) 115Kv DRB OCB #29 is still in open position. (115Kv DRB - Darling T/O, due to broken L/A at DRB) (Counter, R/F are not checked & the line is not patrolled yet) | 3278497 | 1 | 0:29 | Night | Sunday | 2016 | 4
4314 | 2016-04-10 00:29 | 2016-06-10 17:30 | 115KV DURI - PUNGUT LINE | Fair | Unidentified | 0 | Checked & found, 115KV Pungut OCB #21 T/LO. Ctr: 624-625 R/F: 21-G(Z-1 & Z-2) & 87L-@2 . Patrolled the line, but found nothing. Cause: Unidentified. | 3278497 | 1 | 0:29 | Night | Sunday | 2016 | 4
4315 | 2016-04-10 00:29 | 2016-04-10 00:29 | 115KV DURI - DARLING SUBST LINE | Fair | Lightning Arrester | 419 | 00:29 115Kv DRB OCB #29 T/O. 115Kv DRB OCB #31 T/O. 115Kv Darling GCB #1 T/O. 115Kv Darling GCB #2 T/O. (115Kv DRB - Darling line T/O) Respectively load dropped: - Nella fdr #1 Load dropped 208A (293-85A). Prod loss : 144 Bbls / 82 wells - Bangko fdr #1 Load dropped 30A (216-186A). Prod loss : 167Bbls / 85 wells - Bangko fdr #4 Load dropped 108A (248-140A). Prod loss : Bbls / wells - Menggala fdr #1 Load dropped 24A (178-154A). Prod loss : 11 Bbls / 2 wells - Sintong fdr #1 Load dropped 21A (78-57A). Prod loss : Bbls / wells - Sintong fdr #2 Load dropped 42A (214-172A). Prod loss : Bbls / wells - So Bekasap fdr #1 Load dropped 34A (179-145A). Total Prod loss Bekasap. - Bekasap fdr #2 Load dropped 20A (131-111A). : 197 Bbls / 12 wells. - Bekasap fdr #3 Load dropped 41A (149-108A). - Bekasap fdr #2 Load dropped 17A (72-55A). - Petani fdr#1 Load dropped 72A (193-121A). Prod loss : 0 Bbls / wells - Petani fdr#2 Load dropped 7A (44-37A). Prod loss : 0 Bbls / wells - Punggut fdr#2 load dropped 12A (81-69A). Prod loss : 0 Bbls / wells - Libo fdr#1 Load dropped 20A (88-68A). Prod loss : 0 Bbls / wells - N.Duri fdr#2 Load dropped 81A (139-58A). Prod loss : 0 Bbls / wells - D.Field fdr#1 Load dropped 35A (214-179A). Prod loss : 0 Bbls / wells - D.Field fdr#2 Load dropped 17A (148-131A). Prod loss : 0 Bbls / wells - Darling fdr#4 Load dropped 35A (125-90A). Prod loss : 0 Bbls / wells - Darling fdr#7 Load dropped 30A (60-30A). Prod loss : 0 Bbls / wells ------------------------------------ Total Production loss : 519 Bbls / 181 wells. 02:02 Checked & found: -115Kv DRB OCB #29 T/O Ctr: 201-203. -115Kv DRB OCB #31 T/O Ctr: 99-100. -115Kv Darling GCB #1 T/O Ctr: 72-74. R/F: 21@2 & 67N. -115Kv Darling GCB #2 T/O Ctr: 174-177. and Manually Closed at 00:41 but failed. 03:25 Patrolled the line & found, @2 broken 115KV L/A at DRB. Cause: Broken Lightning Arrester. | 3279354 | 1 | 0:29 | Night | Sunday | 2016 | 4
4316 | 2016-04-10 07:30 | 2016-04-10 07:30 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | C.Duri fdr #6 Load dropped 46A (202-156A). Not checked yet. | 3278899 | 1 | 7:30 | Morning | Sunday | 2016 | 4
4317 | 2016-04-10 07:30 | 15/10/2016 07:24 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | Checked & found, Recl. 01-03-01 (C.Duri fdr #6) T/R 2x Crt: 203-205. Patrolled the line, but nothing found. Cause: Unidentified. | 3278899 | 1 | 7:30 | Morning | Sunday | 2016 | 4
4318 | 2016-04-10 07:33 | 2016-04-10 07:33 | MINAS POWER PLANT |  |  | - | 07:33 S/U MGT #1, then Online at. 07:45. Open Tie Breaker ACB #25. (for servicing) 14:18 Re-Offline MGT #1, then S/D the Unit for Standby. (After closing Tie Breaker ACB #25) |  | 1 | 7:33 | Morning | Sunday | 2016 | 4
4319 | 2016-04-10 16:30 | 2016-04-10 16:30 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 16:30 It was reported b/o fuse for Tx o/p #10-J8-15B. (N.Duri fdr #2) 17:30 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx o/p #10-J8-15B. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3278900 | 1 | 16:30 | Afternoon | Sunday | 2016 | 4
4320 | 2016-04-10 17:14 | 2016-04-10 17:14 | 13.8KV RANGAU FEEDER #2 | Fair | Dead End Insulator | 0 | Rangau fdr #2 Load dropped 74A (86-12A). Not checked yet. | 3278901 | 1 | 17:14 | Afternoon | Sunday | 2016 | 4
4321 | 2016-04-10 17:14 | 2016-06-10 08:05 | 13.8KV RANGAU FEEDER #2 | Fair | Dead End Insulator | 0 | Checked & found, Rangau OCB fdr #2 T/R 1x Ctr: 174-175 R/F: 51N. Patrolled the line & found: -@2 Broken Dead end Insulator o/p #22DD-15. -@3 Broken Pin Insulator o/p #22BG-04. Cause: Dead end Insulator. | 3278901 | 1 | 17:14 | Afternoon | Sunday | 2016 | 4
4322 | 2016-05-10 14:00 | 2016-05-10 14:00 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 14 | 14:00 It was reported b/o fuse for Tx at Well Bangko #293. (Bangko fdr #1) Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Bangko #293. 15:40 Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Squirrel) | 3279356 | 1 | 14:00 | Afternoon | Tuesday | 2016 | 5
4323 | 2016-05-10 15:00 | 2016-05-10 15:00 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 15:00 It was reported b/o fuse for Tx o/p #07-T1-03. (D.Field fdr #2) 16:40 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T1-03. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3279357 | 1 | 15:00 | Afternoon | Tuesday | 2016 | 5
4324 | 2016-06-10 08:33 | 2016-06-10 08:33 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning Arrester | 0 | C.Duri fdr #1 Load dropped 24A (176-152A). Not checked yet. | 3279727 | 1 | 8:33 | Morning | Friday | 2016 | 6
4325 | 2016-06-10 08:33 | 16/10/2016 14:15 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning Arrester | 0 | Checked & found, Recl. 38AS-09 (C.Duri fdr #1) T/R 1x Ctr: 192-193. Patrolled the line & found, @3 broken L/A at TP of Well Puncak #08. Cause: Lightning Arrester. | 3279727 | 1 | 8:33 | Morning | Friday | 2016 | 6
4326 | 2016-06-10 09:57 | 2016-06-10 09:57 | CENTRAL DURI POWER PLANT |  |  | - | 09:57 S/U CGT #4, then On line the Unit at 10:18 |  | 1 | 9:57 | Morning | Friday | 2016 | 6
4327 | 2016-06-10 15:15 | 2016-06-10 15:15 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 15:15 It was reported b/o fuse for Tx o/p #08-M3-22. (C.Duri fdr #2) 16:00 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #08-M3-22. Replaced b/o fuse above with the same size, the energized the Tx. Cause: Unidentified (Fuse). | 3279730 | 1 | 15:15 | Afternoon | Friday | 2016 | 6
4328 | 2016-06-10 22:59 | 2016-06-10 22:59 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 35 | 8C VCB fdr #6 T/R 1x. 8C fdr #5 Load dropped 56A (118-63A). T/O WIP at GS-2. 8C fdr #4 Load dropped 260A (283-23A). T/O WIP at GS-2. Not checked yet. | 3279734 | 1 | 22:59 | Night | Friday | 2016 | 6
4329 | 2016-06-10 22:59 | 13/10/2016 07:15 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 35 | Checked & found, 8C VCB fdr #6 T/R 1x Ctr: 571-572 R/F: 50@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3279734 | 1 | 22:59 | Night | Friday | 2016 | 6
4330 | 2016-06-10 23:02 | 2016-06-10 23:02 | MINAS POWER PLANT | Rain and Lightning | Low mega-ohm reading | 0 | MGT #11 Tripped By Alarm: Generator Diff. Trip. (Excitation Trip) Cause: Under Investigation. (No Load shedding) | 3279728 | 1 | 23:02 | Night | Friday | 2016 | 6
4331 | 2016-06-10 23:02 | 2016-07-10 17:00 | MINAS POWER PLANT | Rain and Lightning | Low mega-ohm reading | 0 | Checked & found, Generator Stator Winding phase 1-3 of MGT-11 is short circuit. Cause: Low megger reading Stator Winding. | 3279728 | 1 | 23:02 | Night | Friday | 2016 | 6
4332 | 2016-06-10 23:22 | 2016-06-10 23:22 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 32 | 6D fdr #2 Load Dropped 211A (248-37A). 6D fdr #1 Load dropped 165A (251-86A). Not checked yet. | 3279746 | 1 | 23:22 | Night | Friday | 2016 | 6
4333 | 2016-06-10 23:22 | 2016-08-10 15:00 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 32 | Checked & found, Recl. 6D-298 (6D fdr #2) T/R 1x Ctr: 46-47. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3279746 | 1 | 23:22 | Night | Friday | 2016 | 6
4334 | 2016-07-10 07:29 | 2016-07-10 07:29 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Tree | 0 | Duri Community ACB fdr #1 T/R 1x . Not checked Yet. | 3279744 | 1 | 7:29 | Morning | Sunday | 2016 | 7
4335 | 2016-07-10 07:29 | 2016-08-10 17:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Tree | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 90-91 R/F: 51N. Patrolled the line & found, high palm Tree touching power line at near pole #3DE-40. Cause: Tree. | 3279744 | 1 | 7:29 | Morning | Sunday | 2016 | 7
4336 | 2016-07-10 07:48 | 2016-07-10 07:48 | 13.8KV SURAM FEEDER #1 | Fair | Animal | 0 | Suram fdr #1 Load dropped 25A (76-51A). Not checked yet. | 3280853 | 1 | 7:48 | Morning | Sunday | 2016 | 7
4337 | 2016-07-10 07:48 | 2016-09-10 10:00 | 13.8KV SURAM FEEDER #1 | Fair | Animal | 0 | Checked & found, Recl. 11CW-07 (Suram fdr #1) T/R 1x Ctr: 1176-1177 Patrolled the line & found, a dead Monkey under power line near pole #11CW-15. Cause: Animal. (Monkey) | 3280853 | 1 | 7:48 | Morning | Sunday | 2016 | 7
4338 | 2016-08-10 04:19 | 2016-08-10 04:19 | MINAS POWER PLANT | Fair | Under investigation | 0 | 04:19 MGT #5 Tripped By Alarm: SRV Tracking Error. (Gas Fuel Interval Press Low) Cause: Under Investigation. 17:45 S/U MGT #5, then On line the Unit at 17:55. (After troublesoothing MGT #5) | 3280311 | 1 | 4:19 | Morning | Wednesday | 2016 | 8
4339 | 2016-08-10 05:45 | 2016-08-10 05:45 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Tree | 0 | 05:45 Duri Community ACB fdr#2 T/R 1x. 17:23 Checked & found, Duri Community ACB fdr #2 T/R 1x Ctr: 74-75 R/F: 51N. Patrolled the line & found, high Trees under power line near House Seulawah #21, #24 & 36. Cause: Tree. | 3280854 | 1 | 5:45 | Morning | Wednesday | 2016 | 8
4340 | 2016-08-10 10:55 | 2016-08-10 10:55 | MINAS POWER PLANT |  |  | - | 10:55 S/U MGT #1, then On line the Unit at 11:07. |  | 1 | 10:55 | Morning | Wednesday | 2016 | 8
4341 | 2016-08-10 17:45 | 2016-08-10 17:45 | MINAS POWER PLANT |  |  | - | 17:45 S/U MGT #5, then On line the Unit at 17:55. (After troublesoothing MGT #5) |  | 1 | 17:45 | Afternoon | Wednesday | 2016 | 8
4342 | 2016-09-10 16:45 | 2016-09-10 16:45 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified (Fuse) | 0 | 16:45 It was reported b/o fuse for Tx o/p #05-P5-16. (C.Duri fdr #13 / Darling fdr #7) 21:28 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #05-P5-16. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3280856 | 1 | 16:45 | Afternoon | Saturday | 2016 | 9
4343 | 2016-10-10 13:45 | 2016-10-10 13:45 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 0 | 13:45 It was reported b/o fuse for Tx at Well Bangko #137. (Bangko fdr #4) 16:00 Checked & found, @1, @3 b/o 3.5SF fuses for 150Kva Tx at Well Bangko #137. Tested TTR, Megger the Tx & found, low megger. Cause: Tx Failure. (Low megger reading) (The Tx failure is not replaced yet) | 3281318 | 1 | 13:45 | Afternoon | Monday | 2016 | 10
4344 | 2016-10-10 13:45 | 2016-11-10 10:00 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 0 | Replaced 150Kva Tx failure with the same size & energized the Tx at Well Bangko #137. Cause: Tx failure. (Low megger reading) | 3281318 | 1 | 13:45 | Afternoon | Monday | 2016 | 10
4345 | 2016-10-10 19:15 | 2016-10-10 19:15 | 13.8KV ROKAN FEEDER #2 | Fair | Pin Insulator | 11 | Rokan VCB fdr #2 T/R 1x. Not checked yet. | 3281319 | 1 | 19:15 | Night | Monday | 2016 | 10
4346 | 2016-10-10 19:15 | 2016-11-10 20:00 | 13.8KV ROKAN FEEDER #2 | Fair | Pin Insulator | 11 | Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 1244-1245 R/F: 51N. Patrolled the line & found, @3 broken Pin Insuator o/p #30AV-24. Cause: Pin Insulator. | 3281319 | 1 | 19:15 | Night | Monday | 2016 | 10
4347 | 2016-11-10 13:58 | 2016-11-10 13:58 | 13.8KV SURAM FEEDER #1 | Fair | Unidentified | 0 | Suram fdr #1 Load dropped 43A (77-34A). Not checked yet. | 3281783 | 1 | 13:58 | Afternoon | Thursday | 2016 | 11
4348 | 2016-11-10 13:58 | 15/10/2016 08:24 | 13.8KV SURAM FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 11CW-07 (Suram fdr #1) T/R 1x Ctr: 188-189. Patrolled the line, but found nothing. Cause: Unidentified. | 3281783 | 1 | 13:58 | Afternoon | Thursday | 2016 | 11
4349 | 2016-11-10 15:35 | 2016-11-10 15:35 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 6 | 15:35 C.Duri ACB fdr #16 T/SO. (On block position) Ctr: 292-293 R/F: 51N & 51@1,@2. 16:01 Manually close C.Duri ACB fdr #16, Ok. Then normalized the block. Not Patrolled yet. | 3281802 | 1 | 15:35 | Afternoon | Thursday | 2016 | 11
4350 | 2016-11-10 15:35 | 13/10/2016 17:00 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 6 | Patrolled the line, but found nothing. Cause: Unidentified. | 3281802 | 1 | 15:35 | Afternoon | Thursday | 2016 | 11
4351 | 2016-11-10 18:13 | 2016-11-10 18:13 | 13.8KV 3D TX-1 GFPC | Rain and Lightning | Lightning | 0 | 3D GFPC-TX #1 T/R 1x. Ground fault alarm on 3D fdr #2. (No load droppedat any fdrs) Not checked yet. | 3281805 | 1 | 18:13 | Afternoon | Thursday | 2016 | 11
4352 | 2016-11-10 18:13 | 13/10/2016 17:05 | 13.8KV 3D TX-1 GFPC | Rain and Lightning | Lightning | 0 | Checked & found, 3D GFPC-TX #1 T/R 1x Ctr: 4088-4089. Patrolled 3D fdr #2 line, but found nothing. Cause: Suspected by Lightning. | 3281805 | 1 | 18:13 | Afternoon | Thursday | 2016 | 11
4353 | 2016-12-10 20:22 | 2016-12-10 20:22 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | C.Duri fdr #15 Load dropped 45A (205-160A). Not checked yet | 3282553 | 1 | 20:22 | Night | Saturday | 2016 | 12
4354 | 2016-12-10 20:22 | 16/10/2016 14:20 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | Checked & found, Recl. 05-P3-02 (C.Duri fdr #15) T/R 1x Ctr: 41-42. Patrolled the line, but found nothing. Cause: Unidentified. | 3282553 | 1 | 20:22 | Night | Saturday | 2016 | 12
4355 | 2016-10-13 17:08 | 2016-10-13 17:08 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 136 | Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #1 Load dropped 12A (110-98A). Ketigul fdr #3 Load dropped 19A (22-3A). Not checked yet. | 3283780 | 1 | 17:08 | Afternoon | Thursday | 2016 | 10
4356 | 2016-10-13 17:08 | 2016-10-14 09:50 | 13.8KV KETIGUL FEEDER#2 | Cloudy and Lightning | Lightning | 136 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 217-218 R/F: 51N. Patrolled the line & found, @3 broken Dead end Insulator o/p #29AM-08. Cause: Lightning. | 3283780 | 1 | 17:08 | Afternoon | Thursday | 2016 | 10
4357 | 2016-10-13 20:41 | 2016-10-13 20:41 | 4.16KV SO RUMBAI FEEDER #1 | Rain and Lightning | Lightning | 0 | 4.16Kv So.Rumbai Recl. fdr #1 T/R 1x. Not checked yet. | 3282556 | 1 | 20:41 | Night | Thursday | 2016 | 10
4358 | 2016-10-13 20:41 | 2016-10-15 15:40 | 4.16KV SO RUMBAI FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, So.Rumbai Recl. fdr #1 T/R 1x Ctr: 474-475 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3282556 | 1 | 20:41 | Night | Thursday | 2016 | 10
4359 | 2016-10-14 07:02 | 2016-10-14 07:02 | 13.8KV BANGKO FEEDER #3 | Fair | Animal | 0 | 07:02 Bangko OCB fdr #3 T/R 1x. Bangko fdr #4 load dropped 172A (242-70A). 07:38 Bangko OCB fdr #3 T/R 1x again. Not checked yet. 17:00 Checked & found, Bangko OCB fdr #3 T/R 2x Ctr: 99941-99943 R/F: 50@2,@3. Patrolled the line & found, a dead Monkey under pole #22Z-08. (In camp area) Cause: Animal. (Monkey) | 3283729 | 1 | 7:02 | Morning | Friday | 2016 | 10
4360 | 2016-10-14 07:02 | 2016-10-14 07:02 | 13.8KV BANGKO FEEDER #1 | Fair | Unidentified | 33 | 07:02 Bangko fdr #1 load dropped 73A (216-143A). 07:38 Bangko fdr #1 load dropped 75A again (216-141A). Not Checked yet. | 3283732 | 1 | 7:02 | Morning | Friday | 2016 | 10
4361 | 2016-10-14 07:02 | 2016-10-15 09:30 | 13.8KV BANGKO FEEDER #1 | Fair | Unidentified | 33 | Checked & found, Recl. 23X-08 (Bangko fdr #1) T/R 2x Ctr: 367-369. Patrolled the line, but found nothing. Cause: Unidentified. | 3283732 | 1 | 7:02 | Morning | Friday | 2016 | 10
4362 | 2016-10-14 11:00 | 2016-10-14 11:00 | MINAS POWER PLANT |  |  | - | 11:00 S/U MGT #4, then On line the Unit at 11:30. (NDC will be reduce Load up to 20MW for replace Glycool Fan) 14:35 Off line MGT #4, then S/D the Unit for repairing AA precooler leakage. (AA Pre cooler leakage) |  | 1 | 11:00 | Morning | Friday | 2016 | 10
4363 | 2016-10-14 16:08 | 2016-10-14 16:08 | MINAS POWER PLANT |  |  | - | 16:08 S/U MGT #2, then Online the Unit at 16:30. |  | 1 | 16:08 | Afternoon | Friday | 2016 | 10
4364 | 2016-10-15 16:24 | 2016-10-15 16:24 | CENTRAL DURI POWER PLANT | Fair | Equipment Failure | 0 | 16:24 CGT #5 Tripped. By Alarm: 63QT. (Lube Oil Pressure Low Trip) Cause: Equipment failure. (Instrument 63QT failure) 16-Oct-2016. 14:54 S/U CGT #5, then online the Unit at 15:08. (After replacing Equipment 63QT failure) | 3283247 | 1 | 16:24 | Afternoon | Saturday | 2016 | 10
4365 | 2016-10-15 17:59 | 2016-10-15 17:59 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Rain and Lightning | Lightning | 331 | MSU-2 VCB fdr #2 (So.Balam fdr #3 & fdr #4) T/R 1x. MSU-2 VCB fdr #1 (So.Balam fdr #1 & fdr #2) Load dropped 189A (209-20A). Not checked yet. | 3283754 | 1 | 17:59 | Afternoon | Saturday | 2016 | 10
4366 | 2016-10-15 17:59 | 2016-10-16 15:30 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Rain and Lightning | Lightning | 331 | Checked & found, MSU-2 VCB fdr #2 T/R 1x Ctr: 246-247 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3283754 | 1 | 17:59 | Afternoon | Saturday | 2016 | 10
4367 | 2016-10-15 18:06 | 2016-10-15 18:06 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 52 | Bangko OCB fdr #4 T/R 1x. Not checked yet. | 3283755 | 1 | 18:06 | Afternoon | Saturday | 2016 | 10
4368 | 2016-10-15 18:06 | 2016-10-20 17:05 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 52 | Checked & found, Bangko OCB fdr #4 T/R 2x Ctr: 99995-99997 R/F: 51N. Patrolled the line & found, @1 broken Dead end Insulator o/p #25AB-18. Cause: Lightning. | 3283755 | 1 | 18:06 | Afternoon | Saturday | 2016 | 10
4369 | 2016-10-15 18:10 | 2016-10-15 18:10 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 30 | Sintong OCB fdr #1 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. | 3283758 | 1 | 18:10 | Afternoon | Saturday | 2016 | 10
4370 | 2016-10-15 18:10 | 2016-10-20 13:30 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 30 | Checked & found, Sintong OCB fdr #1 T/R 1x Ctr: 382-383 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator o/p #25AD-46. Cause: Lightning. | 3283758 | 1 | 18:10 | Afternoon | Saturday | 2016 | 10
4371 | 2016-10-15 18:10 | 2016-10-15 18:10 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 563 | 18:10 Sintong OCB fdr #2 T/SO. Sintong GFPC T/R 1x. 19:30 Checked & found, Sintong OCB fdr #2 T/SO. Ctr: 417-418 R/F: 51@1. 19:45 Blocked & closed, Sintong OCB fdr #2, but failed to close. 20:00 Manuall Closed Sintong OCB fdr #2 at OCB unit breaker, but also failed. (Ctr did not change) Decided to Transfering Load of Sintong fdr #2 to fdr #1. 21:15 Open both Isolation Switches of Sintong OCB fdr #2. 21:25 Blocked Sintong OCB fdr #1. 21:45 Closed LBS #26AE-07, Ok. (All Load of Sintong fdr#2 move to Sintong fdr #1) Normalized Block of Sintong fdr #1. Patrolled the line & found, @1 broken Pin Insulator o/p #26AE-23. Cause: Lightning. (Need to check & service the breaker unit of Sintong fdr #2) | 3283761 | 1 | 18:10 | Afternoon | Saturday | 2016 | 10
4372 | 2016-10-16 06:41 | 2016-10-16 06:41 | 13.8KV BANGKO FEEDER #4 | Fair | Dead End Insulator | 62 | 06:41 Bangko OCB fdr #4 T/R 1x. 17:07 Bangko OCB fdr #4 T/R 1x again. Not checked yet. | 3283764 | 1 | 6:41 | Morning | Sunday | 2016 | 10
4373 | 2016-10-16 06:41 | 2016-10-21 08:05 | 13.8KV BANGKO FEEDER #4 | Fair | Dead End Insulator | 62 | Checked & found, Bangko OCB fdr #4 T/R 2x Ctr: 99997-99999 R/F: 51N. Patrolled the line & found, @3 broken Dead end Insulator o/p #25Z-10. Cause: Dead end Insulator. | 3283764 | 1 | 6:41 | Morning | Sunday | 2016 | 10
4374 | 2016-10-16 14:54 | 2016-10-16 14:54 | CENTRAL DURI POWER PLANT |  |  | - | 14:54 S/U CGT #5, then On Line the Unit at 15:08. (After replacing instrument 63QT failure) |  | 1 | 14:54 | Afternoon | Sunday | 2016 | 10
4375 | 2016-10-16 15:17 | 2016-10-16 15:17 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Sintong fdr #1 Load dropped 76A (293-216A). Not checked yet. | 3283766 | 1 | 15:17 | Afternoon | Sunday | 2016 | 10
4376 | 2016-10-16 15:17 | 2016-10-20 14:15 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 25AD-26 (Sintong fdr #1) T/R 1x Ctr: 108-109. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3283766 | 1 | 15:17 | Afternoon | Sunday | 2016 | 10
4377 | 2016-10-16 17:07 | 2016-10-16 17:07 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 70 | Bangko fdr #1 Load dropped 87A (179-92A). Not checked yet. | 3283767 | 1 | 17:07 | Afternoon | Sunday | 2016 | 10
4378 | 2016-10-16 17:07 | 2016-10-23 07:07 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 70 | Checked & found, Recl. 24Y-21 (Bangko fdr #1) T/R 1x Ctr: 101-102 R/F: 50@3. Patrolled the line & found, @3 Flashed over Pin Insulator o/p #24Y-23. Cause: Lightning. | 3283767 | 1 | 17:07 | Afternoon | Sunday | 2016 | 10
4379 | 2016-10-16 19:37 | 2016-10-16 19:37 | MINAS POWER PLANT |  |  | - | 19:37 Off line MGT #2, then S/D the Unit for S/B. |  | 1 | 19:37 | Night | Sunday | 2016 | 10
4380 | 2016-10-17 05:45 | 2016-10-17 05:45 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Dead End Insulator | 0 | C.Duri ACB fdr #6 T/R 1x Ctr: 444-445 R/F: 51N & 51G. Not Patrolled yet. | 3283775 | 1 | 5:45 | Morning | Monday | 2016 | 10
4381 | 2016-10-17 05:45 | 2016-10-19 06:45 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Dead End Insulator | 0 | Patrolled the line & found: -@3 Flashed over Dead end Insulator o/p #01-1-11. -@1 Flashed over Dead end Insulator o/p #03-2-01. Cause: Dead end Insulator. | 3283775 | 1 | 5:45 | Morning | Monday | 2016 | 10
4382 | 2016-10-17 07:00 | 2016-10-17 07:00 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Fair | Unidentified | 119 | 07:00 MSU-2 fdr #1 (So.Balam fdr #1 & fdr #2) Load dropped 178A (200-22A) 14:45 Checked & found, Recl. 16Z-25 (So.Balam fdr #1) T/R 1x Ctr: 23-24. Patrolled the line, but found nothing. Cause: Unidentified. | 3283778 | 1 | 7:00 | Morning | Monday | 2016 | 10
4383 | 2016-10-17 08:52 | 2016-10-17 08:52 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 08:52 CGT #5 Tripped. By Alarm: High Vibration. Cause: Under Investigation. 16:30 Re-S/U CGT #5, then on line the Unit at 16:45. (Running on Test) | 3283247 | 1 | 8:52 | Morning | Monday | 2016 | 10
4384 | 2016-10-17 17:06 | 2016-10-17 17:06 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri ACB fdr #16 T/R 1x Ctr: 273-274 R/F: 51N & 51@1,@2. Not Patrolled yet. | 3284083 | 1 | 17:06 | Afternoon | Monday | 2016 | 10
4385 | 2016-10-17 17:06 | 2016-10-19 06:45 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3284083 | 1 | 17:06 | Afternoon | Monday | 2016 | 10
4386 | 2016-10-17 17:50 | 2016-10-17 17:50 | 13.8KV DARLING VCB FEEDER #6 | Fair | Unidentified (Fuse) | 6 | 17:50 It was reported b/o fuse for Tx o/p #05-P3-09. (Darling fdr #6) 18:40 Checked & found, @1, @2 b/o 3.1SF fuses for 112.5Kva Tx o/p #05-P3-09. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3284085 | 1 | 17:50 | Afternoon | Monday | 2016 | 10
4387 | 2016-10-18 09:06 | 2016-10-18 09:06 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 25 | 09:06 So.Bekasap fdr #1 Load dropped 73A (173-100A). 09:43 Ckecked & found, Recl. 34B1-18 (So.Bekasap fdr #1) T/SO. Ctr: 155-156. Blocked & Closed Recl. 34B1-18, Ok. Then release the blocked. Not patrolled yed. | 3284612 | 1 | 9:06 | Morning | Tuesday | 2016 | 10
4388 | 2016-10-18 09:06 | 2016-10-24 17:00 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 25 | Patrolled the line, but found nothing. Cause: Unidentified. | 3284612 | 1 | 9:06 | Morning | Tuesday | 2016 | 10
4389 | 2016-10-18 16:24 | 2016-10-18 16:24 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 6 | 16:24 It was reported b/o fuse for Tx o/p #08-M3-19. (C.Duri fdr #2) 17:10 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #08-M3-19. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3284620 | 1 | 16:24 | Afternoon | Tuesday | 2016 | 10
4390 | 2016-10-18 17:29 | 2016-10-18 17:29 | 13.8KV 6D FEEDER #1 | Fair | Animal | 31 | 6D fdr #1 Load dropped 125A (197-72A). Not checked yet. | 3284638 | 1 | 17:29 | Afternoon | Tuesday | 2016 | 10
4391 | 2016-10-18 17:29 | 2016-10-19 17:35 | 13.8KV 6D FEEDER #1 | Fair | Animal | 31 | Checked & found, 6D OCB fdr #1 T/R 1x Ctr: 309-310 R/F: 51N. Patrolled the line & found, a dead bird (Owl) o/p #4C-52. Cause: Animal. (Owl) | 3284638 | 1 | 17:29 | Afternoon | Tuesday | 2016 | 10
4392 | 2016-10-18 18:00 | 2016-10-18 18:00 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 5 | 18:00 It was reported b/o fuse for Tx at Well Seruni #2. (Sintong fdr #1) 21:00 Checked & found, @2,@3 b/o 7.8SF fuses for 300Kva Tx at Well Seruni #2. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal. (Squirrel) | 3284650 | 1 | 18:00 | Afternoon | Tuesday | 2016 | 10
4393 | 2016-10-19 07:37 | 2016-10-19 07:37 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT #5, then S/D the Unit for troubleshooting. (the Unit Tripped by alarm: High vibration) 17:25 S/U CGT #5, then on line the Unit at 17:40. |  | 1 | 7:37 | Morning | Wednesday | 2016 | 10
4394 | 2016-10-19 07:38 | 2016-10-19 07:38 | MINAS POWER PLANT |  |  | - | 07:38 S/U MGT #4, then on line the Unit at 08:08. |  | 1 | 7:38 | Morning | Wednesday | 2016 | 10
4395 | 2016-10-19 10:15 | 2016-10-19 10:15 | 13.8KV ROKAN FEEDER #2 | Fair | Planned Maintenance | 218 | 10:47 Manually Open Rokan VCB fdr #2. Repairing the corrosion Cross arm o/p #23AV-23. Also replacing 70Pcs Pin Insulators with Post type Pin at Kopar fields. 16:05 Manually Closed Rokan VCB fdr #2. (After finishing to repairing cross arm above) Cause: Maintenance Job. | 3285053 | 1 | 10:15 | Morning | Wednesday | 2016 | 10
4396 | 2016-10-19 18:56 | 2016-10-19 18:56 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 19 | Sintong fdr #1 Load dropped 178A (296-118A). Not checked yet. | 3285019 | 1 | 18:56 | Afternoon | Wednesday | 2016 | 10
4397 | 2016-10-19 18:56 | 2016-10-20 14:20 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 19 | Checked & found, Recl. 28AF-02 (Sintong fdr #1) Ctr: 629-630. Patrolled the line & found, @1,@2,@3 broken & F/O Pin Insulators o/p #29AD-09. Cause: Lightning. | 3285019 | 1 | 18:56 | Afternoon | Wednesday | 2016 | 10
4398 | 2016-10-19 19:58 | 2016-10-19 19:58 | MINAS POWER PLANT |  |  | - | 19:58 Off Line MGT #5, then S/D the Unit for S/B. |  | 1 | 19:58 | Night | Wednesday | 2016 | 10
4399 | 2016-10-19 21:00 | 2016-10-19 21:00 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 38 | Rangau fdr #2 Load dropped 83A (85-2A). Not checked yet. | 3285047 | 1 | 21:00 | Night | Wednesday | 2016 | 10
4400 | 2016-10-19 21:00 | 2016-10-20 17:30 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 38 | Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 3x Ctr: 175-178. Patrolled the line & found, @2 broken Dead end Insulator o/p #22BD-15. Cause: Lightning. | 3285047 | 1 | 21:00 | Night | Wednesday | 2016 | 10
4401 | 2016-10-20 07:45 | 2016-10-20 07:45 | DURI POWER PLANT |  |  | - | 20 Oct 2016. 07:45 S/U DGT #7, then on line the Unit at 08:03. (Running on Test) 21 Oct 2016. 20:00 Off line DGT #7, then S/D the Unit for S/B. (Running on test after long time for S/B) |  | 1 | 7:45 | Morning | Thursday | 2016 | 10
4402 | 2016-10-20 10:10 | 2016-10-20 10:10 | MINAS POWER PLANT |  |  | - | 10:10 Off line MGT #8, then S/D the Unit for S/B. |  | 1 | 10:10 | Morning | Thursday | 2016 | 10
4403 | 2016-10-20 15:57 | 2016-10-20 15:57 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 40 | Sintong fdr #2 Load dropped 110A (196-86A). Sintong GFPC T/R 1x. Not checked yet. | 3285390 | 1 | 15:57 | Afternoon | Thursday | 2016 | 10
4404 | 2016-10-20 15:57 | 2016-10-24 07:30 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 40 | Checked & found, Recl. 28AF-02 (Sintong fdr #2) T/R 1x Ctr: 630-631 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3285390 | 1 | 15:57 | Afternoon | Thursday | 2016 | 10
4405 | 2016-10-20 19:44 | 2016-10-20 19:44 | 13.8KV BANGKO FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Bangko OCB fdr #2 T/R 1x. Bangko fdr #3 Load dropped 198A (233-35A). Not checked yet. | 3285393 | 1 | 19:44 | Night | Thursday | 2016 | 10
4406 | 2016-10-20 19:44 | 2016-10-23 16:44 | 13.8KV BANGKO FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Checked & found Bangko OCB fdr #4 T/R 1x Ctr: 99957-99958 R/F: 50@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3285393 | 1 | 19:44 | Night | Thursday | 2016 | 10
4407 | 2016-10-20 19:44 | 2016-10-20 19:44 | 13.8KV BANGKO FEEDER #1 | Cloudy | Lightning | 115 | Bangko fdr #1 Load dropped 144A (214-70A). Not checked yet. | 3285395 | 1 | 19:44 | Night | Thursday | 2016 | 10
4408 | 2016-10-20 19:44 | 2016-10-23 07:44 | 13.8KV BANGKO FEEDER #1 | Cloudy | Lightning | 115 | Checked & found Recl. 24Y21 T/R 1x Ctr:101-102 R/F:50@3. Patrolled the line & Found @3 Flashed over Pin Insulator o/p 24Y23. Cause: Lightning. | 3285395 | 1 | 19:44 | Night | Thursday | 2016 | 10
4409 | 2016-10-20 19:44 | 2016-10-20 19:44 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 46 | Bangko fdr #4 Load dropped 174A (238-64A). Not checked yet. | 3285396 | 1 | 19:44 | Night | Thursday | 2016 | 10
4410 | 2016-10-20 19:44 | 2016-10-23 16:50 | 13.8KV BANGKO FEEDER #4 | Cloudy and Lightning | Lightning | 46 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 139-140 R/F: 51N@1. Patrolled the line & found: -@1,@3 B/O fuses for 300KVAR Cap. bank o/p #27Y-01. -@1 Broken Pin Insulator on T/P of Well Benar #20. -@1 B/O fuse for 300KVAR Cap. bank o/p #29Y-17. Cause: Lightning. | 3285396 | 1 | 19:44 | Night | Thursday | 2016 | 10
4411 | 2016-10-21 07:00 | 2016-10-21 07:00 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified (Fuse) | 51 | 07:00 It was reported b/o fuse for Tx at Well Petani #35. (Petani fdr #2) 21:33 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Petani #35. Performed TTR & Megger the Tx, found good reading. Replaced b/o fuse above with same size & energized the Tx. Cause: Unidentified (fuse). | 3286995 | 1 | 7:00 | Morning | Friday | 2016 | 10
4412 | 2016-10-21 08:06 | 2016-10-21 08:06 | CENTRAL DURI POWER PLANT | Fair | Equipment Failure | 0 | 08:06 CGT #5 Tripped, By Alarm: High Vibration Trip. Cause: Under Investigation. 18:40 S/U CGT # 5, then on line the Unit at 19:02. (After replacing Relay-4) | 3283247 | 1 | 8:06 | Morning | Friday | 2016 | 10
4413 | 2016-10-21 09:45 | 2016-10-21 09:45 | 13.8KV DURI FIELD FEEDER #2 | Fair | Planned Maintenance | 0 | 09:45-11:00 Blocked Recl. 06-R5-02. (D.Field fdr #2) Replaced @1 seriously broken Pin Insulator o/p #06-R5-09. (4 wells were off, during the job done) Cause: Maintenance Job. | 3282714 | 1 | 9:45 | Morning | Friday | 2016 | 10
4414 | 2016-10-21 10:25 | 2016-10-21 10:25 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 10:25 It was reported b/o fuse for Tx o/p #05-N1-08A. (C.Duri fdr #14) 11:39 Checked & found, @1,@2 b/o 14.0SF fuses for 750Kva Tx o/p #05-N1-08A. Replaced b/o fuses for 750Kva Tx with the same size & energized the Tx. Cause: Animal. (Monkey). | 3286999 | 1 | 10:25 | Morning | Friday | 2016 | 10
4415 | 2016-10-21 17:37 | 2016-10-21 17:37 | MINAS POWER PLANT |  |  | - | 17:37 S/U MGT #8, then on line the Unit at 17:56. |  | 1 | 17:37 | Afternoon | Friday | 2016 | 10
4416 | 2016-10-21 17:59 | 2016-10-21 17:59 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified | 0 | Darling VCB fdr #4 T/R 1x. Not checked yet. |  | 1 | 17:59 | Afternoon | Friday | 2016 | 10
4417 | 2016-10-21 17:59 | 2016-10-23 07:59 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Darling VCB fdr #4 T/R 1x Ctr: 130-131 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 17:59 | Afternoon | Friday | 2016 | 10
4418 | 2016-10-21 20:00 | 2016-10-21 20:00 | DURI POWER PLANT |  |  | - | 20:00 Off line DGT #7, then S/D the Unit for S/B. (Running on test after long time for S/B) |  | 1 | 20:00 | Night | Friday | 2016 | 10
4419 | 2016-10-22 01:00 | 2016-10-22 01:00 | 13.8KV PETANI FEEDER #2 | Fair | Transformer Failure | 31 | 01:00 It was reported b/o again fuse for Tx at Well Petani #35. (Petani fdr #2) (See report on 21 Oct 2016 at 07:00) 10:45 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Petani #35. Performed TTR & Megger the Tx, found low megger reading. Cause: Tx failure. (Low megger reading) 17:45 Replaced 300Kva Tx failure with the same size & energized the Tx at Well Petani #35. Cause: Tx failure (Low megger reading) | 3286995 | 1 | 1:00 | Night | Saturday | 2016 | 10
4420 | 2016-10-22 17:45 | 2016-10-22 17:45 | 13.8KV PETANI FEEDER #2 | Fair | Transformer Failure | 47 | 17:45 Petani VCB fdr #2 T/LO. Checked & found, Petani VCB fdr #2 T/LO. Ctr: 186-190 R/F: 51N. Patrolled the line & found, @1 b/o 3.5SF fuse for 150Kva at Well Petani #35. 18:08 Blocked & closed Petani VCB fdr #2, Ok. Then release the block. Cause: Transformer failure. | 3287002 | 1 | 17:45 | Afternoon | Saturday | 2016 | 10
4421 | 2016-10-23 08:51 | 2016-10-23 08:51 | 13.8KV CENTRAL KOTABATAK FEEDER #2 | Fair | Unidentified | 0 | CKBS VCB fdr #2 T/R 1x. Checked & found, CKBS VCB fdr #2 T/R 1x Ctr: 93-94 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3287003 | 1 | 8:51 | Morning | Sunday | 2016 | 10
4422 | 2016-10-23 10:28 | 2016-10-23 10:28 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 217 | 10:28 Manual Opened Sintong OCB fdr #2. Replaced @1,@2,@3 seriously broken Pin Insulators o/p #26AE-23. 11:23 Blocked & closed Sintong OCB fdr #2. Cause: Maintenance Job. | 3283761 | 1 | 10:28 | Morning | Sunday | 2016 | 10
4423 | 2016-10-23 14:27 | 2016-10-23 14:27 | 13.8KV MINAS FEEDER #5 | Fair | Unidentified | 2 | 14:27 Minas ACB fdr #5 T/O. Ctr: 79-80 R/F: Not reported yet. 14:32 Blocked & closed Minas ACB fdr #5, Ok. Then released the block. Not patrolled yet. | 3287004 | 1 | 14:27 | Afternoon | Sunday | 2016 | 10
4424 | 2016-10-23 14:27 | 2016-10-25 07:20 | 13.8KV MINAS FEEDER #5 | Fair | Unidentified | 2 | Patrolled the line, but found nothing. Cause: Unidentified. | 3287004 | 1 | 14:27 | Afternoon | Sunday | 2016 | 10
4425 | 2016-10-23 14:45 | 2016-10-23 14:45 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 14:45 It was reported b/o fuse for Tx o/p #06-Q5-03. (C.Duri fdr #14) 16:10 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #06-Q5-03. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3287005 | 1 | 14:45 | Afternoon | Sunday | 2016 | 10
4426 | 2016-10-24 06:51 | 2016-10-24 06:51 | 13.8KV SINTONG FEEDER #2 | Cloudy | Animal | 94 | 06:51 Sintong OCB fdr #2 T/R 1x. Sintong fdr #1 Load dropped 20A (88-68A). Sintong GFPC T/R 1x. Not checked yet. 08:41 Sintong OCB fdr #2 T/R 1x again. Not checked yet. | 3288915 | 1 | 6:51 | Morning | Monday | 2016 | 10
4427 | 2016-10-24 06:51 | 2016-10-25 07:10 | 13.8KV SINTONG FEEDER #2 | Cloudy | Animal | 94 | Checked & found, Sintong OCB fdr #2 T/R 2x Ctr: 446-448 R/F: 51N. Patrolled the line & found, a dead Monkey under TP of Well Sintong #34. Cause: Animal. (Monkey) | 3288915 | 1 | 6:51 | Morning | Monday | 2016 | 10
4428 | 2016-10-24 07:37 | 2016-10-24 07:37 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | C.Duri VCB fdr #6 T/R 1x Ctr: 445-446 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3288918 | 1 | 7:37 | Morning | Monday | 2016 | 10
4429 | 2016-10-24 11:03 | 2016-10-24 11:03 | 13.8KV MENGGALA FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Menggala fdr #1 Load dropped 32A (195-163). Not checked yet. | 3288991 | 1 | 11:03 | Morning | Monday | 2016 | 10
4430 | 2016-10-24 11:03 | 2016-10-26 07:35 | 13.8KV MENGGALA FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 19AO-01 (Menggala fdr #1) T/R 1x Ctr: 459-460. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3288991 | 1 | 11:03 | Morning | Monday | 2016 | 10
4431 | 2016-10-24 14:38 | 2016-10-24 14:38 | 13.8KV SURAM FEEDER #1 | Fair | Guy Wire | 0 | Suram fdr #1 Load dropped 30A (76-36A). Not checked yet. | 3289001 | 1 | 14:38 | Afternoon | Monday | 2016 | 10
4432 | 2016-10-24 14:38 | 2016-10-25 11:30 | 13.8KV SURAM FEEDER #1 | Fair | Guy Wire | 0 | Checked & found, Recl. 14CY-01 (Suram fdr #1) T/R 1x Ctr: 187-188. Patrolled the line & found, broken Guy Wire of pole #14CW-4B. Cause: Guy Wire. | 3289001 | 1 | 14:38 | Afternoon | Monday | 2016 | 10
4433 | 2016-10-24 23:49 | 2016-10-24 23:49 | 115KV PUNGUT - KOTABATAK JUNCTION LINE | Fair | Under investigation | 0 | 24-Oct-2016. 23:49 115KV KBJ GCB #51 T/SO. 115KV KBJ GCB #53 T/SO. 115KV Pungut OCB #22 T/SO. (115KV KBJ - Pungut Line T/SO) 25-Oct-2016. 00:10 Manually closed 115KV KBJ 115 GCB #53, but T/O again. 01:45 Checked & found: -115KV KBJ GCB #51 T/SO. Ctr: 239-240. -115KV KBJ GCB #53 T/SO. Ctr: 213-216. -115KV Pungut OCB #22 T/SO. Ctr: 131-132 R/F: 87L@1,@2,@3. Patrolled the line, but found nothing. 04:25 Manually closed 115KV KBJ GCB #53, Ok. 04:27 Manually closed 115KV KBJ GCB #51, Ok. 04:29 Manually closed 115KV Pungut OCB #22. (failed to close from DSC and Local) Cause: Under investigation. (Suspected Pungut Breaker #22 problem) | 3289005 | 1 | 23:49 | Night | Monday | 2016 | 10
4434 | 2016-10-25 07:19 | 2016-10-25 07:19 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Duri Field VCB fdr #3 T/R 1x Ctr: 344-345 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3289008 | 1 | 7:19 | Morning | Tuesday | 2016 | 10
4435 | 2016-10-25 07:35 | 2016-10-25 07:35 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 43 | OKB OCB fdr #2 T/R 1x. Not checked yet. | 3289012 | 1 | 7:35 | Morning | Tuesday | 2016 | 10
4436 | 2016-10-25 07:35 | 2016-10-26 16:00 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 43 | Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1297-1298 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3289012 | 1 | 7:35 | Morning | Tuesday | 2016 | 10
4437 | 2016-10-25 07:57 | 2016-10-25 07:57 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning Arrester | 38 | Sintong OCB fdr #2 T/R 1x. Sintong fdr #1 Load dropped 30A (90-60A). Sintong GFPC T/R 1x. (Ground fault at Sintong fdr #2) Not checked yet. | 3289014 | 1 | 7:57 | Morning | Tuesday | 2016 | 10
4438 | 2016-10-25 07:57 | 2016-10-27 11:20 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning Arrester | 38 | Checked & found, Sintong OCb fdr #2 T/R 1x Ctr: 447-448 R/F: 51N. Patrolled the line & found, @2 broken L/A o/p #27AF-17. Cause: Lightning Arrester. | 3289014 | 1 | 7:57 | Morning | Tuesday | 2016 | 10
4439 | 2016-10-25 08:31 | 2016-10-25 08:31 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 0 | 08:31 It was reported b/o fuse for Tx o/p #03-03-07. (C.Duri fdr #7) 09:30 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #03-03-07. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3289017 | 1 | 8:31 | Morning | Tuesday | 2016 | 10
4440 | 2016-10-25 10:20 | 2016-10-25 10:20 | MINAS POWER PLANT |  |  | - | 10:20 S/U MGT #2, then on line the Unit at 10:30 (S/D MGT #6, due to Generator CO2 door Problem) |  | 1 | 10:20 | Morning | Tuesday | 2016 | 10
4441 | 2016-10-25 10:54 | 2016-10-25 10:54 | MINAS POWER PLANT |  |  | - | 10:54 Off line MGT #6, then S/D the Unit to Repair Generator CO2 Door. 26-Oct-2016. 15:10 S/U MGT #6, then On Line the Unit at 15:27. (after finishing repair Generator CO2 Door) |  | 1 | 10:54 | Morning | Tuesday | 2016 | 10
4442 | 2016-10-25 13:26 | 2016-10-25 13:26 | 13.8KV CENTRAL DURI FEEDER #14 | Rain and Lightning | Lightning | 18 | 13:26 C.Duri fdr #14 Load dropped 78A (230-152A). 15:00 Checked & found, Recl. 05-P5-22 (C.Duri fdr #14) T/SO. Ctr: 83-84. Blocked & closed Recl. 05-P5-22, Ok. Then released the Block. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289019 | 1 | 13:26 | Afternoon | Tuesday | 2016 | 10
4443 | 2016-10-25 14:37 | 2016-10-25 14:37 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 71 | 5B OCB fdr #3 T/R 1x. 5B fdr #1 Load dropped 76A (92-16A). 5B fdr #2 Load dropped 100A (162-62A). Not checked yet. | 3289022 | 1 | 14:37 | Afternoon | Tuesday | 2016 | 10
4444 | 2016-10-25 14:37 | 2016-10-27 16:45 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 71 | Checked & found, 5B OCB fdr #3 T/R 1x Ctr: 366-367 R/F: Did not appear. Patrolled the line, but found nothing. Cause: Suspected by Lightning. Checked Reclosers at downstream of 5B fdr #1 & fdr #2, are normal operation. (Ctr: Did not operate) Patrolled the line, but found nothing. Cause: Some Wells at downstream of 5B fdr #1 & fdr #2 were down when 5B OCB fdr #3 T/R. | 3289022 | 1 | 14:37 | Afternoon | Tuesday | 2016 | 10
4445 | 2016-10-25 14:44 | 2016-10-25 14:44 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 22 | 8C VCB fdr #4 T/R 1x. 8C fdr #5 Load dropped 56A (169-113A). Not checked yet. | 3289026 | 1 | 14:44 | Afternoon | Tuesday | 2016 | 10
4446 | 2016-10-25 14:44 | 2016-10-27 09:45 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 22 | Checked & found, 8C VCB fdr #4 T/R 1x Ctr: 587-588 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289026 | 1 | 14:44 | Afternoon | Tuesday | 2016 | 10
4447 | 2016-10-25 15:20 | 2016-10-25 15:20 | 13.8KV CENTRAL DURI FEEDER #2 | Rain and Lightning | Lightning | 10 | 15:20 It was reported No Power at Road-M7 Area-8. (C.Duri fdr #2) 16:10 Checked & found, Recl. 08-M7A-01 (C.Duri fdr #2) T/SO. Ctr: 72-73. Blocked & Closed Recl. 08-M7A-01, Ok. Then Released the Block. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289031 | 1 | 15:20 | Afternoon | Tuesday | 2016 | 10
4448 | 2016-10-25 16:20 | 2016-10-25 16:20 | 13.8KV CENTRAL DURI FEEDER #14 | Cloudy | Animal | 0 | 16:20 It was reported b/o fuse for Tx o/p #05-P3-05. (C.Duri fdr #14) 17:35 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #05-P3-05. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3289034 | 1 | 16:20 | Afternoon | Tuesday | 2016 | 10
4449 | 2016-10-26 15:10 | 2016-10-26 15:10 | MINAS POWER PLANT |  |  | - | 15:10 S/U MGT #6, then On Line the Unit at 15:27. (after finishing repair Generator CO2 Door) |  | 1 | 15:10 | Afternoon | Wednesday | 2016 | 10
4450 | 2016-10-26 16:24 | 2016-10-26 16:24 | MINAS POWER PLANT |  |  | - | 16:24 Off line MGT #2, then S/D the Unit for S/B. |  | 1 | 16:24 | Afternoon | Wednesday | 2016 | 10
4451 | 2016-10-27 08:21 | 2016-10-27 08:21 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | C.Duri ACB fdr #6 T/R 1x Ctr: 446-447 R/F: 51N. Not patrolled yet. | 3289039 | 1 | 8:21 | Morning | Thursday | 2016 | 10
4452 | 2016-10-27 08:21 | 2016-10-29 09:05 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3289039 | 1 | 8:21 | Morning | Thursday | 2016 | 10
4453 | 2016-10-27 10:42 | 2016-10-27 10:42 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 0 | 8C fdr #3 Load dropped 132A (210-79A). Not checked yet. | 3289043 | 1 | 10:42 | Morning | Thursday | 2016 | 10
4454 | 2016-10-27 10:42 | 2016-10-28 17:45 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 8D-18A (8C fdr #3) T/R 1x Ctr: 34-35. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289043 | 1 | 10:42 | Morning | Thursday | 2016 | 10
4455 | 2016-10-27 14:23 | 2016-10-27 14:23 | 13.8KV 3D FEEDER #2 | Fair | Unidentified | 5 | 3D OCB fdr #2 T/R 1x. 3D GFPC-Tx #1 T/R 1x. Not checked yet. | 3289044 | 1 | 14:23 | Afternoon | Thursday | 2016 | 10
4456 | 2016-10-27 14:23 | 2016-10-29 07:30 | 13.8KV 3D FEEDER #2 | Fair | Unidentified | 5 | Checked & found, 3D OCB fdr #2 T/R 1x Ctr: 221-222 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 3289044 | 1 | 14:23 | Afternoon | Thursday | 2016 | 10
4457 | 2016-10-27 14:50 | 2016-10-27 14:50 | 13.8KV 8C FEEDER #2 | Rain and Lightning | Lightning | 364 | 14:50 8C VCB fdr #2 T/LO. 15:10 Checked & found, 8C VCB fdr #2 T/LO. Ctr: 499-504 R/F: 51N(@2). Patrolled the Lne, but found nothing. 16:55 Blocked & closed 8C VCB fdr #2, but T/O again. 17:00 Open LBS #8DC-05. (to reduce load of 8C fdr #2 / Load ex 8D fdr #3) 17:27 Blocked & closed 8C VCB fdr #2, but T/O again. 17:45 Open Isolation Switch of 8C VCB fdr #2. (Performed Function Test the breaker, Ok) Transferred part load of 8C fdr #2 to 8C fdr #1. (Load ex 8D fdr #3) 18:30 Unplugged Recl. 8D-30. 18:35 Closed LBS #9D-07. (Total load 8C fdr #1 is 241A) 22:07 Blocked & closed 8C VCB fdr #2, Ok. Re-patrolled the line & found, @2 broken Pin Insulator o/p #9D-51. 22:10 Re-Opened 8C VCB fdr #2, to replace broken Pin Insulator above. 22:31 Blocked & closed 8C VCB fdr #2, Ok. Then release the block. Cause: Lightning. (broken Pin Insulator) | 3289046 | 1 | 14:50 | Afternoon | Thursday | 2016 | 10
4458 | 2016-10-27 16:40 | 2016-10-27 16:40 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 71 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3289047 | 1 | 16:40 | Afternoon | Thursday | 2016 | 10
4459 | 2016-10-27 16:40 | 2016-10-29 19:10 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 71 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 218-219 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289047 | 1 | 16:40 | Afternoon | Thursday | 2016 | 10
4460 | 2016-10-27 23:35 | 2016-10-27 23:35 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 0 | 23:35 It was reported b/o fuse for Tx at Well So.Balam #134. (So.Balam fdr #1) 00:45 Checked & found, @3 b/o 3.1SF fuse for 100Kva Tx at Well So.Balam #34. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3289051 | 1 | 23:35 | Night | Thursday | 2016 | 10
4461 | 2016-10-28 02:34 | 2016-10-28 02:34 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Rain and Lightning | Lightning | 0 | 4.16Kv Dumai (Wharf) ACB fdr #1 T/R 1x. Not checked yet. | 3289052 | 1 | 2:34 | Night | Friday | 2016 | 10
4462 | 2016-10-28 02:34 | 2016-10-29 09:00 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, 4.16Kv Dumai (Wharf) ACB fdr #1 T/R 1x Ctr: 250-251 R/F: 50N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289052 | 1 | 2:34 | Night | Friday | 2016 | 10
4463 | 2016-10-28 10:19 | 2016-10-28 10:19 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Switchboard Problem | 0 | 28-Oct-2016. 10:19 It was reported b/o fuse for Tx o/p #05-P5-14. (C.Duri fdr #15) 11:00 Checked & found, @1,@2,@3 b/o 3.1SF fuses for 112.5Kva Tx o/p #05-P5-14. (Also found, Switchboard spark) Cause: Switchboard. The fuses are not replaced yet. (w/o repairing switchboard) | 3289055 | 1 | 10:19 | Morning | Friday | 2016 | 10
4464 | 2016-10-28 10:19 | 2016-10-30 11:00 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Switchboard Problem | 0 | Replaced replaced b/o fuses above b/o with the same size & energized the Tx. (After Production team repairing the Switchboard) Cause: Switchboard. | 3289055 | 1 | 10:19 | Morning | Friday | 2016 | 10
4465 | 2016-10-29 09:03 | 2016-03-10 23:00 | 13.8KV RANGAU FEEDER #2 | Rain | Lightning | 100 | Checked & found, Recl. 23BD-01 (Rangau #2) T/R 2x Ctr: 178-180. Patrolled the line & found, @2 broken Dead end Insulator o/p #22BD-15. Cause: Lightning. | 3289060 | 1 | 9:03 | Morning | Saturday | 2016 | 10
4466 | 2016-10-29 09:03 | 2016-10-29 09:03 | 13.8KV RANGAU FEEDER #2 | Rain | Lightning | 100 | 09:03 Rangau fdr #2 Load dropped 84A (91-7A). 14:43 Rangau fdr #2 Load dropped 84A (91-7A) again. Not checked yet. | 3289060 | 1 | 9:03 | Morning | Saturday | 2016 | 10
4467 | 2016-10-29 12:51 | 2016-10-29 12:51 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 29 | Pematang fdr #1 Load dropped 35A (153-118A). Not checked yet. | 3289062 | 1 | 12:51 | Afternoon | Saturday | 2016 | 10
4468 | 2016-10-29 12:51 | 2016-03-11 17:15 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 29 | Checked all Recloser at downstream of Pematang fdr #1 & found, normal. (Counter did not change) Patrolled the line, but found nothing. Cause: Unidentified. (Suspected T/O WIP at Pematang-GS) | 3289062 | 1 | 12:51 | Afternoon | Saturday | 2016 | 10
4469 | 2016-10-29 15:08 | 2016-10-29 15:08 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 65 | Bekasap fdr #2 Load dropped 91A (128-37A). Bekasap GFPC-Tx #C T/R 1x. Not checked yet. | 3289064 | 1 | 15:08 | Afternoon | Saturday | 2016 | 10
4470 | 2016-10-29 15:08 | 2016-01-11 11:00 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 65 | Checked & found, Recl. 37BD-40 (Bekasap fdr #2) T/R 2x Ctr: 73-75. Patrolled the line & found, @1,@2,@3 Flashed over Pin Insulators o/p #37BD-54. Cause: Lightning. | 3289064 | 1 | 15:08 | Afternoon | Saturday | 2016 | 10
4471 | 2016-10-29 15:08 | 2016-10-29 15:08 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 0 | Bekasap fdr #3 Load dropped 114A (151-37A). Not checked yet. | 3289076 | 1 | 15:08 | Afternoon | Saturday | 2016 | 10
4472 | 2016-10-29 15:08 | 2016-01-11 13:30 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 1-TL-06 (Bekasap fdr #3) T/R 1x Ctr: 38-39. Patrolled the line & found, @2 broken L/A o/p #37BD-16A. Cause: Lightning. | 3289076 | 1 | 15:08 | Afternoon | Saturday | 2016 | 10
4473 | 2016-10-29 15:30 | 2016-10-29 15:30 | 13.8KV MENGGALA FEEDER #2 | Fair | Transformer Failure | 35 | 29 Oct 2016 15:30 It was reported b/o fuse for Tx at Well Ubi #10. (Menggala fdr #2) 17:30 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Ubi #10. Perform TTR, Megger test the Tx & found, low megger reading. Cause Tx Failure. (Low megger reading) 30 Oct 2016 15:45 Replaced 150Kva Tx failure with the same size & energized the Tx. Cause: Tx failure. | 3289089 | 1 | 15:30 | Afternoon | Saturday | 2016 | 10
4474 | 2016-10-29 15:32 | 2016-10-29 15:32 | 13.8KV DURI FIELD FEEDER #3 | Rain and Lightning | Lightning | 0 | Duri Field VCB fdr #3 T/R 1x. Not checked yet. | 3289119 | 1 | 15:32 | Afternoon | Saturday | 2016 | 10
4475 | 2016-10-29 15:32 | 2016-01-11 18:00 | 13.8KV DURI FIELD FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found, Duri Field ACB fdr #3 T/R 2x Ctr: 345-347 R/F: 51@1. Patrolled the line & found, @1 broken Pin Insulator o/p #01-05-22. Cause: Lightning. | 3289119 | 1 | 15:32 | Afternoon | Saturday | 2016 | 10
4476 | 2016-10-29 15:32 | 2016-10-29 15:32 | 13.8KV CENTRAL DURI FEEDER #6 | Rain and Lightning | Lightning | 0 | C.Duri ACB fdr #6 T/R 1x Ctr: 447-448 R/F: 51@2,@3. Not patrolled yet. | 3289122 | 1 | 15:32 | Afternoon | Saturday | 2016 | 10
4477 | 2016-10-29 15:32 | 2016-01-11 17:55 | 13.8KV CENTRAL DURI FEEDER #6 | Rain and Lightning | Lightning | 0 | Patrolled the line & found, @3 F/O Dead end Insulator o/p #02-03-03. Cause: Lightning. | 3289122 | 1 | 15:32 | Afternoon | Saturday | 2016 | 10
4478 | 2016-10-29 16:00 | 2016-10-29 16:00 | 13.8KV CENTRAL DURI FEEDER #3 | Rain and Lightning | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx at Steam Sta. Area-1. (C.Duri fdr #3) Not checked yet. |  | 1 | 16:00 | Afternoon | Saturday | 2016 | 10
4479 | 2016-10-29 16:00 | 2016-10-30 12:00 | 13.8KV CENTRAL DURI FEEDER #3 | Rain and Lightning | Unidentified (Fuse) | 0 | 12:00 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx at 5s SS-Area-1. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx at 5s SS-Area-1. Cause: Unidentified (Fuse). |  | 1 | 16:00 | Afternoon | Saturday | 2016 | 10
4480 | 2016-10-29 16:51 | 2016-10-29 16:51 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 15 | 4B OCB fdr #2 T/R 1x. Not checked yet. | 3289134 | 1 | 16:51 | Afternoon | Saturday | 2016 | 10
4481 | 2016-10-29 16:51 | 2016-10-30 18:30 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 15 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 230-231 R/F: 51N. Patrolled the line & found, @2 broken Bypass Switch o/p #4B-06. Cause: Lightning. | 3289134 | 1 | 16:51 | Afternoon | Saturday | 2016 | 10
4482 | 2016-10-29 16:51 | 2016-10-29 16:51 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 52 | 5B OCB fdr #3 T/R 1x. 5B fdr #1 Load dropped 74A (91-17A). 5B fdr #2 Load dropped 142A (162-20A). Not checked yet. | 3289135 | 1 | 16:51 | Afternoon | Saturday | 2016 | 10
4483 | 2016-10-29 16:51 | 2016-04-11 16:20 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 52 | Checked & found, 5B OCB fdr #3 T/R 2x Ctr: 367-369 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289135 | 1 | 16:51 | Afternoon | Saturday | 2016 | 10
4484 | 2016-10-29 17:00 | 2016-10-29 17:00 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Unidentified (Fuse) | 0 | 17:00 It was reported b/o fuse for Tx o/p #NN. (near Duri Training Center) 22:10 Checked & found, @1 b/o 2.1SF fuse for 100Kva Tx at near DTC. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 17:00 | Afternoon | Saturday | 2016 | 10
4485 | 2016-10-30 09:20 | 2016-10-30 09:20 | 13.8KV 6DN FEEDER #6 | Fair | Planned Maintenance | 11 | 09:20-12:06 Open HLC o/p #6D-84, to replace Pin Insulator with Post type. (S/D Wells #6D-18 & 6D-19). Minas GS-3. Cause: Maintenance Job. | 3271483 | 1 | 9:20 | Morning | Sunday | 2016 | 10
4486 | 2016-10-30 10:46 | 2016-10-30 10:46 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 10:46 It was reported b/o fuse for Tx at Well Kulin #9. (C.Duri fdr #1) 17:26 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Kulin #9. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3289248 | 1 | 10:46 | Morning | Sunday | 2016 | 10
4487 | 2016-10-30 12:03 | 2016-10-30 12:03 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 12:30 It was reported b/o fuse for Tx o/p #07-V1-15. (D.Field fdr #4) 15:30 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #07-V1-15. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 3289250 | 1 | 12:03 | Afternoon | Sunday | 2016 | 10
4488 | 2016-10-30 17:36 | 2016-10-30 17:36 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 51 | 6DN OCB fdr #6 T/R 1x. 6DN fdr #5 Load dropped 46A (55-9A). 6DN fdr #4 Load dropped 69A (216-147A). T/O WIP at GS-3. Not checked yet | 3289251 | 1 | 17:36 | Afternoon | Sunday | 2016 | 10
4489 | 2016-10-30 17:36 | 2016-04-11 19:35 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 51 | Checked & found, 6DN OCB fdr #6 T/R 1x Ctr: 347-348 R/F: 50@1,@3. Patrolled the Line, but found nothing. Cause: Suspected by Lightning. | 3289251 | 1 | 17:36 | Afternoon | Sunday | 2016 | 10
4490 | 2016-10-30 18:22 | 2016-04-10 16:10 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 139 | Checked & found, MSU-2 VCB fdr #2 T/R 1x Ctr: 247-248 R/F: 51@1,@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289254 | 1 | 18:22 | Afternoon | Sunday | 2016 | 10
4491 | 2016-10-30 18:22 | 2016-10-30 18:22 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 139 | MSU-2 VCB fdr #2 (Balam fdr #3 & fdr #4) T/R 1x. MSU-2 fdr #1 (Balam fdr #1 & fdr #2) Load dropped 148A (207-59A). Not checked yet | 3289254 | 1 | 18:22 | Afternoon | Sunday | 2016 | 10
4492 | 2016-10-30 18:46 | 2016-10-30 18:46 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 83 | Bangko fdr #1 Load dropped 170A (216-46A). Not checked yet. | 3289256 | 1 | 18:46 | Afternoon | Sunday | 2016 | 10
4493 | 2016-10-30 18:46 | 2016-03-11 09:30 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 83 | Checked & found, Recl. 23X-08 (Bangko fdr #1) T/R 1x Ctr: 368-369. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289256 | 1 | 18:46 | Afternoon | Sunday | 2016 | 10
4494 | 2016-10-30 18:46 | 2016-10-30 18:46 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Bangko fdr #4 Load dropped 184A (246-62A). Not checked yet. | 3289259 | 1 | 18:46 | Afternoon | Sunday | 2016 | 10
4495 | 2016-10-30 18:46 | 2016-05-11 07:22 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 139-140. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289259 | 1 | 18:46 | Afternoon | Sunday | 2016 | 10
4496 | 2016-10-30 18:49 | 2016-10-30 18:49 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 98 | Nella VCB fdr #1 T/R 1x. Not checked yet. | 3289261 | 1 | 18:49 | Afternoon | Sunday | 2016 | 10
4497 | 2016-10-30 18:49 | 2016-01-11 07:15 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 98 | Checked & found, Nella VCB fdr #1 T/R 1x Ctr: 496-497 R/F: 51N. Also found, Nella GFPC T/R 2x Ctr: 705-707. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3289261 | 1 | 18:49 | Afternoon | Sunday | 2016 | 10
4498 | 2016-10-31 15:41 | 2016-10-31 15:41 | 13.8KV S. BALAM FEEDER #4 | Fair | Animal | 12 | 15:41 It was reported b/o fuse for Tx at Well SE Balam #06. (S.Balam fdr #4) 16:00 Checked & found, @3 b/o 2.1SF fuse for 100Kva Tx at Well SE.Balam #06 Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Sarang semut, Ant hill) | 3289659 | 1 | 15:41 | Afternoon | Monday | 2016 | 10
4499 | 2016-10-31 17:55 | 2016-10-31 17:55 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | Duri Field ACB fdr #4 T/R 1x. Not checked yet. | 3289667 | 1 | 17:55 | Afternoon | Monday | 2016 | 10
4500 | 2016-10-31 17:55 | 2016-04-11 07:05 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | Checked & found, Duri Field ACB fdr #4 T/R 1x Ctr: 479-480 R/F: 51N. Patrolled the line & found, b/o fuse for Tx o/p #07-V1-15. Cause: Unidentified (Fuse). | 3289667 | 1 | 17:55 | Afternoon | Monday | 2016 | 10
4501 | 2016-10-31 19:33 | 2016-05-10 17:38 | 13.8KV NORTH DURI FEEDER #8 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 10-K2-02 (N.Duri fdr #8) T/R 1x Ctr: 107-108. Patrolled the line & found, @2 broken Dead end Insulator o/p #10-J5-01. Cause: Lightning. | 3289671 | 1 | 19:33 | Night | Monday | 2016 | 10
4502 | 2016-10-31 19:33 | 2016-10-31 19:33 | 13.8KV NORTH DURI FEEDER #8 | Cloudy and Lightning | Lightning | 0 | N.Duri fdr #8 Load dropped 100A (118-18). Ground fault Alarm at N.Duri fdr #8. Not checked yet. | 3289671 | 1 | 19:33 | Night | Monday | 2016 | 10
4503 | 2016-01-11 09:10 | 2016-01-11 09:10 | 13.8KV DURI FIELD FEEDER #4 | Fair | Transformer Failure | 1 | It was reported b/o fuse for Tx o/p #07-V1-15. (Duri Field fdr #4) Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #07-V1-15. Performed TTR, Megger test the Tx & found, low megger reading. (Found Mice in the Panel Box) Cause: Tx Failure. (Low megger reading) The Tx failure is not Replaced yet. | 3290084 | 1 | 9:10 | Morning | Monday | 2016 | 1
4504 | 2016-01-11 09:10 | 2016-04-11 12:10 | 13.8KV DURI FIELD FEEDER #4 | Fair | Transformer Failure | 1 | Replaced 112Kva Tx failure with the same size & energized the Tx o/p #07-V1-15. Cause: Tx failure. (Low megger reading) | 3290084 | 1 | 9:10 | Morning | Monday | 2016 | 1
4505 | 2016-01-11 09:16 | 2016-01-11 09:16 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 20 | Ketigul VCB fdr #1 T/R 1x. Ketigul fdr #2 Load droped 72A (222-150). Not checked yet. | 3290100 | 1 | 9:16 | Morning | Monday | 2016 | 1
4506 | 2016-01-11 09:16 | 2016-05-11 17:51 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 20 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 175-176 R/F: 51. Patrolled the Line, but found nothing. Cause: Unidentified. | 3290100 | 1 | 9:16 | Morning | Monday | 2016 | 1
4507 | 2016-01-11 15:41 | 2016-01-11 15:41 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Duri Field ACB fdr #4 T/R 1x. Not checked yet. | 3290107 | 1 | 15:41 | Afternoon | Monday | 2016 | 1
4508 | 2016-01-11 15:41 | 2016-04-11 06:55 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Duri Field ACB fdr #4 T/R 1x Ctr: 480-481 R/F: 50N. Patrolled the line, but found nothing. Cause: Unidentified. | 3290107 | 1 | 15:41 | Afternoon | Monday | 2016 | 1
4509 | 2016-01-11 17:48 | 2016-01-11 17:48 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 33 | 17:48 It was reported b/o fuse for Tx at Well Pagar #28. (Ketigul fdr #2) Checked & found, @2,@3 b/o 3.5SF fuses for 150Kva Tx at Well Pagar #28. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 3290110 | 1 | 17:48 | Afternoon | Monday | 2016 | 1
4510 | 2016-01-11 20:41 | 2016-01-11 20:41 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Tree | 90 | 4B OCB fdr #2 T/R 1x. Not checked yet. | 3290115 | 1 | 20:41 | Night | Monday | 2016 | 1
4511 | 2016-01-11 20:41 | 2016-03-11 22:00 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Tree | 90 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 231-232 R/F: 51N. Patrolled the line & found, High Trees & hit to power line near pole #4B-52. Cause: Tree. | 3290115 | 1 | 20:41 | Night | Monday | 2016 | 1
4512 | 2016-01-11 20:46 | 2016-01-11 20:46 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 55 | 5B OCB fdr #1 T/R 1x. 5B fdr #2 Load dropped 142A (162-20A). 5B fdr #3 Load dropped 87A (100-13A). 5B fdr #4 Load dropped 170A (235-65A). Not checked yet. | 3290118 | 1 | 20:46 | Night | Monday | 2016 | 1
4513 | 2016-01-11 20:46 | 2016-07-11 11:30 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 55 | Checked & found, 5B OCB fdr #1 T/R 1x Ctr: 226-227 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3290118 | 1 | 20:46 | Night | Monday | 2016 | 1
4514 | 2016-01-11 20:48 | 2016-01-11 20:48 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 57 | 3D OCB fdr #3 T/R 1x. 3D fdr #2 Load dropped 53A (193-140A). 3D fdr #4 Load dropped 27A (221-194A). 3D fdr #7 Load dropped 109A (182-73A). Not checked yet. | 3290122 | 1 | 20:48 | Night | Monday | 2016 | 1
4515 | 2016-01-11 20:48 | 2016-03-11 21:45 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 57 | Checked & found, 3D OCB fdr #3 T/R 1x Ctr: 440-441 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3290122 | 1 | 20:48 | Night | Monday | 2016 | 1
4516 | 2016-01-11 20:57 | 2016-01-11 20:57 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 0 | 4D OCB fdr #4 T/R 3x. Not checked yet. | 3290124 | 1 | 20:57 | Night | Monday | 2016 | 1
4517 | 2016-01-11 20:57 | 2016-06-11 22:20 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, 4D OCB fdr #4 T/R 2x Ctr: 238-240 R/F: 51@3. Patrolled the line & found, @3 broken Pin Insulator o/p #5E-20. Cause: Lightning. | 3290124 | 1 | 20:57 | Night | Monday | 2016 | 1
4518 | 2016-01-11 20:57 | 2016-01-11 20:57 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 0 | 4D OCB fdr #5 T/R 3x. Not checked yet. | 3290125 | 1 | 20:57 | Night | Monday | 2016 | 1
4519 | 2016-01-11 20:57 | 2016-06-11 22:20 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, 4D OCB fdr #5 T/R 3x Ctr: 287-290 R/F: 51@1,@2. Patrolled the line & found, @1,@2 broken Pin Insulators o/p #4D-103. Cause: Lightning. | 3290125 | 1 | 20:57 | Night | Monday | 2016 | 1
4520 | 2016-01-11 20:57 | 2016-01-11 20:57 | 115KV 4D - 6DN LINE | Rain and Lightning | Lightning | 0 | 115KV 4D GCB #23 T/R 1x. 115KV 4D GCB #24 T/R 1x. 115KV 6DN GCB #21 T/R 1x. (115KV 6DN - 4D line T/R) Not checked yet. | 3290127 | 1 | 20:57 | Night | Monday | 2016 | 1
4521 | 2016-01-11 20:57 | 2016-07-11 11:21 | 115KV 4D - 6DN LINE | Rain and Lightning | Lightning | 0 | Checked & found: -115KV 6DN GCB #21 T/R 1x Ctr: 416-417 R/F: Not Checked yet. -115KV 4D GCB #23 T/R 1x Ctr: 481-482 -115KV 4D GCB #24 T/R 1x Ctr: 639-640 R/F: Not checked yet. (115KV 4D - 6DN line is not patrolled yet) Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3290127 | 1 | 20:57 | Night | Monday | 2016 | 1
4522 | 2016-01-11 21:12 | 2016-01-11 21:12 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 0 | 6DN OCB fdr #1 T/R 1x. Not checked yet. | 3290128 | 1 | 21:12 | Night | Monday | 2016 | 1
4523 | 2016-01-11 21:12 | 2016-08-11 19:30 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, 6DN OCB fdr #1 T/R 2x Ctr: 238-240 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3290128 | 1 | 21:12 | Night | Monday | 2016 | 1
4524 | 2016-01-11 21:12 | 2016-01-11 21:12 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 0 | 6DN OCB fdr #5 T/R 1x. Not checked yet. | 3290131 | 1 | 21:12 | Night | Monday | 2016 | 1
4525 | 2016-01-11 21:12 | 2016-07-11 11:23 | 13.8KV 6DN FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, 6DN OCB fdr #5 T/R 1x Ctr: 230-231 R/F: Did not appear. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3290131 | 1 | 21:12 | Night | Monday | 2016 | 1
4526 | 2016-01-11 21:12 | 2016-01-11 21:12 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 0 | 6DN OCB fdr #6 T/R 1x. Not checked yet. | 3290132 | 1 | 21:12 | Night | Monday | 2016 | 1
4527 | 2016-01-11 21:12 | 2016-07-11 11:25 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked & found, 6DN OCB fdr #6 T/R 3x Ctr: 348-351 R/F: 50@3. Patrolled the line & found, @3 broken Pin Insulator o/p #6D-147. Cause: Lightning. | 3290132 | 1 | 21:12 | Night | Monday | 2016 | 1
4528 | 2016-01-11 21:21 | 2016-01-11 21:21 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 0 | 8D OCB fdr #10 T/R 1x. 8D fdr #9 Load dropped 121A (179-58A). 8D fdr #11 Load dropped 165A (194-29A). Not checked yet. | 3290134 | 1 | 21:21 | Night | Monday | 2016 | 1
4529 | 2016-01-11 21:21 | 2016-04-11 20:56 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 0 | Checked & found, 8D OCB fdr #10 T/R 1x Ctr: 224-225 R/F: 50@1,@2,@3. Patrolled the Line, found @1,@2,@3, broken Deadend O/P 8D-B-10. Cause: Lightning. | 3290134 | 1 | 21:21 | Night | Monday | 2016 | 1
4530 | 2016-01-11 21:25 | 2016-01-11 21:25 | 6 DELTA NEW SUBSTATION | Rain and Lightning | Voltage regulator failure | 516 | 21:25 115KV 6DN C/S-TX #1 T/O. (6DN fdr #1, #2, #3 are no Power) 21:30 Manual Opened 6DN OCB fdr #5. (Req. by GS #3, due to Tank Level high) 21:37 Manual Opened 6DN OCB fdr #1,#2, #3. 22:15 Checked & found, 6DN VR-1 was Burn Out (firring). (VR Oil blown out) (S/D 6DN TX #2, by opening 115KV C/S-TX #2. (To Extinguish fire of The VR by Fire team) 22:17 Manual Opened 6DN OCB fdr #4 & #6. Manual Opened 115KV 6DN TX-C/S #2. (from Local) Opened Isolation Switch of 115KV 6DN TX-1. 22:48 Manually Closed 115KV 6DN C/S-TX #2. 22:50 Manual Closed 13.8KV 6DN OCB fdr #4, #5 & #6. 02 NOV 2016 01:20 Transfer Load 6DN fdr #3 to 6D fdr #3. Closed LBS #A. Closed LBS #C. Opened LBS #B. 01:30 Transfer Load 6DN fdr #1 to 4D fdr#4. Closed LBS #36DN-27. 01:42 Transfer Load 6DN fdr #2 to 6DN fdr #6. Closed LBS #6D-142. Cause: VR Failure. (VR-1 burnt out by Lightning) | 3290135 | 1 | 21:25 | Night | Monday | 2016 | 1
4531 | 2016-02-11 10:05 | 2016-02-11 10:05 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 182 | 10:05-12:21 Manually opened Recl. 45BR-01 (Pungut fdr #2). Shut in Wells Tandun # 2, 13, 14, 9, 8, 4, 6, 12, 11, 10, 7, 5, 1 & Tandun GS. 10:54-15:28 Manually opened Recl. 45BZ-05 (Pungut fdr #2). Shut in 14 Wells Asih & Ayu fields: Asih #1, 2 & North Asih #1, 2 Ami #1, Oki #3, 4, 1, 2 & OKI GAS STA. Repairing the Corroded Pole (keropos) of pole #46BT-12. Replaced Seriously broken Pin insulator o/p #DK–84. Replacing Old type Pin insulator with new type. (70Pcs) & Replaced FCO. Cause: Mainteanance Job. | 3283392 | 1 | 10:05 | Morning | Thursday | 2016 | 2
4532 | 2016-02-11 18:54 | 2016-02-11 18:54 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 35 | So.Bekasap OCB fdr #1 T/R 1x. Not checked yet. | 3290607 | 1 | 18:54 | Afternoon | Thursday | 2016 | 2
4533 | 2016-02-11 18:54 | 2016-03-11 16:10 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 35 | Checked & found, So.Bekasap OCB fdr #1 T/R 1x Ctr: 346-347 R/F: 51N. Patrolled the line & found, @3 F/O Pin Insulator o/p #37BI-03. Cause: Lightning. | 3290607 | 1 | 18:54 | Afternoon | Thursday | 2016 | 2
4534 | 2016-02-11 19:21 | 2016-02-11 19:21 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 21 | 3D OCB fdr #2 T/R 4x. Not checked yet. | 3290611 | 1 | 19:21 | Night | Thursday | 2016 | 2
4535 | 2016-02-11 19:21 | 2016-04-11 08:10 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 21 | Checked & found, 3D OCB fdr #2 T/R 4x Ctr: 222-226 R/F: 51@1. Patrolled the line & found, @1 broken Fuse link for 350Kva Tx at Well #4D-29. Cause: Lightning. | 3290611 | 1 | 19:21 | Night | Thursday | 2016 | 2
4536 | 2016-02-11 19:23 | 2016-02-11 19:23 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 0 | Pungut OCB fdr #2 T/R 1x. Not checked yet. | 3290615 | 1 | 19:23 | Night | Thursday | 2016 | 2
4537 | 2016-02-11 19:23 | 2016-03-11 16:20 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Pungut OCB fdr #2 T/R 1x Ctr: 346-347 R/F: 51N. Patrolled the line & found, @3 broken Dead end Insulator o/p #44BX-02. Cause: Lightning. | 3290615 | 1 | 19:23 | Night | Thursday | 2016 | 2
4538 | 2016-02-11 19:30 | 2016-02-11 19:30 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 107 | 19:30 4D fdr #2 Load dropped 108A (148-40A). 23:13 It was reported no Power, some Wells were off at under Recl. 4D-204. Checked & found, Recl. 4D-204 (4D fdr #2) T/SO. Ctr: 18-19. Block & closed Recl. 4D-204, Ok. Then released the Block. Patrolled the Line, but found nothing. Cause: Suspected by Lightning. | 3290620 | 1 | 19:30 | Night | Thursday | 2016 | 2
4539 | 2016-02-11 19:51 | 2016-02-11 19:51 | 4.16KV NO RUMBAI FEEDER #2 | Rain and Lightning | Tree | 0 | 19:51 North Rumbai 4160V VCB fdr #2 T/LO. Ctr: 337-341 R/F: 51N & 51@1,@2. Patrolled the Line & found, Fall down trees touching to @1 conductor o/p #P2-RA.3. (Then Isolated its the Tree) 21:35 Blocked & Closed No.Rumbai VCB fdr #2, Ok. Then released the Block. Cause: Tree. | 3290629 | 1 | 19:51 | Night | Thursday | 2016 | 2
4540 | 2016-02-11 22:20 | 2016-02-11 22:20 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | 22:20 It Was reported No Power at Road-M3 Area-9. (C.Duri fdr #1) 03-Nov-2016 00:00 Checked & found, Recl. 09-M3-01 (C.Duri fdr #1) T/SO. Ctr: 74-75. Blocked & Closed Recl. 09-M3-01, Ok. then released the block. The line is not patrolled yet. | 3290633 | 1 | 22:20 | Night | Thursday | 2016 | 2
4541 | 2016-02-11 22:20 | 2016-04-11 07:00 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3290633 | 1 | 22:20 | Night | Thursday | 2016 | 2
4542 | 2016-02-11 23:48 | 2016-02-11 23:48 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Bangko fdr #4 Load dropped 180A (246-66A). Not checked yet. | 3290638 | 1 | 23:48 | Night | Thursday | 2016 | 2
4543 | 2016-02-11 23:48 | 2016-04-11 14:30 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 140-141. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3290638 | 1 | 23:48 | Night | Thursday | 2016 | 2
4544 | 2016-02-11 23:48 | 2016-02-11 23:48 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 21 | Bangko fdr #1 Load dropped 187A (221-34A). Not checked yet. | 3290634 | 1 | 23:48 | Night | Thursday | 2016 | 2
4545 | 2016-02-11 23:48 | 2016-04-11 14:30 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 21 | Checked & found, Recl. 23X-08 (Bangko fdr #1) T/R 1x Ctr: 369-370 R/F: 50@1,@2. Patrolled the line & found, @1,@2 broken L/As o/p #24Y-09. Cause: Lightning. | 3290634 | 1 | 23:48 | Night | Thursday | 2016 | 2
4546 | 2016-02-11 23:52 | 2016-02-11 23:52 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Lightning | 0 | C.Duri ACB fdr #7 T/R 1x Ctr: 468-469 R/F: 51N. Not Patrolled yet. | 3290631 | 1 | 23:52 | Night | Thursday | 2016 | 2
4547 | 2016-02-11 23:52 | 2016-04-11 06:57 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Lightning | 0 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3290631 | 1 | 23:52 | Night | Thursday | 2016 | 2
4548 | 2016-03-11 00:26 | 2016-03-11 00:26 | 13.8KV NORTH DURI FEEDER #11 | Rain and Lightning | Lightning | 0 | N.Duri VCB fdr #11 T/R 1x. Not checked yet. | 3290641 | 1 | 0:26 | Night | Friday | 2016 | 3
4549 | 2016-03-11 00:26 | 2016-05-11 07:40 | 13.8KV NORTH DURI FEEDER #11 | Rain and Lightning | Lightning | 0 | Checked & found, N.Duri VCB fdr #11 T/R 1x Ctr: 148-149 R/F: 51N. Patrolled the Line & found, @2,@3 broken L/As o/p #11-J2-19. Cause: Lightning. | 3290641 | 1 | 0:26 | Night | Friday | 2016 | 3
4550 | 2016-03-11 01:38 | 2016-03-11 01:38 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 25 | Nella VCB fdr #2 T/R 1x. Nella GFPC T/R 1x. Not checked yet. | 3290645 | 1 | 1:38 | Night | Friday | 2016 | 3
4551 | 2016-03-11 01:38 | 2016-04-11 10:30 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 25 | Checked & found, Nella VCB fdr #2 T/R 1x Ctr: 708-709 R/F: 50@3. Patrolled the Line, but found nothing. Cause: Suspected by Lightning. | 3290645 | 1 | 1:38 | Night | Friday | 2016 | 3
4552 | 2016-03-11 02:23 | 2016-03-11 02:23 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 0 | Sintong fdr #1 Load dropped 40A (90-50A). Not checked yet. | 3290642 | 1 | 2:23 | Night | Friday | 2016 | 3
4553 | 2016-03-11 02:23 | 2016-04-11 07:15 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 25AD-26 (Sintong fdr #1) T/R 1x Ctr: 109-110. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3290642 | 1 | 2:23 | Night | Friday | 2016 | 3
4554 | 2016-03-11 17:55 | 2016-03-11 17:55 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 107 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 17:55 | Afternoon | Friday | 2016 | 3
4555 | 2016-03-11 17:55 | 2016-05-11 18:48 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 107 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 219-220 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified |  | 1 | 17:55 | Afternoon | Friday | 2016 | 3
4556 | 2016-04-11 23:59 | 2016-04-11 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system is normal condition. |  | 1 | 23:59 | Night | Monday | 2016 | 4
4557 | 2016-05-11 06:30 | 2016-05-11 06:30 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | N.Duri VCB fdr #5 T/R 1x. Not checked yet. | 3291930 | 1 | 6:30 | Morning | Wednesday | 2016 | 5
4558 | 2016-05-11 06:30 | 2016-06-11 13:44 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | Checked & found, N.Duri VCB fdr #5 T/R 1x Ctr: 108-109 R/F: 51N. Patrolled the Line, but found nothing. Cause: Unidentified. | 3291930 | 1 | 6:30 | Morning | Wednesday | 2016 | 5
4559 | 2016-05-11 12:19 | 2016-05-11 12:19 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 0 | Bangko fdr #4 Load drop 100A (246-146). Bangko GFPC T/R 1x. Not checked yet. | 3291931 | 1 | 12:19 | Afternoon | Wednesday | 2016 | 5
4560 | 2016-05-11 12:19 | 2016-06-11 14:32 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 0 | Checked & found, Recl. 25Z-07 (Bangko fdr #4) T/R 1x Ctr: 141-142. Patrolled the line & found, @1 broken Pin Insulator o/p #27Y-40. Cause: Pin Insulator. | 3291931 | 1 | 12:19 | Afternoon | Wednesday | 2016 | 5
4561 | 2016-05-11 18:46 | 2016-05-11 18:46 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 8 | Menggala fdr#1 Load dropped 43A(184-141A) Menggala GFPC TX T/R 1x. Not checked yet | 3291935 | 1 | 18:46 | Afternoon | Wednesday | 2016 | 5
4562 | 2016-05-11 18:46 | 2016-06-11 14:40 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 8 | Patrolled & found, Recl. 19AO-01 (Menggala fdr #1) T/R 1x Ctr: 460-461. Repatrolled the line, but found nothing. Cause: Unidentified. | 3291935 | 1 | 18:46 | Afternoon | Wednesday | 2016 | 5
4563 | 2016-05-11 22:30 | 2016-05-11 22:30 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 28 | 22:30 It was reported b/o fuse for Tx o/p #08-M3-16. (C.Duri fdr #2). Nov 06,2016. 09:30 Checked and found @3 b/o fuse for 112.5 Kva Tx o/p 08-M3-16. Replaced b/o fuse above with same size and energized the TX. Cause: Animal (Monkey). | 3291971 | 1 | 22:30 | Night | Wednesday | 2016 | 5
4564 | 2016-06-11 08:40 | 2016-06-11 08:40 | MINAS POWER PLANT |  |  | - | 08:40 S/U MGT #5, then on line the Unit at 08:52. (Due to S/D CGT #5 for replacing Diverter Gear box of HRSG-5) |  | 1 | 8:40 | Morning | Saturday | 2016 | 6
4565 | 2016-06-11 11:05 | 2016-06-11 11:05 | CENTRAL DURI POWER PLANT |  |  | - | 11:05 Off line CGT #5, then S/D the Unit for S/B. (Replacing Diverter Gear box of HRSG-5) |  | 1 | 11:05 | Morning | Saturday | 2016 | 6
4566 | 2016-07-11 03:51 | 2016-07-11 03:51 | 230KV NORTH DURI SWITCH YARD | Cloudy | Under investigation | 0 | 03:51 230KV N.Duri GCB #11 T/O. Ctr: 87-88 R/F: 86B. 230KV N.Duri GCB #21 T/O. Ctr: 120-121. 230KV N.Duri GCB #31 T/O. Ctr: 122-123. 230KV N.Duri GCB #41 T/O. Ctr: 175-176. (230KV N.Duri BUS-2 No power) 230KV N.Duri GCB #43 T/O. Ctr: 177-178 R/F: 86T. 115KV N.Duri GCB #3 T/O. (230KV Power TX-5 Tripped) 05:59 Reset Relay 86T then closed 230KV N.Duri GCB #41, but failed. Closed 230KV N.Duri GCB #41, but failed. 15:00 Re-checked 230KV N.Duri TX-5 & 230KV N.Duri Bus-2 & found, normal. Switching to Normalize 230KV N.Duri TX-5 & 230KV N.Duri Bus-2. 15:36 Closed 230KV GCB #43, Ok. (230KV N.Duri TX-5 energized) 16:00 Opened 115KV C.Duri GCB #53 & GCB #55. (at C.Duri Switchyard) 16:02 Closed 115KV N.Duri GCB #3, Ok. (115KV N.Duri - CDSY line energize from N.Duri Substation) Adjusting LTC of 230KV N.Duri TX-5. (to leveling voltage between CDSY & N.Duri Subst.) 16:13 Closed 115KV C.Duri GCB #53 & #55, Ok. (115KV N.Duri-CDSY line energized) 16:24 Closed 230KV GCB #11, Ok. 16:25 Closed 230KV GCB #31, Ok. Closed 230KV GCB #21, Ok. 16:26 Closed 230KV GCB #41, Ok. (230KV N.DUri TX-5 & 230KV N.Duri Bus-2 back to normal) Cause: Under Investigation. | 3292390 | 1 | 3:51 | Night | Monday | 2016 | 7
4567 | 2016-07-11 14:58 | 2016-07-11 14:58 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 26 | Sintong fdr #2 Load dropped 25A (191-166). Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #2) Not checked yet. | 3292317 | 1 | 14:58 | Afternoon | Monday | 2016 | 7
4568 | 2016-07-11 14:58 | 2016-10-11 07:30 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 26 | Checked & found, Recl. 28AF-02 (Sintong fdr #2) T/R 1x Ctr: 631-632. Also found, Sintong GFPC T/R 2x Ctr: 924-926. Patrolled the line, but found nothing. Cause: Unidentified. | 3292317 | 1 | 14:58 | Afternoon | Monday | 2016 | 7
4569 | 2016-07-11 17:04 | 2016-07-11 17:04 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 29 | Pungut OCB fdr #2 T/R 1x. Not checked yet. | 3292323 | 1 | 17:04 | Afternoon | Monday | 2016 | 7
4570 | 2016-07-11 17:04 | 2016-08-11 13:57 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 29 | Checked & found, Pungut OCB fdr #2 T/R 1x Ctr: 347-348 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3292323 | 1 | 17:04 | Afternoon | Monday | 2016 | 7
4571 | 2016-07-11 17:12 | 2016-07-11 17:12 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 20 | CKBS VCB fdr #1 T/R 1X. CKBS fdr #2 Load dropped 238A (248-10A). CKBS fdr #3 Load dropped 113A (122-19A). Not checked yet. | 3292325 | 1 | 17:12 | Afternoon | Monday | 2016 | 7
4572 | 2016-07-11 17:12 | 2016-09-11 17:00 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 20 | Checked & found, CKBS VCB fdr #1 T/R 1x Ctr: 217-218 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3292325 | 1 | 17:12 | Afternoon | Monday | 2016 | 7
4573 | 2016-07-11 17:30 | 2016-07-11 17:30 | 115KV DURI - KOTABATAK JUNCTION LINE | Rain and Lightning | Lightning | 0 | 115KV KBJ GCB #43 T/R 1x. 115KV KBJ GCB #45 T/R 1x. 115KV Duri GCB #26 T/R 1x. 115KV Duri GCB #28 T/R 1x. (115KV Line Duri - KBJ T/R 1x) Not checked yet. | 3292397 | 1 | 17:30 | Afternoon | Monday | 2016 | 7
4574 | 2016-07-11 17:30 | 2016-08-11 13:51 | 115KV DURI - KOTABATAK JUNCTION LINE | Rain and Lightning | Lightning | 0 | Checked & found: -115KV DRB GCB #26 T/R 1x Ctr: 914-915. -115KV DRB GCB #28 T/R 1x Ctr: 169-170 R/F: 87L(@1,@3). Patrolled the line from DRB toward KBJ line & found, @1,@3 F/O Dead end Insulators o/p #DK-54. Cause: Lightning. -115KV KBJ GCB #43 & GCB #45 are not checked yet. 115KV KBJ toward DRB line is not patrolled yet. 11-Nov-2016. Checked & found: -115KV KBJ GCB #43 T/R 1x Ctr: 420-421. -115KV KBJ GCB #45 T/R 1x Ctr: 303-304 R/F: 87L-@1, 21@1,@2 & 67N (Inst). Patrollled line from KBJ toward Duri line, bu found nothing. Cause: Lightning. | 3292397 | 1 | 17:30 | Afternoon | Monday | 2016 | 7
4575 | 2016-07-11 17:53 | 2016-07-11 17:53 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain and Lightning | Animal | 0 | 17:53 4.16KV Dumai fdr #4 Load dropped 66A (66-2A). 18:30 Checked & found, Recl. H33-08 (Dumai fdr #4) T/LO. Ctr: 103-105. Patrolled the line & found, a dead Monkey hang the conductor o/p #H70-02. (Then removed the dead Monkey above) 19:22 Blocked & closed Recl. H33-08, Ok. Then released the block. Cause: Animal. (Monkey) |  | 1 | 17:53 | Afternoon | Monday | 2016 | 7
4576 | 2016-07-11 18:00 | 2016-07-11 18:00 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Broken Fuse Cut Out | 0 | 18:00 It was reported b/o fuse for Tx o/p #03-06-16R. (For 3SC & 3SW Test Station) 00:10 Checked & found, @1, @3 b/o 14.0SF fuses for 500Kva Tx o/p #03-06-16B. Also found, @1, @3 broken FCOs. Nov 08,2016. 11:10 Replaced @1 & @3 broken FCOs. Energized 500 Kva Transformer. Cause: Broken FCO. | 3292374 | 1 | 18:00 | Afternoon | Monday | 2016 | 7
4577 | 2016-08-11 03:27 | 2016-08-11 03:27 | 230KV NORTH DURI SWITCH YARD | Drizzle | Under investigation | 0 | 03:27 230KV N.Duri GCB #11 T/O. Ctr: 288-289 230KV N.Duri GCB #21 T/O. Ctr: 121-122 230KV N.Duri GCB #31 T/O. Ctr: 122-123 230KV N.Duri GCB #41 T/O. Ctr: 159-160 (230KV N.Duri BUS-2 No power) R/F: 86 Bus-2, 86 (at GCB #41), 50BF (at GCB #41) 230KV N.Duri GCB #43 T/O. Ctr: 179-180 115KV N.Duri GCB #3 T/O. Ctr: 131-132 (230KV Power TX-5 Tripped) 05:30 Visually checked 230KV N.Duri Bus-2, found Normal. Visually checked 230KV N.Duri TX-5, found Transformer Oil leakage at the bottom of Bushing-3. (WTI= 90 deg C; LTI: 50 deg C) Cause: Under Investigation. | 3292713 | 1 | 3:27 | Night | Thursday | 2016 | 8
4578 | 2016-08-11 09:16 | 2016-08-11 09:16 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri ACB fdr #16 T/R 1x Ctr: 294-295 R/F: 51@1,@2. Not patrolled yet. | 3292728 | 1 | 9:16 | Morning | Thursday | 2016 | 8
4579 | 2016-08-11 09:16 | 2016-10-11 19:40 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3292728 | 1 | 9:16 | Morning | Thursday | 2016 | 8
4580 | 2016-08-11 13:25 | 2016-08-11 13:25 | 13.8KV BATANG FEEDER #1 | Fair | Lightning Arrester | 0 | 13:25 Batang OCB fdr #1 T/R 1x. 14:06 Batang OCB fdr #1 T/R 1x. 18:06 Batang OCB fdr #1 T/R 1x again. 18:11 It was reported a spark at Structure of Batang Substation. 20:58 Checked & found, Batang OCB fdr #1 T/R 2x Ctr: 126-128 R/F: 51@1 & 50@1. Also found, @2, @3 broken LAs for Batang OCB fdr #1 on Structure of Batang SS. Also found, LA jumpers near to ground. Decided to Shutdown Batang SS to isolate broken LAs & Jumpers. 21:58 Batang OCB fdr #1 T/R 1x again. 23:14 Manual opened 115KV Batang-C/S. Installed personal ground. 23:39 Isolated broken LAs & its Jumpers above. Removed personal ground. 23:40 Manual opened Batang OCB fdr #1, #2, #3. 23:42 Closed 115KV Batang-C/S. 23:43 Blocked & closed Batang OCB fdr #3, Ok. Then released the block. 23:44 Blocked & closed Batang OCB fdr #2, Ok. Then released the block. 23:45 Blocked & closed Batang OCB fdr #1, Ok. Then released the block. Batang SS back to normal. Cause: Broken Lightning Arrester. | 3292743 | 1 | 13:25 | Afternoon | Thursday | 2016 | 8
4581 | 2016-08-11 13:45 | 2016-08-11 13:45 | 13.8KV BATANG FEEDER #3 | Fair | Transformer Failure | 64 | 13:45 It was reported b/o fuse for Tx at Well Pemburu #20. (Batang fdr #3) 17:24 Checked & found, @1,@3 b/o 3.5SF fuses for 150Kva Tx at Well Pemburu #20. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx failure. (Low megger reading) (This Tx is not replaced yet) | 3292746 | 1 | 13:45 | Afternoon | Thursday | 2016 | 8
4582 | 2016-08-11 13:45 | 2016-09-11 15:23 | 13.8KV BATANG FEEDER #3 | Fair | Transformer Failure | 64 | Replaced 150Kva Tx failure with the same size & energized the Tx at Well Pemburu #20. Cause: Transformer Failure. | 3292746 | 1 | 13:45 | Afternoon | Thursday | 2016 | 8
4583 | 2016-08-11 14:06 | 2016-08-11 14:06 | BATANG SUBSTATION | Fair | Lightning Arrester | 180 | 14:06 Batang 115 KV Circuit Switcher T/O. (No power at Batang Substation). 15:05 Checked and found: 1. 115KV Batang-C/S T/O. Ctr: 144-145 R/F: 51NT. 2. 13.8KV Batang OCB fdr #1 T/R 2x Ctr: 126-128 R/F: 51@1 & 50@1. 15:14 Manually opened Batang VCB fdr #1. 15:14 Manually opened Batang VCB fdr #2. 15:14 Manually opened Batang VCB fdr #3. 15:16 Reset Relay 86T. 15:16 Manually closed 115KV Batang-C/S, but failed. Continued check the Substation. 15:35 Manually closed 115KV Batang-C/S --> Ok. 15:35 Blocked & closed Batang OCB fdr #2, Ok. Then released the block. Ctr: 131-132. 15:36 Blocked & closed Batang OCB fdr #3, Ok. Then released the block. Ctr: 333-334. Patrolled the line at downstream of Batang fdr #1, but found nothing. 15:45 Blocked & closed Batang OCB fdr #1, Ok. Then released the block. Ctr: 128-129. Batang Substation back to normal. 18:06 Batang OCB fdr #1 T/R 1x again. 18:11 It was reported a spark at Structure of Batang Substation. 20:58 Checked & found, @2, @3 broken LAs for Batang VCB fdr #1 on Structure of Batang SS. Also found, LA jumpers near to ground. Decided to Shutdown Batang SS to isolate broken LAs & Jumpers. 21:58 Batang OCB fdr #1 T/R 1x again. 23:14 Manual opened 115KV Batang-C/S. Installed personal ground. 23:39 Isolated broken LAs & its Jumpers above. Removed personal ground. 23:40 Manual opened Batang OCB fdr #1, #2, #3. 23:42 Closed 115KV Batang-C/S. 23:43 Blocked & closed Batang OCB fdr #3, Ok. Then released the block. 23:44 Blocked & closed Batang OCB fdr #2, Ok. Then released the block. 23:45 Blocked & closed Batang OCB fdr #1, Ok. Then released the block. Batang SS back to normal. Cause: Broken Lightning Arrester. | 3292754 | 1 | 14:06 | Afternoon | Thursday | 2016 | 8
4584 | 2016-09-11 17:36 | 2016-09-11 17:36 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 270 | 17:36 Sintong fdr #2 Load dropped 148A (191-43A). (Pagar-GS no power) 18:18 Manually Opened Sintong OCB fdr #2. (Req. by Bangko-GS) 18:24 Manually Closed Sintong OCB fdr #2. Checked & found, Recl. 28AF-17 (Sintong fdr #2) T/SO. Ctr: 434-435. (Found indicator Malfunction on the Recloser control) 20:37 Manually opened Sintong OCB fdr #2. (to close Bypass Switches of Recl. 28AF-17) 20:41 Blocked & Sintong OCB fdr #2, Ok. Then released the block. (Pagar-GS back to normal) (The line is not patrolled yet) | 3293119 | 1 | 17:36 | Afternoon | Sunday | 2016 | 9
4585 | 2016-09-11 17:36 | 2016-12-11 12:36 | 13.8KV SINTONG FEEDER #2 | Cloudy and Lightning | Lightning | 270 | Checked & found, Recl. 28AF-17 (Sintong fdr #1) T/SO. Ctr: 434-435. Patrolled the line, but found Nothing. Cause: Suspected by Lightning. (also appear alarm Recloser control malfunction) | 3293119 | 1 | 17:36 | Afternoon | Sunday | 2016 | 9
4586 | 2016-10-11 10:02 | 2016-10-11 10:02 | CENTRAL DURI SWITCH YARD | Fair | Under investigation | 1234 | 10:02 115Kv CDSY GCB #10 T/O. (Tie Bus#1 & #2), then Closed at 10:25. 115Kv CDSY GCB #21 T/O. then closed at 10:27. 115Kv CDSY GCB #25 T/O. then closed at 10:27. 115Kv CDSY GCB #20 T/O. (Tie Bus#3 & #4), then Closed at 10:25. 115Kv CDSY GCB #41 T/O. then closed at 10:55. 115Kv CDSY GCB #45 T/O. then closed at 12:51. (C.Duri CDSY Power Tx-3 Tripped & 115KV CDSY BUS-2 & BUS-4 no power) (When MTC team functioning test realy-86T & 86HR of Power Tx-4 at CDSY) (13.8KV CDSG BUS-3 & BUS-4 independen & fed by CGT #4) Nella fdr #1 Load dropped 198A (268-70A). Prod Loss : 132 Bbls / 2 wells. Bangko fdr #1 Load dropped 197A (197-0A). Prod Loss : 334 Bbls / 75 wells. Bangko fdr #2 Load dropped 227A (227-0A). Prod Loss : - Bbls / - wells. Bangko fdr #3 Load dropped 214A (214-0A). Prod Loss : - Bbls / - wells. Bangko fdr #4 Load dropped 257A (254-0A). Prod Loss : 63 Bbls / 36 wells. Sintong fdr #1 Load dropped 10A (84-74A). Prod Loss : 49 Bbls / 3 wells. Sintong fdr #2 Load dropped 25A (149-124A). Prod Loss : 89 Bbls / 5 wells. Menggala fdr #1 Load dropped 48A (185-137A). Prod Loss : 67 Bbls / 4 wells. Ketigul fdr #2 load dropped 51A 204-153A). Prod Loss : - Bbls / - wells. Pematang fdr #1 load drooped 18A (157-139A). Prod Loss : 41 Bbls / 22 wells. Pematang fdr #2 load drooped 32A (53-21A). Prod Loss : 32 Bbls / 21wells. Rangau fdr #1 load dropped 24A (24-0A). Prod Loss : - Bbls / - wells. Rangau fdr #2 load dropped 85A (86-1A). Prod Loss : 48 Bbls / 18 wells. Petani fdr #1 load dropped 106A (110-4A). Prod Loss : - Bbls / - wells. Petani fdr #2 load dropped 13A (42-29A). Prod Loss : - Bbls / - wells. 10:02 115KV MSU-2 C/S T/O. Then closed at 10:21. 10:09 Open 13.8KV MSU-2 VCB fdr #1, then closed at 10:22. Prod Loss : 86 Bbls / 91 wells. 10:09 Open 13.8KV MSU-2 VCB fdr #1, then closed at 10:22. Prod Loss : 293 Bbls / 113 wells. --------------------------------------- + Grand total = 1234 Bbls / 390 wells. 10:54 Open Generator Breaker ACB #46 of CGT #4, then S/D the unit. (13.8KV CDSG BUS-3 & BUS-4 no power) 10:55 Closed 115KV CDSY GCB #41. (13.8KV CDSG BUS-3 & BUS-4 energized) 11:35 S/U CGT #4, then on line the Unit at 11:55. Cause: Under Investigation. | 3293440 | 1 | 10:02 | Morning | Tuesday | 2016 | 10
4587 | 2016-10-11 11:00 | 2016-10-11 11:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 743 | 11:00 Do Switching to S/D Ketigul VCB fdr #2. 11:15 Open Ketigul VCB fdr #2 & Its both side isolation SW. (for Pagar fields) 11:18 Open LBS #29AL-07. (for Ubi & Sikeladi Fileds) 13:30 Closed Ketigul VCB fdr #2. (Pagar fields energized & S/U the wells) 16:32 Closed LBS #20AL-07. (Ubi & Sikeladi field energized & S/U all the wells) For some event: Installing new Recl. 29AL-03. Squeeze jumper of Dead-end Ex VR on pole #29AL-17. Replacing Recl. 27AL-21 & Recl. 26AK-02 for Schedule service. Replacing Pin insulator with post type Insulators. (61 pcs) Repainting electric pole. (14 poles) Cause: Maintenance Job. | 3257964 | 1 | 11:00 | Morning | Tuesday | 2016 | 10
4588 | 2016-10-11 16:54 | 2016-10-11 16:54 | 13.8KV NORTH DURI FEEDER #2 | Fair | Animal | 11 | 16:54 It was reported b/o fuse for Tx o/p #10-J4-02. (N.Duri fdr #2) 18:10 Checked & found, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #10-J4-02. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Snake) | 3293446 | 1 | 16:54 | Afternoon | Tuesday | 2016 | 10
4589 | 2016-10-11 19:08 | 2016-10-11 19:08 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified (Fuse) | 67 | 19:08 It was reported b/o fuse for Tx at Well Pematang #57. (Pematang fdr #1) 21:18 Checked & found, @1 b/o 14.0SF fuse for 500Kva Tx at Well Pematang #57. Performed TTR, Megger test the Tx & found, good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (fuse). | 3293461 | 1 | 19:08 | Night | Tuesday | 2016 | 10
4590 | 2016-10-11 22:10 | 2016-10-11 22:10 | 13.8KV KOTABATAK FEEDER #2 | Fair | Lightning Arrester | 33 | OKBS OCB fdr #2 T/R 1x. Not checked yet. | 3293469 | 1 | 22:10 | Night | Tuesday | 2016 | 10
4591 | 2016-10-11 22:10 | 13/11/2016 08:10 | 13.8KV KOTABATAK FEEDER #2 | Fair | Lightning Arrester | 33 | Checked & found, OKB OCB fdr #2 T/R 1x Ctr: 1298-1299 R/F: 51@1,@2,@3. Patrolled the line & found, @1,@2,@3 broken L/As o/p #38CX-11. Cause: Lightning Arrester. | 3293469 | 1 | 22:10 | Night | Tuesday | 2016 | 10
4592 | 2016-10-11 22:12 | 2016-10-11 22:12 | CENTRAL DURI POWER PLANT |  |  | - | 22:12 Off line CGT #2, then S/D the Unit at 22:20. (for S/B-Prior to installing BTU Analyzer) |  | 1 | 22:12 | Night | Tuesday | 2016 | 10
4593 | 2016-11-11 09:56 | 2016-11-11 09:56 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 09:56 It was reported b/o fuse for Tx o/p #01-7-25E. (D.Field fdr #4) 10:40 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #01-7-25E. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3294654 | 1 | 9:56 | Morning | Friday | 2016 | 11
4594 | 2016-11-11 10:50 | 2016-11-11 10:50 | CENTRAL DURI POWER PLANT |  |  | - | 10:50 S/U CGT #5, then on line the Unit at 11:10. |  | 1 | 10:50 | Morning | Friday | 2016 | 11
4595 | 2016-11-11 11:45 | 2016-11-11 11:45 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 11:45 It was reported b/o fuse for Tx at Well KB #409. (CKBS fdr #5) 14:45 Checked & found, @1 b/o 7.8SF fuse for 250Kva Tx at Well KB #409. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 3294659 | 1 | 11:45 | Morning | Friday | 2016 | 11
4596 | 2016-11-11 14:15 | 2016-11-11 14:15 | DURI POWER PLANT |  |  | - | Off line DGT #7, then S/D the Unit for S/B. (Running on test) |  | 1 | 14:15 | Afternoon | Friday | 2016 | 11
4597 | 2016-12-11 06:30 | 2016-12-11 06:30 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Duri Community ACB fdr #1 T/R 1x Ctr: 91-92 R/F: 51N. Not patrolled yet. | 3294670 | 1 | 6:30 | Morning | Sunday | 2016 | 12
4598 | 2016-12-11 06:30 | 13/11/2016 08:30 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 3294670 | 1 | 6:30 | Morning | Sunday | 2016 | 12
4599 | 2016-12-11 10:30 | 2016-12-11 10:30 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Animal | 0 | 10:30 It was reported b/o fuse for Tx o/p #03-6-14. (C.Duri fdr #5) 11:45 Checked & found, @2 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-6-14. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) | 3294674 | 1 | 10:30 | Morning | Sunday | 2016 | 12
4600 | 2016-12-11 10:50 | 2016-12-11 10:50 | CENTRAL DURI POWER PLANT |  |  | - | 10:50 S/U CGT #2, then on line the Unit at 13:20. 11:20 Open ACB #39. (Tie Breaker) |  | 1 | 10:50 | Morning | Sunday | 2016 | 12
4601 | 2016-12-11 14:00 | 2016-12-11 14:00 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT #1, the S/D the Unit for S/B. (Prior to installing HRSG-1 Gear box) 14:06 Closed ACB #39. (Tie Breaker) 22-Nov-2016. 17:00 S/U CGT #1, the On line the Unit 17:50. (after some repair of HRSG-1 & replacing HRSG-1 Gearbox) |  | 1 | 14:00 | Afternoon | Sunday | 2016 | 12
4602 | 2016-12-11 14:42 | 2016-12-11 14:42 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 106 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. | 3294677 | 1 | 14:42 | Afternoon | Sunday | 2016 | 12
4603 | 2016-12-11 14:42 | 16/11/2016 09:00 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 106 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 921-922 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 3294677 | 1 | 14:42 | Afternoon | Sunday | 2016 | 12
4604 | 2016-12-11 17:40 | 2016-12-11 17:40 | 13.8KV MINAS FEEDER #3 | Fair | Animal | 0 | 17:40 It was reported no Power at WDR office Minas. 18:45 Checked & found, @3 b/o 7.0SF fuse for 3x75Kva Tx at WDR Office. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal. (Monkey) | 3294679 | 1 | 17:40 | Afternoon | Sunday | 2016 | 12
4605 | 2016-12-11 19:32 | 2016-12-11 19:32 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Unidentified | 85 | NKBS VCB fdr #3 T/R 1x. NKBS-GFPC T/R 1x. Not checked yet. | 3294680 | 1 | 19:32 | Night | Sunday | 2016 | 12
4606 | 2016-12-11 19:32 | 14/11/2016 13:30 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Unidentified | 85 | Checked & found, NKBS OCB fdr #3 T/R 1x Ctr: 279-280 R/F: 51@1. Patrolled the line, but found nothing. Cause: Unidentified. | 3294680 | 1 | 19:32 | Night | Sunday | 2016 | 12
4607 | 2016-11-13 23:59 | 2016-11-13 23:59 | CPI POWER SYSTEM | Rain | Normal Condition | - | CPI Power system is normal condition. |  | 1 | 23:59 | Night | Sunday | 2016 | 11
4608 | 2016-11-14 23:59 | 2016-11-14 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system is normal condition. |  | 1 | 23:59 | Night | Monday | 2016 | 11
4609 | 2016-11-15 09:50 | 2016-11-15 09:50 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified | 7 | 09:50 It was reported b/o fuse for Tx o/p #04-08-11. (C.Duri fdr #9) 13:23 Checked & found, @1,@2 broken Fuse Holder & fuse link for 112.5Kva Tx. Perform TTR & Megger, the result was good reading. Replaced the Holder and fuses above with the same size & energized the Tx. Cause: Unidentified. |  | 1 | 9:50 | Morning | Tuesday | 2016 | 11
4610 | 2016-11-15 10:16 | 2016-11-15 10:16 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified (Fuse) | 308 | 10:16 Petani fdr #1 Load dropped 60A (195-135A). 11:00 It was reported @1,@2,@3 b/o fuses for 3.75MVA TX at Petani-GS. (HWP Pump was Off) 11:08 Manually Open Petani OCB fdr #2. (to anticipate spill at Petani-GS) 13:30 Perform TTR, Megger test the Tx & found, good reading. Then replaced b/o fuse above with the same size. 14:30 Energized 3.75Mva Tx. Re-Checked the Tx to ensure its normal condition, then S/U Petani-GS HWP Pump, Ok. 14:37 Manually Closed Petani OCB fdr #2. Cause: Unidentified (Fuse). |  | 1 | 10:16 | Morning | Tuesday | 2016 | 11
4611 | 2016-11-15 11:27 | 2016-11-15 11:27 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 11:27 C.Duri fdr #1 load dropped 30A (144-114A). 16:25 C.Duri fdr #1 load dropped 67A (144-77A). Not checked yet. |  | 1 | 11:27 | Morning | Tuesday | 2016 | 11
4612 | 2016-11-15 11:27 | 2016-11-23 08:25 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 242-243. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 11:27 | Morning | Tuesday | 2016 | 11
4613 | 2016-11-15 16:20 | 2016-11-15 16:20 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Animal | 7 | 6D fdr #1 Load dropped 166A (255-89A). 4D fdr # 4 load dropped 15A (217-202A). 6DN fdr #4 Load dropped 64A (135-71A). Not checked yet. |  | 1 | 16:20 | Afternoon | Tuesday | 2016 | 11
4614 | 2016-11-15 16:20 | 2016-11-18 06:10 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Animal | 7 | Checked & found, Recl. 5C-42 (6D fdr #1) T/R 1x Ctr: 22-23. Patrolled the line & found, a dead Bird on the Recl. 5C-42. (Then removed its Bird) Cause: Animal. (Bird) |  | 1 | 16:20 | Afternoon | Tuesday | 2016 | 11
4615 | 2016-11-15 16:20 | 2016-11-15 16:20 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 78 | 16:20 5B fdr #4 Load dropped 177A (237-60A). 22:44 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO. Ctr: 185-186. Blocked & closed Recl. 4B-73, Ok. Then released the block. The line is not patrolled yet. |  | 1 | 16:20 | Afternoon | Tuesday | 2016 | 11
4616 | 2016-11-15 16:20 | 2016-11-16 23:15 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 78 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:20 | Afternoon | Tuesday | 2016 | 11
4617 | 2016-11-15 21:38 | 2016-11-15 21:38 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Lightning | 0 | 44KV N.Duri GCB #44 (44KV N.Duri - Dumai line) T/R 1x. Not checked yet. |  | 1 | 21:38 | Night | Tuesday | 2016 | 11
4618 | 2016-11-15 21:38 | 2016-11-23 08:35 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Lightning | 0 | Checked & found, 44KV N.Duri GCB #44 (Line to Dumai) T/R 1x Ctr: 109-110 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 21:38 | Night | Tuesday | 2016 | 11
4619 | 2016-11-16 08:05 | 2016-11-16 08:05 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Darling VCB fdr #7 T/R 1x Ctr: 152-153 R/F: 51@1,@2. Darling GFPC-TX #2 T/R 1x Ctr: 202-203. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 8:05 | Morning | Wednesday | 2016 | 11
4620 | 2016-11-16 13:30 | 2016-11-16 13:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 2 | 13:30 -14:30 S/D Well Puncak #08. (C.Duri fdr #1) Replaced broken L/A o/p #38AS-09 . Cause: Maintenance Job. |  | 1 | 13:30 | Afternoon | Wednesday | 2016 | 11
4621 | 2016-11-16 17:35 | 2016-11-16 17:35 | 115KV KOTABATAK JUNCTION - 4B LINE | Rain and Lightning | Lightning | 152 | 17:35 115Kv Line KBJ-4B GCB#33 T/SO, Ctr:240-241, R/F:21 @1. 115Kv Line KBJ-4B GCB#35 T/SO, Ctr:216-217, . 115Kv Line KBJ-4B OCB#21 T/SO, Ctr:241-242, R/F:67N, R/F:21 @1. (115KV KBJ - 4B line) Respectively Load dropped: 3D fdr#2 Load dropped 111A (206-95A). 3D fdr#3 Load dropped 33A (145-112A). 3D fdr#4 Load dropped 95A (210-115A). 3D fdr#7 Load dropped 116A (177-61A). 3D fdr#8 Load dropped 11A (86-75A). 4D fdr#2 Load dropped 59A (141-92A). 4D fdr#4 Load dropped 32A (202-170A). 5B fdr#4 Load dropped 46A (222-176A). 5B fdr#1 Load dropped 24A (92-68A). 5B fdr#2 Load dropped 41A (162-121A). 6DN fdr#4 Load dropped 64A (228-164A). OKB fdr#2 Load dropped 135A (230-95A). NKB fdr#3 Load dropped 78A (146-68A). CKB fdr#1 Load dropped 161A (293-132A). CKB fdr#3 Load dropped 65A (123-58A). CKB fdr#5 Load dropped 155A (365-210A). CKB fdr#6 Load dropped 145A (220-75A). Petapahan fdr#1 Load dropped 32A (860-54A). Petapahan fdr#2 Load dropped 152A (191-39A). So.Bek fdr#1 Load dropped 23A (175-152). Libo fdr#1 Load dropped 35A (91-56A). Libo fdr#2 Load dropped 22A (43-21A). Bangko fdr#1 Load dropped 35A (205-170A). Balam MSU-2 fdr#1 Load dropped 47A (204-157A). Balam MSU-2 fdr#2 Load dropped 130A (288-158A). (Ferquency System Raise up to 60.85Hz) 16:36 MGT#1 Manually Open Gen. Breaker, then Closed at 17:48. 17:41 MGT#6 Manually Open Gen. Breaker, then Closed at 17:49. 17:45 MGT#8 Manually Open Gen. Breaker, then Closed at 17:58. Cause : Under Investigation |  | 1 | 17:35 | Afternoon | Wednesday | 2016 | 11
4622 | 2016-11-16 17:35 | 2016-11-19 09:19 | 115KV KOTABATAK JUNCTION - 4B LINE | Rain and Lightning | Lightning | 152 | Checked & found: -115KV 4B OCB #21 T/SO. Ctr: 241-242 R/F: 67N. -115KV KBJ GCB #33 T/SO. Ctr: 240-241 R/F: 21@2. -115KV KBJ GCB #35 T/SO. Ctr: 216-217. (115KV KBJ-4B Line T/SO) Patrolled the Line & found, @2 F/O Deadend Insulator o/p #K4B-20. Cause: Lightning. |  | 1 | 17:35 | Afternoon | Wednesday | 2016 | 11
4623 | 2016-11-16 18:21 | 2016-11-16 18:21 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 35 | 4B OCB fdr #1 T/R 2x. Not checked yet. |  | 1 | 18:21 | Afternoon | Wednesday | 2016 | 11
4624 | 2016-11-16 18:21 | 2016-11-19 19:30 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 35 | Checked & found, 4B OCB fdr #1 T/R 1x Ctr: 291-292 R/F: 51@2. Patrolled the line & found, @2 broken Pin Insulator o/p #K4B-04. Cause: Lightning. |  | 1 | 18:21 | Afternoon | Wednesday | 2016 | 11
4625 | 2016-11-16 19:01 | 2016-11-16 19:01 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 10 | Libo OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 19:01 | Night | Wednesday | 2016 | 11
4626 | 2016-11-16 19:01 | 2016-11-17 14:00 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 10 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 410-411 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 19:01 | Night | Wednesday | 2016 | 11
4627 | 2016-11-17 09:46 | 2016-11-17 09:46 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Powerline - Hot Line Clamp | 4 | 09:46 Its was reported b/o fuse for Tx at Well Kulin #61. (C.Duri fdr #1) 10:30 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Kulin #61. (also found Loss Connection jumper on TP of Well above). Not replaced yet. (W/O bucket truck for this Job) |  | 1 | 9:46 | Morning | Thursday | 2016 | 11
4628 | 2016-11-17 09:46 | 2016-11-19 10:40 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Powerline - Hot Line Clamp | 4 | Replaced b/o fuse above with the same size & energized the Tx at Well Kulin #61. (after Fixing @1,@2 Loss connection HLC jumpers o/p #40AW-30) Cause: HLC Jumpers. |  | 1 | 9:46 | Morning | Thursday | 2016 | 11
4629 | 2016-11-17 14:45 | 2016-11-17 14:45 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 4 | 14:45 It was reported b/o fuse for Tx o/p #04-03-13. (C.Duri fdr #9) 16:30 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-03-13. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 14:45 | Afternoon | Thursday | 2016 | 11
4630 | 2016-11-18 16:40 | 2016-11-18 16:40 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 68 | 16:40 It was reported b/o fuse for Tx at Well BKO #230. (Bangko fdr #4) 17:26 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well BKO #230. Perform TTR & Megger test, the result was Low reading. Cause: Tx Failure. (Low Megger reading) (The Tx failure is not replaced yet) |  | 1 | 16:40 | Afternoon | Friday | 2016 | 11
4631 | 2016-11-18 16:40 | 2016-11-19 11:00 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 68 | Replaced 150Kva Tx failure with the same size at Well Bko #230, the energized the Tx. Cause: Tx failure. (Low Megger reading) |  | 1 | 16:40 | Afternoon | Friday | 2016 | 11
4632 | 2016-11-18 18:55 | 2016-11-18 18:55 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 12 | It was reported b/o fuse for Tx at Well Sintong #48. (Sintong fdr #2) Not checked yet. |  | 1 | 18:55 | Afternoon | Friday | 2016 | 11
4633 | 2016-11-18 18:55 | 2016-11-19 09:00 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 12 | Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Sintong #48. Replaced b/o fuse above with the same & energized the Tx. Cause: Animal. (Bird) |  | 1 | 18:55 | Afternoon | Friday | 2016 | 11
4634 | 2016-11-19 14:35 | 2016-11-19 14:35 | 13.8KV 4B FEEDER #6 | Fair | Planned Maintenance | 9 | 14:35-16:00 S/D some Wells (4B-22, 4B-32, 4B-43, 4B-44, 4B-51, 4B-61). (4B fdr #6) To fixing @3 broken HLC On TP of Well #4B-61. Cause: Planed maintenance. |  | 1 | 14:35 | Afternoon | Saturday | 2016 | 11
4635 | 2016-11-20 10:47 | 2016-11-20 10:47 | 13.8KV LIBO FEEDER #2 | Fair | Animal | 5 | Libo OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 10:47 | Morning | Sunday | 2016 | 11
4636 | 2016-11-20 10:47 | 2016-11-21 09:00 | 13.8KV LIBO FEEDER #2 | Fair | Animal | 5 | Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 428-429 R/F: 51N. Patrolled the line & found, a dead Eagle hung on @2 conductor o/p #29BY-07. Cause: Animal. (Eagle) |  | 1 | 10:47 | Morning | Sunday | 2016 | 11
4637 | 2016-11-20 21:25 | 2016-11-20 21:25 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 56 | Petani OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 21:25 | Night | Sunday | 2016 | 11
4638 | 2016-11-20 21:25 | 2016-11-23 14:45 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 56 | Checked & found, Petani OCB fdr #1 T/R 1x Ctr: 149-150 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 21:25 | Night | Sunday | 2016 | 11
4639 | 2016-11-21 21:35 | 2016-11-21 21:35 | 13.8KV 3D FEEDER #5 | Rain and Lightning | Lightning | 0 | 3D OCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 21:35 | Night | Monday | 2016 | 11
4640 | 2016-11-21 21:35 | 24/11/2016 10:33 | 13.8KV 3D FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, 3D OCB fdr #5 T/R 1x Ctr: 617-618 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 21:35 | Night | Monday | 2016 | 11
4641 | 2016-11-22 05:40 | 2016-11-22 05:40 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Dead End Insulator | 0 | C.Duri ACB fdr #6 T/R 1x Ctr: 448-449 R/F: 51N. Not patrolled yet. |  | 1 | 5:40 | Morning | Tuesday | 2016 | 11
4642 | 2016-11-22 05:40 | 24/11/2016 07:30 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Dead End Insulator | 0 | Patrolled the line & found, @3 F/O Dead end Insulator o/p #01-1-11. Cause: Dead end Insulator. |  | 1 | 5:40 | Morning | Tuesday | 2016 | 11
4643 | 2016-11-22 10:00 | 2016-11-22 10:00 | BATANG SUBSTATION | Fair | Planned Maintenance | 637 | 10:00 Manually opened 115KV Batnag C/S. (at Batang Subtation) 16:55 Manually closed 115KV Batang C/S. (at Batang Subtation) With some events: -Changed out some broken insulators at D/S of Batang fdr #1, #2 & #3. -Changed out 13.8Kv broken L/As at Outgoing of Batang fdr #1, #2 & #3. (on the Structure) -Changed out 115Kv incoming L/A Leakage current meter. -Performed several test & Refill Nitt. of Power Tx & VR at Batang Substation. Cause: Plan maintenance. | 1111 | 1 | 10:00 | Morning | Tuesday | 2016 | 11
4644 | 2016-11-22 16:45 | 2016-11-22 16:45 | 13.8KV DURI FIELD FEEDER #1 | Fair | Transformer Failure | 9 | 16:45 It was reported b/o fuse for Tx o/p #01-04-32. (D.Field fdr #1) 18:01 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-04-32. Replaced b/o fuse above with the same, then energized the Tx. 18:05 The fuse Burnt out again & found, Tx failure. Cause: Tx failure. (The Tx failure is not replaced yet) |  | 1 | 16:45 | Afternoon | Tuesday | 2016 | 11
4645 | 2016-11-22 16:45 | 2016-11-23 11:40 | 13.8KV DURI FIELD FEEDER #1 | Fair | Transformer Failure | 9 | Replaced 112.5Kva Tx failure with the same size & energized the Tx o/p #01-04-32. Cause: Tx failure. |  | 1 | 16:45 | Afternoon | Tuesday | 2016 | 11
4646 | 2016-11-22 17:00 | 2016-11-22 17:00 | CENTRAL DURI POWER PLANT |  |  | - | 17:00 S/U CGT #1, the On line the Unit 17:50. (after some repair & replacing of HRSG-1 Gearbox ) | 1111 | 1 | 17:00 | Afternoon | Tuesday | 2016 | 11
4647 | 2016-11-22 17:44 | 2016-11-22 17:44 | 13.8KV 6DN FEEDER #5 | Fair | Planned Maintenance | 0 | 17:44-19:22 Manually open 6DN OCB fdr #5, due to WIP problem at Minas GS-3. (Its requested by Minas GS-3 operator, to anticipate spill) Cause: Planned maintenance. (Prod. loss is not charged to PGT) | 11111 | 1 | 17:44 | Afternoon | Tuesday | 2016 | 11
4648 | 2016-11-22 21:00 | 2016-11-22 21:00 | MINAS POWER PLANT |  |  | - | 21:00 Off line MGT #4, then S/D the Unit for S/B. (Prior to repairing Atomizing compressor drain Line) |  | 1 | 21:00 | Night | Tuesday | 2016 | 11
4649 | 2016-11-23 11:42 | 2016-11-23 11:42 | 13.8KV DURI FIELD FEEDER #2 | Fair | Secondary Cable | 4 | 11:42 It was reported broken Scondary cable of Tx o/p #06-S3-09. 16:16 Checked & found, @1 broken Secondary Bushing of 112.5Kva Tx o/p #06-S3-09. Replaced broken Secondary Bushing of Tx above, then energized the Tx. Cause: Scondary Buhing Tx. (Bushing broken) | 1111 | 1 | 11:42 | Morning | Wednesday | 2016 | 11
4650 | 2016-11-23 14:35 | 2016-11-23 14:35 | MINAS POWER PLANT |  |  | - | 14:35 Off line MGT #1, then S/D the Unit for S/B. |  | 1 | 14:35 | Afternoon | Wednesday | 2016 | 11
4651 | 2016-11-23 21:03 | 2016-11-23 21:03 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 54 | Menggala OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 21:03 | Night | Wednesday | 2016 | 11
4652 | 2016-11-23 21:03 | 24/11/2016 11:00 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 54 | Checked & found, Menggala OCB fdr #1 T/R 1x Ctr: 304-305 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 21:03 | Night | Wednesday | 2016 | 11
4653 | 2016-11-23 22:48 | 2016-11-23 22:48 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 0 | MSU-2 fdr #2 (Balam fdr #3 & #4) Load dropped 273A (323-50A). MSU-2 fdr #1 (Balam fdr #1 & #2) Load dropped 54A (179-125A). T/O WIP at Balam-GS. Not checked yet. |  | 1 | 22:48 | Night | Wednesday | 2016 | 11
4654 | 2016-11-23 22:48 | 24/11/2016 14:00 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 16AA-08 (MSU-2 fdr #2) T/R 1x Ctr: 71-72. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 22:48 | Night | Wednesday | 2016 | 11
4655 | 2016-11-24 09:39 | 2016-11-24 09:39 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri Community ACB fdr #2 T/R 1x Ctr: 75-76 R/F: 51N. Not patrolled yet. |  | 1 | 9:39 | Morning | Thursday | 2016 | 11
4656 | 2016-11-24 09:39 | 2016-11-27 19:25 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 9:39 | Morning | Thursday | 2016 | 11
4657 | 2016-11-24 18:07 | 2016-11-24 18:07 | CENTRAL DURI SWITCH YARD | Fair | Under investigation | 0 | 115KV CDSY GCB #65 T/O. (on block position)\ (Running on test no load) Not checked yet. | 11111 | 1 | 18:07 | Afternoon | Thursday | 2016 | 11
4658 | 2016-11-24 18:07 | 2016-11-26 19:19 | CENTRAL DURI SWITCH YARD | Fair | Under investigation | 0 | Checked & found: 115KV CDSY GCB #65 T/O. Ctr: 140-141 R/F: 87T(@2,@3). Checked The Tx & found normal. Cause: Under Investigation. (Under Test the Tx & protection Relay) | 11111 | 1 | 18:07 | Afternoon | Thursday | 2016 | 11
4659 | 2016-11-25 01:24 | 2016-11-25 01:24 | 13.8KV 6D FEEDER #5 | Drizzle | Pin Insulator | 20 | 01:24 6D OCB fdr #5 T/R 1x. 09:30 Checked & found, 6D OCB fdr #5 T/R 1x Ctr: 735-736 R/F: 51N. Patrolled the line & found, @1 broken Pin Insulator o/p #6D-504. Cause: Pin Insulator. |  | 1 | 1:24 | Night | Friday | 2016 | 11
4660 | 2016-11-25 15:20 | 2016-11-25 15:20 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Lightning | 31 | Pungut OCB fdr #1 T/R 3x. Not checked yet. | 11111 | 1 | 15:20 | Afternoon | Friday | 2016 | 11
4661 | 2016-11-25 15:20 | 2016-11-26 15:36 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Lightning | 31 | Checked & found, Pungut OCB fdr #1 T/R 3x Ctr: 352-355 R/F: 50N. Patrolled the line & found: -@1,@2 F/O Pin insulators o/p #45BP-29. -@2 Broken Dead end Insulator o/p #45BP-31. Cause: Lightning. | 11111 | 1 | 15:20 | Afternoon | Friday | 2016 | 11
4662 | 2016-11-25 15:36 | 2016-11-25 15:36 | 13.8KV NORTH DURI FEEDER #6 | Cloudy and Lightning | Lightning | 0 | N.Duri VCB fdr #6 T/R 1x. N.Duri GFPC-TX #... Not checked yet. | 11111 | 1 | 15:36 | Afternoon | Friday | 2016 | 11
4663 | 2016-11-25 15:36 | 2016-11-27 15:27 | 13.8KV NORTH DURI FEEDER #6 | Cloudy and Lightning | Lightning | 0 | Checked & found, N.Duri VCB fdr #6 T/R 1x Ctr: 293-294 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 11111 | 1 | 15:36 | Afternoon | Friday | 2016 | 11
4664 | 2016-11-25 16:18 | 2016-11-25 16:18 | 115KV DURI - PUNGUT LINE | Rain and Lightning | Lightning | 0 | 115KV DRB OCB #21 T/R 1x. 115KV DRB OCB #29 T/R 1x. 115KV Pungut OCB #21 T/R 1x. (115KV DRB - Pungut line) Not checked yet. | 11111 | 1 | 16:18 | Afternoon | Friday | 2016 | 11
4665 | 2016-11-25 16:18 | 2016-11-27 16:10 | 115KV DURI - PUNGUT LINE | Rain and Lightning | Lightning | 0 | Checked & found: 115KV DRB OCB #21 T/R 1x Ctr: 244-245. 115KV DRB OCB #29 T/R 1x Ctr: 203-204 R/F: 67N (Inst) & 21@1(Z-1). 115KV Pungut OCB #21 T/R 1x Ctr: 626-627 R/F: 67N (Inst), 87L@1 & 21@1 (Z-1) (115KV DRB - Pungut Line) Patrolled the line, but found nothing. Cause: Supected by Lightning. | 11111 | 1 | 16:18 | Afternoon | Friday | 2016 | 11
4666 | 2016-11-25 16:18 | 2016-11-25 16:18 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 35 | Pungut OCB fdr #2 T/R 1x. Not checked yet. | 11111 | 1 | 16:18 | Afternoon | Friday | 2016 | 11
4667 | 2016-11-25 16:18 | 2016-11-28 07:20 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 35 | Checked & found, Pungut OCB fdr #2 T/R 1x Ctr: 348-349 R/F: 51N. Patrolled the line & found, @3 broken Dead end Insulator o/p #45BC-12. Cause: Lightning. | 11111 | 1 | 16:18 | Afternoon | Friday | 2016 | 11
4668 | 2016-11-26 03:08 | 2016-11-26 03:08 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Bangko fdr #4 Load dropped 98A (248-150A). Bangko GFPC T/R 2x. (Ground fault alarm at Bangko fdr #4) Not checked yet. |  | 1 | 3:08 | Night | Saturday | 2016 | 11
4669 | 2016-11-26 03:08 | 2016-11-29 08:22 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Checked All Recloser at downstream of Bangko fdr #4 & found, normal. (Counter did not operate) Patrolled the line, but found nothing. Cause: Unidentified. (Suspected T/O Shipping Pump at Benar-GS) |  | 1 | 3:08 | Night | Saturday | 2016 | 11
4670 | 2016-11-26 15:13 | 2016-11-26 15:13 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 41 | 15:13 Batang OCB fdr #3 T/R 1X. 15:15 Batang OCB fdr #3 T/R 1X. 15:29 Batang OCB fdr #3 T/R 1X. Not checked yet. | 11111 | 1 | 15:13 | Afternoon | Saturday | 2016 | 11
4671 | 2016-11-26 15:13 | 2016-11-29 16:10 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 41 | Checked & found, Batang OCB fdr #3 T/R 3x Ctr: 337-340 R/F: 51@1,@3. Patrolled the line & found: -@1 Broken L/A jumper o/p #40AJ-11. -@3 Broken L/A jumper o/p #37AL-12. Cause: Lightning. | 11111 | 1 | 15:13 | Afternoon | Saturday | 2016 | 11
4672 | 2016-11-26 19:58 | 2016-11-26 19:58 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Rangau OCB fdr #2 T/R 1x. Not checked yet. Checked Rangau OCB fdr #2 & found, Normal. (No Relay flag & Counter did not operate) Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 3x Ctr: 180-183. Patrolled the line, but found nothing. Cause: Suspected by Lightning. (Also see report on 28 Nov 2016 at 17:27) |  | 1 | 19:58 | Night | Saturday | 2016 | 11
4673 | 2016-11-27 15:02 | 2016-11-27 15:02 | 13.8KV CENTRAL KOTABATAK FEEDER #3 | Fair | Unidentified | 85 | CKBS VCB fdr #3 T/R 1x. CKBS fdr #1 Load dropped 286A (317-31A). CKBS fdr #2 Load dropped 232A (248-16A). Not checked yet. | 1111 | 1 | 15:02 | Afternoon | Sunday | 2016 | 11
4674 | 2016-11-27 15:02 | 2016-11-28 13:12 | 13.8KV CENTRAL KOTABATAK FEEDER #3 | Fair | Unidentified | 85 | Checked & found, CKBS VCB fdr #3 T/R 1x Ctr: 97-98 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 1111 | 1 | 15:02 | Afternoon | Sunday | 2016 | 11
4675 | 2016-11-27 16:00 | 2016-11-27 16:00 | 13.8KV CENTRAL KOTABATAK FEEDER #3 | Fair | Transformer Failure | 116 | 16:00 It was reported b/o fuse for Tx at Well KB #390. 16:15 Checked & found, @1 b/o 14.0SF fuse for 550Kva Tx at Well KB #390. Performed TTR, Megger test the Tx & found, Low Megger reading. Cause: Tx Failure. (Low Megger Reading) (This Tx is not replaced yet) | 11111 | 1 | 16:00 | Afternoon | Sunday | 2016 | 11
4676 | 2016-11-27 16:00 | 2016-11-29 15:30 | 13.8KV CENTRAL KOTABATAK FEEDER #3 | Fair | Transformer Failure | 116 | Replaced 550Kva Tx failure with the same size & energized the Tx at Well KB #390. Cause: Tx Failure. | 11111 | 1 | 16:00 | Afternoon | Sunday | 2016 | 11
4677 | 2016-11-27 18:19 | 2016-11-27 18:19 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Rain and Lightning | Lightning | 114 | MSU-2 fdr #2 (So.Balam fdr #3 & fdr #4) Load dropped 285A (325-40A). MSU-2 fdr #1 (So.Balam fdr #1 & fdr #2) Load dropped 150A (184-34A). Not checked yet. | 11111 | 1 | 18:19 | Afternoon | Sunday | 2016 | 11
4678 | 2016-11-27 18:19 | 2016-02-12 07:32 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Rain and Lightning | Lightning | 114 | Checked & found, MSU-2 VCB fdr #2 T/R 1x Ctr: 72-73 R/F: Not appear. Patrolled the line, but found nothing. Cause: Suspected by Lightning. Checked Recloser at downstream of MSU-2 fdr #1 & found, no Recloser installing at the line. Cause: Suspected T/O WIP at So.Balam-GS, due to voltage dip. (When MSU-2 VCB fdr #2 T/R) | 11111 | 1 | 18:19 | Afternoon | Sunday | 2016 | 11
4679 | 2016-11-27 19:12 | 2016-11-27 19:12 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 102 | Nella VCB fdr #1 T/R 1x. Nella-GFPC T/R 1x. Not checked yet. |  | 1 | 19:12 | Night | Sunday | 2016 | 11
4680 | 2016-11-27 19:12 | 2016-11-29 17:00 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 102 | Checked & found, Nella VCB fdr #1 T/R 1x Ctr: 497-498 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 19:12 | Night | Sunday | 2016 | 11
4681 | 2016-11-27 19:13 | 2016-11-27 19:13 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 0 | So.Bekasap fdr #1 Load dropped 77A (172-95A). Not checked yet. |  | 1 | 19:13 | Night | Sunday | 2016 | 11
4682 | 2016-11-27 19:13 | 2016-11-28 16:05 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 34BI-18 (So.Bekasap fdr #1) T/R 1x Ctr: 156-167. Patrolled the line & found, @3 F/O Dead end Insulator o/p #33BH-12. Cause: Lightning. |  | 1 | 19:13 | Night | Sunday | 2016 | 11
4683 | 2016-11-27 20:14 | 2016-11-27 20:14 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Lightning | 0 | N.Duri VCB fdr #8 T/R 1x. N.Duri GFPC-Tx #.... T/R 1x. Not checked yet. |  | 1 | 20:14 | Night | Sunday | 2016 | 11
4684 | 2016-11-27 20:14 | 2016-11-29 12:40 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Lightning | 0 | Checked & found, N.Duri VCB fdr #8 T/R 1x Ctr: 78-79 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 20:14 | Night | Sunday | 2016 | 11
4685 | 2016-11-27 20:45 | 2016-11-27 20:45 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 43 | Bekasap VCB fdr #6 T/R 1x. Not checked yet. |  | 1 | 20:45 | Night | Sunday | 2016 | 11
4686 | 2016-11-27 20:45 | 2016-11-29 16:00 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 43 | Checked & found, Bekasap Main OCB fdr #6 T/R 1x Ctr: 345-346 R/F: 51@1,@2. Patrolled the line & found: -@1 F/O Pin Insulator o/p #38BE-05. -@1 Broken Pin Insulator o/p #39BE-16. -@2 Broken Dead end Insulator o/p #NN. (Near Well Aman #10) Cause: Lightning. |  | 1 | 20:45 | Night | Sunday | 2016 | 11
4687 | 2016-11-27 21:15 | 2016-11-27 21:15 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Lightning | 0 | C.Duri ACB fdr #7 T/R 1x Ctr: 469-470 R/F: 51@1. Not Patrolled yet. |  | 1 | 21:15 | Night | Sunday | 2016 | 11
4688 | 2016-11-27 21:15 | 2016-11-29 12:35 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Lightning | 0 | Patrolled the line & found, @3 broken L/A o/p #03-01-39. Cause: Lightning. |  | 1 | 21:15 | Night | Sunday | 2016 | 11
4689 | 2016-11-28 08:00 | 2016-11-28 08:00 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Unidentified (Fuse) | 1 | 08:00 It was reported b/o fuse for Tx at Well KB #298. 14:40 Checked & found, @2 b/o 15K fuse for 300Kva Tx at Well KB #298. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 8:00 | Morning | Monday | 2016 | 11
4690 | 2016-11-28 08:45 | 2016-11-28 08:45 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 08:45 It was reported b/o fuse for Tx o/p #03-03-40. 14:53 Checked & found, @3 b/o 2.1SF fuse for 112.5Kva Tx o/p #03-03-40. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 8:45 | Morning | Monday | 2016 | 11
4691 | 2016-11-28 11:07 | 2016-11-28 11:07 | 13.8KV NORTH DURI FEEDER #9 | Fair | Transformer Failure | 0 | 11:07 It was reported b/o fuse for Tx o/p #10-J6-21. Not checked yet. |  | 1 | 11:07 | Morning | Monday | 2016 | 11
4692 | 2016-11-28 11:07 | 2016-11-30 11:00 | 13.8KV NORTH DURI FEEDER #9 | Fair | Transformer Failure | 0 | Replaced 112.5Kva Tx with the same size o/p 10-J6-21, then energized Tx. Cause: Transformer Failure. |  | 1 | 11:07 | Morning | Monday | 2016 | 11
4693 | 2016-11-28 12:50 | 2016-11-28 12:50 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Tree | 0 | 12:50 C.Duri fdr #8 Load dropped 20A (206-186A). 14:20 Checked & found, Recl. 04-05-32 (C.Duri fdr #8) T/LO. Ctr: 134-138. Patrolled the line & found, fall down Tree & touching to Powerline o/p #04-05-22A. (Then clearing its the Tree) 15:38 Blocked & closed Recl. 03-05-32, Ok. Then released the block. Cause: Tree. |  | 1 | 12:50 | Afternoon | Monday | 2016 | 11
4694 | 2016-11-28 14:00 | 2016-11-28 14:00 | 13.8KV KOTABATAK FEEDER #2 | Fair | Animal | 24 | 14:00 It was reported b/o fuse for Tx at Well KB #358. 14:45 Checked & found, @1 b/o 15K fuse for 300Kva Tx at Well KB #358. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Mouse) |  | 1 | 14:00 | Afternoon | Monday | 2016 | 11
4695 | 2016-11-28 16:22 | 2016-11-28 16:22 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 42 | 3D OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 16:22 | Afternoon | Monday | 2016 | 11
4696 | 2016-11-28 16:22 | 2016-02-12 07:39 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 42 | Checked & found, 3D OCB fdr #2 T/R 1x Ctr: 226-227 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:22 | Afternoon | Monday | 2016 | 11
4697 | 2016-11-28 16:41 | 2016-11-28 16:41 | 44KV BEKASAP MAIN - SOUTH BEKASAP LINE | Rain and Lightning | Lightning | 39 | 44KV Bekasap OCB #2 (line to So.Bekasap Substation) T/R 1x. (So.Bekasap Substation No power) Not checked yet. |  | 1 | 16:41 | Afternoon | Monday | 2016 | 11
4698 | 2016-11-28 16:41 | 2016-11-29 16:15 | 44KV BEKASAP MAIN - SOUTH BEKASAP LINE | Rain and Lightning | Lightning | 39 | Checked & found: -44KV Bekasap Main OCB #2 (line to So.Bekasap Subst.) T/R 1x Ctr: 102-103 R/F: 51@1. Patrolled the line & found: -@1 Broken Dead end Insulator o/p #37BF-05. -High danger Trees & touching to power line near pole #SB-17. Cause: Lightning. |  | 1 | 16:41 | Afternoon | Monday | 2016 | 11
4699 | 2016-11-28 16:41 | 2016-11-28 16:41 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 0 | Bekasap Main fdr #2 Load dropped 111A (132-21A). Not checked yet. |  | 1 | 16:41 | Afternoon | Monday | 2016 | 11
4700 | 2016-11-28 16:41 | 2016-04-12 15:38 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 38BD-18 (Bekasap fdr #2) T/R 1x Ctr: 87-88. Patrolled the line & found, @1 broken L/A o/p #38BD-39. Cause: Lightning. |  | 1 | 16:41 | Afternoon | Monday | 2016 | 11
4701 | 2016-11-28 17:27 | 2016-11-28 17:27 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 27 | Rangau OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 17:27 | Afternoon | Monday | 2016 | 11
4702 | 2016-11-28 17:27 | 2016-11-30 17:27 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 27 | Checked Rangau OCB fdr #2 & found, Normal. (No Relay flag & Counter did not operate) Checked & found, Recl. 23BD-01 (Rangau fdr #2) T/R 3x Ctr: 180-183. Patrolled the line, but found nothing. Cause: Suspected by Lightning. (Also see report on 26 Nov 2016 at 19:58) |  | 1 | 17:27 | Afternoon | Monday | 2016 | 11
4703 | 2016-11-29 15:20 | 2016-11-29 15:20 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Secondary Cable | 13 | 15:20 It was reported b/o fuse for Tx at Well Ampuh #26. 18:56 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Ampuh #26. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size & energized the Tx. Cause: Secondary cable. |  | 1 | 15:20 | Afternoon | Tuesday | 2016 | 11
4704 | 2016-11-30 08:00 | 2016-11-30 08:00 | DURI POWER PLANT |  |  | - | 08:00 S/U DGT#7, then on line the Unit at 08:20. 20:07 Off Line DGT #7, then S/D the Unit at 20:08. (There was problem at Exhaust of DGT #7) |  | 1 | 8:00 | Morning | Wednesday | 2016 | 11
4705 | 2016-11-30 14:10 | 2016-11-30 14:10 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 31 | Batang OCB fdr #3 T/R 1x. Not checked yet. |  | 1 | 14:10 | Afternoon | Wednesday | 2016 | 11
4706 | 2016-11-30 14:10 | 2016-02-12 15:50 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 31 | Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 340-341 R/F: 51N. Patrolled the line & found: -@1 Broken L/A o/p #40AJ-11. -@3 Broken L/A o/p #37AL-12. Cause: Lightning. |  | 1 | 14:10 | Afternoon | Wednesday | 2016 | 11
4707 | 2016-11-30 15:41 | 2016-11-30 15:41 | 13.8KV 3D FEEDER #2 | Rain | Unidentified | 312 | 15:41 3D OCB fdr #2 T/LO. 17:00 Checked & found, 3D OCB fdr #2 T/LO. Ctr: 227-232 R/F: 51@2. Patrolled part of the line, but found nothing. 18:20 Open LBS #3E-64. 18:29 Blocked & closed 3D OCB fdr #2, Ok. Then release the block. (Will be continued tomorrow) Prod Loss = 239 Bbls / 23 Wells. ( GS #5 ). Prod loss = 25 Bbls / 6 Wells. ( GS #4 ). ------------------------ + Total = 264 Bbls / 29 Wells. |  | 1 | 15:41 | Afternoon | Wednesday | 2016 | 11
4708 | 2016-11-30 15:41 | 2016-01-12 10:45 | 13.8KV 3D FEEDER #2 | Rain | Unidentified | 312 | Patrolled the line, but found nothing Blocked 3D OCB fdr #2 & GFPC Tx-1. Closed LBS #3E-64, Ok. Then release the block. Cause: Unidentified. Prod Loss = 264 Bbls / 29 Wells. (On Nov. 30, 2016). Prod loss = 132 Bbls / 7 Wells. (On Dec. 01, 2016). ------------------------ + Total = 396 Bbls / 36 Wells. |  | 1 | 15:41 | Afternoon | Wednesday | 2016 | 11
4709 | 2016-01-12 07:56 | 2016-01-12 07:56 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified | 74 | CKBS VCB fdr #6 T/R 1x. No checked yet. |  | 1 | 7:56 | Morning | Tuesday | 2016 | 1
4710 | 2016-01-12 07:56 | 2016-05-12 13:24 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified | 74 | Checked & found, CKBS VCB fdr #6 T/R 1x Ctr: 138-139 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 7:56 | Morning | Tuesday | 2016 | 1
4711 | 2016-01-12 10:03 | 2016-01-12 10:03 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy and Lightning | Lightning | 71 | CKBS VCB fdr #5 T/R 1x. CKBS fdr #6 Load dropped 170A (192-22A). Not checked yet. |  | 1 | 10:03 | Morning | Tuesday | 2016 | 1
4712 | 2016-01-12 10:03 | 2016-05-12 13:22 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy and Lightning | Lightning | 71 | Checked & found, CKBS VCB fdr #5 T/R 1x Ctr: 144-145 R/F: 51@1,@2. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 10:03 | Morning | Tuesday | 2016 | 1
4713 | 2016-02-12 07:19 | 2016-02-12 07:19 | 13.8KV DARLING VCB FEEDER #3 | Cloudy and Lightning | Lightning | 0 | 07:19 Darling VCB fdr #3 T/R 1x. 19:10 Checked & found, Darling VCB fdr #3 T/R 1x Ctr: 243-244 R/F: 51N(@3). Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 7:19 | Morning | Friday | 2016 | 2
4714 | 2016-03-12 12:27 | 2016-03-12 12:27 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 12:27 C.Duri Tie Breaker ACB #39 T/O. CGT #4 Open Generator Breaker. C.Duri fdr #9 Load dropped 148A (148-0A). 12:29 Close C.Duri Tie Breaker ACB #39. 12:47 Close Generator Breaker CGT #4. Cause: Under investigation. |  | 1 | 12:27 | Afternoon | Saturday | 2016 | 3
4715 | 2016-03-12 13:20 | 2016-03-12 13:20 | 13.8KV SURAM FEEDER #2 | Fair | Accident | 17 | 13:20 Suram OCB fdr #2 T/SO. 14:00 Checked & found, Suram OCB fdr #2 T/LO. Ctr: 269-275 R/F: 51@2,@3. Patrolled the line & found, fall down Tree & hit to power line at in front of Suram-GS. (Also found, an Injury person due to hit by the falling down Tree above) The Victim had been sent to Hospital. 14:57 Blocked & closed, Suram OCB fdr #2, Ok. Then released the block. (After clearing the above Tree) Cause: Accident. (When the victim cutting the Tree & hit to power line also hit to him) |  | 1 | 13:20 | Afternoon | Saturday | 2016 | 3
4716 | 2016-03-12 13:29 | 2016-03-12 13:29 | 13.8KV DARLING VCB FEEDER #3 | Fair | Transformer Failure | 0 | 13:29 It was reported high voltage level of the Tx o/p #05-N5-06. 16:00 Checked & found, unbalance voltage of 112.5Kva Tx o/p #05-N5-06. (Then manual open fuses of the Tx o/p #05-N5-06) Cause: Tx Failure. (The Tx failure is not replaced yet) | 1111 | 1 | 13:29 | Afternoon | Saturday | 2016 | 3
4717 | 2016-03-12 13:29 | 2016-04-12 17:00 | 13.8KV DARLING VCB FEEDER #3 | Fair | Transformer Failure | 0 | 17:00 Replaced 112.5Kva TX o/p #05-N5-06 with same size and then energized the TX. ( d/s Darling fdr #3) Cause: Tx Failure. | 1111 | 1 | 13:29 | Afternoon | Saturday | 2016 | 3
4718 | 2016-04-12 14:35 | 2016-04-12 14:35 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 14:35 It was reported b/o fuse for Tx o/p #03-3-03. (C.Duri fdr #5) 15:15 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-3-03. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 14:35 | Afternoon | Tuesday | 2016 | 4
4719 | 2016-04-12 17:12 | 2016-04-12 17:12 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 17:12 It was reported b/o fuse for Tx at Polsek Mandau. (Duri Community fdr #2) 18:25 Checked & found, @3 b/o 2.1SF fuse for 100Kva Tx o/p #2F-15. (for Duri Polsek Mandau) Replaced b/o fuse above with the same size & energized the Tx o/p #2F-15. Cause: Unidentified (Fuse). |  | 1 | 17:12 | Afternoon | Tuesday | 2016 | 4
4720 | 2016-05-12 00:31 | 2016-05-12 00:31 | 13.8KV NORTH DURI GFPC | Fair | Unidentified | 0 | N.Duri GFPC-TX #13 T/R 1x. Ground fault alarm from N.Duri fdr #11. (No load dropped) Not checked yet. | 11111 | 1 | 0:31 | Night | Thursday | 2016 | 5
4721 | 2016-05-12 00:31 | 2016-08-12 17:51 | 13.8KV NORTH DURI GFPC | Fair | Unidentified | 0 | Checked & found, N.Duri GFPC-TX #13 T/R 3x Ctr: 90-93. Patrolled N.Duri fdr #11 line, but found nothing. Cause: Unidentified. | 11111 | 1 | 0:31 | Night | Thursday | 2016 | 5
4722 | 2016-05-12 01:11 | 2016-05-12 01:11 | 13.8KV BATANG FEEDER #3 | Fair | Dead End Insulator | 42 | 01:11 It was reported no power at Well Candi #2,3,11 & Candi #12. (Batang fdr #3) 03:20 Checked & found, Recl. 36AL-13 (Batang fdr #3) T/SO. Ctr : 121-122. Blocked & closed Recl. 36AL-13, Ok. Then released the block. 16:13 Patrolled the line & found, @1 broken Dead end Insulator o/p #35AK-15. Cause: Dead end Insulator. |  | 1 | 1:11 | Night | Thursday | 2016 | 5
4723 | 2016-05-12 01:22 | 2016-05-12 01:22 | 13.8KV NORTH DURI FEEDER #2 | Fair | Transformer Failure | 205 | 01:22 It was reported b/o fuse for Tx near pole #10-K6-38. (N.Duri fdr #2) 07:00 Checked & found: -@1,@2 b/o 50K fuses for 1000Kva Tx & @1 broken fuse holder. -Recl. 10-K4-41 (N.Duri fdr #2) T/R 3x. Ctr: 179-182. 07:30 Manually opened Recl. 10-K4-41. To replacing b/o fuse and fuse holder above with the same size. Blocked & closed Recl. 10-K4-41, but tripped again. Found @1,@2 b/o 50K fuses for 1000Kva Tx, then de energized 1000Kva Tx. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx failure (Low megger reading). 09:00 Blocked & closed Recl. 10-K4-41, Ok. (The Tx failure is not replaced yet) |  | 1 | 1:22 | Night | Thursday | 2016 | 5
4724 | 2016-05-12 01:22 | 2016-12-12 10:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Transformer Failure | 205 | Replaced 100Kva Tx failiure with the same size & energized the Tx atnear pole #10-K6-38 Cause: Tx failure. |  | 1 | 1:22 | Night | Thursday | 2016 | 5
4725 | 2016-05-12 12:40 | 2016-05-12 12:40 | 13.8KV PEMATANG FEEDER #1 | Fair | Low mega-ohm reading | 212 | 12:40 It was reported b/o fuse for Tx at Well Pematang #96. (Pematang fdr #1) 16:00 Checked & found, @1,@2 b/o 3.5SF Fuses for 150Kva Tx at Well Pematang #96 . Performed TTR & Megger, found Low megger reading. Cause: Tx Failure. (Low megger reading) (This Tx is not replaced yet) |  | 1 | 12:40 | Afternoon | Thursday | 2016 | 5
4726 | 2016-05-12 12:40 | 2016-06-12 10:55 | 13.8KV PEMATANG FEEDER #1 | Fair | Low mega-ohm reading | 212 | Replaced B/O 195Kva Tx with 150 Kv Tx at wellPematang #95 (Pematang fdr#1). Cause: Transformer Low Megger. |  | 1 | 12:40 | Afternoon | Thursday | 2016 | 5
4727 | 2016-05-12 16:37 | 2016-05-12 16:37 | CENTRAL DURI POWER PLANT |  |  | - | 16:37 S/U CGT #3, then online the Unit at 17:05 . (Running on test loaded 10MW & 5MVAR / after Major Overhaul) |  | 1 | 16:37 | Afternoon | Thursday | 2016 | 5
4728 | 2016-06-12 06:22 | 2016-06-12 06:22 | MINAS POWER PLANT | Fair | Under investigation | 0 | MGT #9 Trip By Alarm: Fire at Turbine & Accessories compartment. Cause: Under Investigation. Frequency dropped to 59,91Hz. (No load shedding) |  | 1 | 6:22 | Morning | Sunday | 2016 | 6
4729 | 2016-06-12 06:25 | 2016-06-12 06:25 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Transformer Failure | 115 | 06:25 It was reported b/o fuse for Tx o/p #09-R6-08. (C.Duri fdr #7) 09:20 Checked & found, @1, @2, @3 b/o 3.1SF fuses for 112.5Kva Tx o/p #09-R6-08. Performed TTR, Megger test the Tx & found, Low reading reading. Cause: TX Failure. (Low Megger reading) (Not replaced yet) |  | 1 | 6:25 | Morning | Sunday | 2016 | 6
4730 | 2016-06-12 06:25 | 2016-07-12 14:00 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Transformer Failure | 115 | Replaced 112.5Kva Tx failure with the same size & energized the Tx o/p #09-R6-08. Cause: Tx Failure. (Low megger reading) |  | 1 | 6:25 | Morning | Sunday | 2016 | 6
4731 | 2016-06-12 09:12 | 2016-06-12 09:12 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 09:12 CDGT #3 T/O. (While Troubleshooting load hunting / Switched off computer-S) Frequency drop to 59.87 Hz. (no load shedding) Cause: Under investigation 11:10 S/U CDGT #3, then online the Unit at 11:51. (after re-configure jumper of HSAA card) |  | 1 | 9:12 | Morning | Sunday | 2016 | 6
4732 | 2016-06-12 10:08 | 2016-06-12 10:08 | MINAS POWER PLANT |  |  | - | 10:08 S/U MGT #4, then online the Unit at 10:35 . |  | 1 | 10:08 | Morning | Sunday | 2016 | 6
4733 | 2016-06-12 11:30 | 2016-06-12 11:30 | MINAS POWER PLANT |  |  | - | 11:30 S/U MGT #2, then online the Unit at 12:37. |  | 1 | 11:30 | Morning | Sunday | 2016 | 6
4734 | 2016-07-12 06:24 | 2016-07-12 06:24 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | C.Duri fdr #2 Load dropped 112A (194-82A). Not checked yet. |  | 1 | 6:24 | Morning | Tuesday | 2016 | 7
4735 | 2016-07-12 06:24 | 2016-08-12 17:44 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recl. 08-M1-38 (C.Duri fdr #2) T/R 2x Ctr: 162-164. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 6:24 | Morning | Tuesday | 2016 | 7
4736 | 2016-07-12 07:01 | 2016-07-12 07:01 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | D.Field ACB fdr #1 T/R 1x. Not checked yet. |  | 1 | 7:01 | Morning | Tuesday | 2016 | 7
4737 | 2016-07-12 07:01 | 2016-11-12 10:07 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Checked & found, D.Field ACB fdr #1 T/R 1x Ctr: 984-985 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 7:01 | Morning | Tuesday | 2016 | 7
4738 | 2016-07-12 10:08 | 2016-07-12 10:08 | MINAS SWITCH YARD | Fair | Substation Failure (CB) | 1295 | 10:08 Switching to S/D 115KV MSY BUS-2. Opened 115KV MSY GCB #20. Opened 115KV MSY GCB #85. Opened 115KV MSY OCB #26. Opened 115KV MSY OCB #23. Opened 115KV MSY GCB #35. (115KV MSY BUS-2 No power) While performed Switching to S/D 115KV MSY Bus-2, to installing B30 relay. In the same time some load of 8C TX-1 & TX-2 were dropped. (when manually Open 115KV MSY GCB #26, line to 8C Substation) 8C fdr #1 Load dropped 188A (203-15A). 8C fdr #2 Load dropped 58A (78-20A). 8C fdr #3 Load dropped 188A (226-38A). 8C fdr #4 Load dropped 54A (293-239A). 8C fdr #5 Load dropped 116A (116-0A). 8C fdr #6 Load dropped 133A (158-25A). Checked & found, unbalance voltage of 13.8KV side at the fields. Cause: Suspected unbalance voltage at the outgoing of 115KV MSY OCB #22. 15:41 Closed 115KV MSY GCB #20. (115KV Tie BUS #1 & BUS-2) 15:46 Closed 115KV MSY GCB #26. (Line to 8C Substation) Re-Checked & found, 13.8KV side at the field are normal. (Balance voltage) 15:47 Closed 115KV MSY GCB #23, #35 & #85. (115KV MSY BUS-2 Back to normal) 15:48 Open 115KV MSY OCB #22. (to investigate the Breaker Unit & Its isolation Switch) Cause: Under Investigation. | 123 | 1 | 10:08 | Morning | Tuesday | 2016 | 7
4739 | 2016-07-12 10:15 | 2016-07-12 10:15 | MINAS POWER PLANT |  |  | - | 10:15 S/U MGT #1, then On Line the Unit at 10:35. Then open ACB #25 (Tie Breaker) |  | 1 | 10:15 | Morning | Tuesday | 2016 | 7
4740 | 2016-07-12 15:31 | 2016-07-12 15:31 | 13.8KV MINAS FEEDER #3 | Fair | Relay Failure | 45 | 15:31 Minas ACB fdr #3 T/SO. (On Block Status due to Rig Activity ACS-12) Checked & found, Minas ACB fdr #3 T/SO. Ctr: 80098-80099 R/F: 81. Also ensure Rig ACS-12 activity, its normal Operation . 16:35 Block & Closed Minas ACB fdr #3, but Tripped again. (by Same R/F) 16:45 Closed Minas ACB fdr #3, Ok. (After disabled 81 Relay) Cause: Under Investigation. (Suspected Relay 81 problem) |  | 1 | 15:31 | Afternoon | Tuesday | 2016 | 7
4741 | 2016-07-12 20:01 | 2016-07-12 20:01 | 13.8KV MINAS FEEDER #4 | Fair | Relay Failure | 352 | 20:01 Minas ACB fdr #4 T/O. Ctr: 64-65 R/F: 81. 20:12 Blocked & Closed Minas ACB fdr #4, Ok. 20:13 Minas ACB fdr #4 T/O again. Ctr: 65-66 R/F: 81. 20:16 Blocked & Closed Minas ACB fdr #4, Ok. 20:23 Minas ACB fdr #4 T/O again. Crt: 66-67 R/F: 81. 22:53 Blocked & closed Minas ACB fdr #4, Ok. Cause: Under Investigation. |  | 1 | 20:01 | Night | Tuesday | 2016 | 7
4742 | 2016-07-12 20:03 | 2016-07-12 20:03 | MINAS POWER PLANT |  |  | - | Off line MGT #1, the S/D the Unit for S/B. |  | 1 | 20:03 | Night | Tuesday | 2016 | 7
4743 | 2016-07-12 20:33 | 2016-07-12 20:33 | MINAS POWER PLANT | Fair | Under investigation | 0 | MGT #3 Tripped. (No alaram) Cause: Under Investigation. |  | 1 | 20:33 | Night | Tuesday | 2016 | 7
4744 | 2016-07-12 20:33 | 2016-07-12 20:33 | MINAS POWER PLANT | Fair | Under investigation | 0 | 20:33 MGT #2 Open Generator Breaker, then closed at 20:35. Cause: Under Investigation. |  | 1 | 20:33 | Night | Tuesday | 2016 | 7
4745 | 2016-08-12 08:00 | 2016-08-12 08:00 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Fair | Planned Maintenance | 0 | 08:00 Manual Open Recl. 16AA-08 (Balam fdr #4 /MSU-2 fdr #2). Production Team Replacing 6" Check Valve of Prod. Line & Shut down 26 Wells at So.Balam. 13:45 Manual Closed Recl. 16AA-08 (Balam fdr #4 /MSU-2 fdr #2). Cause: Planed Maintenance. | 123 | 1 | 8:00 | Morning | Friday | 2016 | 8
4746 | 2016-08-12 13:55 | 2016-08-12 13:55 | 13.8KV MINAS FEEDER #1 | Fair | Powerline - Conductor | 130 | 13:55 It was reported Broken Conductor and Laying down on the Ground & affected grass firring at near Old Kompleks Guru. 14:30 Checked & found, @1 broken Conductor o/p #7D-99. (Minas fdr #1) 15:05 Manual Open Minas ACB fdr #1, to isolate broken conductor above. 15:15 Open LBS #6D-96, then Closed Minas ACB fdr #1. Transferred part load of Minas fdr #1 to Minas fdr #3. 15:30 -Opened LBS #7D-23. -Closed LBS #7C-23. 16:35 -Open Recl 7D-20 -Closed LBS #7D-23. Cause: Conductor. |  | 1 | 13:55 | Afternoon | Friday | 2016 | 8
4747 | 2016-08-12 15:50 | 2016-08-12 15:50 | 115KV KETIGUL - MENGGALA | Fair | Lightning Arrester | 0 | 15:50 115KV Ketigul GCB #1 T/R 1x. 115KV Ketigul GCB #3 T/So. R/F: 21@1-G (Z-1) & 87L (@A). 115KV Menggala GCB #29 T/SO. R/F: 21@1-G (Z-1) & 87L (@A). (115KV Menggala - Ketigul line T/SO) 17:07 Manual Opened 115KV Ketigul GCB #1. (79C/O on DL) 17:09 Manual Closed 115KV Menggala GCB #29. (Selected 79 C/O to DL from SC) 17:13 Manual Closed 115KV Ketigul GCB #1. (Selected 79CO to SC from DL) 17:46 Manual Closed 115KV Ketigul GCB #3, but fail. (after resetting the Relay Flag) Selected 79CO of 115KV Ketigul GCB #2 to DL. 115KV Ketigul GCB #3 is not closed yet. (Being investigated) Patrolled the Line & found, @A broken L/A o/p #RM-84. Cause: Broken L/A. Note: 115KV Ketigul - Menggala line energized, but 115KV Ketigul GCB #3 is still in Open position. (Under Investigation) |  | 1 | 15:50 | Afternoon | Friday | 2016 | 8
4748 | 2016-08-12 15:55 | 2016-08-12 15:55 | MINAS POWER PLANT |  |  | - | 15:55 S/U MGT #3, then On Line the Unit at 16:07. |  | 1 | 15:55 | Afternoon | Friday | 2016 | 8
4749 | 2016-08-12 17:00 | 2016-08-12 17:00 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 42 | Pinang OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 17:00 | Afternoon | Friday | 2016 | 8
4750 | 2016-08-12 17:00 | 2016-09-12 17:23 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 42 | Checked & found, Pinang OCB fdr #1 T/R 1x Ctr: 411-412 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:00 | Afternoon | Friday | 2016 | 8
4751 | 2016-08-12 18:14 | 2016-08-12 18:14 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 0 | 18:14 Manually Open Minas ACB fdr #3. Requested by Minas GS-2 operator, due to Tank level to high. 20:12 Closed Minas ACB fdr #3. Cause: Planned Maintenance. |  | 1 | 18:14 | Afternoon | Friday | 2016 | 8
4752 | 2016-09-12 02:09 | 2016-09-12 02:09 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 83 | 02:09 Minas ACB fdr #1 T/LO. Ctr: 54-56 R/F: Not appear. 03:09 Blocked & closed Minas ACB fdr #1, Ok. Then release the block. Not patrolled yet. |  | 1 | 2:09 | Night | Monday | 2016 | 9
4753 | 2016-09-12 02:09 | 13/12/2016 04:21 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 83 | Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 2:09 | Night | Monday | 2016 | 9
4754 | 2016-09-12 07:12 | 2016-09-12 07:12 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 0 | Menggala fdr #1 Load dropped 40A (172-132A). Not checked yet. |  | 1 | 7:12 | Morning | Monday | 2016 | 9
4755 | 2016-09-12 07:12 | 2016-10-12 15:20 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 0 | Checked & found, Recl. 10AO-01 (Menggala fdr #1) T/R 1x Ctr: 464-465. Patrolled the line & found, a dead Monkey under TP of Well Meso #10. Cause: Animal. (Monkey) |  | 1 | 7:12 | Morning | Monday | 2016 | 9
4756 | 2016-09-12 07:44 | 2016-09-12 07:44 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri Community ACB fdr #2 T/R 1x. Not checked yet. |  | 1 | 7:44 | Morning | Monday | 2016 | 9
4757 | 2016-09-12 07:44 | 2016-11-12 17:00 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #2 T/R 1x Ctr: 76-77 R/F: 51@1. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 7:44 | Morning | Monday | 2016 | 9
4758 | 2016-09-12 09:07 | 2016-09-12 09:07 | CENTRAL DURI POWER PLANT |  |  | - | 09:07 Off line CGT#3, then S/D the Unit to inspect Generator Cyclone Filter. 10:57 Re-S/U CGT #3, then Online the Unit at 11:13. |  | 1 | 9:07 | Morning | Monday | 2016 | 9
4759 | 2016-09-12 11:00 | 2016-09-12 11:00 | MINAS SWITCH GEAR | Fair | Substation Failure (CB) | 0 | 11:00 It was reported Minas SWGR ACB #6 Open (for TX #1), By R/F: 51TN. (DSC indication CLOSE) 14:32 Manual Opened 115KV Minas GCB #21, to investigate & troubleshoot ACB #6 T/O. Cause: Under investigation. |  | 1 | 11:00 | Morning | Monday | 2016 | 9
4760 | 2016-09-12 15:12 | 2016-09-12 15:12 | MINAS POWER PLANT |  |  | - | 15:12 S/U MGT #1, then Online the Unit at 16:14. |  | 1 | 15:12 | Afternoon | Monday | 2016 | 9
4761 | 2016-09-12 18:00 | 2016-09-12 18:00 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Unidentified (Fuse) | 8 | 18:00 It was reported b/o fuse for Tx at Well Petapahan #63. (Petapahan fdr #2) 19:40 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well Petapahan #63. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 18:00 | Afternoon | Monday | 2016 | 9
4762 | 2016-10-12 08:30 | 2016-10-12 08:30 | 13.8KV S. BALAM FEEDER #4 | Fair | Animal | 36 | 08:30 It was reported b/o fuse for Tx at Well SO.Balam #324. (Balam fdr #4 / MSU-2 fdr #2) 09:26 Checked & found, @2 b/o 3.5SF fuse for 150Kva Tx at Well So.Balam #324. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Mice) |  | 1 | 8:30 | Morning | Wednesday | 2016 | 10
4763 | 2016-11-12 05:00 | 2016-11-12 05:00 | 13.8KV PETANI FEEDER #1 | Fair | Secondary Cable | 0 | 05:00 It was reported b/o fuse for Tx at Well Petani #79. (Petani fdr #1) 15:45 Checked & found, @1 b/o 3.1SF fuse for 100Kva Tx at Well Petani #79. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Secondary cable. (Surface cable shortcircuit) |  | 1 | 5:00 | Morning | Saturday | 2016 | 11
4764 | 2016-11-12 05:06 | 2016-11-12 05:06 | 13.8KV 5B FEEDER #2 | Fair | Animal | 312 | 5B OCB fdr #2 T/R 1x. 5B fdr #1 Load dropped 55A (96-41A). 5B fdr #3 Load dropped 13A (25-12A). Cause: Not checked yet. |  | 1 | 5:06 | Morning | Saturday | 2016 | 11
4765 | 2016-11-12 05:06 | 15/12/2016 18:47 | 13.8KV 5B FEEDER #2 | Fair | Animal | 312 | Checked & found, 5B OCB fdr #2 T/R 1x Ctr: 349-350 R/F: 50@2. Patrolled the line & found, a dead Bird on Recl. 5C-07, also b/o all of Recl. 5C-07 Bushings. Cause: Animal. (Bird) |  | 1 | 5:06 | Morning | Saturday | 2016 | 11
4766 | 2016-11-12 09:26 | 2016-11-12 09:26 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 0 | It was reported b/o fuse for Tx at Well Bangko #180. (Bangko fdr #4) Not checked yet . (Well off, no Production loss) |  | 1 | 9:26 | Morning | Saturday | 2016 | 11
4767 | 2016-11-12 09:26 | 2016-12-12 09:50 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 0 | Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Bangko #180. Performed TTR, Megger test the Tx & found, Tx failure. Replaced 150Kva Tx failure with the same size, then energized the Tx. Cause: Tx Failure. |  | 1 | 9:26 | Morning | Saturday | 2016 | 11
4768 | 2016-11-12 17:52 | 2016-11-12 17:52 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Sintong fdr #1 Load dropped 33A (84-51A). Sintong GFPC T/R 1. (Ground fault alarm on Sintong fdr #1) Not checked yet. |  | 1 | 17:52 | Afternoon | Saturday | 2016 | 11
4769 | 2016-11-12 17:52 | 13/12/2016 08:22 | 13.8KV SINTONG FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 25AD-26 (Sintong fdr #1) T/R 1x Ctr: 111-112. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:52 | Afternoon | Saturday | 2016 | 11
4770 | 2016-12-12 18:01 | 2016-12-12 18:01 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 0 | 18:01 Manual Opened Minas ACB fdr #3. Requested by Minas GS-2 operator, due to WIP problem. 19:40 Manual Closed Minas ACB fdr #3. Cause: Planned maintenance. (Minas GS-2 WIP problem) (No Production loss) |  | 1 | 18:01 | Afternoon | Monday | 2016 | 12
4771 | 2016-12-13 05:05 | 2016-12-13 05:05 | MINAS POWER PLANT | Fair | Under investigation | 0 | 05:05 MGT #1 Trip Off, By Alarm: Gas fuel Pressure Low (Not real). Cause: Under investigation. (Suspected Transducer problem) 06:26 S/U MGT #1, and On Line the Unit at 07:40. |  | 1 | 5:05 | Morning | Tuesday | 2016 | 12
4772 | 2016-12-13 07:48 | 2016-12-13 07:48 | MINAS POWER PLANT |  |  | - | 07:48 S/U MGT #9, and On Line the Unit at 08:45. |  | 1 | 7:48 | Morning | Tuesday | 2016 | 12
4773 | 2016-12-13 08:59 | 2016-12-13 08:59 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | 08:59 N.Duri fdr #11 Load dropped 130A (234-100A). N.Duri GFPC-TX #1 T/R 1x. (Ground fault alarm from N.Duri fdr #11) 11:00 Checked & found, Recl. 10-G2-13 (N.Duri fdr #11) T/SO. Ctr: Not reported yet. Patrolled the line, but found nothing. Blocked & closed Recl. 10-G2-13. Ok. Then released the block. Cause: Unidentified. | 1111 | 1 | 8:59 | Morning | Tuesday | 2016 | 12
4774 | 2016-12-13 09:12 | 2016-12-13 09:12 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 11 | 09:12 It was reported b/o fuse for Tx o/p #08-M3-35. 11:38 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #08-M3-35. Replaced b/o fuses above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 1111 | 1 | 9:12 | Morning | Tuesday | 2016 | 12
4775 | 2016-12-13 14:47 | 2016-12-13 14:47 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 53 | 14:47 It was reported b/o fuse for Tx at Well Menggala #15. Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Menggala #15. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 1111 | 1 | 14:47 | Afternoon | Tuesday | 2016 | 12
4776 | 2016-12-13 15:20 | 2016-12-13 15:20 | 13.8KV NORTH DURI FEEDER #11 | Fair | Animal | 0 | 15:20 It was reported b/o fuse for Tx o/p #13-H5-01. 17:00 Checked & found, @3 b/o 7.8SF fuse for 300Kva Tx o/p #13-H5-01. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) | 11111 | 1 | 15:20 | Afternoon | Tuesday | 2016 | 12
4777 | 2016-12-14 01:55 | 2016-12-14 01:55 | CENTRAL DURI POWER PLANT |  |  | - | 01:55 Off line CGT #3, and S/D the Unit for S/B. (Prior to fixing Hydraulic Pressure hunting) |  | 1 | 1:55 | Night | Wednesday | 2016 | 12
4778 | 2016-12-14 06:22 | 2016-12-14 06:22 | 13.8KV 5B FEEDER #4 | Fair | Unidentified | 51 | 06:22 5B fdr #4 Load dropped 153A (218-65A). 09:00 Checked & found, Recl. 4B-73 (5B fdr #4) T/SO. Ctr: 186-187. Blocked & closed Recl. 4B-73, Ok. Then released the block. Not patrolled yet. | 1111 | 1 | 6:22 | Morning | Wednesday | 2016 | 12
4779 | 2016-12-14 06:22 | 2016-12-23 16:22 | 13.8KV 5B FEEDER #4 | Fair | Unidentified | 51 | Patrolled the line but found nothing. Cause: Unidentified. | 1111 | 1 | 6:22 | Morning | Wednesday | 2016 | 12
4780 | 2016-12-14 09:55 | 2016-12-14 09:55 | 13.8KV 5B FEEDER #2 | Fair | Planned Maintenance | 85 | 09:55-10:45 Manually open LBS #5C-01. (5B fdr #2) To repairing Hot Spot all of Recl. 5C-07 Bushing. Cause: Plan Maintenance. | 1111 | 1 | 9:55 | Morning | Wednesday | 2016 | 12
4781 | 2016-12-14 10:20 | 2016-12-14 10:20 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx o/p #06-R5-16. Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #06-R5-16. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 1111 | 1 | 10:20 | Morning | Wednesday | 2016 | 12
4782 | 2016-12-14 10:51 | 2016-12-14 10:51 | 13.8KV PUNGUT FEEDER #1 | Fair | Planned Maintenance | 0 | 10:51 Manually open Pungut OCB fdr #1. (For tie in new line of Pungut AGRP project) 12:01 Closed Pungut OCB fdr #1. Cause: Planned maintenance. No Production loss. | 1111 | 1 | 10:51 | Morning | Wednesday | 2016 | 12
4783 | 2016-12-14 17:56 | 2016-12-14 17:56 | MINAS POWER PLANT |  |  | - | Off line MGT #1, then S/D the Unit for Stand By. |  | 1 | 17:56 | Afternoon | Wednesday | 2016 | 12
4784 | 2016-12-14 18:00 | 2016-12-14 18:00 | MINAS POWER PLANT |  |  | - | Off line MGT #5, then S/D the Unitv for Stand By. |  | 1 | 18:00 | Afternoon | Wednesday | 2016 | 12
4785 | 2016-12-14 18:13 | 2016-12-14 18:13 | MINAS POWER PLANT |  |  | - | Off line MGT #2, then S/D the Unit for Stand By. |  | 1 | 18:13 | Afternoon | Wednesday | 2016 | 12
4786 | 2016-12-15 17:21 | 2016-12-15 17:21 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | C.Duri ACB fdr #7 T/R 1x Ctr: 470-471 R/F: 51N. Not patrolled yet. | 1111 | 1 | 17:21 | Afternoon | Thursday | 2016 | 12
4787 | 2016-12-15 17:21 | 2016-12-16 18:13 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. | 1111 | 1 | 17:21 | Afternoon | Thursday | 2016 | 12
4788 | 2016-12-16 11:02 | 2016-12-16 11:02 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 185 | Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #3 Load dropped 20A (22-2A). Not checked yet. | 11111 | 1 | 11:02 | Morning | Friday | 2016 | 12
4789 | 2016-12-16 11:02 | 2016-12-20 07:24 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 185 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 222-223 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. | 11111 | 1 | 11:02 | Morning | Friday | 2016 | 12
4790 | 2016-12-16 17:33 | 2016-12-16 17:33 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 0 | 17:33 -22:20 Manually open /closed 3D fdr #4. Mr. YASRI #17557 Requested. (MNS GS #5. WIP problem). No Production Loss. | 11111 | 1 | 17:33 | Afternoon | Friday | 2016 | 12
4791 | 2016-12-16 20:30 | 2016-12-16 20:30 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 31 | 20:30 It was reported B/O Fuse at well S.Balam #434 (Balam Fdr#4). 22:45 Checked and found @3 B/O Fuse for 150 KVA TX. Replace the Fuse with the same size, then energize the TX. Cause: Unidentified. |  | 1 | 20:30 | Night | Friday | 2016 | 12
4792 | 2016-12-17 07:31 | 2016-12-17 07:31 | 13.8KV 6D FEEDER #1 | Fair | Dead End Insulator | 69 | 6D OCB fdr #1 T/R 1x. 6D fdr #2 Load dropped 105A (226-121A). Not checked yet. | 11111 | 1 | 7:31 | Morning | Saturday | 2016 | 12
4793 | 2016-12-17 07:31 | 2016-12-23 17:31 | 13.8KV 6D FEEDER #1 | Fair | Dead End Insulator | 69 | Checked & found, 6D OCB fdr #1 T/R 1x Ctr: 310-311 R/F: 51N. Patrolled the line & found, @1,@2 broken Dead End Insulators Near Well #5B-76. Cause: Dead end Insulator. | 11111 | 1 | 7:31 | Morning | Saturday | 2016 | 12
4794 | 2016-12-17 11:26 | 2016-12-17 11:26 | 13.8KV 3D FEEDER #3 | Fair | Planned Maintenance | 0 | 11:26 Manually opened 3D OCB fdr #3, to anticipate Spill at MinasGS #5. (Req. by ELDI /Minas-GS #5 ) (Minas-GS #5 High level Tank, due to 8 Unit WIPs were problem) Manually opened 3D OCB fdr #2, and closed at 12:37. Manually opened 4D OCB fdr #2, and closed at 12:38. 12:38 Closed 3D OCB fdr #3. Cause: Plan Maintenance. | 1111 | 1 | 11:26 | Morning | Saturday | 2016 | 12
4795 | 2016-12-17 11:26 | 2016-12-17 11:26 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 0 | 11:26 Manually opened 4D OCB fdr #3, to anticipate Spill at MinasGS #5. (Req. by ELDI /Minas-GS #5 ) (Minas-GS #5 High level Tank, due to 8 Unit WIPs were problem) 12:38 Closed 4D OCB fdr #3. Cause: Plan Maintenance. | 11111 | 1 | 11:26 | Morning | Saturday | 2016 | 12
4796 | 2016-12-17 11:29 | 2016-12-17 11:29 | 13.8KV 3D FEEDER #2 | Fair | Planned Maintenance | 0 | 11:26 Manually opened 3D OCB fdr #2, to anticipate Spill at MinasGS #5. (Req. by ELDI /Minas-GS #5 ) (Minas-GS #5 High level Tank, due to 8 Unit WIPs were problem) 12:37 Closed 3D OCB fdr #2. Cause: Plan Maintenance. | 11111 | 1 | 11:29 | Morning | Saturday | 2016 | 12
4797 | 2016-12-17 17:23 | 2016-12-17 17:23 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Dead End Insulator | 0 | C.Duri ACB fdr #7 T/R 1x Ctr: 471-472 R/F: 51N. Not patrolled yet. | 11111 | 1 | 17:23 | Afternoon | Saturday | 2016 | 12
4798 | 2016-12-17 17:23 | 2016-12-19 17:00 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Dead End Insulator | 0 | Patrolled the line & found, @2 F/O Dead end Insulator o/p #03-03-17. Cause: Dead end Insulator. | 11111 | 1 | 17:23 | Afternoon | Saturday | 2016 | 12
4799 | 2016-12-17 22:55 | 2016-12-17 22:55 | CENTRAL DURI POWER PLANT |  |  | - | 22:55 S/U CGT #3, then On line the Unit at: 23:15. (for Running on test after Trip) |  | 1 | 22:55 | Night | Saturday | 2016 | 12
4800 | 2016-12-18 04:55 | 2016-12-18 04:55 | CENTRAL DURI SWITCH YARD | Fair | Substation Failure (Tx SS) | 28181 | 04:55 115KV CDSY GCB #41 T/O. By Relay: 86T & 51N-G(@1,@2,@3). 115KV CDSY GCB #43. (In open position / under service) 13.8KV CDSY ACB #34 T/O. (with Alarm: TX-3 Locked Out) (115KV CDSY Power TX-3 Tripped) In the same time CGT #3 & CGT #4 Tripped. (Under Investigation / Suspected overload) (CDSG BUS-3 & BUS-4 no power) To anticipate Spill at CGS-1. 06:42 Manually open C.Duri ACB fdr #1, ------>and closed at 09:09. (CGS #1, Tank level to High) Tried to Energized The Power TX-3. (after resetting all Realy) 06:45 Manual Closed 13.8KV C.Duri ACB #34, Ok. Manual Closed 115KV GCB #41, but tripped again. (with the same Relay as before) Cause: Under Investigation. (Suspected Power TX-3 problem) Transferring some load of CDSG BUS-3 & BUC-4. 07:18 Open LBS #05-N6-23. 07:35 Rack out C.Duri ACB #42. (C.Duri fdr #10). 07:38 Closed Isolation switch of Darling VCB fdr #3. Closed Darling VCB fdr #3, but tripped again. (Found b/o Tx fuse at CGS-5) 07:55 Closed Isolation switch Darling VCB fdr #6. 07:56 Closed Darling VCB fdr #6. 07:39 Manual open D.Filed fdr #2, ------> and closed at 14:09. (CGS #1, Tank level to High). 07:56 Manual open C.Duri fdr #3, ------> and closed at 15:32. (CGS #3, Tank level to High). 07:56 Manual open C. Duri fdr #5, ------> and closed at 10:00. (CGS#3, Tank level to High). 08:00 Closed C.Duri ACB fdr #11. (Darling fdr #6 paralled with C.Duri fdr #11) (13.8KV CDSG BUS-3 & BUS-4 Energized) 08:13 Closed Darling VCB fdr #3. (Transfer load from C.Duri fdr #10) 08:20 Closed Darling VCB fdr #4. (Transfer load from C.Duri fdr #12). 08:50 Opened Recl. 01-08-31. (C.Duri fdr #6),------> and closed at 14:52. Opened Recl. 02-01-01. (C.Duri fdr #6),------> and closed at 15:12. Closed C.Duri ACB fdr #6. 09:19 Opened Recloser #01-06-30. (D.Field fdr #1),------> and closed at 14:47. 09:21 Closed LBS #01-06-01. (D.Field fdr #1),------> and Opened at 17:00. 09:46 Opened LBS #09-Q1-01. (C.Duri fdr #4) (To Separate load of CD fdr #7 & CD fdr #16). 09:59 Opened Recl. 03-06-03. (C.Duri fdr #5),------> and Closed at 14:54. 10:00 Closed C.Duri fdr #5 10:15 Opened Recl. 03-01-39. (C.Duri fdr #7),------> and Closed at 14:34. 10:17 Closed C.Duri ACB fdr #7. 10:20 S/U CGT #4, then on line the Unit at 10:38. Restore Power CGS #4. 10:30 Opened Recl. 04-03-02. (C.Duri fdr #9),------> and Closed at 14:17. 10:28 Opened Recl. 04-01-02. (C.Duri fdr #9),------> and Closed at 13:15. 10.36 Closed Recl. 02-01-01, then Unplugged its control cable. (to transfer load of C.Duri fdr #6 to C.Duri fdr #9) 10:45 Closed C.Duri ACB fdr #8. 11:46 Closed D.Field ACB fdr #3. 11:50 Opened C.Duri fdr #6. 12:15 Closed C.Duri ACB fdr #15. 13:15 Closed Recl. 04-01-02. (C.Duri fdr #9) Cause: Under Investigation. (Suspected power TX-3 problem) | 11111 | 1 | 4:55 | Morning | Sunday | 2016 | 12
4801 | 2016-12-18 04:55 | 2016-12-18 04:55 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 04:55 CGT #3 Trip Off. (By Alarm: Bus Under Voltage) Cause: Under investigate. (Suspected TX #3 problem) |  | 1 | 4:55 | Morning | Sunday | 2016 | 12
4802 | 2016-12-18 04:55 | 2016-12-18 04:55 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 04:55 CGT #4 Trip Off. (By Alarm: Bus under voltage, due to 115KV CDSY Power TX-3 Trip) 08:10 S/U CGT #4, then On Line to the unit at 08:31. 08:38 CGT #4 T/O. By R/F: 59, 59G, 87G, 86G. 09:32 S/U CGT #4, then On Line the Unit at 09:44. (Put Excitation control to Manual Mode) 09:56 CGT #4 T/O again. By Realy: 24. (BUS-3 & BUS-4 15.4KV 10:20 Re-S/U CGT #4, then on line the Unit at 10:38. (Put Excitation control on Manual mode) Cause: Under investigation. (Due to 115KV CDSY powewr TX-3 trip) |  | 1 | 4:55 | Morning | Sunday | 2016 | 12
4803 | 2016-12-19 08:16 | 2016-12-19 08:16 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri ACB fdr #16 T/R 1x Ctr: 295-296 R/F: 51@1,@2. Not patrolled yet. |  | 1 | 8:16 | Morning | Monday | 2016 | 12
4804 | 2016-12-19 08:16 | 2016-12-20 19:30 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 8:16 | Morning | Monday | 2016 | 12
4805 | 2016-12-19 14:10 | 2016-12-19 14:10 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr #1 Load dropped 40A (140-100A). Not checked yet. |  | 1 | 14:10 | Afternoon | Monday | 2016 | 12
4806 | 2016-12-19 14:10 | 2016-12-20 19:25 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 41Aw-62 (C.Duri fdr #1) T/R 1x Ctr: 243-244. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 14:10 | Afternoon | Monday | 2016 | 12
4807 | 2016-12-19 21:09 | 2016-12-19 21:09 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Tree | 0 | Duri Community ACB fdr #2 T/R 1x. Not checked yet. | 1111 | 1 | 21:09 | Night | Monday | 2016 | 12
4808 | 2016-12-19 21:09 | 2016-12-21 13:11 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Tree | 0 | Checked & found, Duri Community ACB fdr #2 T/R 1x Ctr: 183-184 R/F: 51N. Patrolled the line & found, fall down Tree & hit to power line at near Krakatau-181 housing. Cause: Tree. | 1111 | 1 | 21:09 | Night | Monday | 2016 | 12
4809 | 2016-12-19 22:58 | 2016-12-19 22:58 | MINAS POWER PLANT | Fair | Under investigation | 0 | 22:58 MGT #6 Tripped. By Alarm: "Gas control Valve servo trouble" Cause: Under Investigation. (No load shedding) | 1111 | 1 | 22:58 | Night | Monday | 2016 | 12
4810 | 2016-12-20 06:45 | 2016-12-20 06:45 | 13.8KV PUNGUT FEEDER #2 | Fair | Unidentified (Fuse) | 28 | 06:45 It was reported b/o fuse for Tx at Well Tandun #12. 10:25 Checked & found, @3 b/o 3.5SF fuse for 150Kva Tx at Well Tandun #12. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 6:45 | Morning | Tuesday | 2016 | 12
4811 | 2016-12-20 08:52 | 2016-12-20 08:52 | MINAS POWER PLANT |  |  | - | 08:52 S/U MGT #5, then On Line the Unit at 09:15. |  | 1 | 8:52 | Morning | Tuesday | 2016 | 12
4812 | 2016-12-20 13:40 | 2016-12-20 13:40 | 115KV NELLA SW. STA - S. BALAM LINE | Fair | Planned Maintenance | 734 | 13:40 Manually open 115KV Nella GCB #26 (115KV line to So.Balam Substation) (To shutdown So.Balam Substation for dismanthling 115KV T/Tap jumper of MSU-2) 14:43 Close 115KV Nella GCB #26. Cause: Plan Maintenance. (Open T/Tap jumper of 115KV MSU-2) Prod. Loss for (So.Balam fdr #1 & #2) = 1610 Bbls / 196 wells. | 1111 | 1 | 13:40 | Afternoon | Tuesday | 2016 | 12
4813 | 2016-12-20 14:32 | 2016-12-20 14:32 | MINAS POWER PLANT | Fair |  | - | 14:32 S/U MGT #6, then On Line the Unit at 15:24. |  | 1 | 14:32 | Afternoon | Tuesday | 2016 | 12
4814 | 2016-12-20 16:29 | 2016-12-20 16:29 | MINAS POWER PLANT |  |  | - | 16:29 Off line MGT #4, then S/D the Unit for S/B. |  | 1 | 16:29 | Afternoon | Tuesday | 2016 | 12
4815 | 2016-12-20 23:16 | 2016-12-20 23:16 | 13.8KV NELLA FEEDER #1 | Fair | Transformer Failure | 34 | 23:16 It was reported B/O fuse at well Bangko#230 (Nella fdr#1). Not checked yet. |  | 1 | 23:16 | Night | Tuesday | 2016 | 12
4816 | 2016-12-20 23:16 | 2016-12-21 14:16 | 13.8KV NELLA FEEDER #1 | Fair | Transformer Failure | 34 | Checked TTR & megger 100Kva Tx is failure. (Would be changed tomorrow). Cause: Tx Failure. |  | 1 | 23:16 | Night | Tuesday | 2016 | 12
4817 | 2016-12-20 23:16 | 2016-12-22 10:54 | 13.8KV NELLA FEEDER #1 | Fair | Transformer Failure | 34 | Replaced 100Kva Tx with 150Kva Tx at well Bangko#230. Cause: Transformer Failure. |  | 1 | 23:16 | Night | Tuesday | 2016 | 12
4818 | 2016-12-21 06:30 | 2016-12-21 06:30 | 13.8KV PUNGUT FEEDER #2 | Fair | Unidentified (Fuse) | 10 | 06:30 It was reported b/o fuse for Tx at Well Tandun #18. (Pungut fdr #2) 10:20 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Tandun #18. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 6:30 | Morning | Wednesday | 2016 | 12
4819 | 2016-12-21 08:05 | 2016-12-21 08:05 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified (Fuse) | 54 | 08:05 It was reported b/o fuse for Tx at Well So.Bekasap #05. (So.Bekasap fdr #1) 09:25 Checked & found, @1 b/o 7.0SF fuse for 225Kva Tx at Well So.Bekasap #05. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 8:05 | Morning | Wednesday | 2016 | 12
4820 | 2016-12-21 11:00 | 2016-12-21 11:00 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified (Fuse) | 10 | 11:00 It was reported b/o fuse for Tx at Well Pinang #37. (Pinang fdr #1) 14:25 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well Pinang #37. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 11:00 | Morning | Wednesday | 2016 | 12
4821 | 2016-12-21 21:14 | 2016-12-21 21:14 | 13.8KV 4B FEEDER #2 | Heavy Rain | Lightning | 7 | 4B OCB fdr #2 T/R 1x. 4B fdr #1 Load dropped 39A (97-58A). Not checked yet. | 1111 | 1 | 21:14 | Night | Wednesday | 2016 | 12
4822 | 2016-12-21 21:14 | 2016-12-25 08:24 | 13.8KV 4B FEEDER #2 | Heavy Rain | Lightning | 7 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 232-233 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator o/p #4B-45. Cause: Lightning. And also checked All Reclosers at downstream of 4B fdr #1 & found, normal. (Counter did not change) Patrolled the line & found, @3 broken Pin Insulator o/p #4A-11. Cause: Lightning. | 1111 | 1 | 21:14 | Night | Wednesday | 2016 | 12
4823 | 2016-12-22 08:20 | 2016-12-22 08:20 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified (Fuse) | 6 | 08:20 It was reported b/o fuse for Tx at Well Genting #01. (Sintong fdr #2) Checked & found, @1 b/o 1.0SF fuse for 45Kva Tx at Well Genting #45. 10:15 Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 8:20 | Morning | Thursday | 2016 | 12
4824 | 2016-12-22 20:36 | 2016-12-22 20:36 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 60 | Bekasap main fdr #2 Load dropped 140A (145-5A). Bekasap GFPC T/R 2x. Not checked yet. |  | 1 | 20:36 | Night | Thursday | 2016 | 12
4825 | 2016-12-22 20:36 | 2016-12-26 14:17 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 60 | Checked & found, Recl. 37BD-12 (Bekasap fdr #2) T/R 1x Ctr: 173-174. Patrolled the line & found: -@2 Broken Pin Insualtor o/p #38BD-106. -@1 Broken Pin Insulator on TP of Well Bekasap #38. Also found, Recl. 37BD-40 (Bekasap fdr #2) T/R 1x Ctr: 75-76. Patrolled the line & found: -@1 Broken Dead end Insulator o/p #37BD-153 & #37BD-50. -@3 Broken Dead end Insulator o/p #37BD-46. Cause: Lightning. |  | 1 | 20:36 | Night | Thursday | 2016 | 12
4826 | 2016-12-23 05:51 | 2016-12-23 05:51 | 13.8KV 4B FEEDER #2 | Cloudy and Lightning | Lightning | 11 | 4B OCB fdr #2 T/R 1x. 4B fdr #1 load dropped 63A (97-34A). Not checked yet. |  | 1 | 5:51 | Morning | Friday | 2016 | 12
4827 | 2016-12-23 05:51 | 2016-12-27 18:06 | 13.8KV 4B FEEDER #2 | Cloudy and Lightning | Lightning | 11 | Checked & found, 4B OCB fdr #2 T/R 1x Ctr: 232-233 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 5:51 | Morning | Friday | 2016 | 12
4828 | 2016-12-23 08:22 | 2016-12-23 08:22 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified (Fuse) | 12 | 08:22 It was reported b/o fuse for Tx at Well Hiu #01. (So.Bekasap fdr #1) 10:45 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Hiu #01. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 8:22 | Morning | Friday | 2016 | 12
4829 | 2016-12-23 09:50 | 2016-12-23 09:50 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Animal | 4 | 09:50 It was reported b/o fuse for Tx at Well KB #287. (NKBS fdr #3) 10:45 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well KB #287. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Civet) |  | 1 | 9:50 | Morning | Friday | 2016 | 12
4830 | 2016-12-23 10:14 | 2016-12-23 10:14 | MINAS POWER PLANT |  |  | - | 10:14 S/U MGT #1, then on line the Unit at 10:45. |  | 1 | 10:14 | Morning | Friday | 2016 | 12
4831 | 2016-12-23 10:30 | 2016-12-23 10:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 0 | 10:30 It was reported b/o fuse for Tx at Well Pagar #21. (Ketigul fdr #2) 15:00 Checked & found, @3 b/o 7.8SF fuse for 300Kva Tx at Well Pagar #21. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 10:30 | Morning | Friday | 2016 | 12
4832 | 2016-12-23 22:25 | 2016-12-23 22:25 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Low mega-ohm reading | 0 | 22:25 Duri community fdr #1 Load dropped 64A (119-55A). It was reported No power at Sibayak complex by Oncall FM. 23:25 Checked & found Recl. RK-74 (D.Community fdr #1) T/LO. Ctr: 115-118. Blocked & closed Recl. RK-74, but T/O again. 23:32 Patrolled the line & found, @1 fault indicator o/p #SY-19 indicated on. Open isolation blade for S/D (TX 15,16,17,18,19,20 and 21) at Sibayak housing 23:42 Blocked & closed Recl. RK-74, Ok. Then released the block. Cause: Under Investigation. |  | 1 | 22:25 | Night | Friday | 2016 | 12
4833 | 2016-12-23 22:25 | 2016-12-24 08:30 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Low mega-ohm reading | 0 | 08:30 Checked & found, U/G cable was low reading between Tx-18 & Tx-19, then isolated its cable. 09:56 Energized Tx-20. 09:57 Energized Tx-19. 10:15 Energized Tx-15, Tx-16, Tx-17 & Tx-21. 10:29 Energized Tx-18. 10:30 Sibayak Camp back to normal. Cause: U/Ground Cable Low Megger. (Between Tx-18 & Tx-19) |  | 1 | 22:25 | Night | Friday | 2016 | 12
4834 | 2016-12-24 11:43 | 2016-12-24 11:43 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 18 | 11:43 It was reported b/o fuse for Tx at Well Tilan #14. (Ketigul fdr #1) 14:30 Checked & found, @2,@3 b/o 14.oSF fuses for 500Kva Tx at Well Tilan #14. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Bird) |  | 1 | 11:43 | Morning | Saturday | 2016 | 12
4835 | 2016-12-24 13:45 | 2016-12-24 13:45 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Planned Maintenance | 7 | 13:45 Shutdown 112.5Kva Tx o/p #09-R8-04. (C.Duri fdr #4) 14:45 To replacing it is 112.5Kva Tx oil leakage with the same size o/p #09-R8-04. Cause: Maintenance Job. (Tx oil Leakage) |  | 1 | 13:45 | Afternoon | Saturday | 2016 | 12
4836 | 2016-12-24 15:00 | 2016-12-24 15:00 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Planned Maintenance | 0 | 15:00 Shutdown 112.5Kva Tx o/p #06-S3-03. (C.Duri fdr #14) 15:45 To replacing 112.5Kva Tx oil leakage with the same size o/p #06-S3-03. Cause: Maintenance Job. (Tx oil Leakage) |  | 1 | 15:00 | Afternoon | Saturday | 2016 | 12
4837 | 2016-12-25 06:18 | 2016-12-25 06:18 | 13.8KV LIBO FEEDER #1 | Cloudy and Lightning | Lightning | 5 | 06:18 Libo OCB fdr #1 T/R 1x. Not checked yet. 16:00 Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 411-412 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 1111 | 1 | 6:18 | Morning | Sunday | 2016 | 12
4838 | 2016-12-25 07:10 | 2016-12-25 07:10 | 13.8KV MENGGALA FEEDER #1 | Fair | Pin Insulator | 11 | Menggala fdr #1 Load Dropped 120A (186-66A). Not checked yet. |  | 1 | 7:10 | Morning | Sunday | 2016 | 12
4839 | 2016-12-25 07:10 | 2016-12-28 14:45 | 13.8KV MENGGALA FEEDER #1 | Fair | Pin Insulator | 11 | Checked & found, Recl. 19AN-04 (Menggala fdr #1) T/R 1x Ctr: 323-324. Patrolled the line & found, @3 broken Pin Insulator o/p #19AK-09. Cause: Pin Insulator. |  | 1 | 7:10 | Morning | Sunday | 2016 | 12
4840 | 2016-12-25 08:05 | 2016-12-25 08:05 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 7 | D.Field fdr #3 Load dropped 130A (194-64A) Not checked yet. |  | 1 | 8:05 | Morning | Sunday | 2016 | 12
4841 | 2016-12-25 08:05 | 2017-02-01 16:12 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 7 | Checked & found, D.Field ACB fdr #3 T/R 1x Ctr: 679-680 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 8:05 | Morning | Sunday | 2016 | 12
4842 | 2016-12-25 08:45 | 2016-12-25 08:45 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Transformer Failure | 0 | 08:45 It was reported b/o fuse for Tx o/p #03-5-13. (C.Duri fdr #7) 09:40 Checked & found, b/o fuse for 112.5Kva Tx o/p #03-5-13. Performed TTR, Megger test the Tx & found, Low megger reading. Cause: Tx Failure. 15:15 Replaced 112.5Kva Tx failure with the same size & energized the Tx. Cause: Tx Failure. |  | 1 | 8:45 | Morning | Sunday | 2016 | 12
4843 | 2016-12-25 10:08 | 2016-12-25 10:08 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 32 | 10:08 It was reported b/o fuse for Tx o/p #04-1-17. (C.Duri fdr #9) 14:00 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #04-1-17 Replaced b/o fuse above with the same size & energized the Tx . Cause: Unidentified (Fuse). |  | 1 | 10:08 | Morning | Sunday | 2016 | 12
4844 | 2016-12-25 17:22 | 2016-12-25 17:22 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 29 | 17:22 It was reported no power at CGS #4. 20:43 Checked & found, Recl. 04-05-02 (D.Field fdr #3) T/SO. Ctr: 172-173. Blocked & closed Recl. 04-05-02, Ok. Then released the block. The line is not patrolled yet. |  | 1 | 17:22 | Afternoon | Sunday | 2016 | 12
4845 | 2016-12-25 17:22 | 2017-02-01 16:13 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 29 | Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 17:22 | Afternoon | Sunday | 2016 | 12
4846 | 2016-12-26 04:31 | 2016-12-26 04:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Dead End Insulator | 57 | 04:31 C.Duri fdr #1 Load dropped 51A (142-91A). 15:36 C.Duri fdr #1 Load dropped again 37A (142-105A). Not checked yet. | 11111 | 1 | 4:31 | Morning | Monday | 2016 | 12
4847 | 2016-12-26 04:31 | 2017-02-01 16:17 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Dead End Insulator | 57 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 244-245. Patrolled the line & found, @1 broken Dead end Insulator o/p #39AV-23A. Cause: Dead end Insulator. | 11111 | 1 | 4:31 | Morning | Monday | 2016 | 12
4848 | 2016-12-26 06:51 | 2016-12-26 06:51 | 13.8KV LIBO FEEDER #1 | Cloudy and Lightning | Lightning | 5 | Libo OCB fdr #1 T/R 1x. Not checked yet. | 11111 | 1 | 6:51 | Morning | Monday | 2016 | 12
4849 | 2016-12-26 06:51 | 2016-12-27 10:54 | 13.8KV LIBO FEEDER #1 | Cloudy and Lightning | Lightning | 5 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 412-413 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 11111 | 1 | 6:51 | Morning | Monday | 2016 | 12
4850 | 2016-12-26 14:20 | 2016-12-26 14:20 | 13.8KV 4B FEEDER #1 | Fair | Planned Maintenance | 27 | 14:20-15:35 Manual Open LBS #4B-90. (4B fdr # 1) Replaced @3 Seriously broken Pin Insulator o/p #4A-11. (15 wells were off during the job) Cause: Planed Maintenance. |  | 1 | 14:20 | Afternoon | Monday | 2016 | 12
4851 | 2016-12-26 15:43 | 2016-12-26 15:43 | MINAS POWER PLANT |  |  | - | 15:43 S/U MGT #2, then on line the unit at 16:15. 16:28 Open Minas ACB #25. (Tie Breaker) |  | 1 | 15:43 | Afternoon | Monday | 2016 | 12
4852 | 2016-12-26 18:01 | 2016-12-26 18:01 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified (Fuse) | 0 | 18:01 It was reported that b/o fuse for Tx at Steam Station Area #6 . 20:05 Checked & found, @3 b/o 50K fuse for 1500KVA Tx at Steam Station Area #6 . Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (fuse). |  | 1 | 18:01 | Afternoon | Monday | 2016 | 12
4853 | 2016-12-27 08:26 | 2016-12-27 08:26 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 12 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 8:26 | Morning | Tuesday | 2016 | 12
4854 | 2016-12-27 08:26 | 2016-12-29 16:50 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 12 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 223-224 R/F: 51N. Patrolled the line & found, @2 broken Dead end Insulator o/p #NN. Cause: Dead end Insulator. |  | 1 | 8:26 | Morning | Tuesday | 2016 | 12
4855 | 2016-12-27 08:48 | 2016-12-27 08:48 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 07:00 It was reported b/o fuse for Tx o/p #NN. (near House Seulawah #37) (D.Community fdr # 2) 08:48 Checked & found, @1 b/o 1.0SF fuse for 50Kva Tx o/p #NN. (near House Seulawah #37) Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 8:48 | Morning | Tuesday | 2016 | 12
4856 | 2016-12-27 09:40 | 2016-12-27 09:40 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 1921 | 09:40 Off line NDC-CT #3, then S/D the Unit for Maintenance. (Replacing "Motor lube oil cooler Fan” of Unit-3) 09:07 Inform Minas Production to Reduce Load 20MW. 09:45 Inform BOB to Reduce Load 17 MW. 17:02 S/U NDC-CT #3, then on line the Unit at 17:28. 17:30 Inform Minas Production GS #6 to normalize Load. 17:40 Inform BOB to normalize Load. Cause: NDC-CT #3 S/D for Maintenance. Total Prod loss =1921 Bbls / 146 wells & 20 WIP. | 11111 | 1 | 9:40 | Morning | Tuesday | 2016 | 12
4857 | 2016-12-27 10:00 | 2016-12-27 10:00 | 13.8KV 6D FEEDER #4 | Fair | Unidentified (Fuse) | 12 | 10:00 It was reported b/o fuse for Tx at Minas GS-4. (6D fdr #4) 14:30 Checked & found, @1,@3 b/o 100K fuses for 2500Kva Tx at Minas GS-4. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 10:00 | Morning | Tuesday | 2016 | 12
4858 | 2016-12-27 15:18 | 2016-12-27 15:18 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy | Unidentified | 0 | So.Bekasap fdr #1 Load dropped 153A (164-11). Not checked yet. |  | 1 | 15:18 | Afternoon | Tuesday | 2016 | 12
4859 | 2016-12-27 15:18 | 2017-01-01 17:09 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy | Unidentified | 0 | Checked & found, Recl. 36BI-04 (So.Bekasap fdr #1) T/R 1x Ctr: 252-253. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 15:18 | Afternoon | Tuesday | 2016 | 12
4860 | 2016-12-28 09:02 | 2016-12-28 09:02 | MINAS POWER PLANT |  |  | - | Off line MGT #3, then S/D the Unit for S/B. |  | 1 | 9:02 | Morning | Wednesday | 2016 | 12
4861 | 2016-12-28 09:08 | 2016-12-28 09:08 | MINAS POWER PLANT |  |  | - | Off line MGT #2, then S/D the Unit for S/B. |  | 1 | 9:08 | Morning | Wednesday | 2016 | 12
4862 | 2016-12-28 09:30 | 2016-12-28 09:30 | MINAS POWER PLANT |  |  | - | Off line MGT #4, then S/D the Unit for S/B. |  | 1 | 9:30 | Morning | Wednesday | 2016 | 12
4863 | 2016-12-28 14:52 | 2016-12-28 14:52 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 0 | 14:52-16:51 Manually Open & Closed Minas ACB fdr #3. Requested by Minas GS-2, due to 3Unit WIPs failed to S/U. (To anticipate spill at Minas GS-2) Cause: Planned Maintenance. (No prod. loss charged to PGT) |  | 1 | 14:52 | Afternoon | Wednesday | 2016 | 12
4864 | 2016-12-28 23:27 | 2016-12-28 23:27 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse for Tx o/p #07-V1-33. (D.Field fdr #4) Not checked yet. |  | 1 | 23:27 | Night | Wednesday | 2016 | 12
4865 | 2016-12-28 23:27 | 2016-12-29 10:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-V1-33. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 23:27 | Night | Wednesday | 2016 | 12
4866 | 2016-12-29 10:52 | 2016-12-29 10:52 | 13.8KV 4D FEEDER #3 | Fair | Planned Maintenance | 6 | 10:52-11:04 Manually opened / Closed 4D OCB fdr #3. To Replacing @2 broken Pin Insulator o/p #4D-67. (15Wells were off during the Job done) Cause: Planned Maintenance. |  | 1 | 10:52 | Morning | Thursday | 2016 | 12
4867 | 2016-12-29 15:09 | 2016-12-29 15:09 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 4 | 15:09 It was reported b/o for Tx at Well Pilar #01. (Ketigul fdr #1) Not checked yet, due to heavy rain at the spot. |  | 1 | 15:09 | Afternoon | Thursday | 2016 | 12
4868 | 2016-12-29 15:09 | 2016-12-30 10:41 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 4 | 10:41 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Pilar #01. (Ketigul fdr #1) Replaced the b/o fuse above with same size, then energized the Tx. Cause: Animal. (Monkey) |  | 1 | 15:09 | Afternoon | Thursday | 2016 | 12
4869 | 2016-12-30 06:00 | 2016-12-30 06:00 | 13.8KV 6D FEEDER #6 | Fair | Lightning | 0 | 6D OCB fdr #6 T/R 1x. Not checked yet. (Minas GS-3 WIP Down / no prod. loss) |  | 1 | 6:00 | Morning | Friday | 2016 | 12
4870 | 2016-12-30 06:00 | 2017-02-01 22:02 | 13.8KV 6D FEEDER #6 | Fair | Lightning | 0 | Checked & found, 6D OCB fdr #6 T/R 1x Ctr: 571-572 R/F: 51@1. Patrolled the line & found, @1 broken L/A of LBS #6D-104. Cause: Lightning. |  | 1 | 6:00 | Morning | Friday | 2016 | 12
4871 | 2016-12-30 08:57 | 2016-12-30 08:57 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 170 | 08:57 D.Field VCB fdr #4 T/R 1x Counter & Realay flag are not reported yet. It was reported some wells were off at Area-06, Road-S3. (D.Field fdr #4) 15:00 Checked & found, a Dead Bird (Enggang) on Recl. 06-S3-19. (Also burnt out Recloser bushing o/p #06-S3-19) Transferring load of Recl. 06-S3-19 to D.Field fdr #2. 17:30 Close LBS #06-S3-02. (After isolated Recloser above) Cause: Animal. (Enggang Bird) |  | 1 | 8:57 | Morning | Friday | 2016 | 12
4872 | 2016-12-30 09:33 | 2016-12-30 09:33 | 4.16KV NO RUMBAI FEEDER #2 | Fair | Planned Maintenance | 0 | 09:33-10:54 Manual Open & Closed 4.16Kv N.Rumbai VCB fdr #2 To cutting danger High Trees near power line at near Complex Sawit-133. Cause: Planned Maintenance. |  | 1 | 9:33 | Morning | Friday | 2016 | 12
4873 | 2016-12-31 06:02 | 2016-12-31 06:02 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | D.Field ACB fdr #1 T/R 1x. D.Field fdr #3 Load dropped 9A (114-105A). Not checked yet. |  | 1 | 6:02 | Morning | Saturday | 2016 | 12
4874 | 2016-12-31 06:02 | 2017-04-01 08:12 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Checked & found, D.Field ACB fdr #1 T/R 1x Ctr: 679-680 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 6:02 | Morning | Saturday | 2016 | 12
4875 | 2016-12-31 13:50 | 2016-12-31 13:50 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | 13:50 It was reported b/o fuse for Tx o/p #01-04-30. (D.Field fdr #1) 14:45 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #01-04-30. Replaced b/o fuse above with the same size, then energized the Tx. Couse: Unidentified (Fuse). |  | 1 | 13:50 | Afternoon | Saturday | 2016 | 12
4876 | 2016-12-31 17:18 | 2016-05-12 17:00 | 13.8KV CENTRAL DURI FEEDER #13 | Cloudy and Lightning | Lightning | 0 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:18 | Afternoon | Saturday | 2016 | 12
4877 | 2016-12-31 17:18 | 2016-12-31 17:18 | 13.8KV CENTRAL DURI FEEDER #13 | Cloudy and Lightning | Lightning | 0 | C.Duri ACB fdr #13 T/R 1x Ctr: 196-197 R/F: 51N. The line is not patrolled yet. |  | 1 | 17:18 | Afternoon | Saturday | 2016 | 12
4878 | 2016-12-31 21:57 | 2016-12-31 21:57 | 13.8KV LIBO FEEDER #2 | Fair | Broken Fuse Cut Out | 4 | Libo OCB fdr #2 T/R 1x. Not Checked yet. |  | 1 | 21:57 | Night | Saturday | 2016 | 12
4879 | 2016-12-31 21:57 | 2017-03-01 19:22 | 13.8KV LIBO FEEDER #2 | Fair | Broken Fuse Cut Out | 4 | Checked & found, Libo OCB fdr #2 T/R 1x Ctr: 429-430 R/F: 50@3. Patrolled the line & found, @3 broken FCO o/p #29BZ-02. Cause: Broken Fuse Cut Out. |  | 1 | 21:57 | Night | Saturday | 2016 | 12
4880 | 2017-01-01 14:37 | 2017-01-01 14:37 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 55 | Kutigul VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 14:37 | Afternoon | Sunday | 2017 | 1
4881 | 2017-01-01 14:37 | 2017-02-01 15:38 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 55 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 224-225 R/F: 51@2. Patrolled the line & found, @2 broken FCO on TP of Well Pagar #44. Cause: Lightning. |  | 1 | 14:37 | Afternoon | Sunday | 2017 | 1
4882 | 2017-01-01 15:18 | 2017-01-01 15:18 | MINAS POWER PLANT | Fair |  | - | 15:18 S/U MGT #4, then on line the unit at 15:32. |  | 1 | 15:18 | Afternoon | Sunday | 2017 | 1
4883 | 2017-01-01 15:43 | 2017-01-01 15:43 | MINAS POWER PLANT | Fair |  | - | 15:43 S/U MGT #3, then on line the Unit at 16:16. |  | 1 | 15:43 | Afternoon | Sunday | 2017 | 1
4884 | 2017-01-01 19:44 | 2017-01-01 19:44 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 0 | 19:44 It was reported b/o fuse for Tx o/p #40BA-35 (at WTP-125). (C.Duri fdr #1) 21:24 Checked & found, @1 b/o 3.1SF fuse for 112.5kva Tx o/p #40BA-35. Replaced b/o above with the same size & energized the Tx. Cause: Animal. (Squirrel) |  | 1 | 19:44 | Night | Sunday | 2017 | 1
4885 | 2017-02-01 00:04 | 2017-02-01 00:04 | CENTRAL DURI POWER PLANT |  |  | - | 00:04 Off line CGT #5, then S/D the Unit for S/B. (Prior to repairing Deverter Duct for HRSG-5) |  | 1 | 0:04 | Night | Wednesday | 2017 | 2
4886 | 2017-02-01 10:18 | 2017-02-01 10:18 | 13.8KV DURI FIELD FEEDER #2 | Fair | Planned Maintenance | 0 | 10:18 Open HLC o/p #06-S1-01 to replace Dead End insulator. (after shuting down 2 wells at downstream of HLC above) 11:34 Closed HLC o/p #06-S1-01. (after completing the job) Cause: Plan Maintenance. | 1111 | 1 | 10:18 | Morning | Wednesday | 2017 | 2
4887 | 2017-02-01 10:55 | 2017-02-01 10:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr #1 Load dropped 45A (131-86A). Not checked yet. | 1111 | 1 | 10:55 | Morning | Wednesday | 2017 | 2
4888 | 2017-02-01 10:55 | 2017-04-01 08:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 245-246. Patrolled the line, but found nothing. Cause: Unidentified. | 1111 | 1 | 10:55 | Morning | Wednesday | 2017 | 2
4889 | 2017-02-01 17:34 | 2017-02-01 17:34 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuses for Tx o/p #07-T1-06. Not checked yet. | 11111 | 1 | 17:34 | Afternoon | Wednesday | 2017 | 2
4890 | 2017-02-01 17:34 | 2017-03-01 10:25 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 10:25 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-T1-06. (D.Field fdr #2) Replace b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 11111 | 1 | 17:34 | Afternoon | Wednesday | 2017 | 2
4891 | 2017-03-01 14:26 | 2017-03-01 14:26 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 14:26 It was reported b/o fuses for Tx o/p #04-05-06. (C.Duri fdr #9) 16:20 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-05-06. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 1111 | 1 | 14:26 | Afternoon | Wednesday | 2017 | 3
4892 | 2017-03-01 16:10 | 2017-03-01 16:10 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 0 | 16:10 It was reported b/o fuses for Tx o/p #04-07-28. (C.Duri fdr #8) 17:00 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-07-28. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 11111 | 1 | 16:10 | Afternoon | Wednesday | 2017 | 3
4893 | 2017-03-01 19:49 | 2017-03-01 19:49 | 13.8KV KETIGUL FEEDER#2 | Fair | Broken Fuse Cut Out | 72 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 19:49 | Night | Wednesday | 2017 | 3
4894 | 2017-03-01 19:49 | 2017-04-01 15:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Broken Fuse Cut Out | 72 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 225-226 R/F: 51N. Patrolled the line & found, @2 broken FCO on TP of Well Pagar #44. Cause: Broken Fuse Cut Out. |  | 1 | 19:49 | Night | Wednesday | 2017 | 3
4895 | 2017-03-01 20:36 | 2017-03-01 20:36 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 77 | 4D fdr #4 Load dropped 186A (227-41A). (the weather is heavy rain) Not checked yet. |  | 1 | 20:36 | Night | Wednesday | 2017 | 3
4896 | 2017-03-01 20:36 | 2017-04-01 10:31 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 77 | Checked & found, Recl. 4D-85 (4D fdr #4) T/SO. Ctr: 1614-1615. Blocked & closed Recl. 4D-85, Ok. Then released the block. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 20:36 | Night | Wednesday | 2017 | 3
4897 | 2017-04-01 23:59 | 2017-04-01 23:59 | CPI POWER SYSTEM | Rain | Normal Condition | - | CPI Power system normal condition. |  | 1 | 23:59 | Night | Saturday | 2017 | 4
4898 | 2017-05-01 03:36 | 2017-05-01 03:36 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 35 | Minas ACB fdr #2 T/R 1x Ctr: 61-62 R/F: 51N. The line is not patrolled yet. |  | 1 | 3:36 | Night | Monday | 2017 | 5
4899 | 2017-05-01 03:36 | 2017-06-01 19:35 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 35 | Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 3:36 | Night | Monday | 2017 | 5
4900 | 2017-05-01 10:26 | 2017-05-01 10:26 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 2 | 10:26 It was reported b/o fuse for Tx o/p #06-Q5-04B. (C.Duri fdr #14) 11:36 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #06-Q5-04B. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) |  | 1 | 10:26 | Morning | Monday | 2017 | 5
4901 | 2017-06-01 23:59 | 2017-06-01 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system normal condition. |  | 1 | 23:59 | Night | Thursday | 2017 | 6
4902 | 2017-07-01 09:00 | 2017-07-01 09:00 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified (Fuse) | 29 | 09:00 It was reported b/o fuse for Tx o/p #12-F9-19. 11:00 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #12-F9-19. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 9:00 | Morning | Saturday | 2017 | 7
4903 | 2017-07-01 13:22 | 2017-07-01 13:22 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified (Fuse) | 21 | 13:22 It was reported b/o fuse for Tx at Well Ampuh #22. 15:14 Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Ampuh #22. Tested the Tx & found, normal. (good reading) Then replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). | 1111 | 1 | 13:22 | Afternoon | Saturday | 2017 | 7
4904 | 2017-08-01 08:10 | 2017-08-01 08:10 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 18 | 08:10 It was reported b/o fuses for Tx at Well Sikaladi #04. 09:36 Checked & found, @2,@3 b/o 3.5SF fuses for 150Kva Tx at Well Sikladi #04. Performed TTR test and Megger, The TX good condition. Replaced b/o fuses above with sama size, then energized the Tx. Cause: Unidentified (Fuse). | 11111 | 1 | 8:10 | Morning | Tuesday | 2017 | 8
4905 | 2017-08-01 09:35 | 2017-08-01 09:35 | 13.8KV NORTH DURI FEEDER #1 | Fair | Planned Maintenance | 0 | 09:35 Shutdown 112.5Kva Tx o/p #12-E5-16. (2 Wells #3E-413A & 4E-40B were off during the Job done) To replacing 112.5Kva Tx leakage o/p above. 10:45 Re-Energized the Tx & S/U the wells. Cause: Plan maintenance. | 1111 | 1 | 9:35 | Morning | Tuesday | 2017 | 8
4906 | 2017-08-01 10:00 | 2017-08-01 10:00 | 13.8KV NORTH DURI FEEDER #1 | Fair | Planned Maintenance | 0 | 10:00 Shutdown 112.5Kva Tx o/p #12-E5-19. (Some Wells were off during the Job done) To replacing 112.5Kva Tx leakage o/p above. 12:00 Re-Energized the Tx & S/U the wells. Cause: Plan maintenance. | 1111 | 1 | 10:00 | Morning | Tuesday | 2017 | 8
4907 | 2017-08-01 10:01 | 2017-08-01 10:01 | 13.8KV NORTH DURI FEEDER #1 | Fair | Planned Maintenance | 0 | 10:01 Shutdown 112.5Kva Tx o/p #12-E5-22. (Some Wells were off during the Job done) To replacing 112.5Kva Tx leakage o/p above. 12:00 Re-Energized the Tx & S/U the wells. Cause: Plan maintenance. | 11111 | 1 | 10:01 | Morning | Tuesday | 2017 | 8
4908 | 2017-09-01 23:59 | 2017-09-01 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power System is normal operation. | 1111 | 1 | 23:59 | Night | Friday | 2017 | 9
4909 | 2017-10-01 06:15 | 2017-10-01 06:15 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Dead End Insulator | 0 | C.Duri fdr #6 Load dropped 56A (178-122A). (Load C.Duri fdr #9 fed by C.Duri fdr #6) Not checked yet. | 11111 | 1 | 6:15 | Morning | Sunday | 2017 | 10
4910 | 2017-10-01 06:15 | 2017-12-01 19:15 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Dead End Insulator | 0 | Checked & found, Recl. (C.Duri fdr #6) T/R 1x Ctr: 210-211. Patrolled the line & found, @3 F/O Dead end Insulator o/p #04-7-33. Cause: Dead end Insulator. | 11111 | 1 | 6:15 | Morning | Sunday | 2017 | 10
4911 | 2017-11-01 09:22 | 2017-11-01 09:22 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | Duri Field ACB fdr #2 T/R 1x. Not checked yet. |  | 1 | 9:22 | Morning | Wednesday | 2017 | 11
4912 | 2017-11-01 09:22 | 15/01/2017 14:51 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Duri Field ACB fdr #2 T/R 1x Ctr: 986-987 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 9:22 | Morning | Wednesday | 2017 | 11
4913 | 2017-11-01 14:46 | 2017-11-01 14:46 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 3 | 14:46-15:32 Manually opened fuse to shutdown 150Kva Tx at Well Sintong #02. For replacing broken dead end insulator o/p #26AE-12. Cause: Plan Maintenance. |  | 1 | 14:46 | Afternoon | Wednesday | 2017 | 11
4914 | 2017-12-01 07:09 | 2017-12-01 07:09 | 13.8KV 3D FEEDER #8 | Fair | Dead End Insulator | 23 | 3D OCB fdr #8 T/R 1x. Not checked yet. |  | 1 | 7:09 | Morning | Friday | 2017 | 12
4915 | 2017-12-01 07:09 | 15/01/2017 15:09 | 13.8KV 3D FEEDER #8 | Fair | Dead End Insulator | 23 | Checked & found, 3D OCB fdr #8 T/R 1x Ctr: 299-300 R/F: 51@1. Patrolled the line & found, @1 broken Dead end Insulator o/p #2D-29. Cause: Dead end Insulator. |  | 1 | 7:09 | Morning | Friday | 2017 | 12
4916 | 2017-12-01 08:01 | 2017-12-01 08:01 | 13.8KV 6D FEEDER #2 | Fair | Lightning Arrester | 43 | 6D fdr #2 Load dropped 172A (223-51A). 6DN fdr #4 Load dropped 70A (147-77A). T/O WIP at GS-3. Not checked yet. |  | 1 | 8:01 | Morning | Friday | 2017 | 12
4917 | 2017-12-01 08:01 | 15/01/2017 14:47 | 13.8KV 6D FEEDER #2 | Fair | Lightning Arrester | 43 | Checked & found, Recl. 6D-298 (6D fdr #2) T/R 2x Ctr: 49-51. Patrolled the line & found, @1 broken L/A o/p #6D-54. Cause: Lightning Arrester. |  | 1 | 8:01 | Morning | Friday | 2017 | 12
4918 | 2017-12-01 08:57 | 2017-12-01 08:57 | 13.8KV DARLING VCB FEEDER #6 | Fair | Unidentified | 204 | 08:57 Darling VCB fdr #6 T/O. (In block position for PT CEP clean up canal) (Darling fdr #6 parallel with C.Duri fdr #11 as a connection CDSG Bus #3 & #4 with the system) CGT #4 Islanding. (Bus #3 & #4 with Load C.Duri fdr #7 & fdr #8) 09:18 CGT #4 Tripped. By Alarm: Bearing Header Temperature high. (C.Duri Bus #3 & Bus #4 no power) 09:19 Manually open C.Duri fdr #8. (to reduce load Bus #3 & Bus #4) 09:20 Closed C.Duri ACB fdr #12. (Parallel with Darling fdr #4 to energizing Bus #3 & Bus #4) 09:42 S/U CGT #4, then on line the Unit at 09:58. 09:49 Manually closed Darling VCB fdr #6. (After patrolling the line & found, normal) 09:58 Manually closed C.Duri ACB fdr #8. Cause: Unidentified. |  | 1 | 8:57 | Morning | Friday | 2017 | 12
4919 | 2017-12-01 08:57 | 15/01/2017 10:53 | 13.8KV DARLING VCB FEEDER #6 | Fair | Unidentified | 204 | Checked & found, Darling VCB fdr #6 T/O. (In block position) Ctr: 229-230 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 8:57 | Morning | Friday | 2017 | 12
4920 | 2017-12-01 09:18 | 2017-12-01 09:18 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 09:18 CGT #4 T/O. By Alarm: Bearing header Temperature high. (no power 480V, due to Manually open Generator breaker) SOP to paralleling CGT #4 with the system. (after Bus #3 & Bus #4 energize from Darling fdr #4 & C.Duri fdr #12) 09:42 S/U CGT #4, then on line the Unit at 09:58. |  | 1 | 9:18 | Morning | Friday | 2017 | 12
4921 | 2017-12-01 11:47 | 2017-12-01 11:47 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 0 | 11:47 Manually opened Bekasap OCB fdr #2. (Requested by Bekasap operator) Due to 16" Production line broken at in front of Bekasap-GS. 23:30 Closed Bekasap OCB fdr #2. Cause: Plant Maintenance. (No prod. loss charge to PGT) |  | 1 | 11:47 | Morning | Friday | 2017 | 12
4922 | 2017-12-01 11:47 | 2017-12-01 11:47 | 13.8KV BEKASAP FEEDER #3 | Fair | Planned Maintenance | 0 | 11:47 Manually opened Bekasap OCB fdr #3. (Requested by Bekasap operator) Due to 16" Production line broken at in front of Bekasap-GS. 23:30 Closed Bekasap OCB fdr #3. Cause: Plant Maintenance. (No prod. loss charge to PGT) |  | 1 | 11:47 | Morning | Friday | 2017 | 12
4923 | 2017-12-01 14:46 | 2017-12-01 14:46 | 115KV CENTRAL DURI - BATANG LINE | Fair | Others | 558 | 14:46 115KV CDSY OCB #31 T/R 1x. 115KV CDSY OCB #33 T/R 1x. 115KV Sintong GCB #25 T/SO, then Closed at 14:49. (115KV CDSY - Batang/Sintong line T/SO) Batang Subtation No power at that time. Respectively load dropped: (Due to Voltage drop at Bangko area) So.Balam fdr #1 load dropped 14A (120-106A). Nella fdr #1 load dropped 99A (280-181A). Nella fdr #2 load dropped 24A (86-62A). Bangko fdr #1 load dropped 39A (206-167A). Bangko fdr #4 load dropped 50A (232-182A). Menggala fdr #1 load dropped 125A (186-61A). Sintong fdr #1 load dropped 20A (82-62A). 14:52 115KV CDSY OCB #31 T/R again. 115KV CDSY OCB #33 T/SO, then Closed at 15:12. 115KV Sintong GCB #25 T/SO, then Closed at 15:04. 15:33 115KV CDSY OCB #31 T/R again. 115KV CDSY OCB #33 T/SO, then Closed but tripped again. 115KV Sintong GCB #25 T/SO, then Closed at 15:36. 16:48 It was reported that there was Tarpaulin hanging on 115KV Batang power line o/p #BTG-79. 17:11 Manually open 115KV CDSY OCB #31, then Closed at 17:18. Manually open 115KV Sintong GCB #25, then Closed at 17:19. Manually closed 115KV CDSY OCB #33 at 17:20. (To take down the Tarpaulin o/p #BTG-79) Cause: Others. (Tarpaulin hang on 115KV o/p #BTG-79) Production loss: So.Balam fdr #1 : 179 Bbls / 7 Wells. Menggala fdr #1 : 364 Bbls / 24 Wells. ---------------------------------------------- Total : 543 Bbls / 31 Wells -----> Balam GS. Bangko fdr #1 : 153 Bbls / 78 Wells. Bangko fdr #4 : 72 Bbls / 37 Wells. Nella fdr #1 : 133 Bbls / 73 Wells. Nella fdr #2 : 35 Bbls / 22 Wells. ----------------------------------------------- Total : 393 Bbls / 250 Wells -----> Bangko GS. Grand Total : 936 Bbls / 281 Wells. | 11111 | 1 | 14:46 | Afternoon | Friday | 2017 | 12
4924 | 2017-12-01 14:46 | 13/01/2017 10:46 | 115KV CENTRAL DURI - BATANG LINE | Fair | Others | 558 | Checked & found: -115KV Sintong GCB#25 T/SO. Ctr: 292-296 R/F: 21@3, 21G-Z1, 67N(Inst.) & 87L@3. -115KV CDSY OCB #31 & OCB #33, Counter & Relay flag are not reported yet. | 11111 | 1 | 14:46 | Afternoon | Friday | 2017 | 12
4925 | 2017-12-01 16:15 | 2017-12-01 16:15 | 13.8KV BATANG FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Batang OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 16:15 | Afternoon | Friday | 2017 | 12
4926 | 2017-12-01 16:15 | 19/01/2017 07:22 | 13.8KV BATANG FEEDER #2 | Cloudy and Lightning | Lightning | 0 | Checked & found, Batang OCB fdr #2 T/R 1x Ctr: 135-136 R/F: 51N. Patrolled the line & found: -@1 Broken L/A o/p #35AE-24. -@1 Broken Pin Insulator o/p #20AJ-28. Cause: Lightning. |  | 1 | 16:15 | Afternoon | Friday | 2017 | 12
4927 | 2017-01-13 03:40 | 2017-01-13 03:40 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | 03:40 Sintong fdr #1 Load dropped 29A (82-53A). Sintong GFPC T/R 1x. Not checked yet. 02:16 Checked & found, Recl. 25AD-26 (Sintong fdr #1) T/R 1x Ctr: 112-113. Also found, Sintong GFPC T/R 1x Ctr: 932-933. Patrolled the line, but found nothing. Cause: Unidentified. | 1111 | 1 | 3:40 | Night | Friday | 2017 | 1
4928 | 2017-01-13 09:40 | 2017-01-13 09:40 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified (Fuse) | 6 | 09:40 It was reported b/o fuse for Tx o/p #03-4-39. (C.Duri fdr #5) 10:20 Checked & found, @3 b/o 3.1SF fuse for 112.5Kva Tx o/p #03-4-39. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 9:40 | Morning | Friday | 2017 | 1
4929 | 2017-01-14 10:20 | 2017-01-14 10:20 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 0 | 10:20 It was reported b/o fuse for Tx o/p #04-7-28. (C.Duri fdr #8) 14:00 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #04-7-28. Replaced b/o fuse above with the same size & energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 10:20 | Morning | Saturday | 2017 | 1
4930 | 2017-01-14 14:30 | 2017-01-14 14:30 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Planned Maintenance | 0 | 14:30 Manual open fuse for 112.5Kva Tx o/p #06-Q1-09. (C.Duri fdr #14) 15:20 Replaced 112.5Kva Tx with the same size o/p #06-Q1-09, and energized the Tx. Cause: Maintenance Job. (Tx Leaks) |  | 1 | 14:30 | Afternoon | Saturday | 2017 | 1
4931 | 2017-01-14 17:12 | 2017-01-14 17:12 | CENTRAL DURI POWER PLANT |  |  | - | 17:12 S/U CGT #5, then on line the Unit at 17:29. |  | 1 | 17:12 | Afternoon | Saturday | 2017 | 1
4932 | 2017-01-15 06:23 | 2017-01-15 06:23 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified | 0 | Duri Community ACB fdr #5 T/R 1x. Not checked yet. |  | 1 | 6:23 | Morning | Sunday | 2017 | 1
4933 | 2017-01-15 06:23 | 2017-01-18 16:38 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #5 T/R 1x Ctr: 104-105 R/F: 51N. Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 6:23 | Morning | Sunday | 2017 | 1
4934 | 2017-01-15 06:50 | 2017-01-15 06:50 | 13.8KV 3D TX-1 GFPC | Fair | Unidentified | 0 | 3D GFPC Tx #1 T/R 1x. Ground fault alarm on 3D fdr #4. (No load dropped at any fdrs) Not checked yet. |  | 1 | 6:50 | Morning | Sunday | 2017 | 1
4935 | 2017-01-15 06:50 | 2017-01-17 08:30 | 13.8KV 3D TX-1 GFPC | Fair | Unidentified | 0 | Checked & found, 3D GFPC-TX #1 T/R 1x Ctr: 4099-4100. Patrolled 3D fdr #4 line, but found nothing. Cause: Unidentified. |  | 1 | 6:50 | Morning | Sunday | 2017 | 1
4936 | 2017-01-15 08:00 | 2017-01-15 08:00 | MINAS POWER PLANT |  |  | - | Off line MGT #6, then S/D the Unit for S/B. |  | 1 | 8:00 | Morning | Sunday | 2017 | 1
4937 | 2017-01-15 15:00 | 2017-01-15 15:00 | DARLING SUBSTATION | Fair | Animal | 0 | It was reported b/o fuse for Sta. Service Tx at Darling Substation. Checked & found, @1 b/o 1.0SF fuse for 50Kva Tx at Darling Substation. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Bird) |  | 1 | 15:00 | Afternoon | Sunday | 2017 | 1
4938 | 2017-01-16 05:55 | 2017-01-16 05:55 | 13.8KV KOTABATAK FEEDER #2 | Fair | Others | 142 | It was reported b/o fuse for Tx at Well KB #46. (OKB fdr #2) Not checked yet. |  | 1 | 5:55 | Morning | Monday | 2017 | 1
4939 | 2017-01-16 05:55 | 2017-01-17 16:10 | 13.8KV KOTABATAK FEEDER #2 | Fair | Others | 142 | Checked & found, @2 loose connection & spark on fuse holder for 550Kva Tx on TP of Well KB #46. Replaced Fuse holder & fuse link above with the same size (30K), then energized the Tx. Cause: Others. (Spark & loose connection of Fuse holder) |  | 1 | 5:55 | Morning | Monday | 2017 | 1
4940 | 2017-01-16 10:20 | 2017-01-16 10:20 | 13.8KV NORTH DURI FEEDER #2 | Fair | Planned Maintenance | 2 | 10:20-12:38 Shutdown Well #4J-82F, then Open HLC for 112.5Kva Tx o/p #... To replacing @2,@3 Pin Insulators o/p #10-J8-04 & @1 o/p #10-J8-05. Cause: Planned Maintenance. |  | 1 | 10:20 | Morning | Monday | 2017 | 1
4941 | 2017-01-16 17:26 | 2017-01-16 17:26 | MINAS POWER PLANT |  |  | - | 17:26 S/U MGT #6, then on line the Unit at 17:45. |  | 1 | 17:26 | Afternoon | Monday | 2017 | 1
4942 | 2017-01-16 17:50 | 2017-01-16 17:50 | MINAS POWER PLANT |  |  | - | 17:50 Off line MGT #1, then S/D the Unit for S/B. |  | 1 | 17:50 | Afternoon | Monday | 2017 | 1
4943 | 2017-01-16 18:16 | 2017-01-16 18:16 | MINAS POWER PLANT |  |  | - | 18:16 Off line MGT #4, then S/D the Unit for S/B. |  | 1 | 18:16 | Afternoon | Monday | 2017 | 1
4944 | 2017-01-17 09:00 | 2017-01-17 09:00 | 4.16KV SO RUMBAI FEEDER #2 | Fair | Animal | 0 | 09:00 It was reported b/o fuse for Tx at Rumbai Filling Sta. (S.Rumbai fdr #2) 11:00 Checked & found, @ b/o 1.0SF fuse for 25Kva Tx at Rumbai Filling Sta.. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) |  | 1 | 9:00 | Morning | Tuesday | 2017 | 1
4945 | 2017-01-17 09:50 | 2017-01-17 09:50 | 13.8KV 8D FEEDER #5 | Fair | Planned Maintenance | 5 | 09:50 S/D Well #8E-22N, and Opened FCO for 300Kva Tx on TP of Well #8E-22N. (8D fdr #5) 16:30 Replaced 300Kva Tx due to Oil Leaks and Replaced Secondary cable. Cause: Planned Maintenance. (Transformer Oil Leaks). |  | 1 | 9:50 | Morning | Tuesday | 2017 | 1
4946 | 2017-01-17 14:40 | 2017-01-17 14:40 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 10 | 14:40 It was reported b/o fuse for Tx o/p #09-R4-01. (C.Duri fdr #4) 15:20 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #09-R4-01. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 14:40 | Afternoon | Tuesday | 2017 | 1
4947 | 2017-01-17 17:57 | 2017-01-17 17:57 | MINAS POWER PLANT |  |  | - | 17:57 S/U MGT #1, then On line the Unit at 18:08. |  | 1 | 17:57 | Afternoon | Tuesday | 2017 | 1
4948 | 2017-01-17 19:08 | 2017-01-17 19:08 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Fair | Unidentified | 0 | 19:08 4160V Dumai (Hsg.) ACB fdr #4 T/SO. 19:19 Blocked & closed Dumai 4160V ACB fdr #4, Ok. Then released the block. Not checked & patrolled yet. |  | 1 | 19:08 | Night | Tuesday | 2017 | 1
4949 | 2017-01-17 19:08 | 2017-01-20 08:56 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Fair | Unidentified | 0 | Checked & found, 4160V Dumai (Hsg) ACB fdr #4 T/R 2x Ctr: 264-266 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 19:08 | Night | Tuesday | 2017 | 1
4950 | 2017-01-18 10:37 | 2017-01-18 10:37 | 13.8KV 5B FEEDER #3 | Fair | Planned Maintenance | 8 | 10:37 S/D 8 Wells, and Opened LBS #4C-45. (5B fdr #3) 12:20 Install 3 Span static wire Cause: Planned Maintenance. |  | 1 | 10:37 | Morning | Wednesday | 2017 | 1
4951 | 2017-01-18 13:48 | 2017-01-18 13:48 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 321 | 13:48 N.Duri VCB fdr #11 T/O. (on Block status for PT Multy Structure activity) 14:00 Manually Closed on Block position N.Duri VCB fdr #11, but failed to Close. (from remote) (After Ensuring PT Multy Structure in normal operation) 15:05 Checked & found, N.Duri VCB fdr #11 T/O. Ctr: 149-150 R/F: 51N. Manually Closed N.Duri VCB fdr #11, Ok. (from Local) Not patrolled yet. |  | 1 | 13:48 | Afternoon | Wednesday | 2017 | 1
4952 | 2017-01-18 13:48 | 2017-01-21 19:48 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 321 | Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 13:48 | Afternoon | Wednesday | 2017 | 1
4953 | 2017-01-18 14:17 | 2017-01-18 14:17 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 9 | Libo OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 14:17 | Afternoon | Wednesday | 2017 | 1
4954 | 2017-01-18 14:17 | 2017-01-19 15:50 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 9 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 413-414 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 14:17 | Afternoon | Wednesday | 2017 | 1
4955 | 2017-01-18 15:25 | 2017-01-18 15:25 | 13.8KV 3D TX-1 GFPC | Fair | Unidentified | 0 | 3D GFPC-TX #1 T/R 1x. Ground fault alarm at 3D fdr #2. (No Load dropped at any feeders) Not checked yet. |  | 1 | 15:25 | Afternoon | Wednesday | 2017 | 1
4956 | 2017-01-18 15:25 | 2017-01-20 09:04 | 13.8KV 3D TX-1 GFPC | Fair | Unidentified | 0 | Checked & found, 3D GFPC-TX #1 T/R 1x Ctr: 100-101. Patrolled 3D fdr #2 line, but found nothing. Cause: Unidentified. |  | 1 | 15:25 | Afternoon | Wednesday | 2017 | 1
4957 | 2017-01-19 01:33 | 2017-01-19 01:33 | NORTH DURI POWER PLANT | Fair | Equipment Failure | 2479 | 01:33 NDC-CT #3 Tripped, By Alarm: Loss of Excitation. Frequency System dropped to 59:46Hz. (Load Shedding level #2) 3D fdr #6 T/O, then closed at 02:00. 4D fdr #4 T/O, then closed at 04:30. 4D fdr #5 T/O, then closed at 04:30. 4B fdr #1 T/O, then closed at 02:19. 4B fdr #4 T/O, then closed at 02:17. 5B fdr #4 T/O, then closed at 04:33. 5B fdr #5 T/O, then closed at 03:12. 8D fdr #1 T/O, then closed at 03:14. 8D fdr #3 T/O, then closed at 03:13. BOB load dropped 8MW (17-9 MW). 4D fdr #1 Load dropped 176A (245-69A). 4D fdr #6 Load dropped 89A (149-66A). 3D fdr #5 Load dropped 33A (200-167A). 6D fdr #6 Load dropped 40A (246-206A). 8D fdr #4 Load dropped 52A (173-121A). 8D fdr #8 Load dropped 1136A (180-67A) (Pump Off). 8D fdr #9 Load dropped 120A (175-55A) (Pump Off). CKB fdr #1 Load dropped 16A (325-309A). CKB fdr #5 Load dropped 14A (169-155A). 115KV MSY-LUKUT (BOB) load dropped 8Mw (17-9Mw) Bangko fdr #1 load dropped 48A (209-161A). Bangko fdr #4 load dropped 58A (234-176A). Nella fdr #1 load dropped 17A (286-269A). Sintong fdr #2 load dropped 67A (222-157A). So.Balam fdr #1 load dropped 9A (122-113A). So.Balam fdr #4 load dropped 14A (1692155A). 03:29 NDC-CT #3 Shutdown, but 230KV GCB #33 & GCB #35 Not Open. (NDC #3 as a Motor status) 03:34 Manual Open GCB #35. (From DSC) 04:22 Manual Open GCB #33. (From N.Duri Subst.) 03:29 3D fd #6 T/O, then closd at 04:09. 03:42 Man. Openned 8D fdr #1, then closed at 04:25. Man. Openned 8D fdr #3, then closed at 04:25. 03:43 Man. Openned 4D fdr #3, then closed at 04:30. 03:48 Man. Openned 4D fdr #2, then closed at 04:30. 03:50 Man. Openned 4B fdr #6, then closed at 04:33. 03:56 Man. Openned 5B fdr #5, then closed at 04:33. 03:30 S.Balam fdr #4 Load dropped 30A (169-139A). 03:31 Sintong fdr #1 Load dropped 7A (77-70A). Sintong fdr #2 Load dropped 38A (222-184A). 03:35 Ketigul fdr #2 Load dropped 26A (219-193A). 03:43 CKB fdr #2 Load dropped 41A (253-212A). CKB fdr #3 Load dropped 37A (132-95A). CKB fdr #6 Load dropped 21A (203-182A). 03:38 OKB fdr #2 Load dropped 7A (248-241A). 04:13 5B fdr #6 Load dropped 63A (190-127A). 04:21 6D fdr #1 Load dropped 66A (236-170A). 04:39 4D fdr #3 Load dropped 54A (121-67A). 03:39 6D fdr #3 Load dropped 115A ( 334-219A). Pump Off. 03:35 6D fdr #4 Load dropped 61A (122-61A). Pump Off 02:25 S/U MGT #4, then On Line the Unit at 02:40. 03:25 S/U MGT #2, then On Line the Unit at 04:11. 14:45 Man. Opened 3D OCB fdr #4, then Closed at 17:33. (as Requested by Minas GS-6 operator) Due to Gathering tank at GS#6 High level. 14:38 S/U NDC-CT #3, then on line the unit at 15:05. 16:00 Off line MGT #2, then S/D the Unit for S/B. 16:34 Off line MGT #5, then S/D the Unit for S/B. Cause: Equipment Failure. (Broken Excitaion Diode & burnt out fuse of Relay coil) Production Loss: GS 1 : 121 Bbls, 12 wells. GS 2 : 81 Bbls, 11 wells. GS 3 : 136 Bbls, 21 wells. GS 4 : 81 Bbls, 11 wells. GS 5 : 503 Bbls, 93 wells. GS 6 : 83 Bbls, 37 wells. Bangko : 847 Bbls, 25 wells. Balam : 702 Bbls, 19 wells. Total Prod loss : 2590 Bbls, 223 wells. | 123 | 1 | 1:33 | Night | Thursday | 2017 | 1
4958 | 2017-01-19 09:54 | 2017-01-19 09:54 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | C.Duri fdr #14 Load dropped 40A (239-199). Not checked yet. |  | 1 | 9:54 | Morning | Thursday | 2017 | 1
4959 | 2017-01-19 09:54 | 2017-01-22 07:51 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | Checked & found, Recl. 05-N3-02 (C.Duri fdr #14) T/R 1x Ctr: 149-150. Patrolled the Line & found, a dead Monkey under pole #05-N3-04. Cause: Animal. (Monkey) |  | 1 | 9:54 | Morning | Thursday | 2017 | 1
4960 | 2017-01-19 16:29 | 2017-01-19 16:29 | 44KV BEKASAP MAIN - BEKASAP SUBST LINE | Fair | Substation Failure (LA) | 372 | 16:29 44KV Bekasap Main OCB #1 (Power TX-C) T/O, Ctr:66662-77773, R/F:50 @B, 87T, 86T. Bekasap fdr #1 & fdr #2. (No Power) 17:30 Found, @2 Broken L/A & touching to conductor of 44KV TX-C at Bekasap Subst. 17:50 Man. Opened Bekasap OCB fdr #1 and fdr #2. 18:10 Transfer Load Bekasap fdr #1 to Bekasap fdr #3, by Closing LBS #3S-62. 18:30 Transfer Load Bekasap fdr #2 to Bekasap fdr #3, by Closing LBS #38-BD-35. 19:30 Closed LBS #37-BD-11. 19:32 Opened LBS #38-BD-35. 19:35 Normalized operation of Recl. 37-BD-12. (after unplugging the Recloser control cable) Cause: Substation Failure (Broken L/A). 24-Jan-2017 09:51 Closed 44KV Bekasap Main GCB #1. To energized Bekasap Main TXP-C. (After replacing broken L/A of the TXP-C) To normalize Load Bekasap main fdr #2 and Bekasap Main fdr #3. 10:11 Open LBS #1-2 o/p #37BD-16. 10:16 Closed Bekasap Main OCB fdr #2. (Bekasap Main fdr #2 back to normal) 10:11 Open LBS #1-3 o/p #37BD-16. 10:16 Closed Bekasap Main OCB fdr #1. (Bekasap Main fdr #1 back to normal) | 111 | 1 | 16:29 | Afternoon | Thursday | 2017 | 1
4961 | 2017-01-19 19:00 | 2017-01-19 19:00 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Secondary Cable | 0 | 19:00 It was reported b/o fuse for Tx at Well Ampuh #22. (So.Bekasap fdr #1) 19:45 Electrician found, Surface Cable Low magger. PGT is not checked yet. |  | 1 | 19:00 | Night | Thursday | 2017 | 1
4962 | 2017-01-19 19:00 | 2017-01-20 17:00 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Secondary Cable | 0 | Checked & found, @1 b/o 3.5SF fuse for 150Kva Tx at Well Ampuh #22. Replaced b/o fuse above with the same size & energized the Tx. Cause: Surface cable. (Low megger reading) |  | 1 | 19:00 | Night | Thursday | 2017 | 1
4963 | 2017-01-20 01:56 | 2017-01-20 01:56 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 32 | So.Bekasap OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 1:56 | Night | Friday | 2017 | 1
4964 | 2017-01-20 01:56 | 2017-01-21 18:17 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 32 | Checked & found, So.Bekasap OCB fdr #1 T/R 1x Ctr: 347-348 R/F: 51N. Patrolled the Line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 1:56 | Night | Friday | 2017 | 1
4965 | 2017-01-20 02:44 | 2017-01-20 02:44 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 56 | 02:44 Minas ACB fdr #1 T/SO. Ctr: 56-57 R/F: 51@3. 03:13 Blocked & closed, Minas ACB fdr #1, Ok. Then release the block. Not patrolled yet. |  | 1 | 2:44 | Night | Friday | 2017 | 1
4966 | 2017-01-20 02:44 | 2017-01-23 18:28 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 56 | Patrolled the Line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 2:44 | Night | Friday | 2017 | 1
4967 | 2017-01-20 08:28 | 2017-01-20 08:28 | SOUTH BALAM SUBSTATION | Cloudy | Substation Failure (CT) | 3914 | 08:28 115KV So.Balam C/S T/O. So.Balam VCB fdr #4 T/O. (So.Balam Substation blackout) 09:25 Checked & found, 115KV So.Balam C/S T/O. Ctr: 172-173 R/F: 87@2 & 86T. Checked the Tx Visually is good / normal condition. Also found, 13.8KV So.Balam VCB fdr #4 T/O. Ctr: 306-307 R/F: Back up relay Trip, @B. Then Opened both side Isolation switch of So.Balam fdr #4. Man. Opened So.Balam VCB fdr #1, fdr #2 & fdr #3. 09:34 Man. Closed 115KV So.Balam C/S, Ok. (After resetting the Pick up Relay) 09:38 Man. Closed 13.8KV So.Balam VCB fdr #2. 09:38 Man. Closed 13.8KV So.Balam VCB fdr #3. 09:45 Man. Closed 13.8KV So.Balam VCB fdr #1. 09:50 Closed both side Isolation switches of So.Balam VCB fdr #4 09:57 Man. Closed 13.8KV So.Balam VCB fdr #4. (And Continued patrolling the line) 10:00 115KV So.Balam C/S T/O again. (So.Balam Substation blackout again) 10:03 Checked & found, 115KV So.Balam C/S T/O again. Ctr: 173-174. So.Balam TX R/F: Latchet, W1,N,T,OC. (86T,Primary Winding, 51N) Opened both isolation switches of So.Balam VCB fdr #4. 10:17 Man. Closed 115KV So.Balam C/S, Ok. 10:20 Man. Closed 13.8KV So.Balam VCB fdr #2. 10:23 Man. Closed 13.8KV So.Balam VCB fdr #3. 10:24 Man. Closed 13.8KV So.Balam VCB fdr #1. 11:20 Closed LBS #22Y-24. (So.Balam fdr #4 Transfer to So.Balam fdr #3) (To investigate So.Balam VCB fdr #4 breaker & relay) 11:23 115KV So.Balam C/S T/O again. Ctr: 174-175. So.Balam TX, R/F: Latchet, W1,N,T,OC. (86T,Primary Winding, 51N) 11:26 Man. Opened 13.8KV So.Balam VCB fdr #1, fdr #2 & fdr #3. 11:29 Opened LBS #22Y-24. (to normalize load of So.Balam fdr #4) 11:30 Man. Closed 115KV So.Balam C/S, Ok. 11:31 Man. Closed 13.8KV VCB fdr #2. 11:32 Man. Closed 13.8KV VCB fdr #3. 11:33 Man. Closed 13.8KV VCB fdr #1. So.Balam VCB fdr #4 Under investigation & finishing Patrol the line SoBalam fdr #4. 16:30 Disabled Neutral Over Current Relay (51N) protection of So.Balam TX. (The TX Protection DIfferential Relay 87 still Active) 16:40 Man. Closed So.Balam VCB fdr #4, Ok. Cause: Under Investigation. | 123 | 1 | 8:28 | Morning | Friday | 2017 | 1
4968 | 2017-01-20 08:28 | 2017-01-21 11:00 | SOUTH BALAM SUBSTATION | Cloudy | Substation Failure (CT) | 3914 | 11:00 Continued troubleshooting of 115KV TX So.Balam Substation Prtection system. Checked & found, the input current Relay reading was not balance. (@1-64A, @2-32A, @3-64A) Changed @2 CT with the stand by one. (after Bypassing 115KV So.Balam C/S) Normalized protection system of 115KV So.Balam power Tx. Relay Input Current reading @1-64A, @2-64A, @3-64A. (After replacing CT @2) Cause: Substation Failure (Broken CT). | 123 | 1 | 8:28 | Morning | Friday | 2017 | 1
4969 | 2017-01-20 18:00 | 2017-01-20 18:00 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 53 | It was reported b/o fuse for Tx o/p #02-06-06. (C.Duri fdr #3) Not checked yet. |  | 1 | 18:00 | Afternoon | Friday | 2017 | 1
4970 | 2017-01-20 18:00 | 2017-01-21 10:00 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 53 | Checked & found, @...b/o 3.1SF fuse for 112.5Kva Tx o/p #02-06-06. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 18:00 | Afternoon | Friday | 2017 | 1
4971 | 2017-01-21 03:11 | 2017-01-21 03:11 | 13.8KV BATANG FEEDER #3 | Cloudy and Lightning | Lightning | 41 | 03:11 Batang OCB fdr #3 T/R 1x. 19:20 Checked & found, Batang OCB fdr #3 T/R 1x Ctr: 341-342 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 3:11 | Night | Saturday | 2017 | 1
4972 | 2017-01-21 08:54 | 2017-01-21 08:54 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 29 | C.Duri ACB fdr #1 T/R 1x Ctr: 190-191 R/F: 51N. Not Patrolled yet. |  | 1 | 8:54 | Morning | Saturday | 2017 | 1
4973 | 2017-01-21 08:54 | 2017-01-25 01:56 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 29 | Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 8:54 | Morning | Saturday | 2017 | 1
4974 | 2017-01-22 23:59 | 2017-01-22 23:59 | CPI POWER SYSTEM | Heavy Rain | Normal Condition | - | CPI Power system normal condition. |  | 1 | 23:59 | Night | Sunday | 2017 | 1
4975 | 2017-01-23 10:47 | 2017-01-23 10:47 | 13.8KV PEMATANG FEEDER #1 | Heavy Rain | Transformer Failure | 88 | It was reported b/o fuse for Tx at Well Pematang #79. (Pematang fdr #1) Not checked yet. |  | 1 | 10:47 | Morning | Monday | 2017 | 1
4976 | 2017-01-23 10:47 | 2017-01-25 15:00 | 13.8KV PEMATANG FEEDER #1 | Heavy Rain | Transformer Failure | 88 | Checked & found, @2 b/o 2.1SF fuse for 100Kva Tx at Well Pematang #79. (Pematang fdr #1) Performed TTR test & megger the Tx and found, Low Mega ohm. Replaced 100Kva Tx low megger with 150Kva Tx, then energized the Tx. Cause: Tx Failure. (Low megger reading) |  | 1 | 10:47 | Morning | Monday | 2017 | 1
4977 | 2017-01-23 18:50 | 2017-01-23 18:50 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy and Lightning | Lightning | 0 | So.Bakasap fdr #1 Load dropped 92A (136-44A). Not checked yet. | 11111 | 1 | 18:50 | Afternoon | Monday | 2017 | 1
4978 | 2017-01-23 18:50 | 2017-01-24 18:32 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy and Lightning | Lightning | 0 | Checked & found, Recl. 34BI-18 (So.Bekasap fdr #1) T/R 1x Ctr: 157-158. Patrolled the Line & found, @3 broken L/A o/p #33BH-06. Cause: Lightning. | 11111 | 1 | 18:50 | Afternoon | Monday | 2017 | 1
4979 | 2017-01-23 22:09 | 2017-01-23 22:09 | 13.8KV NORTH DURI FEEDER #5 | Fair | Lightning Arrester | 0 | No.Duri VCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 22:09 | Night | Monday | 2017 | 1
4980 | 2017-01-23 22:09 | 2017-01-26 10:57 | 13.8KV NORTH DURI FEEDER #5 | Fair | Lightning Arrester | 0 | Checked & found, No.Duri VCB fdr #5 T/R 1x Ctr: 109-110 R/F: 51@2. Patrolled the line & found, @2 broken L/A o/p #12-G9.1-01. Cause: Lightning Arrester. |  | 1 | 22:09 | Night | Monday | 2017 | 1
4981 | 2017-01-24 10:11 | 2017-01-24 10:11 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 85 | 09:51 Closed 44KV Bekasap Main GCB #1. To energize Bekasap Main TXP-C. (After replacing broken L/A of the TXP-C) To normalize Load Bekasap main fdr #2 and Bekasap Main fdr #3. 10:11 Open LBS #1-2 o/p #37BD-16. 10:16 Closed Bekasap Main OCB fdr #2. (Bekasap Main fdr #2 back to normal) 10:11 Open LBS #1-3 o/p #37BD-16. 10:16 Closed Bekasap Main OCB fdr #1. (Bekasap Main fdr #1 back to normal) Cause: Plan Maintenance. (after replacing L/A) | 1111 | 1 | 10:11 | Morning | Tuesday | 2017 | 1
4982 | 2017-01-24 12:34 | 2017-01-24 12:34 | 13.8KV PEMATANG FEEDER #2 | Drizzle | Transformer Failure | 0 | It was reported b/o fuse for Tx at Well Pematang #29. Checked & found, @3 b/o 7.8SF fuse for 225Kva Tx at Well Pematang #29. Performed TTR & megger test the Tx and found, Low Mega ohm. Cause: Tx Failure. (Low megger reading) | 11111 | 1 | 12:34 | Afternoon | Tuesday | 2017 | 1
4983 | 2017-01-24 12:34 | 2017-01-25 15:50 | 13.8KV PEMATANG FEEDER #2 | Drizzle | Transformer Failure | 0 | Replaced 225Kva Tx failure with the same size & energized the Tx at Well Pematang #29. Cause: Tx Failure. (Low megger reading) | 11111 | 1 | 12:34 | Afternoon | Tuesday | 2017 | 1
4984 | 2017-01-24 13:44 | 2017-01-24 13:44 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 40 | Minas ACB fdr #2 T/R 1x Crt: 62-63 R/F: 51N. Not checked yet. | 11111 | 1 | 13:44 | Afternoon | Tuesday | 2017 | 1
4985 | 2017-01-24 13:44 | 2017-01-26 07:27 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 40 | Patrolled the line, but found nothing. Cause: Unidentified. | 11111 | 1 | 13:44 | Afternoon | Tuesday | 2017 | 1
4986 | 2017-01-24 14:00 | 2017-01-24 14:00 | MINAS POWER PLANT |  |  | - | 14:00 S/U MGT #5, then On line the Unit at 14:10. | 1111 | 1 | 14:00 | Afternoon | Tuesday | 2017 | 1
4987 | 2017-01-24 14:50 | 2017-01-24 14:50 | MINAS POWER PLANT |  |  | - | 14:50 Off line MGT #7, then S/D the Unit for S/B. (Prior to replacing Fuel Nozzle set) | 11111 | 1 | 14:50 | Afternoon | Tuesday | 2017 | 1
4988 | 2017-01-24 17:55 | 2017-01-24 17:55 | 13.8KV KETIGUL FEEDER#2 | Rain | Lightning | 0 | Ketigul fdr #2 Load dropped 177A (217-40A). Ketigul fdr #3 Load dropped 7A (13-6A). Not checked yet. | 1111 | 1 | 17:55 | Afternoon | Tuesday | 2017 | 1
4989 | 2017-01-24 17:55 | 2017-01-30 07:27 | 13.8KV KETIGUL FEEDER#2 | Rain | Lightning | 0 | Checked & found, Recl. 29AL-02 (Ketigul fdr #2) is normal. (Counter did not change) Patrolled the line & found, @2 broken Dead end insulator & broken Jumper o/p #26AL-19. (Some wells were off, but Recloser upstream did not operate) Cause: Lightning. (The broken Dead end & Jumper had been replaced on 28-Jan-2917) | 1111 | 1 | 17:55 | Afternoon | Tuesday | 2017 | 1
4990 | 2017-01-25 09:30 | 2017-01-25 09:30 | 13.8KV DURI FIELD FEEDER #4 | Fair | Planned Maintenance | 0 | 09:30 Shuted off some wells at downstream of Recl. 07-V5- 02. (D.Field fdr #4) 10:15 Replaced 3 Pcs broken L/As o/p #07-V5-03. Cause: Plan Maintenance. | 11111 | 1 | 9:30 | Morning | Wednesday | 2017 | 1
4991 | 2017-01-25 14:14 | 2017-01-25 14:14 | 13.8KV CENTRAL DURI FEEDER #5 | Cloudy | Tree | 237 | 14:14 C.Duri ACB fdr #5 T/LO. Crt: 231-235 R/F: 51@1,@2. 14:30 Manually closed C.Duri ACB fdr #5, but tripped again. Ctr: 235-236 R/F: 51@2. Patrolled the line, but found nothing. 15:12 It was reported any spark on TX at CGS #3. Checked & found, @1 b/o fuse for 50Kva Tx-5 at CGS #3, Replaced b/o fuse above with same size, then energized the Tx. 16:00 Open Recl. 03-04-16 (C.Duri fdr #5). (to CGS #3) Blocked & closed C.Duri ACB fdr #5, Ok. Re-Patrolled the line & found, Branch Tree hang o/p #03-03-25B, then removed it. 16:40 Closed Recl. 03-04-16 (C.Duri fdr #5), Ok. 16:44 C.Duri ACB fdr #5 T/SO again. (Still on block) 16:47 Man. Opened Recl. 03-04-16 (to CGS #3). 16:50 Blocked & Closed C.Duri ACB fdr #5, Ok. Then released the block. 16:51 Man. Closed Recl. 03-04-16 (C.Duri fdr #5), Ok. Cause: Tree. | 11111 | 1 | 14:14 | Afternoon | Wednesday | 2017 | 1
4992 | 2017-01-25 14:30 | 2017-01-25 14:30 | 13.8KV KOTABATAK FEEDER #2 | Fair | Animal | 0 | It was reported b/o fuse for Tx at Well KB #433. Checked & found, @2 b/o 7.8SF fuse for 300Kva Tx at Well KB #433. Replaced b/o fuse above with same size, then energized the Tx. Cause: Animal. (RAT) | 11111 | 1 | 14:30 | Afternoon | Wednesday | 2017 | 1
4993 | 2017-01-26 06:49 | 2017-01-26 06:49 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 0 | 06:49 Rangau fdr #2 Load dropped 20A (20-0A). Shuted off 4 wells due to High pressure. (Prod. line Congeal) 16:25 Rangau fdr #2 back to normal. Cause: Planned Maintenance. (Prod. line Congeal) (No Prod. loss for PGT). | 11111 | 1 | 6:49 | Morning | Thursday | 2017 | 1
4994 | 2017-01-26 09:33 | 2017-01-26 09:33 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 0 | 09:33 C.Duri fdr #1 Load dropped 12A (146-124A). 10:00 It was reported by Puncak-GS) to shut off 8 wells due to High pressure. (Prod. line Congeal) (Wells off: Puncak #38, 39, 08, 20, 28, 05, 21 and Puncak #03). Cause: Planned Maintenance. (Prod. line Congeal) (No Prod. loss for PGT). | 11111 | 1 | 9:33 | Morning | Thursday | 2017 | 1
4995 | 2017-01-26 09:47 | 2017-01-26 09:47 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | 0 | 09:47 Manually open Bangko OCB fdr #1 to anticipate High Level Tank over flow. (As per Req. by Bangko-GS : Tri Basuki) Cause: Planned Maintenance. (Prod. line Congeal) (No Prod. loss for PGT) | 1111 | 1 | 9:47 | Morning | Thursday | 2017 | 1
4996 | 2017-01-26 09:47 | 2017-01-27 13:50 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | 0 | 13:50 Closed Bangko OCB fdr #1, then re-start up all wells. Cause: Plan Maintenance. | 1111 | 1 | 9:47 | Morning | Thursday | 2017 | 1
4997 | 2017-01-26 10:13 | 2017-01-26 10:13 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | 10:13 It was reported b/o fuse for Tx o/p #01-03-03. 14:00 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #01-03-03. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 1111 | 1 | 10:13 | Morning | Thursday | 2017 | 1
4998 | 2017-01-26 14:06 | 2017-01-26 14:06 | 13.8KV DURI FIELD FEEDER #4 | Heavy Rain | Planned Maintenance | 0 | 14:06-14:46 Manually Open fuse for 112.5Kva Tx o/p #06-R7-03. (D.Field fdr #4) To Replacing 3Pcs L/As o/p #06-R7-03. (4 wells were down during the Job) Cause: Planned Maintenance. | 11111 | 1 | 14:06 | Afternoon | Thursday | 2017 | 1
4999 | 2017-01-26 20:19 | 2017-01-26 20:19 | 13.8KV SINTONG FEEDER #2 | Rain | Lightning | 0 | Sintong fdr #2 Load dropped 100A (158-58A). Sintong GFPC T/R 1x. (Ground fault alarm on Sintong fdr #2) Not checked yet. |  | 1 | 20:19 | Night | Thursday | 2017 | 1
5000 | 2017-01-26 20:19 | 2017-01-27 11:00 | 13.8KV SINTONG FEEDER #2 | Rain | Lightning | 0 | Checked & found, Recl. 28AF-02 (Sintong fdr #2) T/R 1x Ctr: 632-633. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 20:19 | Night | Thursday | 2017 | 1
5001 | 2017-01-27 11:15 | 2017-01-27 11:15 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 0 | 11:15 Manually Open So.Balam VCB fdr #4, to anticipate High Level Tank over flow. (As per Req. by Bangko-GS : Tri Basuki) 15:47 Close So.Balam fdr #4 & re-start up all wells. Cause: Planned Maintenance. (Prod. line Congeal) (No Prod. loss for PGT) | 11111 | 1 | 11:15 | Morning | Friday | 2017 | 1
5002 | 2017-01-27 17:46 | 2017-01-27 17:46 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 129 | Bekasap fdr #3 load dropped 110A (141-31A) Bekasap fdr #5 load dropped 116A (257-141A). ---> WIP Pumps. Bekasap fdr #6 load dropped 18A (72-54A) Not checked yet. | 1111 | 1 | 17:46 | Afternoon | Friday | 2017 | 1
5003 | 2017-01-27 17:46 | 2017-01-29 09:13 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 129 | Checked & found, Recl. 1TL6 (Bekasap fdr #3) T/R 1x Ctr:42-43. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 1111 | 1 | 17:46 | Afternoon | Friday | 2017 | 1
5004 | 2017-01-27 17:49 | 2017-01-27 17:49 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Lightning | 71 | Pematang OCB fdr #2 T/R 1x. Not checked yet. | 11111 | 1 | 17:49 | Afternoon | Friday | 2017 | 1
5005 | 2017-01-27 17:49 | 2017-01-29 14:23 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Lightning | 71 | Checked & found, Pematang OCB fdr #2 T/R 1x Ctr: 456-457 R/F: 51N. Patrolled the line & found, @3 broken Dead end Insulator o/p #34BC-25. Cause: Lightning. | 11111 | 1 | 17:49 | Afternoon | Friday | 2017 | 1
5006 | 2017-01-27 17:49 | 2017-01-27 17:49 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Pematang fdr #1 Load dropped 21A (76-55A). Not checked yet. |  | 1 | 17:49 | Afternoon | Friday | 2017 | 1
5007 | 2017-01-27 17:49 | 2017-01-29 14:48 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 35BC-14 (Pematang fdr #1) T/R 1x Ctr: 320-321. Patrolled the line & found, @2 broken Dead end Insulator o/p #35BD-52. Cause: Lightning. |  | 1 | 17:49 | Afternoon | Friday | 2017 | 1
5008 | 2017-01-28 10:33 | 2017-01-28 10:33 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 126 | 10:33 Open LBS #27AL-03, to repair Hot spot o/p #26AL-14. (Ketigul fdr #2) (18 Wells were shutdown during the Job done) (Well Ubi #32, 28, 26, 24, 33, 27, 35, 06, 10, 22, 30, 34, 14, 02, 29, 23, 36 & Ubi #25) 12:10 Closed LBS #27AL-03. (after finishing the Job) Cause: Planned Maintenance. | 1111 | 1 | 10:33 | Morning | Saturday | 2017 | 1
5009 | 2017-01-28 11:33 | 2017-01-28 11:33 | MINAS POWER PLANT |  |  | - | 11:33 S/U MGT #7, then On line the Unit at 11:54. |  | 1 | 11:33 | Morning | Saturday | 2017 | 1
5010 | 2017-01-28 12:52 | 2017-01-28 12:52 | MINAS POWER PLANT |  |  | - | 12:52 Off line MGT #5, then S/D the Unit for S/B. (Prior to fixing Hot gas leakage at Exhaust Stack) |  | 1 | 12:52 | Afternoon | Saturday | 2017 | 1
5011 | 2017-01-29 06:45 | 2017-01-29 06:45 | 13.8KV DURI FIELD FEEDER #2 | Fair | Others | 0 | 06:45 It was reported b/o fuse for Tx o/p #07-T1-16. (Duri Field fdr #2) 08:30 Checked & found, Main breaker tripped off. performed TTR & Megger test the Tx & found, normal. (Good reading) Cause: Others. (Under Main Breaker) |  | 1 | 6:45 | Morning | Sunday | 2017 | 1
5012 | 2017-01-29 08:50 | 2017-01-29 08:50 | 13.8KV DURI FIELD FEEDER #2 | Fair | Transformer Failure | 0 | 08:50 It was reported b/o fuses for Tx o/p #07-V5-13. 09:15 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #07-V5-13. Performed TTR, Megger test the Tx & found, Low Mega Ohm reading Tx. Cause: TX failure. (Low Megger reading) (The Tx is not replaced yet) | 11111 | 1 | 8:50 | Morning | Sunday | 2017 | 1
5013 | 2017-01-29 08:50 | 2017-01-30 17:50 | 13.8KV DURI FIELD FEEDER #2 | Fair | Transformer Failure | 0 | Replaced 112.5Kva Tx failure with the same size, then energized the Tx. Cause: Tx Failure. | 11111 | 1 | 8:50 | Morning | Sunday | 2017 | 1
5014 | 2017-01-29 10:18 | 2017-01-29 10:18 | 13.8KV S. BALAM FEEDER #4 | Cloudy and Lightning | Lightning | 15 | So.Balam fdr #4 Load dropped 77A (169-92A). So.Balam fdr #1 load dropped 12A (119-107A). So.Balam fdr #2 load dropped 97A (97-0A). T/O WIP at Balam-GS. So.Balam fdr #3 load dropped 70A (70-0A). T/O WIP at Balam-GS. Not checked yet. | 11111 | 1 | 10:18 | Morning | Sunday | 2017 | 1
5015 | 2017-01-29 10:18 | 2017-01-30 12:13 | 13.8KV S. BALAM FEEDER #4 | Cloudy and Lightning | Lightning | 15 | Checked & found, Recl. 16AA-08 (So.Balam fdr #4) T/R 2x Ctr: 74-76 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 11111 | 1 | 10:18 | Morning | Sunday | 2017 | 1
5016 | 2017-01-30 00:10 | 2017-01-30 00:10 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 9 | 00:10 8C fdr #1 Load dropped 139A (211-72A). 03:00 Checked & found, Recl. 9D-25 (8C fdr #1) T/SO. Ctr: 49-50. Blocked & Closed Recloser above, then released the block. Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 0:10 | Night | Monday | 2017 | 1
5017 | 2017-01-30 08:26 | 2017-01-30 08:26 | 13.8KV NORTH DURI FEEDER #5 | Fair | Dead End Insulator | 0 | N.Duri VCB fdr #5 T/R 1x. N.Duri GFPC-Tx #12 T/R 1x. Not checked yet. |  | 1 | 8:26 | Morning | Monday | 2017 | 1
5018 | 2017-01-30 08:26 | 2017-02-02 11:34 | 13.8KV NORTH DURI FEEDER #5 | Fair | Dead End Insulator | 0 | Checked & found, No.Duri VCB fdr #5 T/R 1x Ctr: 110-111 R/F: 51@3. Patrolled the line & found, @3 flashed over Dead end Insulator o/p #12-E7-02. Cause: Dead end Insulator. |  | 1 | 8:26 | Morning | Monday | 2017 | 1
5019 | 2017-01-30 18:51 | 2017-01-30 18:51 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Rain | Lightning | 0 | 18:51 4160V Dumai (Wharf) ACB fdr #1 T/SO. 18:55 Blockec & closed 4160V Dumai ACB fdr #1, Ok. Then release the block. Not checked & patrolled yet. |  | 1 | 18:51 | Afternoon | Monday | 2017 | 1
5020 | 2017-01-30 18:51 | 2017-01-31 17:03 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Rain | Lightning | 0 | Checked & found, 4160V Dumai (Wharf) ACB fdr #1 T/LO. Ctr: 256-258 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 18:51 | Afternoon | Monday | 2017 | 1
5021 | 2017-01-30 22:26 | 2017-01-30 22:26 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 0 | 22:26 It was reported b/o fuses for Tx at NC Test Station Area-3. 23:40 Checked & found, @3 b/o fuse for 500Kva Tx and broken FCO o/p #NN. Cause: Animal. (Monkey) (Will be replaced tomorrow) | 11111 | 1 | 22:26 | Night | Monday | 2017 | 1
5022 | 2017-01-30 23:00 | 2017-01-30 23:00 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified (Fuse) | 31 | 23:00 It was reported b/o fuse for Tx at Well Pematang #97. 00:40 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well Pematang #97. Replaced b/o fuses above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 11111 | 1 | 23:00 | Night | Monday | 2017 | 1
5023 | 2017-01-31 01:40 | 2017-01-31 01:40 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 30 | So.Bakasap OCB fdr #1 T/R 1x Ctr: 348-349 R/F: 50@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. | 11111 | 1 | 1:40 | Night | Tuesday | 2017 | 1
5024 | 2017-01-31 08:41 | 2017-01-31 08:41 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain | Lightning | 129 | CKBS VCB fdr #5 T/R 2x. CKBS fdr #6 Load dropped 167A (190-23A). Not checked yet. |  | 1 | 8:41 | Morning | Tuesday | 2017 | 1
5025 | 2017-01-31 08:41 | 2017-01-02 07:28 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain | Lightning | 129 | Checked & found, CKBS VCB fdr #5 T/R 2x Ctr: 145-147 R/F: 51@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. Checked Recloser at downstream of CKBS fdr #6 & found, normal. (Ctr. did not change) Patrolled the line, but found nothing. Cause: Unidentified. (Suspected by Voltage dip when CKBS VCB fdr #5 T/R 2x) |  | 1 | 8:41 | Morning | Tuesday | 2017 | 1
5026 | 2017-01-31 12:55 | 2017-01-31 12:55 | 13.8KV ROKAN FEEDER #4 | Rain | Animal | 0 | Rokan VCB fdr #4 T/R 1x. Not checked yet. |  | 1 | 12:55 | Afternoon | Tuesday | 2017 | 1
5027 | 2017-01-31 12:55 | 2017-01-02 17:27 | 13.8KV ROKAN FEEDER #4 | Rain | Animal | 0 | Checked & found, Rokan VCB fdr #4 T/R 1x Ctr: 735-736 R/F: 51@1,@2. Patrolled the line & found, a dead Monkey under TP of Well Kirana #01. Cause: Animal. (Monkey) |  | 1 | 12:55 | Afternoon | Tuesday | 2017 | 1
5028 | 2017-01-31 17:21 | 2017-01-31 17:21 | 13.8KV KETIGUL FEEDER#3 | Rain | Lightning | 61 | Ketigul VCB fdr #3 T/R 3x. Ketigul fdr #2 Load dropped 185A (216-21A). Ketigul fdr #1 Load dropped 22A (107-85A). Not checked yet. |  | 1 | 17:21 | Afternoon | Tuesday | 2017 | 1
5029 | 2017-01-31 17:21 | 2017-02-02 18:09 | 13.8KV KETIGUL FEEDER#3 | Rain | Lightning | 61 | Checked & found, Ketigul VCB fdr #3 T/R 2x Ctr: 171-173 R/F: 51@2,@3. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:21 | Afternoon | Tuesday | 2017 | 1
5030 | 2017-01-02 21:13 | 2017-01-02 21:13 | 13.8KV PUNGUT FEEDER #2 | Rain | Tree | 217 | 21:13 Pungut fdr #2 Load dropped 15A (79-64A). 22:15 It was reported no power at Intan Fields. Not checked yet. | 11111 | 1 | 21:13 | Night | Monday | 2017 | 1
5031 | 2017-01-02 21:13 | 2017-02-02 12:13 | 13.8KV PUNGUT FEEDER #2 | Rain | Tree | 217 | 10:25 Checked & found Recl. 46BP-12 (Pungut fdr #2) T/LO. Ctr: 507-514. Patrolled the line & found, falling down Tree & touching to power line near pole #49BT-24. (Line toward Well Penasa #5) 12:15 Blocked & closed Recl. 46BP-12, Ok. Then released the block. (After dismantling the above Tree from Power line) Cause: Tree. | 11111 | 1 | 21:13 | Night | Monday | 2017 | 1
5032 | 2017-02-02 04:55 | 2017-02-02 04:55 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Unidentified | 0 | 4.16KV Dumai (Wharf) ACB fdr #1 T/R 1x. Not checked yet. |  | 1 | 4:55 | Morning | Thursday | 2017 | 2
5033 | 2017-02-02 04:55 | 2017-03-02 10:43 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Unidentified | 0 | Checked & found, 4.16KV Dumai (Wharf) ACB fdr #1) T/R 1x Ctr: 258-259 R/F: 50N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 4:55 | Morning | Thursday | 2017 | 2
5034 | 2017-02-02 08:40 | 2017-02-02 08:40 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 0 | 08:40 It was reported b/o fuse for Tx o/p #06-Q5-04B. (C.Duri fdr #3) 09:45 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #06-Q5-04B. Checked TTR & Megger test the Tx & found, Low megger reading. Cause: Transformer failure. (Low megger reading) (The Tx failure is nt replaced yet) |  | 1 | 8:40 | Morning | Thursday | 2017 | 2
5035 | 2017-02-02 08:40 | 2017-03-02 10:40 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 0 | Replaced 112.5Kva Tx failure with the same size & energized the Tx o/p #06-Q5-04B. Cause: Transformer failure. |  | 1 | 8:40 | Morning | Thursday | 2017 | 2
5036 | 2017-02-02 09:40 | 2017-02-02 09:40 | 13.8KV PUNGUT FEEDER #1 | Fair | Transformer Failure | 32 | 09:40 It was reported b/o fuse for Tx at Well Pungut #1. (Pungut fdr #1) 13:30 Checked & found, @1,@3 b/o 7.8SF fuses for 225Kva Tx at Well Pungut #1. Checked TTR & Megger test the Tx & found, low megger reading. Cause: Transformer failure. (The Tx failure is not replaced yet) |  | 1 | 9:40 | Morning | Thursday | 2017 | 2
5037 | 2017-02-02 09:40 | 2017-03-02 16:19 | 13.8KV PUNGUT FEEDER #1 | Fair | Transformer Failure | 32 | Replaced 225Kva Tx failure with the same size & energized the Tx at Well Pungut #1. Cause: Tx Failure. |  | 1 | 9:40 | Morning | Thursday | 2017 | 2
5038 | 2017-02-02 11:20 | 2017-02-02 11:20 | 13.8KV 8C FEEDER #1 | Fair | Dead End Insulator | 26 | 8C VCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 11:20 | Morning | Thursday | 2017 | 2
5039 | 2017-02-02 11:20 | 2017-06-02 09:56 | 13.8KV 8C FEEDER #1 | Fair | Dead End Insulator | 26 | Checked & found, 8C VCB fdr #1 T/R 1x Ctr: 660-661 R/F: 50@2,@3. Patrolled the line & found: -@2 Broken Dead end Insulator o/p #9C-12. -High Trees & touching to @3 power line near pole #9D-37. Cause: Dead end Insulator. |  | 1 | 11:20 | Morning | Thursday | 2017 | 2
5040 | 2017-02-02 16:37 | 2017-02-02 16:37 | MINAS POWER PLANT |  |  | - | 16:37 S/U MGT #5, then on line the Unit at 16:55. |  | 1 | 16:37 | Afternoon | Thursday | 2017 | 2
5041 | 2017-02-02 17:36 | 2017-02-02 17:36 | MINAS POWER PLANT |  |  | - | 17:36 Off line MGT #6, then S/D the Unit for S/B. (Prior to replacing AA Compressor) |  | 1 | 17:36 | Afternoon | Thursday | 2017 | 2
5042 | 2017-03-02 09:04 | 2017-03-02 09:04 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 68 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 9:04 | Morning | Thursday | 2017 | 3
5043 | 2017-03-02 09:04 | 2017-05-02 12:04 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 68 | Checked & found, Ketigul VCB fdr #2 T/R 1x Ctr: 226-227 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 9:04 | Morning | Thursday | 2017 | 3
5044 | 2017-03-02 11:33 | 2017-03-02 11:33 | CENTRAL DURI SWITCH YARD | Fair | Under investigation | 0 | 11:33 It was reported Oil leaks on Power TX-3 at CDSY. 13:44 115KV GCB #41 T/O. 13.8KV ACB #34 T/O. (Power Tx-3 at CDSY Tripped) (CDSY Bus#3 & Bus #4 Islanding with source CGT #4) 14:25 Checked & found: -R/F 86HR. -Oil Temp. & Winding Temp 60F. -PRD Operated. 14:26 Closed Isolation Switch of 13.8Kv Darling VCB fdr #4. 14:50 S/U CGT #3. 15:04 Open Generator Breaker CGT #4, then S/D the unit. Open C.Duri ACB fdr#8, then closed at 15:12. 15:06 Closed Darling VCB fdr #4. (to parallel CDSY Bus #3 & Bus #4 with Darling fdr #4) 15:10 Closed Generator Breaker CGT #3. 16:00 Rack Out ACB #34. 16:27 Closed 115Kv GCB #41. (Running on test TX-3 / no load). Cause: Under Investigation. |  | 1 | 11:33 | Morning | Thursday | 2017 | 3
5045 | 2017-03-02 16:10 | 2017-03-02 16:10 | 115KV KOTABATAK JUNCTION - 4B LINE | Fair | Others | 0 | 16:15 Manually Open 115KV KBJ GCB #33. Manually Open 115KV KBJ GCB #35. 16:16 Manually Open 115KV 4B GCB #21. (115KV KBJ - 4B Substation line M/O) 17:55 Open 115KV Line Switch KBJ-4B (No: 410-73-006) 17:58 Closed 115KV KBJ GCB #33 & GCB #35. (KBJ SW Station back to Ring) Cause: Other. (Line Diff. Relay Off / problem) |  | 1 | 16:10 | Afternoon | Thursday | 2017 | 3
5046 | 2017-04-02 09:16 | 2017-04-02 09:16 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 47 | 09:16 Opened LBS #5B-67. (6D fdr #1) (14 Wells were off during the job) To replacing @2,@3 seriously broken Dead end Isolator o/p #5B-69. 11:25 Closed LBS #5B-67. Cause: Maintenance job. |  | 1 | 9:16 | Morning | Sunday | 2017 | 4
5047 | 2017-04-02 10:50 | 2017-04-02 10:50 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Planned Maintenance | 0 | 10:50-12:20 Shutdown 112.5Kva Tx o/p #05-P1-20. (C.Duri fdr #15) To replacing 112.5Kva Tx above with the same size o/p #05-P1-20. Cause: Maintenance job. |  | 1 | 10:50 | Morning | Sunday | 2017 | 4
5048 | 2017-04-02 16:35 | 2017-04-02 16:35 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 83 | 16:35 8C fdr #1 Load dropped 124A (209-85A). 18:27 Checked & found, Recl. 9D-25 (8C fdr #1) T/SO. Ctr: 50-51. Blocked & closed Recl. 9D-25, Ok. Then release the block. The line is not Patrolled yet. |  | 1 | 16:35 | Afternoon | Sunday | 2017 | 4
5049 | 2017-04-02 16:35 | 2017-05-02 17:23 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 83 | Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 16:35 | Afternoon | Sunday | 2017 | 4
5050 | 2017-04-02 22:12 | 2017-04-02 22:12 | 13.8KV NELLA FEEDER #1 | Fair | Animal | 26 | It was reported b/o fuse for Tx at Well Bangko #181. (Nella fdr #1) Not checked yet. |  | 1 | 22:12 | Night | Sunday | 2017 | 4
5051 | 2017-04-02 22:12 | 2017-05-02 08:35 | 13.8KV NELLA FEEDER #1 | Fair | Animal | 26 | Checked & found, @2,@3 b/o 3.5SF fuses for 150Kva Tx at Well Bangko #181. Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal. (Monkey) |  | 1 | 22:12 | Night | Sunday | 2017 | 4
5052 | 2017-05-02 02:00 | 2017-05-02 02:00 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 02:00 CGT #1 Tripped Off. By Alarm: Lube Oil Bearing Header Temp. High. (No load shedding) Cause: Under Investigation. (Loss of 480Volt) 02:02-02:54 Closed ACB #19. (Tie breaker / Bus #1 and Bus #2) 02:39 S/U CGT #1, then online the the Unit at 02:58. | 11111 | 1 | 2:00 | Night | Tuesday | 2017 | 5
5053 | 2017-05-02 07:00 | 2017-05-02 07:00 | 13.8KV BATANG FEEDER #2 | Fair | Lightning Arrester | 0 | Batang OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 7:00 | Morning | Tuesday | 2017 | 5
5054 | 2017-05-02 07:00 | 2017-06-02 17:46 | 13.8KV BATANG FEEDER #2 | Fair | Lightning Arrester | 0 | Checked & found, Batang OCB fdr #2 T/R 1x Ctr: 136-137 R/F: 51@1. Patrolled the line & found, @1 broken L/A on TOP of Well Rantaubais #27. Cause: Lightning Arrester. |  | 1 | 7:00 | Morning | Tuesday | 2017 | 5
5055 | 2017-05-02 14:46 | 2017-05-02 14:46 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 197 | 14:46 So.Balam VCB fdr #4 T/SO. 14:49 Blocked & closed, So.Balam VCB fdr #4, Ok. Then released the Block. Not checked & patrolled yet. |  | 1 | 14:46 | Afternoon | Tuesday | 2017 | 5
5056 | 2017-05-02 14:46 | 2017-07-02 08:11 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 197 | Checked & found, So.Balam VCB fdr #4 T/SO. Ctr: 308. (Did not change) R/F: Appear alarm Backup Relay. Patrolled the line, but found nothing. Cause: Unidentified. (Note: Need to functional test breaker operation Counter & Over current Relay) |  | 1 | 14:46 | Afternoon | Tuesday | 2017 | 5
5057 | 2017-06-02 06:57 | 2017-06-02 06:57 | 13.8KV 8C FEEDER #1 | Fair | Lightning Arrester | 33 | 8C VCB fdr #1 T/R 1x. Not checked yet. | 1111 | 1 | 6:57 | Morning | Friday | 2017 | 6
5058 | 2017-06-02 06:57 | 2017-07-02 16:22 | 13.8KV 8C FEEDER #1 | Fair | Lightning Arrester | 33 | Checked & found, 8C VCB fdr #1 T/R 1x Ctr: 661-662 R/F: 51N. Patrolled the line & found, @3 flashed over L/A o/p #9C-15. Cause: Lightning Arrester. | 1111 | 1 | 6:57 | Morning | Friday | 2017 | 6
5059 | 2017-06-02 09:39 | 2017-06-02 09:39 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Planned Maintenance | 0 | 09:39-10:58 Blocked C.Duri ACB fdr #3, to replace broken Pin insulator o/p #02-8-08. (Shutdown Wells #5R-81A & 5R-82A during the Job done) Cause: Planned maintenance . |  | 1 | 9:39 | Morning | Friday | 2017 | 6
5060 | 2017-07-02 07:11 | 2017-07-02 07:11 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 5 | Menggala fdr #1 Load dropped 29A (185-156A). (Ground fault alarm on Menggala fdr #1) Not checked yet. |  | 1 | 7:11 | Morning | Sunday | 2017 | 7
5061 | 2017-07-02 07:11 | 2017-08-02 14:10 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 5 | Checked & found, Recl. 19AO-01 (Menggala fdr #1) T/R 1x Ctr: 466-467. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 7:11 | Morning | Sunday | 2017 | 7
5062 | 2017-07-02 07:52 | 2017-07-02 07:52 | 13.8KV 6D FEEDER #1 | Fair | Pin Insulator | 43 | 6D OCB fdr #1 T/R 1x. Not checked yet |  | 1 | 7:52 | Morning | Sunday | 2017 | 7
5063 | 2017-07-02 07:52 | 2017-09-02 20:43 | 13.8KV 6D FEEDER #1 | Fair | Pin Insulator | 43 | Checked & found, 6D OCB fdr #1 T/R 1x Ctr: 311-312 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator o/p #5B-52. Cause: Pin Insulator. |  | 1 | 7:52 | Morning | Sunday | 2017 | 7
5064 | 2017-07-02 10:40 | 2017-07-02 10:40 | MINAS POWER PLANT |  |  | - | 10:40 S/U MGT #6, then on line the Unit at 10:52. |  | 1 | 10:40 | Morning | Sunday | 2017 | 7
5065 | 2017-07-02 11:00 | 2017-07-02 11:00 | MINAS POWER PLANT |  |  | - | 11:0 Off line MGT #7, then S/D the Unit for S/B. (Prior to Fixing Atomizing Air Pipe leaks) |  | 1 | 11:00 | Morning | Sunday | 2017 | 7
5066 | 2017-07-02 11:55 | 2017-07-02 11:55 | 13.8KV 4D FEEDER #5 | Fair | Unidentified | 15 | 11:55 4D fdr #5 Load dropped 14A (160-146A). 17:40 Checked & found, Recl. 4D-14A (4D fdr #5) T/SO. Ctr: 47-48. Blocked & Closed the Recloser, Ok. Then release the block. Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 11:55 | Morning | Sunday | 2017 | 7
5067 | 2017-07-02 14:00 | 2017-07-02 14:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Transformer Failure | 55 | 14:11 It was reported b/o fuse for Tx o/p #06-R7-03. (D.Field fdr #4) 14:45 Checked & found, @.... b/o fuse for 112.5Kva Tx o/p #06-R7-03. Tested TTR, Megger & found, low megger reading. Cause: Tx Failure. (Low Megger reading) (The Tx failure is not replaced yet) |  | 1 | 14:00 | Afternoon | Sunday | 2017 | 7
5068 | 2017-07-02 14:00 | 2017-11-02 12:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Transformer Failure | 55 | Replace 112.5Kva Tx failure with the same size & energized the Tx o/p #06-R7-03. Cause: Tx Failure. |  | 1 | 14:00 | Afternoon | Sunday | 2017 | 7
5069 | 2017-07-02 18:38 | 2017-07-02 18:38 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 10 | C.Duri fdr #1 Load dropped 43A (139-96A). Not checked yet. |  | 1 | 18:38 | Afternoon | Sunday | 2017 | 7
5070 | 2017-07-02 18:38 | 2017-12-02 18:38 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 10 | Checked & found, Recl. 41AW-62 (C.Duri fdr #1) T/R 1x Ctr: 245-246. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 18:38 | Afternoon | Sunday | 2017 | 7
5071 | 2017-08-02 10:55 | 2017-08-02 10:55 | 13.8KV BEKASAP FEEDER #2 | Fair | Theft | 0 | 10:55 It was reported Vandalism at Well BKS #158 & #67. (Multy pad Wells) 15:30 Checked & found, FCO for 300Kva Tx in Open Condition at Well BKS #158 & #67. Also found, broken Tx fencing & Loss of Reda cables. Re-Closed FCO above after Replacing Reda Cables. Cause: Theft. |  | 1 | 10:55 | Morning | Wednesday | 2017 | 8
5072 | 2017-08-02 15:10 | 2017-08-02 15:10 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 20 | 15:10 It was reported b/o fuse for Tx o/p #04-02-18. (C.Duri fdr #8) 16:20 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #04-02-18. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 15:10 | Afternoon | Wednesday | 2017 | 8
5073 | 2017-09-02 11:57 | 2017-09-02 11:57 | 13.8KV BEKASAP FEEDER #6 | Fair | Planned Maintenance | 0 | 11:57 Manually Opened Bekasap VCB fdr #6. (Requested by Bekasap-GS) Found, 10" Production pipe line jumper from Aman field leaks at near Bekasap-GS. 16:34 Manually Closed Bekasap VCB fdr #6. (after Fixing the Leakage) Cause: Planned Maintenance. (No Production Loss charge to PGT) |  | 1 | 11:57 | Morning | Saturday | 2017 | 9
5074 | 2017-10-02 08:45 | 2017-10-02 08:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 3 | 08:45 Manually Open / close fuses for 112.5Kva Tx o/p #SBB-16. (C.Duri fdr #1) 11:00 Repairing Hot Spot at Secondary connection of the Tx o/p #SBB-16. Cause: Palnned Maintenance. (Hot spot on Secondary Cable connection) |  | 1 | 8:45 | Morning | Monday | 2017 | 10
5075 | 2017-10-02 22:31 | 2017-10-02 22:31 | CENTRAL DURI POWER PLANT |  |  | - | 22:31 S/U CGT #4, then online the Unit at 23:00. |  | 1 | 22:31 | Night | Monday | 2017 | 10
5076 | 2017-10-02 23:06 | 2017-10-02 23:06 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT #3, then S/D the Unit for S/B. (Prior to trouble shooting computer-C problem) |  | 1 | 23:06 | Night | Monday | 2017 | 10
5077 | 2017-11-02 07:20 | 2017-11-02 07:20 | 13.8KV PEMATANG FEEDER #2 | Fair | Dead End Insulator | 33 | Pematang OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 7:20 | Morning | Thursday | 2017 | 11
5078 | 2017-11-02 07:20 | 2017-12-02 19:20 | 13.8KV PEMATANG FEEDER #2 | Fair | Dead End Insulator | 33 | Checked & found, Pematang OCB fdr #2 T/R 1x Ctr: 457-458 R/F: 51N. Patrolled the line & found, @2 broken Dead end Insulator o/p #34BC-77. Cause: Dead end Insulator. |  | 1 | 7:20 | Morning | Thursday | 2017 | 11
5079 | 2017-11-02 07:36 | 2017-11-02 07:36 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 187 | S.Balam VCB fdr #4 T/R 1x. Not checked yet. |  | 1 | 7:36 | Morning | Thursday | 2017 | 11
5080 | 2017-11-02 07:36 | 2017-12-02 19:36 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 187 | Checked & found, So.Balam VCB fdr #4 T/R 1x Ctr: 308 (did not operate) R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 7:36 | Morning | Thursday | 2017 | 11
5081 | 2017-11-02 10:20 | 2017-11-02 10:20 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Planned Maintenance | 0 | 10:20 Manually Open /Close fuse for 112.5Kva Tx o/p #05-N7-19. (C.Duri fdr #14) (4 Wells were off, #6N-84A, 6N-84B, 6N-83C & 6N-84C) 12:10 Replaced 112.5Kva Tx above with the same size & energized the Tx. (due to Oil Leak) Cause: Planned Maintenance. |  | 1 | 10:20 | Morning | Thursday | 2017 | 11
5082 | 2017-11-02 11:30 | 2017-11-02 11:30 | 13.8KV BEKASAP FEEDER #2 | Fair | Theft | 0 | It was reported Tx Vandalism at LTC Well Bekasap #80. (Bekasap fdr #2) Checked & found, ...Kva Tx Fall down on the ground, then dismantled its Tx. Cause: Theft. |  | 1 | 11:30 | Morning | Thursday | 2017 | 11
5083 | 2017-11-02 12:30 | 2017-11-02 12:30 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Planned Maintenance | 0 | 12:30 Manually Opened /Closed fuses for 112.5Kva Tx o/p #06-Q3-09. (C.Duri fdr #15) (4 Wells were off, #6Q-37A, 6Q-38A, 6Q-34A & 6Q-37A) 13:50 Replaced 112.5Kva Tx failure above with the same size & energized the Tx o/p #06-Q3-09. Cause: Planned maintenance. |  | 1 | 12:30 | Afternoon | Thursday | 2017 | 11
5084 | 2017-11-02 14:37 | 2017-11-02 14:37 | 13.8KV KETIGUL FEEDER#3 | Fair | Animal | 9 | Ketigul VCB fdr #3 T/R 1x. Not checked yet. |  | 1 | 14:37 | Afternoon | Thursday | 2017 | 11
5085 | 2017-11-02 14:37 | 2017-12-02 19:37 | 13.8KV KETIGUL FEEDER#3 | Fair | Animal | 9 | Checked & found, Ketigul VCB fdr #3 T/R 1x Ctr: 174-175 R/F: 51N. Patrolled the line & found, a dead Monkey o/p #32AN-01. Cause: Animal. (Monkey) |  | 1 | 14:37 | Afternoon | Thursday | 2017 | 11
5086 | 2017-11-02 16:10 | 2017-11-02 16:10 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | It was reported b/o fuse for Tx at Well Rantaubais #057. (Batang fdr #2) not checked yet. |  | 1 | 16:10 | Afternoon | Thursday | 2017 | 11
5087 | 2017-11-02 16:10 | 2017-12-02 10:20 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Well Rantaubais #057. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Monkey) |  | 1 | 16:10 | Afternoon | Thursday | 2017 | 11
5088 | 2017-11-02 20:24 | 2017-11-02 20:24 | 13.8KV 6D FEEDER #2 | Fair | Lightning Arrester | 49 | 6D fdr #2 Load dropped 162A (235-74A). Not checked yet. |  | 1 | 20:24 | Night | Thursday | 2017 | 11
5089 | 2017-11-02 20:24 | 2017-12-02 21:07 | 13.8KV 6D FEEDER #2 | Fair | Lightning Arrester | 49 | Checked & found, Recl. 6D-298 (6D fdr #2) T/R 1x Ctr: 51-52. Patrolled the line & found, @1 broken L/A o/p #6D-09. Cause: Lightning Arresrter. |  | 1 | 20:24 | Night | Thursday | 2017 | 11
5090 | 2017-12-02 10:30 | 2017-12-02 10:30 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified (Fuse) | 0 | 10:30 It was reported b/o fuse for Tx o/p #13-E10-06. (N.Duri fdr #11) 15:45 Checked & found, @1 b/o 3.1SF fuse for 112.5Kva Tx o/p #13-E10-06. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 10:30 | Morning | Saturday | 2017 | 12
5091 | 2017-02-13 09:22 | 2017-02-13 09:22 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 28 | 09:22 Sintong fdr #2 Load dropped 20A (208-188A). Ground fault alarm at Sintong fdr #2. Sintong GFPC not operate. 10:29 Sintong fdr #2 Load dropped again 108A (188-100A). Sintong fdr #1 load dropped 15A (73-58A). Sintong GFPC T/R 1x. Not checked yet. | 11111 | 1 | 9:22 | Morning | Monday | 2017 | 2
5092 | 2017-02-13 09:22 | 2017-02-15 13:58 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 28 | Checked & found, Recl. 29Y-16 (Sintong fdr #2) T/R 1x Ctr: 88-89. Sintong GFPC is not reported yet. Patrolled the line, but found nothing. Cause: Unidentified. | 11111 | 1 | 9:22 | Morning | Monday | 2017 | 2
5093 | 2017-02-13 10:10 | 2017-02-13 10:10 | MINAS POWER PLANT |  |  | - | 10:10 S/U MGT #7, then on line the Unit at 10:25. |  | 1 | 10:10 | Morning | Monday | 2017 | 2
5094 | 2017-02-13 10:56 | 2017-02-13 10:56 | MINAS POWER PLANT |  |  | - | 10:56 S/U MGT #2, then on line the Unit at 11:16. |  | 1 | 10:56 | Morning | Monday | 2017 | 2
5095 | 2017-02-13 12:01 | 2017-02-13 12:01 | MINAS POWER PLANT |  |  | - | 12:01 Off line MGT #9, then S/D the Unit for S/B. (Prior to fixing hot gas leak at Exhaust Pigtail) |  | 1 | 12:01 | Afternoon | Monday | 2017 | 2
5096 | 2017-02-13 15:20 | 2017-02-13 15:20 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 2 | 15:20 It was reported b/o fuse for Tx o/p #06-S7-12. (D.Field fdr #4) 16:12 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #06-S7-12. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 1111 | 1 | 15:20 | Afternoon | Monday | 2017 | 2
5097 | 2017-02-13 15:28 | 2017-02-13 15:28 | 13.8KV PEMATANG FEEDER #1 | Heavy Rain | Lightning | 31 | Pematang OCB fdr #1 T/R 1x. Pematang fdr #2 Load dropped 10A (31-21A). Not checked yet. | 11111 | 1 | 15:28 | Afternoon | Monday | 2017 | 2
5098 | 2017-02-13 15:28 | 2017-02-14 15:58 | 13.8KV PEMATANG FEEDER #1 | Heavy Rain | Lightning | 31 | Checked & found, Pematang OCB fdr #1 T/R 1x Ctr: 131-132 R/F: 51N. Patrolled the line & found, @1,@2,@3 broken Dead end Insulators o/p #34BC-36A. Cause: Lightning. | 11111 | 1 | 15:28 | Afternoon | Monday | 2017 | 2
5099 | 2017-02-13 16:41 | 2017-02-13 16:41 | 13.8KV 3D FEEDER #2 | Heavy Rain | Tree | 87 | 16:41 3D OCB fdr #2 T/LO. 3D fdr #3 Load dropped 20A (165-143A). 3D fdr #4 Load dropped 64A (202-138A). . 17:50 Checked & found, 3D OCB fdr #2 T/LO. Ctr: 233-239 R/F: 51@2. Blocked & closed 3D OCB fdr #2, Ok. Then released the block. The line is not patrolled yet. | 11111 | 1 | 16:41 | Afternoon | Monday | 2017 | 2
5100 | 2017-02-13 16:41 | 2017-02-15 07:49 | 13.8KV 3D FEEDER #2 | Heavy Rain | Tree | 87 | Patrolled the line & found, high Tree & touching to power line between poles #3E-51 & #3E-52. Cause: Tree. | 11111 | 1 | 16:41 | Afternoon | Monday | 2017 | 2
5101 | 2017-02-14 11:10 | 2017-02-14 11:10 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 11:10 It was reported b/o fuse for Tx o/p #06-R5-06. (D.Field fdr #2) 11:45 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #06-R5-06. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). | 1111 | 1 | 11:10 | Morning | Tuesday | 2017 | 2
5102 | 2017-02-14 13:00 | 2017-02-14 13:00 | CENTRAL DURI POWER PLANT |  |  | - | 13:00 S/U CGT #3, then on line the Unit at 13:20. |  | 1 | 13:00 | Afternoon | Tuesday | 2017 | 2
5103 | 2017-02-14 13:57 | 2017-02-14 13:57 | MINAS POWER PLANT |  |  | - | 13:57 Off line MGT #2, then S/D the Unit for S/B. |  | 1 | 13:57 | Afternoon | Tuesday | 2017 | 2
5104 | 2017-02-14 14:35 | 2017-02-14 14:35 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 3 | 14:35 It was reported b/o fuse for Tx o/p #07-U1-14. 16:20 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #07-U1-14. Replaced b/o fuse above with same size, then energized the Tx. Cause: Unidentified (Fuse). | 11111 | 1 | 14:35 | Afternoon | Tuesday | 2017 | 2
5105 | 2017-02-14 16:48 | 2017-02-14 16:48 | CENTRAL DURI SWITCH YARD | Fair | Under investigation | 0 | 16:48 13.8KV CDSY ACB #34 T/O. 115KV CDSY GCB #41 T/O. 115KV CDSy GCB #43 is still in open position. (115KV CDSY Power TX-3 Trip & 13.8KV Bus #3 & Bus-4 Islanding with sourch CGT #3) Checked & found, CDSY Power TX-3 T/O, By Relay 86T. (In the same time CGT #4 open Generator Breaker ACB #46) 17:02 Man. Closed 480V 52T. (Tie Breaker CD SSTX3 - SSTX4). 17:14 Man. Opened 13.8KV ACB #39. (Tie Breaker CDSY Bus #3 & Bus #4) Man. Closed 13.8KV ACB fdr #11. (Parallel with Darling VCB fdr #6) 17:18 Man. Opened 480V Tie Brk. 52T. 17:22 Man. Closed ACB #46 Generator breaker CGT #4. 17:25 Open Generator Breaker ACB #46. (CGT #4 Full speed no load) (Then S/D CGT #4 for S/B) 17:30 Blocked Darling VCB fdr #6, then Normalize at 17:36. 17:32 Man. Closed 13.8KV ACB #39. (Tie Breaker) to parallel CDSY Bus #3 & Bus#4 with the System) 17:37 Blocked C.Duri fdr #11. Cause: Under Investigation. |  | 1 | 16:48 | Afternoon | Tuesday | 2017 | 2
5106 | 2017-02-15 04:25 | 2017-02-15 04:25 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | N.Duri VCB fdr #5 T/R 1x. Not checked Yet. |  | 1 | 4:25 | Morning | Wednesday | 2017 | 2
5107 | 2017-02-15 04:25 | 2017-02-16 02:36 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | Checked & found, N.Duri VCB fdr #5 T/R 1x Ctr: 111-112 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 4:25 | Morning | Wednesday | 2017 | 2
5108 | 2017-02-15 13:45 | 2017-02-15 13:45 | 13.8KV PEMATANG FEEDER #1 | Fair | Theft | 55 | 13:45 It was reported No Power at Well Pematang #43. (Pematang fdr #1) 17:01 Checked & found, the Fuses were Opened & Loss of Secondary Cable for 100Kva Tx. Perform TTR & Megger test the TX, found good reading. Re-Energized the Tx. (after dismantling secondarys Cable from Tx connection) Cause: Teft. (Vandalism) (The Well is still Down, w/o replacing Secondary cable) |  | 1 | 13:45 | Afternoon | Wednesday | 2017 | 2
5109 | 2017-02-15 19:54 | 2017-02-15 19:54 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 0 | 19:54-21:23 Manually Opened 3D OCB fdr #4 & 4D OCB fdr #2. (As per Minas GS-5 Request, due to WIP problem) Cause: Planned Maintenance. (No LPO Charge to PGT) |  | 1 | 19:54 | Night | Wednesday | 2017 | 2
5110 | 2017-02-15 19:55 | 2017-02-15 19:55 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 0 | 19:55 Manually Opened 4D OCB fdr #2 & 3D OCB fdr #4. (As per Minas GS-5 request, due to WIP problem) Cause: Planned Maintenance. |  | 1 | 19:55 | Night | Wednesday | 2017 | 2
5111 | 2017-02-15 19:55 | 2017-02-16 01:24 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 0 | 01:24 Manually Closed 4D OCB fdr #2. (After S/U WIP at GS-5 & back to normal operation) Cause: Planned Maintenance. (No LPO Charge to PGT) |  | 1 | 19:55 | Night | Wednesday | 2017 | 2
5112 | 2017-02-15 22:27 | 2017-02-15 22:27 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 22:27 It was reported b/o fuse for Tx at Well Bangko #128. (Nella fdr #1) 23:40 Checked & found, @1,@2 b/o 3.5SF fuses for 150Kva Tx at Water Well Bangko #128. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 22:27 | Night | Wednesday | 2017 | 2
5113 | 2017-02-16 06:42 | 2017-02-16 06:42 | 13.8KV ROKAN FEEDER #2 | Cloudy | Lightning | 24 | 06:42 Rokan VCB fdr #2 T/R 1x. 20:33 Checked & found, Rokan VCB fdr #2 T/R 1x Ctr: 1246-1247 R/F: 51@1. Patrolled the Line & found, @1 broken L/A o/p #31AV-30. Cause: Lightning. |  | 1 | 6:42 | Morning | Thursday | 2017 | 2
5114 | 2017-02-16 07:24 | 2017-02-16 07:24 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 24 | 07:24 It was reported b/o fuse for Tx at Well Pagar #45. (Ketigul fdr #2) 11:30 Checked & found, @1,@2 b/o 3.5SF fuse for 150Kva Tx at Well Pagar #45. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Animal. (Bird) |  | 1 | 7:24 | Morning | Thursday | 2017 | 2
5115 | 2017-02-16 08:40 | 2017-02-16 08:40 | 44KV MINAS - RUMBAI LINE | Fair | Powerline - Conductor | 0 | 08:40 13.8KV Minas ACB #21 (44KV Minas-Rumbai line) T/LO. Checked & found, 13.8Kv Minas ACB #21 T/LO. Ctr: 74-77 R/F: 51G-@1. 09:22 Patrolled the line & found, @3 broken Dead end insulator & touching to conductor o/p #MR-77. Isolated Powerline towards South Rumbai Substation by opening 44KV LBS #MR-75. 10:03 Blocked & closed, 13.8KV Minas ACB #21, Ok. (Energized East & North Rumbai substation) 10:20 Manually opened: -44KV South Rumbai OCB #1 & its isolation switch at South Rumbai substation. -4.16KV Recl. fdr #1,#2,#3 & fdr #4 at South Rumbai Substation. Transferring all load feeders of South Rumbai Substation. South Rumbai fdr #2 to East Rumbai fdr #2. (By closing LBS #5RG-03 at 10:39) South Rumbai fdr #3 to East Rumbai fdr #1. (By closing LBS #4RE-12 at 10:48) South Rumbai fdr #4 to North Rumbai fdr #2. (By closing LBS #2RE-09 at 10:50) Part load S.Rumbai fdr #1 to E.Rumbai fdr #2. (By opening LBS #4RF-09 & closing LBS #4RE-15) Part load S.Rumbai fdr #1 to E.Rumbai fdr #1. (By closing LBS #4RF-01) Cause: Conductor. |  | 1 | 8:40 | Morning | Thursday | 2017 | 2
5116 | 2017-02-16 09:26 | 2017-02-16 09:26 | 13.8KV MINAS FEEDER #5 | Fair | Unidentified | 0 | 09:26 Minas ACB fdr #5 T/O. Ctr: 87-88 RF: Did not appear. 09:33 Blocked & closed Minas ACB fdr #5, Ok. Then released the Block. Not patrolled yet. |  | 1 | 9:26 | Morning | Thursday | 2017 | 2
5117 | 2017-02-16 09:26 | 2017-02-19 08:55 | 13.8KV MINAS FEEDER #5 | Fair | Unidentified | 0 | Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 9:26 | Morning | Thursday | 2017 | 2
5118 | 2017-02-16 10:40 | 2017-02-16 10:40 | 13.8KV BANGKO FEEDER #1 | Fair | Unidentified (Fuse) | 32 | 10:40 It was reported b/o fuse for Tx at Well Bangko #274. 11:11 Checked & found, @2 b/o 15K fuse for 300Kva Tx at Well Bangko #274. Tested the Tx & found, normal. (good reading) Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 10:40 | Morning | Thursday | 2017 | 2
5119 | 2017-02-16 16:41 | 2017-02-16 16:41 | 13.8KV DURI FIELD FEEDER #3 | Fair | Dead End Insulator | 0 | Duri Field ACB fdr #3 T/R 1x. Not checked yet. |  | 1 | 16:41 | Afternoon | Thursday | 2017 | 2
5120 | 2017-02-16 16:41 | 2017-02-17 16:00 | 13.8KV DURI FIELD FEEDER #3 | Fair | Dead End Insulator | 0 | Checked & found, Duri Field ACB fdr #3 T/R 1x Ctr: 350-351 R/F: 51N. Patrolled the line & found, @1, @2 flashed over Dead end Insulators o/p #01-04-01. Cause: Dean end Insulator. |  | 1 | 16:41 | Afternoon | Thursday | 2017 | 2
5121 | 2017-02-17 09:30 | 2017-02-17 09:30 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | 09:30 It was reported b/o fuse for Tx o/p #01-05-16. 09:42 Checked & found, @1,@2 b/o 3.1SF fuses for 112.5Kva Tx o/p #01-05-16. Replaced b/o fuse above with same size, then energized the TX. Cause: Unidentified (Fuse). | 1111 | 1 | 9:30 | Morning | Friday | 2017 | 2
5122 | 2017-02-17 09:47 | 2017-02-17 09:47 | 13.8KV 3D FEEDER #2 | Fair | Planned Maintenance | 21 | 09:47 Manual open LBS #3E-64, to replace @2 broken Dead end Insulator o/p #4D-33. (12 Wells were down during the JOB) 10:18 Closed LBS #3E-64. Cause: Planned Maintenance. | 1111 | 1 | 9:47 | Morning | Friday | 2017 | 2
5123 | 2017-02-17 15:13 | 2017-02-17 15:13 | MINAS POWER PLANT |  |  | - | 15:13 S/U MGT #2, then on line the Unit at 15:44. |  | 1 | 15:13 | Afternoon | Friday | 2017 | 2
5124 | 2017-02-17 16:23 | 2017-02-17 16:23 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 6 | LIBO OCB fdr #1 T/R 1x. Not checked yed. | 1111 | 1 | 16:23 | Afternoon | Friday | 2017 | 2
5125 | 2017-02-17 16:23 | 2017-02-19 07:36 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 6 | Checked & found, Libo OCB fdr #1 T/R 1x Ctr: 414-415 R/F: 50N. Patrolled the line, but found nothing. Cause: Unidentified. | 1111 | 1 | 16:23 | Afternoon | Friday | 2017 | 2
5126 | 2017-02-18 07:07 | 2017-02-18 07:07 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | 07:07 Duri Field ACB fdr #2 T/O. Ctr: 987-988 R/F: 51N. (On block due to RIG APS #3519 activity) Confirmed to HES Rig Team & found, their Jobs has finished. 07:23 Manual closed Duri Field ACB fdr #2. Patrolled the Line, but found nothing Cause: Unidentified. | 1111 | 1 | 7:07 | Morning | Saturday | 2017 | 2
5127 | 2017-02-18 08:30 | 2017-02-18 08:30 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 08:30 It was reported b/o fuse for Tx o/p #07-T1-03. ( D.Field fdr #4) 08:47 Checked & found, @1,@3 b/o 3.1SF fuses for 112.5kva Tx o/p #07-T1-03. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 8:30 | Morning | Saturday | 2017 | 2
5128 | 2017-02-18 15:52 | 2017-02-18 15:52 | 13.8KV S. BALAM FEEDER #1 | Fair | Pin Insulator | 142 | So.Balam VCB fdr #1 T/R 1x. Not checked yet. | 1111 | 1 | 15:52 | Afternoon | Saturday | 2017 | 2
5129 | 2017-02-18 15:52 | 2017-02-20 11:48 | 13.8KV S. BALAM FEEDER #1 | Fair | Pin Insulator | 142 | Checked & found, So.Balam VCB fdr #1 T/R 1x Ctr: 384-385 R/F: 51N. Patrolled the line & found, @1 broken Pin Insulator o/p #NN. (Near Well So.Balam #49) Cause: Pin Insulator. | 1111 | 1 | 15:52 | Afternoon | Saturday | 2017 | 2
5130 | 2017-02-19 23:59 | 2017-02-19 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system normal condition. |  | 1 | 23:59 | Night | Sunday | 2017 | 2
5131 | 2017-02-20 23:59 | 2017-02-20 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system was normal condition. |  | 1 | 23:59 | Night | Monday | 2017 | 2
5132 | 2017-02-21 09:45 | 2017-02-21 09:45 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 13 | 09:45-12:15 Blocked Pematang fdr #2. Replaced @1,@2 broken Dead end Insulator o/p #34BC-77. (S/D Well Pematang #41 during the job) Cause: Maintenance job. |  | 1 | 9:45 | Morning | Tuesday | 2017 | 2
5133 | 2017-02-21 15:20 | 2017-02-21 15:20 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 46 | 8D OCB fdr #10 T/R 1x. Not checked yet. |  | 1 | 15:20 | Afternoon | Tuesday | 2017 | 2
5134 | 2017-02-21 15:20 | 2017-02-25 19:45 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 46 | Checked & found, 8D OCB fdr #10 T/R 1x Ctr: 245-246 R/F: Did not appear. Patrolled the line & found, @2,@3 F/O Pin Insulators o/p #NN. Cause: Lightning |  | 1 | 15:20 | Afternoon | Tuesday | 2017 | 2
5135 | 2017-02-21 16:04 | 2017-02-21 16:04 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 34 | Ketigul VCB fdr #1 T/R 1x. Ketigul fdr #2 Load dropped 40A (195-155A). Not checked yet. |  | 1 | 16:04 | Afternoon | Tuesday | 2017 | 2
5136 | 2017-02-21 16:04 | 2017-02-22 16:46 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 34 | Checked & found, Ketigul VCB fdr #1 T/R 1x Ctr: 176-177 R/F: 51@2. Patrolled the line & found, @1,@2 source side Flashed over Recloser bushing o/p #33AK-09. Cause: Lightning. |  | 1 | 16:04 | Afternoon | Tuesday | 2017 | 2
5137 | 2017-02-21 17:14 | 2017-02-21 17:14 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 66 | 17:14 OKB OCB fdr #2 T/R 1x. 17:25 OKB OCB fdr #2 T/R 1x again. Not checked yet. |  | 1 | 17:14 | Afternoon | Tuesday | 2017 | 2
5138 | 2017-02-21 17:14 | 2017-02-22 17:16 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 66 | Checked & found, OKB OCB fdr #2 T/R 2x Ctr: 1299-1301 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:14 | Afternoon | Tuesday | 2017 | 2
5139 | 2017-02-21 17:23 | 2017-02-21 17:23 | 13.8KV CENTRAL KOTABATAK FEEDER #3 | Rain and Lightning | Lightning | 40 | CKBS VCB fdr #3 T/R 1x. CKBS fdr #1 Load dropped 286A (316-30A). CKBS fdr #2 Load dropped 250A (258-8A). Not checked yet. |  | 1 | 17:23 | Afternoon | Tuesday | 2017 | 2
5140 | 2017-02-21 17:23 | 2017-02-23 15:41 | 13.8KV CENTRAL KOTABATAK FEEDER #3 | Rain and Lightning | Lightning | 40 | Checked & found, CKBS VCB fdr #3 T/R 1x Ctr: 98-99 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:23 | Afternoon | Tuesday | 2017 | 2
5141 | 2017-02-22 07:00 | 2017-02-22 07:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 114 | CKBS VCB fdr #5 T/R 1x. CKBS fdr #6 Load dropped 178A (192-14A). Not checked yet. |  | 1 | 7:00 | Morning | Wednesday | 2017 | 2
5142 | 2017-02-22 07:00 | 2017-02-23 15:42 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 114 | Checked & found, CKBS VCB fdr #5 T/R 1x Ctr: 147-148 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 7:00 | Morning | Wednesday | 2017 | 2
5143 | 2017-02-22 09:27 | 2017-02-22 09:27 | 115KV MINAS - 6D LINE | Fair | Guy Wire | 272 | 115Kv MSY GCB #65 T/R 1x. 115Kv MSY GCB #63 T/O. 115Kv 6D OCB #22 T/R 1x. (115KV MSY - 6D line T/R) 4D OCB fdr #4 T/O, then close at 09:40. 4D OCB Fdr #5 T/O, then close at 09:40. 6D fdr #1 Load dropped 104A (212-108A). 6D fdr #2 Load dropped 201A (240-39A). 6D fdr #3 Load dropped 259A (282-23A). 6D fdr #4 Load dropped 179A (179-0A). 6D fdr #5 Load dropped 140A (220-80A). 6D fdr #6 Load dropped 239A (246-7A). Not checked yet. |  | 1 | 9:27 | Morning | Wednesday | 2017 | 2
5144 | 2017-02-22 09:27 | 2017-02-26 11:26 | 115KV MINAS - 6D LINE | Fair | Guy Wire | 272 | Checked & found 115KV MSY GCB #65 T/R 1x Ctr: 242-243. 115KV MSY GCB #63 T/SO. Ctr: 262-263 R/F: 87L-@B & 21G-@B. 115Kv 6D OCB #22 T/R 1x Ctr: 482-483 R/F: 21G-@B. (115KV MSY - 6D line T/R) Patrolled the line & found, broken guy wire & touching to @2 power line o/p #M6D-18. Cause: Broken Guy Wire. |  | 1 | 9:27 | Morning | Wednesday | 2017 | 2
5145 | 2017-02-22 19:42 | 2017-02-22 19:42 | MINAS POWER PLANT |  |  | - | 19:42 Off Line MGT #2, then S/D the Unit for Stand By. |  | 1 | 19:42 | Night | Wednesday | 2017 | 2
5146 | 2017-02-23 08:07 | 2017-02-23 08:07 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Pin Insulator | 0 | C.Duri ACB fdr #15 T/R 1x. Not patrolled yet. |  | 1 | 8:07 | Morning | Thursday | 2017 | 2
5147 | 2017-02-23 08:07 | 2017-02-25 17:50 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Pin Insulator | 0 | Checked & found, C.Duri ACB fdr #15 T/R 1x Ctr: 372-373 R/F: 51N. Patrolled the line, but found nothing. Cause: Pin Insulator. |  | 1 | 8:07 | Morning | Thursday | 2017 | 2
5148 | 2017-02-23 15:25 | 2017-02-23 15:25 | MINAS POWER PLANT |  |  | - | 15:25 S/U MGT #9, then online the Unit at 15:51. |  | 1 | 15:25 | Afternoon | Thursday | 2017 | 2
5149 | 2017-02-23 17:48 | 2017-02-23 17:48 | MINAS POWER PLANT |  |  | - | Off line MGT #5, then S/D the Unit for S/B. |  | 1 | 17:48 | Afternoon | Thursday | 2017 | 2
5150 | 2017-02-23 18:00 | 2017-02-23 18:00 | MINAS POWER PLANT |  |  | - | Off line MGT #1, then S/D the Unit for S/B. |  | 1 | 18:00 | Afternoon | Thursday | 2017 | 2
5151 | 2017-02-23 19:57 | 2017-02-23 19:57 | 13.8KV CENTRAL DURI FEEDER #3 | Rain and Lightning | Lightning | 0 | C.Duri ACB fdr #3 T/R 1x Ctr: 291-292 R/F: 50@1,@2. Not patrolled yet. |  | 1 | 19:57 | Night | Thursday | 2017 | 2
5152 | 2017-02-23 19:57 | 2017-02-25 17:52 | 13.8KV CENTRAL DURI FEEDER #3 | Rain and Lightning | Lightning | 0 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 19:57 | Night | Thursday | 2017 | 2
5153 | 2017-02-23 20:30 | 2017-02-23 20:30 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 55 | Bekasap VCB fdr #6 T/R 1x. Not checked yet. |  | 1 | 20:30 | Night | Thursday | 2017 | 2
5154 | 2017-02-23 20:30 | 2017-02-25 17:30 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 55 | Checked & found, Bekasap VCB fdr #6 T/R 1x Ctr: 347-348 R/F: 51@1. Patrolled the line & found, @1 broken Pin Insulator o/p #30BI-16. Cause: Lightning. |  | 1 | 20:30 | Night | Thursday | 2017 | 2
5155 | 2017-02-24 03:30 | 2017-02-24 03:30 | 13.8KV BATANG FEEDER #1 | Drizzle | Lightning | 0 | Batang OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 3:30 | Night | Friday | 2017 | 2
5156 | 2017-02-24 03:30 | 2017-02-27 14:18 | 13.8KV BATANG FEEDER #1 | Drizzle | Lightning | 0 | Checked & found, Batang OCB fdr #1 T/R 1x Ctr: 135-136 R/F: 51N. Patrolled the line & found, @1 F/O Dead end Insulator on LBS #39AL-01. Cause: Lightning. |  | 1 | 3:30 | Night | Friday | 2017 | 2
5157 | 2017-02-24 10:07 | 2017-02-24 10:07 | 13.8KV 3D FEEDER #2 | Fair | Planned Maintenance | 103 | 10:07-11:20 Manual opened 3D OCB fdr #2. (after transfer part load to 4D fdr #5) To replacing broken Dead-end Insulator & 2 pcs broken Pin Insulator o/p #3D-75. (Some wells were off during this Job). Cause: Planned Maintenance. |  | 1 | 10:07 | Morning | Friday | 2017 | 2
5158 | 2017-02-24 12:18 | 2017-02-24 12:18 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 4 | 12:18 It was reported b/o fuse for Tx o/p #07-T5-11. 14:50 Checked & found, @1, @2, b/o 3.1SF fuses for 112.5Kva Tx o/p #07-T5-11. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 12:18 | Afternoon | Friday | 2017 | 2
5159 | 2017-02-24 18:49 | 2017-02-24 18:49 | 13.8KV KETIGUL FEEDER#3 | Cloudy and Lightning | Lightning | 6 | Ketigul VCB fdr #3 T/R 1X. Not checked yet. |  | 1 | 18:49 | Afternoon | Friday | 2017 | 2
5160 | 2017-02-24 18:49 | 2017-02-26 16:59 | 13.8KV KETIGUL FEEDER#3 | Cloudy and Lightning | Lightning | 6 | Checked & found, Ketigul VCB fdr #3 T/R 1x Ctr: 175-176 R/F: 51@2. Patrolled the line & found, @2 F/O Dead end Insulator o/p #31AR-25. Cause: Lightning. |  | 1 | 18:49 | Afternoon | Friday | 2017 | 2
5161 | 2017-02-24 22:34 | 2017-02-24 22:34 | 13.8KV BANGKO FEEDER #1 | Fair | Transformer Failure | 74 | 22:34 It was reported that b/o fuse for Tx at Well Bangko #240. 23:14 Checked & found, @1,@3 b/o fuses for 150 Kva Tx at Well Bangko # 240. Tested the Tx & found, Low Mega ohm reading. Cause: Tx failure (low megger reading). This Tx is not replaced yet. |  | 1 | 22:34 | Night | Friday | 2017 | 2
5162 | 2017-02-24 22:34 | 2017-02-26 13:41 | 13.8KV BANGKO FEEDER #1 | Fair | Transformer Failure | 74 | Replaced 150Kva Tx failure with the same size & energized the Tx at Well Bangko #240. Cause: Tx Failure. |  | 1 | 22:34 | Night | Friday | 2017 | 2
5163 | 2017-02-24 23:04 | 2017-02-24 23:04 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 19 | 8C fdr #1 Load dropped 114A (188-74A). Not checked yet. |  | 1 | 23:04 | Night | Friday | 2017 | 2
5164 | 2017-02-24 23:04 | 2017-02-26 13:09 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 19 | Checked & found, Recl. 9D-14A (8C fdr #1) T/R 1x Ctr: 173-174. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 23:04 | Night | Friday | 2017 | 2
5165 | 2017-02-25 11:45 | 2017-02-25 11:45 | 115KV KOTABATAK JUNCTION - LIBO LINE | Fair | Unidentified | 16 | 115KV KBJ GCB #53 T/R 1x. 115KV KBJ GCB #55 T/R 1x. (115KV KBJ-Libo Line T/R) Not checked yet. |  | 1 | 11:45 | Morning | Saturday | 2017 | 2
5166 | 2017-02-25 11:45 | 2017-01-03 19:45 | 115KV KOTABATAK JUNCTION - LIBO LINE | Fair | Unidentified | 16 | Checked & Found 115KV KBJ-Libo GCB#53 T/R 1x Ctr:228-229 R/F:21BC. 115KV KBJ-Libo GCB#55 T/R 1x Ctr:312-313 R/F:21BC. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 11:45 | Morning | Saturday | 2017 | 2
5167 | 2017-02-25 11:49 | 2017-02-25 11:49 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 0 | 11:49-12:12 Manually Opened 6D OCB fdr #1. Requested by Minas-GS #4 due to WIP Problem. (No Prod. Loss charge to PGT) Cause: Planned Maintenance. |  | 1 | 11:49 | Morning | Saturday | 2017 | 2
5168 | 2017-02-25 12:12 | 2017-02-25 12:12 | 13.8KV 4D FEEDER #4 | Fair | Planned Maintenance | 0 | 12:12-12:49 Manually Opened 4D OCB fdr #4. Requested by Minas-GS #4 due to WIP Problem. (No Prod. Loss charge to PGT) Cause: Planned Maintenance. |  | 1 | 12:12 | Afternoon | Saturday | 2017 | 2
5169 | 2017-02-25 12:39 | 2017-02-25 12:39 | 115KV BATANG - SINTONG LINE | Fair | Unidentified | 518 | 12:39 115KV Batang GCB #1 T/R 1x. 115KV Sintong GCB #25 T/SO 1x R/F: 21G-Z1 & 67N-@3. (115KV Batang-Sintong line T/SO). 12:45 Manual closed 115KV Sintong GCB #25, Ok. Respectively: Balam fdr #1 load dropped 15A (120-105A). Prod loss: 68 Bbls / 8 wells. Balam fdr #4 load dropped 10A (186-176A). Prod loss: 148 Bbls / 8 wells. Nella fdr #1 load dropped 227A (286-59A). Prod loss: 134 Bbls / 77 wells. Nella fdr #2 load dropped 12A (90-78A). Prod loss: 8 Bbls / 5 wells. Bangko fdr #1 load dropped 35A (217-182A). Prod loss: 25 Bbls / 13 wells. Bangko fdr #4 load dropped 110A (243-133A). Prod loss: 50 Bbls / 28 wells. Menggala fdr #1 load dropped 120A (183-63A). Sintong fdr #1 load dropped 25A (80-55A). Prod loss: 23 Bbls / 8 wells. Sintong fdr #2 load dropped 112A (223-111A). Prod loss: 62 Bbls / 37 wells. Ketigul fdr #2 load dropped 10A (194-184A). --------------------------------------- + Grand Total : 518 Bbls / 184 wells. Not checked yet. | 11111 | 1 | 12:39 | Afternoon | Saturday | 2017 | 2
5170 | 2017-02-25 12:39 | 2017-02-26 08:05 | 115KV BATANG - SINTONG LINE | Fair | Unidentified | 518 | Checked & found: -115KV Sintong GCB #25 T/R 1x Ctr: 296-297 R/F: 67N (Inst) (Z-1) & 21@3. -115KV Batang GCB #1 T/SO. Ctr: 91-92 R/F: 67N (Inst.) (Z-1) & 21@3. (115KV Batang - Sintong line T/SO) Patrolled the line, but found nothing. Cause: Unidentified. | 11111 | 1 | 12:39 | Afternoon | Saturday | 2017 | 2
5171 | 2017-02-25 14:30 | 2017-02-25 14:30 | 13.8KV MENGGALA FEEDER #1 | Fair | Dead End Insulator | 53 | Menggala fdr #1 load dropped 116A (186-70A). Not checked yet. |  | 1 | 14:30 | Afternoon | Saturday | 2017 | 2
5172 | 2017-02-25 14:30 | 2017-02-27 07:55 | 13.8KV MENGGALA FEEDER #1 | Fair | Dead End Insulator | 53 | Checked & found, Recl. 19AN-04 (Menggala fdr #1) T/R 1x Ctr: 634-635. Patrolled the line & found, @1,@3 broken Dead end Insulators o/p #29Y-02. Cause: Dead end Insulator. |  | 1 | 14:30 | Afternoon | Saturday | 2017 | 2
5173 | 2017-02-25 16:27 | 2017-02-25 16:27 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 65 | 16:27 Bangko OCB fdr #4 T/R 1x. Bangko GFPC T/R 1x. Ground fault alarm on Bangko fdr #4. 16:44 Bangko OCB fdr #4 T/R 1x again. Bangko GFPC T/O. 16:45 Manually Close Bangko GFPC, Ok. Not checked yet. |  | 1 | 16:27 | Afternoon | Saturday | 2017 | 2
5174 | 2017-02-25 16:27 | 2017-02-27 10:29 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 65 | Checked & found, Bangko OCB fdr #4 T/R 3x Ctr: 110-113 R/F: 51N. Patrolled the line & found, @2 broken L/A o/p #24Y-21. Cause: Lightning. |  | 1 | 16:27 | Afternoon | Saturday | 2017 | 2
5175 | 2017-02-25 16:27 | 2017-02-25 16:27 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 0 | Bangko fdr #1 Load dropped 115A (211-96A). Not checked yet. |  | 1 | 16:27 | Afternoon | Saturday | 2017 | 2
5176 | 2017-02-25 16:27 | 2017-02-27 10:42 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 24Y-21 (Bangko fdr #1) T/R 1x Ctr: 102-103. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:27 | Afternoon | Saturday | 2017 | 2
5177 | 2017-02-25 16:44 | 2017-02-25 16:44 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 152 | Nella fdr #1 load dropped 213A (286-73A). Prod loss : 122 Bbls / 70 wells. Nella fdr #2 load dropped 45A (90-45A). Prod loss : 30 Bbls / 17 wells. Nella GFPC in blocked position. Not checked yet. |  | 1 | 16:44 | Afternoon | Saturday | 2017 | 2
5178 | 2017-02-25 16:44 | 2017-02-27 07:22 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 152 | Checked all Reclosers at downstream Nella fdr #1 & fdr #2 & found, normal. (Ctr: Did not operate) Checked Nella fdr #1 & fdr #2 breaker and found, normal. (Ctr: Did not operate & No Relay flag) Patrolled the line, but found nothing. Cause: Unidentified. (Suspected some wells of Nella fdr #1 & fdr #2 were down due to voltage Dip when BKO OCB fdr #4 T/R) |  | 1 | 16:44 | Afternoon | Saturday | 2017 | 2
5179 | 2017-02-25 16:59 | 2017-02-25 16:59 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 120 | Sintong fdr #2 load dropped 179A (222-43A). Prod loss : 99 Bbls / 60 wells. Sintong fdr #1 load dropped 22A (78-56A). Prod loss : 21 Bbls / 7 wells. Sintong GFPC T/R 1x. Ground fault alarm on Sintong fdr #1. Not checked yet. |  | 1 | 16:59 | Afternoon | Saturday | 2017 | 2
5180 | 2017-02-25 16:59 | 2017-02-27 07:28 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 120 | Checked & found, Recl. 28AF-02 (Sintong fdr #2) T/R 1x Ctr: 634-635. Patrolled the line & found, @1 broken Pin Insulator o/p #29Y-02. Cause: Lightning. |  | 1 | 16:59 | Afternoon | Saturday | 2017 | 2
5181 | 2017-02-25 17:10 | 2017-02-25 17:10 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 81 | Pungut fdr #2 load dropped 16A (64-48A). Not checked yet. |  | 1 | 17:10 | Afternoon | Saturday | 2017 | 2
5182 | 2017-02-25 17:10 | 2017-02-26 08:00 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 81 | 08:00 It was reported no power at No.Asih Fields. 09:50 Checked & found, Recl. 44BX-06 (Pungut fdr #2) T/SO. Ctr: 355-356. 10:00 Blocked & closed Recl. 44BX-06, Ok. Then released the block. Not Patrolled yet. |  | 1 | 17:10 | Afternoon | Saturday | 2017 | 2
5183 | 2017-02-25 17:10 | 2017-02-27 07:41 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 81 | Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:10 | Afternoon | Saturday | 2017 | 2
5184 | 2017-02-25 17:22 | 2017-04-02 08:22 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked & found C.Duri ACB fdr#1 T/R 1x, Ctr: 198-199, R/F: 51N,@1. Patrolled the Line, but Found Nothing. Cause : Unidentified |  | 1 | 17:22 | Afternoon | Saturday | 2017 | 2
5185 | 2017-02-25 17:22 | 2017-02-25 17:22 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | C.Duri fdr #1 Load dropped 54A (142-88A). Not checked yet. |  | 1 | 17:22 | Afternoon | Saturday | 2017 | 2
5186 | 2017-02-25 17:29 | 2017-02-25 17:29 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 70 | 17:29 Ketigul VCB fdr #1 T/R 1x. Ketigul fdr #2 load dropped 103A (198-95A). Ketigul GFPC in blocked postion. 17:43 Ketigul VCB fdr #1 T/R 1x again. Prod loss : 72 Bbls / 21 wells. Ketigul fdr #2 load dropped 54A (198-95A). Prod loss : 29 Bbls / 5 wells. Ketigul fdr #3 load dropped 8A (23-15A). Prod loss : 30 Bbls / 2 wells. Ketigul GFPC in blocked postion. Not checked yet. |  | 1 | 17:29 | Afternoon | Saturday | 2017 | 2
5187 | 2017-02-25 17:29 | 2017-02-26 17:22 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 70 | Checked & found, Ketigul VCB fdr #1 T/R 3x Ctr: 177-180 R/F: 51N. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:29 | Afternoon | Saturday | 2017 | 2
5188 | 2017-02-25 18:26 | 2017-02-25 18:26 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 0 | 4D OCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 18:26 | Afternoon | Saturday | 2017 | 2
5189 | 2017-02-25 18:26 | 2017-01-03 19:26 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, 4D OCB fdr#5 T/R 2x Ctr:291-293 R/F:51N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 18:26 | Afternoon | Saturday | 2017 | 2
5190 | 2017-02-25 18:29 | 2017-02-25 18:29 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Pin Insulator | 98 | (Pematang, Petani & Ketigul RTU Failed) 44KV Pematang-Petani line load dropped 69A (90-21A). Suspected Petani VCB fdr #1 T/R 1x. Petani fdr #2 load dropped 31A (66-35A). Not checked yet. |  | 1 | 18:29 | Afternoon | Saturday | 2017 | 2
5191 | 2017-02-25 18:29 | 2017-02-27 16:58 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Pin Insulator | 98 | Checked & found, Petani OCB fdr #1 T/R 1x Ctr: 28-29 R/F: 51@1. Patrolled the line & found, @1 F/O Pin Insulator o/p #33AX-10. Cause: Lightning. |  | 1 | 18:29 | Afternoon | Saturday | 2017 | 2
5192 | 2017-02-25 18:39 | 2017-02-25 18:39 | 115KV 4B - 5B LINE | Rain and Lightning | Lightning | 347 | 18:39 115KV 5B GCB #21 T/SO. 115KV 5B GCB #26 T/SO. (115KV 5B-4B line T/SO) 4B Substation no power due to 4B-KBJ Line in open position. (Diff Relay problem) Frequency system raise up to 60.78Hz. Requested NDC, MGT, CGT to decrease load. 18:52 Manually opened 5B OCB fdr #1. (GS #6 Requested) Closed at: 19:00. Manually opened 5B OCB fdr #5. (GS #6 Requested) Closed at: 19:00. 18:53 Offline MGT #6 then Shutdown the unit due to high Freq. 18:53 Manually closed 115KV 5B OCB #21, Ok. 19:53 Manually closed 115KV 5B OCB #26, Ok. Not checked yet. Respectevely feeder load dropped. Bangko fdr #1 Prod loss: 20 Bbls / 10 wells. Bangko fdr #4 Prod loss: 34 Bbls / 19 wells. Nella fdr #1 Prod loss: 121 Bbls / 70 wells. Nella fdr #2 Prod loss: 29 Bbls / 16 wells. Sintong fdr #2 Prod loss: 13 Bbls / 8 Wells. ------------------------------------- + Total : 217 Bbls / 123 wells. |  | 1 | 18:39 | Afternoon | Saturday | 2017 | 2
5193 | 2017-02-25 18:39 | 2017-01-03 19:39 | 115KV 4B - 5B LINE | Rain and Lightning | Lightning | 347 | Checked & found 115KV Line 4B-5B T/SO Ctr:2919-2921 R/F:NN. 115KV Line 5B-4B T/SO Ctr:933-934 R/F:NN. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 18:39 | Afternoon | Saturday | 2017 | 2
5194 | 2017-02-25 18:53 | 2017-02-25 18:53 | MINAS POWER PLANT |  |  | - | 18:53 Offline MGT #6, then S/D the Unit due to 115KV line 5B-4B T/SO (High Freq). |  | 1 | 18:53 | Afternoon | Saturday | 2017 | 2
5195 | 2017-02-25 19:10 | 2017-02-25 19:10 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 25 | 4B OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 19:10 | Night | Saturday | 2017 | 2
5196 | 2017-02-25 19:10 | 2017-01-03 20:10 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 25 | Checked & found 4B OCB fdr#1 T/R 2x Ctr:294-296 R/F:50N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 19:10 | Night | Saturday | 2017 | 2
5197 | 2017-02-26 00:22 | 2017-02-26 00:22 | 13.8KV BANGKO FEEDER #4 | Fair | Switchboard Problem | 21 | 00:22 It was reported b/o fuse for Tx at Well BKO #295. 00:50 Checked & found, @1,@2 b/o 7.8SF fuses for 300Kva Tx at Well BKO #295. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Switchboard Problem. |  | 1 | 0:22 | Night | Sunday | 2017 | 2
5198 | 2017-02-26 00:22 | 2017-02-26 00:22 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified (Fuse) | 14 | 00:22 It was reported b/o fuse for Tx at Well BKO #39. 01:10 Checked & found, @1,@3 b/o 3.5SF fuses for 150Kva Tx at Well BKO #39. Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 0:22 | Night | Sunday | 2017 | 2
5199 | 2017-02-26 00:22 | 2017-02-26 00:22 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 33 | 00:22 It was reported b/o fuse for Tx at Well BKO #59. 02:04 Checked & found, @1 b/o 7.8SF fuse for 300Kva Tx at Well BKO #59). Replaced b/o fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 0:22 | Night | Sunday | 2017 | 2
5200 | 2017-02-26 07:20 | 2017-02-26 07:20 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 33 | 07:20 Ketigul VCB fdr #1 T/R 1x. Prod loss: 36 Bbls / 21 wells. Ketigul fdr #2 load dropped 170A (195- 25A). Prod loss: 6 Bbls / 2 wells. Ketigul fdr #3 load dropped 22A (23-1A). Prod loss: 16 Bbls / 4 wells. Ketigul GFPC in blocked position. Not checked yet. 17:24 Checked & found, Ketigul VCB fdr #1 T/R 3x Ctr: 177-180 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 7:20 | Morning | Sunday | 2017 | 2
5201 | 2017-02-26 10:52 | 2017-02-26 10:52 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy and Lightning | Lightning | 62 | CKBS VCB fdr #5 T/R 1x. CKBS GFPC-TX #2 did not operate. Not checked Yet. |  | 1 | 10:52 | Morning | Sunday | 2017 | 2
5202 | 2017-02-26 10:52 | 2017-02-27 16:39 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy and Lightning | Lightning | 62 | Checked & found, CKBS VCB fdr #5 T/R 1x Ctr: 148-149 R/F: 51@1. Patrolled the line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 10:52 | Morning | Sunday | 2017 | 2
5203 | 2017-02-26 19:34 | 2017-02-26 19:34 | 13.8KV DARLING VCB FEEDER #3 | Fair | Transformer Failure | 0 | 19:34 Darling VCB fdr #3 T/LO. Darling GFPC-TX #1 T/R 1x. 19:55 Blocked & closed Darling VCB fdr #3, but failed. 20:23 Opened LBS #05-N7-20N. (C.Duri fdr #10 and Darling fdr #3 are separated) 20:26 Blocked & closed Darling VCB fdr #3, Ok. Patrolled at D/S of LBS #05-N7-20N & found, @1 b/o fuse for 1500Kva Tx, (at Trench 4C at DIF #5). 21:00 Closed LBS #05-N7-20N, Ok. (C.Duri fdr #10 fed by Darling fdr #3). (After isolating its Tx) Cause: Suspected by Transformer failure. |  | 1 | 19:34 | Night | Sunday | 2017 | 2
5204 | 2017-02-27 08:08 | 2017-02-27 08:08 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 29 | C.Duri ACB fdr #1 T/R 1x Ctr: 191-192 R/F: 51N. Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 8:08 | Morning | Monday | 2017 | 2
5205 | 2017-02-27 21:42 | 2017-02-27 21:42 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 4 | Rangau fdr #2 Load dropped 73A (76-3A). (Suspected Rangau VCB fdr #2 T/R) Not checked yet. |  | 1 | 21:42 | Night | Monday | 2017 | 2
5206 | 2017-02-27 21:42 | 2017-02-03 21:42 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 4 | Checked & found Recl. 23BD01 T/R 1x Ctr:189-190. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 21:42 | Night | Monday | 2017 | 2
5207 | 2017-02-28 09:34 | 2017-02-28 09:34 | CENTRAL DURI POWER PLANT |  |  | - | CGT #4 S/U, then Online to system. for Replacing CGT#3 down, to trouble shoot Load swing. |  | 1 | 9:34 | Morning | Tuesday | 2017 | 2
5208 | 2017-02-28 10:10 | 2017-02-28 10:10 | CENTRAL DURI POWER PLANT |  |  | - | 10:10 Offline CGT #3 then shutdown the unit for S/B. (For troubleshooting load swing). |  | 1 | 10:10 | Morning | Tuesday | 2017 | 2
5209 | 2017-01-03 07:14 | 2017-01-03 07:14 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | D. Field VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 7:14 | Morning | Tuesday | 2017 | 1
5210 | 2017-01-03 07:14 | 2017-04-03 08:13 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | Checked & found, D. Field VCB fdr#2 T/R 1x Ctr: 988-989 R/F: 51N,@1. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 7:14 | Morning | Tuesday | 2017 | 1
5211 | 2017-01-03 09:06 | 2017-01-03 09:06 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Lightning | 0 | D. Community fdr#1 T/R 1x. Not checked yet. |  | 1 | 9:06 | Morning | Tuesday | 2017 | 1
5212 | 2017-01-03 09:06 | 2017-04-03 07:27 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Lightning | 0 | Checked & found, D. Community ACB #25 (fdr#1) T/R 1x Ctr: 94-95 R/F: 51N. Patrolled the Line & found nothing. Cause: Lightning |  | 1 | 9:06 | Morning | Tuesday | 2017 | 1
5213 | 2017-01-03 09:58 | 2017-01-03 09:58 | 13.8KV SINTONG FEEDER #2 | Fair | Powerline - Hot Line Clamp | 210 | 09:58 Sintong VCB fdr#2 T/LO Sintong GFPC T/R 1x Ground fault alarm on Sintong fdr#2. 10:50 Checked & found, Sintong VCB fdr#2 T/LO Ctr: 450-454 R/F: 51 @2. Also found, Sintong GFPC T/R 1x Ctr: 944-945 R/F: 51N. (Recl. 28-AF-17 in Bypassed, under Sintong fdr#2). Patrolled the Line & found, @2 broken Jumper (touched Pole) for Recl. 29-AK-24, (Supplied to Pagar Gas plant). Opened LBS 29-AI-04 to isolated the Recloser above. 10:59 Manually Closed Sintong VCB fdr#2, Ok. (Sintong field back to normal, Except Pagar Gas plant). 12:30 Bypassed Recl. 29-AK-24, then Closed LBS 29-AI-04. (Pagar Gas plant back to normal) Cause: Hot line Clampt (jumper for Recloser). |  | 1 | 9:58 | Morning | Tuesday | 2017 | 1
5214 | 2017-01-03 11:44 | 2017-01-03 11:44 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 19 | 11:44 It was reported b/o fuse for Tx at well S. Balam #328 (S. Balam fdr#4). 15:30 Checked & found, @3 b/o fuse for 150KVATX. Replaced the fuse with the same size, then energized the TX. Cause: Unidentified. |  | 1 | 11:44 | Morning | Tuesday | 2017 | 1
5215 | 2017-01-03 12:54 | 2017-01-03 12:54 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Duri Field fdr #3 T/R 1x. Not checked yet. |  | 1 | 12:54 | Afternoon | Tuesday | 2017 | 1
5216 | 2017-01-03 12:54 | 2017-04-03 08:18 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Checked & found, D. Field VCB fdr#3 T/R 1x Ctr: 351-352 R/F: 51N. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 12:54 | Afternoon | Tuesday | 2017 | 1
5217 | 2017-01-03 17:30 | 2017-01-03 17:30 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 0 | 17:30 It was reported b/o fuse for Tx o/p 10-J8-02 (ND fdr#1). 18:24 Checked & found, @3 b/o fuse for 112.5KVATX. Replaced the fuse with the same size, then energized the TX. Cause : Animal (monkey). |  | 1 | 17:30 | Afternoon | Tuesday | 2017 | 1
5218 | 2017-02-03 | 2017-02-03 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Unidentified (Fuse) | 55 | 00:00 It was reported b/o fuse for Tx at well So. Menggala#08 (Menggala fdr#1). 01:40 Replaced @3 b/o fuse for 300KVA Tx with the same size then energized the Tx. Cause: Unidentified Fuse. |  | 1 | 0:00 | Night | Friday | 2017 | 2
5219 | 2017-02-03 10:43 | 2017-02-03 10:43 | CENTRAL DURI POWER PLANT |  |  | - | 10:43 S/U CGT#3, then online the unit at 11:02. |  | 1 | 10:43 | Morning | Friday | 2017 | 2
5220 | 2017-02-03 16:16 | 2017-02-03 16:16 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning Arrester | 52 | So. Bekasap fdr#1 load dropped 100A (126-26A). Not checked yet. |  | 1 | 16:16 | Afternoon | Friday | 2017 | 2
5221 | 2017-02-03 16:16 | 2017-04-03 15:29 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning Arrester | 52 | Checked & found, Recl. 36-BI-04 T/R 1x Ctr: 740-741 R/F: 51N @3. Patrolled the Line & found, @3 broken LA o/p 35-BI-05. Cause : Lightning Arrester |  | 1 | 16:16 | Afternoon | Friday | 2017 | 2
5222 | 2017-02-03 17:02 | 2017-02-03 17:02 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Pin Insulator | 0 | Sintong fdr#2 load dropped 145A (213-68A). Not checked yet. |  | 1 | 17:02 | Afternoon | Friday | 2017 | 2
5223 | 2017-02-03 17:02 | 2017-04-03 07:48 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Pin Insulator | 0 | Checked & found, Recl. 28-AF-02 T/R 1x Ctr: 635-636 R/F: 51N @1. Patrolled the Line & found, @1 Broken Pin insulator O/P 28-AA-10 Cause : Pin Insulator |  | 1 | 17:02 | Afternoon | Friday | 2017 | 2
5224 | 2017-02-03 17:12 | 2017-02-03 17:12 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Unidentified | 65 | 13.8KV OKB OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 17:12 | Afternoon | Friday | 2017 | 2
5225 | 2017-02-03 17:12 | 2017-03-03 20:12 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Unidentified | 65 | Checked & found, OKB OCB fdr#2 T/R 1x Ctr:1301-1302 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:12 | Afternoon | Friday | 2017 | 2
5226 | 2017-03-03 06:32 | 2017-03-03 06:32 | 13.8KV BEKASAP FEEDER #6 | Cloudy | Dead End Insulator | 52 | Bekasap VCB fdr#6 T/R 1x. Not checked yet. |  | 1 | 6:32 | Morning | Friday | 2017 | 3
5227 | 2017-03-03 06:32 | 2017-04-03 15:15 | 13.8KV BEKASAP FEEDER #6 | Cloudy | Dead End Insulator | 52 | Checked & found, Bekasap VCB fdr#6 T/R 1x Ctr: 348-349 R/F: 51N @2. Patrolled the Line & found, @2 broken Dead-end Insulator O/P 39-BI-16. Cause : Dead End Insulator |  | 1 | 6:32 | Morning | Friday | 2017 | 3
5228 | 2017-03-03 07:32 | 2017-03-03 07:32 | 13.8KV SINTONG GFPC | Fair | Unidentified | 0 | Sintong fdr#2 load dropped 10A (204-194A). Sintong GFPC T/R 1X. Ground fault alarm on Sintong fdr #2. Not checked yet. |  | 1 | 7:32 | Morning | Friday | 2017 | 3
5229 | 2017-03-03 07:32 | 2017-06-03 07:25 | 13.8KV SINTONG GFPC | Fair | Unidentified | 0 | Checked & found, Sintong GFPC T/R 1x ctr: 949-950 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:32 | Morning | Friday | 2017 | 3
5230 | 2017-03-03 11:00 | 2017-03-03 11:00 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 11:00 It was reported B/O fuse at well BKO#291 (Bangko fdr#4). Not checked yet. |  | 1 | 11:00 | Morning | Friday | 2017 | 3
5231 | 2017-03-03 11:00 | 2017-04-03 08:06 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 0 | Checked & found, @2, @3 b/o Fuses for 150KVA TX at well BKO #291. Replaced the Fuse with the same size, then energized the TX. Cause : Unidentified (Fuse) |  | 1 | 11:00 | Morning | Friday | 2017 | 3
5232 | 2017-03-03 11:40 | 2017-03-03 11:40 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Duri Community ACB#25 (fdr#1) T/R 1X. Not checked yet. |  | 1 | 11:40 | Morning | Friday | 2017 | 3
5233 | 2017-03-03 11:40 | 2017-06-03 07:51 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB fdr #1 T/R 1x Ctr: 94-95 R/F: 51N Patrolled the line, but found nothing. Cause: Unidentified. |  | 1 | 11:40 | Morning | Friday | 2017 | 3
5234 | 2017-03-03 17:19 | 2017-03-03 17:19 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Unidentified | 49 | 17:13 So.Bekasap OCB fdr#1 load dropped 100A (121-21A). 17:19 So.Bekasap OCB fdr#1 T/SO. 17:43 Blocked and closed So.Bekasap OCB fdr#1,ok, then released the block. Not checked yet. |  | 1 | 17:19 | Afternoon | Friday | 2017 | 3
5235 | 2017-03-03 17:19 | 2017-04-03 15:29 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Unidentified | 49 | Checked & found, S. Bekasap OCB fdr#1 T/SO, Ctr: 349-350, R/F: None. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 17:19 | Afternoon | Friday | 2017 | 3
5236 | 2017-03-03 23:30 | 2017-03-03 23:30 | 13.8KV DURI FIELD FEEDER #4 | Fair | Low mega-ohm reading | 21 | 23:30 It was reported b/o fuse for Tx o/p 07-U3-11 (D.Field fdr#4). 24:00 Checked & found, @1, @2 b/o fuse for 112.5KVATX. Performed TTR & Megger the TX, found Low megger reading. Cause: Low megger reading. (Will Replaced Soon). |  | 1 | 23:30 | Night | Friday | 2017 | 3
5237 | 2017-03-03 23:30 | 2017-05-03 11:43 | 13.8KV DURI FIELD FEEDER #4 | Fair | Low mega-ohm reading | 21 | 11:43 Replaced Failure 112.5KVA TX o/p 07-U3-11 with the same size then energized the TX. Cause: Low Megger reading. |  | 1 | 23:30 | Night | Friday | 2017 | 3
5238 | 2017-04-03 06:27 | 2017-04-03 06:27 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified (L/A) | 0 | 06:27 Duri Community VCB fdr#5 T/R 1x ctr: 105-106 R/F: 51, @1,@2. Patrolled the Line & found, @1, @2 broken LA o/p 1-KT-48. Cause : Unidentified (L/A) |  | 1 | 6:27 | Morning | Monday | 2017 | 4
5239 | 2017-05-03 16:21 | 2017-05-03 16:21 | 13.8KV 8C FEEDER #2 | Fair | Unidentified | 7 | 16:21 8C VCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 16:21 | Afternoon | Wednesday | 2017 | 5
5240 | 2017-05-03 16:21 | 2017-06-03 17:50 | 13.8KV 8C FEEDER #2 | Fair | Unidentified | 7 | Checked & found, 8C VCB fdr#2 T/R 1x Ctr: 508-509 R/F: 51N. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 16:21 | Afternoon | Wednesday | 2017 | 5
5241 | 2017-05-03 16:26 | 2017-05-03 16:26 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | 25 | 16:26 C.Duri ACB fdr #1 T/R 1x Ctr: 192-193 R/F: 51G, 51N. Not Patrolled yet. |  | 1 | 16:26 | Afternoon | Wednesday | 2017 | 5
5242 | 2017-05-03 16:26 | 2017-11-03 14:00 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | 25 | 14:00 Checked and found, C. Duri 13.8KV ACB #11 T/R 2X ctr: 191 193 R/F: 51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:26 | Afternoon | Wednesday | 2017 | 5
5243 | 2017-06-03 09:45 | 2017-06-03 09:45 | MINAS POWER PLANT |  |  | - | 09:45 S/U MGT #5 and Online the unit at 10:05 to restore the load. |  | 1 | 9:45 | Morning | Saturday | 2017 | 6
5244 | 2017-06-03 10:21 | 2017-06-03 10:21 | MINAS POWER PLANT |  |  | - | 10:21 Offline MGT #7 then S/D the unit for Clean Gas Scrubber Tank. |  | 1 | 10:21 | Morning | Saturday | 2017 | 6
5245 | 2017-06-03 10:22 | 2017-06-03 10:22 | 13.8KV PETANI FEEDER #2 | Fair | Lightning Arrester | 0 | 10:22 Petani OCB fdr #2 T/R 1x. Not checked yet. | 11111 | 1 | 10:22 | Morning | Saturday | 2017 | 6
5246 | 2017-06-03 10:22 | 2017-08-03 17:37 | 13.8KV PETANI FEEDER #2 | Fair | Lightning Arrester | 0 | Checked & found, Petani OCB fdr#2 T/R 1x, Ctr: 216-217, R/F: 51N. Patrolled the Line & found, @1 Broken LA o/p PTN#48. Cause : Lightning | 11111 | 1 | 10:22 | Morning | Saturday | 2017 | 6
5247 | 2017-06-03 16:26 | 2017-06-03 16:26 | 13.8KV 6D FEEDER #5 | Heavy Rain | Lightning | 30 | 16:26 6D OCB fdr#5 T/R 2x Ctr: 736-738 R/F: 50N Not checked yet. | 11111 | 1 | 16:26 | Afternoon | Saturday | 2017 | 6
5248 | 2017-06-03 16:26 | 2017-08-03 17:56 | 13.8KV 6D FEEDER #5 | Heavy Rain | Lightning | 30 | Checked & found, 6D OCB fdr#5 T/R 2x, Ctr: 736-738. R/F: 50N. Patrolled the Line & found, @3 broken Pin support O/P 5D-114. Cause : Lightning | 11111 | 1 | 16:26 | Afternoon | Saturday | 2017 | 6
5249 | 2017-06-03 18:20 | 2017-06-03 18:20 | 13.8KV BATANG FEEDER #2 | Fair | Unidentified | 1 | 11:30 It was reported b/o fuse for Tx at well Rantau Bais #59 (Batang fdr#2). 18:20 Checked & found, @2 ,@3 b/o fuse for 150KVA TX . Replaced b/o fuse above with same size then energized TX. Cause : Unidentified |  | 1 | 18:20 | Afternoon | Saturday | 2017 | 6
5250 | 2017-07-03 08:56 | 2017-07-03 08:56 | 13.8KV 5B FEEDER #1 | Fair | Powerline - Conductor | 74 | 08:56 5B fdr #1 load dropped 47A (94-47A). 10:26 Checked and found, Recl. 5B-06 T/SO ctr: 30-31. Blocked and closed Recl. above but tripped again. 11:05 Patrolled the line and found, @3 broken conductor o/p 5B-33. (8 wells off down). 16:40 Repaired @3 broken conductor o/p 5B-33. Blocked and closed Recl. 5B-06, Ok, then released the block. Cause: Conductor. | 1111 | 1 | 8:56 | Morning | Monday | 2017 | 7
5251 | 2017-07-03 11:18 | 2017-07-03 11:18 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 19 | 11:18 It was reported b/o fuses for Tx at well So. Balam #69. 12:25 Checked and found, @2, @3 b/o fuses for 100KVA TX. Replaced b/o fuse above with same size, then energized the TX. Cause: Animal (Monkey). | 11111 | 1 | 11:18 | Morning | Monday | 2017 | 7
5252 | 2017-07-03 16:01 | 2017-07-03 16:01 | 13.8KV 3D FEEDER #2 | Fair | Lightning | 71 | 16:01 3D OCB fdr #2 T/R 1X. 3D fdr #3 load dropped 15A ( 149-134A). 3D fdr #4 load dropped 27A ( 166-139A). 3D fdr #5 load dropped 12A ( 157-145A). Not checked yet. | 1111 | 1 | 16:01 | Afternoon | Monday | 2017 | 7
5253 | 2017-07-03 16:01 | 2017-08-03 16:01 | 13.8KV 3D FEEDER #2 | Fair | Lightning | 71 | 16:00 Checked and found, 3D OCB fdr #2 T/R 1x Ctr: 240-241 R/F: 51N. Patrolled the line and found nothing. Cause: Lightning. | 1111 | 1 | 16:01 | Afternoon | Monday | 2017 | 7
5254 | 2017-08-03 07:29 | 2017-08-03 07:29 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 07:29 C. Duri fdr #1 load dropped 43A (141-98A). Not checked yet. | 11111 | 1 | 7:29 | Morning | Thursday | 2017 | 8
5255 | 2017-08-03 07:29 | 2017-11-03 13:57 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 13:57 Checked and found, Recl. 38AS09 T/R 1X ctr: 199-200 d/s C. Duri fdr #1. Patrolled the line but nothing found. Cause: Unidentified. | 11111 | 1 | 7:29 | Morning | Thursday | 2017 | 8
5256 | 2017-08-03 10:28 | 2017-08-03 10:28 | 13.8KV ROKAN FEEDER #2 | Fair | Powerline - Jumper | 257 | 10:28 It was reported unbalance voltage at wells Kopar #07, #27 and #34 (Rokan fdr#2) 12:20 Checked and found, @2 broken Jumper o/p 29AV- 47. 15:40 Blocked Rokan VCB fdr#2 Replaced broken Jumper above then released the block. Cause : Jumper | 11111 | 1 | 10:28 | Morning | Thursday | 2017 | 8
5257 | 2017-08-03 21:03 | 2017-08-03 21:03 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 21:03 It was reported b/o fuse for Tx at well KB #385. Will be replaced tomorrow. | 11111 | 1 | 21:03 | Night | Thursday | 2017 | 8
5258 | 2017-08-03 21:03 | 2017-09-03 09:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 09:00 Checked and found, @1 b/o fuse for 550Kva at well KB #385 d/s CKBS fdr #5. Replaced b/o fuse above with same size, then energized the TX. Cause: Unidentified. | 11111 | 1 | 21:03 | Night | Thursday | 2017 | 8
5259 | 2017-09-03 02:57 | 2017-09-03 02:57 | 13.8KV 4D FEEDER #1 | Fair | Unidentified | 0 | 02:57 4D OCB fdr#1 T/R 1x ----->WIP. 4D fdr#6 Load dropped 111A (136-25A) ----->WIP 3D fdr#6 Load dropped 152A (152-55A) ----->WIP 3D fdr#6 Load dropped 112A (113-1A) ----->WIP Manually open Some feeder to anticipated High tank level. (Due to failed to Start WIP). 03:25 Manual Open 3D fdr #F4, and closed at 06:30. 03:50 Manual Open 3D fdr #F7, and closed at 04:06. 03:50 Manual Open 3D fdr #F2, and closed at 06:41. 04:04 Manual Open 4D fdr #F3, and closed at 09:58. 04:05 Manual Open 4D fdr #F5, and closed at 07:22. 04:25 Manual Open 5B fdr #F3, and closed at 10:07. 04:00 Offline MGT #5 and then S/D the unit due to anticipated System High frequency. 17:35 Checked & found, 4D OCB fdr#1 T/R 1x, Ctr: 176-177, R/F: 51. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 2:57 | Night | Sunday | 2017 | 9
5260 | 2017-09-03 03:21 | 2017-09-03 03:21 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 0 | 03:21 Manual Opened 3D OCB fdr #4. Closed back at 06:30. 03:50 Manual Opened 3D OCB fdr #2. Closed back at 06:40. 03:51 Manual Opened 3D OCB fdr #3. Closed back at 06:41. 03:52 Manual Opened 3D OCB fdr #7. Closed back at 04:06. 04:04 Manual Opened 4D OCB fdr #3. Closed back at 09:58. 04:05 Manual Opened 4D OCB fdr #5. Closed back at 07:22. 04:25 Manual Opened 5B OCB fdr #3. Closed back at 10:07. To avoid Over level, due to WIP problem at GS-5. Cause: Planned Maintenance. |  | 1 | 3:21 | Night | Sunday | 2017 | 9
5261 | 2017-09-03 04:00 | 2017-09-03 04:00 | MINAS POWER PLANT |  |  | - | 04:00 Offline MGT #5 then S/D the unit for S/B, due to High Frequency system. (Minas GS 5 all WIP could not start and Open Some feeder for Oil Field). |  | 1 | 4:00 | Morning | Sunday | 2017 | 9
5262 | 2017-09-03 06:45 | 2017-09-03 06:45 | 13.8KV NORTH DURI FEEDER #8 | Fair | Pin Insulator | 1361 | 06:45 N.Duri fdr#8 Load dropped 115A (135-20A). N.Duri fdr#8 Ground fault alarm. 09:40 It was reported No power around Pole 10-K2-27 d/s N. Duri fdr #7. (Load N.Duri fdr #7 feed from N. Duri fdr #8) 10:30 Patrolled the line but found nothing. 11:00 Checked and found Recl. 10-K2-02 T/LO ctr:112-118 d/s N. Duri fdr #8. Continued to patrolled the line. 14:30 Open LBS 10-K4-14 (to separated load N. Duri fdr #7 and N. Duri fdr #8). 14:36 Closed Recl. 10-K2-02. OK Re patrolled the line and found @1, @2, @3 broken Pin Insulator o/p 10. J4. 01A (Ex Recl.). 15:15 Isolated the broken Pin Insulator by opening By-pass Switch o/p 10. J4. 01A (Ex Recl.). 15:27 Closed LBS 10-K4-14 (N. Duri #8 back to supplied load of N. Duri Fdr #7). Cause: Pin Insulator (broken). | 1111 | 1 | 6:45 | Morning | Sunday | 2017 | 9
5263 | 2017-09-03 06:48 | 2017-09-03 06:48 | 13.8KV LIBO FEEDER #2 | Fair | Animal | 8 | Libo OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 6:48 | Morning | Sunday | 2017 | 9
5264 | 2017-09-03 06:48 | 2017-10-03 08:51 | 13.8KV LIBO FEEDER #2 | Fair | Animal | 8 | Checked & found, Libo OCB fdr#2 T/R 1x Ctr: 430-431 R/F: 50N Patrolled the line and found, dead monkey o/p 38-CC-12A Cause: Animal. |  | 1 | 6:48 | Morning | Sunday | 2017 | 9
5265 | 2017-10-03 09:25 | 2017-10-03 09:25 | MINAS POWER PLANT |  |  | - | 09:25 S/U MGT #7 and online the unit at 09:49. |  | 1 | 9:25 | Morning | Tuesday | 2017 | 10
5266 | 2017-10-03 10:03 | 2017-10-03 10:03 | MINAS SWITCH YARD | Fair | Under investigation | 0 | 10:03 115 KV MSY GCB #81 T/O R/F: 86T. 115 KV MSY GCB #83 T/O. 11:26 Checked and found, 115KV Minas TX-11 Bucholz relay operated. Disable relay 86T of TX-11. 11:28 Closed 115KV MSY GCB #81, OK. 11:29 Closed 115KV MSY GCB #83, OK. Cause: Under investigation. |  | 1 | 10:03 | Morning | Tuesday | 2017 | 10
5267 | 2017-10-03 10:45 | 2017-10-03 10:45 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 0 | 10:45 It was reported b/o fuses for Tx o/p 06-R7-16. 14:40 Checked and found, @2 b/o fuse for 112.5Kva TX. Replaced b/o fuse above with same size, then energized the TX. Cause: Animal (Squirrel). | 11111 | 1 | 10:45 | Morning | Tuesday | 2017 | 10
5268 | 2017-10-03 14:15 | 2017-10-03 14:15 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Planned Maintenance | 0 | 14:15 Manually Open fuse for 112.5Kvca TX o/p 09-T1-04 for repair Hot Spot. 15:15 Replaced broken TX with same size, then energized the TX. Cause: Planned Maintenance. | 1111 | 1 | 14:15 | Afternoon | Tuesday | 2017 | 10
5269 | 2017-10-03 15:07 | 2017-10-03 15:07 | MINAS POWER PLANT |  |  | - | 15:07 Offline MGT #8 then S/D the unit for CI. |  | 1 | 15:07 | Afternoon | Tuesday | 2017 | 10
5270 | 2017-10-03 15:28 | 2017-10-03 15:28 | 13.8KV PEMATANG FEEDER #2 | Fair | Animal | 12 | 15:28 It was reported b/o fuses at well Pematang #17. 17:15 Checked and found, @2, @3 b/o fuse for 300Kva TX. Replaced b/o fuse above with same size, then energized the TX. Cause: Animal (Monkey). | 11111 | 1 | 15:28 | Afternoon | Tuesday | 2017 | 10
5271 | 2017-10-03 16:33 | 2017-10-03 16:33 | 13.8KV S. BALAM FEEDER #1 | Heavy Rain | Lightning | 191 | 16:33 Ground fault alarm from So. Balam fdr #1. So. Balam fdr #1 load dropped 102A (125-23A). So. Balam fdr #2 load dropped 63A (98-35A) WIP So. Balam fdr #3 load dropped 100A (100-0A) WIP. So. Balam fdr #4 load dropped 42A (190-148A). Not checked yet. | 1111 | 1 | 16:33 | Afternoon | Tuesday | 2017 | 10
5272 | 2017-10-03 16:33 | 2017-12-03 13:36 | 13.8KV S. BALAM FEEDER #1 | Heavy Rain | Lightning | 191 | 13:36 Checked and found, Recl: 16-Z-25 T/R 1x Counter: 25-26 R/F: 51N. Patrolled the line found nothing. Cause: Suspected by Lightning. | 1111 | 1 | 16:33 | Afternoon | Tuesday | 2017 | 10
5273 | 2017-10-03 18:39 | 2017-10-03 18:39 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Pin Insulator | 23 | Rokan VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 18:39 | Afternoon | Tuesday | 2017 | 10
5274 | 2017-10-03 18:39 | 19/03/2017 19:40 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Pin Insulator | 23 | Checked and found ROKAN VCB fdr #2 T/R 1x R/F: 51N Counter: 1247-1248. Patrolled the line found @3 broken pin insulator on pole 29-AV-35. Cause: Pin Insulator. |  | 1 | 18:39 | Afternoon | Tuesday | 2017 | 10
5275 | 2017-11-03 07:37 | 2017-11-03 07:37 | 13.8KV 3D FEEDER #5 | Fair | Under investigation | 0 | 07:37 3D OCB fdr #5 load dropped 86A (183-97A) --->WIP tripped. Shuted Off same feeders to anticipated Tank over flow due to WIP failed to start. 07:55 Manually open 4D fdr #3, and closed at 10:23. 08:04 Manually open 4D fdr #2, and closed at 10:20. 08:17 Manually open 3D fdr #3, and closed at 10:37. 19:50 Manually open 3D fdr #4, and Closed at 02:07. (March,12, 2017) Manual shuted off some weels : 4D-53E, 3D-86N, 4D-41N, 3D-44, 4D-25 and 4D-51. Cause: under investigation. | 11111 | 1 | 7:37 | Morning | Friday | 2017 | 11
5276 | 2017-11-03 13:20 | 2017-11-03 13:20 | 13.8KV CENTRAL DURI FEEDER #6 | Rain | Lightning | 0 | C Duri ACB #23 ( Feeder #6) T/R 1x R/F: 51N Ctr: 460-461. Not patrolled yet. |  | 1 | 13:20 | Afternoon | Friday | 2017 | 11
5277 | 2017-11-03 13:20 | 14/03/2017 15:34 | 13.8KV CENTRAL DURI FEEDER #6 | Rain | Lightning | 0 | Checked and foundC Duri ACB #23 ( Feeder #6) T/R 1x R/F: 51N Ctr: 460-461. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 13:20 | Afternoon | Friday | 2017 | 11
5278 | 2017-11-03 14:17 | 2017-11-03 14:17 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Unidentified | 148 | 14:17 So. Bekasap 13.8KV OCB fdr #1 T/O R/F: 51@3 Counter: 350-351. 14:25 Blocked and closed 13.8KV So. Bekasap fdr #1 --> OK. 14:29 So Bekasap 13.8KV OCB fdr #1 T/O on blocked position. Patrolled the line nothing found. 15:47 Blocked and close 13.8KV So. Bekasap fdr #1 --> OK and then released the block. Cause: Unidentified. | 1111 | 1 | 14:17 | Afternoon | Friday | 2017 | 11
5279 | 2017-11-03 15:10 | 2017-11-03 15:10 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | 15:10 3D fdr #4 load dropped 126A (173-47A). Ground fault alarm on 3D fdr #4. Not checked yet. | 11111 | 1 | 15:10 | Afternoon | Friday | 2017 | 11
5280 | 2017-11-03 15:10 | 16/03/2017 10:15 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found Recl: 2D-14 T/R 1x Counter: 44-45. Patrolled the line nothing found. Cause: Suspected Lightning. | 11111 | 1 | 15:10 | Afternoon | Friday | 2017 | 11
5281 | 2017-11-03 15:48 | 2017-11-03 15:48 | 230KV N. Duri-KBJ Line - 2 - TWR 129-192 | Fair | Under investigation | 0 | 15:48 230KV Line -2 N.Duri - KBJ T/O, by R/F: Ground Distribution Zone -1 @C to Neutral. (The Line above is In Block Position, due to RIG activity at Well DSF 56-07-13A). 230KV N.Duri GCB #11 T/O, Ctr: 289-290. 230KV N.Duri GCB #13 T/O, Ctr: 277-278. 230KV KBJ GCB #93 T/O, Ctr: 247-248. 230KV KBJ GCB #93 T/O, Ctr: 274-275. Energized 230KV Line -2 N.Duri - KBJ. 17:57 Closed 230KV N.Duri GCB #11. 20:46 Closed 230KV N.Duri GCB #13. 18:01 Closed 230KV KBJ GCB #93. 20:41 Closed 239KV KBJ GCB #94. Cause: Under Investigation. |  | 1 | 15:48 | Afternoon | Friday | 2017 | 11
5282 | 2017-11-03 15:48 | 2017-11-03 15:48 | KOTABATAK JUNCTION SW STA | Fair | Under investigation | 0 | 15:48 230KV-115KV KBJ TX#1 T/O by R/F: 50 BF Pole A,B,C initiated. 115KV KBJ GCB #31 T/O, Ctr: 105-106. 115KV KBJ GCB #33 T/O, Ctr: 245-246. 230KV KBJ GCB #92 T/O, Ctr: 370-371. 230KV KBJ GCB #94 T/O, Ctr: 370-371. Energized the 230KV-115KV KBJ TX#1, after Reset the Relay 20:36 Closed 230KV KBJ GCB #31. 20:40 Closed 230KV KBJ GCB #33. 20:34 Closed 230KV KBJ GCB #92. 20:41 Closed 230KV KBJ GCB #94. Cause: Under Investigation. |  | 1 | 15:48 | Afternoon | Friday | 2017 | 11
5283 | 2017-11-03 17:41 | 2017-11-03 17:41 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Planned Maintenance | 0 | 17:41 Manually opened 8C VCB Feeder #4. Closed at 19:27. 18:05 Manually opened Minas ACB feeder #3. Closed at: 05:24 ( March ,12,2017). 18:17 Manually opened 8D OCB feeder #3. Closed at: 17:24 ( March, 12,2017). Due to WIP Problem at GS #2. Cause: Planned Maintenance. |  | 1 | 17:41 | Afternoon | Friday | 2017 | 11
5284 | 2017-11-03 21:50 | 2017-11-03 21:50 | CENTRAL DURI POWER PLANT |  |  | - | 21:50 Offline CDGT #3, then S/D the unit for S/B, (for troubleshooting over heat at Lower Chasing Boroscope Hole). |  | 1 | 21:50 | Night | Friday | 2017 | 11
5285 | 2017-12-03 08:03 | 2017-12-03 08:03 | MINAS POWER PLANT |  |  | - | 08:03 S/U MGT #5 then Online the unit at 08:22 to restore the load. |  | 1 | 8:03 | Morning | Sunday | 2017 | 12
5286 | 2017-12-03 09:42 | 2017-12-03 09:42 | CENTRAL DURI POWER PLANT |  |  | - | 09:42 S/U CGT #3 then Online the unit at 10:00 to restore the load after fixing Hot gas leakage. |  | 1 | 9:42 | Morning | Sunday | 2017 | 12
5287 | 2017-12-03 16:30 | 2017-12-03 16:30 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Animal | 0 | 16:30 It was reported that B/O fuse for Tx o/p 04-04-20. 17:16 Checked & found, @2 B/O 2.1 SF fuse for 112.5 KVA Tx o/p 04-04-20. Tested the Tx & found normal (good reading). Replaced B/O fuse above with the same size & energized the Tx. Cause: Animal (Monkey). |  | 1 | 16:30 | Afternoon | Sunday | 2017 | 12
5288 | 2017-12-03 17:03 | 2017-12-03 17:03 | 13.8KV BATANG FEEDER #2 | Rain | Lightning | 0 | Batang OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 17:03 | Afternoon | Sunday | 2017 | 12
5289 | 2017-12-03 17:03 | 14/03/2017 20:27 | 13.8KV BATANG FEEDER #2 | Rain | Lightning | 0 | Checked and found Batang OCB fdr #2 T/R 1x Counter: 137-138 R/F: 51N. Patrolled the line found @2,@3 broken pin insulator on pole 36-AG-20. Cause: Lightning. |  | 1 | 17:03 | Afternoon | Sunday | 2017 | 12
5290 | 2017-12-03 19:25 | 2017-12-03 19:25 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 0 | 19:25 Manual Opened 4D VCB fdr#2, Closed at 22:45. To Avoid Over level dueto WIP problem at GS-5. Cause: Planned Maintenance. |  | 1 | 19:25 | Night | Sunday | 2017 | 12
5291 | 2017-03-13 09:49 | 2017-03-13 09:49 | MINAS POWER PLANT |  |  | - | 09:49 Offline MGT#4 and then S/D the unit for S/B. |  | 1 | 9:49 | Morning | Monday | 2017 | 3
5292 | 2017-03-14 03:16 | 2017-03-14 03:16 | MINAS POWER PLANT |  |  | - | 03:16 S/U MGT #2 then online the unit at 03:40. ( to back up load priod NDC #3 will be S/D due to Batt. problem). 14:05 Off line and then S/D MGT #2 for S/B. |  | 1 | 3:16 | Night | Tuesday | 2017 | 3
5293 | 2017-03-14 04:00 | 2017-03-14 04:00 | MINAS POWER PLANT |  |  | - | 04:00 S/U MGT #4 then online the unit at 04:18. ( to back up load priod NDC #3 will be S/D due to Batt. problem). |  | 1 | 4:00 | Morning | Tuesday | 2017 | 3
5294 | 2017-03-14 08:20 | 2017-03-14 08:20 | MINAS POWER PLANT |  |  | - | 08:20 S/U MGT #1 and then On line the unit at 08:58. 13:56 Off line MGT #1 and then S/D the unit for stand by. |  | 1 | 8:20 | Morning | Tuesday | 2017 | 3
5295 | 2017-03-14 08:50 | 2017-03-14 08:50 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 514 | 08:50 Emergency Shut down on NDC #3 (due to replace Battery cell No:57). 08:51 Reduce load of NDC #3. 09:30 Manually opened 4D fdr #5 Closed at :13:11. 09:33 Manually opened 4D fdr #3 Closed at :13:10. 09:42 Manually opened 3D fdr #6 Closed at :13:10. 09:46 Manually opened 5B fdr #5 Closed at :13:09. 09:55 Manually opened 4B fdr #4 Closed at :13:08. 10:02 Manually opened 8D fdr #3 Closed at :13:07. 11:30 Manually opened 5B fdr #4 Closed at :13:08. 10:26 Manually opened 4B fdr #1 Closed at :13:06. 10:03 Off line NDC #3 and then shut down unit. 12:32 S/U NDC #3 and then On line the unit at 13:01. 13:30 Informed to BOB to normalized all Load. Cause: Planned maintenance. Production loss during the JOB: GS #2 -----> 95 Bbls, 13 Wells / 0 WIP. GS #4 -----> 93 Bbls, 15 Wells / 0 WIP. GS #5 -----> 47 Bbls, 07 Wells / 1 WIP. GS #6 ----->264 Bbls 63 Wells / 3 WIP. ----------------------------------------------- TOTAL :499 Bbls 98 Wells / 4 WIP. | 11111 | 1 | 8:50 | Morning | Tuesday | 2017 | 3
5296 | 2017-03-14 09:19 | 2017-03-14 09:19 | CENTRAL KOTABATAK SUBSTATION | Fair | Construction Job | 0 | 09:19 Switching to shut down 115Kv Line CKBS-PTN . 09:36 Opened Suram Fdr#1, -----> then closed at 21:07 09:38 Opened Suram fdr#2, -----> then closed at 21:10 09:43 Opened Petapahan fdr#2, -----> then closed at 20:54. 09:58 Opened Petapahan fdr#1, -----> then closed at 20:19. 10:16 Opened 115Kv Line CKBS-PTN GCB1, then closed at 19:46. Cause: Construction Job. |  | 1 | 9:19 | Morning | Tuesday | 2017 | 3
5297 | 2017-03-14 14:20 | 2017-03-14 14:20 | MINAS POWER PLANT |  |  | - | 14:20 Off line and then S/D MGT #5 for S/B. |  | 1 | 14:20 | Afternoon | Tuesday | 2017 | 3
5298 | 2017-03-14 16:33 | 2017-03-14 16:33 | 13.8KV NORTH DURI FEEDER #2 | Fair | Broken Fuse Cut Out | 0 | 16:33 It was reported B/O fuse o/p 10-J8-04 (N.Duri fdr#2). 17:00 Checked & found @3 B/O FCO for 112.5 KVa Tx o/p 10-J8-04. (Would be changed tomorrow). Cause: Broken Fuse Cut Out. |  | 1 | 16:33 | Afternoon | Tuesday | 2017 | 3
5299 | 2017-03-14 16:33 | 2017-03-15 10:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Broken Fuse Cut Out | 0 | Replaced @3 B/O FCO for 112.5 KVa Tx o/p 10-J8-04, and energized the Tx. Cause: Broken Fuse Cut Out. |  | 1 | 16:33 | Afternoon | Tuesday | 2017 | 3
5300 | 2017-03-14 18:50 | 2017-03-14 18:50 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 78 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 18:50 | Afternoon | Tuesday | 2017 | 3
5301 | 2017-03-14 18:50 | 2017-03-16 17:50 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 78 | Checked & found Ketigul VCB fdr#2 T/R 1x Ctr:227-228 R/F:51@3. Patrolled the line & found Dead Monkey at Terminal pole Pagar#30. Cause : Animal (Monkey). |  | 1 | 18:50 | Afternoon | Tuesday | 2017 | 3
5302 | 2017-03-14 21:21 | 2017-03-14 21:21 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Animal | 0 | 21:21 C. Duri fdr #6 load dropped 41A (179-138A). (All load C.Duri fdr#9 feed from C.Duri fdr#6) Not checked yet. | 11111 | 1 | 21:21 | Night | Tuesday | 2017 | 3
5303 | 2017-03-14 21:21 | 2017-03-16 17:21 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Animal | 0 | Checked & found Recl. 04-5-02 T/R 1x Ctr:211-212 R/F:51@1. Patrolled the line & found Dead Monkey at pole 04-7-03. Cause : Animal (Monkey). | 11111 | 1 | 21:21 | Night | Tuesday | 2017 | 3
5304 | 2017-03-15 17:13 | 2017-03-15 17:13 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Unidentified | 12 | 17:13 Petapahan fdr#1 Load dropped 48A (89-41A). 17:30 Checked & found Recl 30CZ23 T/R 1x Ctr:150-151. 18:00 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:13 | Afternoon | Wednesday | 2017 | 3
5305 | 2017-03-16 02:22 | 2017-03-16 02:22 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 83 | 02:22 5B fdr #2 T/R 1x (5B RTU failed on 02:21). 5B fdr #3 load dropped 27A (32-5A). 5B fdr #1 load dropped 70A (94-24A) 5B fdr #6 load dropped 124A (190-66A) --->WIP. Not checked yet. | 11111 | 1 | 2:22 | Night | Thursday | 2017 | 3
5306 | 2017-03-16 02:22 | 2017-03-21 06:07 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 83 | Checked and found 5B OCB fdr #2 T/R 1x Counter: 351-352 R/F: -. Patrolled the line found nothing. Cause: Suspected Lightning. | 11111 | 1 | 2:22 | Night | Thursday | 2017 | 3
5307 | 2017-03-16 07:48 | 2017-03-16 07:48 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 68 | Sintong VCB fdr # 1 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 7:48 | Morning | Thursday | 2017 | 3
5308 | 2017-03-16 07:48 | 2017-03-18 17:48 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 68 | Checked & found, Sintong VCB fdr#1 T/R 1x Ctr:383-384 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 7:48 | Morning | Thursday | 2017 | 3
5309 | 2017-03-16 08:57 | 2017-03-16 08:57 | 13.8KV DURI FIELD FEEDER #3 | Fair | Guy Wire | 11 | 08:57 It was reported B/O fuse o/p 01-4-28 (D.Field fdr#3). 11:00 Checked and found, @1, @3 B/O fuse for 112.5 Kva Tx o/p 01-4-28. Broken Guy Wire & touched to FCO and secondary cable o/p 01-4-28. @1, @3 Broken FCO & secondary cable. 15:30 Repaired Broken Guy Wire at pole 01-4-28. Replaced @1, @3 broken Fuse Cut Out o/p -1-4-28. Repaired @1, @3 Secondary Cable o/p 01-4-28. Replaced @1, @3 B/O fuse for 112.5Kva Tx with the same size, then energized Tx. Cause: Guy Wire. |  | 1 | 8:57 | Morning | Thursday | 2017 | 3
5310 | 2017-03-16 09:21 | 2017-03-16 09:21 | 8 DELTA SUBSTATION | Fair | Under investigation | 322 | 09:21 115 Kv 8D C/S-1 T/O. 09:49 Opened 8D fdr #1, then closed at 10:30. Prod loss: 34 Bbls / 7 wells. 09:49 Opened 8D fdr #2. Prod loss: 28 Bbls / 4 wells. 09:49 Opened 8D fdr #3, then closed at 10:30. Prod loss: 87 Bbls / 17 wells. 09:49 Opened 8D fdr #4, then closed at 10:26. Prod loss: 24 Bbls / 3 wells. 09:50 Opened 8D fdr #5. Prod loss: 64 Bbls / 14 wells. ------------------------------------ + Total Prod loss: 237 Bbls / 45 wells. 09:56 Checked and found, 115 Kv 8D C/S TX-1 T/O Ctr:82-83 R/F: 87T21@2@3. also found, @2, @3 Flashed Over Bushing of 8D VR-1. 10:15 By Passed 8D VR-1. 10:20 Closed 115Kv 8D C/S Tx-1, ok. 11:00 Closed LBS 8E-18 (8D fdr#2 Transfer to 8D fd#11). 11:24 Closed LBS 8E-02 (8D fdr#5 Transfer to Minas fdr#5). Cause: Under Investigation. |  | 1 | 9:21 | Morning | Thursday | 2017 | 3
5311 | 2017-03-16 12:38 | 2017-03-16 12:38 | 13.8KV BANGKO FEEDER #4 | Cloudy | Dead End Insulator | 68 | Bangko VCB fdr #4 T/R 1x. Bangko fdr #1 load dropped 96A (188-92A). Not checked yet. |  | 1 | 12:38 | Afternoon | Thursday | 2017 | 3
5312 | 2017-03-16 12:38 | 2017-03-18 10:55 | 13.8KV BANGKO FEEDER #4 | Cloudy | Dead End Insulator | 68 | Checked and found, Bangko VCB fdr#4 T/R 1x Ctr:01-02 R/F:51N. Patrolled the line & found, @3 broken Dead end insulator on pole 25-Z-10. Cause: Broken dead end insulator. |  | 1 | 12:38 | Afternoon | Thursday | 2017 | 3
5313 | 2017-03-16 15:20 | 2017-03-16 15:20 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 15:20 It was reported B/O fuse for Tx at well So.Balam#219 (So. Balam fdr#4). 16:35 Replaced @2 B/O fuse for 100 Kva with the same size fuse. Couse : Unidentified fuse. |  | 1 | 15:20 | Afternoon | Thursday | 2017 | 3
5314 | 2017-03-16 17:50 | 2017-03-16 17:50 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 10 | 17:50 It was reported b/o fuses for Tx at well BKO #86. Checked and found, @3 b/o fuse for 300KVA TX. Replaced b/o fuse above with same size, then energized the TX. Cause: Unidentified fuse. | 1111 | 1 | 17:50 | Afternoon | Thursday | 2017 | 3
5315 | 2017-03-16 20:21 | 2017-03-16 20:21 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Recloser - Control Recloser | 198 | 20:21 Ground fault alarm from So. Balam fdr #1. So. Balam fdr #1 load dropped 100A (123-23A). So. Balam fdr #2 load dropped 95A (95-0A). ---->WIP. So. Balam fdr #3 load dropped 103A (103-0A). ---->WIP. 21:40 It was reported no power at loc So Balam 228,178,357,233,118. Checked and found, Recl. 17-Z-01 T/SO Counter: 57-58. Blocked and closed Recl. 17-Z-01 but Failed. Will be executed tomorrow morning. Cause: Suspected Control Recloser. | 11111 | 1 | 20:21 | Night | Thursday | 2017 | 3
5316 | 2017-03-16 20:21 | 2017-03-17 10:30 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Recloser - Control Recloser | 198 | 10:00 Open fuses for 5 well d/s Recl 17Z01. 10:30 Closed By Pass Recl. 17Z01. 10:35 Closed Fuses for 5 well d/s Recl. 17Z01. Cause: Control Recloser. | 11111 | 1 | 20:21 | Night | Thursday | 2017 | 3
5317 | 2017-03-16 20:21 | 2017-03-16 20:21 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Unidentified | 0 | So. Balam fdr #4 load dropped 80A (188-108A). Not checked yet. | 11111 | 1 | 20:21 | Night | Thursday | 2017 | 3
5318 | 2017-03-16 20:21 | 2017-03-19 08:22 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked All Recloser D/S So.Balam fdr#1 & found Normal operation. Patrolled the line but found nothing Cause: Unidentified. | 11111 | 1 | 20:21 | Night | Thursday | 2017 | 3
5319 | 2017-03-16 20:21 | 2017-03-16 20:21 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Unidentified | 0 | Nella fdr #1 load dropped 111A (261-150A). Nella fdr #2 load dropped 7A (83-76A). Not checked yet. |  | 1 | 20:21 | Night | Thursday | 2017 | 3
5320 | 2017-03-16 20:21 | 2017-03-19 07:21 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked All Recloser D/S Nella fdr#1 & found Normal operation. Patrolled the line but found nothing Cause: Unidentified. |  | 1 | 20:21 | Night | Thursday | 2017 | 3
5321 | 2017-03-17 08:30 | 2017-03-17 08:30 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | 08:30 It was reported B/O fuse for Tx o/p SD-03 at EDT Office (D. Comm fdr#3). 10:30 Replaced @2 ,@3 B/O fuse for 3x50Kva Tx with the same size. Cause: Animal (Bird). |  | 1 | 8:30 | Morning | Friday | 2017 | 3
5322 | 2017-03-17 08:42 | 2017-03-17 08:42 | 13.8KV PUNGUT FEEDER #2 | Fair | Dead End Insulator | 4 | Pungut VCB dr#2 T/R 1x. Not checked yet. |  | 1 | 8:42 | Morning | Friday | 2017 | 3
5323 | 2017-03-17 08:42 | 2017-03-19 15:22 | 13.8KV PUNGUT FEEDER #2 | Fair | Dead End Insulator | 4 | Checked and found, Pungut OCB fdr #2 T/R 2x Counter: 349-351 R/F: 51N. Patrolled the line & found, @1 broken dead end insulator on pole 45-BS-01. Cause: Dead End Insulator. |  | 1 | 8:42 | Morning | Friday | 2017 | 3
5324 | 2017-03-17 15:14 | 2017-03-17 15:14 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning | 0 | Menggala fdr#1 Load dropped 103A (174-71A). Not checked yet. |  | 1 | 15:14 | Afternoon | Friday | 2017 | 3
5325 | 2017-03-17 15:14 | 2017-03-19 15:14 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning | 0 | Checked and found, Recl. 19-AN-04 T/R 1x Ctr:325-326 R/F:51N. Patrolled the line & found, @3 Broken Dead End Insulator on Terminal Pole Menggala North #13. Cause : Lightning. |  | 1 | 15:14 | Afternoon | Friday | 2017 | 3
5326 | 2017-03-17 17:16 | 2017-03-17 17:16 | 13.8KV PUNGUT FEEDER #1 | Fair | Unidentified | 0 | 17:16 Pungut VCB fdr#1 T/R 1x. 17:17 Pungut VCB fdr#1 T/R 1x again. Not checked yet. |  | 1 | 17:16 | Afternoon | Friday | 2017 | 3
5327 | 2017-03-17 17:16 | 2017-03-19 16:16 | 13.8KV PUNGUT FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Pungut VCB fdr#1 T/R 2x Ctr:356-358 R/F: 51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:16 | Afternoon | Friday | 2017 | 3
5328 | 2017-03-17 17:18 | 2017-03-17 17:18 | 13.8KV PUNGUT FEEDER #2 | Fair | Unidentified | 0 | Pungut VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 17:18 | Afternoon | Friday | 2017 | 3
5329 | 2017-03-17 17:18 | 2017-03-19 16:18 | 13.8KV PUNGUT FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Pungut VCB fdr#2 T/R 1x Ctr:351-352 R/F: 51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:18 | Afternoon | Friday | 2017 | 3
5330 | 2017-03-17 17:20 | 2017-03-17 17:20 | PUNGUT SUBSTATION | Fair | Voltage regulator failure | 323 | 17:20 115KV Pungut C/S T/O. 115 KV Pungut OCB #21 T/O. 115 KV Pungut OCB #22 T/O. Pungut Substation black out. 17:50 Manually opened Pungut OCB fdr #1. Manually opened Pungut OCB fdr #2. Checked and found: - 115 KV Pungut C/S T/O. - 115 KV Pungut OCB #21 T/O R/F: 87B (86B operate) Ctr: 632 (not operate) - 115 KV Pungut OCB #22 T/O R/F: 87B (86B operate) Ctr: 141-142. 19:17 Closed 115 KV Pungut OCB #21 --> Success. 19:18 Closed 115 KV Pungut OCB #22 --> Failed. 19:20 Closed 115 KV Pungut C/S --> Success. 19:23 115 KV Pungut C/S T/O again. 115 KV Pungut OCB #21 T/O again. Checked and found, Pungut Voltage Regulator oil leaks (in abnormal condition). 19:41 Isolated and By passed Pungut Voltage Regulator. 19:42 Closed 115 KV Pungut OCB #21 --> Success. Closed 115 KV Pungut C/S --> Success. 20:04 Blocked and closed Pungut OCB fdr #1 and then released the block Ctr: 358-359. 20:05 Blocked and closed Pungut OCB fdr #2 and then released the block Ctr: 352-353. Cause: Voltage Regulator failure. |  | 1 | 17:20 | Afternoon | Friday | 2017 | 3
5331 | 2017-03-18 14:13 | 2017-03-18 14:13 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 2 | Pinang VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 14:13 | Afternoon | Saturday | 2017 | 3
5332 | 2017-03-18 14:13 | 2017-03-19 14:13 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 2 | Checked& found, Pinang VCB fdr#1 T/R 1x Ctr:418-419 R/F: 51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 14:13 | Afternoon | Saturday | 2017 | 3
5333 | 2017-03-19 00:47 | 2017-03-19 00:47 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 47 | 00:47 8C VCB fdr #1 T/R 1x. 16:30 Checked & found, 8C OCB fdr#1 T/R 1x Ctr:662-663 R/F: N/A. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 0:47 | Night | Sunday | 2017 | 3
5334 | 2017-03-19 06:34 | 2017-03-19 06:34 | 13.8KV BEKASAP FEEDER #6 | Cloudy | Lightning | 52 | 06:34 Bekasap Main VCB fdr #6 T/R 1x. 15:15 Checked & found, Bekasap VCB fdr#6 T/R 1x Ctr:349-350 R/F:51N. Patrolled the line & found, @1 Broke Pin Insulator on pole 39-BE-05. Cause : Lightning. |  | 1 | 6:34 | Morning | Sunday | 2017 | 3
5335 | 2017-03-19 14:08 | 2017-03-19 14:08 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 0 | C.Duri fdr#1 Load dropped 45A (130-85A). Not checked yet. |  | 1 | 14:08 | Afternoon | Sunday | 2017 | 3
5336 | 2017-03-19 14:08 | 2017-03-21 19:08 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 0 | Checked & found Recl. 38AS09 T/R 1x Ctr:200-201 R/F:51@1@2. Patrolled the line & Found Kite o/p 38AS11. Cause : Others (Kite). |  | 1 | 14:08 | Afternoon | Sunday | 2017 | 3
5337 | 2017-03-19 20:10 | 2017-03-19 20:10 | 13.8KV RANGAU FEEDER #1 | Rain and Lightning | Unidentified | 48 | Rangau OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 20:10 | Night | Sunday | 2017 | 3
5338 | 2017-03-19 20:10 | 2017-03-25 14:50 | 13.8KV RANGAU FEEDER #1 | Rain and Lightning | Unidentified | 48 | Checked and found Rangau OCB Fdr#1 T/R 1X, Ctr:10-11, R/F: 51N. Patroled the line, but found nothing . Cause : Unidentified |  | 1 | 20:10 | Night | Sunday | 2017 | 3
5339 | 2017-03-20 06:38 | 2017-03-20 06:38 | 13.8KV CENTRAL DURI FEEDER #1 | Rain | Others | 0 | 06:38 C. Duri fdr #1 load dropped 40A (135-95A). Not checked yet. |  | 1 | 6:38 | Morning | Monday | 2017 | 3
5340 | 2017-03-20 06:38 | 2017-03-26 08:13 | 13.8KV CENTRAL DURI FEEDER #1 | Rain | Others | 0 | Patrolled the Line found Recl. 38-AS-09 T/R 2x, Ctr: 201-203, R/F: 51 N, @2. (CD fdr#1). Re patrolled the Line, found Kite hank out o/p 38-AS-35. Cause: Other (Kite). |  | 1 | 6:38 | Morning | Monday | 2017 | 3
5341 | 2017-03-20 09:15 | 2017-03-20 09:15 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | 0 | 09:15 Manually open Bangko OCB fdr #1. 09:39 Manually closed Bangko OCB fdr #1 (due to demonstration) 10:53 Manually open Bangko OCB fdr #1. 17:57 Blocked and closed Bangko OCB fdr #1 and then released the block. (after replacing PCV by Production team). Cause: Plan Maintenance (Replaced 12" Pressure Control Valve WIP Phase 1). (No Prod. loss charge to PGT). |  | 1 | 9:15 | Morning | Monday | 2017 | 3
5342 | 2017-03-20 09:15 | 2017-03-20 09:15 | 13.8KV 5B FEEDER #1 | Fair | Recloser | 89 | 09:15 5B OCB fdr#1 T/LO. 5B fdr#2 load dropped 113 A (162-49 A) 5B fdr#3 load dropped 16 A (32-16 A) 5B fdr#6 load dropped 188 A (190-2 A) WIP.GS #4. 10:31 Checked and found, 5B fdr#1 T/LO Counter: 228-232 R/F: 51@2. Patrolled the line & found, burnt out Recloser 5B-06. Dismantled jumpers Recloser and By pass Recloser 5B-06. 11:43 Manually closed 5B OCB fdr#1. Cause: Recloser failure. |  | 1 | 9:15 | Morning | Monday | 2017 | 3
5343 | 2017-03-20 10:12 | 2017-03-20 10:12 | MINAS POWER PLANT |  |  | - | 10:12 S/U MGT#8 then online the unit at 10:33. For running test after Combustion Inspection. |  | 1 | 10:12 | Morning | Monday | 2017 | 3
5344 | 2017-03-20 16:52 | 2017-03-20 16:52 | MINAS POWER PLANT |  |  | - | 16:52 offline MGT#7 then S/D the unit for standby. |  | 1 | 16:52 | Afternoon | Monday | 2017 | 3
5345 | 2017-03-20 19:25 | 2017-03-20 19:25 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 18 | 19:25 It was reported that b/o fuse for Tx at Well Benar #07. 20:45 Checked & found, @1 b/o 8K fuse for 150 Kva Tx at Well Benar #7. Tested the Tx & found normal ( good reading). Replaced b/o fuse above with the same size & energized the Tx. Cause: Animal (Monkey). |  | 1 | 19:25 | Night | Monday | 2017 | 3
5346 | 2017-03-20 20:48 | 2017-03-20 20:48 | 13.8KV DURI FIELD FEEDER #3 | Cloudy | Unidentified | 78 | 20:48 Duri Field VCB #52 (Duri Field fdr #3) T/LO. 21:30 Duri field RTU failed. 21:52 Checked and found, Duri Field VCB fdr #3 T/LO Counter: 352-360 R/F: 51 @1,2,3. Patrolled the line but found nothing. 22:16 Blocked and closed Duri Field VCB fdr #3 --> Success , and then released the block. 22:17 Duri Field SWGR RTU on line. Cause: Unidentified. |  | 1 | 20:48 | Night | Monday | 2017 | 3
5347 | 2017-03-21 14:56 | 2017-03-21 14:56 | MINAS POWER PLANT |  |  | - | 14:56 S/U MGT#5 then online the unit at 15:07. For running after Calibration PSV. |  | 1 | 14:56 | Afternoon | Tuesday | 2017 | 3
5348 | 2017-03-21 15:40 | 2017-03-21 15:40 | MINAS POWER PLANT |  |  | - | 15:40 Offline MGT#4 then S/D the unit for S/B. |  | 1 | 15:40 | Afternoon | Tuesday | 2017 | 3
5349 | 2017-03-22 23:59 | 2017-03-22 23:59 | CPI POWER SYSTEM |  |  | - | Normal System Condition. |  | 1 | 23:59 | Night | Wednesday | 2017 | 3
5350 | 2017-03-23 10:10 | 2017-03-23 10:10 | MINAS POWER PLANT |  |  | - | 10:10 MGT # 4 S/U, and then Online at 10:23. ( Recover power do to MGT # 5 will be down ). |  | 1 | 10:10 | Morning | Thursday | 2017 | 3
5351 | 2017-03-23 10:42 | 2017-03-23 10:42 | MINAS POWER PLANT |  |  | - | 10: 42 MGT # 5 Off line and S/D ( To fix gas scrubber leakage). |  | 1 | 10:42 | Morning | Thursday | 2017 | 3
5352 | 2017-03-23 14:41 | 2017-03-23 14:41 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 0 | Ketigul fdr # 1 load drooped 22A (97-75A). Ketigul fdr # 2 load drooped 24A (178-154A). Ketigul fdr # 3 load drooped 7A (22-15A). Ketigul GFPC in Blocked position. Not checked yet |  | 1 | 14:41 | Afternoon | Thursday | 2017 | 3
5353 | 2017-03-23 14:41 | 2017-03-24 14:41 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 0 | Checked & found, Ketigul VCB fdr #1 T/R 1x ctr: 180-181 R/F: 51 Patrolled the line & found, @3 Flash over Dead-end Insulator o/p 32-AJ-01. Cause: Dead-end Insulator. |  | 1 | 14:41 | Afternoon | Thursday | 2017 | 3
5354 | 2017-03-23 15:08 | 2017-03-23 15:08 | 13.8KV NORTH DURI FEEDER #8 | Fair | Planned Maintenance | 1 | 15:08 Shut off 4 wells : 6K 22A, 6K 31A, 6K 31B, 6K 32A, (N.Duri fdr # 8 ). for Maintenance replaced broken LA O/P 10-K2-10. 16:12 Finished above job, then all wells back to Run (POP). Cause : Planned Maintenance. |  | 1 | 15:08 | Afternoon | Thursday | 2017 | 3
5355 | 2017-03-23 17:23 | 2017-03-23 17:23 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Unidentified | 0 | 17:23 Duri Comm. ACB 26 fdr # 3 T/R 1X. Not checked yet. |  | 1 | 17:23 | Afternoon | Thursday | 2017 | 3
5356 | 2017-03-23 17:23 | 2017-03-26 16:31 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Unidentified | 0 | Checked & found, Duri Community VCB FDR#3 T/R 1x, Ctr: 56-57, R/F: 51N. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 17:23 | Afternoon | Thursday | 2017 | 3
5357 | 2017-03-23 17:41 | 2017-03-23 17:41 | 13.8KV RANGAU FEEDER #2 | Heavy Rain | Unidentified | 49 | 17:41 Rangau OCB fdr # 2 load drooped 153A ( 168 - 15A ). 19:28 Rangau OCB fdr # 2 load drooped 153A ( 168 - 15A ). Not checked yet. |  | 1 | 17:41 | Afternoon | Thursday | 2017 | 3
5358 | 2017-03-23 17:41 | 2017-03-26 16:31 | 13.8KV RANGAU FEEDER #2 | Heavy Rain | Unidentified | 49 | Checked & found, Recl. 23-BD-01 T/R 1x Ctr: 190-192 R/F: N.A. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 17:41 | Afternoon | Thursday | 2017 | 3
5359 | 2017-03-23 18:21 | 2017-03-23 18:21 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Lightning Arrester | 0 | 18:21 C.Duri ACB fdr # 7 T/LO Ctr : 473-476 R/F:... 18:43 Manually closed C.Duri ACB fdr # 7,ok. Not patrolled yet. |  | 1 | 18:21 | Afternoon | Thursday | 2017 | 3
5360 | 2017-03-23 18:21 | 2017-03-28 16:24 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Lightning Arrester | 0 | Checked & found, C. Duri ACB fdr#3 T/R 4x Ctr: 473-477 R/F: 51N @1. Patrolled the Line & found, @1 broken Pin Insulator o/p 03-05-25. Cause : Lightning Arrester |  | 1 | 18:21 | Afternoon | Thursday | 2017 | 3
5361 | 2017-03-23 18:30 | 2017-03-23 18:30 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Transformer leakage | 89 | 18:30 N.Duri fdr#8 Load dropped 121A (136-15A). 21:29 Checked & found, Recl. 10-K2-02 T/LO Ctr:119-123. Opened LBS 10-K3-03. 23:00 Blocked & closed Recl. 10-K2-02. Patrolled the line but found nothing. Opened Recl. 10-L1-17. Opened LBS 10-L1A-02. 24-Mar-2017. 00:05 Closed LBS 10-K3-03. 00:45 Patrolled the line D/S LBS 10-L1A-02, found 1000Kva Tx leaks at Are10 SC-AWT . 25-Mar-2017. 09:00 Opened LBS 10-L1A-02 and Opened the Fuse to perform TTR & Megger 1000KVATX, and Fixed the leakage at Transformer Bushing. 10:30 Closed LBS 10-L1A-02 and Closed the Fuse, then Energized the TX, OK. Cause : Transformer Leakage. |  | 1 | 18:30 | Afternoon | Thursday | 2017 | 3
5362 | 2017-03-24 01:26 | 2017-03-24 01:26 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Broken Fuse Holder | 55 | 01:26 It was reported B/O fuse for Tx at well So. Menggala#09 (Menggala fdr#1). 10:00 Checked and found, @2, @3 B/O fuse for 225 KVA TX. also found @2, @3 broken fuse holder. Replaced B/O Fuse and the holder above with the same size then energize the TX. Cause: Broken Fuse Holder. |  | 1 | 1:26 | Night | Friday | 2017 | 3
5363 | 2017-03-24 01:50 | 2017-03-24 01:50 | 115KV KOTABATAK - PETAPAHAN LINE | Rain and Lightning | Lightning | 375 | 01:50 115Kv Line CKBS-Petapahan GCB#1 T/R 1x. 19:25 Checked & found 115Kv Line CKBS GCB#1 T/R 1x Ctr:37-38 R/F:64@3. Patrolled the line but found nothing. Cause : Lightning. | 123 | 1 | 1:50 | Night | Friday | 2017 | 3
5364 | 2017-03-24 05:00 | 2017-03-24 05:00 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Low mega-ohm reading | 66 | 05:00 It was reported B/O fuse at well Pematang Bow#09 (So.Bekasap fdr#1). 10:10 Checked and found, @1,@2 B/O Fuse for 150 KVA TX. Performed TTR and megger Test, found low Mega-ohm reading, (will be replaced soon). Cause : Low Mega-ohm Reading Tx. |  | 1 | 5:00 | Morning | Friday | 2017 | 3
5365 | 2017-03-24 05:00 | 2017-03-26 15:45 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Low mega-ohm reading | 66 | Replaced Failure 150KVA TX with the same size at Well Pematang bow#29 then energized the TX. Cause: Low Mega-ohm Reading Tx. |  | 1 | 5:00 | Morning | Friday | 2017 | 3
5366 | 2017-03-24 07:53 | 2017-03-24 07:53 | 13.8KV KETIGUL FEEDER#2 | Rain | Unidentified | 56 | Ketigul VCB fdr # 2 T/R 1X. Not cheked yet. |  | 1 | 7:53 | Morning | Friday | 2017 | 3
5367 | 2017-03-24 07:53 | 2017-03-27 15:37 | 13.8KV KETIGUL FEEDER#2 | Rain | Unidentified | 56 | Checked & found Ketigul VCB fdr#2 T/R 1x, Ctr: 228-229, R/F: 51N. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 7:53 | Morning | Friday | 2017 | 3
5368 | 2017-03-24 12:26 | 2017-03-24 12:26 | 13.8KV CENTRAL DURI FEEDER #12 | Fair | Unidentified | 0 | C.Duri VCB fdr # 12 T/R 1X. Ctr : 436 - 437, R/F : 51N, @1. Not patrolled yet. |  | 1 | 12:26 | Afternoon | Friday | 2017 | 3
5369 | 2017-03-24 12:26 | 2017-03-28 16:25 | 13.8KV CENTRAL DURI FEEDER #12 | Fair | Unidentified | 0 | Checked & found, C. Duri ACB fdr#12 T/R 1x, Ctr: 486-487, R/F 51N. Patrolled the Line but found nothing. Cause : Unidentified |  | 1 | 12:26 | Afternoon | Friday | 2017 | 3
5370 | 2017-03-24 14:26 | 2017-03-24 14:26 | 13.8KV NORTH DURI FEEDER #2 | Fair | Recloser | 58 | 14:26 It was reported unbalance voltage o/p 10-J6-09 (N.Duri fdr # 2). 16:30 Checked and found, Unbalance voltage for 112.5 Kva Tx (secondary side @1; 482V, @2: 0V, @3: 490V) ( will be continued tomorrow ). 25-MAR-2017. 10:30 Patrolled the Line & found suspected Recl. 10-J6-18 was failure (After measured Sec. Voltage of Transformer at upstream the Recl.) By passed the Recloser above. Measured the 112.5 Kva Tx Voltage at secondary side @1; 486V, @2: 487V, @3: 490V. Cause: Recloser (Failure). |  | 1 | 14:26 | Afternoon | Friday | 2017 | 3
5371 | 2017-03-25 04:34 | 2017-03-25 04:34 | 13.8KV NELLA FEEDER #1 | Fair | Low mega-ohm reading | 67 | 04:34 It was reported b/o for Tx at well BKO #97. 06:15 Checked & found, @1, @2 b/o fuse for 300KVA Tx. Performed TTR & Megger Test, found low Mega-ohm reading Tx. 11:05 Replaced failure transformer above with the same size then energized the Tx. Cause: Low Mega-ohm reading Tx. |  | 1 | 4:34 | Morning | Saturday | 2017 | 3
5372 | 2017-03-25 09:45 | 2017-03-25 09:45 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Transformer Failure | 123 | 09:45 It was reported B/O fuse o/p 04 02 04.( C.Duri fdr # 9 ). 15:30 Checked and found, @2, @3 B/O fuse for 112.5 Kva Tx. Performed TTR & Megger Test, found low Mega-ohm reading. Cause : Low Megger Reading Tx. |  | 1 | 9:45 | Morning | Saturday | 2017 | 3
5373 | 2017-03-25 09:45 | 2017-03-31 16:37 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Transformer Failure | 123 | Replaced 112.5 Kva Tx failure with the same size & energized the Tx 0n pole 04-02-04. Cause: Tx Failure. (Low megger reading). |  | 1 | 9:45 | Morning | Saturday | 2017 | 3
5374 | 2017-03-26 23:14 | 2017-03-26 23:14 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Unidentified | 0 | 44KV NORTH DURI - DUMAI LINE GCB#1 T/R 1X. Not checked yet. |  | 1 | 23:14 | Night | Sunday | 2017 | 3
5375 | 2017-03-26 23:14 | 2017-03-28 14:23 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Unidentified | 0 | Checked & found 44KV North Duri GCB#44T/R 1x, Ctr: 110-111, R/F: 50N. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 23:14 | Night | Sunday | 2017 | 3
5376 | 2017-03-27 03:37 | 2017-03-27 03:37 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Broken Fuse Cut Out | 0 | 8C OCB fdr#4 T/R 1x. Not checked yet. |  | 1 | 3:37 | Night | Monday | 2017 | 3
5377 | 2017-03-27 03:37 | 2017-03-29 08:25 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Broken Fuse Cut Out | 0 | Checked and found, 8C VCB fdr #4 T/R 1x Counter: 589-590 R/F: 51 @2. Patrolled the line & found, broken Fuse Cut Out at Well 9C-49A. Cause: Broken Fuse Cut Out. |  | 1 | 3:37 | Night | Monday | 2017 | 3
5378 | 2017-03-27 03:37 | 2017-03-27 03:37 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Unidentified | 78 | 8D fdr#1 Load dropped 108A (134-26A). 8D fdr#3 Load dropped 40A (59-19A). 8D fdr#4 Load dropped 48A (173-125A). Not checked yet. |  | 1 | 3:37 | Night | Monday | 2017 | 3
5379 | 2017-03-27 03:37 | 2017-03-29 08:43 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Unidentified | 78 | Checked and found, Recl. 8F-05 did not Operated. Counter:71-71 (D/S 8D fdr #1). Cause: Unidentified. |  | 1 | 3:37 | Night | Monday | 2017 | 3
5380 | 2017-03-27 03:37 | 2017-03-27 03:37 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 32 | 8D OCB fdr#10 T/R 1x. Not checked yet. |  | 1 | 3:37 | Night | Monday | 2017 | 3
5381 | 2017-03-27 03:37 | 2017-03-29 08:45 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 32 | Checked and found, 8D OCB fdr #10 T/R 1x Counter: 246-247 R/F:50 @1,2,3. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 3:37 | Night | Monday | 2017 | 3
5382 | 2017-03-27 03:37 | 2017-03-27 03:37 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning Arrester | 65 | 8D OCB fdr#11 T/R 1x. 8D fdr#9 Load dropped 177A (177-0A). Not checked yet. |  | 1 | 3:37 | Night | Monday | 2017 | 3
5383 | 2017-03-27 03:37 | 2017-03-29 16:16 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning Arrester | 65 | Checked and found, 8D VCB fdr #11 T/R 1x Counter: 909-910 R/F: 51N. Patrolled the line & found, @1 broken Lightning Arrester on pole 8D-134. Cause: Broken Lightning Arrester. |  | 1 | 3:37 | Night | Monday | 2017 | 3
5384 | 2017-03-27 04:06 | 2017-03-27 04:06 | 13.8KV 8C FEEDER #5 | Rain and Lightning | Lightning Arrester | 0 | 8C OCB fdr#5 T/R 1x. Not checked yet. |  | 1 | 4:06 | Morning | Monday | 2017 | 3
5385 | 2017-03-27 04:06 | 2017-03-29 08:33 | 13.8KV 8C FEEDER #5 | Rain and Lightning | Lightning Arrester | 0 | Checked and found, 8C VCB fdr #5 T/R 1x Counter:99-100 R/F: 51N. Patrolled the line & found, @3 broken Lightning Arrester on pole LBS 8D-247. Cause: Broken Lightning Arrester. |  | 1 | 4:06 | Morning | Monday | 2017 | 3
5386 | 2017-03-27 04:06 | 2017-03-27 04:06 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 47 | 8C OCB fdr#6 T/R 1x. Not checked yet. |  | 1 | 4:06 | Morning | Monday | 2017 | 3
5387 | 2017-03-27 04:06 | 2017-03-29 08:39 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 47 | Checked and found, 8C VCB fdr #6 T/R 1x Counter: 272-273 R/F: 50 @2. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 4:06 | Morning | Monday | 2017 | 3
5388 | 2017-03-27 06:00 | 2017-03-27 06:00 | CENTRAL DURI POWER PLANT |  |  | - | 06:00 Offline CGT#3, then S/D the unit for maintenance. 06:04 Close Tie breaker ACB#39. |  | 1 | 6:00 | Morning | Monday | 2017 | 3
5389 | 2017-03-27 06:48 | 2017-03-27 06:48 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 92 | 06:48 13.8KV Sintong VCB fdr #2 T/R 1X. 10:30 Checked and found, Sintong VCB Feeder 2 T/R 1X ctr:454-455 R/F: 51N. And also found Sintong GFPC T/R 2X ctr: 952-954 R/F: 51N Patrolled the line but found nothing. Cause: Lightning. | 11111 | 1 | 6:48 | Morning | Monday | 2017 | 3
5390 | 2017-03-27 09:26 | 2017-03-27 09:26 | 13.8KV NELLA FEEDER #2 | Fair | Planned Maintenance | 2 | 09:26 Manually open fuse for 300KVA TX at well BKO #250 for replace FCO. 10:26 Energized the TX. Cause: Planned maintenance. | 1111 | 1 | 9:26 | Morning | Monday | 2017 | 3
5391 | 2017-03-27 14:22 | 2017-03-27 14:22 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning Arrester | 0 | 14:22 Batang 13.8KV OCB fdr #2 T/R 2X. 14:36 Batang 13.8KV OCB fdr #2 T/R 1X. Not checked yet. | 11111 | 1 | 14:22 | Afternoon | Monday | 2017 | 3
5392 | 2017-03-27 14:22 | 2017-03-31 17:54 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning Arrester | 0 | Checked and found Batang OCB fdr #2 T/R 3x Counter: 138-141 R/F: 51@1 and 51N. Patrolled the line found @1 Broken Lightning Arrester on pole 38-AI-07. Patrolled the line found @3 Broken Pin Insulator at Loc: Rantau Bais #17. Cause: Broken LA and Pin Insulator. | 11111 | 1 | 14:22 | Afternoon | Monday | 2017 | 3
5393 | 2017-03-27 17:20 | 2017-03-27 17:20 | CENTRAL DURI POWER PLANT |  |  | - | 17:20 CGT #3 S/U and On line to the system at 17:35 for running test after repair. |  | 1 | 17:20 | Afternoon | Monday | 2017 | 3
5394 | 2017-03-27 18:21 | 2017-03-27 18:21 | 13.8KV NELLA FEEDER #2 | Cloudy | Lightning | 39 | 18:21 13.8KV Nella VCB fdr #2 T/R 1X. Nella GFPC T/R 1X. Not checked yet. | 11111 | 1 | 18:21 | Afternoon | Monday | 2017 | 3
5395 | 2017-03-28 01:00 | 2017-03-28 01:00 | 13.8KV BATANG FEEDER #3 | Fair | Tree | 41 | Batang VCB fdr#3 T/R. 1x. Not checked yet. |  | 1 | 1:00 | Night | Tuesday | 2017 | 3
5396 | 2017-03-28 01:00 | 2017-03-31 17:58 | 13.8KV BATANG FEEDER #3 | Fair | Tree | 41 | Checked and found Batang OCB fdr #3 T/R 1x Counter: 342-343 R/F: 51 @1,2,3. Patrolled the line found high trees on pole 36-AI-27. Cause: Tree. |  | 1 | 1:00 | Night | Tuesday | 2017 | 3
5397 | 2017-03-28 14:14 | 2017-03-28 14:14 | 13.8KV SINTONG FEEDER #2 | Heavy Rain | Lightning | 0 | 14:14 Sintong fdr #2 load dropped 81A (172-91A). Ground fault alarm from Sintong fdr #2. Not checked yet. | 11111 | 1 | 14:14 | Afternoon | Tuesday | 2017 | 3
5398 | 2017-03-28 14:14 | 2017-03-29 15:05 | 13.8KV SINTONG FEEDER #2 | Heavy Rain | Lightning | 0 | Checked and found, Recl. 28-AF-02 T/R 1x Counter: 636-637 R/F: 50 @1,3. Patrolled the line found nothing. Cause: Suspected by Lightning | 11111 | 1 | 14:14 | Afternoon | Tuesday | 2017 | 3
5399 | 2017-03-28 15:55 | 2017-03-28 15:55 | 13.8KV DURI FIELD FEEDER #3 | Fair | Transformer Failure | 14 | 15:55 It was reported b/o fuses for Tx o/p 01-07-21. Checked and found @1 b/o fuse for 112.5 Kva Tx. Perform TTR and Megger found Low megger reading. Cause: Tx failure (Low megger reading) This Tx is not replaced yet. | 11111 | 1 | 15:55 | Afternoon | Tuesday | 2017 | 3
5400 | 2017-03-28 15:55 | 2017-03-31 08:24 | 13.8KV DURI FIELD FEEDER #3 | Fair | Transformer Failure | 14 | Replaced 112.5 Kva Tx failure with the same size & energized the Tx 0n pole 01-07-21. Cause: Tx Failure. (Low megger reading). | 11111 | 1 | 15:55 | Afternoon | Tuesday | 2017 | 3
5401 | 2017-03-29 10:57 | 2017-03-29 10:57 | 13.8KV 3D FEEDER #4 | Cloudy | Lightning | 65 | 10:57 3D fdr #4 load dropped 119A (178-59A). 16:22 Checked and found Recl. 2D-33 T/SO ctr:36-37. Patrolled the line, but found nothing. 16:35 Blocked and closed Recl. 2D-33, Ok then released the block. Cause: Lightning (suspected). | 1111 | 1 | 10:57 | Morning | Wednesday | 2017 | 3
5402 | 2017-03-29 13:43 | 2017-03-29 13:43 | MINAS POWER PLANT |  |  | - | 13:43 MGT #7 S/U and then on line to the system at 14:05 to restore load during CGT #1 down. |  | 1 | 13:43 | Afternoon | Wednesday | 2017 | 3
5403 | 2017-03-29 15:16 | 2017-03-29 15:16 | CENTRAL DURI POWER PLANT |  |  | - | 15:16 CGT #1 Off line and then S/D to rack down Guelutine blade. (HRSG #1 Re certification). |  | 1 | 15:16 | Afternoon | Wednesday | 2017 | 3
5404 | 2017-03-29 16:44 | 2017-03-29 16:44 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 26 | 16:44 So. Bekasap fdr #1 load dropped 103A (128-25A). Not checked yet. | 11111 | 1 | 16:44 | Afternoon | Wednesday | 2017 | 3
5405 | 2017-03-29 16:44 | 2017-03-04 16:44 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 26 | Checked & found, Recl. 36BI-04 T/R 1x ctr: 742-743 Patrolled the line & found, @1 broken Fuse Cut Out at Well Pudu #03. @2 broken Pin Insulator o/p 35BL-05. @1 broken Pin Insulator o/p 34BJ-12. Cause: Lightning. | 11111 | 1 | 16:44 | Afternoon | Wednesday | 2017 | 3
5406 | 2017-03-29 17:17 | 2017-03-29 17:17 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Unidentified | 0 | Pematang fdr #1 load dropped 85A (140-55A). Not checked yet. |  | 1 | 17:17 | Afternoon | Wednesday | 2017 | 3
5407 | 2017-03-29 17:17 | 2017-03-04 16:29 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked & found, no Breaker & reclosers were operated. Patrolled the line & found nothing. Cause: Unidentified. |  | 1 | 17:17 | Afternoon | Wednesday | 2017 | 3
5408 | 2017-03-29 17:30 | 2017-03-29 17:30 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Tree | 29 | 17:30 Petani OCB fdr #2 T/R 1x. 17:32 Petani OCB fdr #2 T/R again. Not checked yet. |  | 1 | 17:30 | Afternoon | Wednesday | 2017 | 3
5409 | 2017-03-29 17:30 | 2017-02-04 15:29 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Tree | 29 | Checked and found Petani OCB fdr #2 T/R 2x Counter: 217-219 R/F: 50 @1,2,3. Patrolled the line found tree near Petani Substation. Cause: Tree. |  | 1 | 17:30 | Afternoon | Wednesday | 2017 | 3
5410 | 2017-03-29 17:49 | 2017-03-29 17:49 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Recloser - Control Recloser | 0 | N.Duri fdr#8 Load dropped 115A (135-20A). Not checked yet. |  | 1 | 17:49 | Afternoon | Wednesday | 2017 | 3
5411 | 2017-03-29 17:49 | 2017-03-31 17:56 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Recloser - Control Recloser | 0 | 17:56 Checked anf found Recl. 10-K2-02 T/R 1X ctr: 128-129 (d/s N. Duri fdr #8) Patrolled the line and nothing found. Cause:Suspected Control Recloser. |  | 1 | 17:49 | Afternoon | Wednesday | 2017 | 3
5412 | 2017-03-29 18:29 | 2017-03-29 18:29 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 229 | 18:29 Ketigul fdr #2 load dropped 70A (171-101A). 21:52 It was reported No Power at Field UBI (18 Wells were Off). March 30. 2017 00:30 Checked & found Recl. 26-AK-02 T/O, Ctr: 187-189, R/F: N.A. Blocked & Close the Recloser, but fail. (After trouble shoot the Recloser Problem). 01:40 Blocked & Closed the Recloser. OK. (After trouble shoot & reset the Recloser Control). Patrolled the Line, but found nothing. Cause: Lightening. | 11111 | 1 | 18:29 | Afternoon | Wednesday | 2017 | 3
5413 | 2017-03-29 21:10 | 2017-03-29 21:10 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified (Fuse) | 103 | 21:10 It was reported B/O fuse at well Kopar#38 (Rokan fdr#2). 22:10 Checked & found, @1 @2 b/o fuse for 150 KVATX. Replaced the fuse with the same size, then energized the TX. Cause: Unidentified (Fuse). |  | 1 | 21:10 | Night | Wednesday | 2017 | 3
5414 | 2017-03-29 21:30 | 2017-03-29 21:30 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy | Transformer Failure | 264 | 21:30 It was reported B/O fuse at well Ampuh#23 (So Bekasap fdr#1). 00:20 Checked & found @1@3 b/o fuse for 100KVATX. Tested TTR & Megger, but found Low reading. Cause: TX Low Megger reading. |  | 1 | 21:30 | Night | Wednesday | 2017 | 3
5415 | 2017-03-29 21:30 | 2017-03-31 16:00 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy | Transformer Failure | 264 | Replaced B/O 100Kva Tx with the same size at well Ampuh#23 (So Bekasap fdr#1). Cause: Transformer Failure. |  | 1 | 21:30 | Night | Wednesday | 2017 | 3
5416 | 2017-03-31 01:25 | 2017-03-31 01:25 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 0 | 01:25 It was reported B/O fuse for Tx at well Petani #110 (Petani fdr#1). 02:25 Checked & found, @2 b/o fuse for 300KVATX. Replaced the fuse with the same size, then energized the TX. Cause: Unidentified. |  | 1 | 1:25 | Night | Friday | 2017 | 3
5417 | 2017-03-31 06:01 | 2017-03-31 06:01 | 13.8KV 8D FEEDER #8 | Rain | Lightning | 36 | 8D VCB fdr#8 T/R 1x. Not checked yet. |  | 1 | 6:01 | Morning | Friday | 2017 | 3
5418 | 2017-03-31 06:01 | 2017-03-04 20:32 | 13.8KV 8D FEEDER #8 | Rain | Lightning | 36 | Checked and found 8D VCB fdr#8 T/R 1x Counter : 244 - 245 R/F: 51N . Patrolled the line found nothing. Cause: Suspected Lightning. |  | 1 | 6:01 | Morning | Friday | 2017 | 3
5419 | 2017-03-31 10:02 | 2017-03-31 10:02 | 13.8KV DURI FIELD FEEDER #2 | Drizzle | Unidentified | 340 | 10:02 Duri field VCB #42 (Duri field fdr #2) T/LO. 11:26 Checked and found, Duri field fdr #2 T/LO ctr:989-993 R/F: 51 @1, @2 & @3. Patrolled the line but found nothing. 11:35 Blocked and closed Duri field fdr #2, OK then released the blocked. Cause: Unidentified. |  | 1 | 10:02 | Morning | Friday | 2017 | 3
5420 | 2017-03-31 11:11 | 2017-03-31 11:11 | 44KV PEMATANG MAIN - PETANI LINE | Cloudy | Suspension Insulator | 0 | Pematang Main 44KV OCB #1 T/R 1X. Not checked yet. | 11111 | 1 | 11:11 | Morning | Friday | 2017 | 3
5421 | 2017-03-31 11:11 | 2017-02-04 15:23 | 44KV PEMATANG MAIN - PETANI LINE | Cloudy | Suspension Insulator | 0 | Checked and found Pematang Main 44KV OCB #1 T/R 1x R/F: 50N Counter: 4000-4001. Patrolled the line found @2 flash over suspension insulator at Loc Petani #06. Cause: Suspension insulator. | 11111 | 1 | 11:11 | Morning | Friday | 2017 | 3
5422 | 2017-03-31 11:11 | 2017-03-31 11:11 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | Rangau fdr #2 load dropped 86A (165-79A). Not checked yet. | 11111 | 1 | 11:11 | Morning | Friday | 2017 | 3
5423 | 2017-03-31 11:11 | 2017-03-04 11:11 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | Checked & found no Breaker & Reclosers were operated. Patrolled the line & found nothing. Cause : Unidentified Date Patrol : 03-APR-2017 | 11111 | 1 | 11:11 | Morning | Friday | 2017 | 3
5424 | 2017-03-31 12:09 | 2017-03-31 12:09 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | 12:09 It was reported b/o fuse for Tx at well Rantau Bais #57 (D/S Batang fdr #2). 13:45 Checked & found, @1,@2 b/o fuse for 150 Kva Tx. Tested the Tx & found normal ( good reading). Replaced B/O fuse above with the same size & energized the Tx. Cause: Animal (Monkey). |  | 1 | 12:09 | Afternoon | Friday | 2017 | 3
5425 | 2017-03-31 08:02 | 2017-03-31 08:02 | 13.8KV MINAS FEEDER #5 | Fair | Dead End Insulator | 3 | 08:02 Minas ACB #17 (Minas fdr #5) T/O (In block position due to PT Rifansi Job). 08:04 Checked and found Minas ACB fdr #5 T/O Ctr: 88-89 R/F: 51N, 51G 08:36 Blocked and closed Minas ACB fdr #5 Succes (Still in block due to PT Rifansi Job). Not patrolled yet. | 11111 | 1 | 8:02 | Morning | Friday | 2017 | 3
5426 | 2017-03-31 08:02 | 2017-03-04 20:42 | 13.8KV MINAS FEEDER #5 | Fair | Dead End Insulator | 3 | Patrolled the line found @1,2,3 Flash over dead end insulator on pole 7E-156. Cause: Dead end insulator. | 11111 | 1 | 8:02 | Morning | Friday | 2017 | 3
5427 | 2017-03-31 12:07 | 2017-03-31 12:07 | 13.8KV MENGGALA FEEDER #1 | Fair | Theft | 0 | It was reported any Vandalism at well North Menggala#20 (Menggala fdr#1). Checked & found M/O Fuses for 300KVATX. Cause: Theft. |  | 1 | 12:07 | Afternoon | Friday | 2017 | 3
5428 | 2017-03-31 16:00 | 2017-03-31 16:00 | MINAS POWER PLANT |  |  | - | 16:00 MGT #1 S/U and then On Line to the system at 16:25 for running test. | 1111 | 1 | 16:00 | Afternoon | Friday | 2017 | 3
5429 | 2017-01-04 15:38 | 2017-01-04 15:38 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Pin Insulator | 0 | Duri Commuity ACB fdr#1 T/R 1x. Not checked yet. |  | 1 | 15:38 | Afternoon | Wednesday | 2017 | 1
5430 | 2017-01-04 15:38 | 2017-04-04 16:33 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Pin Insulator | 0 | Checked & found, Duri Community VCB fdr #1 T/R 1x ctr: 96-97 R/F: 51N. Patrolled the line & found, @3 broken Pin Support Insulator on Pole KT-39. @3 broken Dead-end Insulator on Pole KT-45. Cause: Pin Insulator. |  | 1 | 15:38 | Afternoon | Wednesday | 2017 | 1
5431 | 2017-02-04 07:19 | 2017-02-04 07:19 | 13.8KV KETIGUL FEEDER#2 | Drizzle | Animal | 75 | Ketigul VCB fdr#2 T/R 1x. Not checked yet. | 11111 | 1 | 7:19 | Morning | Saturday | 2017 | 2
5432 | 2017-02-04 07:19 | 2017-04-04 07:19 | 13.8KV KETIGUL FEEDER#2 | Drizzle | Animal | 75 | Checked & found, Ketigul VCB fdr #2 T/R 1x ctr: 229-230 R/F: 51N. Patrolled the line & found a death monkey around pole at well Pager #43. Cause: Animal (Monkey). | 11111 | 1 | 7:19 | Morning | Saturday | 2017 | 2
5433 | 2017-02-04 08:45 | 2017-02-04 08:45 | MINAS POWER PLANT |  |  | - | 08:45 MGT #2 was S/U and On Line to the system at 09:25 to restore the load. (NDC CT #1 will be down for Off Line Wash). |  | 1 | 8:45 | Morning | Saturday | 2017 | 2
5434 | 2017-02-04 09:30 | 2017-02-04 09:30 | 13.8KV SINTONG FEEDER #2 | Fair | Tree | 89 | Sintong OCB fdr#2 T/R 1x. Sintong fdr #1 load dropped 75A (98-23A). Not checked yet. | 11111 | 1 | 9:30 | Morning | Saturday | 2017 | 2
5435 | 2017-02-04 09:30 | 2017-05-04 07:50 | 13.8KV SINTONG FEEDER #2 | Fair | Tree | 89 | Checked & found Sintong VCB fdr#2 T/R 1x Ctr:455-456 R/F:51N. Patrolleed the line & found Danger trees near Terminal pole Sintong#18. Cause : Tree. | 11111 | 1 | 9:30 | Morning | Saturday | 2017 | 2
5436 | 2017-02-04 09:45 | 2017-02-04 09:45 | MINAS POWER PLANT |  |  | - | 09:45 MGT #2 was S/U and On Line to the system at 09:56 to restore the load. (NDC CT #1 will be down for Off Line Wash). |  | 1 | 9:45 | Morning | Saturday | 2017 | 2
5437 | 2017-02-04 15:04 | 2017-02-04 15:04 | CENTRAL DURI POWER PLANT |  |  | - | 15:04 CGT #1 was S/U and On Line to the system at 15:23 to restore the load. (NDC CT #1 will be down for Off Line Wash). |  | 1 | 15:04 | Afternoon | Saturday | 2017 | 2
5438 | 2017-02-04 19:07 | 2017-02-04 19:07 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 971 | April,02,2017 NDC CT #1 Offline Wash. 10:00 Manually load shedding at SLS - GS#6 S/D 6 Wells + 1 Unit WIP, Prod. Loss 49 Bbls. 19:07 NDC-CT #1 Off line, then S/D the Unit for Not S/B. (Prior to Offline washing program). April,03,2017. 07:41 Inform GS #6 to reduce load 10 MW. 15:21 Inform GS #6 to reload 5 MW. 18:25 S/U NDC#1 and then online the unit at 18:51. GS #4 Prod loss: 251 Bbls / 16 wells + 1 WIP (DB 41). GS #5 Prod loss: 82 Bbls / 16 wells + 1 WIP (DB 5.7). GS #6 Prod loss: 121 Bbls / 13 wells + 1 WIP (SB 6.8). --------------------------------------------------------------------- + Total Prod loss: 454 Bbls / 45 wells + 3 WIP. April,04,2017. GS #4 Prod loss: 278 Bbls / 16 wells + 1 WIP (DB 41). GS #5 Prod loss: 46 Bbls / 6 wells + 1 WIP (DB 5.7). GS #6 Prod loss: 30 Bbls / 5 wells + 1 WIP (SB 6.8). --------------------------------------------------------------------- + Total Prod loss: 354 Bbls / 27 wells + 3 WIP. Grand TOTAL: 49 Bbls / 6 Wells / 1 WIP -------->On April 02, 2017. 454 Bbls / 45 Wells / 3 WIP -------->On April 03, 2017. 354 Bbls / 27 Wells / 3 WIP -------->On April 04, 2017. ----------------------------------+ 857 Bbls / 78 Wells / 7 WIP Cause : Planned Maintenance (NDC-CT #1 Off line wash). | 11111 | 1 | 19:07 | Night | Saturday | 2017 | 2
5439 | 2017-03-04 08:51 | 2017-03-04 08:51 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 13 | 08:51 It was reported B/O fuse O/P 06 Q5 05 d/s C.Duri fdr #14. 10:30 Replace @1,@2 B/O fuse for 112.5 Kva Tx with the same size. Cause : Animal. |  | 1 | 8:51 | Morning | Saturday | 2017 | 3
5440 | 2017-03-04 16:43 | 2017-03-04 16:43 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Pin Insulator | 0 | SO.Bekasap fdr#1 load dropped 83 A (132-49A). Not checked yet. | 11111 | 1 | 16:43 | Afternoon | Saturday | 2017 | 3
5441 | 2017-03-04 16:43 | 2017-09-04 16:00 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Pin Insulator | 0 | Checked & found Recl. 38-BI-18 T/R 1x Ctr:158-159. Patrolled the line & found @1 Broken Pin Insulator O/P 31-BF-26. Cause : Pin Insulator. | 11111 | 1 | 16:43 | Afternoon | Saturday | 2017 | 3
5442 | 2017-03-04 17:49 | 2017-03-04 17:49 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | 17:49 Sintong fdr #2 load dropped 103A (184-81A). Ground fault alarm from Sintong fdr #2. Not checked yet. |  | 1 | 17:49 | Afternoon | Saturday | 2017 | 3
5443 | 2017-03-04 17:49 | 2017-05-04 17:49 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recl. 28AF-02 T/R 1x ctr: 637-638. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:49 | Afternoon | Saturday | 2017 | 3
5444 | 2017-03-04 18:25 | 2017-03-04 18:25 | NORTH DURI POWER PLANT |  |  | - | 18:25 S/U NDC#1 and then online the unit at 18:51. |  | 1 | 18:25 | Afternoon | Saturday | 2017 | 3
5445 | 2017-03-04 21:10 | 2017-03-04 21:10 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 31 | 21:10 It was reported b/o fuse at well Pagar #30. Not checked yet. |  | 1 | 21:10 | Night | Saturday | 2017 | 3
5446 | 2017-03-04 21:10 | 2017-04-04 11:12 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 31 | 11:12 Checked and found @2, @3 b/o fuse for 300KVA TX at well Pagar #30 d/o Ketigul fdr #2. Performed TTR and Megger found the TX Good. Replaced b/o fuse above with same size, then energized the TX. Cause: Animal (Monkey). |  | 1 | 21:10 | Night | Saturday | 2017 | 3
5447 | 2017-03-04 22:23 | 2017-03-04 22:23 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | 22:23 Off line and then S/D NDC CT #3 for Off Line Wash. 04 April 2017 --------------- 21:06 NDC CT #3 was S/U and Online to the system at 21:37. Cause: Planned Maintenance. (See 02-April 2017 at 19:07 for Prod. Loss) |  | 1 | 22:23 | Night | Saturday | 2017 | 3
5448 | 2017-03-04 22:40 | 2017-03-04 22:40 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 38 | 22:40 It was reported b/o fuse at well BKO #291 (Bangko fdr#1). Not checked yet. |  | 1 | 22:40 | Night | Saturday | 2017 | 3
5449 | 2017-03-04 22:40 | 2017-04-04 09:09 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 38 | 09:09 Checked and found @1,@2 b/o fuse at well BKO 291. Perform TTR and megger found good. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (Monkey). |  | 1 | 22:40 | Night | Saturday | 2017 | 3
5450 | 2017-04-04 10:17 | 2017-04-04 10:17 | 13.8KV ROKAN FEEDER #2 | Fair | Planned Maintenance | 76 | 10:17 Manually open Rokan VCB fdr #2. Due to replaced @3 broken pin insulator on pole .... 12:27 Blocked and closed Rokan VCB fdr #2 and released the block. Cause: Plan Maintenance. |  | 1 | 10:17 | Morning | Tuesday | 2017 | 4
5451 | 2017-04-04 19:01 | 2017-04-04 19:01 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Pin Insulator | 18 | Rokan 13.8KV VCB fdr #2 T/R 1X. Not checked yet. | 3353172 | 1 | 19:01 | Night | Tuesday | 2017 | 4
5452 | 2017-04-04 19:01 | 2017-09-04 16:01 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Pin Insulator | 18 | Checked & found Rokan VCB fdr#2 T/R 1x Ctr:1249-1250 R/F: 51N. Patrolled the line & found @1 Broken Pin Insulator o/p 02-08-05 at Rokan Substation. Cause : Pin Insulator. | 3353172 | 1 | 19:01 | Night | Tuesday | 2017 | 4
5453 | 2017-04-04 20:16 | 2017-04-04 20:16 | NORTH DURI POWER PLANT |  |  | - | 21:06 NDC CT #3 was S/U and On LIne to the system at 21:37. |  | 1 | 20:16 | Night | Tuesday | 2017 | 4
5454 | 2017-04-04 20:40 | 2017-04-04 20:40 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 31 | 3D OCB fdr #3 T/R 1x. Not checked yet. | 11111 | 1 | 20:40 | Night | Tuesday | 2017 | 4
5455 | 2017-04-04 20:40 | 2017-05-04 23:35 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 31 | Checked & found, 3D OCB fdr #3 T/R 1x ctr: 443-444 R/F: 51. Patrolled the line but found nothing. Cause: Suspected by Lightning. | 11111 | 1 | 20:40 | Night | Tuesday | 2017 | 4
5456 | 2017-05-04 03:17 | 2017-05-04 03:17 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | 03:17 NDC CT #2 off line and then S/D at 03:20 for Off Line Was JOB. 6-April-2017 --------------- 03:33 S/U NDC CT#2 and then online the unit at 04:11. Cause: Planned Maintenance. (See 02-April-17 at 19:07 for Prod. Loss) |  | 1 | 3:17 | Night | Thursday | 2017 | 5
5457 | 2017-05-04 13:00 | 2017-05-04 13:00 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified (Fuse) | 80 | 13:00 it was reported B/O Fuses at well Pelita #04 ( Rangau Fdr # 2 ). 16:30 Replace @1 Burn out fuses for 225 Kva whit the same size. Cause : Unidentified fuse. |  | 1 | 13:00 | Afternoon | Thursday | 2017 | 5
5458 | 2017-05-04 14:36 | 2017-05-04 14:36 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Powerline - Jumper | 0 | 14:36 it was reported no power at Arwana, Baung WH 125 ( CD FDR # 1 ). 14:45 Checked and found @3 broken jumper load side at Recl.40 BA 02. 14:52 Open Recl 40 BA 02 Repair @3 broken jumper load side at Recl 40 BA 02. 15:33 Block and closed Recl 40 BA 02, than release the block . Cause : Broken jumper. |  | 1 | 14:36 | Afternoon | Thursday | 2017 | 5
5459 | 2017-05-04 18:46 | 2017-05-04 18:46 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 33 | 18:46 3D fdr#4 load dropped 110 A (188-78A). 21:46 Checked & found, Recl. 2D-33 T/SO Ctr: 37-38. 21:49 Blocked & closed Recl. 2D-33, ok, then released the block. Cause: Not patrolled yet. |  | 1 | 18:46 | Afternoon | Thursday | 2017 | 5
5460 | 2017-05-04 18:46 | 2017-06-04 23:25 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 33 | Patrolled the line & found, @2 broken Pin Insulator on Pole 1D-06. Cause: Lightning. |  | 1 | 18:46 | Afternoon | Thursday | 2017 | 5
5461 | 2017-06-04 03:33 | 2017-06-04 03:33 | NORTH DURI POWER PLANT |  |  | - | 03:33 S/U NDC CT#2 and then online the unit at 04:11. |  | 1 | 3:33 | Night | Sunday | 2017 | 6
5462 | 2017-06-04 07:49 | 2017-06-04 07:49 | MINAS POWER PLANT |  |  | - | Off line MGT#5, then S/D the unit for S/B. |  | 1 | 7:49 | Morning | Sunday | 2017 | 6
5463 | 2017-06-04 08:42 | 2017-06-04 08:42 | MINAS POWER PLANT |  |  | - | Off line MGT#2, then S/D the unit for S/B. |  | 1 | 8:42 | Morning | Sunday | 2017 | 6
5464 | 2017-06-04 08:54 | 2017-06-04 08:54 | MINAS POWER PLANT |  |  | - | Off line MGT#1, then S/D the unit for S/B. |  | 1 | 8:54 | Morning | Sunday | 2017 | 6
5465 | 2017-06-04 09:23 | 2017-06-04 09:23 | 13.8KV DARLING VCB FEEDER #3 | Fair | Powerline - Hot Line Clamp | 0 | 09:23 Darling fdr#3 Load dropped 45A (240-195A). 10:00 Checked & found, @3 Broken FCO & HLC for 2500Kva Tx-A at CGS#5. Replaced @3 Broken FCO & HLC for 2500 Kva Tx-A at CGS#5. 12:00 Energized 2500Kva Tx-A at CGS#5. Cause: Broken FCO & HLC. |  | 1 | 9:23 | Morning | Sunday | 2017 | 6
5466 | 2017-06-04 09:25 | 2017-06-04 09:25 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT#1, then S/D the unit for S/B. |  | 1 | 9:25 | Morning | Sunday | 2017 | 6
5467 | 2017-06-04 14:51 | 2017-06-04 14:51 | 13.8KV PETANI FEEDER #2 | Fair | Planned Maintenance | 19 | 14:51 Blocked Petani VCB fdr#2. 15:00 Cut jumper o/p 32AW40 for replacing Pin Insulator on T/P Petani#48. (Petani#119 Shut off during the job). 16:15 Normarlized block Petani fdr#2 (Rain & lightning). (Continued job tomorrow). Cause: Planned Maintenance. |  | 1 | 14:51 | Afternoon | Sunday | 2017 | 6
5468 | 2017-06-04 16:03 | 2017-06-04 16:03 | 13.8KV CENTRAL DURI FEEDER #9 | Rain | Lightning Arrester | 379 | 16:03 C.Duri ACB fdr#9 T/LO Ctr:358-362 R/F:51N, 51@1. 16:36 Patrolled the line but found nothing. 17:06 Blocked & closed C. Duri ACB fdr#9, but failed. Patrolled the line & found, @1 Broken LA o/p 04-7-28. Isolated @1 Broken LA o/p 04-7-28. 17:30 Bloked & closed C.Duri ACB fdr#9, ok, then release the block. Cause: Broken LA. |  | 1 | 16:03 | Afternoon | Sunday | 2017 | 6
5469 | 2017-07-04 09:00 | 2017-07-04 09:00 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified (Fuse) | 22 | It was reported B/O fuse o/p 01-2-30 (C.Duri fdr#3). Replaced @1 B/O fuse for 112.5 Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 9:00 | Morning | Tuesday | 2017 | 7
5470 | 2017-07-04 10:40 | 2017-07-04 10:40 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 0 | 10:45 It was reported B/O fuse o/p 04-4-20(C.Duri fdr#8). 14:45 Replaced @1@3 B/O fuse for 112.5 Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 10:40 | Morning | Tuesday | 2017 | 7
5471 | 2017-07-04 15:15 | 2017-07-04 15:15 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse o/p 03-2-11 (C.Duri fdr#6). Replaced @1 B/O fuse for 112.5 Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 15:15 | Afternoon | Tuesday | 2017 | 7
5472 | 2017-07-04 23:21 | 2017-07-04 23:21 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 85 | 5B OCB fdr #3 T/R 1x. 5B fdr #6 load dropped 188A (191-3A) --> WIP. Not checked yet. |  | 1 | 23:21 | Night | Tuesday | 2017 | 7
5473 | 2017-07-04 23:21 | 2017-11-04 14:36 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 85 | Checked & found, 5B OCB fdr#3 T/R 1x, Ctr: 370-371, R/F: 51N @2. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 23:21 | Night | Tuesday | 2017 | 7
5474 | 2017-07-04 23:21 | 2017-07-04 23:21 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 60 | 5B fdr #1 load dropped 172A (181-9A). Not checked yet. |  | 1 | 23:21 | Night | Tuesday | 2017 | 7
5475 | 2017-07-04 23:21 | 2017-11-04 14:18 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 60 | Checked & found, 5B OCB fdr#1 T/R 1x, Ctr: 232-233, R/F: 51 @2. Patrolled the Line, found @2 Broken Dead end o/p 5B6-D60. Cause : Lightning |  | 1 | 23:21 | Night | Tuesday | 2017 | 7
5476 | 2017-07-04 23:21 | 2017-07-04 23:21 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 0 | 5B fdr #2 load dropped 147A (158-11A). Not checked yet. |  | 1 | 23:21 | Night | Tuesday | 2017 | 7
5477 | 2017-07-04 23:21 | 2017-11-04 15:17 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found 5B OCB fdr#2 Load dropped. Patrolled the line, Found @1 broken Dead end Soe Fiber Optic o/p 4C-59, and @1 broken Suspension for Fiber Optic o/p 5C-06. Cause : Lightning |  | 1 | 23:21 | Night | Tuesday | 2017 | 7
5478 | 2017-07-04 23:30 | 2017-07-04 23:30 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 0 | 23:30 5B fdr #4 load dropped 199A (221-22A). 04:40 Checked and found Recl. 4B-73 T/SO ctr:187-188. Blockec and closed the Recl. Ok, then released the block. Not Patrolled yet. |  | 1 | 23:30 | Night | Tuesday | 2017 | 7
5479 | 2017-07-04 23:30 | 2017-11-04 16:42 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 0 | Re patrolled the Line Under Recl. 4B-73, but found nothing. Cause : Lightning |  | 1 | 23:30 | Night | Tuesday | 2017 | 7
5480 | 2017-07-04 23:33 | 2017-07-04 23:33 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 6 | 3D fdr #3 load dropped 162A (164-2A). Not checked yet. GS#5 Prod loss: 12 Bbls / 14 wells. GS#6 Prod loss: ---------------------------------- + Total Prod loss : |  | 1 | 23:33 | Night | Tuesday | 2017 | 7
5481 | 2017-07-04 23:33 | 2017-09-04 14:00 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 6 | Checked & found 3D OCB fdr#3 T/R 1x, Ctr: 443-443 (not change), R/F: 51 @3. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 23:33 | Night | Tuesday | 2017 | 7
5482 | 2017-07-04 23:33 | 2017-07-04 23:33 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | 3D fdr #4 load dropped 59A (196-137A) Not checked yet. |  | 1 | 23:33 | Night | Tuesday | 2017 | 7
5483 | 2017-07-04 23:33 | 2017-09-04 14:00 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found Recl. 2D-14 T/R 1x, Ctr: 46-47, R/F: N.A. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 23:33 | Night | Tuesday | 2017 | 7
5484 | 2017-08-04 12:50 | 2017-08-04 12:50 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified (Fuse) | 42 | 12:50 It was reported b/o Fuse for Tx at well Pinang#33 (Pinang fdr#1). 15:00 Replaced @1 B/O Fuse for 300Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 12:50 | Afternoon | Friday | 2017 | 8
5485 | 2017-09-04 07:29 | 2017-09-04 07:29 | 13.8KV CENTRAL DURI FEEDER #6 | Cloudy | Unidentified | 0 | C Duri ACB #23 (C Duri fdr #6) T/R 1x. Not checked yet. |  | 1 | 7:29 | Morning | Monday | 2017 | 9
5486 | 2017-09-04 07:29 | 14/04/2017 07:29 | 13.8KV CENTRAL DURI FEEDER #6 | Cloudy | Unidentified | 0 | Checked & found, C. Duri ACB #23 fdr #6 T/R 1x ctr: 461-462 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:29 | Morning | Monday | 2017 | 9
5487 | 2017-09-04 10:50 | 2017-09-04 10:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse at well Puncak#33 (C.Duri fdr#1). Replaced @1@2 B/O fuse for 112.5 Kva Tx with the same size. (After RIG service) Cause: Unidentified Fuse. |  | 1 | 10:50 | Morning | Monday | 2017 | 9
5488 | 2017-10-04 08:54 | 2017-10-04 08:54 | 13.8KV MINAS FEEDER #5 | Fair | Lightning | 3 | Minas ACB#17 (Minas fdr#5) T/R 1x R/F: 51@A Counter: 89-90. Not patrolled yet. |  | 1 | 8:54 | Morning | Wednesday | 2017 | 10
5489 | 2017-10-04 08:54 | 2017-11-04 16:37 | 13.8KV MINAS FEEDER #5 | Fair | Lightning | 3 | Checked & found, Minas ACB fdr#5 T/R 1x, Ctr: 89-90, R/F: 51N @1. Patrolled the Line, found @1 broken Pin Insulator o/p 8D-79. Cause : Lightning |  | 1 | 8:54 | Morning | Wednesday | 2017 | 10
5490 | 2017-10-04 14:28 | 2017-10-04 14:28 | 230KV NORTH DURI SWITCH YARD | Fair | Relay Failure | 0 | 14:28 N.Duri 230 KV GCB #43 T/O Closed at 14:33. N.Duri 230 KV GCB #15 T/O Closed at 14:33. N.Duri 230 KV GCB #25 T/O Closed at 14:33. N.Duri 230 KV GCB #35 T/O Closed at 14:33. Those Breaker was T/O While MTC team perform Trouble Shooting Battery ground. Closed All breaker after Disabled Relay B30 due to broken Power supply Not checked yet. |  | 1 | 14:28 | Afternoon | Wednesday | 2017 | 10
5491 | 2017-10-04 14:28 | 2017-11-04 16:47 | 230KV NORTH DURI SWITCH YARD | Fair | Relay Failure | 0 | Checked & found - ND 230 GCB#15 T/O, Ctr: 142-143, R/F: 87 @1@2@3 - ND 230 GCB#25 T/O, Ctr: 201-202, R/F: 87 @1@2@3 - ND 230 GCB#35 T/O, Ctr: 281-282, R/F: 87 @1@2@3 - ND 230 GCB#43 T/O, Ctr: 193-194, R/F: 87 @1@2@3 Cause: Relay Failure (Broken power supply of Relay B30). |  | 1 | 14:28 | Afternoon | Wednesday | 2017 | 10
5492 | 2017-11-04 20:52 | 2017-11-04 20:52 | 13.8KV MENGGALA FEEDER #1 | Fair | Transformer Failure | 0 | 20:52 It was reported B/O Fuse at well So. menggala#12 (Menggala fdr#1 ). 23:40 Checked & found @1@2 B/O fuse for 500Kva Tx at So.Menggala#12. Checked TTR & Megger 500Kva Tx Failure. (Would be changed tomorrow). Cause: Tx Failure. |  | 1 | 20:52 | Night | Saturday | 2017 | 11
5493 | 2017-11-04 20:52 | 2017-12-04 11:30 | 13.8KV MENGGALA FEEDER #1 | Fair | Transformer Failure | 0 | Replaced B/O 500KVA with 300KVA at well So.Menggala#12. Cause: Transformer Failure. |  | 1 | 20:52 | Night | Saturday | 2017 | 11
5494 | 2017-12-04 01:59 | 2017-12-04 01:59 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified | 0 | Duri community 13.8Kv ACB#33 fdr#5 T/R 1X. Not checked yet. |  | 1 | 1:59 | Night | Monday | 2017 | 12
5495 | 2017-12-04 01:59 | 13/04/2017 17:58 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified | 0 | Checked & found D.Comm. fdr#5 T/R 1x, Ctr: 106-107, R/F: 51N, @3. Patrolled the Line, found Flash Over Dead end o/p SD-06. Cause : Unidentified |  | 1 | 1:59 | Night | Monday | 2017 | 12
5496 | 2017-12-04 05:19 | 2017-12-04 05:19 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 68 | Menggala VCB fdr#1 T/R 1X. Not checked yet. |  | 1 | 5:19 | Morning | Monday | 2017 | 12
5497 | 2017-12-04 10:15 | 2017-12-04 10:15 | 13.8KV 4B FEEDER #6 | Fair | Planned Maintenance | 56 | 10:15 Manually Opened 4B VCB fdr#6. Replaced broken Dead end Insulator o/p 4B-26. (GSS-6 Shut Off 18 Wells; LPO 76 Bbls). 11:38 Finished the job above, then all wells running back (POP). Cause: Planned Maintenance. |  | 1 | 10:15 | Morning | Monday | 2017 | 12
5498 | 2017-12-04 13:30 | 2017-12-04 13:30 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 5 | 13:30 Shut Off well Benar#01, to Cut jumper to isolate broken L/A. 14:40 L/A has been isolated, start on back the well above (POP).. Cause : planned maintenance. |  | 1 | 13:30 | Afternoon | Monday | 2017 | 12
5499 | 2017-12-04 15:43 | 2017-12-04 15:43 | 13.8KV CENTRAL DURI FEEDER #6 | Lightning | Animal | 542 | 15:43 C.Duri ACB fdr#6 T/O. ctr:462-466, R/f : 50 @2, 51G, 51N. 16:02 Man. Closed C.Duri fdr#6 but T/O again. ctr : 466-467. R/f : 50 @3, 51G,51N. 17:08 Man. Closed C.Duri fdr#6 but T/O again. ctr : 467-468. R/f : 50 @3,51G,51N. 17:58 Opened Recl. 02 01 01, Man.Closed C.Duri fdr#6 but T/O again. ctr : 468-469. R/f : 50 @3, 51G,51N. Closed LBS 04 07 01 ( C.Duri fdr#9 ).energize power to area #3,#4. 18:09 Open Recl. 01 03 01. Man.Closed C.Duri fdr#6 but T/O again. ctr : 469-470. R/f : 50 @3, 51G,51N. 19:30 Patrolled the line but found nothing. 20:40 Open LBS Riser pole at C.Duri. 20:42 Blocked & closed C.Duri fdr#6,ok, then open at 20:43. 20:45 Open LBD Riser pole at C.Duri. 22:00 Patrolled the line & Found @1 Dead Squirrel o/p 02-8-03A. Isolatted Dead Squirrel o/p 02-8-03A. 22:15 Blocked & closed C.Duri fdr#6, ok, then release the block. 22:24 Blocked & Closed Recl. 01-3-01, then release the block. Cause: Animal (Squirrel). | 1111 | 1 | 15:43 | Afternoon | Monday | 2017 | 12
5500 | 2017-12-04 15:50 | 2017-12-04 15:50 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 52 | Sintong ground fault fdr#2 T/R. Sintong fdr#2 load drooped 158A (200-42A). Cause : Not checked yet. |  | 1 | 15:50 | Afternoon | Monday | 2017 | 12
5501 | 2017-12-04 17:21 | 2017-12-04 17:21 | 13.8KV S. BALAM FEEDER #4 | Fair | Animal | 0 | 17:21 It was reported B/O fuse at well So.Blm #181 (Balam fdr#4). 18:00 Checked & found @2@3 B/O fuse for 300Kva Tx at well So.Balam#181. 21:30 Checked with Electricia & found Dead Lizard at Switchboard. Broken Scondary cable & Dismantle sec. cable. 22:00 Replaced @2@3 B/O fuse for 300 Kva Tx with the same size & Energized the Tx. (Would be replaced Sec.Cable tomorrow). Cause: Animal (Lizard). |  | 1 | 17:21 | Afternoon | Monday | 2017 | 12
5502 | 2017-04-13 19:22 | 2017-04-13 19:22 | 44KV NORTH DURI - DUMAI LINE | Rain | Lightning | 0 | N.Duri line 44Kv GCB#1 T/R 1x. Not checked yet. |  | 1 | 19:22 | Night | Thursday | 2017 | 4
5503 | 2017-04-13 19:22 | 2017-04-18 18:29 | 44KV NORTH DURI - DUMAI LINE | Rain | Lightning | 0 | Checked & found, 44KV N. Duri GCB #44 T/R 1x Ctr: 96-97 R/F: 51N. Patrolled the Line & found, @ 1 Flash Over Dead end Insulator o/p DD 233. Cause : Lightning |  | 1 | 19:22 | Night | Thursday | 2017 | 4
5504 | 2017-04-14 05:22 | 2017-04-14 05:22 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain | Unidentified | 0 | 4.16kV Dumai VCB fdr#4 T/R Not checked yet. |  | 1 | 5:22 | Morning | Friday | 2017 | 4
5505 | 2017-04-14 05:22 | 2017-04-17 05:22 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain | Unidentified | 0 | Checked & found, 4.16kV Dumai ACB #22 fdr #4 T/R 1x ctr: 266-267 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 5:22 | Morning | Friday | 2017 | 4
5506 | 2017-04-14 09:23 | 2017-04-14 09:23 | 13.8KV PETANI FEEDER #1 | Fair | Low mega-ohm reading | 52 | 09:23 It was reported B/O fuse at well Petani#16 (PTN fdr#1). 10:00 Checked & found, @1, @2 b/o fuse for 150KVA Tx. Performed TTR & Megger Test, found Low Mega-ohm Reading Tx. Cause: Low Mega-ohm reading Tx. (Will be replaced tomorrow). |  | 1 | 9:23 | Morning | Friday | 2017 | 4
5507 | 2017-04-14 09:23 | 2017-04-15 10:45 | 13.8KV PETANI FEEDER #1 | Fair | Low mega-ohm reading | 52 | Replaced the Low Meg Transformer with the same size then energized the Tx. Cause: Low Mega-ohm Reading Tx. |  | 1 | 9:23 | Morning | Friday | 2017 | 4
5508 | 2017-04-14 15:12 | 2017-04-14 15:12 | 115KV DURI - KOTABATAK JUNCTION LINE | Lightning | Lightning | 745 | 15:12 KBJ - DRB 115KV Line T/R 1x. (KBJ GCB#43, GCB#45)-(DRB OCB#26, OCB#28). PGT - DRB 115KV Line T/R 1x. (Pungut OCB#21)-(DRB OCB#21, OCB#9). Frequency system increased to 60.52 Hz. CGT #5 T/O by Alarm Gen. Under voltage (27) 15:17 MGT#7 Man. Open Gen. Brk, Closed at 15:54 (Stabilized frequency) 15:38 CGT#5 S/U, then On Line at 15:56. 6DN fdr#5 Man .Open to avoid Over level, (GS#3 WIP problem). 19:33 6DN Fdr#5 Man close. Cause: Suspected by Lightning. Load dropped Feeder Prod Loss: SPEARS: SLN ; Bangko GS: 545 Bbls, 293 Wells. 530 bbls / 292 wells Balam GS: 0 63 bbls / 23 wells Bekasap GS: 0 37 bbls / 2 wells Pematang GS: 0 Rangau GS: 0 SLS ; Kota Batak : 86 Bbls, 48 wells. 86 bbls / 44 wells Petapahan : 0 Minas GS#3 : 26 Bbls 7 wells. 29 bbls / 6 wells Minas GS#4 : 86 Bbls 38 wells. Minas GS#5 : 177 Bbls 90 wells. Minas GS#6 : 3 Bbls 2 wells. Total Prod Loss : 922 Bbls 478 wells. 745 bbls / 367 wells | 123 | 1 | 15:12 | Afternoon | Friday | 2017 | 4
5509 | 2017-04-14 15:12 | 2017-04-17 15:12 | 115KV DURI - KOTABATAK JUNCTION LINE | Lightning | Lightning | 745 | Checked & found, 115KV KBJ - DRB Line T/R 1x. -115KV KBJ GCB#43 T/R 1x ctr: 421-422 R/F:... -115KV KBJ GCB#45 T/R 1x ctr: 304-305 R/F:... -115KV DRB OCB#26 T/R 1x ctr: 915-916 R/F: 87L, 21P Z1. -115KV DRB OCB#28 T/R 1x ctr: 170-171 R/F: 87L, 21P Z1. 115KV Pungut - DRB Line T/R 1x. -115KV Pungut OCB#21 T/R 1x Ctr: 632 (did not operated) R/F:87L -115KV DRB OCB#21 T/R 1x ctr: 632 (did not change) R/F: 87L -115KV DRB OCB#29 T/R 1x ctr: 125-126 R/F: 87L Patrolled 115KV KBJ-DRB Line but found nothing. Patrolled 115KV Pungut-DRB Line but found nothing. Cause: Suspected by Lightning. | 123 | 1 | 15:12 | Afternoon | Friday | 2017 | 4
5510 | 2017-04-14 15:12 | 2017-04-14 15:12 | CENTRAL DURI POWER PLANT | Rain and Lightning | Under investigation | 0 | 15:12 CGT #5 T/O by Alarm Gen. Under voltage (27). 15:38 S/U CGT#5 then Online the unit at 15:56. Cause: Under Investigation. Note: see outage on 14 Apr at 15:12:02. |  | 1 | 15:12 | Afternoon | Friday | 2017 | 4
5511 | 2017-04-14 17:23 | 2017-04-14 17:23 | 13.8KV 3D FEEDER #3 | Lightning | Lightning | 115 | 17:23 3D fdr#3 T/R 3x. Not checked yet. |  | 1 | 17:23 | Afternoon | Friday | 2017 | 4
5512 | 2017-04-14 17:23 | 2017-04-17 17:23 | 13.8KV 3D FEEDER #3 | Lightning | Lightning | 115 | Checked & found, 3D OCB fdr #3 T/R 1x Ctr: 443 (did not change) R/F:50. Patrolled the Line but found nothing. Cause : Lightning |  | 1 | 17:23 | Afternoon | Friday | 2017 | 4
5513 | 2017-04-14 17:38 | 2017-04-14 17:38 | 13.8KV 4B FEEDER #4 | Lightning | Lightning | 51 | 17:38 4B fdr #4 load dropped 214A (306-92A). 4B fdr #5 load dropped 197A (206-9A). 4B fdr #6 load dropped 117A (133-16A). Not checked yet. | 11111 | 1 | 17:38 | Afternoon | Friday | 2017 | 4
5514 | 2017-04-14 17:38 | 2017-04-18 17:38 | 13.8KV 4B FEEDER #4 | Lightning | Lightning | 51 | Checked & found, 4B OCB fdr #4 T/R 1x ctr: 188-189 R/F:51 @2, @3. Patrolled the line but found nothing. Cause: Lightning | 11111 | 1 | 17:38 | Afternoon | Friday | 2017 | 4
5515 | 2017-04-14 17:38 | 2017-04-14 17:38 | 13.8KV 5B FEEDER #1 | Lightning | Lightning | 80 | 17:38 5B fdr #1 load dropped 172A (181-9A). 5B fdr #2 load dropped 150A (158-8A). 5B fdr #3 load dropped 21A (39-12A). 5B fdr #6 load dropped 130A (189-59A). Not checked yet. | 1111 | 1 | 17:38 | Afternoon | Friday | 2017 | 4
5516 | 2017-04-14 17:38 | 2017-04-18 17:38 | 13.8KV 5B FEEDER #1 | Lightning | Lightning | 80 | Checked & found, 5B OCB fdr#1 T/R 2x, Ctr: 233-235, R/F: 51 @1&@2 Patrolled the Line & found nothing Cause : Lightning | 1111 | 1 | 17:38 | Afternoon | Friday | 2017 | 4
5517 | 2017-04-14 21:07 | 2017-04-14 21:07 | 13.8KV SINTONG FEEDER #2 | Cloudy | Unidentified (Fuse) | 56 | 21:07 It was reported B/O fuse at well Benar#47 ( Sintong fdr#2 ). 23:02 Replaced @1 B/O fuse for 300 Kva with the same size. Cause : Unidentified fuse. |  | 1 | 21:07 | Night | Friday | 2017 | 4
5518 | 2017-04-15 01:47 | 2017-04-15 01:47 | 13.8KV DURI COMMUNITY FEEDER #5 | Cloudy | Dead End Insulator | 0 | Duri Community ACB fdr#5 T/R 1x. Not checked yet. |  | 1 | 1:47 | Night | Saturday | 2017 | 4
5519 | 2017-04-15 01:47 | 2017-04-15 15:00 | 13.8KV DURI COMMUNITY FEEDER #5 | Cloudy | Dead End Insulator | 0 | 15:00 Checked and found Duri community fdr#5 T/R 1X ctr:106-107 R/F:51N. Patrolled the line and found @3 Flash over Dead end insulator o/p SD-06. Cause : Dead end insulator ( Flash over ). |  | 1 | 1:47 | Night | Saturday | 2017 | 4
5520 | 2017-04-15 02:39 | 2017-04-15 02:39 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain | Unidentified | 0 | Dumai 4160V VCB #22 fdr#4 T/R 1x. Not checked yet. |  | 1 | 2:39 | Night | Saturday | 2017 | 4
5521 | 2017-04-15 02:39 | 2017-04-18 18:27 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain | Unidentified | 0 | Checked & found, 4.16kV Dumai ACB fdr#4 T/R 1x Ctr: 267-268 R/F: 51N. Patrolled the line, but found nothing Cause : Unidentified |  | 1 | 2:39 | Night | Saturday | 2017 | 4
5522 | 2017-04-15 11:13 | 2017-04-15 11:13 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 36 | So.Bekasap load 110 A(141-31 A). Cause : Not checked yet. |  | 1 | 11:13 | Morning | Saturday | 2017 | 4
5523 | 2017-04-15 11:13 | 2017-04-17 11:13 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 36 | Checked & found, no Breaker & Recloser operated. Patrolled the line & found nothing. Cause: Unidentified |  | 1 | 11:13 | Morning | Saturday | 2017 | 4
5524 | 2017-04-15 13:59 | 2017-04-15 13:59 | 13.8KV BEKASAP FEEDER #6 | Fair | Planned Maintenance | 0 | 13:59 Manual Opened Bekasap ACB fdr#6 . Bekasap GS requested, Repair 12" Production Line were leak (Incoming from Sobek & Aman Field). 16:57 Manual Closed Bekasap ACB fdr#6 Cause: Planned Maintenance. (No Production Loss Charge). |  | 1 | 13:59 | Afternoon | Saturday | 2017 | 4
5525 | 2017-04-15 15:09 | 2017-04-15 15:09 | 13.8KV NORTH DURI FEEDER #10 | Rain | Lightning | 0 | N.Duri VCB fdr#10 Load dropped 30A (150-120A). Not checked yet. |  | 1 | 15:09 | Afternoon | Saturday | 2017 | 4
5526 | 2017-04-15 15:09 | 2017-04-18 18:30 | 13.8KV NORTH DURI FEEDER #10 | Rain | Lightning | 0 | Checked & found, N.Duri VCB fdr#10 T/R 1x, Ctr: 20-21, R/F: 51N. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 15:09 | Afternoon | Saturday | 2017 | 4
5527 | 2017-04-15 15:57 | 2017-04-15 15:57 | CENTRAL DURI POWER PLANT | Rain | Under investigation | 0 | CGT #2 T/O, by Alarm Fire at Turbine compartment (Not Real) and DC ground. Frequency Lower 59.94 Hz, no Load shedding. Cause : Under investigation. |  | 1 | 15:57 | Afternoon | Saturday | 2017 | 4
5528 | 2017-04-15 19:15 | 2017-04-15 19:15 | CENTRAL DURI POWER PLANT | Fair |  | - | 19:15 S/U CGT#1, then online the unit at 19:38. |  | 1 | 19:15 | Night | Saturday | 2017 | 4
5529 | 2017-04-16 06:47 | 2017-04-16 06:47 | 13.8KV CENTRAL DURI FEEDER #1 | Rain | Lightning | 25 | C.Duri fdr#1 Load dropped 40A (123-83A). Not checked yet. |  | 1 | 6:47 | Morning | Sunday | 2017 | 4
5530 | 2017-04-16 06:47 | 2017-04-18 18:31 | 13.8KV CENTRAL DURI FEEDER #1 | Rain | Lightning | 25 | Checked & found, Recl. 38-AS-09 T/R 2x Ctr: 203-205 R/F: None. Patrolled the line, but found nothing. Cause : Lightning |  | 1 | 6:47 | Morning | Sunday | 2017 | 4
5531 | 2017-04-16 07:00 | 2017-04-16 07:00 | 13.8KV PUNGUT FEEDER #1 | Cloudy | Unidentified (Fuse) | 0 | 07:00 It was reported b/o fuse at well Pungut #61 (Pungut fdr#1). 11:52 Checked & found @3 broken primary jumper of 225KVATX. Replaced the Jumper above, then energized the TX. Cause: Unidentified. |  | 1 | 7:00 | Morning | Sunday | 2017 | 4
5532 | 2017-04-16 07:31 | 2017-04-16 07:31 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 24 | Ketigul VCB fdr#1 T/R 1X. Ketigul fdr#2 load dropped 43A (193-150A) Not checked yet. |  | 1 | 7:31 | Morning | Sunday | 2017 | 4
5533 | 2017-04-16 07:31 | 2017-04-17 07:31 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 24 | Checked & found, Ketigul VCB Fdr #1 T/R 1x Counter: 181-182 R/F: 51N. Patrolled the line & found, @3 flash over dead end isolator on pole 32AJ01. Couse : Dead end isulator |  | 1 | 7:31 | Morning | Sunday | 2017 | 4
5534 | 2017-04-16 10:55 | 2017-04-16 10:55 | 13.8KV MINAS FEEDER #5 | Fair | Powerline - Jumper | 0 | 10:55 Minas fdr#5 Load dropped 79A (126-47). 15:40 It was reported 12 well off under 8D fdr#5 and 2 unit WIP pump at GS#1. 15:54 Patrolled & found, @3 broken jumper O/P 7E-13 (Minas fdr#5 ). Decided to Energize VR #1 at 8D substation. 17:20 Open LBS 7E-153 separate part load MNS fdr #5 to 8D fdr#5. 17:43 Energized VR #1 at 8D Substation (as SP). 17:50 Man. Closed 8D fdr#5. 18:00 Man. Opened Recl. 7E-148. to separate Load from MNS fdr#5. Cause: Jumper. |  | 1 | 10:55 | Morning | Sunday | 2017 | 4
5535 | 2017-04-16 13:40 | 2017-04-16 13:40 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 10 | Menggala VCB fdr#1 Load dropped 65A (183-123A). Not checked yet. |  | 1 | 13:40 | Afternoon | Sunday | 2017 | 4
5536 | 2017-04-16 13:40 | 2017-04-17 11:00 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 10 | Checked & found, no Breaker & Recloser operated. Patrolled the line & found nothing. Cause: Unidentified. |  | 1 | 13:40 | Afternoon | Sunday | 2017 | 4
5537 | 2017-04-16 13:47 | 2017-04-16 13:47 | 13.8KV S. BALAM FEEDER #4 | Fair | Animal | 12 | 13:47 It was reported b/o fuse at well Balam #239 (Balam fdr#4). 14:45 Checked & found @1@2 b/o fuse for 150KVATX. Replaced the fuse with the same size, the energized the TX. Cause: Animal (Bird). |  | 1 | 13:47 | Afternoon | Sunday | 2017 | 4
5538 | 2017-04-17 04:19 | 2017-04-17 04:19 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Fair | Recloser - Control Recloser | 47 | 04:19 Libo MSU fdr#2 Load dropped 35A (52-17A). 06:12 Checked & found, Recl. 23BW02 T/SO Ctr:236-237. Blocked & closed Recl. 23BW02, but failed. (Control Recl. Mulfunction). 06:16 Closed Recl. 23BW-02 with jumper at control Recloser. 06:25 Bypass Recl. by Unplug the Recl. Control Cable. Cause: Control Recloser. |  | 1 | 4:19 | Morning | Monday | 2017 | 4
5539 | 2017-04-17 10:18 | 2017-04-17 10:18 | 13.8KV MINAS FEEDER #5 | Fair | Planned Maintenance | 0 | 10:18 Manually Opened 13.8KV Minas fdr #5 to repair broken Jumper o/p: 7E-13. 11:09 Closed 13.8KV Minas fdr #5. Cause: Planned maintenance. (See 16 April at 10:55) | 1111 | 1 | 10:18 | Morning | Monday | 2017 | 4
5540 | 2017-04-17 17:06 | 2017-04-17 17:06 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified | 0 | C. Duri 13.8KV ACB fdr #13 T/R 1X Counter:197-198 R/F: 51N, 51 @1, @2. Not checked yet. | 11111 | 1 | 17:06 | Afternoon | Monday | 2017 | 4
5541 | 2017-04-17 17:06 | 2017-04-22 07:55 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified | 0 | Checked and found C. Duri 13.8KV ACB fdr #13 T/R 1X Counter:197-198 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. | 11111 | 1 | 17:06 | Afternoon | Monday | 2017 | 4
5542 | 2017-04-18 02:25 | 2017-04-18 02:25 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 0 | 02:25 Bekasap fdr#3 Load dropped 34A (147-112A). (Alarm DSC Recl. 38-BD-39 T/R) Not checked yet. |  | 1 | 2:25 | Night | Tuesday | 2017 | 4
5543 | 2017-04-18 02:25 | 2017-04-19 17:33 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found, Recloser 38-BD-39 T/R 1x Ctr:111-112 R/F 51P,@2. Patrolled the line, but found nothing. Cause : Suspected by Lightning. |  | 1 | 2:25 | Night | Tuesday | 2017 | 4
5544 | 2017-04-18 02:54 | 2017-04-18 02:54 | 13.8KV NORTH DURI FEEDER #11 | Rain and Lightning | Lightning | 0 | 02:54 N. Duri VCB fdr#11 T/R 1X. Ground fault Alarm on ND fdr#11. Not checked yet. |  | 1 | 2:54 | Night | Tuesday | 2017 | 4
5545 | 2017-04-18 02:54 | 2017-04-22 08:00 | 13.8KV NORTH DURI FEEDER #11 | Rain and Lightning | Lightning | 0 | Checked and found N. Duri VCB fdr#11 T/R 1x Counter:153-154 R/F: 51N. patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 2:54 | Night | Tuesday | 2017 | 4
5546 | 2017-04-18 02:56 | 2017-04-18 02:56 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Unidentified | 61 | 02:56 Pungut fdr#1 Load dropped 80A (84-4A). Not checked yet. |  | 1 | 2:56 | Night | Tuesday | 2017 | 4
5547 | 2017-04-18 02:56 | 2017-04-21 17:43 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Unidentified | 61 | Checked and found, Recloser Pungut AGRP T/R 9x R/F: 51 @... Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 2:56 | Night | Tuesday | 2017 | 4
5548 | 2017-04-18 03:01 | 2017-04-18 03:01 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Pin Insulator | 20 | 03:01 Pungut fdr#2 Load dropped 28A (56-28A). Not checked yet. |  | 1 | 3:01 | Night | Tuesday | 2017 | 4
5549 | 2017-04-18 03:01 | 2017-04-21 17:46 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Pin Insulator | 20 | Checked and found Recloser 46-BP-12 T/R:2x Counter:514-516. Patrolled the line found @3 broken pin insulator on pole 47-BP-15. Cause: Pin insulator. |  | 1 | 3:01 | Night | Tuesday | 2017 | 4
5550 | 2017-04-18 03:34 | 2017-04-18 03:34 | 13.8KV CENTRAL DURI FEEDER #3 | Rain and Lightning | Lightning | 0 | 03:34 C.Duri ACB fdr#3 T/O. Ctr: 199-200. R/F: 50 @1,@2,@3. (In Block position for Rig at well 5R-55C). 03:53 Man. Closed ACB Fdr#3, ok. (After get confirmation from RIG BN# 09) Not checked yet. |  | 1 | 3:34 | Night | Tuesday | 2017 | 4
5551 | 2017-04-18 03:34 | 2017-04-23 15:24 | 13.8KV CENTRAL DURI FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found C.Duri ACB fdr#3 T/O. Ctr: 199-200. R/F: 50 @1,@2,@3. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 3:34 | Night | Tuesday | 2017 | 4
5552 | 2017-04-18 03:34 | 2017-04-18 03:34 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Dead End Insulator | 95 | 03:34 C.Duri ACB fdr#4 T/LO, Ctr: 472-476, R/F: 51, @1,@2. Patrolled the Line, but found nothing 04:49 Manually Closed CD ACB fdr#4, OK. Cause : Unidentified. (Will be re patrol the line soon). |  | 1 | 3:34 | Night | Tuesday | 2017 | 4
5553 | 2017-04-18 03:34 | 2017-04-23 15:27 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Dead End Insulator | 95 | Checked and found C.Duri ACB fdr#4 T/LO, Ctr: 472-476, R/F: 51, @1,@2. Patrolled the line found @1 broken dead end insulator on pole 09-P8-04. Cause: Broken Dead end insulator. |  | 1 | 3:34 | Night | Tuesday | 2017 | 4
5554 | 2017-04-18 04:44 | 2017-04-18 04:44 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Pin Insulator | 65 | 8C fdr#6 load dropped 138A (177-39A). Not checked yet. |  | 1 | 4:44 | Morning | Tuesday | 2017 | 4
5555 | 2017-04-18 04:44 | 2017-04-22 09:17 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Pin Insulator | 65 | Checked and found 8C VCB fdr #6 T/R 1x Counter: 573-574 R/F: 51@3. Patrolled the line found @3 broken Pin insulator on pole 8C-02. Cause: Pin Insulator. |  | 1 | 4:44 | Morning | Tuesday | 2017 | 4
5556 | 2017-04-18 05:00 | 2017-04-18 05:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Lightning | Lightning Arrester | 85 | CKBS VCB fdr#5 T/R 1x. Not checked yet. |  | 1 | 5:00 | Morning | Tuesday | 2017 | 4
5557 | 2017-04-18 05:00 | 2017-04-18 17:10 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Lightning | Lightning Arrester | 85 | Checked & found, CKBS VCB fdr#5 T/R 1x, Ctr: 149-150, R/F: 51B @2 Patrolled the Line & found, @2 Broken LA o/p 34-CS-30 Cause : Lightning Arrester |  | 1 | 5:00 | Morning | Tuesday | 2017 | 4
5558 | 2017-04-18 21:41 | 2017-04-18 21:41 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 0 | 21:41 It was reported b/o fuse for Tx at well Balam #344 (Balam fdr#1). 23:06 Checked & found, b/o fuse for 150KVATX. Replaced the fuse with the same size, then energized the TX. Cause : Animal (monkey). |  | 1 | 21:41 | Night | Tuesday | 2017 | 4
5559 | 2017-04-19 07:02 | 2017-04-19 07:02 | 13.8KV DURI FIELD FEEDER #3 | Fair | Recloser | 0 | Duri Field 13.8KV ACB fdr #3 T/R 1X. Not checked yet. | 11111 | 1 | 7:02 | Morning | Wednesday | 2017 | 4
5560 | 2017-04-19 07:02 | 2017-04-22 08:05 | 13.8KV DURI FIELD FEEDER #3 | Fair | Recloser | 0 | Checked and found Duri Field 13.8KV ACB fdr #3 T/R 1x Counter: 360-361 R/F: 51N. Patrolled the line found @1 spark on By pass Recloser: 01-05-01. Cause: Spark on Recloser. | 11111 | 1 | 7:02 | Morning | Wednesday | 2017 | 4
5561 | 2017-04-19 13:30 | 2017-04-19 13:30 | 13.8KV PUNGUT FEEDER #2 | Fair | Animal | 28 | 13:30 It was reported b/o fuse at well Tandun #04. 15:25 Checked and found @1, @2 b/o fuse for 150KVA TX. Replaced b/o fuse above with same size, then energized the TX. Cause: Animal (monkey). |  | 1 | 13:30 | Afternoon | Wednesday | 2017 | 4
5562 | 2017-04-19 21:46 | 2017-04-19 21:46 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Lightning | 0 | 21:46 D.Community ACB fdr #5 T/LO, Ctr: ......, R/F:...... 21:51 Checked & found @2,@3 broken L.A o/p 1T-04, near Hospital back yard. Cut and Isolate the broken L.A. 22:57 Blocked & Manual Closed D.Comm ACB fdr#5, but T/O again. 23:15 Open LBS 1SG-04 toward Hospital. Blocked & Man Closed the ACB fdr#5, OK. Repatrolled the Line but found nothing (suspected Flash over pin Insulator o/p 1KT-04 d/s D.comm. fdr#5). 23:45 Closed back LBS 1SG.04, OK. Cause: Lightening (L.A). |  | 1 | 21:46 | Night | Wednesday | 2017 | 4
5563 | 2017-04-19 23:38 | 2017-04-19 23:38 | 13.8KV 8D FEEDER #4 | Fair | Unidentified | 0 | 8D OCB fdr#4 T/R 2x. Not checked yet. |  | 1 | 23:38 | Night | Wednesday | 2017 | 4
5564 | 2017-04-19 23:38 | 2017-04-22 09:22 | 13.8KV 8D FEEDER #4 | Fair | Unidentified | 0 | Checked and found 8D OCB fdr #4 T/R 2x Counter: 1540-1542 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 23:38 | Night | Wednesday | 2017 | 4
5565 | 2017-04-20 01:56 | 2017-04-20 01:56 | 13.8KV MENGGALA FEEDER #1 | Drizzle | Unidentified | 81 | Menggala fdr#1 Load dropped 100A (171-71A). Not checked yet. |  | 1 | 1:56 | Night | Thursday | 2017 | 4
5566 | 2017-04-20 01:56 | 2017-04-22 07:25 | 13.8KV MENGGALA FEEDER #1 | Drizzle | Unidentified | 81 | Checked and found Menggala fdr#1 Normal condition. Cause: Unidentified. |  | 1 | 1:56 | Night | Thursday | 2017 | 4
5567 | 2017-04-20 11:08 | 2017-04-20 11:08 | 13.8KV KETIGUL FEEDER#1 | Fair | Transformer Failure | 146 | 11:08 It was reported unbalance Voltage at Well Tilan #16. 15:21 Checked and found loss connection at Secondary bushing of 500 KVA TX. Cause: TX failure. (This TX is not replaced yet). |  | 1 | 11:08 | Morning | Thursday | 2017 | 4
5568 | 2017-04-20 11:08 | 2017-04-21 17:00 | 13.8KV KETIGUL FEEDER#1 | Fair | Transformer Failure | 146 | 17:00 C/O 500KVA TX to 300KVA TX then energized at well Tilan #16 d/s Ketigul fdr #1. Cause: TX failure. |  | 1 | 11:08 | Morning | Thursday | 2017 | 4
5569 | 2017-04-20 22:20 | 2017-04-20 22:20 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Others | 177 | 22:20 Mns ACB Fdr#3 T/SO, Ctr:80104-80106, R/F:51@1,@2. Mns ACB Fdr#1 Load drop 28A (80-52). Mns ACB Fdr#2 Load drop 17A (124-107). Mns ACB Fdr#4 Load drop 37A (216-179). 23:28 Checked and found a kite hang up o/p 7D-76, dismantled it. Blocked and closed Mns ACB Fdr#3 then released the block. Cause: Other(kite). |  | 1 | 22:20 | Night | Thursday | 2017 | 4
5570 | 2017-04-20 23:11 | 2017-04-20 23:11 | 5 BRAVO SUBSTATION | Rain and Lightning | Lightning Arrester | 395 | 23:11 5B 115KV OCB #24 T/O. 5B TX#1 T/O, R/F: 87T,86T. 5B RTU Failed. No power at 5B bus#1 (Fdr#1, Fdr#2, Fdr#3, Fdr#6) 01:36 Opened 5B OCB# fdr#1, Fdr#2, Fdr#3, Fdr#6. Manually Closed 5B 115KV OCB#24, 5B TX#1. energized. Manually Closed 5B OCB fdr#1 Manually Closed 5B OCB fdr#2 Manually Closed 5B OCB fdr#3 Manually Closed 5B OCB fdr#6, but Failed, no Relay Flag indication appear. 02:16 Manually Closed 5B OCB fdr#6, but T/O again 5B TX#1 T/O 5B 115KV OCB #24 T/O No power at 5B bus#1 (Fdr#1, Fdr#2, Fdr#3, Fdr#6) 02:30 Opened 5B OCB# fdr#1, Fdr#2, Fdr#3, Fdr#6. Manually Closed 5B 115KV OCB#24, 5B TX#1. energized. Manually Closed 5B OCB fdr#1 Manually Closed 5B OCB fdr#2 Manually Closed 5B OCB fdr#3 5B OCB fdr#6, Keep Open for trouble shooting. 05:57 Patrolled the line, found @2 broken LA o/p 6D.5B16 d/s 5B Fdr#6. Isolate Broken LA, then Manually Closed 5B OCB Fdr#6. Cause : Lightning Arrester (Broken). |  | 1 | 23:11 | Night | Thursday | 2017 | 4
5571 | 2017-04-20 23:23 | 2017-04-20 23:23 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 8 | 23:23 4B fdr#5 T/R 1X. 4B fdr#6 Load drop 56A(135-79). 4B fdr#4 Load drop 40A(269-229). cause: Not checked yet. |  | 1 | 23:23 | Night | Thursday | 2017 | 4
5572 | 2017-04-20 23:23 | 2017-04-25 22:17 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 8 | Checked and found 4B VCB fdr#5 T/R 1X ctr:111-112 R/F:51N. Patrolled the line, found @3 Broken pin insulator o/p: nn. Cause: Lightning. |  | 1 | 23:23 | Night | Thursday | 2017 | 4
5573 | 2017-04-20 23:36 | 2017-04-20 23:36 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 25 | 23:36 4D Fdr#5 Load drop 46A (163-17). Cause: Not checked yet. |  | 1 | 23:36 | Night | Thursday | 2017 | 4
5574 | 2017-04-20 23:36 | 2017-04-22 17:18 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 25 | Checked and found Recloser 4D-51A Normal Counter: 48-48 (did not change). Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 23:36 | Night | Thursday | 2017 | 4
5575 | 2017-04-20 23:49 | 2017-04-20 23:49 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 57 | 23:49 8D Fdr#11 T/R 1X. 8C RTU Failed. Not checked yet |  | 1 | 23:49 | Night | Thursday | 2017 | 4
5576 | 2017-04-20 23:49 | 2017-04-24 23:49 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 57 | Checked & found, 8D OCB fdr #11 T/R 1x ctr: 99912-99913 R/F: 51N. Patrolled the line & found nothing. Cause: Lightning. |  | 1 | 23:49 | Night | Thursday | 2017 | 4
5577 | 2017-04-21 03:04 | 2017-04-21 03:04 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Planned Maintenance | 0 | 03:04 Manually Opened 4D OCB Fdr#4. to Maintain GS 4 Tank level, due to 5B Fdr#6 not Energized yet. 06:04 Closed Back 4D OCB fdr#4 after Success to Energized 5B Fdr#6. Cause : Planned Maintenance ( Production Losses Charged) |  | 1 | 3:04 | Night | Friday | 2017 | 4
5578 | 2017-04-21 08:33 | 2017-04-21 08:33 | MINAS POWER PLANT |  |  | - | 08:33 S/U MGT#5 and Online the unit at 08:48. |  | 1 | 8:33 | Morning | Friday | 2017 | 4
5579 | 2017-04-21 09:01 | 2017-04-21 09:01 | MINAS POWER PLANT |  |  | - | 09:00 Off line MGT#4 and then S/D the unit. For fixing the air leakage at AA.Pre cooler. |  | 1 | 9:01 | Morning | Friday | 2017 | 4
5580 | 2017-04-21 15:41 | 2017-04-21 15:41 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | N.Duri VCB fdr #11 T/R 1X. Cause: Not checked yet. |  | 1 | 15:41 | Afternoon | Friday | 2017 | 4
5581 | 2017-04-21 15:41 | 2017-04-23 15:34 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | Checked and found N.Duri VCB fdr #11 T/R 1x Counter: 154-155 R/F:51N. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 15:41 | Afternoon | Friday | 2017 | 4
5582 | 2017-04-21 20:28 | 2017-04-21 20:28 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning Arrester | 88 | 20:28 Libo 13.8kv OCB fdr#2 T/LO. 21:48 Checked & found, Libo OCB fdr#2 T/LO, Ctr: 268-274, R/F: 51G. Blocked & Closed Libo OCB fdr#2, OK. Not patrolled yet Cause: Lightning ( RTU still Failure, Cannot be reseted). |  | 1 | 20:28 | Night | Friday | 2017 | 4
5583 | 2017-04-21 20:28 | 2017-04-22 16:01 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning Arrester | 88 | Checked and found, Libo OCB fdr #2 T/LO Counter:268-274 R/F: 51N. Patrolled the line found, @2 broken Lightning Arrester on pole KW-118. Cause: Lightning Arrester. |  | 1 | 20:28 | Night | Friday | 2017 | 4
5584 | 2017-04-21 22:03 | 2017-04-21 22:03 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 222 | 22:03 4B 13.8Kv OCB fdr#5 T/SO. 22:12 5B fdr#1 Manual open and Close 22:13. 22:14 4B fdr#6 Manually open. 23:44 5B fdr#4 Manually open. 22 April 2017 02:43 Checked & found 4B VCB fdr#5 T/SO, Ctr: 112-113, R/F: 50/51N. Also found Broken @1 Pin Insulator o/p 5B-04. Replaced the Broken Pin, after Opened Visual Opening Switch VCB Fdr#5. Blocked & Closed 4B VCB fdr#5, OK. the released the Block. 02:46 Manually Closed 4B VCB fdr#6 (MNS GS 6 Requested) 02:47 Manually Closed 5B VCB fdr#4 (MNS GS 6 Requested) Cause: Lightning. |  | 1 | 22:03 | Night | Friday | 2017 | 4
5585 | 2017-04-21 22:03 | 2017-04-21 22:03 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Lightning | 0 | 4B OCB Fdr#6 T/R 1x. Not checked yet. |  | 1 | 22:03 | Night | Friday | 2017 | 4
5586 | 2017-04-21 22:03 | 2017-04-22 17:19 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked & found 4B OCB fdr#6 T/R 1x, Ctr: 140-142, R/F: 51N, @1,@2. Patrolled the Line, found @1,@2Broken L.A On pole 4B-12 Cause : Lightning |  | 1 | 22:03 | Night | Friday | 2017 | 4
5587 | 2017-04-22 10:16 | 2017-04-22 10:16 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 0 | 10:16 Opened LBS 15-Z-16 D/S So Balam fdr#1. Due to replace 30 pcs Pin insulator to post type insulator. 14:32 Closed LBS 15-Z-16 D/S So Balam fdr#1. Cause: Planned maintenance. |  | 1 | 10:16 | Morning | Saturday | 2017 | 4
5588 | 2017-04-22 10:30 | 2017-04-22 10:30 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | N. Duri VCB fdr #1 T/R 1X. Not checked yet. | 11111 | 1 | 10:30 | Morning | Saturday | 2017 | 4
5589 | 2017-04-22 10:30 | 2017-04-23 15:36 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found N. Duri VCB fdr #1 T/R 1x Counter:072-073 R/F: 50 @1. Patrolled the line nothing found. Cause: Unidentified. | 11111 | 1 | 10:30 | Morning | Saturday | 2017 | 4
5590 | 2017-04-22 11:30 | 2017-04-22 11:30 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Broken Fuse Cut Out | 16 | 11:30 It was reported B/O Fuse O/P 04-00-08 d/s Duri fdr#8. 17:20 Checked and found @2 broken Fuse Cut Out on pole 04-00-08. Replaced @2 broken Fuse Cut Out with the same size and energized the Tx. Cause: Broken FCO. |  | 1 | 11:30 | Morning | Saturday | 2017 | 4
5591 | 2017-04-22 13:07 | 2017-04-22 13:07 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 0 | Menggala fdr#1 Load dropped 104A (179-75). Ground fault alarm from Menggala fdr#1. Not checked yet. |  | 1 | 13:07 | Afternoon | Saturday | 2017 | 4
5592 | 2017-04-22 13:07 | 2017-04-23 15:30 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 19 AN 04 T/R 1X Ctr: 326-327 R/F : 50 @3 Patrolled the line and found nothing. Cause: Suspected by Lightning. |  | 1 | 13:07 | Afternoon | Saturday | 2017 | 4
5593 | 2017-04-22 14:29 | 2017-04-22 14:29 | 13.8KV 8C FEEDER #4 | Fair | Planned Maintenance | 5 | 14:29 Opened Hot line clamp on Terminal pole well #9C-49A. Due to replace @2 burnt out FCO and 9pcs Pin Insulator and 3pcs Lightning Arrester. 16:00 Energized well #9C-49A. Cause: Planned Maintenance. |  | 1 | 14:29 | Afternoon | Saturday | 2017 | 4
5594 | 2017-04-22 15:22 | 2017-04-22 15:22 | 13.8KV NORTH DURI FEEDER #2 | Fair | Animal | 59 | 15:22 It was reported b/o Fuse o/p 13-G2-37 D/S N.Duri fdr#2. 17:20 Checked and found @3 b/o fuse for 112.5 Kva Tx on pole 13-G2-37 . Replaced @3 b/o fuse above with the same size and energized the Tx. Cause: Animal (Monkey). |  | 1 | 15:22 | Afternoon | Saturday | 2017 | 4
5595 | 2017-04-22 17:50 | 2017-04-22 17:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 10 | 17:50 It was reported B/O Fuse o/p 08 L7 16 d/s C.Duri fdr#1. Not checked yet. |  | 1 | 17:50 | Afternoon | Saturday | 2017 | 4
5596 | 2017-04-22 17:50 | 2017-04-23 08:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 10 | 08:30 Checked & found @1,@2 b/o fuse for 112.5KVA TX o/p 08 L7 16. Replace b/o fuse above with the same size & energized the TX. Cause: Animal (squirrel). |  | 1 | 17:50 | Afternoon | Saturday | 2017 | 4
5597 | 2017-04-23 00:22 | 2017-04-23 00:22 | 4.16KV SO RUMBAI FEEDER #3 | Rain | Lightning | 0 | 00:22 4.16KV S. Rumbai Recl. Fdr#3 T/R 1X ctr: 29-130 R/F: 51N. 17:00 Patrolled the line & found, @2 broken Pin Insulator on Pole 4RH-02. Cause: Lightning |  | 1 | 0:22 | Night | Sunday | 2017 | 4
5598 | 2017-04-23 00:36 | 2017-04-23 00:36 | 4.16KV EAST RUMBAI FEEDER #2 | Rain | Broken Fuse Cut Out | 0 | 4.16KV E. Rumbai VCB Fdr#2 T/R 1X. Not checked yet. |  | 1 | 0:36 | Night | Sunday | 2017 | 4
5599 | 2017-04-23 00:36 | 2017-04-24 10:36 | 4.16KV EAST RUMBAI FEEDER #2 | Rain | Broken Fuse Cut Out | 0 | Checked & found, 4.16KV East Rumbai VCB fdr #2 T/R 1x ctr: 512-513 R/F: 51 @3. Patrolled the line & found, @3 broken Fuse Cut Out on Pole 5RE-05. Cause: Broken Fuse Cut Out. |  | 1 | 0:36 | Night | Sunday | 2017 | 4
5600 | 2017-04-23 09:25 | 2017-04-23 09:25 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 0 | 09:25 Opened LBS 15-Z-16 D/S So Balam fdr#1. Due to replace 24 pcs Pin insulator to Pin post type insulator. 12:30 Closed LBS 15-Z-16 D/S So Balam fdr#1. Cause: Plan maintenance. |  | 1 | 9:25 | Morning | Sunday | 2017 | 4
5601 | 2017-04-24 09:50 | 2017-04-24 09:50 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Animal | 2 | 09:50 It was reported b/o fuse o/p 01-03-08 d/s C.Duri #6 . 10:14 Checked & found @1,@2 b/o fuse for 112.5KVA TX. Replaced b/o fuse above with the same size & energize the TX. Cause: Animal (squirrel). |  | 1 | 9:50 | Morning | Monday | 2017 | 4
5602 | 2017-04-24 11:13 | 2017-04-24 11:13 | 13.8KV KETIGUL FEEDER#1 | Fair | Lightning | 36 | Ketigul VCB fdr#1 T/R 1x. Ketigul fdr #2 Load dropped 49A (194-145A). Not checked yet. |  | 1 | 11:13 | Morning | Monday | 2017 | 4
5603 | 2017-04-24 11:13 | 2017-04-25 11:13 | 13.8KV KETIGUL FEEDER#1 | Fair | Lightning | 36 | Checked & found, Ketigul VCB fdr #1 T/R 2x ctr: 181-183 R/F: 51N. Patrolled the line & found, @2 broken LA on Pole 32-AK-36. Cause : Lightning |  | 1 | 11:13 | Morning | Monday | 2017 | 4
5604 | 2017-04-24 13:26 | 2017-04-24 13:26 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 13:26 It was reported b/o fuse for Tx on pole 01-09-13 d/s Duri field fdr #3. Checked & found @1,@2 b/o fuse for 112.5KVA TX. Replaced b/o fuse above with the same size & energize the Tx. Cause: Unidentified (fuse). |  | 1 | 13:26 | Afternoon | Monday | 2017 | 4
5605 | 2017-04-24 14:00 | 2017-04-24 14:00 | 13.8KV LIBO FEEDER #2 | Lightning | Lightning | 13 | Checked & found, Libo OCB fdr #2 T/R 1x ctr: 274-275 R/F: 51N. Patrolled the line & found, @2 Broken LA on Pole KW-119. Cause: Lightning. (See outage on 24 Apr at 23:55) | 11111 | 1 | 14:00 | Afternoon | Monday | 2017 | 4
5606 | 2017-04-24 14:00 | 2017-04-24 14:00 | 13.8KV LIBO FEEDER #2 | Lightning | Lightning | 13 | Libo 13.8KV OCB fdr #2 T/R 1x. (Reported by LIBO GS due to LIBO RTU failed). Not checked yet. | 11111 | 1 | 14:00 | Afternoon | Monday | 2017 | 4
5607 | 2017-04-24 15:35 | 2017-04-24 15:35 | 13.8KV NORTH DURI FEEDER #8 | Heavy Rain | Dead End Insulator | 0 | N.Duri VCB fdr #8 T/R 2x. Not checked yet. |  | 1 | 15:35 | Afternoon | Monday | 2017 | 4
5608 | 2017-04-24 15:35 | 2017-04-27 16:17 | 13.8KV NORTH DURI FEEDER #8 | Heavy Rain | Dead End Insulator | 0 | Checked and found N.Duri VCB fdr #8 T/R 3x Counter: 79-82 R/F: 51@3. Patrolled the line found @3 broken Dead End Insulator on pole ND-11A. Cause: Dead end Insulator. |  | 1 | 15:35 | Afternoon | Monday | 2017 | 4
5609 | 2017-04-24 15:58 | 2017-04-24 15:58 | 13.8KV CENTRAL DURI FEEDER #8 | Heavy Rain | Unidentified | 83 | 15:58 C. Duri fdr #8 Load dropped 48A (192-144A). 16:40 It was reported no power o/p 04-2-13A & 04-2-12. 17:37 Checked & found, Recl. 04-02-22 T/O (In blocked Position) Ctr:79-80. Blocked & closed Recl. above, ok. (After got clearance from The Rig). Not Patrolled Yet. |  | 1 | 15:58 | Afternoon | Monday | 2017 | 4
5610 | 2017-04-24 15:58 | 2017-04-26 15:58 | 13.8KV CENTRAL DURI FEEDER #8 | Heavy Rain | Unidentified | 83 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:58 | Afternoon | Monday | 2017 | 4
5611 | 2017-04-24 16:30 | 2017-04-24 16:30 | 13.8KV CENTRAL DURI FEEDER #4 | Heavy Rain | Lightning | 0 | C.Duri ACB #21 (feeder #4) T/R 1x. Not checked yet. |  | 1 | 16:30 | Afternoon | Monday | 2017 | 4
5612 | 2017-04-24 16:30 | 2017-04-27 17:00 | 13.8KV CENTRAL DURI FEEDER #4 | Heavy Rain | Lightning | 0 | Checked and found C.Duri ACB #21 (feeder #4) T/R 1x Counter: 476-477 R/F: 51@1. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 16:30 | Afternoon | Monday | 2017 | 4
5613 | 2017-04-24 16:31 | 2017-04-24 16:31 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Transformer Failure | 192 | 16:31 It was reported b/o fuse for Tx on 4SW CVC Station d/s CD fdr #9. 17:15 Checked and found @1,2,3 b/o fuse for 300 Kva Tx. Perform TTR and megger found Low megger reading and broken LA on pole 04-07-26A. Cause: Transformer failure (Low megger reading). This Tx is not replaced yet. |  | 1 | 16:31 | Afternoon | Monday | 2017 | 4
5614 | 2017-04-24 16:31 | 2017-04-26 16:55 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Transformer Failure | 192 | 16:55 Replaced 300 Kva Tx failure with 750 Kva Tx. And energized the TX. Cause: Transformer failure. |  | 1 | 16:31 | Afternoon | Monday | 2017 | 4
5615 | 2017-04-24 16:32 | 2017-04-24 16:32 | 13.8KV 4B FEEDER #6 | Cloudy | Lightning | 0 | 16:32 4B fdr#6 load dropped 125A (130-5A). 17:15 Checked & found, 4B OCB fdr #6 T/R 1x ctr: 140-142 R/F: 51. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:32 | Afternoon | Monday | 2017 | 4
5616 | 2017-04-24 17:06 | 2017-04-24 17:06 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 14 | Rokan VCB fdr#2 T/R 1X. Not checked yet. |  | 1 | 17:06 | Afternoon | Monday | 2017 | 4
5617 | 2017-04-24 17:06 | 2017-04-25 17:06 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 14 | Checked & found, Rokan VCB fdr #2 T/R 1x ctr: 1250-1251 R/F: 51 @2. Patrolled the line & found, @2 broken LA at Terminal Pole of Well Kopar #08. Cause: Lightning. |  | 1 | 17:06 | Afternoon | Monday | 2017 | 4
5618 | 2017-04-24 17:15 | 2017-04-24 17:15 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 38 | 3D OCB fdr #3 T/R 1x. 3D fdr #2 load dropped 94A (197-103A). 3D fdr #4 load dropped 28A (197-169A). 3D fdr #5 load dropped 111A (209-98A). Not checked yet. |  | 1 | 17:15 | Afternoon | Monday | 2017 | 4
5619 | 2017-04-24 17:15 | 2017-04-26 17:15 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 38 | Checked & found, 3D OCB fdr #3 T/R 1x ctr: 443 (not change) R/F: 50N. Patrolled the line & found nothing. Cause: Lightning |  | 1 | 17:15 | Afternoon | Monday | 2017 | 4
5620 | 2017-04-24 17:19 | 2017-04-24 17:19 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 31 | Petani OCB fdr #2 T/R 1X. Not checked yet. | 1111 | 1 | 17:19 | Afternoon | Monday | 2017 | 4
5621 | 2017-04-24 17:19 | 2017-04-25 17:19 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 31 | Checked & found, Petani OCB fdr #2 T/R 1x ctr: 219-220 R/F: 51N. Patrolled the line & found, @1 Flash Over Pin Insulator on Pole 34-AZ-34. Cause: Lightning. | 1111 | 1 | 17:19 | Afternoon | Monday | 2017 | 4
5622 | 2017-04-24 17:21 | 2017-04-24 17:21 | 4 DELTA SUBSTATION | Rain and Lightning | Lightning | 204 | 17:21 4D 115 Kv GCB #22 T/SO. 4D 115 Kv GCB #23 T/SO. 4D 115 Kv GCB #24 T/SO. KBJ 115 KV GCB #28 and GCB #24 (115 Kv KBJ - 4D Line , No alarm trip at DSC). 3D 115 Kv OCB #22 (115 KV 3D-4D Line , No alarm trip at DSC). 6DN 115 Kv GCB #21 (115Kv 6DN - 4D Line , no alarm trip at DSC). 17:29 Manually closed 4D 115 Kv GCB #24 (Selector switch DL-SC) --> Success. Manually closed 4D 115 Kv GCB #22 but failed. 4D 115 Kv GCB #22 and GCB #23 still open. Respectively load dropped: - 8D fdr #1 load dropped 22A (140-118A). - 8D fdr #5 load dropped 10A (165-155A). - 8D fdr #7 load dropped 60A (236-176A). - 8D fdr #10 load dropped 11A (118-107A). - 8D fdr #11 load dropped 17A (169-152A). - 8C fdr #1 load dropped 28A (222-194A). - 8C fdr #2 load dropped 9A (51-42A). - 8C fdr #3 load dropped 17A (211-194A). - 8C fdr #4 load dropped 53A (230-177A). - 8C fdr #6 load dropped 13A (163-150A). - 5B fdr #2 load dropped 12A (164-152A). - 5B fdr #6 load dropped 120A (191-71A) --> WIP. - 6D fdr #1 load dropped 15A (227-212A). - 6D fdr #2 load dropped 17A (242-225A). - 6D fdr #5 load dropped 11A (229-218A). - 6DN fdr #6 load dropped 23A (190-167A). - 3D fdr #7 load dropped 47A (161-115A). - 4D fdr #2 load dropped 12A (148-136A). - 4D fdr #5 load dropped 7A (162-155A). - OKB fdr #2 load dropped 21A (257-236A). - NKBS fdr #3 load dropped 18A (148-130A). - CKBS fdr #1 load dropped 88A (323-234A). - CKBS fdr #5 load dropped 8A (376-368A). - CKBS fdr #6 load dropped 23A (185-162A). - PTH fdr #2 load dropped 87A (218-131A). 17:35 Manually open 4B fdr #6 by DSC due to maintenance water level. Closed at 18:01. 18:34 Manually open 4B fdr #6 by DSC due to maintenance water level. Closed at 19:07. 19:03 Manually closed 4B fdr #4 by DSC. 20:50 Checked and found 115KV GCB #22 T/SO ctr:627-628 R/F: 51@1. Checked and found 115KV GCB #22 T/SO ctr:482-483 NO R/F. Checked and found 115KV GCB #24 T/SO ctr:640-641 R/F: 51@2, @3. Closed 115KV GCB #22 on SC and DL but failed. Closed 115KV GCB #23 on SC and DL but failed. Cause: Not checked yet. Production loss: GS #5------> 31 Bbls / 18 wells. GS #6------> 73 Bbls / 28 wells. ------------------------------------- + TOTAL : 104 Bbls / 46 Weels. |  | 1 | 17:21 | Afternoon | Monday | 2017 | 4
5623 | 2017-04-24 17:21 | 2017-04-25 11:00 | 4 DELTA SUBSTATION | Rain and Lightning | Lightning | 204 | Checked and found 115 KV 4D - KBJ Line. 4D Substation: 115 KV 4D GCB #22 T/SO Counter: Closed at 11:19. 115 KV 4D GCB #23 T/SO Counter: Closed at 11:20. 115 KV 4D GCB #24 T/SO Counter: Closed at 17:29. (April 24,2017). Relay L 90 R/F: 87 LB , 87 LC , 21P @B-C , 21G> Relay C 60 R/F: Breaker arching operate 86 (breaker failure)24. KBJ SS: 115 KV KBJ GCB #24 T/SO Counter: 419-420. Closed at 13:16. Relay L 90 R/F: 87 LC , 87 LB , 67N Time A , 67N Time B , 67N Inst C. Cause: Not patrolled yet. |  | 1 | 17:21 | Afternoon | Monday | 2017 | 4
5624 | 2017-04-24 23:45 | 2017-04-24 23:45 | 13.8KV LIBO FEEDER #1 | Cloudy and Lightning | Unidentified | 6 | Libo 13.8KV OCB fdr #1 T/R 1x ctr:269-270 R/F:51@1 (Reported by LIBO GS due to LIBO RTU failed). Not patrolled yet. | 1111 | 1 | 23:45 | Night | Monday | 2017 | 4
5625 | 2017-04-24 23:45 | 2017-04-25 13:45 | 13.8KV LIBO FEEDER #1 | Cloudy and Lightning | Unidentified | 6 | Checked & found, Libo OCB fdr #1 T/R 1x ctr: 269-270 R/F: 51N Patrolled the line but found nothing. Cause : Unidentified | 1111 | 1 | 23:45 | Night | Monday | 2017 | 4
5626 | 2017-04-24 23:55 | 2017-04-24 23:55 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning Arrester | 6 | Libo 13.8KV OCB fdr #2 T/LO crt: 275-279 R/F: 51G. Patrolled the line and found, @2 broken LA Jumper o/p KW 118. Cause: Jumper. | 1111 | 1 | 23:55 | Night | Monday | 2017 | 4
5627 | 2017-04-25 00:08 | 2017-04-25 00:08 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Unidentified | 35 | LIBO OCB fdr #1 T/R 1X Counter: 270-271 R/F: 51@1. Not patrolled yet. | 1111 | 1 | 0:08 | Night | Tuesday | 2017 | 4
5628 | 2017-04-25 00:08 | 2017-04-26 17:00 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Unidentified | 35 | Checked & found, Libo OCB fdr #1 T/R 1x ctr: 270-271 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified | 1111 | 1 | 0:08 | Night | Tuesday | 2017 | 4
5629 | 2017-04-25 13:10 | 2017-04-25 13:10 | 13.8KV 8C FEEDER #4 | Drizzle | Unidentified | 25 | 8C OCB fdr#4 T/R 1x. Not checked yet. |  | 1 | 13:10 | Afternoon | Tuesday | 2017 | 4
5630 | 2017-04-25 13:10 | 2017-02-05 19:10 | 13.8KV 8C FEEDER #4 | Drizzle | Unidentified | 25 | Checked & found 8C fdr#4 T/R 1x Ctr:590-592 R/F:50@2@3. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 13:10 | Afternoon | Tuesday | 2017 | 4
5631 | 2017-04-25 14:47 | 2017-04-25 14:47 | 13.8KV CENTRAL DURI FEEDER #6 | Drizzle | Lightning | 0 | C.Duri ACB #23 (feeder#6) T/R 1x Counter:475-476 R/F: 50 @2.@3. Not patrolled yet. |  | 1 | 14:47 | Afternoon | Tuesday | 2017 | 4
5632 | 2017-04-25 14:47 | 2017-04-27 17:32 | 13.8KV CENTRAL DURI FEEDER #6 | Drizzle | Lightning | 0 | Checked and found C.Duri ACB #23 (feeder#6) T/R 1x Counter:475-476 R/F: 51 @2. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 14:47 | Afternoon | Tuesday | 2017 | 4
5633 | 2017-04-25 15:24 | 2017-04-25 15:24 | 4.16KV SO RUMBAI FEEDER #1 | Rain and Lightning | Lightning | 0 | S.Rumbai 4160 V Recloser fdr #1 T/R 1x. Not checked yet. |  | 1 | 15:24 | Afternoon | Tuesday | 2017 | 4
5634 | 2017-04-25 15:24 | 2017-01-05 13:33 | 4.16KV SO RUMBAI FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found SO Rumbai 4.16KV Recl. fdr#1 T/R 1x, Ctr: 476-477, R/F: 51 N. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 15:24 | Afternoon | Tuesday | 2017 | 4
5635 | 2017-04-25 16:02 | 2017-04-25 16:02 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 178 | 16:02 So.Bekasap 13.8 KV Feeder#1 T/SO Counter: 352-354 R/F: 51@3. 17:25 Checked and found, So. Bekasap Feeder#1 T/SO Counter: 352-354 R/F: 51@3. Blocked and closed So. Bekasap fdr #1, Ok then normalized the block. Not patrolled yet. |  | 1 | 16:02 | Afternoon | Tuesday | 2017 | 4
5636 | 2017-04-25 16:02 | 2017-04-26 16:02 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 178 | Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 16:02 | Afternoon | Tuesday | 2017 | 4
5637 | 2017-04-25 16:44 | 2017-04-25 16:44 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 57 | CKBS VCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 16:44 | Afternoon | Tuesday | 2017 | 4
5638 | 2017-04-25 16:44 | 2017-04-26 16:44 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 57 | Checked & found, CKB VCB fdr #1 T/R 1x ctr: 218-219 R/F: 50N. Patrolled the line & found nothing. Cause : Lightning. |  | 1 | 16:44 | Afternoon | Tuesday | 2017 | 4
5639 | 2017-04-25 16:44 | 2017-04-25 16:44 | 13.8KV CENTRAL KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 0 | CKBS VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 16:44 | Afternoon | Tuesday | 2017 | 4
5640 | 2017-04-25 16:44 | 2017-04-26 16:44 | 13.8KV CENTRAL KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, CKB VCB fdr #2 T/R 1x ctr: 94-95 R/F: 50N. Patrolled the line but found nothing. Cause : Lightning |  | 1 | 16:44 | Afternoon | Tuesday | 2017 | 4
5641 | 2017-04-25 17:30 | 2017-04-25 17:30 | 13.8KV CENTRAL DURI FEEDER #2 | Rain and Lightning | Main breaker | 0 | 17:30 It was reported b/o fuse on pole 08-M5-10 d/s CD fdr #2. Not checked yet. |  | 1 | 17:30 | Afternoon | Tuesday | 2017 | 4
5642 | 2017-04-25 17:30 | 2017-04-26 08:00 | 13.8KV CENTRAL DURI FEEDER #2 | Rain and Lightning | Main breaker | 0 | 08:00 Checked and found@2,@3 b/o fuse for 112.5 Kva Tx. Perform TTR and megger found good reading. Replaced b/o fuse above with same size. 15:00 Energized the Tx. Cause: Main breaker 480V. |  | 1 | 17:30 | Afternoon | Tuesday | 2017 | 4
5643 | 2017-04-26 07:00 | 2017-04-26 07:00 | 4.16KV SO RUMBAI FEEDER #1 | Fair | Transformer Failure | 0 | 07:00 It was reported no power at LPT Rumbai d/S So Rumbai fdr #1. 07:45 Checked and found @1,@2 b/o fuse for 3x50 Kva Tx on pole.... Perform TTR and megger found 1 pc 50 Kva Tx low megger reading. 16:30 Replaced 50 Kva Tx failure with same size and energized the Tx. Cause: Tx failure. |  | 1 | 7:00 | Morning | Wednesday | 2017 | 4
5644 | 2017-04-26 09:39 | 2017-04-26 09:39 | 13.8KV MINAS FEEDER #3 | Fair | Others | 92 | 09:39 Minas ACB #2 ( Minas Fdr # 3 ) T/LO. 10:15 Checked and found Minas ACB #2 ( Minas Fdr # 3 ) T/LO Counter : 106 - 108 R/F : 51 @ 1,2. Patrolled line found Kite hang on power line o/p 7D-73E. 10:17 Blocked and Closed ACB #2 ( Minas Fdr #3 ) -> Success. Released block. Cause : Kite. |  | 1 | 9:39 | Morning | Wednesday | 2017 | 4
5645 | 2017-04-26 14:15 | 2017-04-26 14:15 | 13.8KV DARLING VCB FEEDER #3 | Fair | Planned Maintenance | 14 | 14:15 Manually opened LBS 05-N5-22 d/s Darling fdr #3. Due to Squeezed jumper on pole 05-N5-01A (Tie in to Darling fdr #1) 14:51 Manually closed LBS 05-N5-22 . Cause: Plan Maintenance. |  | 1 | 14:15 | Afternoon | Wednesday | 2017 | 4
5646 | 2017-04-26 16:05 | 2017-04-26 16:05 | 13.8KV SINTONG GFPC | Fair | Unidentified | 0 | Sintong GFPC T/R 1x no load dropped on any feeder. Not checked yet. |  | 1 | 16:05 | Afternoon | Wednesday | 2017 | 4
5647 | 2017-04-26 16:05 | 2017-04-29 07:11 | 13.8KV SINTONG GFPC | Fair | Unidentified | 0 | Checked and found Sintong GFPC T/R 1x Counter: 960-961 R/F: 51N Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 16:05 | Afternoon | Wednesday | 2017 | 4
5648 | 2017-04-26 16:37 | 2017-04-26 16:37 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | 55 | Minas ACB #2 ( Minas Fdr # 3 ) T/R 1X. Not Checked yet. |  | 1 | 16:37 | Afternoon | Wednesday | 2017 | 4
5649 | 2017-04-26 16:37 | 2017-04-27 16:37 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | 55 | Checked & found, Minas ACB #02 fdr #3 T/R 1x ctr: 108-109 R/F: 51 @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:37 | Afternoon | Wednesday | 2017 | 4
5650 | 2017-04-26 18:54 | 2017-04-26 18:54 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 17 | 4D OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 18:54 | Afternoon | Wednesday | 2017 | 4
5651 | 2017-04-26 18:54 | 2017-01-05 00:11 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 17 | Checked & found 4D OCB fdr#2 T/R 1x, Ctr: 242-243, R/F: 50 @2,@3. Patrolled the Line, found @2, @3 Broken Pin & Dead end Insulator o/p 36 -DN12 Cause : Lightning |  | 1 | 18:54 | Afternoon | Wednesday | 2017 | 4
5652 | 2017-04-26 18:54 | 2017-04-26 18:54 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 0 | 4D fdr #3 load dropped 46 A (62 - 16) A Not checked yet. |  | 1 | 18:54 | Afternoon | Wednesday | 2017 | 4
5653 | 2017-04-26 18:54 | 2017-01-05 08:27 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found 4D OCB fdr#3 T/R 1x, Ctr: 236-237, R/F: 50 N. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 18:54 | Afternoon | Wednesday | 2017 | 4
5654 | 2017-04-26 18:57 | 2017-01-04 08:26 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 9 | Checked & found 4D OCB fdr#5 T/R 4x, Ctr: 295-299, R/F: 50N. Patrolled the Line, but5 found nothing Cause : Lightning |  | 1 | 18:57 | Afternoon | Wednesday | 2017 | 4
5655 | 2017-04-26 18:57 | 2017-04-26 18:57 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 9 | 4D OCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 18:57 | Afternoon | Wednesday | 2017 | 4
5656 | 2017-04-26 18:58 | 2017-04-26 18:58 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 56 | 4D OCB fdr #3 T/R 1x. Not checked yet. |  | 1 | 18:58 | Afternoon | Wednesday | 2017 | 4
5657 | 2017-04-26 18:58 | 2017-01-05 17:02 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 56 | Checked and found 4D OCB fdr #3 T/R 1x Counter: 236-237 R/F: 50@1,3. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 18:58 | Afternoon | Wednesday | 2017 | 4
5658 | 2017-04-26 20:46 | 2017-04-26 20:46 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Pin Insulator | 174 | Minas fdr #6 T/LO, Ctr: 160-163 R/F: 51 @2 Patrolled the line but found nothing. 22:30 Blocked and closed Minas fdr#6. 22:42 Normalize the block, OK. 23:30 It was reported still no power at Minas Camp. 23:50 Checked and found Recloser 7E-67A T/LO Ctr: 55-57 Blocked and closed recloser 7E-67A. Released the block, OK. (Patroll will continue tomorrow morning). |  | 1 | 20:46 | Night | Wednesday | 2017 | 4
5659 | 2017-04-26 20:46 | 2017-01-05 16:55 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Pin Insulator | 174 | Patrolled the line found @2 broken Pin Insulator on pole 7E-128. Cause: Broken Pin Insulator. |  | 1 | 20:46 | Night | Wednesday | 2017 | 4
5660 | 2017-04-27 07:40 | 2017-04-27 07:40 | 13.8KV 4D FEEDER #5 | Fair | Unidentified | 9 | 4D OCB Fdr # 5 T/R 1X Not Checked Yet. |  | 1 | 7:40 | Morning | Thursday | 2017 | 4
5661 | 2017-04-27 07:40 | 2017-01-05 16:56 | 13.8KV 4D FEEDER #5 | Fair | Unidentified | 9 | Checked and found 4D OCB Fdr #5 T/R 4x Counter: 295-299 R/F: 50@1,2,3. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 7:40 | Morning | Thursday | 2017 | 4
5662 | 2017-04-27 09:10 | 2017-04-27 09:10 | 44KV PEMATANG MAIN - RANGAU LINE | Fair | Static Wire | 66 | 09:10 44 KV OCB #2 (44 KV Pematang Main - Rangau) T/R 1x. It was reported broken static wire. Checked and found 44 KV OCB #2 (44 KV Pematang Main - Rangau) T/R 1x Counter: 05-06 R/F: 50@2 ,50N. Patrolled the line & found, broken static wire on pole RGU #14. 14:49 Manually opened 44 KV OCB #2 (44 KV Pematang Main - Rangau) Counter:06-07 For replacing broken static wire on pole RGU#14. 15:40 Manually closed 44 KV OCB #2 (44 KV Pematang Main - Rangau). Cause: Static wire. |  | 1 | 9:10 | Morning | Thursday | 2017 | 4
5663 | 2017-04-27 18:31 | 2017-04-27 18:31 | 5 BRAVO SUBSTATION | Rain and Lightning | Under investigation | 286 | 18:31 5B 115KV OCB #24 T/O Ctr: 309-310 R/F: 87@1, @2. 5B 115KV OCB #23 (In Service). No power to 5B TX-1 ( 5B fdr #1, 5B fdr #2, 5B fdr #3 & 5B fdr #6). 20:16 Manually open 5B fdr #1----->Closed at 20:23. 20:16 Manually open 5B fdr #2----->Closed at 20:27. 20:16 Manually open 5B fdr #3----->Closed at 20:28. 20:16 Manually open 5B fdr #6----->Closed at 20:20. 20:00 Checked and found 5B 115KV OCB #24 T/O. 20:16 Closed 5B 115KV OCB #24 but failed. Checked and found R/F: 86T, then reset. 20:18 Closed 5B 115KV OCB #24, Ok. Cause: Under investigation. Production loss: GS# 4-----> 61 Bbls / 22 wells (5B fdr #1). GS# 4-----> 127Bbls / 17 wells (5B fdr #2). GS# 4-----> 39 Bbls / 08 wells (5B fdr #3). GS# 6-----> 61 Bbls / 22 wells (5B fdr #1). ------------------------------------- + TOTAL: 288 Bbls / 69 Wells. |  | 1 | 18:31 | Afternoon | Thursday | 2017 | 4
5664 | 2017-04-27 18:31 | 2017-04-28 09:01 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 0 | 09:01 Checked and found Recloser 4B-73 T/SO Counter: 188-189. 09:03 Blocked and closed Recloser 4B-73 --> Success and released the block. Cause: Not Patrolled yet. |  | 1 | 18:31 | Afternoon | Thursday | 2017 | 4
5665 | 2017-04-27 18:31 | 2017-03-05 16:39 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found Recl. 4B73 T/LO, Ctr:189-195, R/F: none. Patrolled the line, found @1, B/O pin insulator O/P 3B-27 and 3C-49. Cause: Lightning. |  | 1 | 18:31 | Afternoon | Thursday | 2017 | 4
5666 | 2017-04-27 18:48 | 2017-04-27 18:48 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 493 | 18:48 13.8 KV Minas ACB fdr#1 T/LO ctr:57-60 R/F:51 @1, @2. 02:21 Open LBS #6D-26A, ----> and closed at 02:55. Patrolled the line but nothing found. 02:23 Blocked and closed Minas fdr #1, OK. 03:00 Released block Minas fdr #1 (Will be continue patrol tomorrow morning). |  | 1 | 18:48 | Afternoon | Thursday | 2017 | 4
5667 | 2017-04-27 18:48 | 2017-01-05 18:48 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 493 | Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 18:48 | Afternoon | Thursday | 2017 | 4
5668 | 2017-04-27 19:01 | 2017-04-27 19:01 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Pin Insulator | 508 | 19:01 6D 13.8 KV OCB fdr#5 T/LO. 22:15 Checked and found 6D OCB fdr#5 T/LO Counter: 759-764 R/F: 51@1,@2 and 51N. 22:40 Manually opened Recloser: 5D-10. 22:50 Manually closed LBS:5D-117. 23:11 Blocked and closed 6D OCB fdr #6 --> Success , and released the block. Patrolled the line found @3 broken pin insulator on pole 5D-111. 23:13 Manually blocked and closed Recloser: 5D-10. 00:45 Manually closed LBS: 5D-117. Cause: Broken Pin Insulator. | 1111 | 1 | 19:01 | Night | Thursday | 2017 | 4
5669 | 2017-04-27 19:01 | 2017-04-27 19:01 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 0 | 8D 13.8 KV OCB fdr#7 T/R 1x. Not checked yet. |  | 1 | 19:01 | Night | Thursday | 2017 | 4
5670 | 2017-04-27 19:01 | 2017-01-05 19:01 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 0 | Checked & found 8D fdr#7 T/R 1x Ctr:630-631 R/F:51@2. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 19:01 | Night | Thursday | 2017 | 4
5671 | 2017-04-27 19:01 | 2017-04-27 19:01 | 13.8KV 8C FEEDER #2 | Rain and Lightning | Lightning | 0 | 8C 13.8 KV OCB fdr#2 T/R 1x. Not patrolled yet. |  | 1 | 19:01 | Night | Thursday | 2017 | 4
5672 | 2017-04-27 19:01 | 2017-01-05 16:41 | 13.8KV 8C FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked and found 8C 13.8 KV OCB fdr#2 T/R 1x Counter:509-510 R/F: 50@2. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 19:01 | Night | Thursday | 2017 | 4
5673 | 2017-04-27 19:01 | 2017-04-27 19:01 | 115KV MINAS - 5B LINE | Rain and Lightning | Under investigation | 58 | 19:01 Minas 115KV GCB #51 T/O (115KV Minas - 5B line). Minas 115KV GCB #53 T/O. Respectively load dropped: - 8D fdr #1 load dropped 98A (120-22A). - 8D fdr #2 load dropped 106A (114-8A). - 8D fdr #3 load dropped 38A (70-32A). - 8D fdr #4 load dropped 112A (176-64A). - 8D fdr #5 load dropped 105A (156-51A). - 8D fdr #6 load dropped 178A (191-131A). - 8D fdr #7 load dropped 222A (230-8A). - 8D fdr #8 load dropped 58A (119-61A). - 8D fdr #9 load dropped 130A (180-30A). - 8D fdr #10 load dropped 88A (118-30A). - 8C fdr #1 load dropped 12A (195-183A). - 8C fdr #2 load dropped 32A (49-17A). - 8C fdr #3 load dropped 14A (218-204A) - 6D fdr #6 load dropped 114A (254-140A). - 6DN fdr #4 load dropped 65A (152-87A). - 6DN fdr #6 load dropped 88A (190-102A). - 6DN fdr #2 load dropped 41A (57-16A). - 3D fdr #5 load dropped 45A (155-110A). - 3D fdr #7 load dropped 107A (174-67A). - 4B fdr #4 load dropped 121A (266-145A) - 4D fdr #5 load dropped 15A (159-144A). - 4D fdr #6 load dropped 64A (144-80A). - OKB fdr #2 load dropped 13A (257-244A). - NKB fdr #3 load dropped 14A (166-152A). - NKB fdr #4 load dropped 40A (167-137A). - CKBS fdr #2 load dropped 100A (254-154A). 19:15 Checked and found Minas 115KV R/F: 87L @3, 21G. 20:33 Blocked and closed 115KV Minas GCB #51, OK then released the block. 20:35 Blocked and closed 115KV Minas GCB #53, OK then released the block. 21:07 Checked and found 115KV 6D OCB #21 T/O R/F: 87@3. 21:10 Closed 115KV 6D OCB # 21, failed. Cause: Under investigation. |  | 1 | 19:01 | Night | Thursday | 2017 | 4
5674 | 2017-04-27 19:04 | 2017-04-27 19:04 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 0 | 8D 13.8KV VCB fdr #5 T/R 1X. Not checked yet. |  | 1 | 19:04 | Night | Thursday | 2017 | 4
5675 | 2017-04-27 19:04 | 2017-02-05 19:04 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found 8D fdr#5 T/R 1x Ctr:565-566 R/F:50@1@2. Patrolled the line but found nothing. Cause : Suspected by Lightning. |  | 1 | 19:04 | Night | Thursday | 2017 | 4
5676 | 2017-04-27 19:09 | 2017-04-27 19:09 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 49 | 13.8 KV 6DN fdr #1 TR 1x. Not patrolled yet. |  | 1 | 19:09 | Night | Thursday | 2017 | 4
5677 | 2017-04-27 19:09 | 2017-01-05 16:45 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 49 | Checked and found 13.8 KV 6DN fdr #1 TR 1x Counter: 117-118 R/F: 50@2. Patrolled the line nothing found. Cause: Suspected lightning. |  | 1 | 19:09 | Night | Thursday | 2017 | 4
5678 | 2017-04-27 19:13 | 2017-04-27 19:13 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 183 | 13.8 KV Minas fdr#3 T/R 1X Minas fdr #2 load dropped 87A (139-52A). Minas fdr #4 load dropped 186A (207-21A). Not Checked Yet. |  | 1 | 19:13 | Night | Thursday | 2017 | 4
5679 | 2017-04-27 19:13 | 2017-01-05 19:13 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 183 | Checked & found Minas fdr#3 T/R 1x Ctr:108-109 R/F:51. Patrolled the line but found nothing. Cause : Suspected by Lightning. |  | 1 | 19:13 | Night | Thursday | 2017 | 4
5680 | 2017-04-28 02:58 | 2017-04-28 02:58 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 0 | 8C fdr #5 load dropped 48A (103-55A). Not checked yet. |  | 1 | 2:58 | Night | Friday | 2017 | 4
5681 | 2017-04-28 02:58 | 2017-03-05 16:50 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found 8D OCB fdr#5 T/R 1x, Ctr: 565-566, R/F: 50N, @1. Patrolled the Line, but found nothing. Cause : Suspected by Lightning |  | 1 | 2:58 | Night | Friday | 2017 | 4
5682 | 2017-04-28 15:25 | 2017-04-28 15:25 | 13.8KV 8D FEEDER #3 | Fair | Unidentified | 33 | 15:25 8D OCB Fdr # 3 T/LO. 16:25 Checked and found 8D OCB Fdr # 3 T/LO Counter : 189 - 193 R/F 50 @2,@3 and 51 @2,@3. Patrolled the line nothing found. 17:04 Blocked and Closed 8D OCB Fdr #3 -> Success and then Released the block Cause : Unidentified. |  | 1 | 15:25 | Afternoon | Friday | 2017 | 4
5683 | 2017-04-28 15:25 | 2017-04-28 15:25 | 13.8KV 8D FEEDER #5 | Fair | Lightning | 6 | 8D Fdr # 5 Load dropped 131A ( 156 - 25 A ). 8D Fdr # 4 Load dropped 73A ( 176 -103 A ) WIP. 8D Fdr # 2 Load dropped 54A ( 114 - 60 A ). 8D Fdr # 1 Load dropped 37A ( 120 - 83 A ). Not Checked yet |  | 1 | 15:25 | Afternoon | Friday | 2017 | 4
5684 | 2017-04-28 15:25 | 2017-02-05 15:25 | 13.8KV 8D FEEDER #5 | Fair | Lightning | 6 | Checked & found, 8D OCB fdr #5 T/R 1x ctr: 565-566 R/F: 50N @1. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 15:25 | Afternoon | Friday | 2017 | 4
5685 | 2017-04-29 07:00 | 2017-04-29 07:00 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 110 | 07:00 It was reported no power at well 9D-99, 9D-28, 10D- 24 and 10D-16 D/S 8C Fdr # 1. 14:45 Checked and found Recloser 9D-111 T/SO Counter : 1234 - 1235. Patrolled the line Found nothing. Block and closed Recloser 9D - 111 -> Success and released the block. Cause : Unidentified. |  | 1 | 7:00 | Morning | Saturday | 2017 | 4
5686 | 2017-04-29 09:42 | 2017-04-29 09:42 | CENTRAL DURI POWER PLANT |  |  | - | 09:42 Offline CDGT #5 and then S/D the unit for Stand By. |  | 1 | 9:42 | Morning | Saturday | 2017 | 4
5687 | 2017-04-29 15:07 | 2017-04-29 15:07 | 13.8KV DARLING VCB FEEDER #7 | Fair | Lightning Arrester | 0 | 15:07 Darling Feeder # 7 T/LO. Patrolled the line Found @ 1,2 and 3 Broken L/A on pole NN 15:15 Open By Pass Central Duri Fdr # 13. 15:19 Blocked and Close Darling Fdr # 7 -> Success and then release the block Cause : Broken L/A. |  | 1 | 15:07 | Afternoon | Saturday | 2017 | 4
5688 | 2017-04-29 22:16 | 2017-04-29 22:16 | 5 BRAVO SUBSTATION | Fair | Under investigation | 181 | 22:16 5B 115KV OCB #24 T/O Ctr: 310-311 R/F: 87@1, @2 & 86T. 5B 115KV OCB #23 (In Service). No power to 5B TX-1 ( 5B fdr #1, 5B fdr #2, 5B fdr #3 & 5B fdr #6). 23:10 Manually open 5B fdr #1----->Closed at 23:24. 23:10 Manually open 5B fdr #2----->Closed at 23:10 Manually open 5B fdr #3----->Closed at 00:17. 23:10 Manually open 5B fdr #6----->Closed at 00:08. 23:08 Checked and found 5B 115KV OCB #24 T/O----->Closed at 23:30. 23:36 closed 5B fdr#6, but fail > function test Ok. 23:40 Manually open 4D fdr#4 ----->Closed at 23:36 Cause: Under investigation. Production loss: GS# 4-----> 46 Bbls / 13 wells (5B fdr #1). GS# 4-----> 76 Bbls / 16 wells (5B fdr #2). GS# 4-----> 19 Bbls / 6 wells (5B fdr #3). GS# 6-----> 40 Bbls / 22 wells (5B fdr #1). ------------------------------------- + TOTAL: 181 Bbls / 57 Wells. On April 30, 2017 00:40 5B 115KV OCB #24 T/O Ctr: ....... R/F: 87@1, @2 & 86T. 5B 115KV OCB #23 (In Service). No power to 5B TX-1 ( 5B fdr #1, 5B fdr #2, 5B fdr #3 & 5B fdr #6). 00:40 Checked and found 5B 115KV OCB #24 T/O----->Closed at 01:00. 00:49 Manually open 4D fdr#4 ----->Closed at 02:16. 00:59 Manually open 5B fdr #1----->Closed at 01:02. 00:59 Manually open 5B fdr #2----->Closed at 02:35. 00:59 Manually open 5B fdr #3----->Closed at 01:52. 00:59 Manually open 5B fdr #6----->Closed at 01:03. Cause: Under investigation. | 11111 | 1 | 22:16 | Night | Saturday | 2017 | 4
5689 | 2017-04-29 22:16 | 2017-04-29 22:16 | 13.8KV 5B FEEDER #4 | Fair | Others | 477 | 22:16 5B fdr #4 load dropped 156A (218-62A). On April 30, 2017 00:40 Checked and found Recloser 4B-73 T/SO Counter:190=191. Blocked and closed Recloser 4B-73, Tripped again. (Checked and found spark on @3 Bushing source of Recloser 4B-73). 01:50 Open LBS- 3C-03. Open LBS: KN-36 (4B-fdr #1). Open LBS: 2D-79 (4B-fdr #1). 02:55 Closed LBS 2D-88 feed from 3D fdr#4. Open LBS 3B-22. 04:03 Man. Open 5B OCB fdr#4. By Pass Recl. 4B-73. 04:10 Closed 5B OCB fdr#4. Patrolled the line but found nothing. (Continued in the morning). |  | 1 | 22:16 | Night | Saturday | 2017 | 4
5690 | 2017-04-29 22:16 | 2017-04-30 13:16 | 13.8KV 5B FEEDER #4 | Fair | Others | 477 | 13:16 Patrolled the line but found nothing. 15:00 Closed LBS 2D-79, but spark at intrupter. then open LBS. 15:20 Closed LBS KN-36. Patrolled D/S Recl. 3B-22, but found nothing. 15:25 Closed LBS 3B-22,ok. Cause: Suspected LBS. |  | 1 | 22:16 | Night | Saturday | 2017 | 4
5691 | 2017-04-30 03:52 | 2017-04-30 03:52 | 13.8KV PETAPAHAN FEEDER #2 | Rain | Unidentified | 372 | 03: 52 Petapahan OCB fdr #2 T/R 1X. Petapahan fdr #1 load dropped 52A (89-37A). 15:21 Petapahan OCB fdr #2 T/R 1x Counter: 372-373 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 3:52 | Night | Sunday | 2017 | 4
5692 | 2017-04-30 05:06 | 2017-04-30 05:06 | 5 BRAVO SUBSTATION | Fair | Under investigation | 494 | 05:06 5B 115KV OCB #24 T/O Ctr: ....... R/F: 87@1, @2 & 86T. 5B 115KV OCB #23 (In Service). No power to 5B TX-1 ( 5B fdr #1, 5B fdr #2, 5B fdr #3 & 5B fdr #6). 05:20 Checked and found 5B 115KV OCB #24 T/O----->Closed at 05:26. 05:15 Manually open 5B fdr #1----->Closed at 05:29 05:15 Manually open 5B fdr #2----->Closed at 06:47. 05:15 Manually open 5B fdr #3----->Closed at 06:13. 05:15 Manually open 5B fdr #6----->Closed at 05:30 (WIP). Cause: Under investigation. Production loss: GS# 4-----> 86 Bbls / 13 wells (5B fdr #1). GS# 4-----> 208 Bbls / 16 wells (5B fdr #2). GS# 4-----> 44 Bbls / 6 wells (5B fdr #3). GS# 6-----> 156 Bbls / 28 wells (5B fdr #1). ------------------------------------- + TOTAL: 494 Bbls / 63 Wells. | 111 | 1 | 5:06 | Morning | Sunday | 2017 | 4
5693 | 2017-04-30 05:38 | 2017-04-30 05:38 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 4 | 05:38 It was reported B/O fuse at well Kulim#47 (C.Duri fdr#1). 11:00 Checked & found @2 B/O fuse for 75Kva Tx at well Kulim#47. Perform TTR & Megger 75Kva Tx good condition. Replaced @2 B/O fuse above with the same size & energized the Tx. Cause: Animal (Monkey). |  | 1 | 5:38 | Morning | Sunday | 2017 | 4
5694 | 2017-04-30 06:27 | 2017-04-30 06:27 | 13.8KV DURI COMMUNITY FEEDER #1 | Cloudy | Unidentified | 0 | Community ACB fdr #1 T/R 1 X. Not checked yet. | 1111 | 1 | 6:27 | Morning | Sunday | 2017 | 4
5695 | 2017-04-30 06:27 | 2017-03-05 16:27 | 13.8KV DURI COMMUNITY FEEDER #1 | Cloudy | Unidentified | 0 | Checked & found, Duri Community ACB #25 fdr #1 T/R 1x Ctr: 97-98 R/F: 50N. Patrolled the line but found nothing. Cause: Unidentified. | 1111 | 1 | 6:27 | Morning | Sunday | 2017 | 4
5696 | 2017-04-30 07:21 | 2017-04-30 07:21 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 07:21 It was reported B/O fuse o/p 06-04-03 (C.Duri fdr#14). 09:02 Checked & found @1@2 B/O fuse for 112.5Kva Tx o/p 06-04-03. Replaced @1@2 B/O fuse above with the same size & Energized the Tx. Cause: Animal (Monkey). |  | 1 | 7:21 | Morning | Sunday | 2017 | 4
5697 | 2017-04-30 13:46 | 2017-04-30 13:46 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | C.Duri ACB fdr#14 T/R 1x Ctr:331-332 R/F: 50@1@2. Not patrolled yet. |  | 1 | 13:46 | Afternoon | Sunday | 2017 | 4
5698 | 2017-04-30 13:46 | 2017-01-05 14:39 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | Checked and found C.Duri ACB fdr#14 T/R 1x Ctr:331-332 R/F: 50@1@2. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 13:46 | Afternoon | Sunday | 2017 | 4
5699 | 2017-04-30 18:56 | 2017-04-30 18:56 | 13.8KV KETIGUL FEEDER#1 | Fair | Lightning Arrester | 33 | Ketigul VCB fdr# 1 T/R 1x. Not patrolled yet. |  | 1 | 18:56 | Afternoon | Sunday | 2017 | 4
5700 | 2017-04-30 18:56 | 2017-01-05 16:02 | 13.8KV KETIGUL FEEDER#1 | Fair | Lightning Arrester | 33 | Checked and found Ketigul VCB fdr# 1 T/R 1x Counter: 182-183 R/F: 51@2. Patrolled the line found @2 Broken Lightning Arrester on pole 32-AK-37. Cause: Broken Lightning Arrester. |  | 1 | 18:56 | Afternoon | Sunday | 2017 | 4
5701 | 2017-01-05 02:11 | 2017-01-05 02:11 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Cloudy | Lightning Arrester | 13 | LIBO 13.8KV MSU OCB fdr #2 T/R 1X. Not checked yet. | 1111 | 1 | 2:11 | Night | Thursday | 2017 | 1
5702 | 2017-01-05 02:11 | 2017-02-05 11:12 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Cloudy | Lightning Arrester | 13 | Checked and found, Libo MSU #2 OCB fdr #2 T/R 1x Counter: 279-280 R/F: 51N. Patrolled the line & found, @1 broken Lightning Arrester on pole 29-BY-12A. Cause: Broken Lightning Arrester. | 1111 | 1 | 2:11 | Night | Thursday | 2017 | 1
5703 | 2017-01-05 05:39 | 2017-01-05 05:39 | 13.8KV DARLING VCB FEEDER #3 | Rain and Lightning | Lightning | 0 | 05:39 Darling 13.8KV VCB fdr #3 T/R 1X (C. Duri fdr #10). 14:39 Checked and found Darling VCB fdr #3 T/R 1x Counter:246-247 R/F: 51@1,@2. Patrolled the line but nothing found. Cause: Suspected by Lightning | 1111 | 1 | 5:39 | Morning | Thursday | 2017 | 1
5704 | 2017-01-05 05:39 | 2017-01-05 05:39 | 13.8KV DARLING VCB FEEDER #7 | Rain and Lightning | Lightning | 0 | 05:39 Darling 13.8KV VCB fdr #7 T/R 1x (C.Duri fdr #13). Darling 13.8KV GFPC TX-2 T/R 2x. !4:39 Checked and found, Darling VCB fdr #7 T/R 1x Counter:157-158 R/F: 50@2. Patrolled the line but nothing found. Cause: Suspected Lightning. | 1111 | 1 | 5:39 | Morning | Thursday | 2017 | 1
5705 | 2017-01-05 14:28 | 2017-01-05 14:28 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 54 | Batang OCB fdr #3 T/R 2x. Not checked yet. |  | 1 | 14:28 | Afternoon | Thursday | 2017 | 1
5706 | 2017-01-05 14:28 | 2017-03-05 14:28 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 54 | Checked & found, Batang OCB fdr #3 T/R 1x ctr: 343-345 R/F: 50N @1, @3 Patrolled the line & found, @1, @3 broken Lightning Arrester on Pole 40 AK 03. Cause: Lightning. |  | 1 | 14:28 | Afternoon | Thursday | 2017 | 1
5707 | 2017-01-05 14:44 | 2017-01-05 14:44 | 13.8KV NELLA GFPC | Rain and Lightning | Unidentified (Fuse) | 0 | Nella GFPC T/R 1x (No load dropped on any feeder). Not checked yet. |  | 1 | 14:44 | Afternoon | Thursday | 2017 | 1
5708 | 2017-01-05 14:44 | 2017-04-05 13:44 | 13.8KV NELLA GFPC | Rain and Lightning | Unidentified (Fuse) | 0 | Checked & found, Nella GFPC T/R 2x Ctr: 273-275 R/F: 51N @1,@2,@3. Patrolled the Line & found @1, @2, @3 b/o fuse for 300KVATX at well BKO#66. Replaced the fuse with the same size then energized the TX Cause : Unidentified (Fuse) |  | 1 | 14:44 | Afternoon | Thursday | 2017 | 1
5709 | 2017-01-05 17:35 | 2017-01-05 17:35 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 0 | 8D fdr#11 Load dropped 126A (168-42A). Not checked yet. |  | 1 | 17:35 | Afternoon | Thursday | 2017 | 1
5710 | 2017-01-05 17:35 | 2017-02-05 19:35 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 9E-02 T/R 1x Ctr:1061-1062. Patrolled the line but found nothing. Cause : suspected by Lightning. |  | 1 | 17:35 | Afternoon | Thursday | 2017 | 1
5711 | 2017-01-05 21:10 | 2017-01-05 21:10 | 13.8KV KETIGUL FEEDER#3 | Fair | Animal | 49 | It was reported B/O fuse at well Gulamo#03 (Ketigul fdr#3). Not checked yet. |  | 1 | 21:10 | Night | Thursday | 2017 | 1
5712 | 2017-01-05 21:10 | 2017-02-05 10:32 | 13.8KV KETIGUL FEEDER#3 | Fair | Animal | 49 | 10:32 Checked and found, @3 burnt out fuse for 300 Kva Tx at well Gulamo #03. Perform TTR and Megger found good reading. Replaced burnt out fuse above with same size and energized the Tx. Cause: Animal (Lizard). |  | 1 | 21:10 | Night | Thursday | 2017 | 1
5713 | 2017-02-05 03:00 | 2017-02-05 03:00 | 13.8KV MINAS FEEDER #6 | Fair | Lightning | 74 | Minas ACB fdr#6 T/R 1x, Ctr: 162-163, R/F: 51N. Not checked yet. |  | 1 | 3:00 | Night | Sunday | 2017 | 2
5714 | 2017-02-05 03:00 | 2017-04-05 03:00 | 13.8KV MINAS FEEDER #6 | Fair | Lightning | 74 | Checked & found, Minas ACB #18 fdr #6 T/R 1x ctr: 162-163 R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator on Pole NN. Cause: Lightning. |  | 1 | 3:00 | Night | Sunday | 2017 | 2
5715 | 2017-02-05 05:00 | 2017-02-05 05:00 | KOTABATAK SUBSTATION | Heavy Rain | Substation Failure (C/S) | 437 | 05:00 115Kv Kota Batak C/S T/O. 06:08 Checked & found 115Kv Kota Batak C/S T/O Ctr:262-263 R/F 87T@1@3. Checked Tx & VR Normal Condition. 06:17 Man. Open Kota Batak Fdr#2. 06:20 Closed 115 Kv Kota Batak C/S, but no respond. Checked Tx, VR & control normal operation. 06:38 Closed 115Kv Kota Batak C/S, but no respond. 08:58 Blocked NKB fdr#5 to Cut jumper o/p 37-CW-37 to Separate NKB fdr#5 with NKB fdr#2. 09:30 Closed LBS 37-CW49. 09:40 Blocked & Closed NKB fdr#2. (Load of OKB fdr#2 Move to NKB fdr#2). Cause: Under investigation. |  | 1 | 5:00 | Morning | Sunday | 2017 | 2
5716 | 2017-02-05 06:20 | 2017-02-05 06:20 | 13.8KV PETANI FEEDER #1 | Rain | Animal | 18 | 06:20 It was reported B/O fuse at well Petani#124 (Petani fdr#1). 10:50 Checked and found @1 burnt out fuse for 500 Kva Tx. Replaced burnt out fuse above with the same size and energized the Tx. Cause: Animal (Mouse). |  | 1 | 6:20 | Morning | Sunday | 2017 | 2
5717 | 2017-02-05 09:35 | 2017-02-05 09:35 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Planned Maintenance | 0 | 09:35 Open Fuse O/P 04-7-20 (d/s C.Duri fdr#8). - Replaced @1 Broken Dead end insulator o/p 04-7-20. (S/D Wells 4P-52, 4P-53C, 4P-61B, 4P-63B, 4P-53D). 11:00 Closed the Fuse back. 11:01 Open Fuse O/P 04-7-28 (d/s C.Duri fdr#8). - Replaced @1@2@3 Broken L.A o/p 04-7-28 (S/D Wells 3P-5A, 3P-56A, 3P-66A, 3P-66C, 3P-66D). 11:44 Closed the fuse back. Cause: Planned Maintenance. |  | 1 | 9:35 | Morning | Sunday | 2017 | 2
5718 | 2017-02-05 10:06 | 2017-02-05 10:06 | 13.8KV PEMATANG FEEDER #1 | Fair | Under investigation | 0 | 10:06 Pematang fdr#1 Load dropped 86A (148-62A). 14:45 Checked & found Pematang GS TX#B Down and the Recloser T/O, for Pump Facility. Ensure the TX, visually good condition. 15:05 Man. Closed the Recloser toward TX#B, but Trip again. Rechecked again, found Grounding Resistor was Burn Out. Open Both Isolation Switch of TX#B, and isolate the Gounding Resistor for trouble Shoot. Cause : Under Investigation. |  | 1 | 10:06 | Morning | Sunday | 2017 | 2
5719 | 2017-02-05 14:34 | 2017-02-05 14:34 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 14:34 It was reported B/O fuse O/P 05-M5-A6 (Darlingfdr#4). 15:15 Checked & found b/o @1@2 fuse fose 112.5 KVATX toward CSS Area#6. Replaced the Fuse with the same size, the energized the TX. Cause: Unidentified Fuse. |  | 1 | 14:34 | Afternoon | Sunday | 2017 | 2
5720 | 2017-02-05 18:00 | 2017-02-05 18:00 | CENTRAL DURI POWER PLANT |  |  | - | 18:00 CGT #2 S/U, then On line at 18:40. to restore Power. |  | 1 | 18:00 | Afternoon | Sunday | 2017 | 2
5721 | 2017-02-05 19:50 | 2017-02-05 19:50 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 0 | It was reported B/O Fuse at well 2F-82N.( 3DFdr#2 ). Replaced the fuse with same size then energize the TX. Cause : Lightning. |  | 1 | 19:50 | Night | Sunday | 2017 | 2
5722 | 2017-02-05 19:50 | 2017-05-05 14:40 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked and found @1 B/O Fuse for 300KVA TX.at well 2F-82N ( 3DFdr#2 ). Replaced fuse with the same size then energized the TX. Cause : Lightning. |  | 1 | 19:50 | Night | Sunday | 2017 | 2
5723 | 2017-02-05 19:50 | 2017-02-05 19:50 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 0 | It was reported B/O fuse at well 2F-92 (3D fdr#2). Not checked yet. |  | 1 | 19:50 | Night | Sunday | 2017 | 2
5724 | 2017-02-05 19:50 | 2017-05-05 14:40 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked and found @2 B/O fuse for 300KVA TX at Loc 2F-92, (3D Fdr#2) Replaced the fuse with the same size then energized the TX. Cause : Lightning. |  | 1 | 19:50 | Night | Sunday | 2017 | 2
5725 | 2017-02-05 21:03 | 2017-02-05 21:03 | 13.8KV BATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Batang OCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 21:03 | Night | Sunday | 2017 | 2
5726 | 2017-02-05 21:03 | 2017-03-05 21:03 | 13.8KV BATANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Batang OCB fdr #1 T/R 1x Ctr: 56-57 R/F: 51N Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 21:03 | Night | Sunday | 2017 | 2
5727 | 2017-02-05 21:16 | 2017-02-05 21:16 | 13.8KV CENTRAL DURI FEEDER #2 | Rain and Lightning | Lightning | 0 | C.Duri ACB fdr#2 Load dropped 100A (191-91A). Not checked yet. |  | 1 | 21:16 | Night | Sunday | 2017 | 2
5728 | 2017-02-05 21:16 | 2017-07-05 08:23 | 13.8KV CENTRAL DURI FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found Recl. 08-M1-38 T/R 1x, Ctr: 167-168, R/F: none. Patrolled the Line, found @3 Broken Lightning Arrester o/p 08-L7-26. Cause: Lightning. |  | 1 | 21:16 | Night | Sunday | 2017 | 2
5729 | 2017-02-05 22:13 | 2017-02-05 22:13 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 187 | Bekasap VCB fdr#3 Load dropped 116A (149-33A). Not checked yet. |  | 1 | 22:13 | Night | Sunday | 2017 | 2
5730 | 2017-02-05 22:13 | 2017-03-05 12:13 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Lightning | 187 | Checked & found, Recloser 1-TL-06 T/R 1x ctr: 54-55 Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 22:13 | Night | Sunday | 2017 | 2
5731 | 2017-02-05 22:52 | 2017-02-05 22:52 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Rangau fdr #2 load dropped 130A (150-20A) Not checked yet. |  | 1 | 22:52 | Night | Sunday | 2017 | 2
5732 | 2017-02-05 22:52 | 2017-07-05 08:23 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found Recl. 23-BD-01 T/R 1x, Ctr: 192-193, R/F: none. Patrolled the Line, found @1 Flash Over Deadend o/p 23-BC-02 Cause : Lightning. |  | 1 | 22:52 | Night | Sunday | 2017 | 2
5733 | 2017-03-05 09:00 | 2017-03-05 09:00 | CENTRAL DURI POWER PLANT |  |  | - | 09:00 CGT #4 Off Line, then S/D for Stand by. as power system Dispatch. |  | 1 | 9:00 | Morning | Sunday | 2017 | 3
5734 | 2017-03-05 09:20 | 2017-03-05 09:20 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 0 | 09:20 It was reported B/O fuse o/p 04-05-26 (CD fdr#8). 09:50 Checked & found @1@2@3 b/o fuse for 112.5KVATX. Replaced fuse with the same size, then energized the TX. Cause: Unidentified (Fuse). |  | 1 | 9:20 | Morning | Sunday | 2017 | 3
5735 | 2017-03-05 10:16 | 2017-03-05 10:16 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 16 | 10:16 It was reported b/o Fuse o/p 13-H11-22 (ND fdr#2). 15:15 Checked & found @1@2@3 b/o fuse for 112.5KVATX. Replaced fuse with the same size, the energized the TX. Cause: Unidentified (Fuse). |  | 1 | 10:16 | Morning | Sunday | 2017 | 3
5736 | 2017-03-05 12:50 | 2017-03-05 12:50 | 13.8KV 8D FEEDER #3 | Fair | Planned Maintenance | 0 | 12:50 Man. Opened 8D fdr#3. to avoid water discharge, due to Pumps fail to start after T/O. 14:48 Man. Closed 8D fdr#3. after the Pumps were Running well. Cause : Planed Maintenance (Minas GS-2). (No Production Loss be charge to PGT). |  | 1 | 12:50 | Afternoon | Sunday | 2017 | 3
5737 | 2017-03-05 14:00 | 2017-03-05 14:00 | MINAS POWER PLANT |  |  | - | 14:00 MGT #4 S/U, then On Line to system at 14:20. to restore Power, due to the system Voltage too low. |  | 1 | 14:00 | Afternoon | Sunday | 2017 | 3
5738 | 2017-03-05 17:02 | 2017-03-05 17:02 | 115KV MINAS - LUKUT LINE | Rain and Lightning | Lightning | 0 | Minas Switch Yard 115KV GCB#31,#33 T/R 1x (Mns-Lukut), R/F: 67N-Z 50G (Ground Over current Inst) Not checked yet. |  | 1 | 17:02 | Afternoon | Sunday | 2017 | 3
5739 | 2017-03-05 17:02 | 2017-04-05 17:02 | 115KV MINAS - LUKUT LINE | Rain and Lightning | Lightning | 0 | Checked & found, Minas Switch Yard GCB #31 T/R 1x ctr: 187-188 R/F: 50G. Minas Switch Yard GCB #33 T/R 1x ctr: 324-325 R/F: 50G. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:02 | Afternoon | Sunday | 2017 | 3
5740 | 2017-03-05 17:51 | 2017-03-05 17:51 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 99 | 17:51 SO.Bekasap Feeder T/O. (On Block Position, RIG Job at Sobek #11). 18:00 Man. Closed SoBek fdr but T/O again. (after confirm to RIG PIC). 18:48 Checked & found Sobek fdr T/O, Ctr: 354-356, R/F: 50 @1@2@3 Man. Closed Sobek fdr,OK. (Keep in Block position). Not patrolled yet. |  | 1 | 17:51 | Afternoon | Sunday | 2017 | 3
5741 | 2017-03-05 17:51 | 2017-05-05 10:26 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 99 | Checked & found SOBEK OCB fdr#1 T/R, Ctr: 354-356, R/F: 51N. Patrolled the line, found Flash Over Pin Insulator o/p well P.Bow #19 Cause : Lightning |  | 1 | 17:51 | Afternoon | Sunday | 2017 | 3
5742 | 2017-03-05 17:51 | 2017-03-05 17:51 | 13.8KV 6D FEEDER #6 | Rain and Lightning | Others | 10 | 17:51 6D OCB fdr#6 T/SO. 18:07 Man. Closed, OK. after confirm with TDO team. Not checked yet. |  | 1 | 17:51 | Afternoon | Sunday | 2017 | 3
5743 | 2017-03-05 17:51 | 2017-04-05 17:51 | 13.8KV 6D FEEDER #6 | Rain and Lightning | Others | 10 | Checked & found, 6D OCB fdr #6 did not operated ctr: 598-598 R/F: None. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:51 | Afternoon | Sunday | 2017 | 3
5744 | 2017-03-05 17:51 | 2017-03-05 17:51 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 80 | 17:51 Minas ACB fdr#6 T/LO Ctr:163-165 R/F:51N. 18:07 Block & Closed ACB fdr#6, OK. then released the Block. Not patrolled yet. |  | 1 | 17:51 | Afternoon | Sunday | 2017 | 3
5745 | 2017-03-05 17:51 | 2017-04-05 17:51 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 80 | Checked & found, Minas ACB #18 fdr #6 T/LO 1x ctr: 163-165 R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator on Pole NN. Cause: Lightning. |  | 1 | 17:51 | Afternoon | Sunday | 2017 | 3
5746 | 2017-03-05 17:58 | 2017-03-05 17:58 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 220 | 6DN fdr #6 T/R 1x. 6DN fdr#1 load dropped 41A(142-1A). 6DN fdr#5 load dropped 58A(59-1A). Not checked yet. |  | 1 | 17:58 | Afternoon | Sunday | 2017 | 3
5747 | 2017-03-05 17:58 | 2017-04-05 17:58 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 220 | Checked & found, 6DN OCB fdr #6 T/R 1x ctr: 354-355 R/F: 50@1. Patrolled the line & found, @1 broken Dead-end Insulator on Pole 6D-147. Cause: Lightning. |  | 1 | 17:58 | Afternoon | Sunday | 2017 | 3
5748 | 2017-03-05 18:00 | 2017-03-05 18:00 | CENTRAL DURI POWER PLANT |  |  | - | 18:00 CGT #5 S/U, then Online to system at 18:25. to restore power. |  | 1 | 18:00 | Afternoon | Sunday | 2017 | 3
5749 | 2017-03-05 18:11 | 2017-03-05 18:11 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 173 | SO.Balam VCB fdr#4 T/R 1x. SO.Balam fdr#1 load dropped 76A(120-44A). So.Balam fdr#3 Load dropped 33A(100-64A). Not checked yet. |  | 1 | 18:11 | Afternoon | Sunday | 2017 | 3
5750 | 2017-03-05 18:11 | 2017-03-05 18:11 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 177 | Nella fdr#1 load dropped 212A(269-57A). Nella fdr#2 load dropped 45A(86-41A). Not checked yet. |  | 1 | 18:11 | Afternoon | Sunday | 2017 | 3
5751 | 2017-03-05 18:11 | 2017-04-05 10:00 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 177 | Checked & found, Nella GFPC T/R 1x ctr: 724-725 R/F: 51N Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 18:11 | Afternoon | Sunday | 2017 | 3
5752 | 2017-03-05 18:22 | 2017-03-05 18:22 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 36 | 6D OCB fdr#1 T/R 1x. 6D fdr#2 load dropped 179A(234-5A). 6D fdr#3 load dropped 270A(350-80A) WIP. Not checked yet |  | 1 | 18:22 | Afternoon | Sunday | 2017 | 3
5753 | 2017-03-05 18:22 | 2017-04-05 18:22 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 36 | Checked & found, 6D OCB fdr #1 T/R 1x ctr: 323-324 R/F: 51 @1. Patrolled the line & found, @1 broken Dead-end Insulator on Pole 5B-121. Cause: Lightning. |  | 1 | 18:22 | Afternoon | Sunday | 2017 | 3
5754 | 2017-03-05 18:22 | 2017-03-05 18:22 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 14 | 6D fdr#5 load dropped 110A9229-119A). 6D fdr#4 load dropped 187A(187-0A)(WIP Trip) 6D fdr#6 load dropped 120A(253-133A)(WIP Trip). Not checked yet. |  | 1 | 18:22 | Afternoon | Sunday | 2017 | 3
5755 | 2017-03-05 18:22 | 2017-04-05 18:22 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 14 | Checked & found, 6D OCB fdr #5 T/R 1x ctr: 769-770 R/F: 51. Patrolled the line & found, @1 broken Dead-end Insulator on Pole 5D-09. Cause: Lightning. |  | 1 | 18:22 | Afternoon | Sunday | 2017 | 3
5756 | 2017-03-05 18:58 | 2017-03-05 18:58 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 0 | Menggala fdr#1 load dropped 94A(143-49A). Not checked yet. |  | 1 | 18:58 | Afternoon | Sunday | 2017 | 3
5757 | 2017-03-05 18:58 | 2017-04-05 15:33 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found Recl. 19-AO-01 T/R, Ctr: 467-468, R/F: 51N @2. Patrolled the Line, but found nothing. Cause : Suspected by Lightning. |  | 1 | 18:58 | Afternoon | Sunday | 2017 | 3
5758 | 2017-03-05 18:58 | 2017-03-05 18:58 | 44KV PEMATANG MAIN - PETANI LINE | Rain and Lightning | Lightning | 305 | 44Kv Line Pematang Main-Petani OCB#1 T/r 1x. Not checked yet. |  | 1 | 18:58 | Afternoon | Sunday | 2017 | 3
5759 | 2017-03-05 18:58 | 2017-06-05 17:08 | 44KV PEMATANG MAIN - PETANI LINE | Rain and Lightning | Lightning | 305 | Checked & found PMT Main 44KV OCB#1 T/R 1x, Ctr: 4001-4002, R/F: 50N. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 18:58 | Afternoon | Sunday | 2017 | 3
5760 | 2017-03-05 19:09 | 2017-03-05 19:09 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Unidentified | 0 | Petani OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 19:09 | Night | Sunday | 2017 | 3
5761 | 2017-03-05 19:09 | 2017-07-05 08:23 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found PTN OCB fdr#2 T/R 1x, Ctr: 220-221, R/F: 50N. Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 19:09 | Night | Sunday | 2017 | 3
5762 | 2017-03-05 19:22 | 2017-03-05 19:22 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 0 | Ketigul OCB fdr#2 Load dropped 164A(191-27A). Not checked yet. |  | 1 | 19:22 | Night | Sunday | 2017 | 3
5763 | 2017-03-05 19:22 | 2017-06-05 14:35 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 0 | Checked & found Recl. 29-AL-03, Ctr: 117 (not change), R/F: n.a. Patrolled the Line, but found nothing. Cause: Un identified |  | 1 | 19:22 | Night | Sunday | 2017 | 3
5764 | 2017-04-05 07:10 | 2017-04-05 07:10 | MINAS POWER PLANT | Fair | Under investigation | 0 | MGT#3 T/O by Alarm Excessive Vibration. Cause : Under Investigation. (Broken Gen. brush and slip ring). |  | 1 | 7:10 | Morning | Wednesday | 2017 | 4
5765 | 2017-04-05 09:30 | 2017-04-05 09:30 | 13.8KV BEKASAP FEEDER #6 | Fair | Planned Maintenance | 252 | 09:30 Manual Open Bekasap OCB fdr#6. To Replace Dead end and pin insulator. 11:53 Man Closed Bekasap OCB fdr#6, After Finished the Job. Cause: Planned Maintenance. | 1111 | 1 | 9:30 | Morning | Wednesday | 2017 | 4
5766 | 2017-04-05 11:34 | 2017-04-05 11:34 | 13.8KV 6DN FEEDER #2 | Fair | Lightning | 125 | 6DN 13.8KV OCB#2 fdr#2 T/R . 6DN fdr#1 load dropped 165A (193-28A). Not checked yet. |  | 1 | 11:34 | Morning | Wednesday | 2017 | 4
5767 | 2017-04-05 11:34 | 2017-06-05 05:34 | 13.8KV 6DN FEEDER #2 | Fair | Lightning | 125 | Checked & found 6DN fdr#2 T/R 1x Ctr:302-303 R/F:51@1@2. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 11:34 | Morning | Wednesday | 2017 | 4
5768 | 2017-04-05 14:01 | 2017-04-05 14:01 | 13.8KV PETANI FEEDER #2 | Fair | Planned Maintenance | 3 | 14:01 Block Petani fdr#2 Open HLC to Repair hot spot o/p 32AW32.toward well Petani 35. 14:53 Close HLC o/p 32AW32.toward well Petani 35. Release block petani fdr#2. |  | 1 | 14:01 | Afternoon | Wednesday | 2017 | 4
5769 | 2017-04-05 15:43 | 2017-04-05 15:43 | 13.8KV CENTRAL DURI FEEDER #7 | Cloudy | Voltage regulator failure | 943 | 15:43 C.Duri 13.8KV ACB#33 fdr#7 T/LO. 16:14 C.Duri 13.8KV ACB#33 fdr#7 T/R. 16:17 C.Duri 13.8KV ACB#33 fdr#7 T/R. 16:23 C.Duri 13.8KV ACB#33 fdr#7 T/R. 16:34 C.Duri 13.8KV ACB#33 fdr#7 T/R. 16:35 C.Duri 13.8KV ACB#33 fdr#7 T/R. 16:39 C.Duri 13.8KV ACB#33 fdr#7 T/R 16:40 C.Duri 13.8KV ACB#33 fdr#7 T/LO. 17:34 C.Duri 13.8KV ACB#33 fdr#7 Closes. 18:00 Closed LBS 03-03-44. 18:37 C.Duri ACB fdr # 7 T/O ( in block position ) Patrolled the line but found nothing. 19:21 Block and Closed C.Duri Fdr # 7. 19:22 Open LBS 03-03-44 19:22 C.Duri fdr # 7 T/O. 20:24 Open LBS 03-07-25. 20:32 Block and closed C.Duri Fdr # 7 , but trip again. 20:51 By Pass Recl 03-03-42 with unplug control Recl. 21:01 Closed LBS 03-03-02 feed from C.Duri Fdr # 6. 21:30 Unplug Recl 09-Q1-06. 21:35 Open Recl 03-03-42 21:43 Closed LBS 09-Q1-01 feed from C.Duri Fdr#4. 21:45 Closed LBS 03-03-44. 21:50 Closed LBS 04-00-27. 21:59 Closed Recl 03-01-39. Cause : Under Investigation. | 1111 | 1 | 15:43 | Afternoon | Wednesday | 2017 | 4
5770 | 2017-04-05 15:43 | 2017-07-05 08:23 | 13.8KV CENTRAL DURI FEEDER #7 | Cloudy | Voltage regulator failure | 943 | Checked & found CD ACB fdr#7 T/R 9x, Ctr: 487- 496, R/F: 51N @1. Patrolled the Line, found Failure VR o/p 03-07-24, and @1 broken LA. Cause : Voltage regulator failure | 1111 | 1 | 15:43 | Afternoon | Wednesday | 2017 | 4
5771 | 2017-04-05 17:00 | 2017-04-05 17:00 | 13.8KV 4D FEEDER #4 | Fair | Planned Maintenance | 0 | 17:00 4D 13.8KV OCB#4 Manual open. GS#4 operator Requested, pipe line leak at injection well 4D-59. 24:00 Manual Close 4D 13.8 KV OCB#4. Cause: planned maintenance Prod. loss not be charge to PGT. |  | 1 | 17:00 | Afternoon | Wednesday | 2017 | 4
5772 | 2017-04-05 18:46 | 2017-04-05 18:46 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse at well Kopar # 38 ( Rokan Fdr # 2 ). Not checked yet |  | 1 | 18:46 | Afternoon | Wednesday | 2017 | 4
5773 | 2017-04-05 18:46 | 2017-06-05 17:09 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified (Fuse) | 0 | Checked & found, @3 b/o fuse for 150KVATX at well Kopar#38 (Rokan fdr#2). Replaced the fuse with the same size, then Energized the TX. Cause : Unidentified (Fuse) |  | 1 | 18:46 | Afternoon | Wednesday | 2017 | 4
5774 | 2017-04-05 23:42 | 2017-04-05 23:42 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning | 55 | Sintong Feeder # 2 T/R 1X. Not checked yet. |  | 1 | 23:42 | Night | Wednesday | 2017 | 4
5775 | 2017-04-05 23:42 | 2017-05-05 12:06 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning | 55 | Checked & found Sintong OCB fdr#2 T/R, Ctr: 456-457, R/F: 51N. Patrolled the Line, found @1 broken Lightning Arrester o/tp Well Sintong #24. Cause : Lightning Arrester |  | 1 | 23:42 | Night | Wednesday | 2017 | 4
5776 | 2017-05-05 01:13 | 2017-05-05 01:13 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 53 | Bekasap fdr#6 T/R 1x. Not checked yet. |  | 1 | 1:13 | Night | Friday | 2017 | 5
5777 | 2017-05-05 01:13 | 2017-06-05 17:48 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 53 | Checked & found BKS VCB fdr#6 T/R 1x, Ctr: 352-353, R/F: 51 @1. Patrolled the Line, found @1 Broken Pin Insulator o/p 38-BF-02 Cause : Pin Insulator |  | 1 | 1:13 | Night | Friday | 2017 | 5
5778 | 2017-05-05 01:27 | 2017-05-05 01:27 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Pin Insulator | 60 | Petani fdr#1 T/R 1x. Not checked yet. |  | 1 | 1:27 | Night | Friday | 2017 | 5
5779 | 2017-05-05 01:27 | 2017-07-05 15:30 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Pin Insulator | 60 | Checked & found PTN OCB fdr#1 T/R 2x, Ctr: 229-231, R/F: 50N @1. Patrolled the Line, found @1 broken pin insulator o/p 33-AY-40. Cause : Pin Insulator |  | 1 | 1:27 | Night | Friday | 2017 | 5
5780 | 2017-05-05 03:51 | 2017-05-05 03:51 | 13.8KV MENGGALA FEEDER #1 | Rain | Unidentified | 62 | Menggala fdr#1 Load dropped 102A (162-60A). Not checked yet. |  | 1 | 3:51 | Night | Friday | 2017 | 5
5781 | 2017-05-05 03:51 | 2017-06-05 16:55 | 13.8KV MENGGALA FEEDER #1 | Rain | Unidentified | 62 | Checked & found the Reclosers 19-AN-01 & 19-AN-04 Normal, Ctr: not change, R/F: n.a.. Patrolled the line, found nothing. Cause : Unidentified. |  | 1 | 3:51 | Night | Friday | 2017 | 5
5782 | 2017-05-05 03:56 | 2017-05-05 03:56 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Rain and Lightning | Unidentified | 0 | 03:56 It was reported Dumai fdr#1 T/O. 04:45 Checked & found Dumai fdr#1 T/O Ctr:259-260 R/F 51@2@3. Patrolled the line but found nothing. 06:00 Blocked & closed Dumai fdr#1, ok, then release the block. Cause: Unidentified. |  | 1 | 3:56 | Night | Friday | 2017 | 5
5783 | 2017-05-05 04:57 | 2017-05-05 04:57 | 13.8KV SINTONG FEEDER #1 | Rain | Lightning | 29 | Sintong fdr#1 Load dropped 32A (91-59A). Not checked yet. |  | 1 | 4:57 | Morning | Friday | 2017 | 5
5784 | 2017-05-05 04:57 | 2017-06-05 09:30 | 13.8KV SINTONG FEEDER #1 | Rain | Lightning | 29 | Checked & found Recl. 26-AE-22 T/R 1x, Ctr: 355-356, R/F : 50 @1@2@3 Patrolled the Line, but found nothing. Cause: Lightning |  | 1 | 4:57 | Morning | Friday | 2017 | 5
5785 | 2017-05-05 10:30 | 2017-05-05 10:30 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 0 | 10:30 It was reported Low Voltage o/p 04-04-15A (CD fdr#8). 15:00 Checked & found @1 b/o fuse for 112.5 KVATX. Replaced the fuse with the same size (3.1SF), the Energized the TX. Cause: Unidentified (fuse). |  | 1 | 10:30 | Morning | Friday | 2017 | 5
5786 | 2017-05-05 11:42 | 2017-05-05 11:42 | 13.8KV SINTONG FEEDER #2 | Fair | Others | 285 | 11:42 It was reported no power at some wells Benar#31,#50,#51,#36 ( Sintong fdr#2). 15:42 Checked & found Recl. 29-AY-16 T/Lo, Ctr: 90-94, R/F: NA. also found the Wood was Short to Cross arm, the Dismantled the wood above. the Blocked & Closed the Recloser, the released the block. Cause: Other. (wood, batang ubi at cross arm). |  | 1 | 11:42 | Morning | Friday | 2017 | 5
5787 | 2017-05-05 14:25 | 2017-05-05 14:25 | CENTRAL DURI POWER PLANT |  |  | - | 14:25 CGT#4 S/U then Online the unit at 14:45. to restore power, CGT #5 wil be S/D. |  | 1 | 14:25 | Afternoon | Friday | 2017 | 5
5788 | 2017-05-05 14:31 | 2017-05-05 14:31 | 13.8KV RANGAU FEEDER #1 | Fair | Planned Maintenance | 0 | 14:31 Open Hot Line Clampt o/tp well Rangau #2 (Rangau fdr#1) to Repair Hot Spot at pole above. 15:06 Closed back the HLC, after finished the Job. Cause: Planed maintenance. |  | 1 | 14:31 | Afternoon | Friday | 2017 | 5
5789 | 2017-05-05 17:10 | 2017-05-05 17:10 | CENTRAL DURI POWER PLANT |  |  | - | 17:10 CGT5 Off Line the S/D for standby. will Servicing transformer, oil purification. |  | 1 | 17:10 | Afternoon | Friday | 2017 | 5
5790 | 2017-05-05 18:20 | 2017-05-05 18:20 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Unidentified | 3 | S.Balam fdr#1 Load dropped 83A (114-83A) S.Balam fdr#2 Load dropped 92A (94-2A) S.Balam fdr#3 Load dropped 100A(186-86A) GFPC S.Balam fdr#1 T/R 1x. Ground fault Alarm at S.alam fdr#1 Not checked yet. |  | 1 | 18:20 | Afternoon | Friday | 2017 | 5
5791 | 2017-05-05 18:20 | 2017-07-05 14:26 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Unidentified | 3 | Checked & found Recl.16-Z-41 T/R 1x, Ctr: 3178-3179, R/F: 50 @1@2. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 18:20 | Afternoon | Friday | 2017 | 5
5792 | 2017-05-05 18:20 | 2017-05-05 18:20 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Unidentified | 26 | S.Balam fdr #4 load drop 94 A ( 186 - 94 ). Not checked yet. |  | 1 | 18:20 | Afternoon | Friday | 2017 | 5
5793 | 2017-05-05 18:20 | 2017-06-05 13:59 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Unidentified | 26 | Checked & found Recl. 16-AB-02 T/R 1x, Ctr: 439-442, R/F: 51N Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 18:20 | Afternoon | Friday | 2017 | 5
5794 | 2017-06-05 20:19 | 2017-06-05 20:19 | 13.8KV BATANG FEEDER #3 | Rain | Lightning | 52 | 20:19 Batang Feeder # 3 T/R 1X. Not checked yet. |  | 1 | 20:19 | Night | Monday | 2017 | 6
5795 | 2017-06-05 20:19 | 2017-07-05 17:04 | 13.8KV BATANG FEEDER #3 | Rain | Lightning | 52 | Checked & found Batang OCB fdr#3 T/R 1x, Ctr: 345-346, R/F: 51N. Patrolled the Lne, found @1 broken Pin Insulator, o/p (none). Cause : Lightning |  | 1 | 20:19 | Night | Monday | 2017 | 6
5796 | 2017-06-05 21:11 | 2017-06-05 21:11 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 25 | C. Duri fdr #1 load dropped 31A (124-93A). Not checked yet. |  | 1 | 21:11 | Night | Monday | 2017 | 6
5797 | 2017-06-05 21:11 | 13/05/2017 20:11 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 25 | Checked and found Recloser 38-AS-09 T/R 5x Ctr: 206-211 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 21:11 | Night | Monday | 2017 | 6
5798 | 2017-06-05 21:36 | 2017-06-05 21:36 | 13.8KV NORTH DURI FEEDER #5 | Rain | Lightning | 0 | N.Duri fdr#5 Load dropped 38A (46-8A). Not checked yet. |  | 1 | 21:36 | Night | Monday | 2017 | 6
5799 | 2017-06-05 21:36 | 13/05/2017 20:00 | 13.8KV NORTH DURI FEEDER #5 | Rain | Lightning | 0 | Checked and found Recloser 12-E11-01 T/R 1x Ctr: 225-226 Patrolled the line but found nothing. Cause: Ligthning. |  | 1 | 21:36 | Night | Monday | 2017 | 6
5800 | 2017-07-05 05:29 | 2017-07-05 05:29 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 52 | 05:29 It wasreported b/o fuses at well Kulim #67. 11:40 Checked and found @1 b/o fuse for 150Kva TX. Performed TTR test and megger the TX, found Low Mega Ohm reading TX. Cause: TX failure. (The TX will be replaced soon). | 11111 | 1 | 5:29 | Morning | Wednesday | 2017 | 7
5801 | 2017-07-05 05:29 | 2017-09-05 15:20 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 52 | 15:00 Replaced 150Kva TX with same size at well Kulim #67 d/s C. Duri fdr #1. Cause: TX failure. | 11111 | 1 | 5:29 | Morning | Wednesday | 2017 | 7
5802 | 2017-07-05 06:36 | 2017-07-05 06:36 | 13.8KV KETIGUL FEEDER#2 | Rain | Lightning | 24 | 06:39 Ketigul Feeder #2 T/R 1X. Not Checked yet. 16:00 Checked & found Ketigul VCB fdr#2 T/R 1x Ctr: 130-131 R/F: 51N. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 6:36 | Morning | Wednesday | 2017 | 7
5803 | 2017-07-05 11:42 | 2017-07-05 11:42 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | 0 | CD fdr#1 Load dropped 48A(131-83A). Not checked yet. |  | 1 | 11:42 | Morning | Wednesday | 2017 | 7
5804 | 2017-07-05 11:42 | 13/05/2017 20:13 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | 0 | Checked and found Recloser 38-AS-09 T/R 5x Ctr: 206-211 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 11:42 | Morning | Wednesday | 2017 | 7
5805 | 2017-07-05 13:11 | 2017-07-05 13:11 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 26 | 13:11 It was reported no power to WIP d/s 8C fdr #4. (8C RTU Analog Module error) 14:00 Checked and found 8C OCB fdr #4 T/R 1X ctr:592-593 R/F:....... Not patrolled yet. | 1111 | 1 | 13:11 | Afternoon | Wednesday | 2017 | 7
5806 | 2017-07-05 13:11 | 2017-09-05 16:50 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 26 | Checked & found 8C VCB fdr#4 T/R 1x, Ctr: 592-593, R/F: 51 @1@2@3. Patrolled the Line, found @1@2@3 broken Pin insulator o/p 8D-59. Cause : Lightning | 1111 | 1 | 13:11 | Afternoon | Wednesday | 2017 | 7
5807 | 2017-08-05 05:48 | 2017-08-05 05:48 | 13.8KV CENTRAL DURI FEEDER #4 | Rain | Lightning | 0 | 05:48 C.Duri feeder # 4 T/R 1X Ctr:477-478 R/F:51N. Not patrolled yet. |  | 1 | 5:48 | Morning | Saturday | 2017 | 8
5808 | 2017-08-05 05:48 | 13/05/2017 20:00 | 13.8KV CENTRAL DURI FEEDER #4 | Rain | Lightning | 0 | Checked and found Recloser CDRSG-13.8ACB21 T/R 1x Ctr: 477-478 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 5:48 | Morning | Saturday | 2017 | 8
5809 | 2017-09-05 01:38 | 2017-09-05 01:38 | 13.8KV PETAPAHAN FEEDER #1 | Rain and Lightning | Others | 325 | 01:38 Petapahan 13.8KV OCB fdr#1 T/R Petapahan fdr#2 load dropped 185A (220-35A). 10:57 Checked & found Petapahan OCB fdr#1 T/R 1x, Ctr: 242-243, R/F: 51 @3. Patrolled the Line, found Kite and Yarn on @3 o/p 29-CY-25. Cause : Others |  | 1 | 1:38 | Night | Tuesday | 2017 | 9
5810 | 2017-09-05 08:58 | 2017-09-05 08:58 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | 0 | C. Duri fdr #1 load dropped 43A (131-88A). Not checked yet. | 1111 | 1 | 8:58 | Morning | Tuesday | 2017 | 9
5811 | 2017-09-05 08:58 | 13/05/2017 19:11 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | 0 | Checked and found Recloser 38-AS-09 T/R 5x Ctr: 206-211 Patrolled the line but found nothing. Cause: Lightning. | 1111 | 1 | 8:58 | Morning | Tuesday | 2017 | 9
5812 | 2017-09-05 09:30 | 2017-09-05 09:30 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 76 | Ketigul 13.8KV VCB fdr #2 T/R 1X. Not checked yet. | 11111 | 1 | 9:30 | Morning | Tuesday | 2017 | 9
5813 | 2017-09-05 09:30 | 2017-10-05 09:30 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 76 | Checked & found, Ketigul VCB fdr #2 T/R ctr: 169-169 (did not operate) R/F: 51N @1. Patrolled the line & found, @1 broken Dead-end Insulator on Pole NN near well Pager #30. Cause: Dead-end Insulator. | 11111 | 1 | 9:30 | Morning | Tuesday | 2017 | 9
5814 | 2017-09-05 10:37 | 2017-09-05 10:37 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Animal | 7 | 10:37 It was reported b/o fuse at well Pagar #15. 12:14 checked and found @3 b/o fuse and broken FCO for 150Kva TX. Replaced b/o fuse and FCO above with same size, then energized the TX. Cause: Animal (squirrel ). | 111 | 1 | 10:37 | Morning | Tuesday | 2017 | 9
5815 | 2017-09-05 11:00 | 2017-09-05 11:00 | 13.8KV DURI FIELD FEEDER #2 | Cloudy | Unidentified | 0 | Duri field 13.8KV VCB fdr #2 T/R 1X. Not checked yet. | 1111 | 1 | 11:00 | Morning | Tuesday | 2017 | 9
5816 | 2017-09-05 11:00 | 13/05/2017 19:11 | 13.8KV DURI FIELD FEEDER #2 | Cloudy | Unidentified | 0 | Checked and found 13.8 KV ACB #42 T/R 1x Ctr: 993-994 R/F: 51 @1 Patrolled the line but found nothing. Cause : Unidentified | 1111 | 1 | 11:00 | Morning | Tuesday | 2017 | 9
5817 | 2017-09-05 14:26 | 2017-09-05 14:26 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 5 | 14:26 It was reported b/o fuses o/p 06-S3-03. 15:00 Checked and found @3 b/o fuse for 112.5Kva TX. Replaced b/o fuse above with same size, then energized the TX. Cause: Unidentified (fuse). 16:30 It was reported unbalance voltage o/p 06-S3-03. Not checked yet. | 1111 | 1 | 14:26 | Afternoon | Tuesday | 2017 | 9
5818 | 2017-09-05 14:26 | 13/05/2017 19:11 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 5 | Checked and found B/O fuse @1, o/p 06-S3-03 Patrolled the line but found nothing. Cause: Unidentified. | 1111 | 1 | 14:26 | Afternoon | Tuesday | 2017 | 9
5819 | 2017-09-05 15:41 | 2017-09-05 15:41 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 0 | 15:41 It was reported b/o fuse at well Pager #12. 17:43 Checked and found @1, @2 b/o fuses for 225KVA TX. Replaced b/o fuse above with same size, then energized the TX. Cause: Animal (Monkey). | 1111 | 1 | 15:41 | Afternoon | Tuesday | 2017 | 9
5820 | 2017-09-05 22:52 | 2017-09-05 22:52 | 13.8KV CENTRAL DURI FEEDER #14 | Heavy Rain | Lightning | 0 | CD ACB fdr#2 T/R 2x, Ctr: 332-334, R/F 51N @1@2. Not checked yet. |  | 1 | 22:52 | Night | Tuesday | 2017 | 9
5821 | 2017-09-05 22:52 | 13/05/2017 19:11 | 13.8KV CENTRAL DURI FEEDER #14 | Heavy Rain | Lightning | 0 | Checked and found 13.8 KV ACB #27 T/R 2x Ctr: 332-334 R/F: 51N Patrolled the line and found Flash Over Bushing @1 at Recloser o/p 06-P8-02 Cause : Lightning |  | 1 | 22:52 | Night | Tuesday | 2017 | 9
5822 | 2017-09-05 23:55 | 2017-09-05 23:55 | 13.8KV PEMATANG FEEDER #2 | Rain | Transformer Failure | 142 | 23:55 It was reported no power at well Pematang #88. Not checked yet. |  | 1 | 23:55 | Night | Tuesday | 2017 | 9
5823 | 2017-09-05 23:55 | 2017-10-05 01:30 | 13.8KV PEMATANG FEEDER #2 | Rain | Transformer Failure | 142 | 01:30 Checked & found unbalance voltage for 150 KVA TX at well Pematang #88 (PMT fdr#2) Performed TTR test & megger found Low megger reading. 15:23 Replaced 150 Kva Tx failure with 300 Kva and energized the Tx . Cause: Tx failure (Low megger reading). |  | 1 | 23:55 | Night | Tuesday | 2017 | 9
5824 | 2017-10-05 03:36 | 2017-10-05 03:36 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Static Wire | 818 | 03:36 5B OCB Fdr#2 T/SO. 5B fdr#1 load dropped 21A (182-161A). 5B fdr#4 load dropped 33A (187-154A). 5B fdr#6 load dropped 123A (190-67A). 08:00 Patrolled the line found broken static wire on pole 5C-07. Replaced 14 spans broken static wire between poles 5C-07 to on pole 5C-21. 15:54 Blocked and closed 5B fdr #2 --> OK and then released the block. Closed LBS 5C-01. Cause: Broken Static wire. (GS6: Prod. Loss 92 Bbls, 7 Wells) | 11111 | 1 | 3:36 | Night | Thursday | 2017 | 10
5825 | 2017-10-05 03:50 | 2017-10-05 03:50 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 456 | 03:50 6DN OCB Fdr#1 T/LO 05:52 Block and close 6DN OCB fdr#1, Then release the Block. 05:53 6DN OCB Fdr#1 T/R 1X 06:09 6DN OCB Fdr#1 T/SO 11:06 Patrolled the Line found, @2 broken Pin insulator o/p 5D-15. Replaced the Pin above. Blocked & Closed 6DN OCB fdr#1 Not Checked yet. (GS3 Prod Loss: 409Bbls, 23 Wells) |  | 1 | 3:50 | Night | Thursday | 2017 | 10
5826 | 2017-10-05 03:50 | 13/05/2017 20:21 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 456 | Checked & found 6DN OCB fdr#1 T/LO, Ctr: 118-128, R/F 51 N @2. Patrolled the Line, found @2 broken Pin support insulator o/p 5D-15. Cause : Lightning |  | 1 | 3:50 | Night | Thursday | 2017 | 10
5827 | 2017-10-05 03:53 | 2017-10-05 03:53 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 0 | 4D fdr#5 load dropped 134A (174-40A).\ 4D fdr#4 load dropped 30A (46-16A). Not checked yet. |  | 1 | 3:53 | Night | Thursday | 2017 | 10
5828 | 2017-10-05 03:53 | 13/05/2017 19:30 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked and found Recloser 4D-14A T/R 1x, Ctr: 9-10. Patrolled the but found nothing. Cause: Lightning. |  | 1 | 3:53 | Night | Thursday | 2017 | 10
5829 | 2017-10-05 03:59 | 2017-10-05 03:59 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 53 | Minas ACB fdr#1 T/R 2x, Ctr: 60-62, R/F: 51 @2@3. Not checked yet. (GS3 Prod Loss: 52Bbls, 20 Wells) |  | 1 | 3:59 | Night | Thursday | 2017 | 10
5830 | 2017-10-05 03:59 | 13/05/2017 19:30 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 53 | Checked and found 13.8 KV, Minas fdr#1 T/R 2x, Ctr: 60-62, R/F: 51 @2, @3 Patrolled the line and found broken pin o/p 7D-18. Cause: Lightning. |  | 1 | 3:59 | Night | Thursday | 2017 | 10
5831 | 2017-10-05 04:11 | 2017-10-05 04:11 | 8 DELTA SUBSTATION | Rain and Lightning | Circuit Breaker | 1463 | 04:11 115KV 8D C/S T/O Counter: 139-140 R/F: 51N @1,2,3. (8DFdr#6,Fdr#7,Fdr#8 no power). 05:48 Checked & found any spark at Bushing of 8D OCB fdr#6 Open the Isolation Switches of 8D OCB fdr#6 Man. Closed 8D C/S. 04:48 Manual opened 8D OCB fdr#1 . 07:05 Manual Closed Back. (Minas GS1 requested, to Maintain Level tank due to 8D fdr#6 T/SO.). (GS1 Prod. Loss:76Bbls, 21 Wells) 04:48 Manual opened 8D OCB fdr#2 . 07:05 Manual Closed Back. Cause: Planed maintenance (Minas GS1 requested, to Maintain Level tank due to 8D fdr#6 T/SO.). (GS1 Prod Loss: 133Bbls, 17Wells). 04:48 Manual opened 8D OCB fdr#10 . 08:17 Manual Closed Back. Cause: Planed maintenance (Minas GS1 requested, to Maintain Level tank due to 8D fdr#6 T/SO.). (GS1 Prod Loss: 76Bbls, 21Wells). 05:05 Manual opened 8D OCB fdr#11 . 09:03 Manual Closed Back. Cause: Planed maintenance (Minas GS1 requested, to Maintain Level tank due to 8D fdr#6 T/SO.). (GS1 Prod Loss: 279Bbls, 39Wells). 05:05 Manual opened MNS ACB fdr#4 . 07:43 Manual Closed Back. Cause: Planed maintenance (Minas GS1 requested, to Maintain Level tank due to 8D fdr#6 T/SO.). (GS1 Prod Loss: 224Bbls, 32Wells) (GS2 Prod Loss: 109Bbls, 13Wells) 05:05 Manual opened MNS ACB fdr#2 . 05:58 Manual Closed Back. Cause: Planed maintenance (Minas GS1 requested, to Maintain Level tank due to 8D fdr#6 T/SO.). (GS1 Prod Loss:31 Bbls, 14Wells). (GS3 Prod Loss:9 Bbls, 4 Wells). 05:05 Manual opened 8D OCB fdr#5 . 07:57 Manual Closed Back. Cause: Planed maintenance (Minas GS1 requested, to Maintain Level tank due to 8D fdr#6 T/SO.). (GS1 Prod. Loss: 116Bbls, 16Wells). 05:30 Manual opened 8C OCB fdr#1. 13:02 Manual Closed Back. Cause: Planed maintenance (Minas GS1 requested, to Maintain Level tank due to 8D fdr#6 T/SO.). (GS1 Prod Loss: 322Bbls, 27Wells). GS2 Prod Loss: 102Bbls, 5Wells). 05:30 Manual opened 8C OCB fdr#3 . 13:03 Manual Closed Back. Cause: Planed maintenance (Minas GS1 requested, to Maintain Level tank due to 8D fdr#6 T/SO.). (GS1 Prod Loss: 258Bbls, 14Wells). (GS2 Prod Loss: 405Bbls, 21Wells). 05:30 Manual opened 8C OCB fdr#2 . 13:09 Manual Closed Back. Cause: Planed maintenance (Minas GS1 requested, to Maintain Level tank due to 8D fdr#6 T/SO.). (GS1 Prod Loss: 120Bbls, 10Wells). (GS2 Prod Loss: 47Bbls, 5Wells). 06:30 Man Closed 8D OCB fdr#7 Man Closed 8D OCB fdr#8 Cause: Circuit Breaker. (8D OCB fdr#6 load transfer to 8D fdr#9) (GS1 Prod Loss: 132Bbls, 15Wells) | 11111 | 1 | 4:11 | Morning | Thursday | 2017 | 10
5832 | 2017-10-05 04:11 | 2017-10-05 04:11 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 23 | 8D OCB fdr#5 T/R 1X. Not checked yet. |  | 1 | 4:11 | Morning | Thursday | 2017 | 10
5833 | 2017-10-05 04:11 | 13/05/2017 09:15 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 23 | Checked & found 8D OCB fdr#5 T/R 1x, Ctr: 565-566, R/F: 51 @1@2@3. Patrolled the Line, found @1@2@3 broken LA LBS o/p 8D-76. Cause : Lightning |  | 1 | 4:11 | Morning | Thursday | 2017 | 10
5834 | 2017-10-05 04:11 | 2017-10-05 04:11 | 13.8KV 8D FEEDER #4 | Rain and Lightning | Lightning | 0 | 8D OCB fdr#4 T/R 1X. (GS 1 WIP) Not checked yet. |  | 1 | 4:11 | Morning | Thursday | 2017 | 10
5835 | 2017-10-05 04:11 | 13/05/2017 20:56 | 13.8KV 8D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found 8D OCB fdr#4 T/R 1x, Ctr: 1542-1543, R/F: 51 @1. Patrolled the Line, found @1 broken LA LBS o/p 8D-32. Cause : Lightning |  | 1 | 4:11 | Morning | Thursday | 2017 | 10
5836 | 2017-10-05 04:11 | 2017-10-05 04:11 | 13.8KV 8D FEEDER #6 | Rain and Lightning | Circuit Breaker | 2 | 04:11 8D VCB fdr#6 T/LO ctr: 211-215 R/F: 51N @1, @2, @3 Checked & found, broken 13.8KV 8D VCB fdr #6. 11:43 Transfer all Load of 8D fdr#6 to 8D fdr#9 Cause: Circuit Breaker (Broken) (GS1 Prod Loss: 48Bbls, 2Wells) |  | 1 | 4:11 | Morning | Thursday | 2017 | 10
5837 | 2017-10-05 04:14 | 2017-10-05 04:14 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 63 | 8C VCB fdr#6 T/R 1x. (GS2 WIP) Not checked yet. |  | 1 | 4:14 | Morning | Thursday | 2017 | 10
5838 | 2017-10-05 04:14 | 13/05/2017 20:32 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 63 | Checked & found 8C VCB fdr#6 T/R 1x, Ctr: 575-576, R/F: 50 @2. Patrolled the Line, found @2 broken pin insulator o/p no name. Cause : Lightning |  | 1 | 4:14 | Morning | Thursday | 2017 | 10
5839 | 2017-10-05 04:15 | 2017-10-05 04:15 | 13.8KV 6D FEEDER #3 | Rain and Lightning | Lightning | 69 | 6D OCB fdr#3 T/R 1X. Not checked yet. (GS3 Prod Loss: 14 Bbls, 7Wells) |  | 1 | 4:15 | Morning | Thursday | 2017 | 10
5840 | 2017-10-05 04:15 | 13/05/2017 19:30 | 13.8KV 6D FEEDER #3 | Rain and Lightning | Lightning | 69 | Checked and found 13.8 KV, OCB fdr #3 T/R: 1x Ctr: 217-218 R/F: 51 @1 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 4:15 | Morning | Thursday | 2017 | 10
5841 | 2017-10-05 04:16 | 2017-10-05 04:16 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 40 | 6D fdr#1 load dropped 191A (233-42A). Not checked yet. |  | 1 | 4:16 | Morning | Thursday | 2017 | 10
5842 | 2017-10-05 04:16 | 13/05/2017 10:00 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 40 | Checked and found Recloser 5C-42 normal operation. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 4:16 | Morning | Thursday | 2017 | 10
5843 | 2017-10-05 04:16 | 2017-10-05 04:16 | 13.8KV 5B FEEDER #6 | Rain and Lightning | Lightning | 0 | 5B fdr#6 load dropped 120A (190-70A) 5B fdr#4 load dropped 26A (180-154A). Not checked yet. |  | 1 | 4:16 | Morning | Thursday | 2017 | 10
5844 | 2017-10-05 04:16 | 13/05/2017 19:30 | 13.8KV 5B FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked and found 13.8 KV, 5B fdr#6 normal operation. Patrolled the line and found nothing. Cause: Lightning. |  | 1 | 4:16 | Morning | Thursday | 2017 | 10
5845 | 2017-10-05 04:35 | 2017-10-05 04:35 | MINAS POWER PLANT | Rain and Lightning | Under investigation | 0 | MGT#4 T/O By Alarm Over Excitation (41AC Excitation Open) under investigate |  | 1 | 4:35 | Morning | Thursday | 2017 | 10
5846 | 2017-10-05 05:40 | 2017-10-05 05:40 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Planned Maintenance | 2 | 05:40 Manual opened 4D OCB fdr#4 . 06:00 Manual Closed Back. Cause: Planed maintenance (Minas GS4 requested, to Maintain Level tank due to WIP T/O). |  | 1 | 5:40 | Morning | Thursday | 2017 | 10
5847 | 2017-10-05 14:46 | 2017-10-05 14:46 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 0 | 14:46 It was reported b/o fuse o/p 03-05-25 d/s C.Duri fdr#7. 15:27 Checked and found @1 b/o fuse for 112.5 TX. Replace b/o fuse above with same size then energized TX Cause: Animal (Squirrel). |  | 1 | 14:46 | Afternoon | Thursday | 2017 | 10
5848 | 2017-10-05 16:30 | 2017-10-05 16:30 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Broken Fuse Cut Out | 0 | It was reported B/O fuse O/p 04-06-02 (CD fdr#9). Not checked yet. |  | 1 | 16:30 | Afternoon | Thursday | 2017 | 10
5849 | 2017-10-05 16:30 | 13/05/2017 19:11 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Broken Fuse Cut Out | 0 | Checked and found broken FCO o/p 04-06-02 @2 Patrolled the line and found broken FCO. Cause : Broken Fuse Cut Out |  | 1 | 16:30 | Afternoon | Thursday | 2017 | 10
5850 | 2017-10-05 18:10 | 2017-10-05 18:10 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | C.Duri fdr#1 Load dropped 33A(123-90A). Not checked yet. |  | 1 | 18:10 | Afternoon | Thursday | 2017 | 10
5851 | 2017-10-05 18:10 | 13/05/2017 19:11 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked and found Recloser 41-AW-62 T/R 1x Ctr: 247-248 R/F: 51@1. Patrolled the line and found nothing. Cause: Suspected Lightning. |  | 1 | 18:10 | Afternoon | Thursday | 2017 | 10
5852 | 2017-10-05 23:26 | 2017-10-05 23:26 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 0 | Batang OCB fdr#2 T/R 2x. Not checked yet. |  | 1 | 23:26 | Night | Thursday | 2017 | 10
5853 | 2017-10-05 23:26 | 13/05/2017 17:49 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found Batang OCB fdr#2 T/R 2x, Ctr: 141-143, R/F: 51 @1@2@3. Patrolled the Line, found @1@2@3 broken LA. o/p 38AH-17, 35AF-30, 34AD-13. Cause : Lightning |  | 1 | 23:26 | Night | Thursday | 2017 | 10
5854 | 2017-11-05 15:24 | 2017-11-05 15:24 | 13.8KV PUNGUT FEEDER #2 | Cloudy and Lightning | Unidentified | 54 | Pungut OCB fdr #2 T/R 2x. Not checked yet. |  | 1 | 15:24 | Afternoon | Sunday | 2017 | 11
5855 | 2017-11-05 15:24 | 13/05/2017 19:58 | 13.8KV PUNGUT FEEDER #2 | Cloudy and Lightning | Unidentified | 54 | Checked & found, Pungut OCB fdr#2 T/R 2x, Ctr: 253-255, R/F: 51 @2. Patrolled the Line, found Recl. 46BP-12 T/R 1x Cause : Unidentified |  | 1 | 15:24 | Afternoon | Sunday | 2017 | 11
5856 | 2017-11-05 17:33 | 2017-11-05 17:33 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 26 | 6D fdr #5 load dropped 159A (234-75A). 6D fdr #4 load dropped 179A (182-34A)---->WIP. 6D fdr #6 load dropped 237A (249-12A)---->WIP. Not checked yet. |  | 1 | 17:33 | Afternoon | Sunday | 2017 | 11
5857 | 2017-11-05 17:33 | 16/05/2017 17:33 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 26 | Checked & found, 6D OCB fdr #5 T/R 1x ctr: 770-771 R/F: 51 @2. Patrolled the line & found, @2 broken Pin Insulator on Pole 5D 106. Cause: Lightning. |  | 1 | 17:33 | Afternoon | Sunday | 2017 | 11
5858 | 2017-11-05 17:36 | 2017-11-05 17:36 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | 5B fdr #1 load dropped 171A (182-11A). 5B fdr #3 load dropped 32A (48-16A). 5B fdr #6 load dropped 120A (188-68A). Not checked yet. |  | 1 | 17:36 | Afternoon | Sunday | 2017 | 11
5859 | 2017-11-05 17:36 | 15/05/2017 17:36 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, 5B OCB fdr #1 T/R 2x ctr: 242-244 R/F: 51 @1. Patrolled the line & found, - @1 broken Pin Insulator on Pole 5B-97 & 5C-75. - @1 broken Dead-end Insulator on Pole 4B-81. Cause: Lightning. |  | 1 | 17:36 | Afternoon | Sunday | 2017 | 11
5860 | 2017-11-05 17:36 | 2017-11-05 17:36 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 0 | 5B fdr #2 load dropped 141A (153-12A). Not check yet. |  | 1 | 17:36 | Afternoon | Sunday | 2017 | 11
5861 | 2017-11-05 17:36 | 15/05/2017 17:36 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, 5B OCB fdr #2 T/R 1x ctr: 378-379 R/F: 51N @1. Patrolled the line & found, @1 broken Pin Insulator on Pole 5C-30 & 5C-09. Cause: Lightning. |  | 1 | 17:36 | Afternoon | Sunday | 2017 | 11
5862 | 2017-11-05 17:47 | 2017-11-05 17:47 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 40 | 6D 13.8KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 17:47 | Afternoon | Sunday | 2017 | 11
5863 | 2017-11-05 17:47 | 15/05/2017 17:47 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 40 | Checked & found, 6D OCB fdr #1 T/R 1x ctr: 324-325 R/F: 51 @1. Patrolled the line & found, @1 broken Dead-end Insulator on Pole 5C-43. Cause: Lightning. |  | 1 | 17:47 | Afternoon | Sunday | 2017 | 11
5864 | 2017-11-05 17:47 | 2017-11-05 17:47 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 63 | 5B 13.8KV OCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 17:47 | Afternoon | Sunday | 2017 | 11
5865 | 2017-11-05 17:47 | 15/05/2017 17:47 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 63 | Checked & found, 5B OCB fdr #2 T/R 1x ctr: 378-379 R/F: 51N @1. Patrolled the line & found, @1 broken Pin Insulator on Pole 5C-30 & 5C-09. Cause: Lightning. |  | 1 | 17:47 | Afternoon | Sunday | 2017 | 11
5866 | 2017-11-05 17:47 | 2017-11-05 17:47 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 59 | 6D fdr #2 load dropped 229A (250-21A). Not checked yet. |  | 1 | 17:47 | Afternoon | Sunday | 2017 | 11
5867 | 2017-11-05 17:47 | 16/05/2017 17:47 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 59 | Checked & found, Recl. 6D-298 T/R 7x ctr: 53-60 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 17:47 | Afternoon | Sunday | 2017 | 11
5868 | 2017-11-05 17:48 | 2017-11-05 17:48 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 56 | 5B 13.8KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 17:48 | Afternoon | Sunday | 2017 | 11
5869 | 2017-11-05 17:48 | 15/05/2017 17:48 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 56 | Checked & found, 5B OCB fdr #1 T/R 2x ctr: 242-244 R/F: 51 @1. Patrolled the line & found, - @1 broken Pin Insulator on Pole 5B-97 & 5C-75. - @1 broken Dead-end Insulator on Pole 4B-81. Cause: Lightning. |  | 1 | 17:48 | Afternoon | Sunday | 2017 | 11
5870 | 2017-11-05 17:57 | 2017-11-05 17:57 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 13 | 15:57 4D 13.8KV OCB fdr #5 T/R 1X. 15:59 4D 13.8KV OCB fdr #5 T/R 1X. 18:14 4D 13.8KV OCB fdr #5 T/R 1X. Not checked yet. |  | 1 | 17:57 | Afternoon | Sunday | 2017 | 11
5871 | 2017-11-05 17:57 | 16/05/2017 17:57 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 13 | Checked & found, 4D OCB fdr #5 T/R 3x ctr: 299-302 R/F: 50 @1. Patrolled the line & found, @1 broken Pin Insulator on Pole 4D-147. Cause: Lightning. |  | 1 | 17:57 | Afternoon | Sunday | 2017 | 11
5872 | 2017-11-05 21:52 | 2017-11-05 21:52 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Dead End Insulator | 97 | Sintong OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 21:52 | Night | Sunday | 2017 | 11
5873 | 2017-11-05 21:52 | 13/05/2017 17:00 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Dead End Insulator | 97 | Checked and found Sintong OCB fdr #2 T/R 1x Counter: 457-458 R/F: 50@2. Patrolled the line found @2 flash over Dead end insulator on pole 28-AF-28. Cause: Dead end insulator. |  | 1 | 21:52 | Night | Sunday | 2017 | 11
5874 | 2017-11-05 23:30 | 2017-11-05 23:30 | 13.8KV 6D FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported broken FCO at well 6B-25. Not checked yet. |  | 1 | 23:30 | Night | Sunday | 2017 | 11
5875 | 2017-11-05 23:30 | 2017-12-05 16:30 | 13.8KV 6D FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked & found, @2 b/o Fuse for 225KVa Tx at well 6B-25. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 23:30 | Night | Sunday | 2017 | 11
5876 | 2017-11-05 23:35 | 2017-11-05 23:35 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Powerline - Jumper | 0 | 23:35 It was reported any Spark at near MCC out side of CGS 5. (CD fdr#10, Darling fdr#3) 01:08 Checked & found broken jumper on 4160V TX A. Closed Tie Breaker of 4160V from TXB d/s CD fdr#11. Cause: Jumper, (Will Repaired soon). |  | 1 | 23:35 | Night | Sunday | 2017 | 11
5877 | 2017-12-05 15:15 | 2017-12-05 15:15 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 0 | 15:15 It was reported any B/O Fuse at well Pagar #32, D/S Ketigul fdr#2. Not checked yet. |  | 1 | 15:15 | Afternoon | Tuesday | 2017 | 12
5878 | 2017-12-05 15:15 | 13/05/2017 13:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 0 | 13:00 Checked and found @3 b/o fuse for 150KVA TX at well Pagar #32. Replaced b/o fuse above with same size. then energized the TX. Cause: Animal (monkey). |  | 1 | 15:15 | Afternoon | Tuesday | 2017 | 12
5879 | 2017-05-13 09:12 | 2017-05-13 09:12 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 166 | 09:12 It was reported @ 2 broken Dead end Insulator o/p 37-B1-01 D/S SO.Bek. 13:38 Manually open So.Bek OCB fdr#1. (Replaced Broken @2 Dead end Insulator). 13:41 Manually Open 44 KV SO.Bek. OCB #2. (Repaired Hot spot @1,@3 Primary Transformer at So.Bek substation. 14:50 Manually Closed 44KV So.Bek OCB #2. 14:53 Manually Closed So.Bek#1. Counter: 356-357. Cause: Planed Maintenance. |  | 1 | 9:12 | Morning | Saturday | 2017 | 5
5880 | 2017-05-13 09:48 | 2017-05-13 09:48 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 61 | 09:48 It was reported No Power at Tandun field. 10:45 Checked & found Recloser 45-BR-01 T/SO counter: 494-495. Blocked & Closed Recloser , but failed. 12:19 Manually opened Pungut OCB fdr#2. Closed By Pass Recloser 45-BR-01. 12:45 Closed Pungut OCB fdr#2. Cause: Planned Maintenance (Control Recloser Problem). |  | 1 | 9:48 | Morning | Saturday | 2017 | 5
5881 | 2017-05-13 12:56 | 2017-05-13 12:56 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 13 | 12:56 It was reported B/O fuse O/p 08-M3-26 (CD fdr#2). 14:00 Checked and found @2,@3 b/o fuse for 112.5Kva TX. Perform TTR and Megger fond good reading. Replaced b/o fuse above with the same size, then energized the TX. Cause: Animai(Squirell). |  | 1 | 12:56 | Afternoon | Saturday | 2017 | 5
5882 | 2017-05-13 13:00 | 2017-05-13 13:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 0 | 13:00 It was reported b/o fuse at well Pager #25. 15:00 Checked and found @1 b/o fuse for 150KVA TX. Replaced b/o fuse above with same size. then energized the TX. Cause: Animal (Squirrel). |  | 1 | 13:00 | Afternoon | Saturday | 2017 | 5
5883 | 2017-05-13 23:55 | 2017-05-13 23:55 | 13.8KV 6DN FEEDER #2 | Fair | Broken Fuse Cut Out | 26 | It was reported that any over heat FCO at location 5D-85 D/S 6DN fdr #2. Not check yet. |  | 1 | 23:55 | Night | Saturday | 2017 | 5
5884 | 2017-05-13 23:55 | 2017-05-16 15:10 | 13.8KV 6DN FEEDER #2 | Fair | Broken Fuse Cut Out | 26 | Checked & found, @2 B/O Fuse Cut Out at well 5D 85. Replaced b/o Fuse Cut Out above then energized the Tx. Cause: Broken Fuse Cut Out. |  | 1 | 23:55 | Night | Saturday | 2017 | 5
5885 | 2017-05-14 01:35 | 2017-05-14 01:35 | 13.8KV 4B FEEDER #4 | Fair | Tree | 426 | 01:35 4B VCB fdr#4 T/SO, Ctr: Not visible, R/F: 51 @1@2. (4Bfdr#4 Carry partial load of 4B fdr#1) 4B fdr#5 Load dropped 257A(264-7A). (GS6; 4 Units WIP) 4B fdr#6 load dropped 90A(128-38A). GS6 requested Opened some feeder to maintain tank level 01:44 Man. Opened 4B VCB fdr#6, ---- Closed at 02:30, Opened at 03:13, Closed back at 03:36. 01:53 Man. Opened 5B VCB fdr#4, ---- Closed at 02:31, Opened at 03:12, Closed back at 03:37. (5B fdr#4 Carry Part of 3Dfdr#4 & 4B fdr#1) 01:54 Man. Opened 5B VCB fdr#5, ---- Closed at 03:37. 03:13 Man. Opened 4B VCB fdr#6, ---- Closed at 03:36. 03:14 Open LBS 4B 100A. (to Separate 4B fdr#1 from 4B fdr#4). 03:15 Man Closed 4B VCB fdr#4. 09:48 Opened LBS 4B-90 and LBS 4A-70. (d/s 4B fdr#1) Patrolled down stream LBS 4B-100A, but found nothing. Closed LBS 4B-100A. (d/s 4B fdr#1) Patrolled down stream LBS 4A-70, but found nothing . 09:50 Blocked 4B OCB fdr #4. Closed LBS 3A-22A. (d/s 4B fdr#1) Closed LBS 4A-70. (energized power line to KBJ). Patrolled down stream LBS 4B-90, found fallen tree hits power line between poles 4B-27 to 4B-28. 11:18 Closed LBS 4B-90 --> OK and then released the block 4B OCB fdr #4. (Part load 4B fdr #1 feed by 4B fdr #4 back to normal) Cause : Tree. |  | 1 | 1:35 | Night | Sunday | 2017 | 5
5886 | 2017-05-14 08:06 | 2017-05-14 08:06 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 1 | 08:06 It was reported B/O fuse for TX at well R.Bais #57. 10:35 Checked and found @1 b/o fuse for 112.5Kva TX. Replaced b/o fuse above with the same size, then energized the TX. Cause: Animal (Monkey). |  | 1 | 8:06 | Morning | Sunday | 2017 | 5
5887 | 2017-05-15 03:26 | 2017-05-15 03:26 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Unidentified | 55 | Nella fdr#1 Load dropped 221A(278-57). Nella fdr#2 Load dropped 46A(93-47)A. Nella GFPC in Block position. Not checked yet. |  | 1 | 3:26 | Night | Monday | 2017 | 5
5888 | 2017-05-15 03:26 | 2017-05-19 03:26 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Unidentified | 55 | Checked & found, no breaker & recloser operated. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 3:26 | Night | Monday | 2017 | 5
5889 | 2017-05-15 03:26 | 2017-05-15 03:26 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Recloser | 195 | 03:26 Bangko fdr#1 Load dropped 160A (215-55A). Bangko fdr#2 load dropped 210A (257-47). WIP Bangko fdr#3 load dropped 113A (200-97A). WIP Bangko fdr#4 Load dropped 160A (223-63A) Bangko fdr#1 Ground fault Alarm. 09:00 Checked & found, Recloser 23W-12 T/SO ctr: 239-240 R/F:51N. Blocked & closed Recl. above, ok, then released the block. Patrolled the line but found nothing. Cause: Recloser (Suspected Recloser Problem due to Recloser Flag Indicated in Close Position) |  | 1 | 3:26 | Night | Monday | 2017 | 5
5890 | 2017-05-15 09:40 | 2017-05-15 09:40 | 13.8KV KETIGUL FEEDER#2 | Fair | Recloser | 962 | 09:40 It was reported no power at UBI field (Ketigul RTU was failed). 11:42 Checked and found Recloser 29-AL-03 T/LO Counter: 119-123. Patrolled the line found @2,@3 broken primary bushing Recloser 29-AL-03. 13:19 Manually opened Ketigul VCB fdr #2. - By pass Recloser. - Opened visual opening. 13:37 Blocked and closed Keigul VCB fdr #2 --> OK and released the block. Cause: Recloser. Production loss: 933 bbls / 48 wells. | 123 | 1 | 9:40 | Morning | Monday | 2017 | 5
5891 | 2017-05-15 10:35 | 2017-05-15 10:35 | MINAS POWER PLANT |  |  | - | 10:35 MGT #4 S/U, then On Line to system at 11:00. |  | 1 | 10:35 | Morning | Monday | 2017 | 5
5892 | 2017-05-15 10:56 | 2017-05-15 10:56 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 35 | 10:56 Blocked Bangko fdr#4 & GFPC. 13:51 Replaced @1,@2 Broken dead end insulator. on pole 25-Z-15. Opened / Closed HLC on pole 25-Z-15. Well were off BKO #249,# 75,# 245. Replaced @1, @2 broken dead end insulator O/P 25-2-15. Opened / closed HLC on pole 25-Z-16. Well were off BKO 257, 252. Replaced @1 broken pin insulator O/P 25-Z-15. Cause: Plan Maintenance. |  | 1 | 10:56 | Morning | Monday | 2017 | 5
5893 | 2017-05-16 08:25 | 2017-05-16 08:25 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 08:25 It was reported B/O fuse o/p 2D-F2-3 at Leuser Camp. (Duri Community fdr#3 ) 09:35 Replaced @1, b/o fuse for 100 Kva Tx with the same size. Cause:Unidentified fuse. |  | 1 | 8:25 | Morning | Tuesday | 2017 | 5
5894 | 2017-05-16 09:39 | 2017-05-16 09:39 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 0 | 09:39 It was reported B/O fuse o/p 06-S7-15 at Duri Field fdr #4. 11:07 Replaced @1, b/o fuse for 112.5 Kva Tx with the same size. Cause:Animal (Monkey) |  | 1 | 9:39 | Morning | Tuesday | 2017 | 5
5895 | 2017-05-16 10:25 | 2017-05-16 10:25 | CENTRAL DURI POWER PLANT |  |  | - | 10:25 CGT#4 S/U then Online the unit at 10:45. |  | 1 | 10:25 | Morning | Tuesday | 2017 | 5
5896 | 2017-05-16 10:55 | 2017-05-16 10:55 | CENTRAL DURI POWER PLANT |  |  | - | 10:55 CGT#4 Off Line the S/D for standby. 10:58 Closed Tie Breaker OCB #39. |  | 1 | 10:55 | Morning | Tuesday | 2017 | 5
5897 | 2017-05-16 16:14 | 2017-05-16 16:14 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 25 | C.Duri fdr#1 load drooped 41A (129-88 A). Not checked yet. |  | 1 | 16:14 | Afternoon | Tuesday | 2017 | 5
5898 | 2017-05-16 16:14 | 2017-05-20 08:14 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 25 | Checked & found Recl. 38AS09 T/R 1x Ctr:212-213. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 16:14 | Afternoon | Tuesday | 2017 | 5
5899 | 2017-05-17 08:27 | 2017-05-17 08:27 | CENTRAL DURI POWER PLANT | Fair |  | - | 08:27 S/U CGT#4 then online the unit at 08:45. 08:30 Open Tie breaker ACB#39. |  | 1 | 8:27 | Morning | Wednesday | 2017 | 5
5900 | 2017-05-17 14:53 | 2017-05-17 14:53 | 13.8KV 8C FEEDER #6 | Fair | Lightning | 48 | 8C Feeder # 6 T/R 1 X (WIP). Weather : Fair Not checked yet. |  | 1 | 14:53 | Afternoon | Wednesday | 2017 | 5
5901 | 2017-05-17 14:53 | 2017-05-23 20:53 | 13.8KV 8C FEEDER #6 | Fair | Lightning | 48 | Checked & found 8C fdr#6 T/R 1x Ctr:576-577 R/F:51N. Patrolled the line & found @3 Broken Dead End Insulator o/p 8C-101. Cause : Lightning. |  | 1 | 14:53 | Afternoon | Wednesday | 2017 | 5
5902 | 2017-05-18 02:14 | 2017-05-18 02:14 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 926 | 02:14 Ketigul 13.8KV VCB fdr #2 T/LO. 04:40 Checked and found Ketigul 13.8KV VCB fdr #2 T/LO ctr: 233-237 R/F: 51 N.T. Patrolled the line till LBS 29-AL-07 but found nothing. 06:00 Open LBS 27-AL-05 ------> Closed at 07:00. 06:10 Blocked and closed Ketigul feeder #2 => Failed from DSC 06:40 Blocked and closed Ketigul feeder #2, Ok. => From Subs. Patrolled the line until LBS 27 AL 03, OK. Open the LBS 27-AL-03------> Closed at 10:20. Continued Patrol the line and found, @2 broken Pin insulator o/p 23 AJ 11. Replace @2 Broken Pin Insulator o/p 23 AJ 11. Caused : Lightning. | 123 | 1 | 2:14 | Night | Thursday | 2017 | 5
5903 | 2017-05-18 03:29 | 2017-05-18 03:29 | 13.8KV RANGAU FEEDER #2 | Fair | Animal | 155 | 03:29 Rangau fdr #2 load dropped 143A (152-9A). 05:50 Checked and found Recl. 23BD-01 T/LO ctr: 193-197 R/F: 51G @1. Blocked and closed Recl 23BD-01, but tripped again. 07:23 Patrolled the line & found, Dead BAT o/p 20BC09. 07:45 Blocked & closed Recl. 23BD01, ok, then release the block. Cause: Animal (Bat). |  | 1 | 3:29 | Night | Thursday | 2017 | 5
5904 | 2017-05-18 12:58 | 2017-05-18 12:58 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 32 | It was reported form Bangko GS B/O Fuse link at Bangko #294 @ 2. Not checked yet. |  | 1 | 12:58 | Afternoon | Thursday | 2017 | 5
5905 | 2017-05-18 12:58 | 2017-05-19 15:00 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 32 | Checked and found B/O fuse @2, o/p Bko #294 Patrolled the line but found nothing. Cause: Unidentified |  | 1 | 12:58 | Afternoon | Thursday | 2017 | 5
5906 | 2017-05-18 13:50 | 2017-05-18 13:50 | 13.8KV 6D FEEDER #2 | Heavy Rain | Pin Insulator | 194 | 13:50 6D feeder #2 load drop 163 Amp ( 250 - 87 ). 6D feeder #3 load drop 216 Amp ( 356 - 140 )(WIP off). 6DN feeder #4 load drop 68 Amp ( 142 - 74 ) (WIP off). 15:49 Checked & found Recl. 6D-298 T/LO Ctr:53-64. 17:45 Patrolled the line & found, @2 broken Pin Insulator o/p 6D-14. 17:50 Open LBS 6D-66, ----->closed at 19:25. 17:55 Blocked & closed Recl. 6D-298, then release the block Cause: Pin Insulator. Production loss: GS #3 : 181 Bbls / 16 Wells ----->6D fdr #2. 13 Bbls / 7 Wells ----->6D fdr #3. ----------------------------------------------------+ TOTAL: 194 bbls / 23 Wells. |  | 1 | 13:50 | Afternoon | Thursday | 2017 | 5
5907 | 2017-05-18 15:00 | 2017-05-18 15:00 | 13.8KV MINAS FEEDER #1 | Heavy Rain | Dead End Insulator | 65 | 15:00 Minas Feeder #1 T/R 1X. R/F 51 @1 and @2. Counter : 62 - 63. Minas Feeder # 2 load drop 31 Amp ( 119 - 88 ). Minas Feeder # 3 load drop 169 Amp ( 266 - 97 ). Minas Feeder # 4 load drop 140 Amp ( 193 - 53 ). Not checked yet. Production loss: GS:1 : 11 Bbls / 3 wells. ----->Minas fdr #1. GS:3 : 50 Bbls / 21 wells. ----->Minas fdr #1. -------------------------------------------------------+ TOTAL : 61 Bbls / 24 Wells |  | 1 | 15:00 | Afternoon | Thursday | 2017 | 5
5908 | 2017-05-18 15:00 | 2017-05-23 20:00 | 13.8KV MINAS FEEDER #1 | Heavy Rain | Dead End Insulator | 65 | Patrolled the line & found @1 Broken Dead End Insulator o/p 6D-25. Cause: Dead End Insulator. |  | 1 | 15:00 | Afternoon | Thursday | 2017 | 5
5909 | 2017-05-18 15:00 | 2017-05-18 15:00 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 57 | Minas Feeder # 3 load drop 169 Amp ( 266 - 97 ). Not checked yet. |  | 1 | 15:00 | Afternoon | Thursday | 2017 | 5
5910 | 2017-05-18 15:00 | 2017-05-23 20:00 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 57 | Checked Feeder & Recloser Not Operated. Patrolled the line but found nothing. Cause: lightning. |  | 1 | 15:00 | Afternoon | Thursday | 2017 | 5
5911 | 2017-05-18 15:06 | 2017-05-18 15:06 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 37 | 15:06 Pematang feeder #1 T/R 1X. Pematang feeder #2 load drop 45 Amp ( 56 - 11 ). Not checked yet. |  | 1 | 15:06 | Afternoon | Thursday | 2017 | 5
5912 | 2017-05-18 15:06 | 2017-05-20 16:00 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 37 | Checked and found 13.8 KV Pematang OCB fdr#1 T/R 1x, Ctr: 133-134, R/F: 51N Patrolled the line and found @1,@2,@3 Broken dean end insulator on TOP PMT #22. Cause: Lightning. |  | 1 | 15:06 | Afternoon | Thursday | 2017 | 5
5913 | 2017-05-18 17:52 | 2017-05-18 17:52 | 13.8KV RANGAU FEEDER #2 | Rain | Animal | 0 | Rangau fdr#2 Load dropped 138A (152-14A). Not checked yet. |  | 1 | 17:52 | Afternoon | Thursday | 2017 | 5
5914 | 2017-05-18 17:52 | 2017-05-20 07:42 | 13.8KV RANGAU FEEDER #2 | Rain | Animal | 0 | Checked and found recloser 23-BD-01 T/LO, Ctr: 193-197, R/F: 51G @1 Patrolled the line and found dead animal. Cause: Animal |  | 1 | 17:52 | Afternoon | Thursday | 2017 | 5
5915 | 2017-05-18 18:29 | 2017-05-18 18:29 | 13.8KV KETIGUL FEEDER#2 | Rain | Unidentified | 227 | 18:29 Ketigul VCB fdr#2 T/O (blocked position). 20:40 Checked and found Ketigul VCB fdr#2 T/O ctr:237-238 R/F: 51N Time. 20:48 Blocked and closed Ketigul fdr #2, OK then normalized block. Not patrolled yet. |  | 1 | 18:29 | Afternoon | Thursday | 2017 | 5
5916 | 2017-05-18 18:29 | 2017-05-20 16:00 | 13.8KV KETIGUL FEEDER#2 | Rain | Unidentified | 227 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 18:29 | Afternoon | Thursday | 2017 | 5
5917 | 2017-05-19 00:12 | 2017-05-19 00:12 | NEW PETAPAHAN SUBSTATION | Rain and Lightning | Under investigation | 694 | 00:12 Petapahan 115KV C/S T/O. (No power to Petapahan fdr #1 & #2). 00:50 Checked and found Petapahan 115KV C/S T/O ctr:159-160 R/F: 51G. 01:00 Open Petapahan fdr #1,-----> Closed at 01:45. 01:00 Open Petapahan fdr #2,-----> Closed at 01:46 Closed 115KV Petapahan C/S, but failed. Continued to checked and found b/o fuse control of C/S. 01:44 Closed Petapahan 1152v C/S, OK. Cause: Under investigation. | 123 | 1 | 0:12 | Night | Friday | 2017 | 5
5918 | 2017-05-19 06:34 | 2017-05-19 06:34 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | 06:34 Sintong fdr #2 load dropped 50A (89-39A). Ground fault alarm from Sintong fdr #1. 15:00 Checked & found, Recloser 25AD-26 T/R 1x ctr: 113-114. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:34 | Morning | Friday | 2017 | 5
5919 | 2017-05-19 09:45 | 2017-05-19 09:45 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 09:45 It was reported B/O fuse at Kopar #37 D/S Rokan fdr#2. 15:29 Checked and found B/O fuse @1, @2 for TX 300 KVA. Performed Megger test --> OK, change fuse with new one. Patrolled the line but found nothing. Cause: Unidentified. | 123 | 1 | 9:45 | Morning | Friday | 2017 | 5
5920 | 2017-05-19 12:41 | 2017-05-19 12:41 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | 362 | 12:41 Minas fdr#4 T/LO, Ctr: 268-270 R/F: 51 @1, 51N. Minas fdr#3 load dropped 242 A (283-41) A Minas fdr#1 load dropped 84 A ( 84 - 0) A Minas fdr#2 load dropped 46 A (116-70) A 12:55 Checked and found Recloser 7D-121 T/SO Patrolled the line and found nothing. 14:40 Blocked and closed Minas fdr#4, then released the block. 14:45 Blocked and closed Recloser 7D-121, then released the blocked, Ctr: 11-12. Cause: Unidentified. Production loss: GS #1 : 233 Bbls / 27 wells -----> Minas fsr #4. GS #2 : 112 Bbls / 12 wells -----> Minas fsr #4. --------------------------------+ TOTAL : 345 bbls / 39 wells. |  | 1 | 12:41 | Afternoon | Friday | 2017 | 5
5921 | 2017-05-19 12:41 | 2017-05-19 12:41 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | 60 | 12:41 Minas fdr#3 load dropped 242 A (283-41A). Not checked yet. |  | 1 | 12:41 | Afternoon | Friday | 2017 | 5
5922 | 2017-05-19 12:41 | 2017-05-23 21:41 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | 60 | Checked Feeder & Recloser Not Operated. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 12:41 | Afternoon | Friday | 2017 | 5
5923 | 2017-05-19 16:43 | 2017-05-19 16:43 | CENTRAL DURI POWER PLANT |  |  | - | Offline CGT #5 then S/D the unit for S/B. |  | 1 | 16:43 | Afternoon | Friday | 2017 | 5
5924 | 2017-05-19 16:50 | 2017-05-19 16:50 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 0 | It was reported B/O fuse o/p 05-P5-12B (C.Duri fdr#15). Not checked yet. |  | 1 | 16:50 | Afternoon | Friday | 2017 | 5
5925 | 2017-05-19 16:50 | 2017-05-20 11:00 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 0 | Replaced @3 B/O fuse for 112.5 Kva Tx with the same size o/p 05-P5-12B. Cause: Animal (Monkey). |  | 1 | 16:50 | Afternoon | Friday | 2017 | 5
5926 | 2017-05-20 02:14 | 2017-05-20 02:14 | 13.8KV 8D FEEDER #4 | Fair | Lightning | 3 | 8D 13.8KV OCB fdr #4 T/R 1X ------>WIP. 8D fdr #5 load dropped 43A (110-67A). 8D fdr #9 load drooped 121A (176-55A) ----->WIP. Not checked yet. | 1111 | 1 | 2:14 | Night | Saturday | 2017 | 5
5927 | 2017-05-20 02:14 | 2017-05-24 20:14 | 13.8KV 8D FEEDER #4 | Fair | Lightning | 3 | Checked & found 8D OCB fdr#4 T/r 1x Ctr:1543-1544 R/F:51@1@2. Patrolled the line & found @1@2 Broken Pin Insulator o/p 8D-78. Cause : Lightning. | 1111 | 1 | 2:14 | Night | Saturday | 2017 | 5
5928 | 2017-05-20 10:38 | 2017-05-20 10:38 | 13.8KV 4D FEEDER #3 | Heavy Rain | Lightning | 13 | 4D fdr#3 T/R 1x 4D fdr#2 load dropped 112 A (147-35) A Not checked yet. |  | 1 | 10:38 | Morning | Saturday | 2017 | 5
5929 | 2017-05-20 10:38 | 2017-05-24 20:38 | 13.8KV 4D FEEDER #3 | Heavy Rain | Lightning | 13 | Checked & found 4D OCB fdr#3 T/R 1x Ctr:237-238 R/F:51@1. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 10:38 | Morning | Saturday | 2017 | 5
5930 | 2017-05-20 12:45 | 2017-05-20 12:45 | 13.8KV LIBO FEEDER #1 | Fair | Secondary Cable | 15 | 12: 45 It was reported B/O fuse at SE Libo #50 D/S Libo fdr#1 16:00 Replaced @1 B/O fuse for 300 KVA TX with the same size Cause: Broken Secondary cable. |  | 1 | 12:45 | Afternoon | Saturday | 2017 | 5
5931 | 2017-05-20 14:20 | 2017-05-20 14:20 | 13.8KV CENTRAL DURI FEEDER #15 | Cloudy | Unidentified (Fuse) | 0 | 14: 20 It was reported B/O fuse o/p 06-Q5-4B D/S Central Duri fdr#15 Not cheked yet. 14:50 Checked and found B/O fuse @2 Patrolled the line and found nothing. Cause: Unidentified (fuse). |  | 1 | 14:20 | Afternoon | Saturday | 2017 | 5
5932 | 2017-05-20 16:47 | 2017-05-20 16:47 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Duri Community 13.8 KV ACB fdr#3 T/R 1x. Not checked yet. |  | 1 | 16:47 | Afternoon | Saturday | 2017 | 5
5933 | 2017-05-20 16:47 | 2017-05-21 16:47 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Checked & found, Duri Community ACB #26 fdr #3 T/R 1x ctr: 57-58 R/F: 51N @3. Patrolled the line & found, @3 broken Pin Insulator on Pole 3DC32. Cause: Pin Insulator. |  | 1 | 16:47 | Afternoon | Saturday | 2017 | 5
5934 | 2017-05-20 19:07 | 2017-05-20 19:07 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 41 | Pematang 13.8KV OCB fdr #1 T/R 1X. Pematang fdr #2 load dropped 36A ( 56-20A ). Rangau fdr #2 load dropped 15A (160-145A ). Petani fdr #1 load dropped 65A (210-145A ). Not checked yet. | 1111 | 1 | 19:07 | Night | Saturday | 2017 | 5
5935 | 2017-05-20 19:07 | 2017-05-21 19:07 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 41 | Checked & found, Pematang OCB fdr #1 T/R 1x ctr: 134-135 R/F: 50N. Patrolled the line but found nothing. Cause: Unidentified. | 1111 | 1 | 19:07 | Night | Saturday | 2017 | 5
5936 | 2017-05-21 06:58 | 2017-05-21 06:58 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Animal | 0 | 06:58 C.Duri ACB#13 T/R 1x. 13:30 Checked and found 13.8 KV ACB #13 T/R 1x, Ctr: 200-201, R/F: 50/51 @2,@3, 51G Patrolled the line and found dead monkey o/p 03-08-02. Cause: Animal (monkey) |  | 1 | 6:58 | Morning | Sunday | 2017 | 5
5937 | 2017-05-21 09:15 | 2017-05-21 09:15 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 0 | 09:15 It was reported B/O fuse o/p 06-Q3-03 D/S Central Duri fdr#3 11:05 Replaced @2 B/O fuse for 112.2 KV TX with the same size. Patrolled the line and found dead squirell. Cause: Animal (squirell). |  | 1 | 9:15 | Morning | Sunday | 2017 | 5
5938 | 2017-05-21 11:12 | 2017-05-21 11:12 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Animal | 6 | 11:12 It was reported B/O fuse o/p 03-08-02 D/S Central Duri fdr#3. 11:15 Replaced @1 B/O fuse for 112.5 KV TX with the same size. Patrolled the line and found dead monkey. Cause: Animal (monkey). |  | 1 | 11:12 | Morning | Sunday | 2017 | 5
5939 | 2017-05-21 16:07 | 2017-05-21 16:07 | 13.8KV BANGKO FEEDER #4 | Fair | Powerline - Conductor | 521 | 16:07 Bangko 13.8 KV OCB fdr#4 T/LO Bangko GFPC T/R 4x 16:50 Checked and found Bagko VCB fdr#4 T/LO Ctr:002-006 R/F:51N Patrolled the line and found @3 broken conductor o/p 24-Z-22. 17:04 Isolated broken conductor. Blocked and closed Bangko fdr#4 then released the block. 17:29 It was reported Benar GS no power from Bangko fdr#4 Checked and found Recloser 25-Z-07 T/LO Ctr:154-158 (Four wells Off still off during isolated @3 broken Conductor and well be continued this morning). Monday, 22 May 2017 12:00 Completed install new conductor. Cause: broken conductor. | 11111 | 1 | 16:07 | Afternoon | Sunday | 2017 | 5
5940 | 2017-05-22 07:21 | 2017-05-22 07:21 | 13.8KV NELLA GFPC | Fair | Unidentified | 129 | 07:21 GFPC Nella substation T/R 2x Ground Fault alarm at fdr #1 and fdr #2 Nella fdr#1 load dropped 210 A (275-66) A Nella fdr #2 load dropped 68 A (88-20) A 16:20 Checked & found, Nella GFPC T/R 2x Counter: 725-727 R/F: 50N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:21 | Morning | Monday | 2017 | 5
5941 | 2017-05-22 10:01 | 2017-05-22 10:01 | 13.8KV NEW KOTABATAK FEEDER #2 | Fair | Unidentified | 53 | 10:01 NKBS fdr #2 T/R 1x Not checked yet. |  | 1 | 10:01 | Morning | Monday | 2017 | 5
5942 | 2017-05-22 10:01 | 2017-05-23 10:01 | 13.8KV NEW KOTABATAK FEEDER #2 | Fair | Unidentified | 53 | Checked & found, NKBS OCB fdr #2 T/R 1x ctr: 99911-99912 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:01 | Morning | Monday | 2017 | 5
5943 | 2017-05-22 13:57 | 2017-05-22 13:57 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Powerline - Conductor | 408 | 13:57 CKB fdr #5 T/LO CKB fdr #2 load dropped 100 A (260-160) A CKB fdr #6 load dropped 40 A (180-140) A 14:48 Checked and found CKB fdr #5 T/LO Ctr: 151-154 R/F:51 @1, @2 Blocked and tried to close but trip again, continue patrol the line. 15:14 Patrolled the line and found broken conductor @1 o/p 36-CU-38. 15:48 Opened isolation switch CKB fdr #5. 18:04 Blocked and close CKB fdr #5, then released the block. (after repaired the broken conductor). Cause: Broken conductor. |  | 1 | 13:57 | Afternoon | Monday | 2017 | 5
5944 | 2017-05-23 05:53 | 2017-05-23 05:53 | 13.8KV RANGAU FEEDER #2 | Fair | Tree | 16 | Rangau fdr#2 Load dropped 135 (144-9A) Not checked yet. |  | 1 | 5:53 | Morning | Tuesday | 2017 | 5
5945 | 2017-05-23 05:53 | 2017-05-26 20:53 | 13.8KV RANGAU FEEDER #2 | Fair | Tree | 16 | Checked & found Recl. 23BD01 T/R 7x Ctr:193-200. Patrolled the line & found Danger trees between pole 22BD02. Cause : Tree. |  | 1 | 5:53 | Morning | Tuesday | 2017 | 5
5946 | 2017-05-23 10:18 | 2017-05-23 10:18 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 6 | 10:18 It was reported broken fuse at Bangko #271, D/S Bangko fdr #4. 11:00 Checked and found broken fuse for 300 KVA TX, replaced broken fuse with new one. Patrolled the line and found dead animal. Cause: Animal. |  | 1 | 10:18 | Morning | Tuesday | 2017 | 5
5947 | 2017-05-23 10:19 | 2017-05-23 10:19 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified (Fuse) | 12 | 10:19 It was reported broken fuse at Petani #39 @1, D/S Petani fdr #1. 11:55 Checked and found broken fuse @1 for 150 KVA TX, replaced with same size. Cause: Unidentified. |  | 1 | 10:19 | Morning | Tuesday | 2017 | 5
5948 | 2017-05-23 11:38 | 2017-05-23 11:38 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 0 | 11:38 It was reported B/O fuse at Kulim #31 D/S Central Duri fdr#1. 14:31 Checked and found broken fuse @1, replaced with new and same size. Patrolled the Line, but found nothing. Cause : Lightning (suspected) |  | 1 | 11:38 | Morning | Tuesday | 2017 | 5
5949 | 2017-05-23 14:53 | 2017-05-23 14:53 | 4.16KV SO RUMBAI FEEDER #3 | Fair | Unidentified | 0 | South Rumbai fdr #3 T/R 1x Not checked yet. |  | 1 | 14:53 | Afternoon | Tuesday | 2017 | 5
5950 | 2017-05-23 14:53 | 2017-05-30 17:42 | 4.16KV SO RUMBAI FEEDER #3 | Fair | Unidentified | 0 | Checked & found S.Rumbai fdr#3 T/R 1x, Ctr: 130-131, R/F: 51N. Patrolled the Line, but Found nothing. Cause : Unidentified |  | 1 | 14:53 | Afternoon | Tuesday | 2017 | 5
5951 | 2017-05-23 16:00 | 2017-05-23 16:00 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Lightning | 3 | 16:00 It was reported B/O fuse o/p 04-03-20, D/S Central Duri fdr #9 Not checked yet. |  | 1 | 16:00 | Afternoon | Tuesday | 2017 | 5
5952 | 2017-05-23 16:00 | 2017-05-24 17:15 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Lightning | 3 | Checked & found @2 b/o fuse for 112.5KVATX. Replaced the fuse with the same size, the energized the TX. Patrolled the Line, but found nothing. Cause : Lightning (suspected) |  | 1 | 16:00 | Afternoon | Tuesday | 2017 | 5
5953 | 2017-05-23 17:56 | 2017-05-23 17:56 | 13.8KV NORTH DURI FEEDER #1 | Fair | Lightning | 0 | North Duri fdr 1 T/R 1x Not checked yet |  | 1 | 17:56 | Afternoon | Tuesday | 2017 | 5
5954 | 2017-05-23 17:56 | 2017-05-30 14:31 | 13.8KV NORTH DURI FEEDER #1 | Fair | Lightning | 0 | Checked & found N.Duri ACB fdr#1 T/R: 282-283, R/F: 51N. Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 17:56 | Afternoon | Tuesday | 2017 | 5
5955 | 2017-05-23 17:56 | 2017-05-23 17:56 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Lightning | 0 | Central Duri fdr #16 T/R 1x Ctr:297-298 R/F:51N Not checked yet. |  | 1 | 17:56 | Afternoon | Tuesday | 2017 | 5
5956 | 2017-05-23 17:56 | 2017-05-30 14:50 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Lightning | 0 | checked & found C.Duri ACB fdr#16 T/R 1x, Ctr: 297-298, R/F: 51N. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 17:56 | Afternoon | Tuesday | 2017 | 5
5957 | 2017-05-24 07:12 | 2017-05-24 07:12 | 13.8KV S. BALAM FEEDER #1 | Cloudy | Unidentified | 137 | So Balam VCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 7:12 | Morning | Wednesday | 2017 | 5
5958 | 2017-05-24 07:12 | 2017-05-25 02:51 | 13.8KV S. BALAM FEEDER #1 | Cloudy | Unidentified | 137 | Checked & found S.Balam VCB fdr#1 T/R 1x, Ctr: 385-386, R/F: 51N. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 7:12 | Morning | Wednesday | 2017 | 5
5959 | 2017-05-24 11:38 | 2017-05-24 11:38 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 74 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 11:38 | Morning | Wednesday | 2017 | 5
5960 | 2017-05-24 11:38 | 2017-05-27 20:38 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 74 | Checked & found Ketigul fdr#2 T/R 1x ctr:231-232 R/F:51N. Patrolled the li8ne & found @1 Broken Dead End Insulator o/p NN. Cause : Dead End Insulator. |  | 1 | 11:38 | Morning | Wednesday | 2017 | 5
5961 | 2017-05-25 08:42 | 2017-05-25 08:42 | 13.8KV RANGAU FEEDER #2 | Cloudy | Tree | 24 | 08:42 Rangau fdr#2 Load drop 150A(159-9A). Not checked yet. 19:05 Rangau fdr#2 Load drop 176A(192-16A). Not checked yet. |  | 1 | 8:42 | Morning | Thursday | 2017 | 5
5962 | 2017-05-25 08:42 | 2017-05-26 20:42 | 13.8KV RANGAU FEEDER #2 | Cloudy | Tree | 24 | Checked & found Recl. 23BD01 T/R 7x Ctr:193-200. Patrolled the line & found Danger trees between pole 22BD02. Cause : Tree. |  | 1 | 8:42 | Morning | Thursday | 2017 | 5
5963 | 2017-05-25 09:09 | 2017-05-25 09:09 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 4 | 09:09 It was reported b/o fuse on pole 01-04-16 D/S Duri field fdr#1. 14:25 Replaced the B/O fuse with the same size then energize the TX. Cause : Unidentified. |  | 1 | 9:09 | Morning | Thursday | 2017 | 5
5964 | 2017-05-25 09:48 | 2017-05-25 09:48 | 13.8KV 4B FEEDER #4 | Fair | Unidentified | 36 | 09:48 4B VCB fdr#4 T/LO Ctr: 201-205 , R/F: 51 @1,@2. 09:57 4B VCB fdr#6 Manually opened and closed at:10:11. 09:58 4B VCB fdr#4 Blocked and closed --> OK and then realesed the block. Cause: Unidentified. |  | 1 | 9:48 | Morning | Thursday | 2017 | 5
5965 | 2017-05-25 10:49 | 2017-05-25 10:49 | 13.8KV NEW KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 8 | 10:49 Blocked Recloser: 38-CX-25 D/S NKBS fdr #2. 11:15 Closed LBS 39-CY-01. 11:40 Cut jumper on pole 38-CW-08 ( Jumper by pass) Manually opened Recloser 38-CW-08 (due to replaced Recloser and @1 broken by pass). 12:10 Cut jumper on pole 37-CW-07 (Source side). 13:30 Shut down well KB #23. 13:35 Cut jumper on pole 38-CW-12. Replaced Recloser C/W by pass. Squeezed jumper on pole 38-CW-12. 17:00 Energized well KB #23. Cause: Plan Maintenance. |  | 1 | 10:49 | Morning | Thursday | 2017 | 5
5966 | 2017-05-25 20:50 | 2017-05-25 20:50 | 13.8KV NORTH DURI FEEDER #2 | Cloudy | Animal | 26 | It was reported B/O fuse o/p 10-J4-06 (N.Duri fdr#2). Not checked yet. |  | 1 | 20:50 | Night | Thursday | 2017 | 5
5967 | 2017-05-25 20:50 | 2017-01-06 07:46 | 13.8KV NORTH DURI FEEDER #2 | Cloudy | Animal | 26 | 26-May-2017 20:50 Checked & found @1 b/o fuse o/p 10-J4-06 for 112.5KVATX. Replaced the fuse with the same size, then energized the TX. Cause : Animal (Monkey). |  | 1 | 20:50 | Night | Thursday | 2017 | 5
5968 | 2017-05-26 02:46 | 2017-05-26 02:46 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Unidentified | 0 | 02:46 Sintong fdr#2 load dropped 76A (156-80A) Sintong GFPC T/R 1X. 20:00 Checked & found Recl. 28-AF-02 T/R 1x, Ctr: 640-641, R/F: 51G. Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 2:46 | Night | Friday | 2017 | 5
5969 | 2017-05-26 02:46 | 2017-05-26 02:46 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Bangko fdr#4 load dropped 122A (226-104A) Not checked yet. |  | 1 | 2:46 | Night | Friday | 2017 | 5
5970 | 2017-05-26 07:48 | 2017-05-26 07:48 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Lightning | 67 | Petani OCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 7:48 | Morning | Friday | 2017 | 5
5971 | 2017-05-26 07:48 | 2017-05-28 08:20 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Lightning | 67 | Checked and found Petani OCB fdr#1 T/R 1x Ctr:31-32 R/F: 51@2. Patrolled the line nothing found. Cause: Suspected lightning. |  | 1 | 7:48 | Morning | Friday | 2017 | 5
5972 | 2017-05-26 09:16 | 2017-05-26 09:16 | 13.8KV PUNGUT FEEDER #1 | Drizzle | Lightning | 33 | Pungut OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 9:16 | Morning | Friday | 2017 | 5
5973 | 2017-05-26 09:16 | 2017-05-28 07:26 | 13.8KV PUNGUT FEEDER #1 | Drizzle | Lightning | 33 | Checked & found Pungut OCB fdr#1 T/R 1x, Ctr: 370-371, R/F: 51N. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 9:16 | Morning | Friday | 2017 | 5
5974 | 2017-05-27 01:24 | 2017-05-27 01:24 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified | 0 | Duri Community fdr#5 T/R 1x. Not checked yet. |  | 1 | 1:24 | Night | Saturday | 2017 | 5
5975 | 2017-05-27 01:24 | 2017-05-28 07:39 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified | 0 | Checked and found Duri Community fdr#5 T/R 1x Counter: 111-112 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 1:24 | Night | Saturday | 2017 | 5
5976 | 2017-05-27 08:43 | 2017-05-27 08:43 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 33 | Petani OCB fdr#2 T/R 2x. Petani fdr#1 Load dropped 73A(209-136A). Not checked yet. |  | 1 | 8:43 | Morning | Saturday | 2017 | 5
5977 | 2017-05-27 08:43 | 2017-05-28 08:14 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 33 | Checked and found Petani OCB fdr#2 T/R 2x Counter: 31-32 R/F: 51@2. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 8:43 | Morning | Saturday | 2017 | 5
5978 | 2017-05-27 13:47 | 2017-05-27 13:47 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | Sintong fdr #2 load dropped 9A (149-140A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 13:47 | Afternoon | Saturday | 2017 | 5
5979 | 2017-05-27 20:04 | 2017-05-27 20:04 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Dead End Insulator | 0 | 4.16KV East Rumbai fdr#2 T/R 1x. Not checked yet. |  | 1 | 20:04 | Night | Saturday | 2017 | 5
5980 | 2017-05-27 20:04 | 2017-05-29 17:52 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Dead End Insulator | 0 | Checked & found, Rumbai VCB fdr#2 T/R 1x , Ctr: 513-515, R/F: 51N. Patrolled the Line, @2 Broken Dead-end o/p 5 RE02 Cause : Dead-end Insulator. |  | 1 | 20:04 | Night | Saturday | 2017 | 5
5981 | 2017-05-27 22:46 | 2017-05-27 22:46 | 13.8KV MINAS FEEDER #3 | Cloudy | Others | 57 | 22:46 Minas ACB fdr#3 T/SO. 22:50 Checked & found Minas ACB fdr#3 T/SO Ctr:110-111 R/F:51N. 23:21 Patrolled the line & found Kite on T/P well 7D-65. Isolated Kite on T/P well 7D-65. 23:23 Blocked & closed Minas ACB fdr#3, then release the blok. Cause: Other (Kite). |  | 1 | 22:46 | Night | Saturday | 2017 | 5
5982 | 2017-05-28 02:31 | 2017-05-28 02:31 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Lightning | 0 | C.Duri ACB fdr#14 T/R 1x. Not patrolled yet. |  | 1 | 2:31 | Night | Sunday | 2017 | 5
5983 | 2017-05-28 02:31 | 2017-01-06 07:51 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Lightning | 0 | Checked & found C.Duri ACB fdr#14 T/R 1x, Ctr: 339-340, R/F: 51N. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 2:31 | Night | Sunday | 2017 | 5
5984 | 2017-05-28 07:03 | 2017-05-28 07:03 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | D Community ACB #25 (Feeder #1) T/R 1x. Not checked yet. |  | 1 | 7:03 | Morning | Sunday | 2017 | 5
5985 | 2017-05-28 07:03 | 2017-05-31 07:03 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Checked & found C.Duri ACB fdr#1 T/R 1x, Ctr: 98-99, R/F: 51N. Patrolled the Line, found @2@3 Broken Pin Insulator o/p KT-28. Cause : Unidentified |  | 1 | 7:03 | Morning | Sunday | 2017 | 5
5986 | 2017-05-28 07:11 | 2017-05-28 07:11 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Lightning | 0 | S Balam fdr #4 load dropped 67A (186-119A). S Balam GFPC T/R 1x. Not checked yet. |  | 1 | 7:11 | Morning | Sunday | 2017 | 5
5987 | 2017-05-28 07:11 | 2017-05-29 11:38 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Lightning | 0 | Checked and found Recloser: 16-AA-08 T/R 1x counter: 76-77, R/F: 51N. Patrolled the Line, found @1 Broken LA o/tp of well So.Balam #380 Cause : Lightning Arrester |  | 1 | 7:11 | Morning | Sunday | 2017 | 5
5988 | 2017-05-28 12:55 | 2017-05-28 12:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 25 | C.Duri ACB fdr#1 T/R 1x, Ctr: 199-200, R/F: 51G, 51N. Not checked yet. |  | 1 | 12:55 | Afternoon | Sunday | 2017 | 5
5989 | 2017-05-28 12:55 | 2017-05-31 07:51 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 25 | Checked & found C.Duri ACB fdr#11 T?R 1x, Ctr: 199-200, R/F: 51N. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 12:55 | Afternoon | Sunday | 2017 | 5
5990 | 2017-05-28 23:00 | 2017-05-28 23:00 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 59 | 23:00 It was reported B/O fuse at well So.Bekasap#12 (So.Bek fdr#1). 29 May 2017. 00:30 Replaced @1 B/O fuse for 150Kva Tx with the same size. Casue: Unidentified Fuse. |  | 1 | 23:00 | Night | Sunday | 2017 | 5
5991 | 2017-05-29 00:27 | 2017-05-29 00:27 | 13.8KV 8C FEEDER #3 | Fair | Lightning | 0 | 8C fdr#3 Load dropped 182A (215-33A). Not checked yet. |  | 1 | 0:27 | Night | Monday | 2017 | 5
5992 | 2017-05-29 00:27 | 2017-05-30 17:45 | 13.8KV 8C FEEDER #3 | Fair | Lightning | 0 | Checked & found Recl. 8D-18A T/R 1x, Ctr: 36-37, R/F: Nothing. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 0:27 | Night | Monday | 2017 | 5
5993 | 2017-05-29 07:20 | 2017-05-29 07:20 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 0 | Sintong fdr #1 load dropped 50A (95-45A). Not checked yet. |  | 1 | 7:20 | Morning | Monday | 2017 | 5
5994 | 2017-05-29 07:20 | 2017-05-30 11:30 | 13.8KV SINTONG FEEDER #1 | Fair | Animal | 0 | Checked & found, Recl. 25-AD-26 T/R 1X, Ctr: 114-115, R/F : 51 @3. Patrolled the line, found nothing. cause: unidentified. |  | 1 | 7:20 | Morning | Monday | 2017 | 5
5995 | 2017-05-29 07:52 | 2017-05-29 07:52 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Lightning | 0 | 4160 V East Rumbai VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 7:52 | Morning | Monday | 2017 | 5
5996 | 2017-05-29 07:52 | 2017-05-30 17:52 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Lightning | 0 | Checked & found Rumbai VCB fdr#2 T/R 1x , Ctr: 513-515, R/F: 51N. Patrolled the Line, @2 Broken Deadend o/p 5 RE02 Cause : Lightning |  | 1 | 7:52 | Morning | Monday | 2017 | 5
5997 | 2017-05-29 15:10 | 2017-05-29 15:10 | CENTRAL DURI SWITCH YARD | Fair | Under investigation | 0 | 15:10 115 Kv GCB #63 T/O Counter: 106-107. 115 Kv GCB #65 T/O. Counter: 143-144. 13.8 Kv ACB #44 T/O. (115KV CDSY Power Tx #4 Tripped) 15:43 Closed Tie breaker ACB #39. 16:00 Checked and found - Indication pressure relief device grounding TX #4 appear. - Relay 86T and deferential TX. Cause: Under Investigation. |  | 1 | 15:10 | Afternoon | Monday | 2017 | 5
5998 | 2017-05-29 15:15 | 2017-05-29 15:15 | 13.8KV MINAS FEEDER #3 | Fair | Others | 171 | 15:15 Minas ACB #2 (feeder #3) T/LO Counter: 811-812 R/F: 51N. Minas fdr #4 load dropped 159A (189-30A). 15:29 Patrolled the line found KITE hang on power line between poles 7D-71 to 7D-72. 16:40 Blocked and Manually closed Minas ACB #2 (feeder #3), OK and then released the block. Cause: Other (KITE). |  | 1 | 15:15 | Afternoon | Monday | 2017 | 5
5999 | 2017-05-30 04:10 | 2017-05-30 04:10 | CENTRAL KOTABATAK SUBSTATION | Rain | Under investigation | 323 | 04:10 CKB C/S TX#1 T/O, No Power CKB fdr#1 and fdr#2. 05:17 Checked & found, TX#1 R/F: 86T, Oil Level : Low (-10). Man. Opened CKB OCB fdr#1 & fdr#2. Resetted 86T, then Closed CKB C/S TX#1, but fail. 05:59 Opened Isolation switch of VRTX#1 (Isolated VR Tx #1). 06:45 Closed tie bus. 06:50 Manually closed CKBS VCB fdr #3 (no load). 06:58 Manually closed CKBS VCB fdr #1. 07:17 Manually closed CKBS VCB fdr #2. Cause: Under investigation. | 111 | 1 | 4:10 | Morning | Tuesday | 2017 | 5
6000 | 2017-05-30 08:43 | 2017-05-30 08:43 | 13.8KV NELLA FEEDER #1 | Fair | Lightning | 270 | 08:43 Nella VCB fdr#1 T/R 1X Nella fdr#2 load dropped 14 A (90-76A) 09:46 Nella VCB fdr#1 T/R 1X Nella fdr#2 load dropped 31 A (90-59A). Not checked yet. | 111 | 1 | 8:43 | Morning | Tuesday | 2017 | 5
6001 | 2017-05-30 08:43 | 2017-05-31 14:00 | 13.8KV NELLA FEEDER #1 | Fair | Lightning | 270 | Checked and found 13.8 KV VCB fdr #1 T/R 2x Ctr: 498-500 R/F: 51N @2 Patrolled the line and found broken LA o/p TP-BKO-18 Cause: Lightning Arrester | 111 | 1 | 8:43 | Morning | Tuesday | 2017 | 5
6002 | 2017-05-30 16:40 | 2017-05-30 16:40 | CENTRAL DURI POWER PLANT |  |  | - | 16:40 CGT #3 Off Line, then S/D for Stand by. Replaced A.A.Compressor. |  | 1 | 16:40 | Afternoon | Tuesday | 2017 | 5
6003 | 2017-05-31 02:12 | 2017-05-31 02:12 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | CD ACB fdr#2 T/R 1x, Ctr: 278-279, R/F: 50, @2,@3. Not checked yet. |  | 1 | 2:12 | Night | Wednesday | 2017 | 5
6004 | 2017-05-31 02:12 | 2017-04-06 07:10 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 0 | Checked & found C.Duri ACB fdr#12 T/R 1x, Ctr: 278-279, R/F: 50 @2. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 2:12 | Night | Wednesday | 2017 | 5
6005 | 2017-05-31 10:25 | 2017-05-31 10:25 | 13.8KV PETANI FEEDER #1 | Fair | Planned Maintenance | 439 | 10:25 Manually opened PETANI OCB fdr #1 Counter:33. Due to installed new Recloser on pole 33-AY-47. 13:38 Manually closed PETANI fdr #1. Cause: Plan Maintenance. |  | 1 | 10:25 | Morning | Wednesday | 2017 | 5
6006 | 2017-01-06 06:40 | 2017-01-06 06:40 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Pin Insulator | 0 | Duri Community ACB fdr#2 T/R 1x. Not checked yet. |  | 1 | 6:40 | Morning | Friday | 2017 | 1
6007 | 2017-01-06 06:40 | 2017-04-06 07:23 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Pin Insulator | 0 | Checked & found Duri Community ACB fdr#2 T/R 1x, Ctr: 77-78, R/F: 51N. Patrolled the Line , found @3 Broken Pin insulator Cause : Pin Insulator |  | 1 | 6:40 | Morning | Friday | 2017 | 1
6008 | 2017-01-06 07:25 | 2017-01-06 07:25 | CENTRAL DURI POWER PLANT |  |  | - | 07:25 CGT#5 S/U then Online the unit at 07:45. |  | 1 | 7:25 | Morning | Friday | 2017 | 1
6009 | 2017-01-06 15:40 | 2017-01-06 15:40 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 53 | 15:40 C.Duri fdr#2 T/LO, Ctr: 379-383 R/F: 51 @2, 50 @3 16:03 Blocked & closed C.Duri ACB #12 (feeder #2) ok. and then released block. Not patrolled yet. |  | 1 | 15:40 | Afternoon | Friday | 2017 | 1
6010 | 2017-01-06 15:40 | 2017-04-06 07:10 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 53 | Checked & found C.Duri ACB fdr#12 T/LO, Ctr: 379-383, R/F: 50 @2. Patrolled the line, found Dead monkey O/P SBB-12. Cause : Animal |  | 1 | 15:40 | Afternoon | Friday | 2017 | 1
6011 | 2017-02-06 06:05 | 2017-02-06 06:05 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 64 | 06:05 Petani OCB fdr#1 T/O Ctr: 33-34 R/F: 51N. (in block position, Rig activity). 06:10 Man. close Petani OCB fdr#1 afther confirm Rig APS#354. it was reported B/O fuse at AWT#02 TX Pet.GS. 09:10 Patrolled the Line found @3 b/o fuse for TX at AWT-02 Petani GS (the TX still Energize). Replaced the Fuse with the same size, then energized the TX. Cause : Animal (Bird) Not checked yet. |  | 1 | 6:05 | Morning | Monday | 2017 | 2
6012 | 2017-02-06 06:05 | 2017-03-06 18:01 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 64 | Patrolled the Line & found, @1, @3 Flash Over Pin Insulator. Cause : Lightning |  | 1 | 6:05 | Morning | Monday | 2017 | 2
6013 | 2017-02-06 06:07 | 2017-02-06 06:07 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 48 | 06:07 It was reported no power at well 10D-16 D/S 8C fdr #1. 10:32 Checked and found Recloser: 9D-111 T/SO Counter: 1235-1236. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 6:07 | Morning | Monday | 2017 | 2
6014 | 2017-02-06 06:23 | 2017-02-06 06:23 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 0 | Darling VCB fdr#3 T/R 1X. Not checked yet. |  | 1 | 6:23 | Morning | Monday | 2017 | 2
6015 | 2017-02-06 06:23 | 2017-04-06 13:19 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 0 | Checked & found Darling VCB fdr#3 T/R 1x, Ctr: 247-248, R/F: 51N @1. Patrolled the line, but found nothing. Cause : Unidentified |  | 1 | 6:23 | Morning | Monday | 2017 | 2
6016 | 2017-02-06 07:45 | 2017-02-06 07:45 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | C.Duri 13.8 Kv ACB #23 fdr #6 T/R 1x. Not checked yet. |  | 1 | 7:45 | Morning | Monday | 2017 | 2
6017 | 2017-02-06 07:45 | 2017-06-06 07:45 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | Checked & found, C. Duri ACB #23 fdr #6 T/R 1x ctr: 476-477 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:45 | Morning | Monday | 2017 | 2
6018 | 2017-02-06 09:33 | 2017-02-06 09:33 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 49 | Pinang OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 9:33 | Morning | Monday | 2017 | 2
6019 | 2017-02-06 09:33 | 2017-03-06 16:28 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 49 | Checked and found Pinang OCB fdr #1 T/R 1x Counter: 419-420 R/F: 51@2, Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 9:33 | Morning | Monday | 2017 | 2
6020 | 2017-02-06 09:51 | 2017-02-06 09:51 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Animal | 1 | 09:51 It was reported b/o fuse on pole 01-03-08 D/S C.Duri #6. 11:25 Checked and found @2,3 b/o fuse for Tx on pole 01-03-08. Peform TTR and Megger found good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (Squirrel). |  | 1 | 9:51 | Morning | Monday | 2017 | 2
6021 | 2017-02-06 21:15 | 2017-02-06 21:15 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr#1 Load dropped 32A(131-99A). Not checked yet. |  | 1 | 21:15 | Night | Monday | 2017 | 2
6022 | 2017-02-06 21:15 | 2017-05-06 21:15 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 38AS-09 T/R 1x ctr: 212-213. Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 21:15 | Night | Monday | 2017 | 2
6023 | 2017-03-06 05:49 | 2017-03-06 05:49 | 13.8KV MINAS FEEDER #3 | Fair | Lightning | 52 | 05:49 Minas ACB fdr#3 T/R 1X, ctr: 113-114, R/F: 51N. Not checked yet. |  | 1 | 5:49 | Morning | Monday | 2017 | 3
6024 | 2017-03-06 05:49 | 2017-09-06 05:49 | 13.8KV MINAS FEEDER #3 | Fair | Lightning | 52 | Check and found Minas Fdr #3 T/R 1X Ctr 113 - 114 R/F 51N Patrol the line but found nothing Cause : Lightning |  | 1 | 5:49 | Morning | Monday | 2017 | 3
6025 | 2017-03-06 10:44 | 2017-03-06 10:44 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Animal | 0 | 10:44 It was reported b/o fuse O/p 04-01-13A (C.Duri fdr#9). Checked and found @1, b/o fuse for 112.5 KVATX. Replaced the fuse with the same size then energized the Tx. Cause: Unidentified. |  | 1 | 10:44 | Morning | Monday | 2017 | 3
6026 | 2017-03-06 11:09 | 2017-03-06 11:09 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 65 | Sintong VCB fdr #2 T/R 1x. Sintong fdr#1 Load dropped 73A(96-23A). Not checked yet. |  | 1 | 11:09 | Morning | Monday | 2017 | 3
6027 | 2017-03-06 11:09 | 2017-06-06 08:09 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 65 | Checked & found Sintong VCB fdr#2 T/r 1x Ctr:458-459 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 11:09 | Morning | Monday | 2017 | 3
6028 | 2017-03-06 12:47 | 2017-03-06 12:47 | 13.8KV RANGAU FEEDER #2 | Fair | Animal | 13 | 12:47 It was reported b/o fuse at well Lampu#3 (Rangau fdr#2). 15:50 Checked & found @2 b/o fuse for 300KVATX. Replaced the fuse with the same size then Energized the TX. Cause: Animal. |  | 1 | 12:47 | Afternoon | Monday | 2017 | 3
6029 | 2017-04-06 00:05 | 2017-04-06 00:05 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | 00:05 Duri Community ACB fdr#1 T/R 1x. 15:18 Checked & found, Duri Community ACB fdr #1 T/R 1x ctr: 99-100 R/F: 51 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 0:05 | Night | Thursday | 2017 | 4
6030 | 2017-04-06 01:15 | 2017-04-06 01:15 | 13.8KV DARLING VCB FEEDER #4 | Rain and Lightning | Unidentified | 0 | 01:15 Darling VCB fdr #4 T/R 1X. 13:25 Checked & found Darling VCB fdr#4 Ctr: 134-135, R/F: 51 @1@2@3. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 1:15 | Night | Thursday | 2017 | 4
6031 | 2017-04-06 12:21 | 2017-04-06 12:21 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 43 | 12:21 It was reported b/o fuse at well Balam #156 (S.Balam #1) 14:26 Checked and found @3, b/o fuse for 100 Kva. Replaced the fuse with the same size then energized the Tx. Cause: Animal (Squirrel). |  | 1 | 12:21 | Afternoon | Thursday | 2017 | 4
6032 | 2017-04-06 15:07 | 2017-04-06 15:07 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr#1 Load dropped 39A(100-61A). Not checked yet. |  | 1 | 15:07 | Afternoon | Thursday | 2017 | 4
6033 | 2017-04-06 15:07 | 2017-05-06 15:07 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 38AS-09 T/R 1x ctr: 213-214. Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 15:07 | Afternoon | Thursday | 2017 | 4
6034 | 2017-05-06 02:36 | 2017-05-06 02:36 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Powerline - Jumper | 195 | 02:36 C.Duri fdr#4 Load dropped 90A(157-67A). It was reported No Power at Area#3 Road #1 and Area#4 Road #00. 04:30 Checked & found Recl. 03-01-39 T/SO (CD fdr#7). Found broken L.A and Dead Animal Squirrel. Tried Blocked & Closed the Recloser above, but Failed. Unplug the Recloser, transfer Loads to CD fdr#6. 05:06 Closed LBS 03-01-02 d/s CD fdr#6, now Area #3 Roads #1 back to normal. be continued trouble shoot Road. 07:00 Patrolled the line & found @2 Broken Jumper o/p 09-Q1-06. Repaired @2 Broken Jumper o/p 09-Q1-06. 07:55 Closed by pass switch off Recl. o/p 09-Q1-06. Cause: Broken Jumper. | 1111 | 1 | 2:36 | Night | Saturday | 2017 | 5
6035 | 2017-05-06 17:53 | 2017-05-06 17:53 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning Arrester | 173 | 17:53 Bangko 13.8KV OCB fdr #4 T/SO. Bangko GFPC T/R 1X. 18:46 Checked and found Bangko fdr #4 T/SO ctr:06-07 R/F:51N. Blocked and closed Bangko fdr #4, OK then released the block. Not patrolled yet. | 1111 | 1 | 17:53 | Afternoon | Saturday | 2017 | 5
6036 | 2017-05-06 17:53 | 2017-06-06 17:53 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning Arrester | 173 | Checked & found, Bangko OCB fdr #4 T/SO 1x ctr: 00006-00007 R/F: 51N @1. Patrolled the line & found, @1 broken Lightning Arrester at Terminal Pole of well Bangko #176. Cause : Lightning Arrester. | 1111 | 1 | 17:53 | Afternoon | Saturday | 2017 | 5
6037 | 2017-06-06 16:00 | 2017-06-06 16:00 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | 0 | 16:00 It was reported B/O fuse o/p 05-P5-16 (C.Duri fdr#15). 17:15 Replaced @1@2 B/O fuse for 112.5 Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 16:00 | Afternoon | Tuesday | 2017 | 6
6038 | 2017-06-06 16:44 | 2017-06-06 16:44 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 35 | Rangau fdr#2 Load dropped 184A (197-13A). Not checked yet. |  | 1 | 16:44 | Afternoon | Tuesday | 2017 | 6
6039 | 2017-06-06 16:44 | 2017-09-06 16:44 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 35 | Checked & found Recl. 23BD01 T/R 1x Ctr:203-204. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 16:44 | Afternoon | Tuesday | 2017 | 6
6040 | 2017-06-06 19:58 | 2017-06-06 19:58 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | 19:58 C. Duri 13.8KV ACB fdr #14 T/R 1X ctr:340-341 R/F 51 @1, @2 23:15 C. Duri 13.8KV ACB fdr #14 T/R 1X ctr:341-342 R/F 51 @1, @2. Not patrolled yet. | 1111 | 1 | 19:58 | Night | Tuesday | 2017 | 6
6041 | 2017-06-06 19:58 | 2017-07-06 19:58 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. | 1111 | 1 | 19:58 | Night | Tuesday | 2017 | 6
6042 | 2017-07-06 10:21 | 2017-07-06 10:21 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 259 | 10:21 Man. Opened Main Bekasap VCB fdr#2. (Replacing Recloser o/p 37BD12). 11:54 Closed Main Bekasap VCB fdr#2. Cause: Maintenance Job. |  | 1 | 10:21 | Morning | Thursday | 2017 | 7
6043 | 2017-07-06 14:45 | 2017-07-06 14:45 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Animal | 26 | 14:45 It was reported B/O fuse o/p 03-2-38. 15:15 Checked and founf @2 b/o fuse for 112.5KVA TX. Replaced @2 b/o fuse above with the same size, then energized the TX. Cause: Animal (Squirrel). |  | 1 | 14:45 | Afternoon | Thursday | 2017 | 7
6044 | 2017-08-06 10:17 | 2017-08-06 10:17 | 13.8KV NORTH DURI FEEDER #1 | Fair | Powerline - Conductor | 177 | 10:17 It was reported Broken conductor o/p 10-L1-35 (N.Duri fdr#1). 10:30 Checked & found @2 Broken Conductor o/p 10-L1-35. Recl. 10-L1-44 T/LO Ctr;139-141. Repaired @2 Broken conductor o/p 10-L1-35. 16:50 Closed LBS 10-L1-33A (Feed from N.Duri fdr#10). Cause: Broken Conductor. |  | 1 | 10:17 | Morning | Sunday | 2017 | 8
6045 | 2017-08-06 10:39 | 2017-08-06 10:39 | 13.8KV 5B FEEDER #4 | Fair | Planned Maintenance | 2 | 10:39-11:30 Blocked 5B fdr#4. Open HLC on TOP for replaced Broken Pin Insulator. 2 wells off during the job (4C-73 & 4C-54). Cause: Maintenance Job. |  | 1 | 10:39 | Morning | Sunday | 2017 | 8
6046 | 2017-09-06 02:32 | 2017-09-06 02:32 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 101 | 02:32 CKBS VCB fdr#5 T/R 1X. CKBS fdr#1 load dropped 13 A (265-252A) CKBS fdr#6 load dropped 86A (188-252A) Not checked yet. | 11111 | 1 | 2:32 | Night | Wednesday | 2017 | 9
6047 | 2017-09-06 02:32 | 2017-11-06 08:22 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 101 | Checked and found CKBS VCB Fdr # 5 T/R 1X Ctr: 156 R/F :NN Patrol the line found nothing Cause : Lightning | 11111 | 1 | 2:32 | Night | Wednesday | 2017 | 9
6048 | 2017-09-06 14:23 | 2017-09-06 14:23 | MINAS POWER PLANT |  |  | - | 14:23 S/U MGT#1, then on line the unit at 14:55 (Running Test). |  | 1 | 14:23 | Afternoon | Wednesday | 2017 | 9
6049 | 2017-09-06 14:47 | 2017-09-06 14:47 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 373 | 14:37 Man. Open Sintong VCB fdr#2. Replaced Broken Voltage Regulator at Benar . Replaced Pin Insulator at Benar field. 15:20 Blocked & closed Sintong fdr#2, then release the block. Blocked & closed Recl. 28AF02, then release the block. Casuse: Maintenance job. |  | 1 | 14:47 | Afternoon | Wednesday | 2017 | 9
6050 | 2017-09-06 17:37 | 2017-09-06 17:37 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | N. Duri VCB fdr #9 T/R 1X. Not checked yet. | 111111 | 1 | 17:37 | Afternoon | Wednesday | 2017 | 9
6051 | 2017-09-06 17:37 | 13/06/2017 07:30 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | Checked and found 13.8 KV N.Duri fdr #9 T/R 1x Ctr:043-044 R/F:51 Patrolled the line but found nothing (normal operation). Cause: Unidentified. | 111111 | 1 | 17:37 | Afternoon | Wednesday | 2017 | 9
6052 | 2017-09-06 19:02 | 2017-09-06 19:02 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Recloser | 0 | C. Duri ACB fdr #14 T/R 1X ctr:342-343 R/F: 51 @1, @2 Not checked yet. | 1111 | 1 | 19:02 | Night | Wednesday | 2017 | 9
6053 | 2017-09-06 19:02 | 13/06/2017 07:30 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Recloser | 0 | Checked and found 13.8 KV C.Duri fdr #14 (ACB #27) T/R 1x Ctr:342-343 R/F:51 @1 @2 Patrolled the line and found Broken Bushing Recloser o/p 06-P8-02 Cause: Recloser. | 1111 | 1 | 19:02 | Night | Wednesday | 2017 | 9
6054 | 2017-09-06 23:13 | 2017-09-06 23:13 | MINAS POWER PLANT |  |  | - | 23:13 MGT #5 S/D for S/B waiting for checking SRV. |  | 1 | 23:13 | Night | Wednesday | 2017 | 9
6055 | 2017-10-06 12:32 | 2017-10-06 12:32 | 13.8KV 4D FEEDER #2 | Rain | Lightning | 0 | 12:32 4D Fdr #2 T/LO 12:45 It was reported Broken Conductor at well 3D-96. 13:25 Checked & found 4D OCB fdr#2 T/LO Ctr:243-247 R/F: 51@2@3. Patrolled the line & found @2 Broken conductor Near well 3D-96 & 4D-11. 15:00 Isolated @2 Broken Conductor on TOP NN. 15:30 Blocked & closed 4D OCB fdr#2, then release the block. Cause: Lightning. |  | 1 | 12:32 | Afternoon | Friday | 2017 | 10
6056 | 2017-10-06 12:34 | 2017-10-06 12:34 | 4 DELTA SUBSTATION | Rain | Lightning Arrester | 261 | 12:34 4D 115Kv Tx-1 C/S T/O. 12:53 Open 3D OCB fdr#4 (Req GS#5), then closed at 13:48. 13:24 Open 4D OCB fdr#1, then closed at 13:32. Open 4D OCB fdr#3, the closed at 13:56. 13:25 Checked & found 4D 115Kv Tx-1 C/S T/O Ctr:1767-1768 R/F:87T @1@2@3. @2 Broken LA at 4D VR Tx-1. 13:30 Closed 4D 115Kv Tx-1 C/S. Cause: Lightning Arrester. |  | 1 | 12:34 | Afternoon | Friday | 2017 | 10
6057 | 2017-10-06 13:05 | 2017-10-06 13:05 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Rain | Lightning Arrester | 0 | 13:05 Dumai 4160V fdr#1 T/LO. 13:45 Checked & found Dumai 4160V fdr#1 T/LO Ctr:272-273 R/F:51N. Patrolled the line but found nothing. 13:50 Blocked & Closed Dumai 4160V fdr#1, then release the block. 14:30 Dumai 4160V fdr#1 T/SO again. 16:30 Checked & found Dumai 4160V fdr#1 T/SO Ctr:273-274 R/F 51N. Patrolled the line but found nothing. 16:30 Blocked & Closed Dumai 4160V fdr#1, but failed. 16:58 Patrolled again & found @1 Broken LA o/p WW-21. Dismantle @1 Broken LA o/p WW-21 . 17:30 Blocked & closed Dumai 4160V fdr#1, then release the block. Cause: Lightning Arrester. |  | 1 | 13:05 | Afternoon | Friday | 2017 | 10
6058 | 2017-10-06 13:54 | 2017-10-06 13:54 | BEKASAP MAIN SUBSTATION | Heavy Rain | Under investigation | 183 | 13:54 Bekasap Main 115Kv Tx-B C/S T/O. 14:18 Checked & found Bekasap Main 115Kv Tx-B C/S T/O Ctr:323-324 R/F:51G, 51N. 14:20 Open 44Kv GCB#1 BKS Main, then closed at 14:30. Open 44Kv GCB#2 BKS Main, then closed at 14:30. 14:22 Closed 115Kv Bekasap Main 115Kv Tx-B C/S. 14:29 Open Bekasap fdr#1, then closed at 14:33. Open Bekasap fdr#1, then closed at 14:34. Cause: Lightning. |  | 1 | 13:54 | Afternoon | Friday | 2017 | 10
6059 | 2017-10-06 16:34 | 2017-10-06 16:34 | 13.8KV CENTRAL DURI FEEDER #6 | Rain and Lightning | Lightning | 0 | C.Duri 13.8KV ACB#23 fdr#6 T/R 3x Ctr:477-480 R/F:51N,51@2. Not patrolled yet. |  | 1 | 16:34 | Afternoon | Friday | 2017 | 10
6060 | 2017-10-06 16:34 | 13/06/2017 07:30 | 13.8KV CENTRAL DURI FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked and found 13.8 KV C.Duri fdr #6 (ACB #23) T/R 3x Ctr:477-480 R/F:51 @2 @3 Patrolled the line and found Broken LA o/p 01-01-31 Cause: Lightning Arrester |  | 1 | 16:34 | Afternoon | Friday | 2017 | 10
6061 | 2017-11-06 12:12 | 2017-11-06 12:12 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | C.Duri Fdr #14 T/R 1X. Not checked yet. |  | 1 | 12:12 | Afternoon | Monday | 2017 | 11
6062 | 2017-11-06 12:12 | 14/06/2017 08:00 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | Checked and found 13.8 KV ACB #27 (C.Duri fdr #14) T/R 1x Ctr:342-343 Patrolled the line and found @1, @2 Broken bushing Recloser o/p 06-P8-02. Cause: Unidentified. |  | 1 | 12:12 | Afternoon | Monday | 2017 | 11
6063 | 2017-11-06 14:24 | 2017-11-06 14:24 | 13.8KV BATANG FEEDER #1 | Fair | Unidentified | 0 | Batang Fdr#1 T/R 1X Not checked yet. |  | 1 | 14:24 | Afternoon | Monday | 2017 | 11
6064 | 2017-11-06 14:24 | 15/06/2017 07:24 | 13.8KV BATANG FEEDER #1 | Fair | Unidentified | 0 | Checked and found 13.8 KV Batang fdr #1 T/R 1x Ctr:137-138 R/F:51 @1 Patrolled the line but found nothing. Cause: Unidentified |  | 1 | 14:24 | Afternoon | Monday | 2017 | 11
6065 | 2017-11-06 15:40 | 2017-11-06 15:40 | 13.8KV DURI FIELD FEEDER #4 | Fair | Under investigation | 0 | 15:40 Duri Field fdr#4 T/R 2x. 15:00 Checked & found Duri Field fdr#4 T/R 2x Ctr:483-485 R/F:50@1@2@3. Also found broken Re closing coil of ACB#51 Duri Field fdr#4. 17:24 Closed LBS 06-R4-02 Transfer to C.Duri fdr#14. Cause: Broken Closing Coil. |  | 1 | 15:40 | Afternoon | Monday | 2017 | 11
6066 | 2017-11-06 15:40 | 2017-11-06 15:40 | DURI FIELD SWITCH GEAR | Fair | Circuit Breaker | 368 | 15:40 115Kv DRB GCB#28 T/O, ----->Closed at 16:42 115Kv DRB GCB#30 T/O, ----->Closed at 16:55. 13.8Kv Duri Field SW ACB#54 T/O, ----->Closed at 16:50. (No power to Duri Field TX-5). 13.8KV Duri Field ACB fdr #4 T/SO 2X. 15:55 Checked & found 115Kv DRB GCB#28 T/O Ctr:173. 115Kv DRB GCB#30 T/O Ctr:95. 13.8Kv Duri Field SW ACB#54 T/O Ctr:514. 13.8KV Duri Field ACB fdr #4 T/SO 2X ctr:485 R/F:50 @1, @2, @3. Also found broken Tripping Coil of Duri Field ACB fdr #4. Checked 28MVA Tx-5 DRB Good Condition no R/F. 16:00 Open Duri Field ACB fdr#3, ----->then closed at 16:54. Cause: Broken Tripping Coil of Breaker. |  | 1 | 15:40 | Afternoon | Monday | 2017 | 11
6067 | 2017-12-06 02:05 | 2017-12-06 02:05 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri Community ACB fdr #2 T/R 1X. Not checked yet. | 111 | 1 | 2:05 | Night | Wednesday | 2017 | 12
6068 | 2017-12-06 02:05 | 13/06/2017 20:05 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Checked & found Duri Community fdr#2 T/R 1x Ctr:78-79 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. | 111 | 1 | 2:05 | Night | Wednesday | 2017 | 12
6069 | 2017-12-06 06:08 | 2017-12-06 06:08 | CENTRAL DURI POWER PLANT |  |  | - | Off line and then S/D CGT #2 to Re Certification Gas Scrubber SRV. |  | 1 | 6:08 | Morning | Wednesday | 2017 | 12
6070 | 2017-12-06 14:30 | 2017-12-06 14:30 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 112 | Manually opened 4D OCB fdr #2. Due to Tie in near well 3D-96. Cause: Plan Maintenance. |  | 1 | 14:30 | Afternoon | Wednesday | 2017 | 12
6071 | 2017-12-06 17:08 | 2017-12-06 17:08 | 6 DELTA SUBSTATION | Fair | Animal | 627 | 17:08 6D OCB fdr #4 Trip. 6D OCB fdr #5 Trip. 17:09 6D OCB fdr #2 Trip (in blocked position). 17:12 115 Kv 6D C/S Tx #2 Trip Closed at :18:12. 115 Kv 6D C/S Tx #1 Trip Closed at :18:15. 17:45 Checked & found 115 Kv 6D C/S Tx #2 T/O Ctr:296-297 R/F:51N. 115 Kv 6D C/S Tx #1 T/O Ctr:115-116 R/F:87T,51G. 13.8Kv 6D OCB fdr#4 T/O Ctr:556-557 R/F:81. 13.8Kv 6D OCB fdr#5 T/O Ctr:771-772 R/F:81. 17:50 Checked 6D Tx-1 & Tx-2 Good condition. 18:47 Opened 6DOCB fdr#1, then closed at 18:19. 18:49 Opened 6DOCB fdr#3, then closed at 18:19. 17:45 Opened 6DOCB fdr#6, then closed at 18:17. 17:15 Opened 6DN OCB fdr#5 (Req GS#5), then closed at 19:21. 17:43 Opened 6DN OCB fdr#6 (Req GS#5), then closed at 18:17. 18:12 Closed 115Kv 6D Tx-2 C/S. 18:15 Closed 115Kv 6D Tx-1 C/S. 18:16 Closed 6D OCB fdr#4. 19:34 Closed 6D OCB fdr#5. 19:35 Closed 6D OCB fdr#2. Cause: Animal (Monkey). | 11111 | 1 | 17:08 | Afternoon | Wednesday | 2017 | 12
6072 | 2017-12-06 17:08 | 14/06/2017 08:11 | 6 DELTA SUBSTATION | Fair | Animal | 627 | Checked & found 6D Substation -- 115KV CS TX#1 T/O , Ctr: 115-116, R/F: 87T. 115KV CS TX#2 T/O , Ctr: 296-301, R/F: 51N. Patrolled the Line, found Monkey got electric shock Under those TX. Cause : Animal | 11111 | 1 | 17:08 | Afternoon | Wednesday | 2017 | 12
6073 | 2017-12-06 20:05 | 2017-12-06 20:05 | 13.8KV 6D FEEDER #2 | Fair | Lightning | 25 | 20:05 6D fdr#2 load dropped 170A (240-70A). 20:42 Checked & Found Recl. 6D-298 T/LO Ctr:66. Blocked & closed Recl. 6D-298, but failed 21:44 Patrolled The line but not found. 21:45 Open LBS 6D-68. 21:47 Blocked & Closed Recl 6D-298,ok 22:08 Patrolled the line & found ,broken LA at LBS 6D-68 22:14 Isolated broken LA at LBS 6D-68 22:25 Open LBS 6D-66, then closed at 22:30 22:27 Closed LBS 6D-68. Cause: Broken LA. |  | 1 | 20:05 | Night | Wednesday | 2017 | 12
6074 | 2017-12-06 20:05 | 14/06/2017 08:17 | 13.8KV 6D FEEDER #2 | Fair | Lightning | 25 | Checked & found Recl. 6D-298 T/LO, Ctr: 62-66, R/F: None. Patrolled the Line, found @2 broken LA o/p 6D-68 Cause : Lightning |  | 1 | 20:05 | Night | Wednesday | 2017 | 12
6075 | 2017-06-13 06:00 | 2017-06-13 06:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 184 | 06:00 C Duri ACB #11 (fdr #1) T/R 1x Counter : 200-201 R/F: 51@1. 06:25 It was reported no power at road 09-0L7 & 08-L5. 07:26 Checked and found Recloser SBB #06 T/O ( in blocked position due to PT WKS clean up canal) Counter:131-132. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 6:00 | Morning | Tuesday | 2017 | 6
6076 | 2017-06-13 10:00 | 2017-06-13 10:00 | CENTRAL DURI POWER PLANT |  |  | - | CDGT#2 Started Up, then On Line to System at 11:04. To Restore Power after Re sertification Gas Scrubber & SRV. |  | 1 | 10:00 | Morning | Tuesday | 2017 | 6
6077 | 2017-06-13 20:03 | 2017-06-13 20:03 | 13.8KV DURI FIELD FEEDER #4 | Rain | Unidentified | 0 | Duri Field ACB#51 Fdr #4 T/R 1X Not Checket yet. |  | 1 | 20:03 | Night | Tuesday | 2017 | 6
6078 | 2017-06-13 20:03 | 2017-06-17 07:56 | 13.8KV DURI FIELD FEEDER #4 | Rain | Unidentified | 0 | Checked & found DF ACB fdr#4 T/R 1x, Ctr: 503-504, R/F: 51N. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 20:03 | Night | Tuesday | 2017 | 6
6079 | 2017-06-13 21:35 | 2017-06-13 21:35 | 13.8KV 8C FEEDER #3 | Fair | Unidentified | 97 | 8C Fdr# 3 Load dropped 176 A (208-32A) Not Checked yet. |  | 1 | 21:35 | Night | Tuesday | 2017 | 6
6080 | 2017-06-13 21:35 | 2017-06-14 15:41 | 13.8KV 8C FEEDER #3 | Fair | Unidentified | 97 | Checked & found Recl. 8D-18A T/R 1x, Ctr: 37-38, R/F: None. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 21:35 | Night | Tuesday | 2017 | 6
6081 | 2017-06-14 00:19 | 2017-06-14 00:19 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 44 | 8D OCB fdr#7 T/R 1x. Checked & found 8D OCB fdr#7 T/R 1x, Ctr: 632-633, R/F: 51N. Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 0:19 | Night | Wednesday | 2017 | 6
6082 | 2017-06-14 07:12 | 2017-06-14 07:12 | 13.8KV MINAS FEEDER #4 | Rain | Lightning | 110 | 07:12 Minas ACB #1 (fdr #4) T/R 1x, Ctr: 70-71, R/F: 51N. 12:12 Minas ACB #1 (fdr #4) T/R 1x, Ctr: 71-72, R/F: 51@1. Not Patrolled yet. |  | 1 | 7:12 | Morning | Wednesday | 2017 | 6
6083 | 2017-06-14 07:12 | 2017-06-24 04:36 | 13.8KV MINAS FEEDER #4 | Rain | Lightning | 110 | Checked & found Rcl: 7D121 T/SO, Ctr: 12-14, R/F: None. Patrolled the Line, found @2 broken Conductor o/p 7D122 Cause : Lightning |  | 1 | 7:12 | Morning | Wednesday | 2017 | 6
6084 | 2017-06-14 13:15 | 2017-06-14 13:15 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 1 | 13:15 It was reported b/o fuse on pole 02-03-02 D/S C.Duri fdr #3. 16:00 Checked and found @1,@1 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above and energized the Tx. Cause: Unidentified. |  | 1 | 13:15 | Afternoon | Wednesday | 2017 | 6
6085 | 2017-06-15 06:50 | 2017-06-15 06:50 | 13.8KV 8D FEEDER #5 | Fair | Unidentified | 27 | Minas 8D Fdr #5 T/R 1X. Not Checked yet. |  | 1 | 6:50 | Morning | Thursday | 2017 | 6
6086 | 2017-06-15 06:50 | 2017-06-23 23:10 | 13.8KV 8D FEEDER #5 | Fair | Unidentified | 27 | Checked & found 8D OCB fdr#5 T/R 1x, Ctr: 566-566, R/F: None. Was Not Patrolled, due to OCBs counter not change. Cause : Unidentified |  | 1 | 6:50 | Morning | Thursday | 2017 | 6
6087 | 2017-06-15 08:59 | 2017-06-15 08:59 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Low mega-ohm reading | 0 | 08:59 It was reported b/o fuse on pole 09-S4-04 D/S C Duri fdr #4. 15:17 Checked and found @2,@3 b/o fuse for 112.5 Kva Tx. Perform TTR and Megger found low megger reading. Cause: Tx failure (low megger reading). This Tx is not replaced yet. |  | 1 | 8:59 | Morning | Thursday | 2017 | 6
6088 | 2017-06-15 08:59 | 2017-06-17 09:00 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Low mega-ohm reading | 0 | Replaced Failure 112.5KVATX with the Same Size o/p 09-S4-04 (C.Duri fdr#4). Then Energized the TX. Cause : Low megger reading |  | 1 | 8:59 | Morning | Thursday | 2017 | 6
6089 | 2017-06-15 10:40 | 2017-06-15 10:40 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 102 | 10:40 Manually opened PUNGUT OCB fdr #2. For replacing 2 pcs Recloser on pole 45-BR-01 and 43-BY-25. 13:37 Manually closed PUNGUT OCB fdr #2. Cause: Plan Maintenance. Production loss PUNGUT GS : 71 Bbls / 15 wells. LIBO GS :19 Bbls / 6 wells. --------------------------------------- + Total : 90 Bbls / 21 wells. |  | 1 | 10:40 | Morning | Thursday | 2017 | 6
6090 | 2017-06-15 21:54 | 2017-06-15 21:54 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Lightning | 0 | C.Duri ACB fdr#5 T/R 1x Ctr:245-246 R/F:51G@2, 51N@2. Not patrolled yet. |  | 1 | 21:54 | Night | Thursday | 2017 | 6
6091 | 2017-06-15 21:54 | 2017-06-17 08:01 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Lightning | 0 | Checked & found CD ACB fdr#5 T/R 1x, Ctr: 245-246, R/F: 51N @2. Patrolled the Line, found broken Jumper LA o/p 03-06-17. Cause : Lightning |  | 1 | 21:54 | Night | Thursday | 2017 | 6
6092 | 2017-06-15 23:17 | 2017-06-15 23:17 | 13.8KV MINAS FEEDER #3 | Fair | Others | 54 | 23:17 Minas ACB Fdr#3 T/LO Ctr : 80114 - 80116 R/F 50 @2@3. Minas Fdr # 1 Load drop 107 Amp ( 193 - 86 ) Minas Fdr#4 Load drop 76 Amp ( 220 - 144 ) 23:23 Blocked & closed Minas ACB fdr#3, then release the block. Not patrolled yet. |  | 1 | 23:17 | Night | Thursday | 2017 | 6
6093 | 2017-06-15 23:17 | 2017-06-22 06:07 | 13.8KV MINAS FEEDER #3 | Fair | Others | 54 | Checked & found Minas ACB fdr#2 T/LO, Ctr: 80114 - 80116, R/F: 50 @2@3. Patrolled the Line, found Kite hank up o/p 7D-140. Cause : Others |  | 1 | 23:17 | Night | Thursday | 2017 | 6
6094 | 2017-06-15 23:18 | 2017-06-15 23:18 | MINAS POWER PLANT | Fair | Under investigation | 0 | MGT #1 Trip By alarm exiter trouble and differential lock out. |  | 1 | 23:18 | Night | Thursday | 2017 | 6
6095 | 2017-06-16 00:02 | 2017-06-16 00:02 | MINAS POWER PLANT | Fair |  | - | 00:02 S/U MGT # 5 , then on line the limit at 00:24. |  | 1 | 0:02 | Night | Friday | 2017 | 6
6096 | 2017-06-16 10:38 | 2017-06-16 10:38 | 13.8KV ROKAN FEEDER #2 | Fair | Planned Maintenance | 2 | 10:38 Opened HLC on pole 29-AV-40 D/S ROKAN fdr #2. For repairing @1 broken LA on Terminal pole Kopar #08. 11:05 Closed Hot line clamp on pole 29-AV-40. Cause: Plan Maintenance. |  | 1 | 10:38 | Morning | Friday | 2017 | 6
6097 | 2017-06-16 14:34 | 2017-06-16 14:34 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Powerline - Jumper | 41 | 14:34 It was reported b/o fuse on pole 03-04-20 D/S C. Duri fdr #5. 15:08 Checked and found @1 broken jumper HLC on pole 02-04-20. Cause: Broken Jumper. Will be replace tomorrow. |  | 1 | 14:34 | Afternoon | Friday | 2017 | 6
6098 | 2017-06-16 16:30 | 2017-06-16 16:30 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 12 | 16:30 It was reported b/o fuse on pole 13-G4-10 D/S N.Duri fdr #2. 18:00 Checked and found @3 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified. |  | 1 | 16:30 | Afternoon | Friday | 2017 | 6
6099 | 2017-06-17 18:23 | 2017-06-17 18:23 | 4.16KV NO RUMBAI FEEDER #2 | Rain and Lightning | Unidentified | 0 | N.Rumbai 4160V fdr#2 T/R 1x. Not checked yet. |  | 1 | 18:23 | Afternoon | Saturday | 2017 | 6
6100 | 2017-06-17 18:23 | 2017-06-23 10:13 | 4.16KV NO RUMBAI FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found North Rumbai fdr#2 T/R 1x, Ctr: 342-343, R/F: 51. Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 18:23 | Afternoon | Saturday | 2017 | 6
6101 | 2017-06-17 18:56 | 2017-06-17 18:56 | 13.8KV 6D FEEDER #3 | Rain and Lightning | Unidentified | 22 | 6D Fdr #3 Load dropped 213 A(234-21A). 6D fdr#1 Load drooped 105A (233-128A). Not checked yet. |  | 1 | 18:56 | Afternoon | Saturday | 2017 | 6
6102 | 2017-06-17 18:56 | 2017-06-24 04:45 | 13.8KV 6D FEEDER #3 | Rain and Lightning | Unidentified | 22 | Checked & found Recl: 6D03 Open, Ctr: not change, R/F: None. Patrolled the Line, but found nothing, (6DN fdr#3 transfer to 6D fdr#3) Cause : Unidentified |  | 1 | 18:56 | Afternoon | Saturday | 2017 | 6
6103 | 2017-06-17 18:56 | 2017-06-17 18:56 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Unidentified | 43 | 6D fdr#2 Load dropped 121A (231-110A). Not checked yet. |  | 1 | 18:56 | Afternoon | Saturday | 2017 | 6
6104 | 2017-06-17 18:56 | 2017-06-24 04:44 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Unidentified | 43 | Checked & found - Rcl: 6D87 Not working, Ctr: 67-67, R/F : None. - Rcl: 6D87 Not working, Ctr: 61-61, R/F : None. Patrolled the Lne, but found nothing. Cause : Unidentified |  | 1 | 18:56 | Afternoon | Saturday | 2017 | 6
6105 | 2017-06-17 19:00 | 2017-06-17 19:00 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 0 | 6D fdr#5 Load dropped 158A (238-80A), Not checked yet. |  | 1 | 19:00 | Night | Saturday | 2017 | 6
6106 | 2017-06-17 19:00 | 2017-06-22 06:51 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found Minas 6D OCB fdr#5 T/R 1x, Ctr: 772-773, R/F: 50 @2. Patrolled the Line, found @2 broken Pin and Deadend insulator o/p 6D-504. Cause : Lightning |  | 1 | 19:00 | Night | Saturday | 2017 | 6
6107 | 2017-06-17 19:01 | 2017-06-17 19:01 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning Arrester | 368 | 19:01 Minas ACB#2 fdr#3 T/R 1x Counter: 80116-80117. 19:03 Minas ACB#2 fdr#3 T/R 1x Counter: 80117-80118. 19:13 Minas ACB#2 fdr#3 T/R 1x Counter: 80118-80119. 19:28 Minas ACB#2 fdr#3 T/R 1x Counter: 80119-80120. 19:29 Minas ACB#2 fdr#3 T/LO. June 18,2017. 20:00 Checked and found Minas ACB#2 fdr#3 T/LO Counter:80120-80122 R/F:51N. 00:30 Manually opened Recloser 7D-81. Closed at 01:13 Manually opened Recloser 7D-93. Closed at 01:16 00:42 Blocked and closed Minas ACB #2 (feeder #3) but failed. Patrolled the line found @2 broken Lightning Arrester on pole 7D-80 (600 Kvar Cap Bank) touch to cross arm. Opened jumper of Cap Bank. 01:10 Blocked and closed Minas ACB #2 (feeder #3) --> OK and then released the block. Cause: Broken Lightning Arrester. |  | 1 | 19:01 | Night | Saturday | 2017 | 6
6108 | 2017-06-17 19:01 | 2017-06-21 02:30 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning Arrester | 368 | It was reported Minas ACB fdr#3 T/LO, Ctr: 80116-80120, R/F: 51N @2. Patrolled the Line, found broken LA jumper closed to Cross arm o/p 7D-80. Cause : Lightning Arrester |  | 1 | 19:01 | Night | Saturday | 2017 | 6
6109 | 2017-06-17 19:08 | 2017-06-17 19:08 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | 3D fdr#4 Load Dropped 142A(235-93A). Not checked yet. |  | 1 | 19:08 | Night | Saturday | 2017 | 6
6110 | 2017-06-17 19:08 | 2017-06-22 06:49 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found Recloser 2D-14 T/R 1x, Ctr: 47-48, R/F: None. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 19:08 | Night | Saturday | 2017 | 6
6111 | 2017-06-17 19:09 | 2017-06-17 19:09 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Powerline - Jumper | 558 | 19:09 Minas ACB#1 fdr#4 T/LO. 22:20 Checked and found Minas ACB #1 (feeder #4) T/LO Counter: 72-74 R/F:51 @1,2,3. Patrolled the line found @2 broken conductor between poles 7D-121 to 7D-122. 22:31 Manually opened Recloser 7D-121 to isolated broken conductor. Blocked and closed Minas ACB #1 (feeder#4) --> OK and then released the block. 23:43 Cut jumpers on pole 7D-122 to isolated wells 8D-12 and 8D-23N (LTC well). Blocked and closed Recloser 7D-121 --> OK and then released the block. Cause: Broken jumper. | 11111 | 1 | 19:09 | Night | Saturday | 2017 | 6
6112 | 2017-06-17 19:09 | 2017-06-21 02:30 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Powerline - Jumper | 558 | Checked & found Minas ACB fdr#4 T/LO, Ctr: 72-74, R/F: 51 @1@2@3. Patrolled the Line, found broken jumper o/p 7D-122, toward well 7D-12 Cause : Jumper | 11111 | 1 | 19:09 | Night | Saturday | 2017 | 6
6113 | 2017-06-17 19:09 | 2017-06-17 19:09 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 78 | Minas fdr#1 Load dropped 157A (204-47A). Not checked yet. |  | 1 | 19:09 | Night | Saturday | 2017 | 6
6114 | 2017-06-17 19:09 | 2017-06-24 04:49 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 78 | Checked & found MNS ACB fdr#1 T/R 1x, Ctr: 70-71, R/F: 51N Patrolled the line, found broken Dead end Cause : Lighning |  | 1 | 19:09 | Night | Saturday | 2017 | 6
6115 | 2017-06-17 19:33 | 2017-06-17 19:33 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Tree | 27 | 3D OCB fdr#3 T/R 1x. 3D GFPC Tx-1 T/R 1x ctr: 4117-4118. Not checked yet 3D Fdr #4 Load drop 142 Amp ( 235 - 93 ) 06:30 Checked and found Recl 2D - 33 T/SO. Blocked and closed Recl 2D - 33 counter : 42 - 43 Not Patrolled yet. |  | 1 | 19:33 | Night | Saturday | 2017 | 6
6116 | 2017-06-17 19:33 | 2017-06-22 07:07 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Tree | 27 | Patrolled the line & found, Palm Tree touched power line on Pole 4C 24B. Cause: Tree. |  | 1 | 19:33 | Night | Saturday | 2017 | 6
6117 | 2017-06-17 19:35 | 2017-06-17 19:35 | 13.8KV 4D FEEDER #6 | Rain and Lightning | Lightning | 4 | 4D OCB fdr#6 T/R 1x. 4D fdr#4 Load dropped 32A (50-18A). 4D fdr#5 Load dropped 108A (170-62A). Not checked yet. |  | 1 | 19:35 | Night | Saturday | 2017 | 6
6118 | 2017-06-17 19:35 | 2017-06-24 04:57 | 13.8KV 4D FEEDER #6 | Rain and Lightning | Lightning | 4 | Checked & found, 4D OCB fdr#6 T/R 2x, Ctr: 182-184, R/F: 51 @2@3. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 19:35 | Night | Saturday | 2017 | 6
6119 | 2017-06-17 20:06 | 2017-06-17 20:06 | 13.8KV PETANI FEEDER #1 | Rain | Unidentified | 66 | Petani fdr#1 Load dropped 97A (198-101A) Production loss : 65 Bbls / 36 wells. Petani fdr#2 Load dropped 47A (60-13A). Production loss : 32 Bbls / 24 wells. Not checked yet. ----------------------------------------- + Total : 97 Bbls / 60 wells. |  | 1 | 20:06 | Night | Saturday | 2017 | 6
6120 | 2017-06-17 20:06 | 2017-06-22 09:38 | 13.8KV PETANI FEEDER #1 | Rain | Unidentified | 66 | Checked & Patrolled the line of Petani fdr #2 But found nothing Cause : Unidentified |  | 1 | 20:06 | Night | Saturday | 2017 | 6
6121 | 2017-06-17 20:54 | 2017-06-17 20:54 | 4.16KV SO RUMBAI FEEDER #3 | Rain and Lightning | Unidentified (Fuse) | 0 | It was reported no power at Enau 251 and 252 ( So Rumbai Fdr#3 ) 02:30 Checked and found @1 Broken fuse for 50 Kva TX o/p NN Replaced @1 B/O fuse for 50 Kva Tx Caused : unidentified. |  | 1 | 20:54 | Night | Saturday | 2017 | 6
6122 | 2017-06-17 21:23 | 2017-06-17 21:23 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Powerline - Conductor | 832 | 21:23 Bekasap VCB fdr #6 T/LO. Checked and found Bekasap VCB fdr #6 T/LO Counter: 353-357 R/F: 51@2,3. 23:02 Patrolled the line found @2,@3 broken conductor between poles 39-BH-01A to 39-BH-01C. June,18,2017. 00:30 Isolated conductor by cut jumpers on pole 39-BH-01A towards well Aman #12 & 02. Blocked and closed Bekasap VCB fdr #6 --> OK and then released the block. Cause: Broken conductor. 00:46 Bekasap ACB fdr#6 T/LO again. Patrolled the Line, found @2 broken bypass switch for Recl. 38-BE-10. Open & Cut Jumper @2 bypass switch. 02:28 Blocked & Closed BKS fdr#6, then released the Block. (No Power under Recl. 38-BE-10. 10-20 Man. Open BKS ACB fdr#6 to Replace broken Jumper and bypass switch Recl. 38-BE-10. (18 Wells were Down while doing the Jobs). 11:45 Blocked & Closed Bekasap ACB fdr#6, then released the block. Cause: Jumper (Bypass switch). | 11111 | 1 | 21:23 | Night | Saturday | 2017 | 6
6123 | 2017-06-18 23:59 | 2017-06-18 23:59 | CPI POWER SYSTEM |  |  | - | Normal system condition. |  | 1 | 23:59 | Night | Sunday | 2017 | 6
6124 | 2017-06-19 05:58 | 2017-06-19 05:58 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 86 | Ketigul VCB fdr #2 T/R 1x. Ketigul fdr #1 load dropped 10A (95-85A). not checked yet. |  | 1 | 5:58 | Morning | Monday | 2017 | 6
6125 | 2017-06-19 05:58 | 2017-06-22 09:42 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 86 | Checked & found Ketigul ACB fdr#2 T/R 1x, Ctr: 308-309, R/F: 51N @1. Patrolled the Line, found @1 broken dead end insulator o/p NN Take off pole of well Pagar #30. Cause : Lightning |  | 1 | 5:58 | Morning | Monday | 2017 | 6
6126 | 2017-06-19 11:04 | 2017-06-19 11:04 | 13.8KV BEKASAP FEEDER #6 | Fair | Planned Maintenance | 232 | 11:04-14:10 Manual open Bekasap Fdr#6 and rackout the breaker to modification HLC to T Tap of bypass Recl 38 BE 10 Recloser Bypass position due to control problem Cause : Plan Maintenance. |  | 1 | 11:04 | Morning | Monday | 2017 | 6
6127 | 2017-06-19 11:20 | 2017-06-19 11:20 | 13.8KV 5B FEEDER #8 | Fair | Planned Maintenance | 46 | 11:20 Manually opened 5B OCB fdr #6. Due to replaced @1 broken Fuse Cut Out for DBP #45 at GS #4. 12:12 Manually closed 5B OCB fdr #6. Cause : Plan Maintenance. |  | 1 | 11:20 | Morning | Monday | 2017 | 6
6128 | 2017-06-19 14:12 | 2017-06-19 14:12 | 13.8KV PEMATANG FEEDER #1 | Fair | Powerline - Conductor | 410 | 14:12 Pematang OCB fdr#1 T/R 1x. Pematang fdr #2 load dropped 42A (58-16A). Rangau fdr #1 load dropped 35A (73-38A). Rangau fdr #2 load dropped 163A (178-15A). 14:55 Checked and found Pematang OCB fdr #1 T/R 1x Counter:136-137 R/F: 51@3. Patrolled the line found @3 broken conductor in front of Pematang GS. Manually opened Pematang OCB fdr #1 15:15 Manually opened Rangau fdr #2 (request Rangau GS) to maintain oil level. 15:23 Manually opened Pematang fdr #2 Repair @3 broken conductor in front of Pematang GS. 16:47 Manually closed Pematang fdr #1. Production loss : 180 Bbls / 18 wells. 17:10 Manually closed Pematang fdr #2. Production loss : 161 Bbls / 17 wells. 18:58 Manually closed Rangau fdr #2. Production loss : 135 Bbls / 54 wells. --------------------------------------------- + Total : 476 Bbls / 89 wells. Cause: Broken Conductor. |  | 1 | 14:12 | Afternoon | Monday | 2017 | 6
6129 | 2017-06-19 19:56 | 2017-06-19 19:56 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | C.Duri ACB # 27 ( Feeder #14 ) T/R 2X Counter : 344-346 R/F : 51 @1,2. Not Patrolled yet. |  | 1 | 19:56 | Night | Monday | 2017 | 6
6130 | 2017-06-19 19:56 | 2017-06-24 12:20 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | Checked & found CD fdr#14 T/R 2x, Ctr: 344-346, R/F: 51 @1. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 19:56 | Night | Monday | 2017 | 6
6131 | 2017-06-20 08:54 | 2017-06-20 08:54 | CENTRAL DURI POWER PLANT |  |  | - | Started Up CGT #3 and On line at 09:12 to back up load. |  | 1 | 8:54 | Morning | Tuesday | 2017 | 6
6132 | 2017-06-20 10:33 | 2017-06-20 10:33 | KETIGUL SUBSTATION | Fair | Planned Maintenance | 1082 | 10:33 Manually open 13.8KV Ketigul VCB fdr # 1, ----->Closed at 15:11 Prod loss: 234 Bbls / 20 wells. 10:35 Manually open 13.8KV Ketigul VCB fdr # 2, ----->Closed at 15:11 Prod loss: 830 Bbls / 45 wells. 10:36 Manually open 13.8KV Ketigul VCB fdr # 3, ----->Closed at 15:10 Prod loss: 57 Bbls / 4 wells. ---------------------------------- + Total : 1121 Bbls/69 wells. 10:37 Manually open 115KV Ketigul GCB # 2, ----->Closed at 15:06. 10:46 Manually open 115KV Ketigul GCB # 3, ----->Closed at 15:10. Purpose: Service leakage on Terminal Bushing of Ketigul Transformer. Replaced broken Recloser. Production loss: Dismantled Line VR. Replace broken Insulator. Cause: Plan Maintenance. | 11111 | 1 | 10:33 | Morning | Tuesday | 2017 | 6
6133 | 2017-06-20 10:40 | 2017-06-20 10:40 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 49 | 10:40 It was reported b/o fuse at well MeNo #15. 16:30 Checked and found @2 b/o fuse for 150KVA TX. Replaced b/o fuse above with same size, then energized the TX. OK. Cause: Animal (Monkey). |  | 1 | 10:40 | Morning | Tuesday | 2017 | 6
6134 | 2017-06-20 17:00 | 2017-06-20 17:00 | CENTRAL DURI POWER PLANT |  |  | - | 17:00 Off line and then S/D CGT #4 for S/B waiting for Cleaning Inlet House. |  | 1 | 17:00 | Afternoon | Tuesday | 2017 | 6
6135 | 2017-06-21 00:41 | 2017-06-21 00:41 | 13.8KV 6D FEEDER #1 | Fair | Unidentified | 68 | 6D OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 0:41 | Night | Wednesday | 2017 | 6
6136 | 2017-06-21 00:41 | 2017-06-26 08:00 | 13.8KV 6D FEEDER #1 | Fair | Unidentified | 68 | Checked and found no Recloser operated. Causes: Unidentified. |  | 1 | 0:41 | Night | Wednesday | 2017 | 6
6137 | 2017-06-21 00:42 | 2017-06-21 00:42 | 13.8KV 6D FEEDER #3 | Fair | Unidentified | 0 | 6D fdr #2 load dropped 61A (250-189A). Production loss: 0. 6D fdr #3 load dropped 125A (340-215A) Production loss: 26 Bbls / 16 wells. Not checked yet. |  | 1 | 0:42 | Night | Wednesday | 2017 | 6
6138 | 2017-06-21 00:42 | 2017-06-24 05:04 | 13.8KV 6D FEEDER #3 | Fair | Unidentified | 0 | Checked & found Recl.6D03 T/SO, R/F: None. Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 0:42 | Night | Wednesday | 2017 | 6
6139 | 2017-06-21 15:00 | 2017-06-21 15:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 4 | 15:00 It was reported Lube Oil leakage of 112.5KVA TX o/p 08. L7. 18. 16:45 Replaced the TX with same size. then energized the TX. OK. Cause: TX. failure. |  | 1 | 15:00 | Afternoon | Wednesday | 2017 | 6
6140 | 2017-06-21 16:17 | 2017-06-21 16:17 | 13.8KV DURI FIELD FEEDER #3 | Fair | Others | 9 | 16:17 Duri Field 13.8KV VCB fdr #3 T/LO ctr: 362-366 R/F: 51 @!, @2 & @3. 16:40 Checked and found D. Field fdr #3 T/LO. 16:52 Blocked and closed Duri Field fdr #3. OK then released the block. It was reported unbalance voltage at CGS #1. 17:10 Checked and found broken insulator of Bypass switch of Recloser o/p 01. 05. 01. (Recloser was dismantled & its by Pass switches were closed). Open LBS 01.05.01 and closed LBS 01.03.01A. (CGS #1 de feed from C. Duri fdr #6). 17:20 Checked and found @1, @2 &@3 broken insulator of Bypass Switch of Recloser 01. 05. 01. Isolated the by Pass Switch above. Open LBS 01. 03. 01A. 17:40 Closed LBS 01.05.32 (CGS #1 de feed from Duri Field fdr #1). Cause: Others (broken by Pass Switch Insulator of Recloser). |  | 1 | 16:17 | Afternoon | Wednesday | 2017 | 6
6141 | 2017-06-22 16:27 | 2017-06-22 16:27 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Others | 0 | 16:27 It was reported low Voltage o/p 03-07-17 d/s C.Duri fdr #7. Not checked yet. |  | 1 | 16:27 | Afternoon | Thursday | 2017 | 6
6142 | 2017-06-22 16:27 | 2017-06-23 15:30 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Others | 0 | 15:30 Adjusted 112.5KVA TX o/p 03. 07. 17 d/s C. Duri fdr #7. from Tapping-1 to Tapping-3, Volage: 445V to 480V. |  | 1 | 16:27 | Afternoon | Thursday | 2017 | 6
6143 | 2017-06-22 16:27 | 2017-06-22 16:27 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Others | 0 | 16:27 It was reported over voltage o/p 04-08-13 d/s C.Duri fdr#9. Not checked yet |  | 1 | 16:27 | Afternoon | Thursday | 2017 | 6
6144 | 2017-06-22 16:27 | 2017-06-23 11:00 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Others | 0 | 11:00 Adjusted 112.5KVA TX o/p 04-08-13 d/s C.Duri fdr#9. from Tapping-5 to Tapping-2, Volage: 485V. |  | 1 | 16:27 | Afternoon | Thursday | 2017 | 6
6145 | 2017-06-22 23:02 | 2017-06-22 23:02 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Lightning | 0 | 23:02 East Rumbai fdr#2 T/R 1X. Not checked yet. |  | 1 | 23:02 | Night | Thursday | 2017 | 6
6146 | 2017-06-22 23:02 | 2017-06-24 05:13 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Lightning | 0 | Checked & found, East Rumbai fdr#2 T/R 1x, Ctr: 526-527, R/F: 51 @2. Patrolled the line, found @2 broken Dead end insulator o/p 5RE2. Cause : Lightning |  | 1 | 23:02 | Night | Thursday | 2017 | 6
6147 | 2017-06-23 02:28 | 2017-06-23 02:28 | 13.8KV PETAPAHAN FEEDER #1 | Rain and Lightning | Lightning | 0 | Petapahan Fdr#1 Load dropped 70A (100-30A). Petapahan Fdr#2 Load dropped 200A(250-50A). Not checked yet. |  | 1 | 2:28 | Night | Friday | 2017 | 6
6148 | 2017-06-23 02:28 | 2017-06-24 07:38 | 13.8KV PETAPAHAN FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found Recl. 30-CZ-23, T/R 1x, Ctr: 153-153, R/F: 51N @3. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 2:28 | Night | Friday | 2017 | 6
6149 | 2017-06-23 06:30 | 2017-06-23 06:30 | 13.8KV NORTH DURI FEEDER #3 | Fair | Transformer Failure | 0 | 06:30 It was reported b/o fuse for Tx at CGS #10 D/S N Duri fdr #3. NDC HRSG #1,#2,#3 Trip OFF and Start up at 15:42. Due to Generate Feed Water Pump A and E at CGS #10 Trip open. 09:00 Checked and found @1 b/o fuse for 1500 Kva Tx. Perform TTR and Megger tested found Low megger reading. Cause: Tx failure (Low megger reading). |  | 1 | 6:30 | Morning | Friday | 2017 | 6
6150 | 2017-06-23 06:30 | 2017-01-07 15:47 | 13.8KV NORTH DURI FEEDER #3 | Fair | Transformer Failure | 0 | Replaced 1500 Kva Transformer failure with the same size and energized the Tx. Cause: Tx failure. |  | 1 | 6:30 | Morning | Friday | 2017 | 6
6151 | 2017-06-23 10:10 | 2017-06-23 10:10 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Animal | 0 | 10:10 It was reported b/o fuses o/p 04. 06. 41. 11:10 Checked and found @1, @1 ,@3 b/o fuses for 112.5KVA TX. Replaced b/o fuses above with same size. then energized the TX. Cause: Animal (Monkey). |  | 1 | 10:10 | Morning | Friday | 2017 | 6
6152 | 2017-06-23 14:45 | 2017-06-23 14:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 14:45 It was reported b/o fuses o/p 01. 07 25E. Not checked yet. |  | 1 | 14:45 | Afternoon | Friday | 2017 | 6
6153 | 2017-06-23 14:45 | 2017-06-24 08:22 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 08:22 Checked and found @3 b/o fuse for 112.5KVA TX o/p 01. 07.25E. Replaced b/o fuse above with same size, then energized the TX. Cause: Unidentified (fuse). |  | 1 | 14:45 | Afternoon | Friday | 2017 | 6
6154 | 2017-06-24 05:54 | 2017-06-24 05:54 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Unidentified | 0 | C.Duri fdr#11 T/R 3X, Ctr: 322-325, R/F: 51 @1. Not checked yet. |  | 1 | 5:54 | Morning | Saturday | 2017 | 6
6155 | 2017-06-24 05:54 | 2017-06-25 14:58 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Unidentified | 0 | Checked & found C.Duri ACB fdr#11 T/R 3x, Ctr: 322-325, R/F: 51 @1. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 5:54 | Morning | Saturday | 2017 | 6
6156 | 2017-06-24 08:14 | 2017-06-24 08:14 | 13.8KV S. BALAM FEEDER #1 | Cloudy | Animal | 140 | 08:14 So.Balam VCB fdr#1 T/R 1x. So.Balam fdr #2 load dropped 30A (94-64A). Wip. So.Balam fdr #3 load dropped 100A (100-0A). Wip. So.Balam fdr #4 Load dropped 124A (190-66A). 10:00 Checked & found So Balam VCB Fdr#1 T/R 1x, Ctr: 386-387, R/F: 51 @1@2. Patrolled the Line, found some Monkey near well So Balam #49. Cause: Animal (Monkey). |  | 1 | 8:14 | Morning | Saturday | 2017 | 6
6157 | 2017-06-24 08:14 | 2017-06-25 10:00 | 13.8KV S. BALAM FEEDER #1 | Cloudy | Animal | 140 | 10:00 Checked and found 13.8KV So Balam VCB Feeder 1 T/R 1X counter: 386-387, R/F : 51 @1, @2. Patrolled the line and found some Monkey near well So Balam # 49. Cause: Suspected Animal (monkey). |  | 1 | 8:14 | Morning | Saturday | 2017 | 6
6158 | 2017-06-24 08:14 | 2017-06-24 08:14 | 13.8KV NELLA FEEDER #1 | Cloudy | Switchboard Problem | 0 | 08:14 Nella VCB fdr#1 load dropped 137A (287-150A) Nella VCB fdr#2 load dropped 28A (124-96A) Not checked yet. |  | 1 | 8:14 | Morning | Saturday | 2017 | 6
6159 | 2017-06-24 08:14 | 2017-06-24 08:14 | 13.8KV BANGKO FEEDER #1 | Cloudy | Pin Insulator | 28 | 08:14 Bangko OCB fdr#1 load dropped 22A (230-208A) Bangko OCB fdr#24 load dropped 10A (223-213A) Not checked yet. |  | 1 | 8:14 | Morning | Saturday | 2017 | 6
6160 | 2017-06-24 08:14 | 2017-06-26 15:20 | 13.8KV BANGKO FEEDER #1 | Cloudy | Pin Insulator | 28 | 15:20 Checked and found Recl. 23 X 08 T/R 1X ctr:371-371 d/s Bangko fdr #1. Patrolled the line and found @2, @3 broken Pin Insulator o/p 24 Y 27. Cause:Pin Insulator. |  | 1 | 8:14 | Morning | Saturday | 2017 | 6
6161 | 2017-06-24 14:35 | 2017-06-24 14:35 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 14:35 It was reported b/o fuse o/p 03.06.10. 15:00 Checked and found @3 b/o fuse with same size, then energized the TX. Cause: Unidentified fuse. |  | 1 | 14:35 | Afternoon | Saturday | 2017 | 6
6162 | 2017-06-24 19:01 | 2017-06-24 19:01 | 13.8KV NELLA GFPC | Fair | Unidentified | 0 | Nella GFPC T/R 1x. No Load dropped. Unidentified. |  | 1 | 19:01 | Night | Saturday | 2017 | 6
6163 | 2017-06-24 19:01 | 2017-06-26 13:01 | 13.8KV NELLA GFPC | Fair | Unidentified | 0 | it was reported Nella GFPC T/R 1X, R/F Ground IOC #3, Ctr : 731 - 732. |  | 1 | 19:01 | Night | Saturday | 2017 | 6
6164 | 2017-06-24 22:40 | 2017-06-24 22:40 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 0 | Petani fdr#1 Load dropped 116A(208-92). Petani fdr#2 Load dropped 10A(66-56). Not checked yet. |  | 1 | 22:40 | Night | Saturday | 2017 | 6
6165 | 2017-06-24 22:40 | 2017-06-27 08:00 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 0 | Checked and found Recloser 33-AY-47 T/R 1x Patrolled the line and found Flash Over on Dead end insulator o/p 33-AX-12 R/F: 51 @2 Ctr: 155-156 Cause: Lightning. |  | 1 | 22:40 | Night | Saturday | 2017 | 6
6166 | 2017-06-25 16:00 | 2017-06-25 16:00 | 13.8KV NELLA FEEDER #1 | Fair | Animal | 64 | 16:00 It wa sreported b/o fuse at well BKO-64. 17:00 Checked and found @2 b/o fuse with same size, then energized. Cause: Animal (squirrel). |  | 1 | 16:00 | Afternoon | Sunday | 2017 | 6
6167 | 2017-06-25 16:04 | 2017-06-25 16:04 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 129 | 16:04 Sintong VCB fdr #2 T/R 1x. 17:33 Sintong fdr #2 load dropped 75A (165-90A). Not checked yet. |  | 1 | 16:04 | Afternoon | Sunday | 2017 | 6
6168 | 2017-06-25 16:04 | 2017-06-28 08:04 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 129 | it was reported Sintong Fdr #2 T/R 1X, ctr : 460 - 461, R/F 51N. Cause : unidentified Patroll : Found nothing. |  | 1 | 16:04 | Afternoon | Sunday | 2017 | 6
6169 | 2017-06-26 02:58 | 2017-06-26 02:58 | EAST RUMBAI SUBSTATION | Fair | Lightning | 0 | 02:58 East Rumbai VCB fdr#2 T/SO. 03:30 Blocked & Closed E.RBI VCB fdr#2, then released the block. Not checked yet. |  | 1 | 2:58 | Night | Monday | 2017 | 6
6170 | 2017-06-26 02:58 | 2017-06-07 07:30 | EAST RUMBAI SUBSTATION | Fair | Lightning | 0 | Checked and found 4.16 KV VCB #2 T/R 1x R/F: 51N Ctr: 527-528 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 2:58 | Night | Monday | 2017 | 6
6171 | 2017-06-26 09:53 | 2017-06-26 09:53 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 09:53 It was reported b/o fuse o/p 05-N7-19 d/s C.Duri fdr#14. 12:00 Checked and found @2 b/o fuse 112.5 Kva Tx. Replaced b/o fuse above with same size then energized the Tx. Cause: Animal (Bird). |  | 1 | 9:53 | Morning | Monday | 2017 | 6
6172 | 2017-06-27 06:19 | 2017-06-27 06:19 | MINAS SWITCH GEAR | Fair | Lightning | 0 | Minas 13.8KV ACB#21 T/R (13.8KV/44KV TX to Rumbai). Ctr: 82-83, R/F: not Appear. All Rumbai Feeder Back to Normal. Cause: Not Checked yet. |  | 1 | 6:19 | Morning | Tuesday | 2017 | 6
6173 | 2017-06-27 06:19 | 2017-04-07 07:30 | MINAS SWITCH GEAR | Fair | Lightning | 0 | Checked and found 13.8 KV ACB #21 T/R 1x R/F: 51 @2 Ctr: 80124-80125 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 6:19 | Morning | Tuesday | 2017 | 6
6174 | 2017-06-27 07:23 | 2017-06-27 07:23 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | C.Duri ACB #22 T/R 1 X ( Feeder # 2 C.Duri ) R/F : 51 G , 51 N, Counter : 246 - 247. Not Checked yet. |  | 1 | 7:23 | Morning | Tuesday | 2017 | 6
6175 | 2017-06-27 07:23 | 2017-06-30 08:00 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | Checked and found 13.8 KV ACB #22 T/R 1x R/F: 51G @1 Ctr: 246-247 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:23 | Morning | Tuesday | 2017 | 6
6176 | 2017-06-27 23:12 | 2017-03-06 17:42 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Unidentified | 0 | Checked and found Dumai 4.16KV VCB fdr #1 T/SO Counter: 275-276 R/F: 51@1. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 23:12 | Night | Tuesday | 2017 | 6
6177 | 2017-06-27 23:12 | 2017-06-27 23:12 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Unidentified | 0 | Dumai 4.16KV VCB fdr #1 T/SO. Checked and found Dumai VCB fdr #1 T/SO ctr:275-276 R/F: 51@1. Blocked and closed Dumai VCB fdr #1, OK then released the block. Not patrolled yet. |  | 1 | 23:12 | Night | Tuesday | 2017 | 6
6178 | 2017-06-28 08:59 | 2017-06-28 08:59 | 13.8KV PETANI FEEDER #2 | Fair | Pin Insulator | 22 | Petani OCB Fdr # 2 T/R 1X. Petani Fdr # 1 Load drop 117 Amp ( 206 - 89 ) Not Patrolled yet. |  | 1 | 8:59 | Morning | Wednesday | 2017 | 6
6179 | 2017-06-28 08:59 | 2017-06-30 08:00 | 13.8KV PETANI FEEDER #2 | Fair | Pin Insulator | 22 | Checked and found Petani 13.8 KV OCB #2 T/R 1x R/F: 51 @1 Ctr: 223-224 Patrolled the line and found Broken pin insulator o/p 32-AW-06. Cause: Pin insulator. |  | 1 | 8:59 | Morning | Wednesday | 2017 | 6
6180 | 2017-06-28 08:59 | 2017-06-28 08:59 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 0 | Pematang Fdr #1 load drop 72 Amp ( 150 - 78 ). Not patrolled yet. |  | 1 | 8:59 | Morning | Wednesday | 2017 | 6
6181 | 2017-06-28 08:59 | 2017-01-07 15:25 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 0 | Checked and found Pematang Fdr #1 load drop 72 Amp ( 150 - 78 ). Patrolled the line found Recloser 35-BC-14 Normal. Cause: Unidentified. |  | 1 | 8:59 | Morning | Wednesday | 2017 | 6
6182 | 2017-06-28 08:59 | 2017-06-28 08:59 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 13 | Rangau Fdr #2 load drop 182 Amp ( 197 - 15 ) Not Patrolled yet. |  | 1 | 8:59 | Morning | Wednesday | 2017 | 6
6183 | 2017-06-28 08:59 | 2017-01-07 14:59 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 13 | Checked and found Recloser: 23-BD=01 T/R 4x Counter: 281-285. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 8:59 | Morning | Wednesday | 2017 | 6
6184 | 2017-06-28 10:26 | 2017-06-28 10:26 | 13.8KV 3D FEEDER #4 | Fair | Lightning | 54 | 10:26 3 Delta Fdr #4 Load drop 107 Amp ( 235 - 128 Amp ) 3 Delta GFPC T/R 1X. 15:19 It was reported no power D/S Recloser 2D-33. 17:02 Checked and found Recloser 2D-33 T/SO Counter: 43-44. Blocked and closed Recloser 2D-33 --> OK and then released the block. Not Patrolled yet. |  | 1 | 10:26 | Morning | Wednesday | 2017 | 6
6185 | 2017-06-28 10:26 | 2017-03-07 08:00 | 13.8KV 3D FEEDER #4 | Fair | Lightning | 54 | Checked and found Recloser 2D-14 T/R 1x Patrolled the line but found nothing. Cause : Lightning |  | 1 | 10:26 | Morning | Wednesday | 2017 | 6
6186 | 2017-06-28 19:26 | 2017-06-28 19:26 | 13.8KV 4B FEEDER #4 | Rain and Lightning | Lightning | 19 | 4B 13.8KV VCB fdr #4 T/R 1X. 4b fdr #5 load dropped 220A (303-83A)--->WIP. Not checked yet. |  | 1 | 19:26 | Night | Wednesday | 2017 | 6
6187 | 2017-06-28 19:26 | 2017-03-07 08:00 | 13.8KV 4B FEEDER #4 | Rain and Lightning | Lightning | 19 | Checked and found 13.8 KV OCB fdr #4 T/R 1x R/F: 51 @2,@3 Ctr: 205-206. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 19:26 | Night | Wednesday | 2017 | 6
6188 | 2017-06-28 19:26 | 2017-06-28 19:26 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Lightning | 13 | 4B fdr #6 load dropped 107A (128-21A). Not checked yet. |  | 1 | 19:26 | Night | Wednesday | 2017 | 6
6189 | 2017-06-28 19:26 | 2017-01-07 08:24 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Lightning | 13 | Checked and found Recloser 4B-148 in By pass position. Cause: Suspected Lightning. |  | 1 | 19:26 | Night | Wednesday | 2017 | 6
6190 | 2017-06-28 19:27 | 2017-06-28 19:27 | 5 BRAVO SUBSTATION | Rain and Lightning | Under investigation | 214 | 19:27 115KV 5B OCB #25 T/O. 115KV 5B OCB #26 T/O. ( No power to 5B TX-2 and 5B fdr #4, #5 anf 5B fdr #8). 20:20 Checked and found 115KV 5B OCB #25 T/O. Checked and found 115KV 5B OCB #26 T/O. Checked and found 5B TX-2 R/F: 86T, 51G and 51 @1. 21:07 Manually open 5B fdr #4, ---->Closed at........... (4B fdr #1 de feed from 5B fdr #4). 21:07 Manually open 5B fdr #5, ---->Closed at 21:45. 21:07 Manually open 5B fdr #8, ---->Closed at 21:44. 21:23 Manually open 5B fdr #2, ---->Closed at 00:36. (As per GS #4 request to maintenance High Tank Level). 21:15 Closed 115KV 5B OCB #25 (DL), but tripped again. 21:25 Open both side isolation switch of 5B fdr #4. 21:44 Closed 115KV 5B OCB # 25 (DL), OK. Closed 115KV 5B OCB # 26(SC), OK. 23:30 Patrolled the line and found @2, @3 broken Dead End Insulator o/p KN-28 (under 4B fdr #1). Also found @1 Jumper o/p KN-28 (under 4B fdr #1). 23:40 Open LBS 3C-03 (4B fdr #1 separated from 5B fdr #4). 29-June-2017. 00:25 Closed both side Isolation Switch of 5B fdr #4. 01:18 Blocked and closed 5B fdr #4. OK then released the block. 02:25 Open LBS KN-36 and Closed LBS KN-38. 11:00 Checked and found: * @1,2,3 Broken dead end insulator. * @3 Broken jumper. * @3 Broken pin support. Replaced broken dead end , pin insulator and squeezed jumper. 15:35 Closed LBS 3C-03. (Part load 5B fdr #4 transfer to 3D fdr #4 by closed LBS KN-38 and opened LBS KN-36. Cause: Broken Dead End Insulator and Jumper. | 1111 | 1 | 19:27 | Night | Wednesday | 2017 | 6
6191 | 2017-06-28 19:28 | 2017-06-28 19:28 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Dead End Insulator | 20 | 3D 13.8KV OCB fdr #3 T/R 1X. Not checked yet. | 1111 | 1 | 19:28 | Night | Wednesday | 2017 | 6
6192 | 2017-06-28 19:28 | 2017-01-07 08:26 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Dead End Insulator | 20 | Checked and found 3D OCB fdr #3 T/R 1x Counter: 443-443 R/F: None. Patrolled the line found @3 broken dead end insulator on pole 3C-22. Cause: Broken Dead end Insulator. | 1111 | 1 | 19:28 | Night | Wednesday | 2017 | 6
6193 | 2017-06-28 19:28 | 2017-06-28 19:28 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 38 | 3D fdr #4 load dropped 157A (235-78A). Not checked yet. | 1111 | 1 | 19:28 | Night | Wednesday | 2017 | 6
6194 | 2017-06-28 19:28 | 2017-03-07 08:00 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 38 | Checked and found Recloser 2D-14 T/R 1x R/F: none Ctr: 48-49. Patrolled the line but nothing. Cause: Lightning. | 1111 | 1 | 19:28 | Night | Wednesday | 2017 | 6
6195 | 2017-06-28 19:28 | 2017-06-28 19:28 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 10 | 3D fdr #2 load dropped 108A (200-92A ). Not checked yet. | 11111 | 1 | 19:28 | Night | Wednesday | 2017 | 6
6196 | 2017-06-28 19:28 | 2017-03-07 08:00 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 10 | Checked and found Recloser CL-2F-11 normal operation. No finding patrol. Cause: Lightning. | 11111 | 1 | 19:28 | Night | Wednesday | 2017 | 6
6197 | 2017-06-28 19:43 | 2017-06-28 19:43 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | 5B 13.8KV OCB fdr #6 T/R 1X. 5B fdr #3 load dropped 31A (31-0A). Not checked yet. | 111 | 1 | 19:43 | Night | Wednesday | 2017 | 6
6198 | 2017-06-28 19:43 | 2017-03-07 08:00 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked and found 13.8 KV OCB fdr #1 T/R 1x R/F: none Ctr: 261-262 Patrolled the line but found nothing. Cause: Lightning. | 111 | 1 | 19:43 | Night | Wednesday | 2017 | 6
6199 | 2017-06-28 19:43 | 2017-06-28 19:43 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 28 | 5B fdr #1 load dropped 168A (182-14A). not checked yet. | 1111 | 1 | 19:43 | Night | Wednesday | 2017 | 6
6200 | 2017-06-28 19:43 | 2017-04-07 07:30 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 28 | Checked and found 13.8 KV OCB #1 normal. No finding patrol. Cause: Lightning. | 1111 | 1 | 19:43 | Night | Wednesday | 2017 | 6
6201 | 2017-06-28 19:43 | 2017-06-28 19:43 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning Arrester | 30 | 5B OCB fdr #2 T/R 1x. Not checked yet. | 111 | 1 | 19:43 | Night | Wednesday | 2017 | 6
6202 | 2017-06-28 19:43 | 2017-06-30 20:34 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning Arrester | 30 | Checked and found 5B fdr #2 T/R 2x Counter: 379-381 R/F: None. Patrolled the line found @1 broklen Lightning Arrester on pole 4C-55. Cause: Lightning Arrester. | 111 | 1 | 19:43 | Night | Wednesday | 2017 | 6
6203 | 2017-06-28 19:44 | 2017-06-28 19:44 | 13.8KV 6D FEEDER #3 | Rain and Lightning | Lightning | 0 | 6D fdr #3 load dropped 195A (329-134A)--->WIP not checked yet. |  | 1 | 19:44 | Night | Wednesday | 2017 | 6
6204 | 2017-06-28 19:44 | 2017-04-07 07:30 | 13.8KV 6D FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found 13.8 KV OCB #3 normal. No finding patrol. Cause: Lightning. |  | 1 | 19:44 | Night | Wednesday | 2017 | 6
6205 | 2017-06-28 19:44 | 2017-06-28 19:44 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning Arrester | 320 | 28-June-2017. 19:44 6D fdr #1 load dropped 201A (234-33A). 6D fdr #2 load dropped 25A (250-225A). 29-June-2017. 10:52 It was reported no power at well 6B-15,15C,25,25N,24,66. 15:39 Checked and found Recloser 5C-42 T/LO Counter:24-28. Patrolled the line found @1,2,3 broken Lightning Arrester. Dismantled LA above. 16:08 Blocked and closed Recloser 5C-42 --> OK and then released the block. Cause: Broken LA. Production loss: 21 bbls / 11 Wells. 299 Bbls / 10 Wells, ----->Under Recloser 5C-42 ------------------------+ Grand Tota: 320 Bbls / 21 Wells. | 1111 | 1 | 19:44 | Night | Wednesday | 2017 | 6
6206 | 2017-06-28 19:59 | 2017-06-28 19:59 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 30 | 5B 13.8KV fOCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 19:59 | Night | Wednesday | 2017 | 6
6207 | 2017-06-28 19:59 | 2017-01-07 08:31 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 30 | Checked and found 5B OCB fdr #2 T/R 2x Counter: 379-381 R/F: None. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 19:59 | Night | Wednesday | 2017 | 6
6208 | 2017-06-28 20:24 | 2017-06-28 20:24 | 115KV DURI - KOTABATAK JUNCTION LINE | Rain and Lightning | Lightning | 0 | KBJ-Duri 115KV GCB #43 T/R 1X. KBJ-Duri 115KV GCB #45 T/R 1X. Duri-KBJ 115KV OCB #26 T/R 1X. Duri-KBJ 115KV OCB #28 T/R 1X. Not checked yet. |  | 1 | 20:24 | Night | Wednesday | 2017 | 6
6209 | 2017-06-28 20:24 | 2017-04-07 08:32 | 115KV DURI - KOTABATAK JUNCTION LINE | Rain and Lightning | Lightning | 0 | Checked & Found 115KV Line DRB-KBJ T/R, Ctr: (not checked yet), R/F: 67N. Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 20:24 | Night | Wednesday | 2017 | 6
6210 | 2017-06-28 20:24 | 2017-06-28 20:24 | PUNGUT SUBSTATION | Rain and Lightning | Under investigation | 163 | 20:24 Pungut 115KV C/S T/O. Pungut 13.8KV T/R 1X. (No power to Pungut TX, and P{ungut fdr #1 & fdr #2). 21:50 Checked and found Pungut 115KV C/S t/O ctr:170-171 R/F : NoN. Checked anf found Pungut 13.8KV OCB fdr #1 T/R 1X ctr: 372-373 R/F: 51G. 21:52 Manually open Pungut fdr #1, ---->Closed at 22:04. Manually open Pungut fdr #2, ---->Closed at 22:08. Under investigation. Production loss: Pungut fdr #1: 136 Bbls / 22 Wells. Pungut fdr #2: 48 Bbls / 15 Wells. ------------------------------------------+ TOTAL : 184 Bbls / 37 Wells. | 1111 | 1 | 20:24 | Night | Wednesday | 2017 | 6
6211 | 2017-06-29 05:53 | 2017-06-29 05:53 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Others | 0 | Duri Comm. 13.8KV ACB fdr #1 T/R 1X. Not checked yet. |  | 1 | 5:53 | Morning | Thursday | 2017 | 6
6212 | 2017-06-29 05:53 | 2017-06-30 08:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Others | 0 | Checked and found 13.8 KV ACB #25 T/R 1x R/F:51N Ctr: 101-102 Patrolled the line but found nothing. Cause : Others. |  | 1 | 5:53 | Morning | Thursday | 2017 | 6
6213 | 2017-06-29 11:05 | 2017-06-29 11:05 | CENTRAL DURI POWER PLANT |  |  | - | 11:05 S/U CDGT #4 and then On Line the unit at 11:36. |  | 1 | 11:05 | Morning | Thursday | 2017 | 6
6214 | 2017-06-29 11:22 | 2017-06-29 11:22 | 13.8KV KETIGUL FEEDER#2 | Fair | Powerline - Conductor | 216 | 11:22 It was reported no power at wells UBI field D/S Ketigul fdr #2. 12:41 Checked and found Recloser: 26-AK-02 T/LO Counter: 190-192. Patrolled the line found @3 broken conductor on pole 26-AJ-06. 17:04 Blocked and closed Recloser: 26-AK-02 --> OK and then released the block. Cause: Broken Conductor. |  | 1 | 11:22 | Morning | Thursday | 2017 | 6
6215 | 2017-06-29 11:52 | 2017-06-29 11:52 | CENTRAL DURI POWER PLANT |  |  | - | 11:52 S/D CDGT #3 for Stand By. |  | 1 | 11:52 | Morning | Thursday | 2017 | 6
6216 | 2017-06-30 23:59 | / | CPI POWER SYSTEM |  |  | - | - |  | 1 | 23:59 | Night | Friday | 2017 | 6
6217 | 2017-01-07 12:04 | 2017-01-07 12:04 | 13.8KV BATANG FEEDER #2 | Cloudy | Lightning Arrester | 0 | Batang OCB Fdr #2 T/R 1X Not Patrolled yet. |  | 1 | 12:04 | Afternoon | Saturday | 2017 | 1
6218 | 2017-01-07 12:04 | 2017-04-07 19:07 | 13.8KV BATANG FEEDER #2 | Cloudy | Lightning Arrester | 0 | Checked & found Batang OCB fdr#2 T/R, Ctr: 143-144, R/F: 51N @1 @2. Patrolled the Line, found ; broken @2 Pin Insulator o/p 36-AF-07 broken @2 L.A o/p 35-AF-29. broken @1 Dead end o/p 35-AD-08 broken @2 Pin insulator o/p 34-AD-03 Cause : Lightning Arrester |  | 1 | 12:04 | Afternoon | Saturday | 2017 | 1
6219 | 2017-01-07 17:17 | 2017-01-07 17:17 | 13.8KV MINAS FEEDER #3 | Fair | Lightning | 47 | Minas ACB #2 (Feeder #3) T/R 1x Counter: 80124-80125 R/F: 51@2. Not patrolled yet. |  | 1 | 17:17 | Afternoon | Saturday | 2017 | 1
6220 | 2017-01-07 17:17 | 2017-04-07 07:30 | 13.8KV MINAS FEEDER #3 | Fair | Lightning | 47 | Checked and found 13.8 KV ACB #2 T/R 1x R/F: 51 @2 Ctr: 80124-80125 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 17:17 | Afternoon | Saturday | 2017 | 1
6221 | 2017-02-07 10:52 | 2017-02-07 10:52 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Lightning | 19 | So Bekasap fdr #1 Load dropped 74A (141-67A). Not checked yet. |  | 1 | 10:52 | Morning | Tuesday | 2017 | 2
6222 | 2017-02-07 10:52 | 2017-06-07 07:30 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Lightning | 19 | Checked and found Recloser 34-BI-18 T/R 2x R/F: none Ctr: 159-161 Patrolled the line and found Broken pin @3 o/p 31-BF-26 Cause: Lightning. |  | 1 | 10:52 | Morning | Tuesday | 2017 | 2
6223 | 2017-02-07 17:14 | 2017-02-07 17:14 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Unidentified | 0 | C Duri ACB #43 (feeder #11) T/R 1x Counter:325-326 R/F: 51@1. Not patrolled yet. |  | 1 | 17:14 | Afternoon | Tuesday | 2017 | 2
6224 | 2017-02-07 17:14 | 2017-03-07 17:39 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Unidentified | 0 | Checked and found C Duri ACB #43 (feeder #11) T/R 1x Counter:325-326 R/F: 51@1. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 17:14 | Afternoon | Tuesday | 2017 | 2
6225 | 2017-02-07 19:33 | 2017-02-07 19:33 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Pin Insulator | 0 | Nella 13.8KV VCB fdr #1 T/R 1X. Nella GFPC T/R 1X. Nella fdr #2 load dropped 51A (110-59A). Not checked yet. | 1111 | 1 | 19:33 | Night | Tuesday | 2017 | 2
6226 | 2017-02-07 19:33 | 2017-04-07 19:11 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Pin Insulator | 0 | Checked & found Nella VCB fdr#1 T/R, Ctr: 500-5001, R/F: 51N @1. Patrolled the Line, found broken @1 Pin insulator o/p 21-V-24. Cause : Pin Insulator | 1111 | 1 | 19:33 | Night | Tuesday | 2017 | 2
6227 | 2017-02-07 19:37 | 2017-02-07 19:37 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 128 | 19:37 So Balam 13.8KV VCB fdr #4 T/R 1X. 19:39 So Balam 13.8KV VCB fdr #4 tripped again. Not checked yet. | 1111 | 1 | 19:37 | Night | Tuesday | 2017 | 2
6228 | 2017-02-07 19:37 | 2017-04-07 13:46 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 128 | Checked & found Balam VCB fdr#4 T/R 2x, Ctr: 337-339, R/F: 51N @2. Patrolled the Line, found @2 Broken LA O/Tp Balam 162 Cause: Lightning | 1111 | 1 | 19:37 | Night | Tuesday | 2017 | 2
6229 | 2017-02-07 19:50 | 2017-02-07 19:50 | NELLA SUBSTATION | Rain and Lightning | Circuit Breaker | 358 | 19:50 Nella 115KV C/S T/O. No power to Nella Subtation. Also no power Nella fdr #1 and fdr #2. 21:30 Checked and found Nella 115KV C/S T/O ctr:183-184 R/F:W-2 N. Nella 13.8KV VCB fdr #1 T/R 1X ctr: Not changed R/F: 51@1, @2. Nella fdr #2 Closed position ctr:501 R/F:51N. Nella GFPC T/R 5X ctr: 1732-1737. 21:40 Manually oped Nella fdr #1. Manually oped Nella fdr #2, failed. ( Clossing coil of Nella Fdr # 2 Burn out ) Open both side isolation switch Nella fdr #2. 22:00 Closed 115KV Nella C/S, OK Closed Nella Cap. Bank. 22:02 Closed Nella fdr #1. Checked and exercised 52CS Nella fdr #2 (can not tripped). 22:30 Patrolled the line under Nella fdr #2, Normal. 00:30 Closed LBS 21 V 24, transfer all load Nella fdr #2 to Nella fdr #1. Cause: Breaker failure (closing coil burnt out). Production Loss: Nella frd #1 : 872 Bbls / 80 Wells. Nella frd #2 : 361 Bbls / 14 Wells. -----------------------------------------+ TOTAL : 1233 Bbls / 94 Wells. | 1111 | 1 | 19:50 | Night | Tuesday | 2017 | 2
6230 | 2017-02-07 19:57 | 2017-02-07 19:57 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 49 | 19:57 Bangko 13.8KV OCB fdr #4 T/R 1X. Bangko fdr #2 load dropped 234A (260-26A ). Bangko fdr #3 load dropped 180A (206-26A ). 21:36 Checked VR Bangko, found stug on R-16 and Voltage 15.5KV. Also found Bangko Cap. Bank Recloser T/O. Exercised VR Banko, OK. found VR position on R-9 and Voltage 14.0KV . 00:30 Closed Reclose Bangko Cap Bank. OK Not patrolled yet. | 111 | 1 | 19:57 | Night | Tuesday | 2017 | 2
6231 | 2017-02-07 19:57 | 2017-04-07 07:30 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 49 | Checked and found 13.8 KV OCB #4 (Bangko fdr #4) T/R 1x R/F: 51 @3 Ctr: 00007-00008 Patrolled the line but found nothing. Cause: Unidentified. | 111 | 1 | 19:57 | Night | Tuesday | 2017 | 2
6232 | 2017-02-07 19:57 | 2017-02-07 19:57 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 54 | 19:57 Bangko fdr #1 load dropped 185A (220-35A ). Not checked yet. | 11111 | 1 | 19:57 | Night | Tuesday | 2017 | 2
6233 | 2017-02-07 19:57 | 2017-04-07 07:30 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 54 | Checked and found Recloser 23-X-08 o/p 25-X-12 T/R 3x R/F: 51N @1 Ctr: 372-375 Patrolled the line and found broken Lightning Arrester. Cause: Lightning. | 11111 | 1 | 19:57 | Night | Tuesday | 2017 | 2
6234 | 2017-03-07 10:40 | 2017-03-07 10:40 | MINAS POWER PLANT |  |  | - | 10:40 S/U MGT #1 and then On Line the unit at 11:00. |  | 1 | 10:40 | Morning | Tuesday | 2017 | 3
6235 | 2017-03-07 11:30 | 2017-03-07 11:30 | CENTRAL DURI POWER PLANT |  |  | - | 11:30 S/U CDGT #3 and then On Line the unit at 11:48. |  | 1 | 11:30 | Morning | Tuesday | 2017 | 3
6236 | 2017-03-07 23:12 | 2017-03-07 23:12 | 13.8KV 8C FEEDER #3 | Fair | Lightning | 1 | 8C fdr #3 load dropped 225A (233-8A). Not checked yet. | 1111 | 1 | 23:12 | Night | Tuesday | 2017 | 3
6237 | 2017-03-07 23:12 | 2017-06-07 08:33 | 13.8KV 8C FEEDER #3 | Fair | Lightning | 1 | Checked & found Recl. 8D-18A T/R 3x, Ctr: 38-41, R/F: None. Patrolled the Line, found @3 burn out L.A o/p 8C-57 Cause : Lightning | 1111 | 1 | 23:12 | Night | Tuesday | 2017 | 3
6238 | 2017-04-07 22:00 | 2017-04-07 22:00 | 13.8KV ROKAN FEEDER #2 | Fair | Theft | 9 | 22:00 It was reported b/o fuse at well Kopar #07 d/s Rokan fdr #2. 23:51 Checked and found @1 b/o fuse for Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Theft trial. |  | 1 | 22:00 | Night | Friday | 2017 | 4
6239 | 2017-05-07 10:30 | 2017-05-07 10:30 | 13.8KV NELLA FEEDER #1 | Fair | Transformer Failure | 1 | 10:30 Change out 150 Kva Transformer at well Bangko #23. 11:30 Energized 150 Kva Tx at well Bangko #23. Cause: Tx failure. |  | 1 | 10:30 | Morning | Sunday | 2017 | 5
6240 | 2017-05-07 23:07 | 2017-05-07 23:07 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 18 | Manggala Fdr #1 Load drop 100 A ( 152 - 52 A ). Not Patrolled Yet. |  | 1 | 23:07 | Night | Sunday | 2017 | 5
6241 | 2017-05-07 23:07 | 2017-07-07 13:57 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 18 | Checked & found Recl. 19-AN-04 T/R 1x, Ctr: 334-335, R/F: 51 Not Patrolled yet. |  | 1 | 23:07 | Night | Sunday | 2017 | 5
6242 | 2017-06-07 00:18 | 2017-06-07 00:18 | 13.8KV NELLA FEEDER #1 | Fair | Powerline - Conductor | 3784 | 00:18 Nella fdr #1 load dropped 349A (375-26A). Nella GFPC T/R 1x. 00:31 It was reported broken conductor at near Test station D Nella field. 02:16 Opened LBS 20-U-01 to isolate broken conductor 04:26 Opened LBS 21-V-24 to isolate FDR#2 to FDR#1 ( Herman ) 04:36 Manually Opened C/S at Nella Substation ( Agusyoto ) 04:37 Closed bypass switch Fdr#2 Nella substation (Back to normal load Nella fdr #2). 04:39 Manually Closed C/S Nella Substation Nella Fdr#2 energized witch bypass switch. 12:05 Closed LBS 20-U-01, after Finished Fixed the broken conductor d/s Nella fdr#1. 14:28 Man. Closed Nella VCB fdr#2 (after Disable 51N relay, then back to normal) Cause: Broken conductor. | 11111 | 1 | 0:18 | Night | Wednesday | 2017 | 6
6243 | 2017-06-07 09:00 | 2017-06-07 09:00 | 13.8KV DURI FIELD FEEDER #4 | Fair | Transformer Failure | 16 | 09:00 It was reported b/o fuse o/p 07-V1-28 (d/s DF fdr#4). 15:40 Checked & found, @1 @2 b/o fuse for 112.5KVATX. Tested TTR & Megger, the result TX Low reading. Replaced the TX and fuses with the same size, then Energized the TX. Cause: Transformer Failure. |  | 1 | 9:00 | Morning | Wednesday | 2017 | 6
6244 | 2017-06-07 14:02 | 2017-06-07 14:02 | MINAS POWER PLANT |  |  | - | 14:02 MGT#9 S/U then On Line to system at 14:56. to Restore Power after Fixed the leakage at Combustion Chamber #10. |  | 1 | 14:02 | Afternoon | Wednesday | 2017 | 6
6245 | 2017-06-07 15:36 | 2017-06-07 15:36 | MINAS POWER PLANT |  |  | - | 15:36 MGT#5 Off Line then S/D for Standby. |  | 1 | 15:36 | Afternoon | Wednesday | 2017 | 6
6246 | 2017-06-07 16:28 | 2017-06-07 16:28 | CENTRAL DURI POWER PLANT |  |  | - | 16:28 CGT#4 Off Line, then S/D the unit for S/B. |  | 1 | 16:28 | Afternoon | Wednesday | 2017 | 6
6247 | 2017-07-07 08:00 | 2017-07-07 08:00 | 13.8KV BANGKO FEEDER #4 | Fair | Broken Fuse Holder | 0 | 08:00 Bangko fdr#4 load dropped 100A (232-132A). 14:00 Checked & found Recl. 25.Z.07 T/R 3x, Ctr: 159-162, R/F: None. Patrolled the Line, found @2 @3 b/o fuse for 150KVATX o/p 25.Z.16. Cause : Broken Fuse Holder |  | 1 | 8:00 | Morning | Friday | 2017 | 7
6248 | 2017-07-07 15:29 | 2017-07-07 15:29 | 13.8KV NORTH DURI FEEDER #1 | Cloudy | Unidentified | 0 | N.Duri 13.8KV VCB fdr#1 T/R 1X. Not checked yet. |  | 1 | 15:29 | Afternoon | Friday | 2017 | 7
6249 | 2017-07-07 15:29 | 2017-12-07 15:29 | 13.8KV NORTH DURI FEEDER #1 | Cloudy | Unidentified | 0 | Checked found, N. Duri VCB fdr #1 T/R 1x ctr: 283-284 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:29 | Afternoon | Friday | 2017 | 7
6250 | 2017-08-07 06:26 | 2017-08-07 06:26 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Duri field Sw.Gear VCB #52 T/R 1X ( Feeder #3 ). Not Patrolled yet. |  | 1 | 6:26 | Morning | Monday | 2017 | 8
6251 | 2017-08-07 06:26 | 2017-12-07 06:26 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Checked & found, D. Field fdr #3 T/R 1x ctr: 366-367 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:26 | Morning | Monday | 2017 | 8
6252 | 2017-08-07 07:13 | 2017-08-07 07:13 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri Fdr#1 Load dropped 30A (127-97A). Not checked yet. |  | 1 | 7:13 | Morning | Monday | 2017 | 8
6253 | 2017-08-07 07:13 | 13/07/2017 05:13 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found Recl. 41-AW-62 T/R 1x, Ctr: 249 - 250, R/F: None. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 7:13 | Morning | Monday | 2017 | 8
6254 | 2017-08-07 16:00 | 2017-08-07 16:00 | 13.8KV BEKASAP FEEDER #3 | Fair | Unidentified | 0 | 16:00 It was reported b/o Fuse at well BKS#69 (d/s Bekasap fdr#3). 17:15 Replaced the Fuse with the same size, then energized the TX. Patrolled the Line , but found nothing. Cause: Unidentified. |  | 1 | 16:00 | Afternoon | Monday | 2017 | 8
6255 | 2017-08-07 22:19 | 2017-08-07 22:19 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Unidentified | 0 | Dumai 4160 VCB #12 T/R 1x (Feeder #1 WHARF ) Not Patrolled yet . |  | 1 | 22:19 | Night | Monday | 2017 | 8
6256 | 2017-08-07 22:19 | 19/07/2017 09:00 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Unidentified | 0 | Checked and found 4.16 KV Dumai Wharf fdr #1 T/R 1x R/F: 50 Ctr: 276-277 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 22:19 | Night | Monday | 2017 | 8
6257 | 2017-09-07 10:10 | 2017-09-07 10:10 | CENTRAL DURI POWER PLANT |  |  | - | 10 10 CGT #4 S/U then On Line at 11:27. to Restore power due to CGT #3 will be Down. |  | 1 | 10:10 | Morning | Thursday | 2017 | 9
6258 | 2017-09-07 10:46 | 2017-09-07 10:46 | CENTRAL DURI POWER PLANT |  |  | - | 10:46 CGT#3 Off Line And S/D for S/B. waiting to Fix Fuel nozzle Leakage. |  | 1 | 10:46 | Morning | Thursday | 2017 | 9
6259 | 2017-10-07 08:18 | 2017-10-07 08:18 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | 08:18 Bangko fdr#4 Load dropped 61A(191-130A) 09:30 Checked and found Recloser: 25 Z 07 T/R 1x Counter: 192-193. Patrolled the line found nothing. Cause Unidentified. |  | 1 | 8:18 | Morning | Saturday | 2017 | 10
6260 | 2017-10-07 11:20 | 2017-10-07 11:20 | 44KV PEMATANG MAIN - RANGAU LINE | Fair | Powerline - Conductor | 2295 | 11:20 Pematang Main 44KV OCB #2 T/LO (44 KV Line Pematang Rangau). 11:30 Got Inform From Security DMG, Any fire at house under Power Line, Burning & Broken out 2 Phases of Conductor. it came from Gas stove Explotion. 11:35 Manually Open Rangau OCB fdr#1. Manually Open Rangau OCB fdr#2. 12:20 Opened Isolation Switch of Pematang Main 44KV Line to Rangau and Installed Personal ground. Rangau fdr #1 Production loss= 82 Bbls / 4 wells. Rangau fdr #2 Production loss= 959 Bbls / 17 wells. -------------------------------------------- + T o t a l = 1041 Bbls / 21 wells. | 12345 | 1 | 11:20 | Morning | Saturday | 2017 | 10
6261 | 2017-10-07 11:20 | 2017-11-07 13:30 | 44KV PEMATANG MAIN - RANGAU LINE | Fair | Powerline - Conductor | 2295 | 13:50 Manual Closed Pematang Main 44KV OCB#2. 14:15 Manual Closed Rangau 13.8KV OCB fdr#1. (After confirm with Rangau GS, and wait for next OCB fdr#2) 15:15 Manual Closed Rangau 13.8KV OCB fdr#2. (after Confirm with Rangau GS). Cause: Conductor (Broken @1@2@3 44KV Line). Rangau fdr #1 Production loss= 83 Bbls / 4 wells. Rangau fdr #2 Production loss= 1225 Bbls / 17 wells. -------------------------------------------- + T o t a l = 1308 Bbls / 21 wells. | 12345 | 1 | 11:20 | Morning | Saturday | 2017 | 10
6262 | 2017-10-07 12:40 | 2017-10-07 12:40 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 2 | 12:40 It was reported b/o fuse at well S.Balam#61 (d/s S.Balam fdr#1). 15:45 Checked & found @2@3 b/o fuse for 75KVATX. Replaced the fuse with the same size, then energized the TX. Cause: Animal (Squirrel) |  | 1 | 12:40 | Afternoon | Saturday | 2017 | 10
6263 | 2017-10-07 14:53 | 2017-10-07 14:53 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | 14:53 It was reported b/o fuse o/p 05-P3-05 (d/s CD fdr#15). 15:23 Checked & found @1 b/o fuse for 112.5 KVA TX. Replaced the fuse with the same size, then energized the TX. Cause: Unidentified. |  | 1 | 14:53 | Afternoon | Saturday | 2017 | 10
6264 | 2017-11-07 13:55 | 2017-11-07 13:55 | MINAS POWER PLANT | Fair |  | - | 13:55 S/U MGT#3,then online the unit at 14:13,for testing generator balancing. |  | 1 | 13:55 | Afternoon | Tuesday | 2017 | 11
6265 | 2017-11-07 15:30 | 2017-11-07 15:30 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 211 | 15:30 It was reported No Power at Jurong Field (d/s Rangau fdr#2) 18:05 Checked & found Recl. 23.BD.01 T/SO, Ctr: 285-286, R/F: None. Manual Closed the Recloser. Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 15:30 | Afternoon | Tuesday | 2017 | 11
6266 | 2017-11-07 20:07 | 2017-11-07 20:07 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Recloser | 2202 | 20:07 C Duri ACB fdr #21 (feeder #4) T/LO Counter: 481-485 R/F: 51@1,2. 20:33 Blocked and closed C Duri ACB fdr #4 but failed. 23:10 Opened LBS 09-R5-10 and then Blocked and closed C Duri ACB fdr #4 but failed again. 23:34 Opened By pass Recloser: 09-Q1-06. Blocked and closed C Duri ACB fdr #4 --> Success and then released the block. 23:43 Closed LBS 09-R5-10. --> Success. Patrolled down stream Recloser: 09-Q1-06 but nothing found. July 12,2017. 01:06 Manually opened C Duri ACB fdr #4 for closing by pass Recloser: 09-Q1-06. Closed by pass Recloser but failed due to damage of blade by pass. 01:09 Blocked and closed C Duri ACB fdr #4. Forwarded the morning because of the rain. Not patrolled yet. | 11111 | 1 | 20:07 | Night | Tuesday | 2017 | 11
6267 | 2017-11-07 20:07 | 2017-12-07 16:17 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Recloser | 2202 | 16:17 Replaced all Blades By Pass switch Recloser #09 Q1 06 d/s C. Duri fdr #4. Manually open C. Duri fdr #4. Closeed By Pass switch Recloser 09 Q1 06, OK. 18:05 LBS 09 Q1 01 and open LBS 03 03 44. (Part load C. Duri fdr #7 de feed from C. Duri fdr #4) 18:08 Manual closed C. Duri fdr #4. Cause: Recloser (Broken By Pass switch). | 11111 | 1 | 20:07 | Night | Tuesday | 2017 | 11
6268 | 2017-11-07 20:08 | 2017-11-07 20:08 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Unidentified | 0 | C Duri ACB #22 (feeder #5) T/R 1x Counter:247-248 R/F: 51@2 ,3. Not patrolled yet. |  | 1 | 20:08 | Night | Tuesday | 2017 | 11
6269 | 2017-11-07 20:08 | 17/07/2017 08:00 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Unidentified | 0 | Checked and found 13.8 KV C. Duri fdr #5 (ACB #22) T/R 1x R/F:50 Ctr:247-248 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 20:08 | Night | Tuesday | 2017 | 11
6270 | 2017-11-07 20:54 | 2017-11-07 20:54 | 13.8KV NORTH DURI FEEDER #9 | Rain and Lightning | Unidentified | 0 | N Duri VCB fdr #9 T/R 1x. Not checked yet. |  | 1 | 20:54 | Night | Tuesday | 2017 | 11
6271 | 2017-11-07 20:54 | 17/07/2017 08:00 | 13.8KV NORTH DURI FEEDER #9 | Rain and Lightning | Unidentified | 0 | Checked and found 13.8 KV VCB #9 (N. Duri fdr #9) T/R 1x R/F: 51N Ctr: 44-45 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 20:54 | Night | Tuesday | 2017 | 11
6272 | 2017-11-07 20:55 | 2017-11-07 20:55 | 13.8KV DARLING VCB FEEDER #7 | Rain and Lightning | Lightning | 0 | Darling VCB fdr #7 T/R 1x. Not checked yet. |  | 1 | 20:55 | Night | Tuesday | 2017 | 11
6273 | 2017-11-07 20:55 | 17/07/2017 08:00 | 13.8KV DARLING VCB FEEDER #7 | Rain and Lightning | Lightning | 0 | Checked and found 13.8 KV Darling fdr #7 T/R 1x R/F: @3 50 Ctr: 159 - 160. Patrolled the line and found broken LA o/p SA-1. Cause: Lightning. |  | 1 | 20:55 | Night | Tuesday | 2017 | 11
6274 | 2017-12-07 10:45 | 2017-12-07 10:45 | 13.8KV NORTH DURI FEEDER #2 | Fair | Transformer Failure | 16 | 10:45 It was reported B/O fuse o/p 13H1.1-22, (d/s ND fdr#2). 15:35 Checked and found B/O @1,@2,@3 Fuse for 112.5KVATX. Replaced the fuse with the same size, then energized the TX. Cause: Unidentified. |  | 1 | 10:45 | Morning | Thursday | 2017 | 12
6275 | 2017-12-07 10:45 | 13/07/2017 11:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Transformer Failure | 16 | 11:00 It was reported b/o fuse o/p 13. H1.1 22 d/s N. Durim fdr #2. 16:00 Checked and found @1, @2, @3 b/o fuse for 112.5KVA TX. Performed TTR test and Megger the TX, but found TX failure. Cause: TX failure (will be replaced soon). |  | 1 | 10:45 | Morning | Thursday | 2017 | 12
6276 | 2017-12-07 10:45 | 17/07/2017 11:05 | 13.8KV NORTH DURI FEEDER #2 | Fair | Transformer Failure | 16 | 11:05 Replaced 112.5 Kva Tx o/p 13-H1.1-22 d/s N.Duri fdr #2 Energized the Tx . OK. Cause: Tx failure. |  | 1 | 10:45 | Morning | Thursday | 2017 | 12
6277 | 2017-12-07 16:08 | 2017-12-07 16:08 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | 16:08 It was reported b/o Fuse o/p 09-08-03 (d/s CD fdr#4). 22:30 Checked & found @1 b/o fuse for 112.5KVATX. Replaced the fuse with the same size, then energized the TX. Cause: Unidentified. |  | 1 | 16:08 | Afternoon | Thursday | 2017 | 12
6278 | 2017-12-07 17:57 | 2017-12-07 17:57 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 23 | OKB fdr#2 Load dropped 158A (244-86A). Not checked yet. |  | 1 | 17:57 | Afternoon | Thursday | 2017 | 12
6279 | 2017-12-07 17:57 | 13/07/2017 17:57 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 23 | Checked & found, Recl. 38-CW-08 T/R 2x ctr: 83-85. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:57 | Afternoon | Thursday | 2017 | 12
6280 | 2017-07-13 09:16 | 2017-07-13 09:16 | CENTRAL DURI POWER PLANT | Fair |  | - | 09:16 S/U CDGT# 3 then online the unit at 09:29 , to restore load for service ACB#39 ( Tie ) Broken. |  | 1 | 9:16 | Morning | Thursday | 2017 | 7
6281 | 2017-07-13 15:20 | 2017-07-13 15:20 | MINAS POWER PLANT | Fair |  | - | 15:20 MGT#3 Off Line then S/D due to Hight Vibration. |  | 1 | 15:20 | Afternoon | Thursday | 2017 | 7
6282 | 2017-07-13 20:30 | 2017-07-13 20:30 | 13.8KV ROKAN FEEDER #2 | Heavy Rain | Lightning | 17 | Rokan VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 20:30 | Night | Thursday | 2017 | 7
6283 | 2017-07-13 20:30 | 2017-07-16 14:49 | 13.8KV ROKAN FEEDER #2 | Heavy Rain | Lightning | 17 | Checked & found Rokan VCB fdr#2 T/R 1x, Ctr: 1251-1252, R/F: 51. Patrolled the Line, found @3 flash over post type pin insulator o/p 31 AV 26. Cause : Lightning |  | 1 | 20:30 | Night | Thursday | 2017 | 7
6284 | 2017-07-14 09:30 | 2017-07-14 09:30 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 0 | 09:30 It was reported unbalance voltage TX o/p 01-03-06 (C.Duri fdr #14). 11:01 Checked and found B/O @1 Fuse for 112.5KVA TX. Replaced the fuse with the same size, then energized the TX. Cause: Unidentified. |  | 1 | 9:30 | Morning | Friday | 2017 | 7
6285 | 2017-07-15 17:37 | 2017-07-15 17:37 | 13.8KV 3D FEEDER #4 | Fair | Unidentified | 99 | 17:37 3D 13.8 Kv OCB fdr #4 T/LO. 3D fdr #2 load dropped 138A (178-40A). 3D fdr #3 load dropped 99A (148-49A). 3D fdr #5 dropped 110A (203-93) Wip. 17:50 Blocked and Closed 3D fdr #4 , released the block. 21:53 3D fdr#4 Load, was not Reach to normal, 52A (260-208A). Patrolledthe Line, found Recl. 2D-33 T/So, Ctr:44 - 45,R/F: ......... Blocked & Closed the Recloser, then released the block. Not Patrolled yed. |  | 1 | 17:37 | Afternoon | Saturday | 2017 | 7
6286 | 2017-07-15 17:37 | 2017-07-19 09:00 | 13.8KV 3D FEEDER #4 | Fair | Unidentified | 99 | Checked and found 13.8 KV 3D fdr #4 T/LO R/F: 51 Ctr: 566 - 572 Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:37 | Afternoon | Saturday | 2017 | 7
6287 | 2017-07-16 11:45 | 2017-07-16 11:45 | 13.8KV SURAM FEEDER #2 | Fair | ESP Failure | 0 | 11:45 It was reported b/o fuse at well Suram #06. Checked and found @2 b/o fuse fir 45KVA TX. TTR test and Megger the TX. Good condition. TTR test and Megger the Reda, but found Zero Meg Reda Motor. Replaced b/o fuse with same, then energized the TX. OK. Cause:ESP (Zero Meg). | 1111111111 | 1 | 11:45 | Morning | Sunday | 2017 | 7
6288 | 2017-07-16 11:55 | 2017-07-16 11:55 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 48 | 11:55 It was reported b/o fuse at well Menggala Shouth #08. 14:45 Checked and found @3 b/o fuse for 300KVA TX. Performed TTR test test and Megger the TX. Good condition. Replaced b/o fuse above with same size, then anergized the TX. Cause: Animal (Squarrel). | 11111 | 1 | 11:55 | Morning | Sunday | 2017 | 7
6289 | 2017-07-17 14:00 | 2017-07-17 14:00 | CENTRAL DURI POWER PLANT |  |  | - | 14:00 Off line and than S/D CDGT #4 for replace 88 BT . |  | 1 | 14:00 | Afternoon | Monday | 2017 | 7
6290 | 2017-07-17 15:47 | 2017-07-17 15:47 | 13.8KV SINTONG FEEDER #2 | Fair | Others | 0 | 15:47 Sintong 13.8KV GFPC T/R 1X. Sintong fdr #2 load dropped 6A (158-152A). Checked and found Sintong 13.8KV GFPC T/R 5x Counter: 975-980. 16:50 It was reported (Mr. SOSKI), out sider touch PGT power line around Genting Area. 17:20 It was reported no power at Genting Area. 17:40 Checked and found Recl. 29 Z 13A T/O ctr:130-132(?) 17:52 Blocked and closed Recl. 29 Z 13A, OK then released the block. Cause: Others. |  | 1 | 15:47 | Afternoon | Monday | 2017 | 7
6291 | 2017-07-17 17:08 | 2017-07-17 17:08 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning Arrester | 27 | 17:08 Menggala fdr #1 load dropped 44A (172-128A). Ground fault alarm from Menggala fdr #1. Not checked yet. | 111 | 1 | 17:08 | Afternoon | Monday | 2017 | 7
6292 | 2017-07-17 17:08 | 2017-07-19 07:31 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning Arrester | 27 | Checked and found Recloser: 19-AN-04 T/R 2x Counter: 468-480. Patrolled the line found @1 broken Lightning Arrester on Terminal pole Meso #01. Cause: Broken Lightning Arrester. | 111 | 1 | 17:08 | Afternoon | Monday | 2017 | 7
6293 | 2017-07-18 14:20 | 2017-07-18 14:20 | MINAS POWER PLANT |  |  | - | 14:20 MGT#3 S/U then On Line to system at 14:26. For testing and monitoring Vibration. |  | 1 | 14:20 | Afternoon | Tuesday | 2017 | 7
6294 | 2017-07-18 15:31 | 2017-07-18 15:31 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Accident | 236 | 15:31 C.Duri ACB fdr#8 T/LO Ctr:326 (not operated) R/F:TOC1-N. 15:41 Bambang S. melaporkan melalui HP bahwa Kristhoporus tersengat listrik 13.8 KV di tiang 04-04-22 (C.Duri fdr#8). Call emergency #123 untuk pertolongan Ambulan. 16:00 DSC diinfokan korban menuju Rumah Sakit dengan ambulan. 16:46 Blocked & closed C.Duri ACB fdr#8, then release the block. Cause: Accident. |  | 1 | 15:31 | Afternoon | Tuesday | 2017 | 7
6295 | 2017-07-18 18:22 | 2017-07-18 18:22 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 51 | S.Balam fdr#4 T/R 1x. S.Balam GFPC T/R 1x. S.Balam fdr#1 Load dropped 48A (115-67A). Not checked yet. |  | 1 | 18:22 | Afternoon | Tuesday | 2017 | 7
6296 | 2017-07-18 18:22 | 2017-07-22 13:22 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 51 | Checked & found So.Balam VCB fdr#4 T/R 1x Ctr:339-340 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 18:22 | Afternoon | Tuesday | 2017 | 7
6297 | 2017-07-19 06:24 | 2017-07-19 06:24 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri Comm. 13.8KV ACB fdr #2 T/R 1X. Not checked yet. |  | 1 | 6:24 | Morning | Wednesday | 2017 | 7
6298 | 2017-07-19 06:24 | 2017-07-24 08:00 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Checked and found 13.8 KV D. Community fdr #2 (ACB #30) T/R 1x R/F: @1 51N Ctr: 79 - 80 Patrolled the line and found Broken pin o/p SLI-1A-05B Cause: Unidentified. |  | 1 | 6:24 | Morning | Wednesday | 2017 | 7
6299 | 2017-07-19 07:22 | 2017-07-19 07:22 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 340 | 07:22 Duri Field feeder #2 load dropped 80A (158-78A). 10:10 Checked and found Recloser: 07-V3-21 T/SO Counter: 156-157. Patrolled the line nothing found. 10:42 Blocked and closed Recloser: 07-V3-21 --> OK and then released the block. Cause: Unidentified. |  | 1 | 7:22 | Morning | Wednesday | 2017 | 7
6300 | 2017-07-19 15:14 | 2017-07-19 15:14 | 13.8KV PEMATANG FEEDER #1 | Fair | Transformer Failure | 2805 | It was reported B/O fuse at well Pematang#96 (Pematang fdr#1). Not checked yet. | 11111 | 1 | 15:14 | Afternoon | Wednesday | 2017 | 7
6301 | 2017-07-19 15:14 | 2017-07-20 14:50 | 13.8KV PEMATANG FEEDER #1 | Fair | Transformer Failure | 2805 | Checked & found @1@2 B/O fuse for 225Kva Tx at well Pematang#96. Test TTR & Megger 225Kva Tx is failure. (Would be changed tomorrow). Cause: Transformer failure. | 11111 | 1 | 15:14 | Afternoon | Wednesday | 2017 | 7
6302 | 2017-07-19 15:14 | 2017-07-25 09:58 | 13.8KV PEMATANG FEEDER #1 | Fair | Transformer Failure | 2805 | 09:56 Manually opened Pematang OCB fdr #1. 09:58 Opened both side 13.8 Kv visual opening Pematang fdr #1. Due to replaced 225 Kva with 300 Kva Transformer for well Pematang #96. 10:31 Closed both side 13.8 Kv visual opening Pematang fdr #1. Blocked and closed Pematang OCB fdr #1 and then released the block. See PIDOD on 25 July 2017 at 09:56 | 11111 | 1 | 15:14 | Afternoon | Wednesday | 2017 | 7
6303 | 2017-07-20 14:58 | 2017-07-20 14:58 | 13.8KV 4D FEEDER #5 | Fair | Planned Maintenance | 5 | 14:58 Opened LBS 4D-160 (D/S 4D fdr #5) For repairing @2 broken jumper fuse cut out on terminal pole well 4D-63. 8 wells were shut down during the job. 16:00 Closed LBS 4D-160 and then energized of the wells. Cause: Plan Maintenance. |  | 1 | 14:58 | Afternoon | Thursday | 2017 | 7
6304 | 2017-07-20 16:14 | 2017-07-20 16:14 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 60 | Bangko OCB fdr #4 T/R 1x. Bangko fdr #1 load dropped 152A (205-53A). Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 16:14 | Afternoon | Thursday | 2017 | 7
6305 | 2017-07-20 16:14 | 2017-07-22 13:14 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 60 | Checked & found Bangko VCB fdr#4 T/R 1x Ctr:0008-0009 R/F:51N. Patrolled the line & found @3 Broken Pin Insulator o/p 24Z20. Cause : Pin Insulator. |  | 1 | 16:14 | Afternoon | Thursday | 2017 | 7
6306 | 2017-07-20 22:20 | 2017-07-20 22:20 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | 22:20 It was reported unbalance voltage at CIF area #10. Not checked yet. |  | 1 | 22:20 | Night | Thursday | 2017 | 7
6307 | 2017-07-20 22:20 | 2017-07-23 14:15 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | Checked and found @3 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified. |  | 1 | 22:20 | Night | Thursday | 2017 | 7
6308 | 2017-07-21 06:07 | 2017-07-21 06:07 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Fair | Unidentified | 15 | M. SUB. LIBO 13.8KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 6:07 | Morning | Friday | 2017 | 7
6309 | 2017-07-21 06:07 | 2017-07-24 08:00 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Fair | Unidentified | 15 | Checked and found 13.8 KV MSU (North) VCB #1 (Libo fdr #1) T/R 1x R/F: 51N Ctr: 271-272 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:07 | Morning | Friday | 2017 | 7
6310 | 2017-07-21 07:26 | 2017-07-21 07:26 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 49 | 8C VCB fdr #1 T/R 1x. 8C fdr #2 load dropped 21A (82-61A). 8C fdr #3 load dropped 30A (210-180A). Not checked yet. |  | 1 | 7:26 | Morning | Friday | 2017 | 7
6311 | 2017-07-21 07:26 | 2017-07-24 16:52 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 49 | Checked & found 8C vcb fdr#1 T/R 1x, Ctr: 664-665, R/F: 51 @2. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 7:26 | Morning | Friday | 2017 | 7
6312 | 2017-07-21 11:42 | 2017-07-21 11:42 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 0 | It was reported B/O fuse at well Kulim#09 (C.Duri fdr#1). Not checked yet. |  | 1 | 11:42 | Morning | Friday | 2017 | 7
6313 | 2017-07-21 11:42 | 2017-07-22 15:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 0 | Checked and found@2,@3 b/o fuse for 45 Kva Tx at well Kulim #09 Perform TTR and Megger found Low megger reading. Cause: Tx failure (Low megger reading). This Transformer is not replaced yet. |  | 1 | 11:42 | Morning | Friday | 2017 | 7
6314 | 2017-07-21 11:42 | 2017-07-24 12:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 0 | Replaced 45 Kva Tx failure with 112.5 Kva Tx. Energized 112.5 Kva Tx. Cause: Tx failure. |  | 1 | 11:42 | Morning | Friday | 2017 | 7
6315 | 2017-07-21 14:41 | 2017-07-21 14:41 | 13.8KV ROKAN FEEDER #4 | Fair | Animal | 20 | 14:41 It was reported B/O fuse at well Kirana#1 (Rokan fdr#4). 16:30 Checked & found @2@3 B/O fuse for 300Kva Tx at well Kirana#1. Dead Monkey on T/P well Kirana#1. 16:41 Opened Rokan VCB fdr#4. Dismantle Dead monkey on T/P Kirana#1. 16:51 Blocked & closed Rokan VCB fdr#4,then release the block. 17:00 Replaced @2@3 B/O fuse for 300Kva Tx with the same size. Cause: Animal (Monkey). |  | 1 | 14:41 | Afternoon | Friday | 2017 | 7
6316 | 2017-07-21 16:28 | 2017-07-21 16:28 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 162 | It was reported B/O fuse at well Kulim#67 (C.Duri fdr#1). Not checked yet. |  | 1 | 16:28 | Afternoon | Friday | 2017 | 7
6317 | 2017-07-21 16:28 | 2017-07-22 16:20 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 162 | 16:20 Checked and found @3 b/o fuse for 75 Kva Tx at well Kulim #67 (D/S C.Duri fdr #1). Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified. |  | 1 | 16:28 | Afternoon | Friday | 2017 | 7
6318 | 2017-07-22 06:19 | 2017-07-22 06:19 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Sintong fdr #2 load dropped 61A (157-96A). Sintong GFPC T/R 1X. Not checked yet. |  | 1 | 6:19 | Morning | Saturday | 2017 | 7
6319 | 2017-07-22 06:19 | 2017-07-25 07:23 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Checked & found Recloser 28 AF 02 T/R 1x, Ctr: 1140 – 1141, R/F: none Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 6:19 | Morning | Saturday | 2017 | 7
6320 | 2017-07-22 06:20 | 2017-07-22 06:20 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 82 | 06:20 C.Duri 13.8 KV ACB fdr #16 T/LO Counter: 298 - 302 R/F: 51@1,@2 & 50@2. 07:10 Blocked and closed C.Duri 13.8 KV ACB fdr #16 --> OK and then released the block. 08:10 It was reported no power on road #3 on pole 09-M3-10. Checked and found Recloser: 09-M3-01 T/SO Counter:201-202 R/F: 51@3. 08:52 Patrolled the line nothing found. 08:56 Blocked and closed Recloser: 09-M3-01 --> OK and then released the block. Cause: Unidentified. |  | 1 | 6:20 | Morning | Saturday | 2017 | 7
6321 | 2017-07-22 09:28 | 2017-07-22 09:28 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 12 | 09:28 C. Duri 13.8KV ACB fdr #1 T/O ctr: 201-202 R/F: 51N. (In Block position during RIG activity). 09:40 Blocked and closed C. Duri ACB #11 (fdr #1), OK then released the Block. Cause: Not patrolled yet. |  | 1 | 9:28 | Morning | Saturday | 2017 | 7
6322 | 2017-07-22 09:28 | 2017-07-24 17:29 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 12 | Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 9:28 | Morning | Saturday | 2017 | 7
6323 | 2017-07-22 09:30 | 2017-07-22 09:30 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Animal | 0 | 09:30 It was reported b/o fuse on pole 04-02-13B (Station 4SC) D/S C Duri fdr #8. 15:20 Checked and found @1,@2 b/o fuse for 112.5 Kva Tx. Perform TTR and megger found good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (Monkey). |  | 1 | 9:30 | Morning | Saturday | 2017 | 7
6324 | 2017-07-22 13:20 | 2017-07-22 13:20 | 13.8KV BEKASAP FEEDER #2 | Fair | Animal | 0 | 13:20 It was reported b/o fuse at well Bekasap #06 (D/S Bekasap fdr #2). 15:39 Checked and found @2,@3 b/o fuse for 150 Kva Tx. Perform TTR and megger found good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (Bird). |  | 1 | 13:20 | Afternoon | Saturday | 2017 | 7
6325 | 2017-07-22 13:20 | 2017-07-22 13:20 | 13.8KV BEKASAP FEEDER #3 | Fair | Low mega-ohm reading | 0 | 13:20:01 It was reported b/o fuse at well Bekasap #146 (LTC well) d/s Bekasap fdr #3. 16:18:00 Checked and found @1,@2,@3 b/o fuse for 150 Kva Tx. Perform TTR and megger found Low megger reading. Cause: Low megger reading Tx. This Transformer is not replaced yet. |  | 1 | 13:20 | Afternoon | Saturday | 2017 | 7
6326 | 2017-07-22 13:20 | 27/09/2017 10:58 | 13.8KV BEKASAP FEEDER #3 | Fair | Low mega-ohm reading | 0 | Replaced 300KVA Tx with the same size then energized the Tx at well Bekasap #146. Cause : Low Megger Reading. See PIDOD; 27 Sep On 10:58. |  | 1 | 13:20 | Afternoon | Saturday | 2017 | 7
6327 | 2017-07-23 00:05 | 2017-07-23 00:05 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 95 | 00:05 It was reported b/o fuse for Tx at well Bangko #167 D/S Nella fdr #1. 10:12 Checked and found @1,@2 b/o fuse for 300 Kva Tx. Perform TTR and megger found good reading. Replaced b/o fuse above with the same size and energizes the Tx. Cause: Animal (Monkey). |  | 1 | 0:05 | Night | Sunday | 2017 | 7
6328 | 2017-07-24 09:03 | 2017-07-24 09:03 | 13.8KV 8D FEEDER #11 | Fair | Lightning | 0 | 8D fdr #11 load dropped 106A (172-66A). Not checked yet. |  | 1 | 9:03 | Morning | Monday | 2017 | 7
6329 | 2017-07-24 09:03 | 2017-07-27 08:53 | 13.8KV 8D FEEDER #11 | Fair | Lightning | 0 | Checked & found Recl. 9E-02 T/R 1x, Ctr: 0062-0063, R/F: None Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 9:03 | Morning | Monday | 2017 | 7
6330 | 2017-07-24 09:03 | 2017-07-27 08:53 | 13.8KV 8D FEEDER #11 | Fair | Lightning | 0 | Checked & found Recl. 9E-02 T/R 1x, Ctr: 0062-0063, R/F: None Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 9:03 | Morning | Monday | 2017 | 7
6331 | 2017-07-24 10:49 | 2017-07-24 10:49 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 238 | 10:49 Manually opened Recloser: 41-AW-62 due to: 1. Replaced secondary cable at well Kulin #87 and #88. 2. Change out transformerat well Kulin #09. 10:52 Opened yellow switch of Recloser 41-AW-62. 10:56 Opened visual opening of Recloser 41-AW-62. 12:48 Closed visual opening and yellow switch of Recloser 41-AW-62. 12:50 Blocked and closed Recloser: 41-AW-62 and then released the block. Cause: Plan Maintenance. |  | 1 | 10:49 | Morning | Monday | 2017 | 7
6332 | 2017-07-24 14:38 | 2017-07-24 14:38 | CENTRAL DURI POWER PLANT |  |  | - | 14:38 S/U CGD#4 ,then on line the unit at 14:58 14:36 Open Tie breaker ACB#39. |  | 1 | 14:38 | Afternoon | Monday | 2017 | 7
6333 | 2017-07-24 15:04 | 2017-07-24 15:04 | CENTRAL DURI POWER PLANT |  |  | - | 15:04 Off line CGT#3 then S/D the unit for S/B. 15:07 Closed Tie breaker ACB#39. |  | 1 | 15:04 | Afternoon | Monday | 2017 | 7
6334 | 2017-07-25 09:45 | 2017-07-25 09:45 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 47 | 09:45 Opened LBS 27-AL-03 D/S Ketigul fdr #2. Due to Disconnecting exiting transformer and installed buck arm at well UBI #32. 10:05 Closed 27-AL-03 D/S Ketigul fdr #2. Cause: Plan Maintenance. |  | 1 | 9:45 | Morning | Tuesday | 2017 | 7
6335 | 2017-07-25 09:56 | 2017-07-25 09:56 | 13.8KV PEMATANG FEEDER #1 | Fair | Planned Maintenance | 68 | 09:56 Manually opened Pematang OCB fdr #1. 09:58 Opened both side 13.8 Kv visual opening Pematang fdr #1. Due to replaced 225 Kva with 300 Kva Transformer for well Pematang #96. 10:31 Closed both side 13.8 Kv visual opening Pematang fdr #1. Blocked and closed Pematang OCB fdr #1 and then released the block. cause: Planned maintenance. |  | 1 | 9:56 | Morning | Tuesday | 2017 | 7
6336 | 2017-07-26 10:30 | 2017-07-26 10:30 | 13.8KV MENGGALA FEEDER #1 | Fair | Construction Job | 0 | 10:30 Manual Opened Menggala OCB fdr#1 . Production loss: 65 Bbls / 33 wells. 10:45 Manual Closed Menggala OCB fdr#1. Open & Close HLC, Project team install Buck Arm for New well near Meno #21. 14:50 Manual Opened Menggala OCB fdr#1 Production loss: 54 Bbls / 33 wells. 15:14 Manual Closed Menggala OCB fdr#1 Open Isolation Switch to install Static Wire for New Well Near Meno #21. Cause : Planned Maintenance. Total Production loss: 109 Bbls / 33 wells. |  | 1 | 10:30 | Morning | Wednesday | 2017 | 7
6337 | 2017-07-26 11:08 | 2017-07-26 11:08 | 13.8KV PUNGUT FEEDER #1 | Fair | Unidentified | 1 | 11:08 It was reported b/o fuse at well Pungut #24 (d/s Pungut fdr#1). 14:10 Checked & found b/o fuse for 150KvaTx. Replaced fuse with the same size, the energized the TX. Cause: Unidentified |  | 1 | 11:08 | Morning | Wednesday | 2017 | 7
6338 | 2017-07-27 03:47 | 2017-07-27 03:47 | 13.8KV 8C FEEDER #1 | Fair | Animal | 39 | 03:47 8C fdr #1 load dropped 90 A (196-106A). 05:45 Checked and found Recloser 9D-25 T/SO Counter:51-52. Blocked and closed Recloser 9D-25 but failed. 06:30 Patrolled the line found Bat hang on powerline on Terminal pole 8E-94. Dismantle Bat from powerline. 06:42 Blocked and closed Recloser 9D-25 --> OK. Cause: Animal (Bat/ Kelelawar). |  | 1 | 3:47 | Night | Thursday | 2017 | 7
6339 | 2017-07-27 07:30 | 2017-07-27 07:30 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 57 | Sintong vcb fdr#2 T/R. Not checked yet. |  | 1 | 7:30 | Morning | Thursday | 2017 | 7
6340 | 2017-07-27 07:30 | 2017-07-28 17:10 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 57 | Checked & found Sintong Fdr#2 T/R 1X counter: 461-462, R/F : 51N. GFPC T/R 4x, Ctr: 982-986, R/F : 51N. Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 7:30 | Morning | Thursday | 2017 | 7
6341 | 2017-07-28 03:41 | 2017-07-28 03:41 | 13.8KV PUNGUT FEEDER #2 | Fair | Unidentified (L/A) | 3 | 03:41 Pungut fdr #2 load dropped 25A (61-36A). Production loss : 46 Bbls / 3 wells --> Pungut GS. Pungut fdr #1 load dropped 15A (79-64A). Production loss : 3 Bbls / 6 wells --> Libo GS. Bus voltage 14.9 Kv at Pungut substation. ------------------------------------------------- + 04:53 Bus voltage 13.8 Kv at Pungut substation. Total : 49 Bbls / 9 wells. Pungut fdr #1 load dropped 8A (79-71A). Pungut fdr #2 load dropped 13A (61-48A). 05:39 Patrolled the line found Recloser 46-BP-12 Normal condition. Patrolled the line found Recloser 45-BR-01 T/R 1x Counter:502-503. Not patrolled yet. |  | 1 | 3:41 | Night | Friday | 2017 | 7
6342 | 2017-07-28 03:41 | 2017-04-08 18:24 | 13.8KV PUNGUT FEEDER #2 | Fair | Unidentified (L/A) | 3 | Patrolled the Line, found Recl. 45RB01 T/R 1x, Ctr: 593-594, R/F: None. also found @3 Broken LA o/p 45-BT-7 Cause : Unidentified (L/A) |  | 1 | 3:41 | Night | Friday | 2017 | 7
6343 | 2017-07-28 07:05 | 2017-07-28 07:05 | 13.8KV SINTONG FEEDER #1 | Fair | Post Pin Insulator | 0 | Sintong fdr #1 Load dropped 17A (84-67A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 7:05 | Morning | Friday | 2017 | 7
6344 | 2017-07-28 07:05 | 2017-07-29 13:52 | 13.8KV SINTONG FEEDER #1 | Fair | Post Pin Insulator | 0 | Checked & found Recl. 26.AE.22 T/R 1x, Ctr: 356-357, R/F: None. Patrolled the Line, found @1 broken Pin Insulator o/p 26-AH-12 Cause : Post Pin Insulator |  | 1 | 7:05 | Morning | Friday | 2017 | 7
6345 | 2017-07-28 14:45 | 2017-07-28 14:45 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Tree | 389 | 14:45 So Bekasap OCB fdr#1 T/LO, Checked & found OCB fdr#1 Ctr: 386-389, R/F: 51 @2. Patrolled the Line, but found nothing, (Recl. 37.BI.01 in bypass status) toward Pmt Bow field. 17:07 Blocked & Closed OCB fdr#1, but Failed. 17:46 Opened Isolation Switch OCB fdr#1 at Load side. Blocked & Closed OCB fdr#1, OK. 17:50 Closed & Closed Isolation Switch OCB fdr#1 Blocked & Closed OCB fdr#1, but Failed. 18:07 Opened Recl. 37.BG.48 and Opened the Visual Opening Blocked & Closed OCB fdr#1, success. Continued Patrolled Downstream Recl. 37.BG.48, found Fallen Tree at @2. 18:57 Opened OCB fdr#1. Closed Bypass of Recl. 37.BG.48 19:01 Blocked & Closed OCB fdr#1, Sucess then released the Block. Cause : Tree. Production Loss : 280 Bbls / 16 wells --> Ampuh GS. Production Loss : 199 Bbls / 19 wells --> So Bek GS. ------------------------------------------------------------- + Total : 479 Bbls / 35 wells. |  | 1 | 14:45 | Afternoon | Friday | 2017 | 7
6346 | 2017-07-28 18:45 | 2017-07-28 18:45 | MINAS POWER PLANT |  |  | - | 18:45 MGT#10 offline and S/D for S/B. |  | 1 | 18:45 | Afternoon | Friday | 2017 | 7
6347 | 2017-07-29 00:59 | 2017-07-29 00:59 | 13.8KV 5B FEEDER #8 | Fair | Unidentified | 38 | 00:59 5B fdr#8 load dropped 70A (187-117A). 01:18 It was reported b/o fuse at GS#4. 10:50 Checked & found @2@3 b/o fuse for 2.5MVATX (WIP BD45) Tested TTR & Megger found good reading Replaced b/o fuse above with the same size, then energized the TX Cause: Unidentified. |  | 1 | 0:59 | Night | Saturday | 2017 | 7
6348 | 2017-07-29 07:35 | 2017-07-29 07:35 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Dead End Insulator | 0 | C.Duri ACB #28 (fdr#16) T/R 1x Ctr: 302-303 R/F: 51@1@2. Not patrolled yet. |  | 1 | 7:35 | Morning | Saturday | 2017 | 7
6349 | 2017-07-29 07:35 | 2017-01-08 17:00 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Dead End Insulator | 0 | 17:00 Patrolled the line and found @1 broken Dead End insulator o/p 03-H-03 d/s C. Duri fdr #16. Cause: Broken Dead End. |  | 1 | 7:35 | Morning | Saturday | 2017 | 7
6350 | 2017-07-29 07:35 | 2017-07-29 07:35 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | C.Duri ACB #22 (fdr#5) T/R 1x. Ctr: 248-249 R/F: 51 @2, 51G. Not patrolled yet. |  | 1 | 7:35 | Morning | Saturday | 2017 | 7
6351 | 2017-07-29 07:35 | 2017-01-08 17:00 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | 17:00 Patrolled the line, but not found abnormal d/s C. Duri fdr #5. Cause: Unidentified. |  | 1 | 7:35 | Morning | Saturday | 2017 | 7
6352 | 2017-07-29 10:45 | 2017-07-29 10:45 | 13.8KV BEKASAP FEEDER #3 | Fair | Construction Job | 0 | 10:45 Manually Open LBS 37.BD.22 (d/s BKS fdr#3) Project team install TX for New well BKS 183. 11:30 Manually Closed back the LBS, OK. Cause: Planned Maintenance (Project). |  | 1 | 10:45 | Morning | Saturday | 2017 | 7
6353 | 2017-07-29 12:14 | 2017-07-29 12:14 | 13.8KV 8C FEEDER #4 | Fair | Fire | 25 | 8C VCB fdr #4 T/R 1x. Not checked yet. |  | 1 | 12:14 | Afternoon | Saturday | 2017 | 7
6354 | 2017-07-29 12:14 | 2017-07-30 11:40 | 13.8KV 8C FEEDER #4 | Fair | Fire | 25 | Checked & found 8C VCB fdr#4 T/R 1x, Ctr:593 - 595, R/F: 51 @2@3. Patrolled the Line, found land Fire under power Line near 8C Substation. Cause : Fire. |  | 1 | 12:14 | Afternoon | Saturday | 2017 | 7
6355 | 2017-07-29 16:57 | 2017-07-29 16:57 | MINAS POWER PLANT |  |  | - | 16:57 MGT 10 S/U, then On Line at 17:14. (Keep Load 25 Mw, 20 Mvar), for Testing. |  | 1 | 16:57 | Afternoon | Saturday | 2017 | 7
6356 | 2017-07-30 10:40 | 2017-07-30 10:40 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 0 | 10:40 Man. Opened Bekasap OCB fdr#2 Project team Install 150KVATX for New Well BKS#184. 11:40 Man. Closed Bekasap OCB fdr#2. Cause: Construction job. |  | 1 | 10:40 | Morning | Sunday | 2017 | 7
6357 | 2017-07-30 18:52 | 2017-07-30 18:52 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 0 | 18:52 Man. Open Rangau OCB fdr#2. (Production Line Leaks near Rangau GS). 23:11 Manually Blocked and closed Rangau fdr #2 and then released the block. Cause: Planned Maintenance. |  | 1 | 18:52 | Afternoon | Sunday | 2017 | 7
6358 | 2017-07-30 21:56 | 2017-07-30 21:56 | 13.8KV PUNGUT FEEDER #2 | Fair | Powerline - Conductor | 176 | 21:56 It was reported spark on pole 46-BT-17 towards Tandun#12 D/S Pungut fdr #2. 23:02 Checked and found spark on pole 46-BT-17. 23:35 Shut down well Tandun #12 and opened fuse holder for 100 Kva Tx due to reduce spark. Cause: spark on conductor. |  | 1 | 21:56 | Night | Sunday | 2017 | 7
6359 | 2017-07-31 00:49 | 2017-07-31 00:49 | 13.8KV CENTRAL DURI FEEDER #16 | Rain and Lightning | Lightning | 0 | C. Duri 13.8KV ACB fdr # 16 T/R 1X Counter:303-304 R/F: 50 @1, @2. Not patrolled yet. |  | 1 | 0:49 | Night | Monday | 2017 | 7
6360 | 2017-07-31 00:49 | 2017-01-08 17:00 | 13.8KV CENTRAL DURI FEEDER #16 | Rain and Lightning | Lightning | 0 | 17:00 Patrolled the line and found broken @1 Dead End Insulator o/p 030H-03 d/s C. Duri fdr #16. Cause: Lightning. |  | 1 | 0:49 | Night | Monday | 2017 | 7
6361 | 2017-07-31 21:38 | 2017-07-31 21:38 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 47 | Batang OCB fdr #3 T/R 1x. Not checked yet. |  | 1 | 21:38 | Night | Monday | 2017 | 7
6362 | 2017-07-31 21:38 | 2017-05-08 03:39 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | 47 | Checked & found Batang OCB fdr#3 T/R 2x, Ctr: 346-348, R/F: 51N. Patrolled the Line, found @ 3 Broken LA. o/p 37-AL-12 and @1 o/p 40-AJ-11. Cause : Lightning |  | 1 | 21:38 | Night | Monday | 2017 | 7
6363 | 2017-01-08 10:07 | 2017-01-08 10:07 | MINAS POWER PLANT |  |  | - | 10:07 MGT #10 S/U, then On line at 10:37. for Running test. 16:32 MGT #10 Off Line and S/D for S/B waiting Gen. balancing. |  | 1 | 10:07 | Morning | Sunday | 2017 | 1
6364 | 2017-01-08 10:30 | 2017-01-08 10:30 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Transformer Failure | 0 | 10:30 It was reported b/o fuses at well KB #333. 11:10 Checked and found @1 b/o fuse for 550KVA TX. Performed TTR test and Megger the TX and found TX failure. Cause: TX failure (will be replaced soon). | 1111 | 1 | 10:30 | Morning | Sunday | 2017 | 1
6365 | 2017-01-08 10:30 | 2017-04-08 16:30 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Transformer Failure | 0 | 16:30 Replaced 550Kva Tx with same size at KB 333 d/s NKB fdr #3. Cause: Tx failure. | 1111 | 1 | 10:30 | Morning | Sunday | 2017 | 1
6366 | 2017-01-08 10:33 | 2017-01-08 10:33 | 44KV BEKASAP MAIN - SOUTH BEKASAP LINE | Fair | Planned Maintenance | 683 | 10:33 Manually Opened 44KV Bekasap Main OCB#2, toward So.Bekasap Substation. Job Done - Replace 150KVATX at well Sakti #02. - Repair Hot spot at Sobek Substation. - Sleeve Corrosive Pole. - Replace Pin Insulator o/p.... - Dismantle 150KVATX at OBS well Tegar#05. - Replace Recl. 37.BI.01. 17:09 Manually Closed 44KV Bekasap Main OCB #2, after Normalized Grounding and Isolation Switches. 17:12 Manually Closed 13.8 KV Sobek fdr OCB #1, after got Clearance with Bekasap GS, Ampuh GS and Field Operator. Cause: Planned Maintenance. | 12345 | 1 | 10:33 | Morning | Sunday | 2017 | 1
6367 | 2017-01-08 14:28 | 2017-01-08 14:28 | 13.8KV SINTONG FEEDER #1 | Fair | Construction Job | 0 | 14:28 Manually Open LBS 26-AE-06 (d/s Sintong fdr#1). Project Team install New Power Line for New Well, Near Seruni#32. 15:27 Manually Closed the LBS above after finished the Job. Cause: Planned Maintenance (project). |  | 1 | 14:28 | Afternoon | Sunday | 2017 | 1
6368 | 2017-01-08 14:36 | 2017-01-08 14:36 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 34 | 14:36 4D OCB fdr#4 T/R 2x. 4D fdr#5 Load dropped 143A (254-111A). 4D fdr#5 Load dropped 78A (84-5A). Not checked yet. |  | 1 | 14:36 | Afternoon | Sunday | 2017 | 1
6369 | 2017-01-08 14:36 | 2017-04-08 16:43 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 34 | Checked & found, 4D OCB fdr#4 T/R 1x, 249-251, R/F; 51 @2. Patrolled the Line, found @2 broken Dean end insulator o/p 5E-32. Cause : Lightning |  | 1 | 14:36 | Afternoon | Sunday | 2017 | 1
6370 | 2017-01-08 15:45 | 2017-01-08 15:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 51 | 15:45 It was reported B/O fuse at well KULIN #67 (CD fdr#1). 17:20 Checked & found @3 b/o fuse for 75KVATX, Pad mounted. Replaced fuse with the same size, the Energized the TX. Cause : Unidentified (Fuse). |  | 1 | 15:45 | Afternoon | Sunday | 2017 | 1
6371 | 2017-02-08 07:14 | 2017-02-08 07:14 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 38 | 07:14 Batang fdr #3 load dropped 24A ( 61-37A ). Batang GFPC T/R 1x. 11:00 It was reported No Power at Candi field d/s Batang fdr #3 . 12:30 Checked and found Recl. 36-AL-13 T/SO ctr:122-123 R/F: No. Blocked and closed the Recloser, then released the Block. Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 7:14 | Morning | Wednesday | 2017 | 2
6372 | 2017-02-08 08:20 | 2017-02-08 08:20 | MINAS POWER PLANT |  |  | - | 08:20 MGT #10 S/U, then On Line at 09:27 for Running test 14:10 MGT #10 Off line and S/D for Gen. Balancing 17:50 MGT #10 S/U for running test until 24MW, 20Mvar, Vibration higher 0.45 I/s. |  | 1 | 8:20 | Morning | Wednesday | 2017 | 2
6373 | 2017-02-08 10:30 | 2017-02-08 10:30 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 10:30 It was reported B/O fuse at well Petapahan #135 (Petapahan fdr#2). Checked & found @2 b/o fuse for 400KVATX . Performed TTR Test & Megger the TX . Ok. Replaced the fuse with same size, then energized the Tx. Cause : Unidentified (Fuse) | 1111 | 1 | 10:30 | Morning | Wednesday | 2017 | 2
6374 | 2017-02-08 11:21 | 2017-02-08 11:21 | 13.8KV PEMATANG FEEDER #2 | Fair | Transformer Failure | 0 | 11:21 It was reported B/O fuse at well Pematang #07 (Pematang fdr#2). Checked & found Tx failure @1. |  | 1 | 11:21 | Morning | Wednesday | 2017 | 2
6375 | 2017-02-08 11:21 | 2017-03-08 16:16 | 13.8KV PEMATANG FEEDER #2 | Fair | Transformer Failure | 0 | 16:16 Replaced energized 150KVA TX at well Pematang #07 d/s Pematang fdr #2. Cause: TX failure. (See Outage 03 Aug at 09:49). |  | 1 | 11:21 | Morning | Wednesday | 2017 | 2
6376 | 2017-03-08 07:25 | 2017-03-08 07:25 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 07:25 It was reported B/O fuse o/p 09-T3-03 for well 3-T3-45C, 3-T3-45B, 3-T3-34. 14:41 Checked and found B/O fuse @2 112.5 KVA TX, D/S C. Duri #4. Performed TTR and Megger, result OK. Replaced fuse with same size. Cause: Unidentified (Fuse). |  | 1 | 7:25 | Morning | Wednesday | 2017 | 3
6377 | 2017-03-08 09:49 | 2017-03-08 09:49 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 564 | 09: 49 Manual open Pematang fdr #2. Replaced 150 KVA TX at location Pematang 07 D/S Pematang fdr #2. Replaced Recloser o/p 34-BC-08. 16:12 Closed Pematang fdr #2, Ctr: 461-462. Closed Recloser o/p 34-BC-08. Cause: Planned Maintenance. | 1111 | 1 | 9:49 | Morning | Wednesday | 2017 | 3
6378 | 2017-03-08 10:15 | 2017-03-08 10:15 | 115KV MINAS - LUKUT LINE | Fair | Planned Maintenance | 0 | S/D power to BOB due to NDC off line wash and CI program. Cause: Planned Maintenance. |  | 1 | 10:15 | Morning | Wednesday | 2017 | 3
6379 | 2017-03-08 10:15 | 2017-07-08 16:12 | 115KV MINAS - LUKUT LINE | Fair | Planned Maintenance | 0 | 16:12 Closed 115KV Breaker at Lukut (Power to BOB). |  | 1 | 10:15 | Morning | Wednesday | 2017 | 3
6380 | 2017-03-08 10:48 | 2017-03-08 10:48 | CENTRAL DURI POWER PLANT | Fair |  | - | 10:48 S/U CGT #3 11:05 Online to system. 11:03 Open Tie Breaker ACB #39. |  | 1 | 10:48 | Morning | Wednesday | 2017 | 3
6381 | 2017-03-08 10:54 | 2017-03-08 10:54 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse o/p 01-09-25 D/S Duri field fdr #3. Checked and found @3 B/O fuse for 112.5 KVA TX. Performed TTR & Megger the TX, result OK. Replaced B/O TX with same size and energized the TX. Cause: Unidentified (Fuse). |  | 1 | 10:54 | Morning | Wednesday | 2017 | 3
6382 | 2017-03-08 15:47 | 2017-03-08 15:47 | 13.8KV 4D FEEDER #4 | Fair | Planned Maintenance | 103 | 15:47 Open LBS 36-DN-27 D/S 6DN fdr #1 (feed by 4D fdr #4) and D/S 4D fdr #4 to repair critical hot spot o/p 5D-18. --> Replace FCO. 16:38 Close LBS 36-DN-27. Cause: Planned Maintenance. |  | 1 | 15:47 | Afternoon | Wednesday | 2017 | 3
6383 | 2017-03-08 16:30 | 2017-03-08 16:30 | MINAS POWER PLANT |  |  | - | 16:30 S/U MGT #2 16:50 Online to system. |  | 1 | 16:30 | Afternoon | Wednesday | 2017 | 3
6384 | 2017-03-08 18:08 | 2017-03-08 18:08 | MINAS POWER PLANT |  |  | - | 18:08 S/U MGT #5 18:25 Online to system. |  | 1 | 18:08 | Afternoon | Wednesday | 2017 | 3
6385 | 2017-03-08 20:55 | 2017-03-08 20:55 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | 20:55 NDC CT #3 Off line then S/D for Off Line Wash. Cause: Planned Maintenance. 04 Aug 2017 --------------- 18:05 NDC#3 S/U, then On line at 18:31. 18:43 NDC#3 Of Line and S/D due to Vibration 7.7 mils. 19:03 NDC#3 S/U, then On line at 19:30. 21:33 NDC#3 Off Line and S/D due to 8.1 mils. 21:51 NDC#3 S/U, then On line at 22.19. 00:43 NDC#3 Base Load 100MW, 56Mvar, Vibration average 2.7 mils After Perform Off Line wash. Cause: Planned Maintenance |  | 1 | 20:55 | Night | Wednesday | 2017 | 3
6386 | 2017-03-08 22:55 | 2017-03-08 22:55 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 62 | 22:55 It was reported B/O fuse at Well Meso#12 (d/s Menggala fdr#1). Not Checked yet. |  | 1 | 22:55 | Night | Wednesday | 2017 | 3
6387 | 2017-03-08 22:55 | 2017-04-08 09:45 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 62 | 09:45 Checked and found @3 b/o fuse for 300KVA TX at well MESO #12 d/s Menggala fdr #1. Performed TTR test and Megger the TX and found Good condition. Replaced b/o fuse above with same size, then energized the TX. OK. Cause: Animal (squirrel). |  | 1 | 22:55 | Night | Wednesday | 2017 | 3
6388 | 2017-04-08 07:50 | 2017-04-08 07:50 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Animal | 0 | 07:50 It was reported spark on Tx o/p 2F-15-03 ( at Kapolsek Duri ) 14:00 Check and found @1 , b/o fuse for 100 Kva Tx ( single fhase ). 14:15 Open LBS 2F-15-01. 15:00 Replaced broken b/o fuse above with same size and energize the Tx. Close LBS 2F-15-01. Cause: Animal (squirrel ). |  | 1 | 7:50 | Morning | Saturday | 2017 | 4
6389 | 2017-04-08 09:38 | 2017-04-08 09:38 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified (Fuse) | 4 | 09:38 It was reported B/O fuse at well Balam #315. 10:15 Checked and found @1,@2 b/o fuse for 100 Kva Tx at well Balam #315. Performed TTR test and magger the TX, ok. Replace B/O fuse with the same size , then energized the TX. OK Cause: Unidentified (Fuse). |  | 1 | 9:38 | Morning | Saturday | 2017 | 4
6390 | 2017-04-08 18:05 | 2017-04-08 18:05 | NORTH DURI POWER PLANT |  |  | - | 18:05 NDC#3 S/U, then On line at 18:31. 18:43 NDC#3 Of Line and S/D due to Vibration 7.7 mils. 19:03 NDC#3 S/U, then On line at 19:30. 21:33 NDC#3 Off Line and S/D due to 8.1 mils. 21:51 NDC#3 S/U, then On line at 22.19. 00:43 NDC#3 Base Load 100MW, 56Mvar, Vibration average 2.7 mils After Perform Off Line wash. |  | 1 | 18:05 | Afternoon | Saturday | 2017 | 4
6391 | 2017-05-08 00:52 | 2017-05-08 00:52 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 86 | 00:52 Ketigul VCB fdr#2 T/R 1x. Ketigul fdr#1 Load dropped 24A (102-78A) Ketigul fdr#3 Load dropped 19A (25-6A) Not checked yet. |  | 1 | 0:52 | Night | Monday | 2017 | 5
6392 | 2017-05-08 00:52 | 2017-12-08 16:52 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 86 | Checked & found Ketigul VCB fdr#2 T/R 3x Ctr:246-249 R/F:50@1@2. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 0:52 | Night | Monday | 2017 | 5
6393 | 2017-05-08 02:42 | 2017-05-08 02:42 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | 02:42 NDC CT#1 Off Line & S/D, for Off Line Wash. 18:48 NDC CT#1 S/U, then On Lne at 19:23 after Of line Wash program. Cause: Planned Maintenance. |  | 1 | 2:42 | Night | Monday | 2017 | 5
6394 | 2017-05-08 07:08 | 2017-05-08 07:08 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 0 | 07:08 C. Duri 13.8KV ACB fdr#8 T/SO Ctr: 327-327 (Not change) R/F: 51@1, 51N. Not patrolled yet. |  | 1 | 7:08 | Morning | Monday | 2017 | 5
6395 | 2017-05-08 07:08 | 2017-06-08 14:40 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 0 | 14:40 Patrolled the line but nothing found. Cause: Unidentified. |  | 1 | 7:08 | Morning | Monday | 2017 | 5
6396 | 2017-05-08 12:00 | 2017-05-08 12:00 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 26 | 12:00 It was reported no power at Genting field. 14:15 Checked and found Recl 29-Z-13A T/So ctr:171-172. Blocked and closed Recloser. OK then released the Block. Patrolled the Line, but found nothing Cause: Unidentified. |  | 1 | 12:00 | Afternoon | Monday | 2017 | 5
6397 | 2017-05-08 18:26 | 2017-05-08 18:26 | 13.8KV KETIGUL FEEDER#2 | Fair | Theft | 196 | 18:26 Ketigul fdr #2 load dropped 58A ( 168-110A ) 22:15 It was reported some vandalism (Losses @1@2@3 fuses) at well Sikladi#23, Ubi#28, Ubi#30. Ubi#21 & Ubi#36. Not checked yet. |  | 1 | 18:26 | Afternoon | Monday | 2017 | 5
6398 | 2017-05-08 18:26 | 2017-06-08 15:45 | 13.8KV KETIGUL FEEDER#2 | Fair | Theft | 196 | 15:45 Repaired and energized 500KVA TX (vandalism) at well UBI-28 d/s Ketigul fdr #2. (after replaced 3Pcs FCO, Scondary cable and Connector). 16:20 Repaired and energized 500KVA TX (Vandalism) at well SIkaladi - 23. (after replaced 3Pcs FCO, Scondary cable and Connector). (will be replaced tomorrow 500KVA TX (Vandalism) at well UBI - 30). Cause: Theft. |  | 1 | 18:26 | Afternoon | Monday | 2017 | 5
6399 | 2017-05-08 18:26 | 2017-07-08 11:12 | 13.8KV KETIGUL FEEDER#2 | Fair | Theft | 196 | 11:12 Repaired and energized 150KVA TX (vandalism) at well UBI-30 d/s Ketigul fdr #2. (after replaced 500KVA TX to 150KVA TX, 3Pcs FCO, Scondary cable and Connector). Cause: Theft. |  | 1 | 18:26 | Afternoon | Monday | 2017 | 5
6400 | 2017-06-08 02:05 | 2017-06-08 02:05 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | 02:05 NDC CT#2 Off line & S/D for CI and Off line wash. Cause: Planned Maintenance. |  | 1 | 2:05 | Night | Thursday | 2017 | 6
6401 | 2017-06-08 02:05 | 13/08/2017 17:17 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | 17:17 S/U NDC#2 the on line at 17:43 after CI and Off line wash. |  | 1 | 2:05 | Night | Thursday | 2017 | 6
6402 | 2017-07-08 06:03 | 2017-07-08 06:03 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Duri field sw gear VCB#41 fdr#1 T/R 1x. Not patrolled yet. |  | 1 | 6:03 | Morning | Saturday | 2017 | 7
6403 | 2017-07-08 06:03 | 14/08/2017 08:00 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Checked and found 13.8 KV Duri field fdr #1 T/R: 1x Ctr:680-681 R/F: @1 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:03 | Morning | Saturday | 2017 | 7
6404 | 2017-07-08 17:15 | 2017-07-08 17:15 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 17:15 C. Duri fdr #1 load drpped 40A (108-68A). Not checked yet. |  | 1 | 17:15 | Afternoon | Saturday | 2017 | 7
6405 | 2017-07-08 17:15 | 14/08/2017 08:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found Recloser 41-AW-62 T/R 1x Ctr: 252-253 R/F: @1 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:15 | Afternoon | Saturday | 2017 | 7
6406 | 2017-07-08 18:53 | 2017-07-08 18:53 | 13.8KV 8C FEEDER #1 | Fair | Lightning | 29 | 8 C13.8KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 18:53 | Afternoon | Saturday | 2017 | 7
6407 | 2017-07-08 18:53 | 2017-09-08 08:53 | 13.8KV 8C FEEDER #1 | Fair | Lightning | 29 | Checked & found Recl. 9D-11 T/R 1x Ctr;1236-1237 R/F:51@1. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 18:53 | Afternoon | Saturday | 2017 | 7
6408 | 2017-08-08 07:01 | 2017-08-08 07:01 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | 204 | 07:01 Minas Fdr#4 T/LO Ctr:74-76 R/F:51N. Patrolled the line but found nothing. 08:10 Block and close Minas Fdr#4, then release the block. Cause: unidentified. |  | 1 | 7:01 | Morning | Tuesday | 2017 | 8
6409 | 2017-08-08 10:34 | 2017-08-08 10:34 | 13.8KV 5B FEEDER #1 | Rain | Lightning | 71 | 5B Fdr#1 T/R 1X. 5B fdr#2 Load dropped 150A (161-11A). 5B fdr#3 Load drooped 27A (40-13A). Not checked yet. |  | 1 | 10:34 | Morning | Tuesday | 2017 | 8
6410 | 2017-08-08 10:34 | 2017-10-08 08:00 | 13.8KV 5B FEEDER #1 | Rain | Lightning | 71 | Checked and found 13.8 KV 5B fdr #1 T/R 1x R/F: @2 51 Ctr: 244-245. Patrolled the line and found B/O fuse X.mer fact pak o/p 5B-22. Cause: Lightning. |  | 1 | 10:34 | Morning | Tuesday | 2017 | 8
6411 | 2017-08-08 15:46 | 2017-08-08 15:46 | 13.8KV 6D FEEDER #2 | Cloudy | Lightning | 55 | 6D fdr#2 Load dropped 170A (245-75A). Not checked yet. |  | 1 | 15:46 | Afternoon | Tuesday | 2017 | 8
6412 | 2017-08-08 15:46 | 14/08/2017 08:00 | 13.8KV 6D FEEDER #2 | Cloudy | Lightning | 55 | Checked and found Recloser 6D-298 T/R 1x Ctr: 67-68. Patrolled the line and found broken Pin Insulator o/p 6D-12. Cause: Lightning. |  | 1 | 15:46 | Afternoon | Tuesday | 2017 | 8
6413 | 2017-09-08 07:13 | 2017-09-08 07:13 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | 07:13 It was reported Gading and Security building no power. 07:30 Checked and found 13.8 KV Recl. at Sinabung mini subst. T/O ctr: 234-235. Checked the TX 13.8 KV/4160 Volt normal operation. 07:33 Block and close 13.8 KV Recl. Sinabung mini subst. then release the block. Cause Unidentified. |  | 1 | 7:13 | Morning | Friday | 2017 | 9
6414 | 2017-09-08 09:30 | 2017-09-08 09:30 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Planned Maintenance | 233 | 09:30 Manual open Rec.08-M1-38 Open LBS 08-M1-27. Replaced 112 KVA TX with the same size o/p: 08-M1-12. Replaced pin insulator o/p 08-M3-06 & 08-M3-20. Repaired hot spot o/p: 08-M1-12. 12:10 Block & closed rec.08-M1-38 then release the block. Cause: Maintenance job. |  | 1 | 9:30 | Morning | Friday | 2017 | 9
6415 | 2017-09-08 16:15 | 2017-09-08 16:15 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 16:15 It was reported B/O fuse O/P: 01-5-23 D/S Duri field fdr#3. 16:54 Checked and found B/O fuse @3, Replaced B/O fuse with the same size then energize the TX. Cause: Unidentified(fuse). |  | 1 | 16:15 | Afternoon | Friday | 2017 | 9
6416 | 2017-09-08 19:55 | 2017-09-08 19:55 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Unidentified | 92 | 19:55 Bangko fdr #1 load dropped 148A (199-51A). Bangko fdr #4 load dropped 102A (205-103A). 20:04 Ground fault alarm from Bangko fdr #1. Not checked yet. |  | 1 | 19:55 | Night | Friday | 2017 | 9
6417 | 2017-09-08 19:55 | 2017-12-08 15:55 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Unidentified | 92 | Checked & found Recl. 23-X-08 T/R 2X Ctr:375-377. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 19:55 | Night | Friday | 2017 | 9
6418 | 2017-09-08 20:36 | 2017-09-08 20:36 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain | Unidentified | 0 | Duri Community 13.8 Kv ACB fdr #3 T/R 1X. Not checked yet. |  | 1 | 20:36 | Night | Friday | 2017 | 9
6419 | 2017-09-08 20:36 | 2017-12-08 16:36 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain | Unidentified | 0 | Checked & found Duri Community fdr#3 T/R 1x Ctr:58-59 R/F:51N. Patrolled the line & found Danger trees Near power line 2-SG-1. Cause : Unidentified. |  | 1 | 20:36 | Night | Friday | 2017 | 9
6420 | 2017-10-08 07:35 | 2017-10-08 07:35 | 13.8KV MINAS FEEDER #2 | Fair | Tree | 30 | Minas ACB fdr#2 T/R 1x Ctr:70-71 R/F:51N. Not Patrolled yet. |  | 1 | 7:35 | Morning | Sunday | 2017 | 10
6421 | 2017-10-08 07:35 | 17/08/2017 16:05 | 13.8KV MINAS FEEDER #2 | Fair | Tree | 30 | Checked and found Minas ACB # 13 T/R 1X, R/F 51N @0, Counter : 70 - 71. Patrolled the line found high trees touching the line on pole 7D 58. Couse : High trees. |  | 1 | 7:35 | Morning | Sunday | 2017 | 10
6422 | 2017-10-08 08:01 | 2017-10-08 08:01 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Fair | Animal | 0 | 08:01 Dumai 4160V fdr#5 T/R 1x Ctr:278-279 R/F:50,51@1@2@3. 08:45 Checked & found Dead Monkey at T/P 1-H behind WTP. Isolated Dead Monkey at T/P 1-H. Cause: Animal (Monkey). |  | 1 | 8:01 | Morning | Sunday | 2017 | 10
6423 | 2017-10-08 10:50 | 2017-10-08 10:50 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | 10:50 It was reported no power at Security & Kutilang building. 11:20 Checked & found 13.8Kv Recl Tx Singgalang Mini Subst T/O. Checked Tx condition normal. Opened Recl. 4160Volt at Singgalang Mini Subst. 11:27 Closed 13.8Kv Recl. Tx at Singgalang Mini Subst. 11:30 Closed Recl. 4160Volt at Singgalang Mini Subst. Cause: Unidentified. |  | 1 | 10:50 | Morning | Sunday | 2017 | 10
6424 | 2017-10-08 15:19 | 2017-10-08 15:19 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain and Lightning | Unidentified | 0 | Dumai 4160 V ACB#22 Fdr#4 T/R: 1X. Not checked yet. |  | 1 | 15:19 | Afternoon | Sunday | 2017 | 10
6425 | 2017-10-08 15:19 | 2017-11-08 11:00 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked & found 4160V Dumai fdr#4 T/R 1x Ctr:268-269 R/F 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:19 | Afternoon | Sunday | 2017 | 10
6426 | 2017-11-08 10:10 | 2017-11-08 10:10 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Planned Maintenance | 0 | 10:10-10:45 Opened & cloase Recl. 40BA02 (C.Duri fdr#2). Plat S/D for repaired Hot spot at Adi Karya Building. Cause: Planned Maintenance. |  | 1 | 10:10 | Morning | Wednesday | 2017 | 11
6427 | 2017-11-08 15:47 | 2017-11-08 15:47 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | 3D fdr#4 load dropped 112A (240-128A). 3D GFPC T/R. Not checked yet. |  | 1 | 15:47 | Afternoon | Wednesday | 2017 | 11
6428 | 2017-11-08 15:47 | 2017-12-08 16:15 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | 16:15 Checked & found Recl. 2D-33 T/SO Ctr:45-46. @1@2@3 Broken LA at Recl.2D-33 )Load side). 17:12 Opened Recl. 2D-14. Opened Visual opening Recl. 2D-33. 17:56 Isolated Broken LA at Recl 2D-33. 18:00 Blocked & closed Recl. 2D-14, then release the block. 18:20 Blocked & closed Recl. 2D-14, then release the block. Cause: Lightning. |  | 1 | 15:47 | Afternoon | Wednesday | 2017 | 11
6429 | 2017-11-08 15:54 | 2017-11-08 15:54 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Tree | 26 | 3D 13.8KV OCB fdr#8 T/R 1X. Not checked yet. |  | 1 | 15:54 | Afternoon | Wednesday | 2017 | 11
6430 | 2017-11-08 15:54 | 17/08/2017 15:45 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Tree | 26 | Checked and found 3D OCB Fdr # 8 T/R 1X, Ctr : 302 - 303, R/F : 51 @3. Patrolled the line found the tree touching conductor @3 o/p 2D 28. Couse : High Tree. |  | 1 | 15:54 | Afternoon | Wednesday | 2017 | 11
6431 | 2017-11-08 16:11 | 2017-11-08 16:11 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Tree | 360 | 16:11 4B Fdr#6 T/LO . 18:08 Checked & foun 4B OCB fdr#6 T/LO Ctr:148-152 R/F:51@1@2. 18:15 Patrolled the line & found @2 Broken LA on T/P well 4B-12. 18:20 Blocked & closed 4B OCB fdr#6, but tripped again. 20:00 Continued to patrol the line, but nothing found. 20:30 open LBS #4B-150. 20:35 Blocked & closed 4B OCB fdr#6, but tripped again. 21:00 Open By Pass Recloser #4B-148. 21:09 Blocked & closed 4B OCB fdr#6, OK then released the block. (Patrol the line will be continued tomorrow). |  | 1 | 16:11 | Afternoon | Wednesday | 2017 | 11
6432 | 2017-11-08 16:11 | 2017-12-08 09:00 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Tree | 360 | 09:00 Patrolled the line & found Danger trees at conductor pole 4B-24 & 4B-25. 11:54 Open 4B fdr#6 for closed by pass switch Recl. 4B-148. 11:58 Blocked & closed 4B fdr#6, then release the block. Cause: Trees. |  | 1 | 16:11 | Afternoon | Wednesday | 2017 | 11
6433 | 2017-11-08 16:51 | 2017-11-08 16:51 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Unidentified | 49 | Rangau fdr#2 load dropped 150A (153-3). Not checked yet. |  | 1 | 16:51 | Afternoon | Wednesday | 2017 | 11
6434 | 2017-11-08 16:51 | 17/08/2017 16:10 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Unidentified | 49 | Checked and found Recloser 23 BD 01 T/R 1X, R/F 51N Ctr : 187 - 188. Patrolled the line but found nothing Cause : Unidentified. |  | 1 | 16:51 | Afternoon | Wednesday | 2017 | 11
6435 | 2017-12-08 09:20 | 2017-12-08 09:20 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 13 | 09:20 Opened Recl. 40AW17. Replaced 112.5Kva Tx at well Kulim#21. 11:30 Blocked & closed Recl. 40AW17, then release the block. Cause: Planned Maintenance. |  | 1 | 9:20 | Morning | Friday | 2017 | 12
6436 | 2017-12-08 09:40 | 2017-12-08 09:40 | 13.8KV NELLA FEEDER #1 | Fair | Emergency | 0 | 09:40 Manually Open Nella 13.8KV VCB fdr #1. Due Production Line Leakage (4" broken Gasket near Header Line) at Bangko #129. Cause: Emergency. |  | 1 | 9:40 | Morning | Friday | 2017 | 12
6437 | 2017-12-08 09:40 | 13/08/2017 03:49 | 13.8KV NELLA FEEDER #1 | Fair | Emergency | 0 | 03:349 Closed Nella 13.8KV VCB fdr #1. (After fixing Production Line Leakage). Cause: Emergency. |  | 1 | 9:40 | Morning | Friday | 2017 | 12
6438 | 2017-12-08 09:40 | 2017-12-08 09:40 | 13.8KV NELLA FEEDER #2 | Fair | Emergency | 0 | 09:4:01 Manually Open Nella 13.8KV VCB fdr #2. Due Production Line Leakage (4" broken Gasket near Header Line) at Bangko #129. Cause: Emergency. |  | 1 | 9:40 | Morning | Friday | 2017 | 12
6439 | 2017-12-08 09:40 | 13/08/2017 03:32 | 13.8KV NELLA FEEDER #2 | Fair | Emergency | 0 | 03:32 Closed Nella 13.8KV VCB fdr #2. (After fixing Production Line Leakage). Cause: Emergency. |  | 1 | 9:40 | Morning | Friday | 2017 | 12
6440 | 2017-12-08 18:55 | 2017-12-08 18:55 | 13.8KV KETIGUL FEEDER#2 | Rain | Theft | 247 | 18:55 It was reported Transformer vandalism at Sikeladi #10. 21:00 Checked and found lost 3Fcs, Scondary Cable for 100KVA TX. Cause: Theft. (will be repaired tomorrow due to Bad weather). |  | 1 | 18:55 | Afternoon | Friday | 2017 | 12
6441 | 2017-12-08 19:12 | 2017-12-08 19:12 | 13.8KV KETIGUL FEEDER#2 | Rain | Theft | 25 | 18:55 It was reported Transformer vandalism at Sikeladi #4. 21:00 Checked and found lost 3Fcs, Scondary Cable for 150KVA TX. Cause: Theft. (will be repaired tomorrow due to Bad weather). |  | 1 | 19:12 | Night | Friday | 2017 | 12
6442 | 2017-08-13 01:08 | 2017-08-13 01:08 | 13.8KV MENGGALA FEEDER #1 | Drizzle | Lightning Arrester | 84 | 01:08 Menggala fdr #1 load dropped 115A (175-60). 02:00 It was reported no power to MeSo. GS. 03:25 Checked and found Recloser 19 AO 1 T/LO ctr: 470-474. Patrolled the line and found @1 broken LA o/p - 30 AO 2. Open @1 HLC o/p 30 AO 2 to isolated broken LA. 04:10 Closed Recloser 19 AO 1, OK. Cause: Broken LA. |  | 1 | 1:08 | Night | Sunday | 2017 | 8
6443 | 2017-08-13 17:17 | 2017-08-13 17:17 | NORTH DURI POWER PLANT |  |  | - | 17:17 S/U NDC#2 the on line at 17:43. |  | 1 | 17:17 | Afternoon | Sunday | 2017 | 8
6444 | 2017-08-13 17:17 | 2017-08-14 10:41 | NORTH DURI POWER PLANT |  |  | - | 10:41 NDC CT #2 T/O by Lube Oil problem ( The unit still Running test after CI). 20:49 NCD CT #2 was S/U and On Line to the system at 21:25 for Running test. |  | 1 | 17:17 | Afternoon | Sunday | 2017 | 8
6445 | 2017-08-13 17:18 | 2017-08-13 17:18 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified (Fuse) | 9 | 17:18 It was reported B/O Fuse at So. Balam#207 19:30 Checked and found @2 b/o fuse for 100KVA TX. Performed TTR test and Megger the TX, OK. Replace the b/o fuse above with same size, then energized the TX. OK. Cause: Unidentified fuse. |  | 1 | 17:18 | Afternoon | Sunday | 2017 | 8
6446 | 2017-08-13 17:34 | 2017-08-13 17:34 | 13.8KV MINAS FEEDER #2 | Fair | Planned Maintenance | 0 | 17:34 Manually Open Minas 13.8KV ACB fdr #2. Closed 4160V Breaker of Minas Mini substation. 17:37 Closed Minas 13.8KV ACB fdr #2. Cause: Plan Maintenance. |  | 1 | 17:34 | Afternoon | Sunday | 2017 | 8
6447 | 2017-08-13 18:35 | 2017-08-13 18:35 | 13.8KV KETIGUL FEEDER#3 | Cloudy | Unidentified | 35 | 18:35 Ketigul 13.8KV VCB Fdr#3 T/LO. Ketigul Fdr#1 Load drop 22A (103-81). 20:45 Checked and found Ketigul feeder #3 T/LO ctr:277-280 R/F:51N. Patrolled the line but found nothing. 20:30 Blocked and closed Ketigul fdr #3, OK then released the block. Cause: Unidentified. |  | 1 | 18:35 | Afternoon | Sunday | 2017 | 8
6448 | 2017-08-13 18:35 | 2017-08-13 18:35 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 22 | 18:35 Ketigul Fdr#2 Load drop 45A (167-128). 20:45 Checked and found Ketigul fdr #2 T/R 1X ctrL.... R/F:51N. Not patrolled yet. |  | 1 | 18:35 | Afternoon | Sunday | 2017 | 8
6449 | 2017-08-13 18:35 | 2017-08-17 20:35 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 22 | Patrolled the line & found @3 Broken Dead End Insulator o/p 29AN04. Cause : Lightning. |  | 1 | 18:35 | Afternoon | Sunday | 2017 | 8
6450 | 2017-08-14 09:44 | 2017-08-14 09:44 | 13.8KV NORTH DURI FEEDER #7 | Fair | Planned Maintenance | 5 | 09:44 Manually opened N.Duri OCB fdr #7. Opened By pass Recloser 10-K6-16. 09:52 Manually closed N.Duri OCB fdr #7. Replacing secondary cable on pole 10-K6-23. 10:17 Manually opened N.Duri OCB fdr #7. Closed By pass Recloser 10-K6-23. 10:18 Manually closed N.Duri OCB fdr #7. Cause: Plan Maintenance. |  | 1 | 9:44 | Morning | Monday | 2017 | 8
6451 | 2017-08-14 10:00 | 2017-08-14 10:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 10:00 It was reported b/o fuse on pole 10-J4-14 D/S N.Duri OCB fdr #2. 10:45 Checked and found @1 b/o fuse for 112.5 Kva. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (fuse). |  | 1 | 10:00 | Morning | Monday | 2017 | 8
6452 | 2017-08-14 10:59 | 2017-08-14 10:59 | 13.8KV MENGGALA FEEDER #1 | Fair | Construction Job | 0 | 10:59 Manually opened Menggala OCB fdr #1. Shut down well Menggala North #19, Due to Tie in new well Menggala North #38. 11:45 Blocked and closed Menggala OCB fdr #1 and then released the block. Cause: Construction job. |  | 1 | 10:59 | Morning | Monday | 2017 | 8
6453 | 2017-08-14 13:45 | 2017-08-14 13:45 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified (Fuse) | 6 | 13:45 It was reported b/o fuse at well Balam #27 D/S Balam fdr #4. 15:15 Checked and found @3 b/o fuse for 100 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (fuse). |  | 1 | 13:45 | Afternoon | Monday | 2017 | 8
6454 | 2017-08-15 08:30 | 2017-08-15 08:30 | 13.8KV CENTRAL DURI FEEDER #5 | Drizzle | Guy Wire | 160 | 08:30 C.Duri ACB #22 (feeder#5) T/LO Ctr: 249-253 R/F: 50 @2, 51N. 09:03 Blocked and closed C.Duri ACB fdr #5 but failed Counter: 253-255 R/F: 50 @2,51N. Patrolled the line found @1,2,3 conductor touched the cross arm on pole 03-03-25 due to broken guy wire. 09:05 Opened Recloser: 03-04-16. 09:18 Blocked and closed C.Duri ACB fdr #5 --> Success. Repair broken guy wire. 11:36 Blocked and closed Recloser: 03-04-16 but trip C.Duri ACB fdr #5 T/O (in block position). Counter: 255-256 R/F: R/F: 50 @2,51N. Opened Recloser: 03-04-16. 11:38 Blocked and closed C.Duri ACB fdr #5 --> Success. Patrolled the line found @2,@3 b/o fuse for Tx. Opened FCO to isolate Tx. 11:42 Blocked and closed Recloser: 03-04-16 --> success. Cause: Broken guy wire. |  | 1 | 8:30 | Morning | Tuesday | 2017 | 8
6455 | 2017-08-15 11:26 | 2017-08-15 11:26 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 11:26 It was reported b/o fuse on pole 08-M5-07 D/S Darling fdr #3. Not checked yet. |  | 1 | 11:26 | Morning | Tuesday | 2017 | 8
6456 | 2017-08-15 11:26 | 2017-08-26 09:35 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 09:35 Checked and found @1 b/o fuse for 112.5 Kva TX o/p 05-M5-07 d/s Darling fdr #3. Ferformed TTR Test and Megger the Tx. Ok. Replaced b/o fuse above with same size, then energize TTX. Couse:Unidentiffied (fuse). |  | 1 | 11:26 | Morning | Tuesday | 2017 | 8
6457 | 2017-08-15 13:11 | 2017-08-15 13:11 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 851 | 13:11 Manually opened Sintong OCB fdr #2. Due to repair hot spot on by pass Recloser: 28-AF-17. 17:11 Manually blocked and closed Sintong OCB fdr #2 and then released the block. Cause: Plan Maintenance. | 123 | 1 | 13:11 | Afternoon | Tuesday | 2017 | 8
6458 | 2017-08-15 21:15 | 2017-08-15 21:15 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | Off line NDC#2,then S/D the unit for Maintenance. |  | 1 | 21:15 | Night | Tuesday | 2017 | 8
6459 | 2017-08-15 21:15 | 2017-08-16 11:35 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | 11:35 S/U then On Line at 12:05 after Inspection(CI & Off line Wash). |  | 1 | 21:15 | Night | Tuesday | 2017 | 8
6460 | 2017-08-15 21:39 | 2017-08-15 21:39 | 13.8KV NELLA FEEDER #1 | Cloudy | Unidentified | 70 | Nella fdr#1 load dropped 138A (255-117A) Nella GFPC T/R 1X. Not checked yet. |  | 1 | 21:39 | Night | Tuesday | 2017 | 8
6461 | 2017-08-15 21:39 | 2017-08-16 20:39 | 13.8KV NELLA FEEDER #1 | Cloudy | Unidentified | 70 | Checked & found Recl. 22V01 T/R 1x Ctr:102-103 R/F:51@1@2@3. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 21:39 | Night | Tuesday | 2017 | 8
6462 | 2017-08-16 04:54 | 2017-08-16 04:54 | KOTABATAK JUNCTION SW STA | Fair | Unidentified | 0 | 04:54 KBJ 115KV GCB #20 T/O , Ctr: 90-91 KBJ 115KV GCB #35 T/O , Ctr: 221-222 KBJ 115KV GCB #45 T/O , Ctr: 306-307 KBJ 115KV GCB #55 T/O , Ctr: 314-315 (KBJ 115KV Line Bus #1 was T/O, with R/F 87B @A @B @C) 07:01 Man. Closed KBJ 115KV GCB #20 Man. Closed KBJ 115KV GCB #35 Man. Closed KBJ 115KV GCB #45 Man. Closed KBJ 115KV GCB #55 Cause: Unidentified |  | 1 | 4:54 | Morning | Wednesday | 2017 | 8
6463 | 2017-08-16 10:10 | 2017-08-16 10:10 | 13.8KV ROKAN FEEDER #3 | Fair | Planned Maintenance | 0 | 10:10 Perform Plan Shutdown Rokan OCB fdr#3. (HO COC team Repair 30" Water Line from Rangau and Service OCB #3) 17:11 Finished Repair Water Line and Service OCB #3 Man. Closed Rokan OCB fdr#3. Cause : Planned Maintenance (HO COC) |  | 1 | 10:10 | Morning | Wednesday | 2017 | 8
6464 | 2017-08-16 11:35 | 2017-08-16 11:35 | NORTH DURI POWER PLANT |  |  | - | 11:35 S/U then On Line at 12:05 after Inspection(CI & Off line Wash). |  | 1 | 11:35 | Morning | Wednesday | 2017 | 8
6465 | 2017-08-16 15:22 | 2017-08-16 15:22 | NORTH DURI POWER PLANT | Fair | Under investigation | 906 | 15:22 NDC CT#2 T/O Frequency 59.47 Hz, Load shedding Level 2 3D OCB fdr#2, #3, #5, #6 T/O, then Closed at 15:43. 4D OCB fdr#2, #3, #4, #5, #6 T/O, then Closed at 15:35. 4B OCB fdr#4, #5, #6 T/O, then Closed at 15:36 5B OCB fdr#1, #2, #3, #4, #5 T/O, then Closed at 15:38 8D OCB fdr#1, #3, #10 T/O, then Closed at 15:44 8C OCB fdr#1, T/O, then Closed at 15:45 Suram OCB fdr#1, T/O, then Closed at 15:37 BOB Pusaka GCB #21, #22 T/O, then Closed at 16:40 Cause : GT under investigation. Prod. Loss: GS#1 : 166 Bbls, 64 Wells. GS#2 : 90 Bbls, 33 Wells. GS#3 : 0 Bbls. 0 Wells. GS#4 : 107 Bbls, 42 Wells. GS#5 : 311 Bbls, 152 Wells. GS#6 : 168 Bbls, 91 Wells. ___________________________ Total Prod. Loss : 842 Bbls, 382 Wells. | 123 | 1 | 15:22 | Afternoon | Wednesday | 2017 | 8
6466 | 2017-08-16 15:22 | 2017-08-17 14:15 | NORTH DURI POWER PLANT | Fair | Under investigation | 906 | 14:15 S/U NDC CT-2 then online the unit at 15:05. | 123 | 1 | 15:22 | Afternoon | Wednesday | 2017 | 8
6467 | 2017-08-16 18:41 | 2017-08-16 18:41 | 13.8KV BATANG FEEDER #1 | Fair | Unidentified | 0 | 18:41 Batang OCB fdr#1 T/R 1x. Not Checked yet. |  | 1 | 18:41 | Afternoon | Wednesday | 2017 | 8
6468 | 2017-08-16 18:41 | 2017-08-17 15:50 | 13.8KV BATANG FEEDER #1 | Fair | Unidentified | 0 | Checked and found Batang OCB Fdr# 1 T/R 1X, R/F 51 @1 , Counter : 138 - 139. Patroled the line but Found nothing. |  | 1 | 18:41 | Afternoon | Wednesday | 2017 | 8
6469 | 2017-08-17 05:15 | 2017-08-17 05:15 | 13.8KV MINAS FEEDER #6 | Cloudy | Lightning | 56 | Minas fdr #6 load dropped 152A (195-43A). Not checked yet. |  | 1 | 5:15 | Morning | Thursday | 2017 | 8
6470 | 2017-08-17 05:15 | 2017-08-20 09:15 | 13.8KV MINAS FEEDER #6 | Cloudy | Lightning | 56 | Checked and found Recl. 7E-67A T/R 1X Ctr:61-62. Patrolled the line but found nothing Cause : Lightning. |  | 1 | 5:15 | Morning | Thursday | 2017 | 8
6471 | 2017-08-17 13:41 | 2017-08-17 13:41 | 13.8KV MINAS FEEDER #4 | Rain | Lightning | 126 | MINAS SW GR 13.8KV ACB #1 (MNS FDR #4) T/R 1X Not Checked Yet Weather: Rain |  | 1 | 13:41 | Afternoon | Thursday | 2017 | 8
6472 | 2017-08-17 13:41 | 2017-08-22 07:56 | 13.8KV MINAS FEEDER #4 | Rain | Lightning | 126 | Checked and found MNS ACB # 1 T/R 1X R/F 51N @0 Counter : 76 - 77 Patrolled the line found nothing. Cause: Lightning. |  | 1 | 13:41 | Afternoon | Thursday | 2017 | 8
6473 | 2017-08-17 14:15 | 2017-08-17 14:15 | NORTH DURI POWER PLANT |  |  | - | S/U NDC CT #2 then online the unit at 15:05 after maintenance. |  | 1 | 14:15 | Afternoon | Thursday | 2017 | 8
6474 | 2017-08-17 21:20 | 2017-08-17 21:20 | 13.8KV MENGGALA FEEDER #1 | Heavy Rain | Tree | 255 | 21:20 Menggala fdr #1 load dropped 90A (149-59A). Checked & found, Recl. 19-AN-04 T/LO ctr: 336-339. Patrolled the line & found fallen tree touching power line between poles 19-AE-11 to 19-AE-12. Dismantled tree from power line. 00:15 Blocked and closed Recloser:19-AN-04 and then released the block. Cause: Tree. |  | 1 | 21:20 | Night | Thursday | 2017 | 8
6475 | 2017-08-18 08:56 | 2017-08-18 08:56 | 13.8KV RANGAU FEEDER #2 | Cloudy | Animal | 190 | 08:56 Rangau Fdr #2 Load drop 179 Amp ( 188 - 9 A) 10:40 Checked and Found Recloser 23 BD 1 T/Lo Inform from Line patrol about Monkey Hang Up O/P 22 AC 2 toward Loc Pelita # 3 11:10 Block and Closed Recloser 23 BD 1 Succes than release Block Cause : Animal ( Monkey ) |  | 1 | 8:56 | Morning | Friday | 2017 | 8
6476 | 2017-08-18 14:15 | 2017-08-18 14:15 | MINAS POWER PLANT | Fair |  | - | Minas GT # 10 Shut Down for standby due to NDC #2 had been Online |  | 1 | 14:15 | Afternoon | Friday | 2017 | 8
6477 | 2017-08-18 14:33 | 2017-08-18 14:33 | MINAS POWER PLANT | Fair |  | - | Minas GT # 5 Shut Down for standby due to NDC #2 had been Online |  | 1 | 14:33 | Afternoon | Friday | 2017 | 8
6478 | 2017-08-18 14:40 | 2017-08-18 14:40 | MINAS POWER PLANT | Fair |  | - | Minas GT # 2 Shut Down for standby due to NDC #2 had been Online |  | 1 | 14:40 | Afternoon | Friday | 2017 | 8
6479 | 2017-08-18 14:45 | 2017-08-18 14:45 | MINAS POWER PLANT | Fair |  | - | Minas GT # 3 Shut Down for standby due to NDC #2 had been Online |  | 1 | 14:45 | Afternoon | Friday | 2017 | 8
6480 | 2017-08-18 17:59 | 2017-08-18 17:59 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Broken Fuse Cut Out | 0 | 17:59 It was reported unbalance voltage on Tx #7 at CGS #3. 23:11 Checked and found @3 broken Fuse Cut Out for 2500 Kva Tx #6 at CGS #3. August 19, 2017. 01:34 Manually opened C.Duri ACB #33 (feeder #7) for replacing broken Fuse Cut Out. 01:35 Rack out C.Duri ACB #33 (feeder #7) and install personal ground at job side. 02:02 Replaced @3 broken Fuse Cut Out and then dismantled personal ground. 02:07 Rack in C.Duri ACB #33 ( feeder #7). 02:08 Manually blocked and closed C.Duri ACB #33 (feeder #7) and then released the block. 02:14 Energized 2500 Kva Tx #6 at CGS #3. Cause: Broken Fuse Cut Out. |  | 1 | 17:59 | Afternoon | Friday | 2017 | 8
6481 | 2017-08-18 20:30 | 2017-08-18 20:30 | 13.8KV KETIGUL FEEDER#3 | Fair | Pin Insulator | 6 | Ketigul VCB fdr #3 T/R 1x. Ketigul fdr #2 load dropped 48A (170-122A). Ketigul fdr #1 load dropped 24A (103-79A). Not checked yet. |  | 1 | 20:30 | Night | Friday | 2017 | 8
6482 | 2017-08-18 20:30 | 2017-08-19 15:58 | 13.8KV KETIGUL FEEDER#3 | Fair | Pin Insulator | 6 | Checked and found Katigul VCB Fdr #3, T/R 3X R/F 51 Ctr: 180 - 183. Patrolled the Line found broken P/Ins O/terminal pole Gulamo #03 Cause : Lightning. |  | 1 | 20:30 | Night | Friday | 2017 | 8
6483 | 2017-08-19 09:30 | 2017-08-19 09:30 | 13.8KV MENGGALA FEEDER #2 | Fair | Construction Job | 22 | 09:30 Manually opened LBS 27-AL-03 D/S Menggala fdr #2. Due to opened HLC on terminal pole Location UBI #34. 09:45 Manually closed LBS 27-AL-03. Cause: Construction job. |  | 1 | 9:30 | Morning | Saturday | 2017 | 8
6484 | 2017-08-19 11:39 | 2017-08-19 11:39 | 13.8KV SINTONG FEEDER #1 | Fair | Construction Job | 0 | 11:39 Manually opened Sintong OCB fdr #1. For energizing reactive well Kerang #08 by closed Hot Line Clamp. 12:07 Manually closed Sintong OCB fdr #1. Cause: Constrution job. |  | 1 | 11:39 | Morning | Saturday | 2017 | 8
6485 | 2017-08-19 18:25 | 2017-08-19 18:25 | 13.8KV KETIGUL FEEDER#3 | Fair | Powerline - Hot Line Clamp | 258 | 18:25 Ketigul VCB fdr #3 T/SO. Ketigul fdr #1 load dropped 33A (102-79A). Ketigul fdr #2 load dropped 36A (170-136A). 21:30 Checked & found Ketigul VCB fdr#3 T/LO, Ctr: 183-186, R/F: 51N 21:57 Patrolled the Line, found Broken @1 @2 Conductor o/p 31-AR-02 towards Gulamo #3 & #7. (Will be repaired tomorrow). |  | 1 | 18:25 | Afternoon | Saturday | 2017 | 8
6486 | 2017-08-19 18:25 | 2017-08-20 09:30 | 13.8KV KETIGUL FEEDER#3 | Fair | Powerline - Hot Line Clamp | 258 | 09:30 Opened LBS 32-AN-01 Repaired @1, @2 broken Conductor o/p 31-AR-02. 13:59 Normalized Ketigul fdr #3 Cause : Hot Line Clamp. |  | 1 | 18:25 | Afternoon | Saturday | 2017 | 8
6487 | 2017-08-20 06:14 | 2017-08-20 06:14 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | Sintong fdr #1 load dropped 13A (77-64A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 6:14 | Morning | Sunday | 2017 | 8
6488 | 2017-08-20 06:14 | 2017-08-22 08:00 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | Checked and found Recloser 26-AE-22 T/R 1x Ctr: 357-358 R/F: @1,@2,@3 50. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:14 | Morning | Sunday | 2017 | 8
6489 | 2017-08-20 07:14 | 2017-08-20 07:14 | 13.8KV NORTH DURI FEEDER #5 | Fair | Lightning | 0 | N.Duri VCB Fdr#5 T/R 1X. Not Checked yet. |  | 1 | 7:14 | Morning | Sunday | 2017 | 8
6490 | 2017-08-20 07:14 | 2017-08-24 17:00 | 13.8KV NORTH DURI FEEDER #5 | Fair | Lightning | 0 | 17:00 Checked and found N. Duri 13.8KV VCB fdr #5 T/R 1X ctr:112-113 R/F: 51@3. Patrolled the line and found @3 broken LA o/p 12-E1-01. Cause: Lightning. |  | 1 | 7:14 | Morning | Sunday | 2017 | 8
6491 | 2017-08-20 11:20 | 2017-08-20 11:20 | 13.8KV MENGGALA FEEDER #2 | Fair | Construction Job | 0 | 11:20 Manually opened LBS 27-AL-03 D/S Manggala Fdr#2. To tie in new well UBI #37. 11:37 Manually closed LBS 27-AL-03. Cause: Construction job. |  | 1 | 11:20 | Morning | Sunday | 2017 | 8
6492 | 2017-08-20 16:30 | 2017-08-20 16:30 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | It was reported Broken fuse link o/p 06-S7-17 D/S Duri field fdr #4. Not checked yet. |  | 1 | 16:30 | Afternoon | Sunday | 2017 | 8
6493 | 2017-08-20 16:30 | 2017-08-26 16:30 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | Checked and found @3 b/o fuse for 112.5KVA TX o/p 06-S7-17 d/s Duri field fdr #4. Performed TTR test and Megger the TX and found Normal. Replaced b/o fuse above with same size, then energized the TX. OK. Cause: Unidentified fuse. |  | 1 | 16:30 | Afternoon | Sunday | 2017 | 8
6494 | 2017-08-20 17:34 | 2017-08-20 17:34 | CENTRAL DURI POWER PLANT |  |  | - | 17:34 Off line CGT#2, then S/D the unit for S/B. 17:50 Closed Tie Breaker ACB#39. |  | 1 | 17:34 | Afternoon | Sunday | 2017 | 8
6495 | 2017-08-21 07:51 | 2017-08-21 07:51 | 13.8KV RANGAU FEEDER #2 | Fair | Dead End Insulator | 0 | Ranggau VCB Fdr#2 load drop 177 A ( 192 - 15 A ) Not checked yet. |  | 1 | 7:51 | Morning | Monday | 2017 | 8
6496 | 2017-08-21 07:51 | 2017-08-23 07:51 | 13.8KV RANGAU FEEDER #2 | Fair | Dead End Insulator | 0 | Checked & found, Recloser 23BD-01 T/R 3x ctr: 292-295. Patrolled the line & found, @1 flash over Dead-end Insulator on Pole 22BB-01. Cause: Dead-end Insulator. |  | 1 | 7:51 | Morning | Monday | 2017 | 8
6497 | 2017-08-21 09:28 | 2017-08-21 09:28 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | C.Duri ACB #22 Fdr #5 T/R 1X R/F 50 Ctr: 256 - 257. Not patrolled yet. |  | 1 | 9:28 | Morning | Monday | 2017 | 8
6498 | 2017-08-21 09:28 | 2017-08-24 17:00 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | 17:00 Checked and found C.Duri 13.8KV ACB fdr #5 T/R 1X ctr:256-257 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:28 | Morning | Monday | 2017 | 8
6499 | 2017-08-22 09:56 | 2017-08-22 09:56 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 88 | 09:56 It was reported no power o/p 09. L7. 06. 10:30 Checked and found Recl. 09. L7. 01 T/SO ctr:239-240. Blocked and closed the Recloser, Ok then released the block. Cause: Unidentified. |  | 1 | 9:56 | Morning | Tuesday | 2017 | 8
6500 | 2017-08-22 10:00 | 2017-08-22 10:00 | 13.8KV NORTH DURI FEEDER #7 | Fair | Powerline - Conductor | 171 | 10:00 It was reported no power o/p 10. L1. 24 and o/p 10. L3. 03. 10:30 Checke and found @1 broken Conductor o/p 10. L1. 22. Manually open Recloser 10. L1. 17 to repaired broken Conductor. 18:30 Closed Visual opening Recloser 10 L1 17. Closed Recloser 10 L1 17, OK. Cause: Conductor (broken). |  | 1 | 10:00 | Morning | Tuesday | 2017 | 8
6501 | 2017-08-22 10:30 | 2017-08-22 10:30 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 882 | 10:30 Manually oped 13.8KV So. Balam fdr #1. (Replaced Recl.7 Z 01 and install LBS 16 Z 57). 16:53 Close 13.8KV So. Balam fdr #1. Cause: Plan Maintenance. | 12345 | 1 | 10:30 | Morning | Tuesday | 2017 | 8
6502 | 2017-08-22 10:53 | 2017-08-22 10:53 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 82 | 10:53 Manually open Pungut 13.8KV OCB fdr #2. (Replaced TX at well Panasa #01) 13:39 Closed Pungut 13.8KV OCB fdr #2. Cause: Plan Maintenance. |  | 1 | 10:53 | Morning | Tuesday | 2017 | 8
6503 | 2017-08-22 13:50 | 2017-08-22 13:50 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Fair | Unidentified | 18 | Libo 13.8KV MSU fdr #1 T/R 1X. Not checked yet. |  | 1 | 13:50 | Afternoon | Tuesday | 2017 | 8
6504 | 2017-08-22 13:50 | 2017-08-24 13:50 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Fair | Unidentified | 18 | Checked & found, MSU #2 VCB fdr #1 (Libo fdr #1) T/R 1x ctr: 272-273 R/F: None. Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 13:50 | Afternoon | Tuesday | 2017 | 8
6505 | 2017-08-23 13:44 | 2017-08-23 13:44 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Tree | 992 | 13:44 C.Duri 13.8 KV ACB fdr #1 load dropped 49A ( 98-49A ). 14:41 Checked & found Recl. 41-AW-62 T/LO ctr: 253 - 258. Patrolled the line under Recl. 41-AW-17, & 39-AV-36. found Fallen Tree touching @3 Conductor at Near Well Kulin #01 21:35 Blocked & closed Recl. 41-AW-62, 41-AW-17, & 39-AV-36, after Isolated the Fallen Trees. Cause: Tree. | 11111 | 1 | 13:44 | Afternoon | Wednesday | 2017 | 8
6506 | 2017-08-23 14:03 | 2017-08-23 14:03 | 115KV KOTABATAK JUNCTION - LIBO LINE | Fair | Planned Maintenance | 460 | 14:03 Switching to De Energized 115KV KBJ-Lbo GCB #53 and GCB #55. (Re Tied in power line to Libo Substation). 18:36 Re Energized back the 115KV KBJ-Libo GCB #53 and GCB #55. 14:03 Man Opened MSU Libo fdr#1 ----> Closed at 18:35 14:04 Man Opened MSU Libo fdr#2 ----> Closed at 18:34 14:06 Man Opened 115 KV Libo C/S ----> Closed at 18:29 Cause: Plan Maintenance. |  | 1 | 14:03 | Afternoon | Wednesday | 2017 | 8
6507 | 2017-08-23 14:45 | 2017-08-23 14:45 | MINAS POWER PLANT | Fair | Under investigation | 0 | 14:45 MGT #8 T/O by alarm Generator Diff.Tripped. 17:50 MGT #8 S/U and online the system at :18:03. |  | 1 | 14:45 | Afternoon | Wednesday | 2017 | 8
6508 | 2017-08-23 16:11 | 2017-08-23 16:11 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 82 | 16:11 It was reported un balance voltage at well Bangko #48. Checked & found 150 Kva Tx Unbalance. Cause: Tx Failure ( Will be replaced Tomorrow ). |  | 1 | 16:11 | Afternoon | Wednesday | 2017 | 8
6509 | 2017-08-23 16:11 | 2017-08-25 16:00 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 82 | 16:00 Replaced and anergized.150KVA TX at well Bangko #48. Cause: Tx Failure. |  | 1 | 16:11 | Afternoon | Wednesday | 2017 | 8
6510 | 2017-08-23 18:16 | 2017-08-23 18:16 | 13.8KV RANGAU FEEDER #2 | Fair | Tree | 0 | 18:16 Rangau fdr #2 load dropped 173A (188-15A). Not checked yet. |  | 1 | 18:16 | Afternoon | Wednesday | 2017 | 8
6511 | 2017-08-23 18:16 | 2017-08-24 18:16 | 13.8KV RANGAU FEEDER #2 | Fair | Tree | 0 | Checked & found, Recl. 23BD-01 T/R 3x ctr: 295-298. Patrolled the line & found, High tree at power line near well Jorang #20. Cause: Tree. |  | 1 | 18:16 | Afternoon | Wednesday | 2017 | 8
6512 | 2017-08-24 02:36 | 2017-08-24 02:36 | 13.8KV KETIGUL FEEDER#3 | Rain | Lightning | 6 | 02:36 Ketigul OCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 2:36 | Night | Thursday | 2017 | 8
6513 | 2017-08-24 02:36 | 2017-08-26 19:52 | 13.8KV KETIGUL FEEDER#3 | Rain | Lightning | 6 | Checked and found Katigul VCB Fdr # 3 T/R 1X R/F 51 Ctr:186 - 187. Patrolled the Line found Broken L/A @ 1,2 and Broke P/Ins @2 O/P TP Kelok #01. Caused :Lightning. |  | 1 | 2:36 | Night | Thursday | 2017 | 8
6514 | 2017-08-24 07:47 | 2017-08-24 07:47 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 0 | 07:47 Bangko fdr #4 load dropped 65A (211-146A). Ground fault alarm from Bangko fdr #4. 16:00 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:47 | Morning | Thursday | 2017 | 8
6515 | 2017-08-24 09:03 | 2017-08-24 09:03 | MINAS POWER PLANT |  |  | - | 09:03 S/U MGT #10 and online the system at 09:37. |  | 1 | 9:03 | Morning | Thursday | 2017 | 8
6516 | 2017-08-24 10:00 | 2017-08-24 10:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 0 | 10:00 It was reported b/o fuse at well Kulim #67. 17:45 Checked and found @3 b/o fuse for 75KVA TX. TTR test and Megger the TX and found TX failure. Cause: TX failure. (the TX will be replaced soon). |  | 1 | 10:00 | Morning | Thursday | 2017 | 8
6517 | 2017-08-24 10:00 | 2017-11-09 14:18 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 0 | Replaced the Failure 75KVATX with 112.5KVA at Well Kulin #67. Cause: Failure Transformer |  | 1 | 10:00 | Morning | Thursday | 2017 | 8
6518 | 2017-08-24 10:01 | 2017-08-24 10:01 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 10:01 It was reported b/o fuse at well Kulim #01. 17:45 Checked and found @3 b/o fuse for 45KVA TX. TTR test and Megger the TX and found good condition. Replaced b/o fuse above with same size, then energized the TX. OK. Cause: Unidentified fuse. |  | 1 | 10:01 | Morning | Thursday | 2017 | 8
6519 | 2017-08-24 10:44 | 2017-08-24 10:44 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 233 | 10:44 Manually open 13.8KV OCB Pematang fdr #2. Replaced TX at well Pematang #38 and #45. 12:57 Closed 13.8 KV OCB Pematang #2 . Cause: Plan Maintenance. |  | 1 | 10:44 | Morning | Thursday | 2017 | 8
6520 | 2017-08-24 10:50 | 2017-08-24 10:50 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy | Unidentified | 39 | 10:50 SO.Bekasap 13.8KV OCB fdr #1 T/R 1x. 10:54 SO.Bekasap 13.8KV OCB fdr #1 T/SO . 11:30 Checked & found SO.Bekasap OCB fdr #1 T/SO ctr:396-397 R/F: 51@3 and 51G. 11:56 Blocked & closed SO.Bekasap OCB fdr #1, Ok then release the Block. Not Patrolled yet. |  | 1 | 10:50 | Morning | Thursday | 2017 | 8
6521 | 2017-08-24 10:50 | 2017-08-27 22:21 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy | Unidentified | 39 | Checked and found SoBek OCB Fdr #1 T/R 1X R/F 51N @3 Ctr: 296 - 297. Patrolled the line found nothing. Cause : unidentified. |  | 1 | 10:50 | Morning | Thursday | 2017 | 8
6522 | 2017-08-24 13:05 | 2017-08-24 13:05 | MINAS POWER PLANT |  |  | - | 13:05 Off line and then S/D MGT #8 for replaced 88 BQ. |  | 1 | 13:05 | Afternoon | Thursday | 2017 | 8
6523 | 2017-08-24 18:18 | 2017-08-24 18:18 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 0 | 18:18 Bangko GFPC T/R 1X. Ground fault alarm from Bangko fdr #4. Bangko fdr #4 load dropped 90A (200-110A). Not checked yet. |  | 1 | 18:18 | Afternoon | Thursday | 2017 | 8
6524 | 2017-08-24 18:18 | 2017-08-26 21:47 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 0 | Checked and found Recl 25 Z 07 T/R 2X Ctr : 67 - 69 R/F 51N. Patrolled the line found Broken p/ins @2 at Terminal pole # Benar #20. Caused : Animal. |  | 1 | 18:18 | Afternoon | Thursday | 2017 | 8
6525 | 2017-08-24 21:23 | 2017-08-24 21:23 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Lightning | 0 | Duri comy 13.8KV ACB#30 fdr#2 T/R 1X. Not checked yet. |  | 1 | 21:23 | Night | Thursday | 2017 | 8
6526 | 2017-08-24 21:23 | 2017-08-26 20:34 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Lightning | 0 | Checked and Found DCSG ACB #30 T/R 1X R/F 51N Ctr:82 - 83. Patrolled the line found Broken p/ins @1 o/p SL 1-05. Caused : Lightning. |  | 1 | 21:23 | Night | Thursday | 2017 | 8
6527 | 2017-08-25 01:04 | 2017-08-25 01:04 | CENTRAL DURI POWER PLANT |  |  | - | 01:04 CGT #3 Off Line & S/D for S/B. |  | 1 | 1:04 | Night | Friday | 2017 | 8
6528 | 2017-08-25 10:10 | 2017-08-25 10:10 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 178 | 10:10 Manually open 13.8KV Bekasap OCB fdr #2. Replaced TX at well Bekasap #74. 11:13 Closed 13.8KV Bekasap OCB fdr #2. Cause: Plan Maintenance. |  | 1 | 10:10 | Morning | Friday | 2017 | 8
6529 | 2017-08-25 12:45 | 2017-08-25 12:45 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | 12:45 Ground fault alarm from Menggala fdr #1. Menggala fdr #1 load dropped 49A (192-143A). Not checked yet. |  | 1 | 12:45 | Afternoon | Friday | 2017 | 8
6530 | 2017-08-25 12:45 | 2017-08-28 12:45 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 19-AO-01 T/R 3x ctr: 474-477. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 12:45 | Afternoon | Friday | 2017 | 8
6531 | 2017-08-25 13:59 | 2017-08-25 13:59 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Pin Insulator | 0 | 13:59 E.Rumbai 4160V VCB Fdr#2 T/R 1X. Not checked yet. |  | 1 | 13:59 | Afternoon | Friday | 2017 | 8
6532 | 2017-08-25 13:59 | 2017-08-31 13:59 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Pin Insulator | 0 | East Rumbai Recl. fdr #2 T/R 1x ctr: 531-532 R/F: 50. Patrolled the line & found, @1 broken Pin Support Insulator on Pole 3 RG 18. Cause: Pin Insulator. |  | 1 | 13:59 | Afternoon | Friday | 2017 | 8
6533 | 2017-08-25 15:03 | 2017-08-25 15:03 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 374 | 15:03 Manually open 13.8KV Bangko OCB fdr #4. Replaced broken Pin insulator at well Benar #20. 16:49 Closed 13.8KV Bangko OCB fdr #4. Cause: Plant Maintenance. |  | 1 | 15:03 | Afternoon | Friday | 2017 | 8
6534 | 2017-08-25 15:20 | 2017-08-25 15:20 | MINAS POWER PLANT |  |  | - | 15:20 Minas GT #3 S/U and On Line to the system at 15:40. (MGT #1 will be S/D for minor repair). |  | 1 | 15:20 | Afternoon | Friday | 2017 | 8
6535 | 2017-08-25 16:27 | 2017-08-25 16:27 | MINAS POWER PLANT |  |  | - | 16:27 Off line and then S/D MGT #1 for repair Brider line pipe leak. |  | 1 | 16:27 | Afternoon | Friday | 2017 | 8
6536 | 2017-08-26 09:02 | 2017-08-26 09:02 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 207 | 09:12-12:05 Switching De-Energize Minas 13.8KV fdr #6. Manual open & rack out Minas fdr #6. Manual close Minas fdr #6. Replaced Recl. 6E-26A. Repair Hot spot @2 , Recl. 7E-68A. Replaced HLC @2 o/p 6E-68. Service ACB #68. Cause: Planned Maintenance. |  | 1 | 9:02 | Morning | Saturday | 2017 | 8
6537 | 2017-08-26 14:11 | 2017-08-26 14:11 | 115KV SINTONG - BANGKO LINE | Fair | Tree | 543 | 14:11 Alarm 115KV Breaker T/R . Suspected one of Bangko 115KV OCB #24, Nella 115KV GCB #27 or GCB #26 T/R. SO.Balam fdr #1 load dropped 94A (97-13A) SO.Balam fdr #2 load dropped 97A (97-0A) SO.Balam fdr #3 load dropped 68A (68-0A) SO.Balam fdr #4 load dropped 182A (183-1A) Nella fdr #1 load dropped 261A (263-2A) Nella fdr #2 load dropped 90A (90-0A) Bangko fdr #1 load dropped 190A (212-22A) Bangko fdr #2 load dropped 260A (260-11A) Bangko fdr #3 load dropped 209A (225-16A) Bangko fdr #4 load dropped 131A (207-76A) Pinang fdr #1 load dropped 94A (94-0A) Menggala fdr #1 load dropped 12A (190-178A) Sintong fdr #1 load dropped 20A (80-60A) Sintong fdr #2 load dropped 38A (148-110A) 15:24 Checked Nella 115KV GCB #26 ===>Normal ctr:126. (115KV Line Nella - Balam). 15:24 Checked Nella 115KV GCB #27 ===>Normal ctr:184 (115KV Line Nella - Pinang). 15:30 Checked Nella 115KV OCB #24 ===>Normal ctr:.... (115KV Line Bangko - Nella). 15:30 It was reported a sparks between Pole BKO #28 to BKO #29. Checked & found, @C high trees between poles above. Also found, Sintong OCB #22 T/R 1x ctr: 660-661 R/F: 67N Time. Cause: Tree. Production Loss : Bangko GS 828 Bbls, 206 Wells Balam GS 18 Bbls, 6 Wells | 1111 | 1 | 14:11 | Afternoon | Saturday | 2017 | 8
6538 | 2017-08-26 15:58 | 2017-08-26 15:58 | 13.8KV 6D FEEDER #2 | Fair | Emergency | 0 | 15:18 Manually open LBS-6D-66 to lifting Truck at Minas #1. Seven wells (6D-34E, 35, 45, 46, 54, 56 & 56N) down during the JOB. 20:00 Closed LBS-6D-66. Cause: Emergency. |  | 1 | 15:58 | Afternoon | Saturday | 2017 | 8
6539 | 2017-08-27 00:31 | 2017-08-27 00:31 | 13.8KV 5B FEEDER #1 | Rain | Unidentified | 117 | 00:31 5B OCB fdr#1 T/R 1x 5B fdr#2 Load dropped 149A(160-11A) 5B fdr#3 Load dsropped 38A(49-12A) 5B fdr#6 Load dropped 128A(194-66A) 01:50 5B OCB fdr#1 T/R 1x Not checked Yet. |  | 1 | 0:31 | Night | Sunday | 2017 | 8
6540 | 2017-08-27 00:31 | 2017-04-09 08:00 | 13.8KV 5B FEEDER #1 | Rain | Unidentified | 117 | Checked and found 13.8 KV OCB #1 T/LO Ctr:247-249. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 0:31 | Night | Sunday | 2017 | 8
6541 | 2017-08-27 09:00 | 2017-08-27 09:00 | 13.8KV NORTH DURI FEEDER #7 | Fair | Powerline - Conductor | 12 | 09:00 It was reported broken Conductor between o/p- 10-K4-25 and 10-K4-26. 10:07 Checked and found @1 broken Conductor between o/p- 10-K4-25 and 10-K4-26. 10:53 Manually open N. Duri fdr #7, and close at :10:55. 10:55 Open By Pass Recloser # 10-K2-18. Repairing Broken Conductor. 12:52 Manually open N. Duri fdr #7, and close at :12:56. 12:53 Closed By Pass Recloser # 10-K2-18. Cause: Conductor. |  | 1 | 9:00 | Morning | Sunday | 2017 | 8
6542 | 2017-08-27 10:52 | 2017-08-27 10:52 | 13.8KV BANGKO GFPC | Fair | Animal | 0 | Bangko GFPC T/R 1X. Ground fault alarm from Bangko fdr #4. No load dropped. No checked yet. |  | 1 | 10:52 | Morning | Sunday | 2017 | 8
6543 | 2017-08-27 10:52 | 2017-08-29 13:00 | 13.8KV BANGKO GFPC | Fair | Animal | 0 | Checked & found Bangko GFPC T/R 4 X Ctr:138–142 R/F : IOC5. Patrolled the line & found Dead Chicken at Tx bushing well Bangko#152. Cause: Animal (Chicken). |  | 1 | 10:52 | Morning | Sunday | 2017 | 8
6544 | 2017-08-27 12:07 | 2017-08-27 12:07 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | 12:07 Duri field 13.8KV ACB fdr #4 T/O ctr: 504-504 R/F: 51 @1, 2, 3 (On block due to Rig BN #08 at well 7S- 23A). 12:25 Blocked and closed Duri Field 13.8KV ACB fdr #4, OK. 17:00 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 12:07 | Afternoon | Sunday | 2017 | 8
6545 | 2017-08-27 12:08 | 2017-08-27 12:08 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 0 | 12:08 Ground fault alarm from So. Balam fdr #4. So. Balam fdr #4 load dropped 172A (173-1A). So. Balam fdr #1 load dropped 12A (95-83A) ---->EOR. So. Balam fdr #2 load dropped 101A (101-0A) ---->EOR. So. Balam fdr #3 load dropped 36A (36-0A). Not checked yet. |  | 1 | 12:08 | Afternoon | Sunday | 2017 | 8
6546 | 2017-08-27 12:08 | 2017-08-29 14:08 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 0 | Checked So Balam Fdr & all Recl Normal Operation (Not operated). |  | 1 | 12:08 | Afternoon | Sunday | 2017 | 8
6547 | 2017-08-27 12:20 | 2017-08-27 12:20 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified (Fuse) | 6 | 12:20 It was reported b/o fuse at well Balam #116. Checked and found @1, @2 b/o fuses for 100KVA TX. Performed TTR test and Megger the TX. OK. Replaced b/o fuse above with same size, then energized the TX. OK. Cause: Unidentified fuse. |  | 1 | 12:20 | Afternoon | Sunday | 2017 | 8
6548 | 2017-08-27 14:00 | 2017-08-27 14:00 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 135 | 14:00 It was reported b/o fuse at well Bangko #75. 15:00 Checked and found @1, @2 & @3 b/o fuses for 225KVA TX. Performed TTR test and Megger the TX. OK. Replaced b/o fuse above with same size, then energized the TX. OK. Cause: Animal (Chicken and 2 Lizards). |  | 1 | 14:00 | Afternoon | Sunday | 2017 | 8
6549 | 2017-08-27 14:01 | 2017-08-27 14:01 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 14 | 14:01 It was reported b/o fuse at well Bangko #152. 16:30 Checked and found @1, @2 b/o fuses for 150KVA TX. Performed TTR test and Megger the TX and found Low Mega reading TX. Cause: Low Mega reading TX. (The TX will be replace soon). |  | 1 | 14:01 | Afternoon | Sunday | 2017 | 8
6550 | 2017-08-27 14:01 | 2017-08-28 11:00 | 13.8KV BANGKO FEEDER #4 | Fair | Transformer Failure | 14 | Replaced 150Kva Tx with 100Kva Tx at well Bangko#152. Cause: Tx Failure. |  | 1 | 14:01 | Afternoon | Sunday | 2017 | 8
6551 | 2017-08-27 14:02 | 2017-08-27 14:02 | 13.8KV KETIGUL FEEDER#2 | Fair | Switchboard Problem | 0 | 14:02 It was reported b/o fuse at well Sikaladi # 20. 16:30 Checked and found @3 b/o fuse for 100Kva TX. Performed TTR test and Megger the TX. OK. Replaced b/o fuse above with same sized, then energized the TX. Cause: Other (switch Board). |  | 1 | 14:02 | Afternoon | Sunday | 2017 | 8
6552 | 2017-08-28 23:59 | 2017-08-28 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power System Normal Condition. |  | 1 | 23:59 | Night | Monday | 2017 | 8
6553 | 2017-08-29 05:57 | 2017-08-29 05:57 | 13.8KV 8C FEEDER #6 | Fair | Unidentified | 57 | 8C OCB Fdr #6 T/R 2 X 8C OCB Fdr #5 Load drop 197 A ( 199 - 2A ) 8C OCB Fdr #4 Load drop 144 A ( 284 - 140 A ) GFPC 8C FDR#6 Alarm. |  | 1 | 5:57 | Morning | Tuesday | 2017 | 8
6554 | 2017-08-29 05:57 | 2017-08-30 05:57 | 13.8KV 8C FEEDER #6 | Fair | Unidentified | 57 | Checked & found, 8C VCB fdr #6 T/R 2x ctr: 577-579 R/F: 51 @2, @3. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 5:57 | Morning | Tuesday | 2017 | 8
6555 | 2017-08-29 13:57 | 2017-08-29 13:57 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Pin Insulator | 0 | East Rumbai fdr#2 T/R 1x. Not checked yet. |  | 1 | 13:57 | Afternoon | Tuesday | 2017 | 8
6556 | 2017-08-29 13:57 | 2017-08-31 13:57 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Pin Insulator | 0 | East Rumbai Recl. fdr #2 T/R 1x ctr: 531-532 R/F: 50. Patrolled the line & found, @1 broken Pin Support Insulator on Pole 3 RG 18. Cause: Pin Insulator. |  | 1 | 13:57 | Afternoon | Tuesday | 2017 | 8
6557 | 2017-08-29 14:30 | 2017-08-29 14:30 | MINAS POWER PLANT |  |  | - | 14:30 S/U MGT#8 the on line then unit at 15:22. |  | 1 | 14:30 | Afternoon | Tuesday | 2017 | 8
6558 | 2017-08-29 17:42 | 2017-08-29 17:42 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | N.Duri 13.8KV VCB fdr#9 T/R 1X. Not checked yet. |  | 1 | 17:42 | Afternoon | Tuesday | 2017 | 8
6559 | 2017-08-29 17:42 | 2017-04-09 08:00 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | Checked and found 13.8 KV VCB #9 T/R 1x Ctr:45-46 R/F:@1 51 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:42 | Afternoon | Tuesday | 2017 | 8
6560 | 2017-08-29 18:56 | 2017-08-29 18:56 | MINAS POWER PLANT |  |  | - | 18:56 Off line and then S/DGT 36 for S/B. |  | 1 | 18:56 | Afternoon | Tuesday | 2017 | 8
6561 | 2017-08-30 09:51 | 2017-08-30 09:51 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Animal | 0 | 09:51 It was reported b/o fuse on pole 09-P1-07 (C.Duri fdr#8). 17:00 Checked & found @3 B/O fuse for 112.5 Kva Tx. Replaced @3 B/O fuse with the same size. Cause: Animal (Monkey). |  | 1 | 9:51 | Morning | Wednesday | 2017 | 8
6562 | 2017-08-30 09:51 | 2017-08-30 09:51 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 14 | 09:51 It was reported b/o fuse on pole 08-L3-10 D/S C.Duri fdr #1. 15:45 Checked and found @3 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (monkey). |  | 1 | 9:51 | Morning | Wednesday | 2017 | 8
6563 | 2017-08-30 10:02 | 2017-08-30 10:02 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 6 | Ketigul fdr# 3 T/R 1X. Not checked yet. |  | 1 | 10:02 | Morning | Wednesday | 2017 | 8
6564 | 2017-08-30 10:02 | 2017-04-09 08:02 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 6 | Checked and found 13.8 KV VCB #3 T/R 1x Ctr:187-188 R/F:51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:02 | Morning | Wednesday | 2017 | 8
6565 | 2017-08-30 14:07 | 2017-08-30 14:07 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Pin Insulator | 0 | East Rumbai VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 14:07 | Afternoon | Wednesday | 2017 | 8
6566 | 2017-08-30 14:07 | 2017-08-31 14:07 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Pin Insulator | 0 | East Rumbai Recl. fdr #2 T/R 1x ctr: 531-532 R/F: 50. Patrolled the line & found, @1 broken Pin Support Insulator on Pole 3 RG 18. Cause: Pin Insulator. |  | 1 | 14:07 | Afternoon | Wednesday | 2017 | 8
6567 | 2017-08-30 16:37 | 2017-08-30 16:37 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 42 | RANGAU OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 16:37 | Afternoon | Wednesday | 2017 | 8
6568 | 2017-08-30 16:37 | 2017-04-09 08:00 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 42 | Checked and found Recloser 23-BD-01 T/R 6x Ctr:298-304 R/F:@1,2,3 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:37 | Afternoon | Wednesday | 2017 | 8
6569 | 2017-08-30 19:36 | 2017-08-30 19:36 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | 132 | 19:36 Minas 13.8KV ACB fdr #3 T/LO ctr:125-127 R/F: 51@1, 51@2. 20:03 Blocked and closed Minas fdr #3, OK then released the block. Not patrolled yet. |  | 1 | 19:36 | Night | Wednesday | 2017 | 8
6570 | 2017-08-30 19:36 | 2017-04-09 08:00 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | 132 | Checked and found 13.8 KV ACB #2 T/SO Ctr:125-127 R/F:@1,@2 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 19:36 | Night | Wednesday | 2017 | 8
6571 | 2017-08-30 19:36 | 2017-08-30 19:36 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 0 | Minas fdr #1 load dropped 92A (92-0A). Not checked yet. |  | 1 | 19:36 | Night | Wednesday | 2017 | 8
6572 | 2017-08-30 19:36 | 2017-08-09 08:00 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 0 | Checked and found 13.8 KV Minas fdr #1 (ACB #14) normal. Cause: Unidentified. |  | 1 | 19:36 | Night | Wednesday | 2017 | 8
6573 | 2017-08-30 19:36 | 2017-08-30 19:36 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 0 | Minas fdr #2 load dropped 52A (118-66A). Not checked yet. |  | 1 | 19:36 | Night | Wednesday | 2017 | 8
6574 | 2017-08-30 19:36 | 2017-08-09 19:36 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 0 | Checked and found Recloser M2-01 T/O Ctr:45-46 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 19:36 | Night | Wednesday | 2017 | 8
6575 | 2017-08-30 19:37 | 2017-08-30 19:37 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | 83 | Minas fdr #4 load dropped 174A (216-42A). Not checked yet. |  | 1 | 19:37 | Night | Wednesday | 2017 | 8
6576 | 2017-08-30 19:37 | 2017-04-09 08:00 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | 83 | Checked and found 13.8 KV ACB #1 normal. Cuase: Unidentified. |  | 1 | 19:37 | Night | Wednesday | 2017 | 8
6577 | 2017-08-31 06:39 | 2017-08-31 06:39 | 13.8KV PINANG FEEDER #1 | Fair | Pin Insulator | 37 | 07:39 Pinang 13.8KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 6:39 | Morning | Thursday | 2017 | 8
6578 | 2017-08-31 06:39 | 2017-02-09 15:34 | 13.8KV PINANG FEEDER #1 | Fair | Pin Insulator | 37 | Checked and found Pinang 13.8KV OCB fdr #1 T/R 1X R/F: 51N Counter: 420-421. Patrolled the line found: 1. @2 Broken Pin Insulator on pole 10-D-01. 2. @2 Broken Pin Insulator on pole 10-D-02. 3. @2 Broken Lightning Arrester at location Pinang #15. Cause: Broken Pin insulator and Lightning Arrester. |  | 1 | 6:39 | Morning | Thursday | 2017 | 8
6579 | 2017-08-31 07:58 | 2017-08-31 07:58 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 28 | 07:58 Rangau fdr #2 load dropped 161A (165-4A). Not checked yet. |  | 1 | 7:58 | Morning | Thursday | 2017 | 8
6580 | 2017-08-31 07:58 | 2017-05-09 08:00 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 28 | Checked and found Recloser 23-BD-01 T/R 6x Ctr:298-304 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:58 | Morning | Thursday | 2017 | 8
6581 | 2017-08-31 09:03 | 2017-08-31 09:03 | 13.8KV LIBO FEEDER #2 | Fair | Animal | 11 | Libo OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 9:03 | Morning | Thursday | 2017 | 8
6582 | 2017-08-31 09:03 | 2017-01-09 09:03 | 13.8KV LIBO FEEDER #2 | Fair | Animal | 11 | Checked & found, Libo OCB fdr #2 T/R 1x ctr: 465-466 R/F: 51N Patrolled the line & found, an Animal (Squirrel) around Pole KW-98 (Pole B). Cause: Animal. |  | 1 | 9:03 | Morning | Thursday | 2017 | 8
6583 | 2017-08-31 09:38 | 2017-08-31 09:38 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified (Fuse) | 5 | 09:38 It was reported b/o fuse on pole 01-06-21 D/S Duri Field fdr #3. 15:40 Checked and found @2 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above with the same size and then Energized the Tx Cause: Unidentified (fuse). |  | 1 | 9:38 | Morning | Thursday | 2017 | 8
6584 | 2017-08-31 10:20 | 2017-08-31 10:20 | 13.8KV BATANG FEEDER #2 | Fair | Planned Maintenance | 40 | 10:20 Manually opened Batang OCB fdr #2 due to: 1. Dismantled Recloser 36-AG-11 and repair By pass. 2. Replaced Pin to Pin Post insulator. 3. Replaced transformer at location Rantau Bais #11. 13:33 Blocked and Manually closed Batang OCB fdr #2 and then released the block. Cause: Plan maintenance. |  | 1 | 10:20 | Morning | Thursday | 2017 | 8
6585 | 2017-08-31 14:04 | 2017-08-31 14:04 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Pin Insulator | 0 | East Rumbai Recl. fdr #2 T/R 1x ctr: 531-532 R/F: 50. Patrolled the line & found, @1 broken Pin Support Insulator on Pole 3 RG 18. Cause: Pin Insulator. |  | 1 | 14:04 | Afternoon | Thursday | 2017 | 8
6586 | 2017-08-31 16:54 | 2017-08-31 16:54 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 27 | C.Duri ACB #11 (feeder #1) T/R 1x R/F: 51N Counter: 202-203. Not checked yet. |  | 1 | 16:54 | Afternoon | Thursday | 2017 | 8
6587 | 2017-08-31 16:54 | 2017-02-09 16:54 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 27 | Checked & found, C. Duri ACB #11 fdr #1 T/R 1x ctr: 202-203 R/F: 51 @1 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:54 | Afternoon | Thursday | 2017 | 8
6588 | 2017-01-09 09:19 | 2017-01-09 09:19 | 13.8KV SINTONG FEEDER #1 | Fair | Lightning | 66 | Sintong VCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 9:19 | Morning | Monday | 2017 | 1
6589 | 2017-01-09 09:19 | 2017-05-09 08:00 | 13.8KV SINTONG FEEDER #1 | Fair | Lightning | 66 | Checked and found 13.8 KV Sintong OCB #1 T/R 1x Ctr:385-386 R/F:@1 51N. Patrolled the line and found Dead end flash o/p 25-AD-23. Cause: Lightning. |  | 1 | 9:19 | Morning | Monday | 2017 | 1
6590 | 2017-02-09 06:41 | 2017-02-09 06:41 | 13.8KV 8D FEEDER #10 | Fair | Unidentified | 68 | 8D fdr #10 load dropped 71A ( 137-66A). Not checked yet. |  | 1 | 6:41 | Morning | Thursday | 2017 | 2
6591 | 2017-02-09 06:41 | 2017-08-09 08:00 | 13.8KV 8D FEEDER #10 | Fair | Unidentified | 68 | Checked and found Recloser 7E-21 T/R 1x Ctr:33-34 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:41 | Morning | Thursday | 2017 | 2
6592 | 2017-02-09 10:11 | 2017-02-09 10:11 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 10:11 Opened LBS: 27-AL-03 due to Opened HLC on terminal pole Loc UBI #26 D/S Ketigul fdr #2. 10:33 Closed LBS: 27-AL-03. Cause: Construction Job. |  | 1 | 10:11 | Morning | Thursday | 2017 | 2
6593 | 2017-02-09 10:15 | 2017-02-09 10:15 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified (Fuse) | 1 | 10:15 It was reported b/o fuse at well Benar #44. 11:00 Checked & found, @1, @3 b/o fuse for 150KVA Tx. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 10:15 | Morning | Thursday | 2017 | 2
6594 | 2017-02-09 22:55 | 2017-02-09 22:55 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Unidentified | 0 | Bekasap fdr #6 load dropped 47A ( 70-23A ) Not checked yet. |  | 1 | 22:55 | Night | Thursday | 2017 | 2
6595 | 2017-02-09 22:55 | 2017-05-09 08:00 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Unidentified | 0 | Checked and found Recloser 38-BE-10 T/R 1x Ctr:586-587 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 22:55 | Night | Thursday | 2017 | 2
6596 | 2017-02-09 23:34 | 2017-02-09 23:34 | NORTH DURI POWER PLANT | Fair | Under investigation | 944 | 23:34 NDC CT #3 Generator Breaker Tripped off. N.Duri 230 KV GCB #33 T/O, ------> Closed at 23:55. N.Duri 230 KV GCB #35 T/O, ------> Closed at 23:53. Load shedding level-3, Freq........Hzs. Freq. at NDC =63.87 Hzs. Freq. at System = 60.01 Hzs. 3D fdr #2 T/O, --------> Closed at 00:03. 3D fdr #3 T/O, --------> Closed at 00:04. 3D fdr #5 T/O, --------> Closed at 23:51 -----> Wip. 3D fdr #6 T/O, --------> Closed at 23:50 -----> Wip. 4D fdr #2 T/O, --------> Closed at 00:04. 4D fdr #3 T/O, --------> Closed at 00:05. 4D fdr #4 T/O, --------> Closed at 00:05. 4D fdr #5 T/O, --------> Closed at 00:05 4D fdr #6 T/O, --------> Closed at 23:51. ------> Wip. 4B fdr #4 T/O, --------> Closed at 23:48. ------> Wip. 4B fdr #5 T/O, --------> Closed at 23:45, ------> Wip. 4B fdr #6 T/O, --------> Closed at 24:00. 5B fdr #1 T/O, --------> Closed at 23:47. 5B fdr #3 T/O, --------> Closed at 00:02. 5B fdr #4 T/O, --------> Closed at 00:02. 5B fdr #5 T/O, --------> Closed at 00:05. 8C fdr #1 T/O, --------> Closed at 23:58. 8D fdr #1 T/O, --------> Closed at 23:58. 8D fdr #3 T/O, --------> Closed at 23:59. 8D fdr #10 T/O, --------> Closed at 23:59. Suram fdr #1 T/O, -------> Closed at 23:56. 8D fdr #9 load dropped 123A (177-54A), ---->WIP Weather :Rain and Lightning. Cause : Under investigation. Production loss: 47 Bbls / 61 Wells, ----->GS #6. 227 Bbls / 80 Wells, ----->GS #5. 224 Bbls / 90 Wells, ----->GS #1. ----------------------------------------+ Grand Total : 498 Bbls / 231 Wells. | 11111 | 1 | 23:34 | Night | Thursday | 2017 | 2
6597 | 2017-03-09 09:07 | 2017-03-09 09:07 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Animal | 28 | 09:07 C Duri ACB fdr #8 T/O. Checked and found C Duri ACB fdr #8 T/SO Counter: 328-329 R/F: 50@1. 09:23 Blocked and closed C Duri ACB fdr #8 --> Success. 10:09 Patrolled the line found animal (Monkey) under the power pole 04-04-22. Cause: Animal (monkey). |  | 1 | 9:07 | Morning | Thursday | 2017 | 3
6598 | 2017-03-09 13:48 | 2017-03-09 13:48 | BEKASAP MAIN SUBSTATION | Rain and Lightning | Relay Failure | 465 | 13:48 Bekasap Main C/S#B (TX #B) Trip. No power at : 1. So Bekasap fdr #1. 2. Bekasap fdr #1. 3. Bekasap fdr #2. 13:56 Manually opened So Bekasap fdr #1 Blocked & Closed at 15:00 Counter: 897-899 R/F: 50N. 13:56 Manually opened Bekasap fdr #1 Blocked & Closed at 15:07 Counter: 584-585. 13:57 Manually opened Bekasap fdr #2 Blocked & Closed at 15:08 Counter: 880-881. 14:45 Checked and found Bekasap Main C/S#B (TX #B) Trip Counter:324-325 R/F: 51N & 51G. 14:47 Manually opened 44Kv OCB #1 Blocked & Closed at 15:06. 14:47 Manually opened 44Kv OCB #2 Blocked & Closed at 14:59. 14:51 Manually closed Bekasap Main C/S #B (TX#B) --> Success. Cause: Relay failure. |  | 1 | 13:48 | Afternoon | Thursday | 2017 | 3
6599 | 2017-03-09 13:50 | 2017-03-09 13:50 | CENTRAL DURI POWER PLANT |  |  | - | 13:50 S/U CDGT #3 and On Line the unit at 14:07. |  | 1 | 13:50 | Afternoon | Thursday | 2017 | 3
6600 | 2017-03-09 16:09 | 2017-03-09 16:09 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 16:09 Opened LBS: 27-AL-03 due to Closed HLC on terminal pole Loc UBI #26 D/S Ketigul fdr #2. 16:30 Closed LBS: 27-AL-03. Cause: Construction Job. |  | 1 | 16:09 | Afternoon | Thursday | 2017 | 3
6601 | 2017-03-09 16:41 | 2017-03-09 16:41 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 76 | 6DN fdr #6 load dropped 145A (169-24A). Not checked yet. |  | 1 | 16:41 | Afternoon | Thursday | 2017 | 3
6602 | 2017-03-09 16:41 | 2017-05-09 16:41 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 76 | Checked & found, Recloser 6E-64 T/R 2x ctr: 49-51. Patrolled the line & found @2 broken Pin Insulator on Pole 6E-86. Cause: Lightning. |  | 1 | 16:41 | Afternoon | Thursday | 2017 | 3
6603 | 2017-03-09 16:44 | 2017-03-09 16:44 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 71 | 5B OCB fdr #2 T/R 1x. 5B fdr #1 load dropped 39A (170-131A). 5B fdr #3 load dropped 12A (49-37A). 5B fdr #6 load dropped 123A (192-69A) WIP GS #4. Not checked yet. |  | 1 | 16:44 | Afternoon | Thursday | 2017 | 3
6604 | 2017-03-09 16:44 | 2017-05-09 16:44 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 71 | Checked & found, 5B OCB fdr #2 T/R 1x ctr: 381-382 R/F:51 @2. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:44 | Afternoon | Thursday | 2017 | 3
6605 | 2017-03-09 16:48 | 2017-03-09 16:48 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Lightning | 0 | 16:48 Minas fdr #2 load dropped 70A (112-50A). 20:00 Checked and found Recloser #M2-01 T/O (On blocked) ctr:45-46. Patrolled the line, but foud nothing. 21:30 Blocked and closed Recloser #M2-01, OK then released the block. Will be continued patrolled tomorrow. |  | 1 | 16:48 | Afternoon | Thursday | 2017 | 3
6606 | 2017-03-09 16:48 | 2017-04-09 16:48 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Lightning | 0 | Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:48 | Afternoon | Thursday | 2017 | 3
6607 | 2017-03-09 16:54 | 2017-03-09 16:54 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 73 | 3D OCB fdr #4 T/R 1x. 3D fdr #3 load dropped 75A (152-77A). 3D fdr #5 Load dropped 57A (153-96A) WIP GS #5. Not checked yet. |  | 1 | 16:54 | Afternoon | Thursday | 2017 | 3
6608 | 2017-03-09 16:54 | 2017-08-09 08:00 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 73 | Checked and found 13.8 KV OCB #4 T/R 1x Ctr:572-573 R/F: @2 50 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 16:54 | Afternoon | Thursday | 2017 | 3
6609 | 2017-03-09 16:54 | 2017-03-09 16:54 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Unidentified | 29 | 3D fdr #2 load dropped 141A (181-40A). Not checked yet. |  | 1 | 16:54 | Afternoon | Thursday | 2017 | 3
6610 | 2017-03-09 16:54 | 2017-06-09 16:54 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Unidentified | 29 | Checked & found, 3D OCB fdr #2 T/R 1x ctr: 244-245 R/F: None. Patrolled the line & found, @2 broken fuse for Tx on Pole 3D-52. Cause: Unidentified. |  | 1 | 16:54 | Afternoon | Thursday | 2017 | 3
6611 | 2017-03-09 16:59 | 2017-03-09 16:59 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 19 | 6D OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 16:59 | Afternoon | Thursday | 2017 | 3
6612 | 2017-03-09 16:59 | 2017-05-09 16:59 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 19 | Checked & found, 6D OCB fdr #1 T/R 1x ctr: 328-329 R/F: 51 @1. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:59 | Afternoon | Thursday | 2017 | 3
6613 | 2017-03-09 16:59 | 2017-03-09 16:59 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 0 | 6D fdr #2 load dropped 66A (250-184A). Not checked yet. |  | 1 | 16:59 | Afternoon | Thursday | 2017 | 3
6614 | 2017-03-09 16:59 | 2017-05-09 16:59 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recloser 6D-87 T/R 1x ctr: 61-62. Patrolled the line & found, @1, @2 Flash over Dead-end Insulator on Pole 6C-21. Cause: Lightning. |  | 1 | 16:59 | Afternoon | Thursday | 2017 | 3
6615 | 2017-03-09 17:04 | 2017-03-09 17:04 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 32 | 5B OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 17:04 | Afternoon | Thursday | 2017 | 3
6616 | 2017-03-09 17:04 | 2017-05-09 17:04 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 32 | Checked & found, 5B OCB fdr #1 T/R 2x ctr: 249-251 R/F: 51 @2. Patrolled the line & found @2 broken Dead-end Insulator on Pole 4B-11. Cause: Lightning. |  | 1 | 17:04 | Afternoon | Thursday | 2017 | 3
6617 | 2017-03-09 18:20 | 2017-03-09 18:20 | CENTRAL DURI POWER PLANT |  |  | - | 18:20 S/D CDGT #1 and then Open Gen Breaker at 18:21 for stand by. |  | 1 | 18:20 | Afternoon | Thursday | 2017 | 3
6618 | 2017-04-09 06:37 | 2017-04-09 06:37 | 13.8KV 4B FEEDER #4 | Fair | Powerline - Conductor | 110 | 4B 13.8 KV VCB fdr #4 T/R 1x 4B fdr #5 load dropped 52A (256-204A). 4B fdr #6 load dropped 12A (157-204A) 06:44 It was reported broken conductor behind KBJ Substation. 08:57 Checked and found @1 broken conductor between poles 46-CH-09 - 46-CH-11. Opened LBS 3A-22. 10:15 Opened HLC on pole 46-CH-07. Replaced @1 broken conductor. 12:15 Closed LBS 3A-22. 16:40 Opened LBS 3A-22. Closed Hot Line Clamp on pole 46-CH-07. 17:03 Closed LBS 3A-22. Cause: Broken Conductor. |  | 1 | 6:37 | Morning | Sunday | 2017 | 4
6619 | 2017-04-09 11:00 | 2017-04-09 11:00 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 289 | 11:00 Manually opened Bekasap OCB fdr #2. Due to replaced transformer at location Bekasap #37. 12:15 Manually closed Bekasap OCB fdr #2. Cause: Plan Maintenance. |  | 1 | 11:00 | Morning | Sunday | 2017 | 4
6620 | 2017-04-09 14:09 | 2017-04-09 14:09 | 13.8KV NELLA FEEDER #1 | Fair | Low mega-ohm reading | 265 | 14:09 It was reported b/o fuse at well Bangko #228 D/S Nella fdr #1. 15:30 Checked and found @1 & @3 b/o fuse for 500 KVa Tx. Perform TTR and Megger found Low megger reading. Cause: low megger reading. This Tx is not replaced yet. |  | 1 | 14:09 | Afternoon | Sunday | 2017 | 4
6621 | 2017-04-09 14:09 | 2017-08-09 06:59 | 13.8KV NELLA FEEDER #1 | Fair | Low mega-ohm reading | 265 | Replaced the 500KVA Burn Out TX with 300KVA at Well Banko #228 (850Volt, for 147HP motor) |  | 1 | 14:09 | Afternoon | Sunday | 2017 | 4
6622 | 2017-04-09 16:00 | 2017-04-09 16:00 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Transformer Failure | 0 | 16:00 It was reported b/o fuse at well PTH #23 D/S PTH fdr #1. 16:30 Checked and found @1 & @2 b/o fuse for 550 KVa Tx. Perform TTR and Megger found Low megger reading. Cause: Tx failure (low megger reading). This Tx is not replaced yet. |  | 1 | 16:00 | Afternoon | Sunday | 2017 | 4
6623 | 2017-04-09 16:00 | 2017-05-09 10:25 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Transformer Failure | 0 | Replaced 550 Kva transformer failure with the same size and energized the Tx. Cause: Transformer failure. |  | 1 | 16:00 | Afternoon | Sunday | 2017 | 4
6624 | 2017-04-09 17:28 | 2017-04-09 17:28 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Dead End Insulator | 78 | 17:28 So Bekasap OCB fdr #1 T/SO. 18:10 Checked and found So Bekasap OCB fdr #1 T/SO Ctr: 399-400 R/F: do not appear. 18:15 Blocked and closed So Bekasp OCB fdr #1 --> Ok and then released the block. Cause: Not patrolled yet. |  | 1 | 17:28 | Afternoon | Sunday | 2017 | 4
6625 | 2017-04-09 17:28 | 2017-05-09 17:28 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Dead End Insulator | 78 | Patrolled the line & found, @3 broken Dead-end Insulator on Pole 37-BF-02. Cause : Dead End Insulator |  | 1 | 17:28 | Afternoon | Sunday | 2017 | 4
6626 | 2017-04-09 20:15 | 2017-04-09 20:15 | 115KV KOTABATAK - PETAPAHAN LINE | Fair | Others | 408 | 20:15 CKBS 115 KV OCB #1 T/R 1X (CKBS 115 KV Line to Petapahan). ( No Power to Petapahan Substation & Suram Substation ). CKBS fdr #2 Load dropped 190A ( 253-63A ) ----> WIP. Not checked yet. Productions loss. Petapahan fdr#1 : 26 bbls / 9 wells Petapahan fdr#2 : 398 bbls /80 wells. Suram fdr : 8 bbls / 2 wells. ---------------------------------------------+ Grand Total : 432 bbls / 91 wells |  | 1 | 20:15 | Night | Sunday | 2017 | 4
6627 | 2017-04-09 20:15 | 2017-05-09 11:15 | 115KV KOTABATAK - PETAPAHAN LINE | Fair | Others | 408 | Checked & found, CKBS 115 KV OCB #1 T/R 1x Ctr: 0039-0040 R/F: 21AG. Patrolled the line & found, PLN Service Drop Cable touched powerline between Pole KP 41 to KP 42. Cause: Others. |  | 1 | 20:15 | Night | Sunday | 2017 | 4
6628 | 2017-05-09 09:30 | 2017-05-09 09:30 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | 09:30 Manually opened So Balam VCB fdr #4. Due to: 1. Replaced Recloser on pole 17-AA-43. 2. Tie in new well near well So Balam #323. 16:51 Blocked and closed So Balam VCB fdr #4 and then released the block. Cause: Construction Job. |  | 1 | 9:30 | Morning | Tuesday | 2017 | 5
6629 | 2017-05-09 10:42 | 2017-05-09 10:42 | 13.8KV DURI FIELD FEEDER #4 | Fair | Lightning | 0 | D Field VCB #51 (feeder #4) T/R 1x. Not checked yet. |  | 1 | 10:42 | Morning | Tuesday | 2017 | 5
6630 | 2017-05-09 10:42 | 2017-10-09 08:02 | 13.8KV DURI FIELD FEEDER #4 | Fair | Lightning | 0 | Checked & found D.Field ACB fdr#4 T/R 3X, Ctr: 505-509, R/F: 51N. Patrolled the Lune, found @3 Broken LA O/P 07-V1-16. Cause : Lightning |  | 1 | 10:42 | Morning | Tuesday | 2017 | 5
6631 | 2017-05-09 12:27 | 2017-05-09 12:27 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Powerline - Jumper | 0 | It was reported b/o fuse for Tx at well Ampuh #24. Not checked yet. |  | 1 | 12:27 | Afternoon | Tuesday | 2017 | 5
6632 | 2017-05-09 12:27 | 2017-07-09 10:45 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Powerline - Jumper | 0 | 10:45 Checked & found, @3 b/o fuse for 300KVATX. Replaced the fuse with the same size, then energized the TX. Cause: Jumper (Loss Connection). |  | 1 | 12:27 | Afternoon | Tuesday | 2017 | 5
6633 | 2017-05-09 14:18 | 2017-05-09 14:18 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 21 | 14:18 Bangko fdr #4 load dropped 113A (201-88A). 15:39 Checked & found Recl 27Y23 T/O (for WIP Tx Benar GS). Blocked & closed Recl. 27Y23, then release the block. Cause: Lightning. |  | 1 | 14:18 | Afternoon | Tuesday | 2017 | 5
6634 | 2017-05-09 14:44 | 2017-05-09 14:44 | 13.8KV PETAPAHAN FEEDER #2 | Rain and Lightning | Unidentified | 296 | Petapahan fdr #2 load dropped 186A (231-45A). Checked & found RCL. 29CX-05 Counter not change, R/F: not appear. Patrolled the Line, found nothing Cause : Unidentified. |  | 1 | 14:44 | Afternoon | Tuesday | 2017 | 5
6635 | 2017-05-09 15:39 | 2017-05-09 15:39 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Powerline - Conductor | 296 | 15:39 C Duri fdr #1 load dropped 54A (104-50A). 15:54 It was reported Broken Conductor o/p 38AT28. Checked & found Recl 39AV36 T/LO Ctr:229-234. 18:50 Opened HLC on TOP Kulim#54. 18:55 Blocked & closed Recl. 39AV36, then release the block. (Repaired conductor tomorrow). Cause: Broken Conductor. |  | 1 | 15:39 | Afternoon | Tuesday | 2017 | 5
6636 | 2017-05-09 16:14 | 2017-05-09 16:14 | 13.8KV DURI FIELD FEEDER #4 | Rain | Powerline - Conductor | 154 | 16:14 Duri Field OCB fdr#4 T/R 2x, Ctr:.........., R/F:.......... 16:55 It was reported Broken Conductor o/p 07.U3.04. 18:12 Checked & found @1 Broken Conductor On Pole above, under Recl. 07.U3.02 (in Bypass status). Manually Open D.Field OCB fdr#4, to Isolate the Broken Conductor. Open Bypass Recl. 07.U3.02. 18:16 Blocked & Closed D.Field OCB fdr#4, then released the Block. 06/09/2017 13:17 Closed LBS 07-U3-17 (Recl. 07-U3-02 Open, problem) Transfer Part Load D.field fdr#4 to D.Field fdr#2 After Finished Replaced the Broken Conductor. Cause: Broken Conductor. |  | 1 | 16:14 | Afternoon | Tuesday | 2017 | 5
6637 | 2017-06-09 09:55 | 2017-06-09 09:55 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 09:55 Open LBS 28-AL-05 (Ketigul fdr#2) Project team Tie In new well near Ubi #26. 10:20 Closed back the LBS 28-AL-05 After finished Tie In Jobs. Cause: Planned Maintenance Project. |  | 1 | 9:55 | Morning | Friday | 2017 | 6
6638 | 2017-06-09 10:30 | 2017-06-09 10:30 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 106 | 10:30 It was reported no power at well 10D-16, 10D-24, 9D-98, 9D-99. (8C fdr#1). 14:50 Checked & found Recl. 9D-111 T/SO. Blocked & Closed the Recloser above, then released the Block. Cause: Unidentified |  | 1 | 10:30 | Morning | Friday | 2017 | 6
6639 | 2017-06-09 10:40 | 2017-06-09 10:40 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | 10:40 Manually Open S.Balam OCB fdr#4. Continued Project, Tie In new well Balam#302. 14:05 Closed Back the S.Balam OCB fdr#4. Cause: Planned Maintenance Project Construction. | 12345 | 1 | 10:40 | Morning | Friday | 2017 | 6
6640 | 2017-06-09 11:30 | 2017-06-09 11:30 | 13.8KV BATANG FEEDER #2 | Fair | Powerline - Conductor | 252 | 11:30 It was reported Broken Conductor O/P 34-AE-04Nera well R.bais #24. (Batang fdr#2). 13:45 Checked & found @2 Broken Conductor on pole above. 16:28 Manually Open Batang OCB fdr#2 to Isolate the Broken Conductor. 16:45 Manually Closed Batang OCB fdr#2, (Wells Down R.Bais #24 & #35). Cause : Broken Conductor (Will be Replace soon). |  | 1 | 11:30 | Morning | Friday | 2017 | 6
6641 | 2017-06-09 18:35 | 2017-06-09 18:35 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified | 0 | C.Duri ACB fdr#13 T/R 1x, Ctr: 199-200, R/F: 51 @1,@2. Not checked yet. |  | 1 | 18:35 | Afternoon | Friday | 2017 | 6
6642 | 2017-06-09 18:35 | 2017-10-09 17:49 | 13.8KV CENTRAL DURI FEEDER #13 | Fair | Unidentified | 0 | Checked & found C.Duri ACB fdr#13 T/R 1x. Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 18:35 | Afternoon | Friday | 2017 | 6
6643 | 2017-06-09 21:00 | 2017-06-09 21:00 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 16 | 21:00 It was reported B/O fuse at Well Balam #203 (S.Balam fdr#1). Not checked yet. |  | 1 | 21:00 | Night | Friday | 2017 | 6
6644 | 2017-06-09 21:00 | 2017-07-09 10:00 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 16 | 10:01 Checked & found @1@2 B/O fuse for 300KVATX at Well Balam #203. Replaced the fuse with the same size, then Energized the TX. Cause: Un identified. |  | 1 | 21:00 | Night | Friday | 2017 | 6
6645 | 2017-06-09 22:20 | 2017-06-09 22:20 | 13.8KV SINTONG FEEDER #2 | Fair | Low mega-ohm reading | 49 | 22:20 It was reported B/O fuse at Well Benar#44 (Sintong fdr#2) Checked & found @1@2 B/O fuse for 100KVATX. Tested TTR & Megger, it was Low Megger. Cause : Transformer Low megger reading. |  | 1 | 22:20 | Night | Friday | 2017 | 6
6646 | 2017-06-09 22:20 | 2017-07-09 10:30 | 13.8KV SINTONG FEEDER #2 | Fair | Low mega-ohm reading | 49 | 10:30 Replaced the 150KVA Broken TX to 100KVATX , then Energized the TX. Cause: Transformer Low Megger reading. |  | 1 | 22:20 | Night | Friday | 2017 | 6
6647 | 2017-07-09 10:17 | 2017-07-09 10:17 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 307 | 10:01 Manually Opened Recl. 39-AV-36, Supply toward Kulin & Puncal Field (CD fdr#1). to - Repair Broken Conductor at Well Kulin #54. - Replace 300KVATX at Well Kulin #09 - Repair Hot Spot .. 14:00 Manually Closed the Recloser above after finished Repair Above Jobs. Cause : Planned Maintenance. Production loss = 214 Bbls / 17 wells SLN. Production loss = 88 Bbls / 27 wells HO. --------------------------------------------------- Total = 302 Bbls / 44 wells. |  | 1 | 10:17 | Morning | Sunday | 2017 | 7
6648 | 2017-07-09 17:11 | 2017-07-09 17:11 | 44KV NORTH DURI - DUMAI LINE | Rain | Unidentified | 0 | N.DURI 44KV GCB#1 T/R 1x, (44KV Line N.Duri - Dumai). Not checked yet. |  | 1 | 17:11 | Afternoon | Sunday | 2017 | 7
6649 | 2017-07-09 17:11 | 2017-10-09 17:20 | 44KV NORTH DURI - DUMAI LINE | Rain | Unidentified | 0 | Checked & found 44Kv Line ND-Dumai GCB#44 T/R 1x Ctr:113-114 R/F:None. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:11 | Afternoon | Sunday | 2017 | 7
6650 | 2017-08-09 15:13 | 2017-08-09 15:13 | 13.8KV 8C FEEDER #4 | Heavy Rain | Lightning | 72 | 8C OCB fdr #4 T/R 1x Not checked yet. |  | 1 | 15:13 | Afternoon | Wednesday | 2017 | 8
6651 | 2017-08-09 15:13 | 2017-11-09 20:13 | 13.8KV 8C FEEDER #4 | Heavy Rain | Lightning | 72 | Checked & found 8C fdr#4 T/R 1x Ctr:595-596 R/F:51N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 15:13 | Afternoon | Wednesday | 2017 | 8
6652 | 2017-08-09 15:13 | 2017-08-09 15:13 | 13.8KV 8C FEEDER #3 | Heavy Rain | Lightning | 0 | 8C Fdr # 3 Load drop 184 Amp (196 - 12 Amp) Not Checked yet. |  | 1 | 15:13 | Afternoon | Wednesday | 2017 | 8
6653 | 2017-08-09 15:13 | 13/09/2017 08:00 | 13.8KV 8C FEEDER #3 | Heavy Rain | Lightning | 0 | Checked and found Recloser 8D-18A T/R 1x Patrolled the line and found broken suspension insulator o/p 8D-16A @1, @2. Cause: Lightning. |  | 1 | 15:13 | Afternoon | Wednesday | 2017 | 8
6654 | 2017-08-09 15:20 | 2017-08-09 15:20 | 13.8KV 8C FEEDER #6 | Heavy Rain | Lightning | 0 | 8C Fdr # 6 T/R 3X. 8C Fdr # 5 Load Drop 198 Amp ( 198 - 0 Amp ) WIP at GS #2. Not Checked yet. |  | 1 | 15:20 | Afternoon | Wednesday | 2017 | 8
6655 | 2017-08-09 15:20 | 2017-10-09 15:20 | 13.8KV 8C FEEDER #6 | Heavy Rain | Lightning | 0 | Checked & found, 8C VCB fdr #6 T/R 3x ctr: 579-582 R/F: 51 @2, @3, 50. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 15:20 | Afternoon | Wednesday | 2017 | 8
6656 | 2017-08-09 15:23 | 2017-08-09 15:23 | 13.8KV 6D FEEDER #3 | Heavy Rain | Lightning | 104 | 6D OCB fdr#3 T/R 1x. 6D fdr #1 load dropped 165A (210-45A). 6D fdr #2 load dropped 222A (242-20A). Not Checked yet. |  | 1 | 15:23 | Afternoon | Wednesday | 2017 | 8
6657 | 2017-08-09 15:23 | 2017-11-09 14:40 | 13.8KV 6D FEEDER #3 | Heavy Rain | Lightning | 104 | Checked & found 6D OCB fdr#3 T/R 1x, Ctr: 216-217, R/F: 50 @1@2. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 15:23 | Afternoon | Wednesday | 2017 | 8
6658 | 2017-08-09 15:23 | 2017-08-09 15:23 | 13.8KV 6DN FEEDER #3 | Heavy Rain | Lightning | 0 | 6 DN Fdr # 3 T/R 1 X Not checked yet. |  | 1 | 15:23 | Afternoon | Wednesday | 2017 | 8
6659 | 2017-08-09 15:23 | 2017-11-09 20:23 | 13.8KV 6DN FEEDER #3 | Heavy Rain | Lightning | 0 | Checked 6DN fdr#3 Not operated. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 15:23 | Afternoon | Wednesday | 2017 | 8
6660 | 2017-08-09 15:30 | 2017-08-09 15:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 61 | 15:30 Manually opened Recloser 38-AV-09 D/S CD Fdr # 1 Due to replaced transformer at well Kulim #67. 16:18 Blocked and manually closed Recloser 38-AV-09. Cause: Plan Maintenance. |  | 1 | 15:30 | Afternoon | Wednesday | 2017 | 8
6661 | 2017-08-09 22:13 | 2017-08-09 22:13 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 64 | 22:13 So Balam fdr #4 load dropped 15A (188-173A). 22:45 It was reported no power at Test Station #E. 23:45 Checked and found Recloser 16-AB-03 T/O Counter: 442-443 R/F: 51 @2. (in block position due to Rig HPS #09 activity at location So Balam #47). 23:50 Blocked and closed Recloser 16-AB-03 --> OK (still in block position due to Rig activity). Cause: Not patrolled yet. |  | 1 | 22:13 | Night | Wednesday | 2017 | 8
6662 | 2017-08-09 22:13 | 2017-10-09 08:38 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 64 | Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 22:13 | Night | Wednesday | 2017 | 8
6663 | 2017-09-09 06:10 | 2017-09-09 06:10 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 836 | 06:10 C Duri fdr# 1 load dropped 33A (107-74A). 08:45 Checked & found, Recl. 41.AW.62 T/O (In block status, Rig job at well Kulim#01) ctr: 260-261 Blocked & closed recl. 41 AW 62, then released the block, after Confirm with Rig representative. Patrolled the Line, but found nothing. 12:30 It was reported No Power at Kulin GS2, Under Recl. 38.AS.09. 14:00 Checked & found, Recl.38.AS.09 was T/LO, Ctr: 222-225. Patrolled the Line, but found Nothing. 15:25 Blocked & Closed The Recloser, then Released the block. Cause: Unidentified. | 12345 | 1 | 6:10 | Morning | Saturday | 2017 | 9
6664 | 2017-09-09 10:40 | 2017-09-09 10:40 | 115KV KOTABATAK JUNCTION - LIBO LINE | Fair | Planned Maintenance | 83 | 10:40 Man. Open KBJ 115KV GCB#53 & GCB#55 Line KBJ-LIBO (Planned Shut down Libo Substation ). to - Isolate MSU; - Install T tap jumper 115KV Incoming Libo Substation. - Install T tap jumper 13.8KV out going Libo Substation. - Repair Hot Spot at Secondary TX Libo Substation. 12:00 Man. Closed KBJ 115KV GCB#53 & GCB#55 Line KBJ-LIBO (Energized Libo Substation). after Finished Maintenance Jobs above. Cause: Planned Maintenance. |  | 1 | 10:40 | Morning | Saturday | 2017 | 9
6665 | 2017-10-09 08:54 | 2017-10-09 08:54 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | Menggala fdr#1 load drooped 41A(185-134A). Menggala GFPC T/R 1x. Not checked yet. |  | 1 | 8:54 | Morning | Monday | 2017 | 10
6666 | 2017-10-09 08:54 | 13/09/2017 14:43 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | Checked & found Recl. 19-AO-01 T/R 1x, Ctr: 478-479. R/F: 51N. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 8:54 | Morning | Monday | 2017 | 10
6667 | 2017-10-09 18:10 | 2017-10-09 18:10 | CENTRAL DURI POWER PLANT |  |  | - | 18:10 S/U CGT#1, then on line the unit at 18:38. 18:35 Opened Tie Breaker ACB#19. |  | 1 | 18:10 | Afternoon | Monday | 2017 | 10
6668 | 2017-11-09 00:20 | 2017-11-09 00:20 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT#4, then S/D the unit for S/B. 00:21 Closed tie breaker ACB#39. |  | 1 | 0:20 | Night | Thursday | 2017 | 11
6669 | 2017-11-09 08:55 | 2017-11-09 08:55 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Construction Job | 0 | 08:55 Man. Opened Petapahan OCB fdr#2. to Tie In New Well PTH #138. 12:02 Man. Closed Petapahan OCB fdr#2. after Finished Tie in. Cause: Planned Maintenance (Project Constraction). |  | 1 | 8:55 | Morning | Thursday | 2017 | 11
6670 | 2017-11-09 10:17 | 2017-11-09 10:17 | 5 BRAVO SUBSTATION | Fair | Planned Maintenance | 0 | Manually Opened 115KV 5B OCB #21. Planned Maintenance service 5 Yearly OCB#21. Cause: Planned Maintenance. |  | 1 | 10:17 | Morning | Thursday | 2017 | 11
6671 | 2017-11-09 11:28 | 2017-11-09 11:28 | 13.8KV SINTONG FEEDER #1 | Fair | Planned Maintenance | 798 | 11:28 Man Opened Sintong OCB fdr#1. - Repair Cross Arm o/p 26-AE-22 - Install HLC of bay pass switch o/p 25-AD-26. - Replace broken Insulator O/Top Well seruni #32. 17:10 Man. Closed Sintong OCB fdr#1. After finished the Jobs. Cause: Planed Maintenance. | 123 | 1 | 11:28 | Morning | Thursday | 2017 | 11
6672 | 2017-11-09 16:47 | 2017-11-09 16:47 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 0 | S.Balam fdr#1 Load dropped 72A(104-32A). Ground fault alarm at Fdr#1. Not checked yet. |  | 1 | 16:47 | Afternoon | Thursday | 2017 | 11
6673 | 2017-11-09 16:47 | 2017-12-09 16:47 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 0 | Checked and found Recl. 16 Z 25 T/R 1X ctr:28-29. Patrolled the line and found nothing. Cause: Unidentified |  | 1 | 16:47 | Afternoon | Thursday | 2017 | 11
6674 | 2017-11-09 17:30 | 2017-11-09 17:30 | 13.8KV BANGKO FEEDER #4 | Fair | Secondary Cable | 0 | 17:30 It was reported b/o fuse for Tx at Well Bangko #48 D/S Bangko fdr #4. 22:50 Checked and found @2 b/o fuse for 150 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Secondary cable lost connection. |  | 1 | 17:30 | Afternoon | Thursday | 2017 | 11
6675 | 2017-11-09 22:30 | 2017-11-09 22:30 | 13.8KV BEKASAP FEEDER #3 | Fair | Broken Fuse Cut Out | 35 | It was reported B/O fuse at well Bekasap#33 (Bekasap fdr#3). (Would be changed tomorrow). Not checked yet. |  | 1 | 22:30 | Night | Thursday | 2017 | 11
6676 | 2017-11-09 22:30 | 2017-12-09 14:00 | 13.8KV BEKASAP FEEDER #3 | Fair | Broken Fuse Cut Out | 35 | 14:00 Checked and found @1 broken FCO for 300KVA TX at well BKS #33. Replaced broken FCO above, then energized the TX.OK. Cause: Broken FCO. |  | 1 | 22:30 | Night | Thursday | 2017 | 11
6677 | 2017-12-09 08:31 | 2017-12-09 08:31 | 13.8KV NORTH DURI FEEDER #11 | Fair | Animal | 431 | 08:31 N. Duri 13.8KV VCB fdr #11 T/R 1X. N. Duri GFPC T/R 2X. 09:50 It was reported no power around 13 E11 04. 11:15 Checked and found Recl. 13-F3-49 T/LO ctr: Also found dead Monkey at secondary Bushing of Recloser. 14:45 Open LBS 13 G5.1 38, -----> closed at 15:00. Removed Dead monkey and By Pass Recl.13-F3-49 (Broken Bushing). Cause: Animal (Monkey). |  | 1 | 8:31 | Morning | Saturday | 2017 | 12
6678 | 2017-12-09 08:35 | 2017-12-09 08:35 | 5 BRAVO SUBSTATION | Fair | Under investigation | 83 | 08:35 5B 115KV OCB #25 T/O ctr:212-213 R/F: 86T and 59T. 5B 115KV OCB #26 T/O ctr:835-836. No power to 5B TX-2 ( 5B fdr #4, #5 and #8). 09:40 Checked and found, 5B 115KV OCB #25 T/O ctr:212-213 R/F: 86T and 59T. 5B 115KV OCB #26 T/O ctr:835-836. 09:41 Manually open 5B fdr #4, ------>Closed at 09:57. Manually open 5B fdr #5, ------>Closed at 09:57. Manually open 5B fdr #8, ------>Closed at 09:57. 09:49 Closed 5B 115KV OCB #25, but tripped again. Un plug 59T Relay. 09:55 closed 115KV OCB #25. OK. 09:55 closed 115KV OCB #26. OK. Cause: Under investigation. |  | 1 | 8:35 | Morning | Saturday | 2017 | 12
6679 | 2017-12-09 09:51 | 2017-12-09 09:51 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 3 | 09:51 It was reported b/o fuse o/p 04-06-02. 17:00 Checked and found @1 b/o fuse for 112.5KVA TX. Performed TTR test and Megger the TX and found, Good. Replaced b/o fuse above with same size, then energized the TX.OK. Cause: Un identified Fuse. |  | 1 | 9:51 | Morning | Saturday | 2017 | 12
6680 | 2017-12-09 10:04 | 2017-12-09 10:04 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 10:04 Open LBS 28 AL 05 to replaced Production valve at well UBI # 39. (Shuted off wells at UBI field and Sikaladi field). 14:15 Open LBS 27 AL 03 and closed LBS 28 AL 05. (Shuted off wells at Sikaladi field) Cause: Planned Maintenance. | 12345 | 1 | 10:04 | Morning | Saturday | 2017 | 12
6681 | 2017-12-09 12:30 | 2017-12-09 12:30 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 0 | 12:30 It was reported Oil Leakege at well Petani 109. Checked and found, oil leakage for 300KVA TX. Manual Opened Fuse for The Tx. Cause: TX failure (Well off, waiting RIG Moving, will be replaced after RIG Completion). |  | 1 | 12:30 | Afternoon | Saturday | 2017 | 12
6682 | 2017-12-09 12:30 | 28/09/2017 12:00 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 0 | Replaced 300KVA Tx with the same Size then energized the Tx. (After RIG activity completion). Cause: Transformer Failure. |  | 1 | 12:30 | Afternoon | Saturday | 2017 | 12
6683 | 2017-09-13 06:20 | 2017-09-13 06:20 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Unidentified | 14 | 06:20 Menggala fdr#1 Load dropped 114A (187-73A). Menggala GFPC T/R 1x. Ground fault at fdr#1. 14:45 Checked & found Recl. 19-AN-04 T/R 1x, Ctr: 339-341, R/F: 51N. Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 6:20 | Morning | Wednesday | 2017 | 9
6684 | 2017-09-13 07:49 | 2017-09-13 07:49 | 13.8KV LIBO FEEDER #1 | Cloudy | Unidentified | 15 | 07:49 Libo 13.8 KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 7:49 | Morning | Wednesday | 2017 | 9
6685 | 2017-09-13 07:49 | 2017-09-14 07:49 | 13.8KV LIBO FEEDER #1 | Cloudy | Unidentified | 15 | Checked & found, Libo OCB fdr #1 T/R 1x ctr: 555-556 R/F: 50N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:49 | Morning | Wednesday | 2017 | 9
6686 | 2017-09-13 09:35 | 2017-09-13 09:35 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified (Fuse) | 36 | 09:35 It was reported b/o fuse S.Balam #152 (d/s S.Balam fdr #4). Checked and found @1,@2,@3 b/o fuse for 100 KVA TX. Performed TTR test and Megger the TX and found, Good. Replaced b/o fuse above with the same size, then energized the TX.OK. Cause: Unidentified Fuse. |  | 1 | 9:35 | Morning | Wednesday | 2017 | 9
6687 | 2017-09-13 09:41 | 2017-09-13 09:41 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 0 | 09:41 It was reported b/o fuse at well S.Balam #183, (the Well was Off status) d/s S.Balam fdr #1. 10:17 Checked and found b/o fuse for 100 KVA TX. Performed TTR test and Megger the TX and found, Good. Replaced b/o fuse above with same size, then energized the TX.OK. Cause: Animal ( Squirrel ). |  | 1 | 9:41 | Morning | Wednesday | 2017 | 9
6688 | 2017-09-13 10:07 | 2017-09-13 10:07 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 430 | 10:07 Open 13.8 Kv So,Bekasap VCB fdr#1. Replaced Recl. 37BD48, then function test Recl. Replaced Broken Dead End Insulator o/p 38BF08, 38BF02, 38BF14. 14:37 Blocked & closed 13.8 Kv So.Bekasap VCB fdr#1, then release the block. Cause: Planned Maintenance. |  | 1 | 10:07 | Morning | Wednesday | 2017 | 9
6689 | 2017-09-13 12:00 | 2017-09-13 12:00 | 13.8KV S. BALAM FEEDER #1 | Fair | Secondary Cable | 0 | 12:00 It was reported b/o fuse at well S.Balam#309 (Balam fdr#1). Checked & found @1@2@3 b/o fuse for 300KVATX, also found Broken the secondary cable. Replaced the fuses with the same size, then Energized the TX. after isolate the broken cable. Cause : Secondary Cable (ground). |  | 1 | 12:00 | Afternoon | Wednesday | 2017 | 9
6690 | 2017-09-13 13:34 | 2017-09-13 13:34 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 0 | Sintong GFPC T/R 1X. Ground fault alarm from Sintong fdr #2. Sintong fdr #2 load dropped 28A (147-19A). Not checked yet. |  | 1 | 13:34 | Afternoon | Wednesday | 2017 | 9
6691 | 2017-09-13 13:34 | 2017-09-16 14:12 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found Rcl: 29-Z -13A T/R 1x, Ctr: 172-173, R/F : 50 @1. GFPC T/R 4X counter: 992-996 R/F: 51N Patrolled the Line, but found nothing. Cause: Unidentified (Suspected Lightening) |  | 1 | 13:34 | Afternoon | Wednesday | 2017 | 9
6692 | 2017-09-13 14:44 | 2017-09-13 14:44 | 115KV N. DURI SUBST - CD. SW. YARD LINE | Rain and Lightning | Under investigation | 0 | 14:44 C. Duri 115KV GCB #53 T/R 1X. C. Duri 115KV GCB #55 T/R 1X. N. Duri 115KV GCB #3 T/SO (DL Mode). (115KV C. Duri - N. Duri line to N. Duri TX-5). 15:13 Checked and found N. Duri 115KV GCB #3 T/SO ctr:236-237 R/F: @ to ground. Checked and found C. Duri 115KV, found R/F:Zoe-1, A-G Km58. 15:17 Closed N. Duri 115KV GCB #3 (DL and SC), but failed. 15:37 Manually open C. Duri 115KV GCB# 53, ----->Closed at 15:49. Manually open C. Duri 115KV GCB# 55, ----->Closed at 15:51. 15:38 Closed N. Duri 115KV GCB #3, OK (DL Mode). (N. Duri TX-5 back to normal). Cause: Under investigation. |  | 1 | 14:44 | Afternoon | Wednesday | 2017 | 9
6693 | 2017-09-13 14:46 | 2017-09-13 14:46 | 13.8KV NORTH DURI FEEDER #7 | Rain and Lightning | Recloser | 32 | 14:46 N.Duri 13.8 KV VCB fdr # 7 T/O (in Block status, PT WKS). 15:39 Blocked & Closed N.Duri fdr #7, after Confirm with PT WKS. 17:00 It was reported no power o/p 10 L1 28. 17:45 Checked and found @3 broken Jumper of Recloser 10 L1 17. 19:05 Man. Opened N. Duri VCB fdr #7 19:35 Man. Closed N.Duri VCB fdr#7, after bypassed the Recl. 10-L1-17, due to Recloser Control Failure and Broken Jumper Cause: Recloser Control Failure and Broken Jumper |  | 1 | 14:46 | Afternoon | Wednesday | 2017 | 9
6694 | 2017-09-13 14:46 | 2017-09-13 14:46 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Recloser | 67 | 14:46 N.Duri fdr #8 load dropped 19A (54-35A). 17:00 It was reported No Power o/p 10-L1-28 (No power AWT Area 10). 18:06 Checked & found Recloser 10-L1-02 T/SO Counter: Blocked & Closed Recloser 10-L1-02, but failed. 18:35 Man. Opened N.Duri VCB fdr#8 18:38 Man. Closed N.Duri VCB fdr#8 after Bypassed Recloser 10-L1-02. Cause: Recloser (Control problem). |  | 1 | 14:46 | Afternoon | Wednesday | 2017 | 9
6695 | 2017-09-14 07:30 | 2017-09-14 07:30 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 0 | It was reported b/o fuse for Tx on Pole 01-02-06. Checked & found, unbalance voltage for Tx above. Cause: Transformer Failure Not replaced yet. |  | 1 | 7:30 | Morning | Thursday | 2017 | 9
6696 | 2017-09-14 07:30 | 2017-09-17 07:30 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Transformer Failure | 0 | Replaced Failure Transformer with the same size then energized the Tx. Cause: Transformer Failure. |  | 1 | 7:30 | Morning | Thursday | 2017 | 9
6697 | 2017-09-14 13:35 | 2017-09-14 13:35 | 13.8KV KETIGUL FEEDER#1 | Fair | Construction Job | 0 | 13:35 Open LBS 32 AJ 01 (d/s Ketigul fdr#1) to Tie in new Well at Kelok field. (3 wells down during the JOB). 13:50 Closed The LBS after finished Tie In the New well. Cause: Plan maintenance (Project). |  | 1 | 13:35 | Afternoon | Thursday | 2017 | 9
6698 | 2017-09-14 16:30 | 2017-09-14 16:30 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 122 | It was reported b/o fuse o/p 08 M3 03 (d/s C.Duri fdr#3) Not checked yet. |  | 1 | 16:30 | Afternoon | Thursday | 2017 | 9
6699 | 2017-09-14 16:30 | 2017-09-18 15:19 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 122 | Replaced b/o Fuse for 112.5KVA Tx on Pole 08-M3-03. Cause: Unidentified (Fuse). See PIDOD at 18 Sep, 15:19 |  | 1 | 16:30 | Afternoon | Thursday | 2017 | 9
6700 | 2017-09-15 10:30 | 2017-09-15 10:30 | 13.8KV PETANI FEEDER #1 | Fair | Planned Maintenance | 150 | 10:30 Transfer Load Petani fdr #1 to Temporary Petani fdr #3. Man.Opened Petani OCB fdr#1 11:39 Man.Closed Petani OCB fdr#1 after Finished Replaced 300KVA TX at well Petani #53 and Petani #122. Cause: Planned maintenance. |  | 1 | 10:30 | Morning | Friday | 2017 | 9
6701 | 2017-09-15 11:10 | 2017-09-15 11:10 | MINAS POWER PLANT |  |  | - | 11:10 Started Up MGT #5 and On Line at 11:20 To restore the load. (CGT #1 will be S/D for S/B). |  | 1 | 11:10 | Morning | Friday | 2017 | 9
6702 | 2017-09-15 13:55 | 2017-09-15 13:55 | CENTRAL DURI POWER PLANT |  |  | - | Off line and then S/D CGT #1 for S/B. |  | 1 | 13:55 | Afternoon | Friday | 2017 | 9
6703 | 2017-09-15 15:21 | 2017-09-15 15:21 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 0 | 15:21 Sintong fdr #2 load dropped 118A (149-31A) ). Not checked yet |  | 1 | 15:21 | Afternoon | Friday | 2017 | 9
6704 | 2017-09-15 15:21 | 2017-09-16 14:14 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found Recl. 28-AF-02 T/R 3x, Ctr: 1517-1520, R/F : 50 @1 Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 15:21 | Afternoon | Friday | 2017 | 9
6705 | 2017-09-15 16:10 | 2017-09-15 16:10 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 0 | OKB fdr #2 load dropped 108A (202-94A). Not checke yet. |  | 1 | 16:10 | Afternoon | Friday | 2017 | 9
6706 | 2017-09-15 16:10 | 2017-09-18 05:23 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 0 | Checked and found OKB Fdr#2 Found Nothing Cause : Unidentified. |  | 1 | 16:10 | Afternoon | Friday | 2017 | 9
6707 | 2017-09-16 16:45 | 2017-09-16 16:45 | 13.8KV DURI FIELD FEEDER #4 | Fair | Transformer Failure | 14 | 16:45 It was reported unbalance voltage o/p 07 V5 10. 17:00 Checked and found low voltage for 112.5KVA TX. (well be continued to check tomorrow). Suspected TX failure. |  | 1 | 16:45 | Afternoon | Saturday | 2017 | 9
6708 | 2017-09-16 16:45 | 2017-09-19 10:50 | 13.8KV DURI FIELD FEEDER #4 | Fair | Transformer Failure | 14 | Replaced 112.5KVA Tx with the same size on Pole 07-V5-10 Cause : Transformer failure. (See PIDOD on 19 Sep at 10:50). |  | 1 | 16:45 | Afternoon | Saturday | 2017 | 9
6709 | 2017-09-16 22:09 | 2017-09-16 22:09 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 27 | Pinang fdr #1 Load dropped 21A (170-149) It was reported 28 Wells were Down. Not checked yet. |  | 1 | 22:09 | Night | Saturday | 2017 | 9
6710 | 2017-09-16 22:09 | 2017-09-18 15:20 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 27 | Checked & found, Pinang VCB fdr # 1 counter & R/F did not operate. Patrolled the line but found nothing, Cause: Unidentified. |  | 1 | 22:09 | Night | Saturday | 2017 | 9
6711 | 2017-09-17 05:39 | 2017-09-17 05:39 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Lightning Arrester | 0 | 05:39 Dumai 4160V VCB fdr #1 T/LO. Patrolled the line and found @2 broken Jumper LA o/p W-21. Isolated @2 broken Jumper, Ctr: 277-278 R/F: 50 @1, @3. 09:13 Blocked and closed Dumai 4160V VCB fdr #1, then released the block. Cause: Lightning Arrester. |  | 1 | 5:39 | Morning | Sunday | 2017 | 9
6712 | 2017-09-17 10:50 | 2017-09-17 10:50 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 5 | 10:50 Open LBS 32 AZ 01 d/s Ketigul fdr #1. Three wells down during the JOB. Adjusted Tapping 50KVA TX at Tilan Fery. 11:20 Closed LBS 32 AZ 01. Cause: Plan Maintenance. |  | 1 | 10:50 | Morning | Sunday | 2017 | 9
6713 | 2017-09-17 13:31 | 2017-09-17 13:31 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Fair | Unidentified | 0 | 13:31 Dumai 4160 KV VCB #5 T/R 1X. Not checked yet. |  | 1 | 13:31 | Afternoon | Sunday | 2017 | 9
6714 | 2017-09-17 13:31 | 2017-09-21 17:27 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Fair | Unidentified | 0 | Checked and found Dumai 4160 KV VCB #5 T/R 1X Counter:279-280 R/F: 51@1,@3. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 13:31 | Afternoon | Sunday | 2017 | 9
6715 | 2017-09-18 06:21 | 2017-09-18 06:21 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 13 | S.Bekasap fdr#1 Load dropped 60A(128-68A) Not checked yet. |  | 1 | 6:21 | Morning | Monday | 2017 | 9
6716 | 2017-09-18 06:21 | 2017-09-20 17:07 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 13 | Checked and found Recloser: 37-BG-48 T/R 1x Counter:170-171 R/F: 51. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 6:21 | Morning | Monday | 2017 | 9
6717 | 2017-09-18 10:46 | 2017-09-18 10:46 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 225 | 10:46 Manual Open Rangau 13.8KV OCB fdr #2. Replaced TX at Well Jorang #16 & Jorang #17. Replaced bearing insulation o/p 22-BB-01. 15:05 Closed Rangau 13.8KV VCB fdr #2. Cause : plant maintenance. |  | 1 | 10:46 | Morning | Monday | 2017 | 9
6718 | 2017-09-18 11:15 | 2017-09-18 11:15 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Planned Maintenance | 5 | 11:15 Open LBS 04-06-01B d/s C.Duri fdr #9. Repair Hot Spot o/p 04-01-02. 11:40 Closed LBS 04-06-01B. Cause:Planned Maintenance. |  | 1 | 11:15 | Morning | Monday | 2017 | 9
6719 | 2017-09-18 11:19 | 2017-09-18 11:19 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 227 | 11:19 Manually open 3D fdr #4. Replaced Recloser 2D-38 & repair Hot spot. 14:45 Closed 3D fdr #4. Counter: 87. Cause: Plant Maintenance. |  | 1 | 11:19 | Morning | Monday | 2017 | 9
6720 | 2017-09-18 14:00 | 2017-09-18 14:00 | CENTRAL DURI POWER PLANT |  |  | - | 14:00 S/U CDGT #1 on line the system at :14:22. |  | 1 | 14:00 | Afternoon | Monday | 2017 | 9
6721 | 2017-09-18 15:19 | 2017-09-18 15:19 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Planned Maintenance | 0 | 15:19 Manually open Recloser 08-M3-38 d/s C.Duri fdr #2. Replaced b/o fuse for 112.5 KVA TX o/p 08-M3-03. 15:24 Closed Recloser 08-M3-38. Cause: Plant Maintenance. |  | 1 | 15:19 | Afternoon | Monday | 2017 | 9
6722 | 2017-09-18 15:45 | 2017-09-18 15:45 | MINAS POWER PLANT |  |  | - | 15:45 MGT #3 offline and shutdown. |  | 1 | 15:45 | Afternoon | Monday | 2017 | 9
6723 | 2017-09-18 15:45 | 2017-09-18 15:45 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Planned Maintenance | 0 | 15:45 Open Recloser 01-02-34 d/s C.Duri fdr #3. Replaced @3, b/o fuse for 112.5 KV TX o/p 01-02-02. 15:56 Closed recloser 01-02-34. Cause: Plant Maintenance. |  | 1 | 15:45 | Afternoon | Monday | 2017 | 9
6724 | 2017-09-18 16:45 | 2017-09-18 16:45 | MINAS POWER PLANT |  |  | - | 16:45 MGT #5 offline and shutdown. |  | 1 | 16:45 | Afternoon | Monday | 2017 | 9
6725 | 2017-09-18 20:12 | 2017-09-18 20:12 | 13.8KV MENGGALA FEEDER #1 | Heavy Rain | Unidentified | 0 | Menggala Fdr#1 Load dropped 138A (180-42A). Not checked yet. |  | 1 | 20:12 | Night | Monday | 2017 | 9
6726 | 2017-09-18 20:12 | 2017-09-19 20:12 | 13.8KV MENGGALA FEEDER #1 | Heavy Rain | Unidentified | 0 | Checked & found, Recl. 19-AN-04 T/R 1x ctr: 341-342. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 20:12 | Night | Monday | 2017 | 9
6727 | 2017-09-19 06:33 | 2017-09-19 06:33 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | N.Duri VCB Fdr # 7 T/R 1X Not Checked yet. | 11111 | 1 | 6:33 | Morning | Tuesday | 2017 | 9
6728 | 2017-09-19 06:33 | 2017-09-21 17:24 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | Checked and found N.Duri VCB Fdr # 7 T/R 1x Counter: 100-101 R/F: 51@1. Patrolled the line found nothing. Cause: Unidentified. | 11111 | 1 | 6:33 | Morning | Tuesday | 2017 | 9
6729 | 2017-09-19 07:30 | 2017-09-19 07:30 | 44KV MINAS - RUMBAI LINE | Fair | Unidentified | 0 | 44KV Line Minas-Rumbai ACB#21 T/R 1x. Not patrolled yet. |  | 1 | 7:30 | Morning | Tuesday | 2017 | 9
6730 | 2017-09-19 07:30 | 2017-09-21 19:19 | 44KV MINAS - RUMBAI LINE | Fair | Unidentified | 0 | Checked and found 44KV Line Minas-Rumbai ACB#21 T/R 1x. Counter: 83-84 R/F: 51G @2. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 7:30 | Morning | Tuesday | 2017 | 9
6731 | 2017-09-19 10:28 | 2017-09-19 10:28 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 731 | 10:28 Open Bekasap VCB fdr#2. Repaired Hot spot Recl. 37BD40. Replaced Broken LA at T/P Bekasap#74. Replaced Broken PIN Insulator o/p 37BD54. 13:38 Blocked & closed Bekasap fdr#2, then release the block. Cause: Maintenance Job. | 11111 | 1 | 10:28 | Morning | Tuesday | 2017 | 9
6732 | 2017-09-19 10:50 | 2017-09-19 10:50 | 13.8KV DURI FIELD FEEDER #4 | Fair | Planned Maintenance | 21 | 10:50 Open Recl. 07-V5-02 (D.Field fdr#4). Replaced 112.5 Kva Tx o/p 07-V5-10. 12:15 Blocked & closed Recl. 07-V5-02. 13:30 It was reported no power o/p 07-V5-12. 15:11 Open D.Field fdr#4 for by-pass Recl. 07-V5-02. 15:15 Blocked & closed D.Field fdr#4, then release the block. Cause: Maintenance Job. |  | 1 | 10:50 | Morning | Tuesday | 2017 | 9
6733 | 2017-09-19 16:37 | 2017-09-19 16:37 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified (Fuse) | 28 | It was reported B/O at well So.Balam #49 Not checked yet. |  | 1 | 16:37 | Afternoon | Tuesday | 2017 | 9
6734 | 2017-09-19 16:37 | 2017-09-20 09:30 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified (Fuse) | 28 | Replaced @1@2 B/O fuse for 150Kva with the same size. Cause: Unidentified Fuse. |  | 1 | 16:37 | Afternoon | Tuesday | 2017 | 9
6735 | 2017-09-20 10:15 | 2017-09-20 10:15 | 13.8KV CENTRAL DURI FEEDER #11 | Fair | Planned Maintenance | 25 | 10:15 Opened LBS: 05-M7-24. For replacing Recloser: 05-M6-23A. 14:26 Closed LBS: 05-M7-24. 14:33 Manually closed Recloser: 05-M6-23A. Cause: Plan Maintenance. |  | 1 | 10:15 | Morning | Wednesday | 2017 | 9
6736 | 2017-09-20 14:04 | 2017-09-20 14:04 | 13.8KV 8C FEEDER #1 | Fair | Lightning Arrester | 232 | 14:04 8C VCB fdr #1 T/O. 15:41 Checked and found 8C VCB fdr #1 T/LO Counter: 668-672 R/F: 51N. 16:15 Patrolled the line found @1 broken Lightning Arrester on pole 9C-15. and spark on Capacitor bank on pole 9C-08. Opened HLC of Capacitor bank on pole 9C-08. 16:51 Blocked and closed 8C VCB fdr #1 --> Success and then released the block. Cause: Broken Lightning Arrester. |  | 1 | 14:04 | Afternoon | Wednesday | 2017 | 9
6737 | 2017-09-20 15:15 | 2017-09-20 15:15 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Planned Maintenance | 66 | 15:15 Manually opened Recloser:06-Q3-02. Due to replaced @1,@2 b/o fuse on pole 06-Q3-11. 15:20 Manually closed Recloser: 06-Q3-02. Cause: Plan maintenance. |  | 1 | 15:15 | Afternoon | Wednesday | 2017 | 9
6738 | 2017-09-20 16:53 | 2017-09-20 16:53 | MINAS POWER PLANT | Fair |  | - | 16:53 S/U MGT #3 and then On Line the unit at 17:05. |  | 1 | 16:53 | Afternoon | Wednesday | 2017 | 9
6739 | 2017-09-21 06:21 | 2017-09-21 06:21 | 13.8KV S. BALAM FEEDER #1 | Fair | Suspension Insulator | 135 | So. Balam 13.8KV VCB fdr #1 T/R 1X. Not checket yet. |  | 1 | 6:21 | Morning | Thursday | 2017 | 9
6740 | 2017-09-21 06:21 | 2017-09-24 08:21 | 13.8KV S. BALAM FEEDER #1 | Fair | Suspension Insulator | 135 | Checked & found Balam VCB fdr#1 T/R 1x Ctr:388-389 R/F:51N. Patrolled the line & found @2 Broken Suspension o/p 16 Z 04. Cause : Suspension Insulator. |  | 1 | 6:21 | Morning | Thursday | 2017 | 9
6741 | 2017-09-21 11:05 | 2017-09-21 11:05 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 12 | 11:05 Opened LBS 35-AJ-01 D/S Ketigul fdr #1. Due to 50 Kva Tx with 25 Kva Tx on pole 35-AJ-19. 3 wells were OFF during this job (Tilan #14 , 16 , 28). 14:20 Closed LBS 35-AJ-01. Cause: Plan Maintenance. |  | 1 | 11:05 | Morning | Thursday | 2017 | 9
6742 | 2017-09-21 14:10 | 2017-09-21 14:10 | MINAS POWER PLANT |  |  | - | 14:10 S/U MGT #1 and then On Line the unit at 14:50. |  | 1 | 14:10 | Afternoon | Thursday | 2017 | 9
6743 | 2017-09-21 15:20 | 2017-09-21 15:20 | MINAS POWER PLANT |  |  | - | 15:20 Off Line MGT #3 and then S/D the unit for Stand By. |  | 1 | 15:20 | Afternoon | Thursday | 2017 | 9
6744 | 2017-09-22 00:20 | 2017-09-22 00:20 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Duri Comy 13.8KV ACB#26 fdr#3 T/R 1X. Not checked yet. |  | 1 | 0:20 | Night | Friday | 2017 | 9
6745 | 2017-09-22 00:20 | 2017-09-24 15:52 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Cheked and found Duri Comy 13.8KV ACB#26 fdr#3 T/R 1x Counter: 59-60 R/F: 51N. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 0:20 | Night | Friday | 2017 | 9
6746 | 2017-09-22 09:20 | 2017-09-22 09:20 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Construction Job | 0 | 09:20 Manually opened Recloser: 36-CT-10 D/S CKBS fdr #1. Due to opened Hot Line Clamp on pole 36-CT-12 for Rig activity at well KB #82. 2 wells were OFF during this job (KB #33,91). 09:47 Manually closed Recloser: 36-CT-10. Cause: Construction Job. |  | 1 | 9:20 | Morning | Friday | 2017 | 9
6747 | 2017-09-22 11:32 | 2017-09-22 11:32 | 13.8KV SURAM FEEDER #1 | Fair | Unidentified | 0 | Suram OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 11:32 | Morning | Friday | 2017 | 9
6748 | 2017-09-22 11:32 | 2017-09-24 11:32 | 13.8KV SURAM FEEDER #1 | Fair | Unidentified | 0 | Checked & found Suram VCB fdr#1 T/R 1x Ctr:111-112 R/F 51@3. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 11:32 | Morning | Friday | 2017 | 9
6749 | 2017-09-22 11:41 | 2017-09-22 11:41 | CENTRAL DURI SW GEAR 3-4 | Fair | Under investigation | 0 | 11:41 C.Duri SW GR 13.8 Kv ACB #34 (Tx #3) T/O. 11:43 Closed C. Duri SW GR 13.8 Kv ACB #34. Cause: Under Investigation. |  | 1 | 11:41 | Morning | Friday | 2017 | 9
6750 | 2017-09-22 15:48 | 2017-09-22 15:48 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 118 | 15:48 C Duri SW GR ACB #21 (C Duri fdr #4) T/O. 15:50 Checked and found C Duri SW GR ACB #21 (C Duri fdr #4) T/LO Counter: 489-493 R/F: 51N. (All load CDuri fdr #8 transfer to C Duri fdr #4). 16:17 Opened LBS: 04-08-29 separated C Duri fdr #4 and C Duri fdr #8. 16:18 Blocked and manually closed C Duri fdr #4 --> Success and then released the block. 16:25 Blocked and manually closed C Duri fdr #8 --> Success and then released the block. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 15:48 | Afternoon | Friday | 2017 | 9
6751 | 2017-09-22 17:25 | 2017-09-22 17:25 | MINAS POWER PLANT | Fair | Under investigation | 0 | 17:25 MGT #10 Trip by alarm Inlet Guide Vane control Trip. 18:00 S/U MGT#10, then On Line the unit at 18:19. |  | 1 | 17:25 | Afternoon | Friday | 2017 | 9
6752 | 2017-09-23 04:40 | 2017-09-23 04:40 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 04:40 It was reported b/o fuse for Tx o/p 05-P2-01 D/S C Duri #14. 14:10 Checked and found @2 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (monkey). |  | 1 | 4:40 | Morning | Saturday | 2017 | 9
6753 | 2017-09-23 09:25 | 2017-09-23 09:25 | 13.8KV SINTONG FEEDER #1 | Fair | Construction Job | 0 | 09:25 Opened LBS 26-AE-06 D/S Sintong fdr #1 (Load 53A). Opened Hot Line Clamp on terminal pole well Seruni #37. Well Seruni #37 was OFF during this job. Due to Tie in new well Seruni #45. 10:10 Closed LBS 26-AE-06. 16:00 Opened LBS 26-AE-06. Closed Hot Line Clamp on terminal pole well Seruni #37. Cause: Construction job. |  | 1 | 9:25 | Morning | Saturday | 2017 | 9
6754 | 2017-09-23 14:35 | 2017-09-23 14:35 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Animal | 0 | 14:35 It was reported b/o fuse on pole 03-02-17 D/S C Duri fdr #6. Checked and found @2 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (monkey). |  | 1 | 14:35 | Afternoon | Saturday | 2017 | 9
6755 | 2017-09-23 17:37 | 2017-09-23 17:37 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 0 | D Field SW GR ACB #41 (D Field fdr #1) T/R 1x Counter: 681-682 R/F: 51N. Not patrolled yet. |  | 1 | 17:37 | Afternoon | Saturday | 2017 | 9
6756 | 2017-09-23 17:37 | 2017-09-25 08:00 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 0 | Checked and found D. Field Switch Gear ACB #34 T/R 1x Ctr:681-682 R/F:@1 51 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:37 | Afternoon | Saturday | 2017 | 9
6757 | 2017-09-24 09:39 | 2017-09-24 09:39 | CENTRAL DURI POWER PLANT |  |  | - | 09:39 S/U CDGT #4 and then Online the unit at. 10:05. |  | 1 | 9:39 | Morning | Sunday | 2017 | 9
6758 | 2017-09-24 15:53 | 2017-09-24 15:53 | 13.8KV DARLING VCB FEEDER #6 | Fair | Animal | 0 | 15:53 It was reported b/o fuse for Tx o/p 05-M5-20 d/s Darling fdr #6. 16:53 Checked and found @2, @3 b/o fuse for 112.5 Kv Tx. Perform TTR and megger found good reading. Replace b/o fuse above with the same size and energized the Tx. Cause : Annimal ( Monkey ). |  | 1 | 15:53 | Afternoon | Sunday | 2017 | 9
6759 | 2017-09-24 17:47 | 2017-09-24 17:47 | CENTRAL DURI POWER PLANT |  |  | - | 17:47 Off line CGT#2, then S/D the unit for S/B. 17:50 Closed Tie Breaker ACB#19. |  | 1 | 17:47 | Afternoon | Sunday | 2017 | 9
6760 | 2017-09-25 07:14 | 2017-09-25 07:14 | 13.8KV BANGKO FEEDER #4 | Fair | Suspension Insulator | 55 | Bangko OCB fdr #4 T/R 1x. Not checked yet. |  | 1 | 7:14 | Morning | Monday | 2017 | 9
6761 | 2017-09-25 07:14 | 2017-09-26 07:14 | 13.8KV BANGKO FEEDER #4 | Fair | Suspension Insulator | 55 | Checked & found, Bangko VCB fdr #4 T/R 1x ctr: 10-11 R/F: 51N @3. Patrolled the line & found, @3 Flash-over Suspension Insulator on Pole 25-Z-02. Cause: Suspension Insulator. |  | 1 | 7:14 | Morning | Monday | 2017 | 9
6762 | 2017-09-25 09:59 | 2017-09-25 09:59 | 13.8KV S. BALAM FEEDER #1 | Cloudy | Unidentified | 107 | So Balam VCB fdr #1 T/R 1x. So Balam fdr #2 load dropped 95A (97-2A) EOR pump. So Balam fdr #3 load dropped 70A (70-0A) EOR pump. So Balam fdr #4 load dropped 15A (201-186A). Not checked yet. |  | 1 | 9:59 | Morning | Monday | 2017 | 9
6763 | 2017-09-25 09:59 | 2017-09-26 09:59 | 13.8KV S. BALAM FEEDER #1 | Cloudy | Unidentified | 107 | Checked & found, S. Balam VCB fdr #1 T/R 1x ctr: 389-390 R/F: 51N @1 Patrolled the lin but found nothing. Cause: Unidentified. |  | 1 | 9:59 | Morning | Monday | 2017 | 9
6764 | 2017-09-25 10:50 | 2017-09-25 10:50 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 10 | 10:50 It was reported b/o fuse O/P 03-0-19SAA (CD fdr #14). 15:45 Checked and found @3 b/o fuse for 112.5 Kva Tx. Replace b/o fuse above with the same size & energized the Tx. Cause : Unidentified fuse. |  | 1 | 10:50 | Morning | Monday | 2017 | 9
6765 | 2017-09-25 18:14 | 2017-09-25 18:14 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Pin Insulator | 483 | 18:14 C Duri 13.8KV ACB fdr #4 T/LO. 18:16 Checked and found C Duri SW GR ACB #21 (C Duri fdr #4) T/LO Counter:493-497 R/F: 51N. (All load CDuri fdr #8 transfer to C Duri fdr #4). Opened LBS: 04-08-29 separated C Duri fdr #4 and C Duri fdr #8. Blocked and closed C Duri fdr #4 --> Success and then released the block. 18:50 C.Duri 13.8KV ACB fdr #4 T/R 5X. 18:53 C.Duri 13.8KV ACB fdr#4 T/O (on block). Patrolled the line and found @1 broken insulator of By Pass recl. 09-Q1-06. Isolated @1 broken insulator of By Pass recl. 09-Q1-06. 19:23 Blocked and closed C Duri fdr #8 --> Success and then released the block. 20:20 Blocked and Closed C.Duri fdr #4 --> Success and then released the block. 20:24 Closed LBS 04-08-09 --> part load C.Duri fdr #4 de feed from C.Duri fdr #8. Cause: Broken insulator. Production loss: 266 Bbls / 187 Wells ---->d/s C. Duri fdr #4. 146 Bbls / 186 Wells ---->d/s C. Duri fdr #8. ----------------------------------------------------+ TOTAL :412 Bbls / 373 Wells. | 1111 | 1 | 18:14 | Afternoon | Monday | 2017 | 9
6766 | 2017-09-26 09:52 | 2017-09-26 09:52 | 4 BRAVO SUBSTATION | Fair | Construction Job | 0 | Switching De-Energized 4B Fdr #4, 5, 6. 09:38 Man Open 4B Fdr# 6 09:43 Man Open 4B Fdr #4 15:53 Man open 4B Fdr # 5 For Tie In HPS Project at GS-6. 27 Sept 2017 -------------------------------- Reenergized 4B Fdr # 4,5,6 11:50 Closed 4B Fdr # 5 13:36 Closed 4B Fdr # 4 14:05 Closed 4B Fdr # 6 |  | 1 | 9:52 | Morning | Tuesday | 2017 | 9
6767 | 2017-09-26 13:52 | 2017-09-26 13:52 | 13.8KV PINANG FEEDER #1 | Cloudy | Unidentified | 26 | Pinang OCB fdr#1 T/R 1x, Checked & found Pinang OCB fdr#1 Ctr: 421-422, R/F: 51N. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 13:52 | Afternoon | Tuesday | 2017 | 9
6768 | 2017-09-26 21:10 | 2017-09-26 21:10 | MINAS POWER PLANT |  |  | - | 21:10 Off Line MGT#1, then S/D the unit for S/B. 21:08 Closed Tie Breaker ACB#16. |  | 1 | 21:10 | Night | Tuesday | 2017 | 9
6769 | 2017-09-27 08:51 | 2017-09-27 08:51 | 13.8KV DURI FIELD FEEDER #2 | Fair | Recloser - Control Recloser | 36 | 08:51 D Field ACB Fdr #2 Load drop 98A (273-175A). Checked and found recl. 07-U3-21 T/SO. Ctr.157-158. 09:31 Manual Closed recl. 07-U3-21 Patrolled the line and nothing found. Cause : Control recloser. |  | 1 | 8:51 | Morning | Wednesday | 2017 | 9
6770 | 2017-09-27 10:58 | 2017-09-27 10:58 | 13.8KV BEKASAP FEEDER #3 | Fair | Construction Job | 0 | 10:58 Open LBS 38-BD-94. (d/s BKS Fdr #3). Change 300KvaTx at well Bks #146, 159. 12:28 Closed the LBS after finished install Tx. Cause : Planning project. |  | 1 | 10:58 | Morning | Wednesday | 2017 | 9
6771 | 2017-09-27 11:34 | 2017-09-27 11:34 | 13.8KV NORTH DURI FEEDER #11 | Fair | Planned Maintenance | 108 | 11:34 Man. Open LBS.13-G5-138. to S/D line under Recl.13-F3-49 (D/S ND Fdr #11) 13:25 Closed back the LBS after finish replace broken bushing of Recloser on Pole 13-F3-49. Cause : Planned maintenance. |  | 1 | 11:34 | Morning | Wednesday | 2017 | 9
6772 | 2017-09-27 14:55 | 2017-09-27 14:55 | 13.8KV 5B FEEDER #3 | Fair | Planned Maintenance | 15 | 14:55 Man. opened 5B Fdr #3 for replace b/o fuse at. well 4C-69E. 15:05 Man. Closed the feeder after replaced the fuse the same size for 500Kva. Cause : Unidentified. |  | 1 | 14:55 | Afternoon | Wednesday | 2017 | 9
6773 | 2017-09-27 14:58 | 2017-09-27 14:58 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 97 | 14:58 It was reported b/o fuse o/p. 10-K2A-04 (ND Fdr #2). Cause : Not checked yet. |  | 1 | 14:58 | Afternoon | Wednesday | 2017 | 9
6774 | 2017-09-27 14:58 | 2017-09-30 15:15 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 97 | Replaced @1 b/o fuse for 112.5KVA Tx on Pole 10-K2A-04 with the same size then energized the Tx. Cause: Unidentified (Fuse). (See Pidod; 30 Sep at 15:15) |  | 1 | 14:58 | Afternoon | Wednesday | 2017 | 9
6775 | 2017-09-27 16:25 | 2017-09-27 16:25 | CENTRAL DURI POWER PLANT |  |  | - | 16:25 CDGT #2 S/U the unit and Online at.17:05. To back up CDGT #5 due to reboote computer S. |  | 1 | 16:25 | Afternoon | Wednesday | 2017 | 9
6776 | 2017-09-27 16:30 | 2017-09-27 16:30 | 13.8KV DURI FIELD FEEDER #2 | Fair | Broken Fuse Cut Out | 0 | 16:30 It was reported b/o fuse o/p. 06-S01-10 (DF Fdr #2). Cause : Not checked yet. |  | 1 | 16:30 | Afternoon | Wednesday | 2017 | 9
6777 | 2017-09-27 16:30 | 2017-09-29 14:00 | 13.8KV DURI FIELD FEEDER #2 | Fair | Broken Fuse Cut Out | 0 | 14:00 Manual Opened Recloser 06.S1.02. D/S DF #2. for repl. fuse o/p 06.S1.10. (same well were off) 14:55 Manual Closed Recloser 06.S1.02. after repl. the fuse. Cause : Planned maintenance. |  | 1 | 16:30 | Afternoon | Wednesday | 2017 | 9
6778 | 2017-09-27 17:21 | 2017-09-27 17:21 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 17:21 CDGT #5 T/O while reboote computer S No Load Sheeding. |  | 1 | 17:21 | Afternoon | Wednesday | 2017 | 9
6779 | 2017-09-28 07:57 | 2017-09-28 07:57 | 13.8KV BEKASAP FEEDER #5 | Fair | Unidentified | 274 | 07:57 Bks Fdr #5 T/R 1x. Bks Fdr #2 Load drop 34A (188-154A). Bks Fdr #3 Load drop 123A (147-24A ). Bks Fdr #6 Load drop 57A ( 82-25A ). Sobek Fdr #1 Load drop 21A (135-114A). |  | 1 | 7:57 | Morning | Thursday | 2017 | 9
6780 | 2017-09-28 07:57 | 2017-04-10 17:35 | 13.8KV BEKASAP FEEDER #5 | Fair | Unidentified | 274 | Checked & found Bekasap VCB fdr#5 T/R 1x, Ctr: 509-510, R/F: 51 @1 Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 7:57 | Morning | Thursday | 2017 | 9
6781 | 2017-09-28 15:56 | 2017-09-28 15:56 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Planned Maintenance | 0 | 15:56 Man. Opened LBS KRC20 (Duri Community Fdr #2). Replace fuse @1. 16:17 Man. Closed LBS KRC20 (Duri Community Fdr #2).after Replace fuse @1. |  | 1 | 15:56 | Afternoon | Thursday | 2017 | 9
6782 | 2017-09-29 01:06 | 2017-09-29 01:06 | 13.8KV MINAS FEEDER #4 | Cloudy | Lightning | 111 | Minas ACB 1 (fdr#4) T/R 1x. Minas fdr#3 load dropped 180A (306-126A). Not checked yet. |  | 1 | 1:06 | Night | Friday | 2017 | 9
6783 | 2017-09-29 01:06 | 2017-02-10 16:06 | 13.8KV MINAS FEEDER #4 | Cloudy | Lightning | 111 | Checked & found, Minas ACB fdr #4 T/R 1x ctr: 76-77 R/F: 51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 1:06 | Night | Friday | 2017 | 9
6784 | 2017-09-29 06:44 | 2017-09-29 06:44 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy | Lightning Arrester | 225 | 06:44 So Bekasap fdr #1 load dropped 87A (135-48A). 08:30 Checked and found Recl. 34-BI-18 T/SO Counter: 161-162 R/F: 51N. Patrolled the Line, found @ 1 broken LA on pole 32-BE-08. 09:20 Blocked and Closed Recl.34-BI-18 --> Success Cause : Broken Lightning Arrester. |  | 1 | 6:44 | Morning | Friday | 2017 | 9
6785 | 2017-09-29 07:57 | 2017-09-29 07:57 | 13.8KV CENTRAL DURI FEEDER #6 | Drizzle | Unidentified | 0 | C.Duri ACB #23 (fdr#6) T/R 1x R/F 51 @2 and @3 Counter: 480-481. Not checked yet. |  | 1 | 7:57 | Morning | Friday | 2017 | 9
6786 | 2017-09-29 07:57 | 2017-03-10 07:57 | 13.8KV CENTRAL DURI FEEDER #6 | Drizzle | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:57 | Morning | Friday | 2017 | 9
6787 | 2017-09-29 10:28 | 2017-09-29 10:28 | 13.8KV BATANG FEEDER #2 | Fair | Planned Maintenance | 0 | 10:28 Manually opened Batang OCB fdr #2. Due to Huff Puff moving from well Rantau Bais #07 to Rantau Bais #16. 11:30 Manually blocked and closed Batang OCB fdr #2 and then released the block. Cause: Planned Maintenance. |  | 1 | 10:28 | Morning | Friday | 2017 | 9
6788 | 2017-09-29 10:28 | 2017-09-29 10:28 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 471 | It was reported b/o fuse at well Pagar #27. D/S Katigul Fdr #2. Not checked yet. |  | 1 | 10:28 | Morning | Friday | 2017 | 9
6789 | 2017-09-29 10:28 | 2017-05-10 15:06 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 471 | 15:06 Manually open LBS 30 AN 38 (d/s Ketigul fdr#2) -----> Closed at 15:48. Replaced 300KVA TX at well Pagar #27. Cause: Transformer Failure. See Pidod; 05 Oct at 15:06:00 |  | 1 | 10:28 | Morning | Friday | 2017 | 9
6790 | 2017-09-29 11:25 | 2017-09-29 11:25 | 13.8KV NORTH DURI FEEDER #2 | Fair | Transformer Failure | 36 | It was reported b/o fuse o/p 10-J4-09. D/S ND Fdr #2. Not checked yet. |  | 1 | 11:25 | Morning | Friday | 2017 | 9
6791 | 2017-09-29 11:25 | 2017-07-10 09:26 | 13.8KV NORTH DURI FEEDER #2 | Fair | Transformer Failure | 36 | 09:26 Manual open LBS 10 J4A 07 D/S ND Fdr #10 (Fdr #2). Replaced 112.5 Kva Tx o/p 10 J4 09. Cause : Transformer Failure. See PIDOD; on 07 Oct at 09:26:00 |  | 1 | 11:25 | Morning | Friday | 2017 | 9
6792 | 2017-09-29 18:00 | 2017-09-29 18:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Broken Fuse Holder | 0 | It was reported b/o fuse at well Kulim #53 D/S CD Fdr #1. Not checked yet. |  | 1 | 18:00 | Afternoon | Friday | 2017 | 9
6793 | 2017-09-29 18:00 | 2017-02-10 10:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Broken Fuse Holder | 0 | 10:50 Man Opened Recl.38.AS.09 (d/s Cduri fdr#1). to replace Broken Fuse Holder at pole Well Kulin #53. 12:15 Man Closed back the Reclosser Cause: Broken Fuse Holder. (See PIDOD; 02 Oct at 10:50) |  | 1 | 18:00 | Afternoon | Friday | 2017 | 9
6794 | 2017-09-30 09:40 | 2017-09-30 09:40 | 13.8KV MENGGALA FEEDER #1 | Fair | Construction Job | 0 | 09:40 Man. Opened Manggala OCB Fdr#1 to Cut jumper to relocated pole at well Meno #21. 10:22 Man. Closed Manggala OCB Fdr#1 after Cut the jumper toward pole above. 16:16 Man. Opened Menggala OCB fdr#1 to Connect Jumper to new T/OP Well Meno#21. 17:20 Man. Closed Menggala OCB fdr#1 after Connected the Jumper toward Well above. Cause: Construction Job. |  | 1 | 9:40 | Morning | Saturday | 2017 | 9
6795 | 2017-09-30 10:05 | 2017-09-30 10:05 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Powerline - Conductor | 0 | 10:00 Open LBS KRC#2 (d/s D Com fdr#2) to repair under ground cable & FM team replaced Main breaker. 16:16 Closed back LBS KRC#2 after finished fixed the Problem. Cause: conductor (Under ground cable). |  | 1 | 10:05 | Morning | Saturday | 2017 | 9
6796 | 2017-09-30 14:45 | 2017-09-30 14:45 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Construction Job | 0 | 14:45 Manual opened LBS 36.CU.5 d/s CKB #1 Open/Closed HLC for Project (Semen plug well KB #82) 15:30 Manual closed LBS 36.CU.5 d/s CKB #1. Cause : Construction Job. |  | 1 | 14:45 | Afternoon | Saturday | 2017 | 9
6797 | 2017-09-30 15:15 | 2017-09-30 15:15 | 13.8KV NORTH DURI FEEDER #2 | Fair | Planned Maintenance | 0 | 15:15 Man. Opened Recl. 10.K2A.19 (d/s N Duri fdr#2). 15:40 Checked & found @1 b/o fuse for 112.5KVATX o/p 10.K2A.16 Replaced the fuse with the same size, then Closed the TX. Man Closed the Recloser above after replaced the Fuse. Cause: Plan maintenance. |  | 1 | 15:15 | Afternoon | Saturday | 2017 | 9
6798 | 2017-09-30 15:25 | 2017-03-09 11:18 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Unidentified (Fuse) | 260 | Checked and found @1, @2 b/o fuse for 112.5KVA TX o/p 05 N5 18. Replaced b/o fuse above with same size, then energized the TX. Cause: Un identified fuse. See Pidod 03 Oct at 11:00 |  | 1 | 15:25 | Afternoon | Saturday | 2017 | 9
6799 | 2017-09-30 15:25 | 2017-09-30 15:25 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Unidentified (Fuse) | 260 | It was reported Unbalance & Low voltage O/P 05-N5-18 (d/s Darling fdr#3, Move from C.Duri fdr#10) Checked & found Visually the Fuses is good, will be checked the TX soon. Cause: Not checked yet. |  | 1 | 15:25 | Afternoon | Saturday | 2017 | 9
6800 | 2017-09-30 17:00 | 2017-09-30 17:00 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 26 | 15:15 It was reported B/O fuse O/P 02.08.02 (d/s C duri fdr36). Not checked yet. |  | 1 | 17:00 | Afternoon | Saturday | 2017 | 9
6801 | 2017-09-30 17:00 | 2017-01-10 15:10 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 26 | 15:10 Man Open C.Duri ACB Fdr# 6 To Replace @1 Broken Fuse Link o/p 02 08 02 15:15 Manually closed C.Duri ACB 23 (fdr #6). Cause: Unidentified (Fuse). |  | 1 | 17:00 | Afternoon | Saturday | 2017 | 9
6802 | 2017-01-10 10:11 | 2017-01-10 10:11 | 13.8KV MENGGALA FEEDER #2 | Fair | Construction Job | 0 | 10:11 Man Open Recl 26 AK 02 D/S Manggala Fdr # 2 To open HLC o/p 26 AK 12 for Relocated terminal pole Ubi # 30 10:28 Closed Recl 26 AK 02. Cause: Planned Project Construction. |  | 1 | 10:11 | Morning | Tuesday | 2017 | 1
6803 | 2017-01-10 13:49 | 2017-01-10 13:49 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Planned Maintenance | 0 | 13:39 Man Open Recl 30 CZ 23 to replace Fuse PT of Recloser 14:45 Closed Recloser. Cause: Planned Maintenance. |  | 1 | 13:49 | Afternoon | Tuesday | 2017 | 1
6804 | 2017-01-10 15:10 | 2017-01-10 15:10 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Planned Maintenance | 0 | 15:10 Man Open C.Duri ACB Fdr# 6 To Replace @1 Broken Fuse Link o/p 02 08 02 15:15 Manually closed C.Duri ACB 23 (fdr #6). Cause: Plan Maintenance. See PIDOD on 30-Sep at 17:00 |  | 1 | 15:10 | Afternoon | Tuesday | 2017 | 1
6805 | 2017-01-10 15:30 | 2017-01-10 15:30 | 13.8KV DURI FIELD FEEDER #1 | Fair | Pin Insulator | 0 | D.Field VCB # 41 Fdr # 1 T/R 1X Not Checked yet. |  | 1 | 15:30 | Afternoon | Tuesday | 2017 | 1
6806 | 2017-01-10 15:30 | 2017-03-10 15:30 | 13.8KV DURI FIELD FEEDER #1 | Fair | Pin Insulator | 0 | Checked & found, Duri Field ACB #41 fdr #1 T/R 1x ctr: 682-683 R/F: 51N. Patrolled the line & found, @1 broken Pin Insulator on Pole 42 BD 55. Cause: Pin Insulator. |  | 1 | 15:30 | Afternoon | Tuesday | 2017 | 1
6807 | 2017-01-10 15:40 | 2017-01-10 15:40 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 2 | It was reported B/O Fuse o/p 06.Q5.14 D/S CD Fdr#15. Not Checked Yet. |  | 1 | 15:40 | Afternoon | Tuesday | 2017 | 1
6808 | 2017-01-10 15:40 | 2017-03-10 11:38 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 2 | Checked and found @1 b/o fuse for 112.5KVA TX. Replaced b/o fuse above with same size, then energized the TX. Cause: Animal (monkey). See Pidod 03-10-2017 at 11:38 |  | 1 | 15:40 | Afternoon | Tuesday | 2017 | 1
6809 | 2017-01-10 19:12 | 2017-01-10 19:12 | 13.8KV RANGAU FEEDER #1 | Rain and Lightning | Unidentified | 2 | RANGAU OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 19:12 | Night | Tuesday | 2017 | 1
6810 | 2017-01-10 19:12 | 2017-04-10 17:36 | 13.8KV RANGAU FEEDER #1 | Rain and Lightning | Unidentified | 2 | Checked & found Rangau OCB fdr#1 T/R1x, Ctr: 16-17, R/F: 51N. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 19:12 | Night | Tuesday | 2017 | 1
6811 | 2017-01-10 20:28 | 2017-01-10 20:28 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 101 | Nella fdr #1 load dropped 186A (257-81A). Nella GFPC T/R 1x. Not checked yet. |  | 1 | 20:28 | Night | Tuesday | 2017 | 1
6812 | 2017-01-10 20:30 | 2017-01-10 20:30 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Unidentified | 17 | Nella fdr #2 load dropped 24A (120-96A). Not checked yet. |  | 1 | 20:30 | Night | Tuesday | 2017 | 1
6813 | 2017-01-10 20:30 | 2017-03-10 12:30 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Unidentified | 17 | Checked & found, no Recloser operated. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 20:30 | Night | Tuesday | 2017 | 1
6814 | 2017-01-10 23:58 | 2017-01-10 23:58 | 13.8KV 8D FEEDER #4 | Rain and Lightning | Lightning | 0 | 8D OCB fdr #4 T/R 1x. Not checked yet. |  | 1 | 23:58 | Night | Tuesday | 2017 | 1
6815 | 2017-01-10 23:58 | 2017-02-10 23:58 | 13.8KV 8D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, 8D OCB fdr #4 T/R 1x ctr: 1544-1545 R/F: 50 @1, @2, @3. Patrolled the line but found nothing. Cause : Suspected by Lightning. |  | 1 | 23:58 | Night | Tuesday | 2017 | 1
6816 | 2017-01-10 23:58 | 2017-01-10 23:58 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 26 | 8D OCB fdr #5 T/R 1x. 8D fdr #1 load dropped 63A (142-79A). 8D fdr #2 load dropped 18A (103-83A). 8D fdr #3 load dropped 21A (88-67A). 8D fdr #9 load dropped 124A (370-246A) WIP Pump. Not checked yet. |  | 1 | 23:58 | Night | Tuesday | 2017 | 1
6817 | 2017-01-10 23:58 | 2017-02-10 23:58 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 26 | Checked & found, 8D OCB fdr #5 T/R 1x ctr: 566 (did not operated) R/F: 51 Patrolled the line but found nothing. Cause : Suspected by Lightning. |  | 1 | 23:58 | Night | Tuesday | 2017 | 1
6818 | 2017-02-10 09:40 | 2017-02-10 09:40 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 0 | 09:40 Man. Opened Recl. 40.CY.16 (d/s OKB fdr#2). to Check TTR & Megger 300KVATX at well KB# 237. 10:00 Closed Back the Reclosser. after finished the Jobs. Cause : Planned Maintenance. 13:31 Man Opened Recl. 40.CY.16. Replaced 300KVATX with the same size. 13:50 Man Closed back the Recloser, also the TX energized normal. Cause: Planned Maintenance. |  | 1 | 9:40 | Morning | Friday | 2017 | 2
6819 | 2017-02-10 10:01 | 2017-02-10 10:01 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 349 | 10:01 Man. Opened Rangau OCB fdr#2 to Replaced broken Suspention insulator o/p 23.BD.3. 15:12 Man. Closed back Rangau OCB fdr#2 Cause : Planned Maintenance. |  | 1 | 10:01 | Morning | Friday | 2017 | 2
6820 | 2017-02-10 10:27 | 2017-02-10 10:27 | 13.8KV BATANG FEEDER #3 | Fair | Construction Job | 0 | 10:27 Man. Opened Batang OCB fdr#3 Man. Opened Recl. 36.AL.13, and Opened Isolation Switch Load side. to Tie In new well Candi 65B and 44B. 10:39 Man. Closed back Batang OCB fdr#3 and Recl. 36.AL.13 Keep stay Open the isolation switch at Load side, 2 days. Cause: Planned Construction Project. |  | 1 | 10:27 | Morning | Friday | 2017 | 2
6821 | 2017-02-10 10:27 | 2017-04-10 16:36 | 13.8KV BATANG FEEDER #3 | Fair | Construction Job | 0 | 16:36 Man. Opened Batang OCB fdr#3 (after Tie In new well Candi 65B and 44B). 16:49 Closed back Batang OCB fdr#3. 17:00 Closed Recl. 36.AL.13. Cause: Planned Construction Project. |  | 1 | 10:27 | Morning | Friday | 2017 | 2
6822 | 2017-02-10 10:50 | 2017-02-10 10:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 91 | 10:50 Man Opened Recl.38.AS.09 (d/s Cduri fdr#1). to replace Broken FCO at pole Well Kulin #53. 12:15 Man Closed back the Reclosser Cause: Planned Maintenance. |  | 1 | 10:50 | Morning | Friday | 2017 | 2
6823 | 2017-02-10 10:55 | 2017-02-10 10:55 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | 10:55 Man Opened Recl. 16.AB.03 (d/s S Balam fdr#4) to Connect X-0 300KVATX POP new well Balam #181. 12:15 Man Closed back the Recloser. Cause: Planned Construction. |  | 1 | 10:55 | Morning | Friday | 2017 | 2
6824 | 2017-02-10 14:05 | 2017-02-10 14:05 | 13.8KV 4B FEEDER #6 | Fair | Planned Maintenance | 8 | 14:05 Man.Opened Recl. 4B.48 (d/s 4B fdr6). to trouble shoot and Adjust voltge at well 4B.23N. 14:27 Man Closed back the Recloser. Cause: Planned Maintenance. |  | 1 | 14:05 | Afternoon | Friday | 2017 | 2
6825 | 2017-02-10 15:00 | 2017-02-10 15:00 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 7 | 15:00 Man Opened Recl. 2D.44 (d/s 3D fdr#4). to Adjust Voltage at well 1E.84N. 15:20 Man Closed back the Recloser. Cause: Planned Maintenance. |  | 1 | 15:00 | Afternoon | Friday | 2017 | 2
6826 | 2017-02-10 17:43 | 2017-02-10 17:43 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 265 | 17:43 C.Duri ACB #11 (fdr # 1) T/O. Checked and found C.Duri ACB #11 (fdr #1) T/LO Counter:203 - 208 R/F 51 @1,2. 19:21 Patrolled the line found monkey under the power pole 41-AW-61. 19:23 Blocked and closed C.Duri ACB #11 (fdr #1) and then released the block. Cause: Animal (Monkey). |  | 1 | 17:43 | Afternoon | Friday | 2017 | 2
6827 | 2017-03-10 10:06 | 2017-03-10 10:06 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 95 | 10:06 Manually open Recloser 36 BI 04. Adjusted voltage of TX at well Ampuh # 17. 11:40 Closed Recloser 36 BI 04, but failed (control failure). 13:33 Manually open So. Bekasp fdr #1, ----->Close at 13:48. Closed By Pass switch Recloser 36 BI 04. Cause: Plan maintenance. |  | 1 | 10:06 | Morning | Friday | 2017 | 3
6828 | 2017-03-10 10:22 | 2017-03-10 10:22 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 17 | 10:06 Manually open Recloser 26 AK 02, -----> Closed at 10:30. Adjusted voltage for 300KVA TX at well Ubi # 29. Cause: Plan maintenance. |  | 1 | 10:22 | Morning | Friday | 2017 | 3
6829 | 2017-03-10 11:00 | 2017-03-10 11:00 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Planned Maintenance | 0 | 11:00 Manually open LBS 05 N5 22, -----> Closed at 11:18. Replaced @1, @2 b/o fuse for 112.5KVA TX o/p 05 N5 18. Cause: Plan maintenance. See PIDOD on 30-09-2017 15:25 |  | 1 | 11:00 | Morning | Friday | 2017 | 3
6830 | 2017-03-10 11:38 | 2017-03-10 11:38 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Planned Maintenance | 0 | Open LBS 06 Q5 02, -----> Closed at 11:45. Replaced b/o @1 fuse for 112.5KVA TX o/p 06 Q5 14. Cause: Plan Maintenance. See PIDOD on 01-10-2017 15:40:00 |  | 1 | 11:38 | Morning | Friday | 2017 | 3
6831 | 2017-03-10 15:46 | 2017-03-10 15:46 | 13.8KV MENGGALA FEEDER #1 | Fair | Construction Job | 0 | 15:46 Manually open Recloser 19-AN-04, -----> Closed at 15:57. Replaced 300KVA TX at well N. Manggala # 43 (New well). Cause: Construction Job (Project). |  | 1 | 15:46 | Afternoon | Friday | 2017 | 3
6832 | 2017-03-10 20:12 | 2017-03-10 20:12 | 44KV PEMATANG MAIN - PETANI LINE | Rain and Lightning | Unidentified | 102 | Pematang Main 44KV OCB#1T/R 1x (Pematang petani 44 KV Line) Petani fdr#1, #2 no power Not checked yet. |  | 1 | 20:12 | Night | Friday | 2017 | 3
6833 | 2017-03-10 20:12 | 2017-09-10 08:00 | 44KV PEMATANG MAIN - PETANI LINE | Rain and Lightning | Unidentified | 102 | Checked and found 44KV OCB #1 (PMTMSB) T/R 1x Ctr:402-403 R/F: 50N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 20:12 | Night | Friday | 2017 | 3
6834 | 2017-03-10 20:45 | 2017-03-10 20:45 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Unidentified (L/A) | 0 | D.Community ACB#26 fdr#3 T/R 1x. Not checked yet. |  | 1 | 20:45 | Night | Friday | 2017 | 3
6835 | 2017-03-10 20:45 | 2017-09-10 08:00 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Unidentified (L/A) | 0 | Checked and found 13.8 KV ACB #26 T/R m1x Ctr:60-61 R/F: @3 51N Patrolled the line and found Broken L/A o/p IR-7 Cause: Unidentified (L/A) |  | 1 | 20:45 | Night | Friday | 2017 | 3
6836 | 2017-03-10 21:10 | 2017-03-10 21:10 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Dead End Insulator | 0 | Ketigul fdr#2 Load dropped 44A (150-106A). Not checked yet. |  | 1 | 21:10 | Night | Friday | 2017 | 3
6837 | 2017-03-10 21:10 | 2017-06-10 14:17 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Dead End Insulator | 0 | 14:17 Checked and found Recloser 29 AL 03 T/R 1X Ctr:126-127 R/F 51@1, 51G. Patrolled the line and found broken @1 Dead End o/p 26 AM 20B (Line to well UBI #28). Cause: Broken Dead End. |  | 1 | 21:10 | Night | Friday | 2017 | 3
6838 | 2017-03-10 21:34 | 2017-03-10 21:34 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Unidentified | 195 | 21:34 So. Bekasap fdr#1 Load dropped 65A (115-50A). 23:46 Checked and found Recloser: 34-BI-18 T/O, Counter:162-163, R/F: 51N. (Recloser:34-BI-18 in block position due to Rig APS 3523 activity at location Ampuh #3). 23:52 Blocked and closed Recloser:34-BI-18 --> Success. (Recloser:34-BI-18 still in block position due to Rig APS 3523 activity at location Ampuh #3). Patrolled the Line, but found nothing. Cause: unidentified. |  | 1 | 21:34 | Night | Friday | 2017 | 3
6839 | 2017-04-10 01:54 | 2017-04-10 01:54 | 13.8KV CENTRAL DURI FEEDER #8 | Heavy Rain | Recloser | 0 | C.Duri ACB fdr#8 T/R 1x, Ctr: 434-435, R/F: 51 @B,@C. Not patrolled yet |  | 1 | 1:54 | Night | Monday | 2017 | 4
6840 | 2017-04-10 01:54 | 2017-12-10 17:30 | 13.8KV CENTRAL DURI FEEDER #8 | Heavy Rain | Recloser | 0 | Checked and found C.Duri ACB fdr#8 T/R 1x, Ctr: 434-435, R/F: 51 @B,@C. Patrolled the line found @2 broken By pass Recloser: 09-N6-06. Cause: Broken By pass. |  | 1 | 1:54 | Night | Monday | 2017 | 4
6841 | 2017-04-10 08:23 | 2017-04-10 08:23 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 1415 | 08:23 CD Fdr #8 Load drop 18A (228-210A). 10:05 It was reported no power o/p 09.N6.04. 10:50 It was reported broken pole o/p 09.P1.02. 11:00 Checked and found recl. 09.N6.06 T/LO Ctr.72-76. Also found broken pole o/p 09.P1.01. Opened jumper o/p 09.P1.07. 11:30 Blocked and closed recl.09.N6.06, ok then released the block/ok. Caused : Under Investigation. | 111111 | 1 | 8:23 | Morning | Monday | 2017 | 4
6842 | 2017-04-10 09:42 | 2017-04-10 09:42 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 63 | 09:42 Manual open recl. 16 Z 25 D/S S.Balam Fdr #1 Replaced @1 b/o fuse for 100Kva Tx at well S.Balam 186 09:45 Manual Closed recl. 16 Z 25. Cause : Animal (Monkey). |  | 1 | 9:42 | Morning | Monday | 2017 | 4
6843 | 2017-05-10 10:41 | 2017-05-10 10:41 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Broken Fuse Holder | 434 | It was reported b/o fuse o/p 05 M7 13. Not checked yet. |  | 1 | 10:41 | Morning | Wednesday | 2017 | 5
6844 | 2017-05-10 10:41 | 19/10/2017 13:58 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Broken Fuse Holder | 434 | Checked & found, @1 b/o fuse for 112.5KVA Tx on Pole 05-M7-13. Replaced b/o fuse above with the same size then energized the Tx. Cause: Broken Fuse Holder. (See Outage on 19 Oct at 13:58). |  | 1 | 10:41 | Morning | Wednesday | 2017 | 5
6845 | 2017-05-10 13:44 | 2017-05-10 13:44 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 30 | 13:44 Manually Open LBS 32 AK3, ----->Closed at 14:40. Replaced 150 to 300KVA TX at well Tilan #31. (C/O Reda Motor from 87HP to 104HP). Cause: Plan Maintenance. |  | 1 | 13:44 | Afternoon | Wednesday | 2017 | 5
6846 | 2017-05-10 14:45 | 2017-05-10 14:45 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 47 | 14:45 Manually open Recloser 8D-18A (d/s 8D fdr#3), -----> Closed at 15:43. Replaced Vacuum Switch Board at well 8C-79. Cause: Planned construction. |  | 1 | 14:45 | Afternoon | Wednesday | 2017 | 5
6847 | 2017-05-10 15:06 | 2017-05-10 15:06 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 122 | 15:06 Manually open LBS 30 AN 38 (d/s Ketigul fdr#2) -----> Closed at 15:48. Replaced 300KVA TX at well Pagar #27. Cause: Plan Maintenance. See PIDOD at 29-09-2017 10:28 |  | 1 | 15:06 | Afternoon | Wednesday | 2017 | 5
6848 | 2017-05-10 16:15 | 2017-05-10 16:15 | 13.8KV 6DN FEEDER #6 | Fair | Planned Maintenance | 44 | 16:15 Manually Open Recloser 6E 64 (d/s 6DN fdr#6) ----->Closed at 16:24. Trouble shooting Switch Board at well 6E. 35. Cause: Planned construction. |  | 1 | 16:15 | Afternoon | Wednesday | 2017 | 5
6849 | 2017-05-10 16:30 | 2017-05-10 16:30 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 0 | 16:30 Manually Open Recloser 16 AA08, ---->Close at 16:34 Adjusted voltage for .....KVA TX at well S. Balam # 421. Cause: Plan Maintenance. |  | 1 | 16:30 | Afternoon | Wednesday | 2017 | 5
6850 | 2017-05-10 17:00 | 2017-05-10 17:00 | 13.8KV MENGGALA FEEDER #1 | Fair | Planned Maintenance | 0 | 17:00 Manually Open Recloser 19 AN 04 (d/s Menggala fdr#1) ---->Closed at 17:07. Replaced VSD to Switch Board at well N. Menggala #43. Cause: Planned construction. |  | 1 | 17:00 | Afternoon | Wednesday | 2017 | 5
6851 | 2017-05-10 18:44 | 2017-05-10 18:44 | 13.8KV 6D FEEDER #5 | Fair | Tree | 774 | 18:44 6D OCB Fdr #5 T/LO. 6D Fdr #6, Load droped 238A (248-10A) WIP 6D Fdr #4, Load droped 145A (148-3A) WIP. 21:00 Checked & found 6D OCB fdr#5 T/LO, Ctr: ............... R/F: 51 @2@3 Patrolled the Line under 6D fdr#5, found nothing. 21:57 Opened LBS 5D-117, to separate 6D fdr#5 from 6DN fdr#2. 22:04 Patrolled the Line, found Recl. 5D -122 T/LO, ctr: 25-28. 22:07 Closed LBS 5D-117 22:09 Closed 6D fdr#5 , OK. Continued Patrolled the Line Under Recl.5D-112. Found Fall down Trees to Cross arm and touching conductor @ @ @ o/p....... Cut the Trees.... Cause: Tree. | 1111111 | 1 | 18:44 | Afternoon | Wednesday | 2017 | 5
6852 | 2017-06-10 00:40 | 2017-06-10 00:40 | LIBO SUBSTATION | Fair | Relay Failure | 120 | 00:40 Libo 11kKV C/S T/O, Ctr: 364-365, R/F: ....... Libo Substation no Power, the Feeders still in Close. 01:45 Checked & found nothing. 02:00 Man. Opened Libo fdr#1, -----> Closed at 02:39. Man. Opened Libo fdr# 2 -----> Closed at 02:39. 02:05 Man. Closed Libo 115KV Circuit Switcher but Fail. 02:20 Man. Opened KBJ 115KV GCB# 53, ---->Closed at 02:37. Man. Opened KBJ 115KV GCB# 55, ---->Closed at 02:37. 02:25 Closed Libo C/S bypass Switch. Cause: Relay failure. Production Loss : 126 Bbls, 16 Wells. Libo fdr#1 ; 69 Bbsl, 9 Wells Libo fdr#2 ; 57 Bbls, 7 Wells |  | 1 | 0:40 | Night | Saturday | 2017 | 6
6853 | 2017-06-10 00:40 | 2017-07-10 10:00 | LIBO SUBSTATION | Fair | Relay Failure | 120 | 10:00 Switching to Normalized 115Kv C/S Libo Substation. Manual opened 13.8Kv VCB Libo Fdr #1,2, --------------> Closed at 10:22. 10:04 Manual opened KBJ 115Kv GCB # 53, 55. --------------> Closed at 10:17. Manual Close 115Kv Circuit Switcher Libo Substation.. Cause : Plan Maintenance. |  | 1 | 0:40 | Night | Saturday | 2017 | 6
6854 | 2017-06-10 09:50 | 2017-06-10 09:50 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Planned Maintenance | 0 | 09:50 Manual open NKB Fdr #3, -----> Closed at 10:16. Replaced 300Kva to 225Kva Tx at well KB #359. Replaced Switch Board Bus Fuse for 300Kva Tx at well KB #19. Cause : Plan Maintance. |  | 1 | 9:50 | Morning | Saturday | 2017 | 6
6855 | 2017-06-10 10:55 | 2017-06-10 10:55 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 63 | 10:55 Manual opened BKO Fdr #4. Adjusted voltage for 300 Kva Tx at well BKO #295. 10:57 Manual closed BKO Fdr #4. Cause : Plan Maintanace. |  | 1 | 10:55 | Morning | Saturday | 2017 | 6
6856 | 2017-06-10 15:04 | 2017-06-10 15:04 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 17 | 15:04 Manual open LBS 7C-33 D/S Minas Fdr #3, ----> Closed at 16:50. Replaced 150 Kva to 225 Kva Tx at well 7C-59. (well be continued tomorrow). Cause : Plan Maintenance. |  | 1 | 15:04 | Afternoon | Saturday | 2017 | 6
6857 | 2017-06-10 15:04 | 2017-07-10 14:35 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 17 | 14:35 Manual open LBS 7C-33 D/S Minas Fdr #3, ----> Closed at 14:39. Continued to Replace 150 Kva to 225 Kva Tx at well 7C-59. Cause : Plan Maintenance. |  | 1 | 15:04 | Afternoon | Saturday | 2017 | 6
6858 | 2017-06-10 15:41 | 2017-06-10 15:41 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 83 | 15:41 Manual open S.Balam Fdr #4, ----->Closed at 15:48. Adjusted voltage 100 Kva Tx at well So. Balam 58. Cause : Plant Maintenance. |  | 1 | 15:41 | Afternoon | Saturday | 2017 | 6
6859 | 2017-06-10 16:02 | 2017-06-10 16:02 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Pin Insulator | 92 | 5 B fdr# 2 load dropped 174A (198-24A). Not checked yet. |  | 1 | 16:02 | Afternoon | Saturday | 2017 | 6
6860 | 2017-06-10 16:02 | 13/10/2017 20:20 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Pin Insulator | 92 | Checked and found Recloser 4D-85 T/R 1x Counter:1616-1617. Patrolled the line found @1 broken Pin Insulator on pole 4D-86. Cause: Broken Pin Insulator. |  | 1 | 16:02 | Afternoon | Saturday | 2017 | 6
6861 | 2017-06-10 16:03 | 2017-06-10 16:03 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 337 | 16:03 Minas fdr #6 Load dropped 85A (176-91A). 20:58 Checked, found Recl. 6E.23A T/SO, Ctr: 520-521. Blocked & Closed the Recloser, then released the block. Not Patrolled yet. |  | 1 | 16:03 | Afternoon | Saturday | 2017 | 6
6862 | 2017-06-10 16:03 | 2017-09-10 08:03 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Lightning | 337 | Checked and found Recloser 6E-23-A T/SO Ctr:520-521 Patrolled the line and found @3 Broken L/A o/p 6E-51 Cause: Lightning. |  | 1 | 16:03 | Afternoon | Saturday | 2017 | 6
6863 | 2017-06-10 16:14 | 2017-06-10 16:14 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 27 | 8C fdr #3 load dropped 174A (192-18A). Not checked yet. |  | 1 | 16:14 | Afternoon | Saturday | 2017 | 6
6864 | 2017-06-10 16:14 | 2017-09-10 08:14 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 27 | Checked and found Recloser 8D-18-A T/R 1x Ctr:44-45 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 16:14 | Afternoon | Saturday | 2017 | 6
6865 | 2017-06-10 16:17 | 2017-06-10 16:17 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 0 | 8C 13.8KV OCB fdr #4 T/R, ----->WIP. Not checked yet. |  | 1 | 16:17 | Afternoon | Saturday | 2017 | 6
6866 | 2017-06-10 16:17 | 2017-09-10 08:17 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found 13.8 KV VCB #4 T/R 1x Ctr:596-597 R/F:@1,@2 50 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 16:17 | Afternoon | Saturday | 2017 | 6
6867 | 2017-06-10 16:19 | 2017-06-10 16:19 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 24 | 8D 13.8KV OCB fdr #3 T/R 1X. 8D fdr #1 load dropped 20A (130-110A). 8D fdr #2 load dropped 17A (103-86A). Not checked yet. |  | 1 | 16:19 | Afternoon | Saturday | 2017 | 6
6868 | 2017-06-10 16:19 | 2017-12-10 08:19 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 24 | Checked & found 8D fdr#3 T/R 2x Ctr:196-198 R/F:50@1@2. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 16:19 | Afternoon | Saturday | 2017 | 6
6869 | 2017-06-10 16:36 | 2017-06-10 16:36 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 58 | 3D fdr #4 load dropped 200A (257-57A ). 3D fdr #2 load droped 7A (185-178A). Not checked yet. |  | 1 | 16:36 | Afternoon | Saturday | 2017 | 6
6870 | 2017-06-10 16:36 | 14/10/2017 16:36 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 58 | checked & found Recl. 2D-33 T/R 1x Ctr:43-54. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 16:36 | Afternoon | Saturday | 2017 | 6
6871 | 2017-07-10 05:44 | 2017-07-10 05:44 | 13.8KV 8C FEEDER #6 | Fair | Lightning | 45 | 8C Feeder # 6 T/R 1X Not checked yet. |  | 1 | 5:44 | Morning | Monday | 2017 | 7
6872 | 2017-07-10 05:44 | 2017-09-10 08:00 | 13.8KV 8C FEEDER #6 | Fair | Lightning | 45 | Checked and found 13.8 KV VCB #6 T/R 1x Ctr:582-583 R/F: 51N Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 5:44 | Morning | Monday | 2017 | 7
6873 | 2017-07-10 07:21 | 2017-07-10 07:21 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 133 | 07:21 Ground foult alarm from Manggala Fdr #1. Manggala Fdr #1 drop 146A (195-49A). Not checked yet |  | 1 | 7:21 | Morning | Monday | 2017 | 7
6874 | 2017-07-10 09:26 | 2017-07-10 09:26 | 13.8KV NORTH DURI FEEDER #10 | Fair | Planned Maintenance | 155 | 09:26 Manual open LBS 10 J4A 07 D/S ND Fdr #10 (Fdr #2). Replaced 112.5 Kva Tx o/p 10 J4 09. Cause : Plan Mantenace. See PIDOD at 29-09-2017 11:25 |  | 1 | 9:26 | Morning | Monday | 2017 | 7
6875 | 2017-07-10 09:34 | 2017-07-10 09:34 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Construction Job | 0 | 09:34 Manual opened Recl. 28 CW 05 -------> Closed 10:44 Manual opened Recl. 29 CX 05 -------> Closed 10:22. Phasing checked Old PTP Fdr #2 to New PTP Fdr #3. Phasing checked Old PTP Fdr #2 to New PTP Fdr #4. Cause : Project. |  | 1 | 9:34 | Morning | Monday | 2017 | 7
6876 | 2017-07-10 11:15 | 2017-07-10 11:15 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Tree | 22 | 11:15 It was reported weel off o/p 03.07.13 d/s CD Fdr #7 12:00 Checke and found recl. 03.07.24 T/LO, Counter : 104 - 107. 12:20 Closed recl. 03.07.24. Cause : Tree. |  | 1 | 11:15 | Morning | Monday | 2017 | 7
6877 | 2017-07-10 11:30 | 2017-07-10 11:30 | 13.8KV 3D FEEDER #4 | Fair | Lightning | 60 | 11:30 It was reported no Power at well 2D 22, 2D 23 and 1D 98. 13:45 Checked and found Recloser 2D 33 T/SO ctr:46. Blocked and closed Recloser 2D 33, OK then released the block. Not patrolled yet. |  | 1 | 11:30 | Morning | Monday | 2017 | 7
6878 | 2017-07-10 11:30 | 14/10/2017 11:30 | 13.8KV 3D FEEDER #4 | Fair | Lightning | 60 | Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 11:30 | Morning | Monday | 2017 | 7
6879 | 2017-07-10 13:39 | 2017-07-10 13:39 | 13.8KV NELLA GFPC | Rain and Lightning | Unidentified | 0 | Nella 13.8KV GFPC T/R 1X. Nella fdr #1 load dropped 172A (262-90A). Nella fdr #2 load dropped 54A (124-70A). Not checked yet. |  | 1 | 13:39 | Afternoon | Monday | 2017 | 7
6880 | 2017-07-10 13:39 | 2017-10-10 09:39 | 13.8KV NELLA GFPC | Rain and Lightning | Unidentified | 0 | Checked & found Nella GFPC T/R 2x Ctr:745-747. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 13:39 | Afternoon | Monday | 2017 | 7
6881 | 2017-07-10 13:41 | 2017-07-10 13:41 | CENTRAL DURI POWER PLANT |  |  | - | 13:41 CGT #1 Generator Breake T/O, ----->Closed at 14:30. Re Closed CGT #1 Generator Breaken, but tipped again (twice). Trouble shot and simulation R70-L4RL. Cause: Under investigation. |  | 1 | 13:41 | Afternoon | Monday | 2017 | 7
6882 | 2017-07-10 16:39 | 2017-07-10 16:39 | CENTRAL DURI POWER PLANT | Fair |  | - | 16:39 S/U CDGT #5. 16:56 O/L to restore power. |  | 1 | 16:39 | Afternoon | Monday | 2017 | 7
6883 | 2017-07-10 20:45 | 2017-07-10 20:45 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Duri comy 13.8KV ACB-26 fdr#3 T/R 1X. Not checked yet. |  | 1 | 20:45 | Night | Monday | 2017 | 7
6884 | 2017-07-10 20:45 | 13/10/2017 08:00 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Checked and found 13.8 KV ACB #26 T/R 1x R/F: @2 51 Patrolled the line and found Broken pin insulator o/p 6F-02. Cause: Pin Insulator. |  | 1 | 20:45 | Night | Monday | 2017 | 7
6885 | 2017-08-10 09:39 | 2017-08-10 09:39 | CENTRAL DURI POWER PLANT |  |  | - | 09:39 Off Line. 09:46 S/D The unit for S/B, |  | 1 | 9:39 | Morning | Thursday | 2017 | 8
6886 | 2017-08-10 10:44 | 2017-08-10 10:44 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 102 | 10:44 Manual open So.Balam fdr#1 to setting voltage for 300Kva Tx at wells S.Balam#376 and S.Balam #436. Cause : Plan maintenance. |  | 1 | 10:44 | Morning | Thursday | 2017 | 8
6887 | 2017-08-10 14:25 | 2017-08-10 14:25 | 13.8KV 8C FEEDER #2 | Fair | Planned Maintenance | 43 | 14:25 Manually Open 8C Fdr #2 ---->Closed at 14:39. Replaced VSD to Switch Board at well 8D.79 16:15 Manually Open 8C Fdr #2 ---->Closed at 16:17. After Replaced VSD to Switch Board at well 8D.79 Cause: Planned construction. |  | 1 | 14:25 | Afternoon | Thursday | 2017 | 8
6888 | 2017-08-10 15:05 | 2017-08-10 15:05 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Construction Job | 0 | 15:05 Manual open C.Duri fdr#8.---------> Closed at 15:08. Open Recl 09.N6.06. to tie in 13.8Kv power line o/p 09. P1.07. 16:47 Manual closed Recl 09.N6.06. Cause : Plan Mantenace. |  | 1 | 15:05 | Afternoon | Thursday | 2017 | 8
6889 | 2017-08-10 22:14 | 2017-08-10 22:14 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 238 | 22:14 Ketigul VCB fdr#1 T/LO, Ctr:....... , R/F:......... 02:00 Checked & found Broken @1 Conductor o/p 33.AJ.17. also found Animal monkey on Pole above. 02:05 Open LBS 32.AJ.01, then Locked, to isolate broken conductor. 02:07 Blocked & Closed Ketigul VCB fdr#1, then released the block. Cause: Animal (monkey). (will Repaired the conductor Soon). |  | 1 | 22:14 | Night | Thursday | 2017 | 8
6890 | 2017-08-10 22:14 | 2017-09-10 12:30 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 238 | 12:30 Open HLC o/p nn (beside Tilan Fery) to isolated broken Conductor o/p33 AJ 17. 13:00 Closed LBS 32 AJ 01. ( the JOB to repair broken Conductor will be done tomorrow). |  | 1 | 22:14 | Night | Thursday | 2017 | 8
6891 | 2017-09-10 07:20 | 2017-09-10 07:20 | 13.8KV S. BALAM FEEDER #1 | Fair | Dead End Insulator | 0 | 07:20 S.Balam Fdr #1. GFPC Ground fault alarm. Load drop 72A (110-38A). Not checked yet. |  | 1 | 7:20 | Morning | Sunday | 2017 | 9
6892 | 2017-09-10 07:20 | 13/10/2017 07:20 | 13.8KV S. BALAM FEEDER #1 | Fair | Dead End Insulator | 0 | Checked and found Recloser 16-Z-25 T/R 3x Ctr:29-32 Patrolled the line and found broken Dead End insulator o/p 16-Z-26. Cause: Dead End insulator. |  | 1 | 7:20 | Morning | Sunday | 2017 | 9
6893 | 2017-09-10 10:14 | 2017-09-10 10:14 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 38 | 10:11 Manually Open So. Balam fdr #4, ----->Closed at 10:40. Setting voltage for 100KVA TX at well So. Balam #326. Cause: Planned Maintenance. |  | 1 | 10:14 | Morning | Sunday | 2017 | 9
6894 | 2017-09-10 10:45 | 2017-09-10 10:45 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 7 | 10:11 Manually Open Recloser 26 AK 02, ----->Closed at 10:54. Setting voltage for 300KVA TX at well UBI #3. Cause: Plan Maintenance. |  | 1 | 10:45 | Morning | Sunday | 2017 | 9
6895 | 2017-09-10 11:25 | 2017-09-10 11:25 | 13.8KV PETAPAHAN FEEDER #1 | Fair | Construction Job | 0 | 11:25 Open LBS 30 CZ 04A. (Petapahan fdr #1 load dropped 18A (147-128A) Closed 13.8KV New Petapahan TIE breaker VCB #9. 11:35 Closed 13.8KV New Petapahan VCB fdr #6. (Part load Old Petapahan fdr #1 (d/s LBS 30 CZ 04A) transfer to New Petapahan fdr #6). Cause: Project. |  | 1 | 11:25 | Morning | Sunday | 2017 | 9
6896 | 2017-09-10 13:55 | 2017-09-10 13:55 | 13.8KV BATANG FEEDER #2 | Fair | Planned Maintenance | 0 | 13:55 Manually Open 13.8KV Batang fdr #2, ----->Closed at 15:34. Disconnected/ Connected power of H&P at Wells RB057 ---R/B 033. Disconnected/ Connected power of H&P at Wells RB011 ---R/B 069. Cause: Plan Maintenance. |  | 1 | 13:55 | Afternoon | Sunday | 2017 | 9
6897 | 2017-09-10 14:38 | 2017-09-10 14:38 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 14 | 14:38 Manually Open Recloser 9D-25, ----->Closed at 15:00. Replaced 300KVA TX at well 9D-76 (Re-active well) Cause: Plan Maintenance. |  | 1 | 14:38 | Afternoon | Sunday | 2017 | 9
6898 | 2017-09-10 15:08 | 2017-09-10 15:08 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Construction Job | 0 | 15:08 Manually Open Recloser 29 C2 05, d/s PTP Fdr #2. PTP Fdr #2 Load drop 204A (254-50A). Cut Jumper o/p 28 CX 4. Squeeze jumper o/p 28 CX 4 to New PTP Fdr #3 15:29 Blocked and closed 13.8 Kv New PTP Fdr #3. (Tranfer Part load PTP Fdr #2 under recl. 28 CX 05A to New PTP fdr #3 Cause: Project. |  | 1 | 15:08 | Afternoon | Sunday | 2017 | 9
6899 | 2017-09-10 15:42 | 2017-09-10 15:42 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Construction Job | 0 | 15:42 Manual open PTP Fdr #2 (Load 72A) Cut Jumper o/p 29 CY 21. 17:16 Closed New PTP Fdr #4. Part load Old PTP Fdr #2 (72A) Transfer to New PTP Fdr #4. Cause : Project. |  | 1 | 15:42 | Afternoon | Sunday | 2017 | 9
6900 | 2017-09-10 15:48 | 2017-09-10 15:48 | 13.8KV 8D FEEDER #7 | Fair | Planned Maintenance | 38 | 15:48 Manually Open Recloser 8D-88A, ----->Closed at 15:57. d/s 8D fdr #7. Load drop 80A (220-140A). Replaced Bus fuse at well 8D-27E. Cause: Plan Maintenance. |  | 1 | 15:48 | Afternoon | Sunday | 2017 | 9
6901 | 2017-10-10 08:30 | 2017-10-10 08:30 | CENTRAL KOTABATAK SUBSTATION | Fair | Construction Job | 0 | 08:30 Manual open 115Kv GCB #1 CKBS to PTP. To tie in 115Kv o/p PS #02, dismantled existing 115Kv four pole, dismantled existing 13.8Kv fdr 1,2 at Petapahan Subtation and works related to Petapahan Substation Upgrate Project. 16:30 Manual closed 115Kv GCB #1 CKBS to PTP. Cause : Project Upgrade Petapahan Substation. |  | 1 | 8:30 | Morning | Tuesday | 2017 | 10
6902 | 2017-10-10 09:00 | 2017-10-10 09:00 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 5 | 09:00 It was reported no power o/p 05-P2-20. 09:40 Checked and founded recl.05-P7-02 T/LO ctr: 501-505. Patrol the line & found nothing Blocke & Closed recl.05-P7-02. 09:57 C. Duri 13.8KV ACB fdr #14 T/R 2X. ctr: 252-254 R/F 51N. Patroled the line and found Snake at bypass recl.05-P7-02. Cause : Animal (Snake) |  | 1 | 9:00 | Morning | Tuesday | 2017 | 10
6903 | 2017-10-10 15:06 | 2017-10-10 15:06 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 15:06 Manual open recl.26 AK 02 d/s Katigul fdr #2, -----> Closed at 15:16. Connected HLC at UBI #30. Cause : Contruction Tie-In New well. |  | 1 | 15:06 | Afternoon | Tuesday | 2017 | 10
6904 | 2017-10-10 17:18 | 2017-10-10 17:18 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Pin Insulator | 0 | Duri Community 13.8KV ACB fdr#1 T/R 1x. Not checked yet. |  | 1 | 17:18 | Afternoon | Tuesday | 2017 | 10
6905 | 2017-10-10 17:18 | 13/10/2017 08:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Pin Insulator | 0 | Checked and found 13.8 kV ACB #25 T/R 1x Ctr: 102-103 R/F: @1,@2,@3 .. Patrolled the line and found Flash Pin Insulator o/p KT-39. Cause: Pin Insulator. |  | 1 | 17:18 | Afternoon | Tuesday | 2017 | 10
6906 | 2017-10-10 21:39 | 2017-10-10 21:39 | 13.8KV 3D FEEDER #3 | Fair | Tree | 38 | 21:39 3D 13.8KV OCB fdr #3 T/LO. 3D fdr #5 load dropped 93A (184-91A) -----> WIP. 21:53 Blocked and closed 3D fdr #3, OK then released Block. Not checked yet. |  | 1 | 21:39 | Night | Tuesday | 2017 | 10
6907 | 2017-10-10 21:39 | 14/10/2017 21:39 | 13.8KV 3D FEEDER #3 | Fair | Tree | 38 | Checked & found 3D fdr#3 T/LO Ctr;443 (not operated). R/F:51@1@2. Patrolled the line & found Sawit between Loc. 4C-24B. Cause: Trees. |  | 1 | 21:39 | Night | Tuesday | 2017 | 10
6908 | 2017-10-10 21:39 | 2017-10-10 21:39 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 46 | 3D fdr #2 load dropped 155A (178-23A ). Not checked yet. |  | 1 | 21:39 | Night | Tuesday | 2017 | 10
6909 | 2017-10-10 21:39 | 14/10/2017 21:39 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 46 | Checked & found Recl. 2F-11 T/R 1x Ctr:12-13. Patrolled the line but found nothing. (see patrolled 11 oct 2017 at 05:40) Cause : Lightning. |  | 1 | 21:39 | Night | Tuesday | 2017 | 10
6910 | 2017-10-10 21:39 | 2017-10-10 21:39 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 58 | 3D fdr #4 load dropped 193A (244-51A ). Not checked yet. |  | 1 | 21:39 | Night | Tuesday | 2017 | 10
6911 | 2017-10-10 21:39 | 14/10/2017 21:39 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 58 | Checked & found Recl. 2D-14 T/R 1x Ctr:53-54. Patrolled the line but found nothing. (see patrolled 11Oct 2017). Cause : Lightning. |  | 1 | 21:39 | Night | Tuesday | 2017 | 10
6912 | 2017-11-10 02:22 | 2017-11-10 02:22 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Recloser | 0 | 02:22 C. Durim13.8KV ACB fdr #14 T/R 2X ctr:354-356 R/F: 51 @1. 06:26 C. Durim13.8KV ACB fdr #14 T/R 1X ctr:356-357 R/F:51 @1, @2. Not checked yet. |  | 1 | 2:22 | Night | Friday | 2017 | 11
6913 | 2017-11-10 02:22 | 2017-12-10 17:36 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Recloser | 0 | Checked and found C. Duri ACB #27 (fdr #14) T/R 3x Counter: 354-357 R/F:51 @1, @2. Patrolled the line found @1 Broken By Pass Recloser: 07-P7-02. Cause: Broken By pass Recloser. |  | 1 | 2:22 | Night | Friday | 2017 | 11
6914 | 2017-11-10 05:40 | 2017-11-10 05:40 | 13.8KV 3D FEEDER #3 | Cloudy | Tree | 173 | 05:40 3D 13.8KV OCB fdr #3 T/O. 3D fdr #5 load dropped 93A (184-91A) -----> WIP. 07:20 Checked and found 3D OCB fdr #3 T/LO Counter: 443 (Do not change) R/F: 51@1,@2. Patrolled the line found tree touching power line. 10:38 Manually blocked and closed 3D OCB fdr #3 --> OK and then released the block. Cause: Tree. Production loss: 165 Bbls / 16 Wells, ----->GS #5. 38 Bbls / 06 Wells, ----->GS #6. --------------------------------------+ TOTAL : 203 Bbls / 22 Wells. |  | 1 | 5:40 | Morning | Friday | 2017 | 11
6915 | 2017-11-10 05:40 | 14/10/2017 05:40 | 13.8KV 3D FEEDER #3 | Cloudy | Tree | 173 | Checked & found 3D fdr#3 T/LO Ctr:243(not operated). R/F:50@1@2. Patrolled the line & found Sawit between well 4C-24B. Cause : Tree |  | 1 | 5:40 | Morning | Friday | 2017 | 11
6916 | 2017-11-10 05:40 | 2017-11-10 05:40 | 13.8KV 3D FEEDER #2 | Cloudy | Lightning | 46 | 3D fdr #2 load dropped 155A (178-23A ). Not checked yet. |  | 1 | 5:40 | Morning | Friday | 2017 | 11
6917 | 2017-11-10 05:40 | 14/10/2017 05:40 | 13.8KV 3D FEEDER #2 | Cloudy | Lightning | 46 | Checked & found Recl. 2F-11 T/R 1x Ctr:12-13. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 5:40 | Morning | Friday | 2017 | 11
6918 | 2017-11-10 05:40 | 2017-11-10 05:40 | 13.8KV 3D FEEDER #4 | Cloudy | Lightning | 60 | 3D fdr #4 load dropped 193A (244-51A ). Not checked yet. |  | 1 | 5:40 | Morning | Friday | 2017 | 11
6919 | 2017-11-10 05:40 | 14/10/2017 05:40 | 13.8KV 3D FEEDER #4 | Cloudy | Lightning | 60 | Checked & found Recl. 2D-14 T/R 1x Ctr:53-54. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 5:40 | Morning | Friday | 2017 | 11
6920 | 2017-11-10 05:52 | 2017-11-10 05:52 | LIBO SUBSTATION | Rain | Under investigation | 54 | 05:52 LIBO 115KV C/S T/O. 07:00 Manually opened LIBO OCB fdr #1. Manually opened LIBO OCB fdr #2. 07:10 Checked and found 115 KV C/S T/O Counter: 369-370 R/F: None. 07:12 Manually closed LIBO 115 KV C/S --> OK. 07:13 Manually closed LIBO OCB fdr #1 --> OK Counter: 558-559. 07:14 Manually closed LIBO OCB fdr #2 --> OK Counter: 458-459. Cause: Under investigation. |  | 1 | 5:52 | Morning | Friday | 2017 | 11
6921 | 2017-11-10 06:26 | 2017-11-10 06:26 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | C. Durim13.8KV ACB fdr #3 T/R 1X ctr:201-201 R/F: 51G. Not checked yet. |  | 1 | 6:26 | Morning | Friday | 2017 | 11
6922 | 2017-11-10 06:26 | 15/10/2017 17:24 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | Checked and found C. Duri ACB #13 (fdr #3) T/R 1X Counter:200-201 R/F: 51G. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 6:26 | Morning | Friday | 2017 | 11
6923 | 2017-11-10 10:30 | 2017-11-10 10:30 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 38 | 10:30 Manually opened Recloser: 16-Z-25 D/S So Balam OCB fdr #1. due to adjust voltage at well Balam #249. 10:32 Manuallyblocked and closed Recloser: 16-Z-25 and then released the block. Cause: Plan Maintenance. |  | 1 | 10:30 | Morning | Friday | 2017 | 11
6924 | 2017-11-10 10:52 | 2017-11-10 10:52 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 81 | 10:52 Manually opened So Balam VCB fdr #4. due to external connection for 150 Kva Tx at well So Balam #37. 11:00 Manually blocked and closed So Balam VCB fdr #4 and then released the blocked. Cause: Plan Maintenance. |  | 1 | 10:52 | Morning | Friday | 2017 | 11
6925 | 2017-11-10 13:43 | 2017-11-10 13:43 | 13.8KV DURI FIELD FEEDER #4 | Fair | Planned Maintenance | 31 | 13:43 Manually opened LBS 07-U2-02 D/S D Field fdr #4. due to trouble shot Recloser: 07-T7-02 (wells were off on 6T 70 to 6T 80). 15:54 Manually closed LBS 07-U2-02. Cause: Plan Maintenance. |  | 1 | 13:43 | Afternoon | Friday | 2017 | 11
6926 | 2017-11-10 14:12 | 2017-11-10 14:12 | 13.8KV BEKASAP FEEDER #3 | Fair | Planned Maintenance | 0 | 14:12 Manually opened LBS 38-BD-94 D/S Bekasap fdr #3. due to requested SPS team replace secondary cable at well Bekasap #146. 15:54 Manually closed LBS 38-BD-94. Cause: Construction job. |  | 1 | 14:12 | Afternoon | Friday | 2017 | 11
6927 | 2017-11-10 14:56 | 2017-11-10 14:56 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 93 | It was reported b/o fuse on pole 06-05-13 D/S D Field fdr #2. Not checked yet. |  | 1 | 14:56 | Afternoon | Friday | 2017 | 11
6928 | 2017-11-10 14:56 | 15/10/2017 13:27 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 93 | Checked and found @2 & @3 b/o fuse for 112.5Kva Tx. Performed TTR & Megger found good reading. Replaced b/o fuse above with the same size and Energized the Tx. Cause : Animal (Monkey). |  | 1 | 14:56 | Afternoon | Friday | 2017 | 11
6929 | 2017-11-10 21:35 | 2017-11-10 21:35 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Capasitor Bank | 520 | 21:35 It was reported no power o/p 08 L5 04. 22:56 Checked and found Recloser 08 L5 35 T/SO ctr: 926-927. Blocked and closed Recloser 08 L5 35, but failed. Patrolled the line and found @1 broken Bushing for 300KVAR Cap. Bank o/p 08 L5 19. (Will be continued tomorrow)----->SWA. | 1111 | 1 | 21:35 | Night | Friday | 2017 | 11
6930 | 2017-11-10 21:35 | 2017-12-10 09:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Capasitor Bank | 520 | 09:55 Disconnect Cap Bank on pole 08-L5-19. Blocked and closed Recloser: 08-L5-35 --> OK and then released the block. Cause: Broken Bushing Cap Bank. | 1111 | 1 | 21:35 | Night | Friday | 2017 | 11
6931 | 2017-12-10 03:05 | 2017-12-10 03:05 | LIBO SUBSTATION | Fair | Under investigation | 65 | 03:05 LIBO 115KV C/S T/O. No power to LIBO Subtation n Libo fdr #1 & #2. 04:09 Checked and found LIBO 115KV C/S T/O ctr:370-371 R/F:86T @1. 04:10 Manually opened LIBO OCB fdr #1, ---->Closed at 04:20 Counter: 559-560. Manually opened LIBO OCB fdr #2, ---->Closed at 04:20 Counter: 469-470. 04:12 Manually Open 115KV KBJ GCB #53, ----->Closed at 04:19. Manually Open 115KV KBJ GCB #55, ----->Closed at 04:19. 04:18 Manually closed 115KV LIBO C/S By Pass Switch. Cause: Under investigation. |  | 1 | 3:05 | Night | Sunday | 2017 | 12
6932 | 2017-12-10 05:48 | 2017-12-10 05:48 | 13.8KV BATANG GFPC | Fair | Tree | 0 | Batang 13.8KV GFPC T/R 1X. No load dropped at any feeder. |  | 1 | 5:48 | Morning | Sunday | 2017 | 12
6933 | 2017-12-10 05:48 | 18/10/2017 19:22 | 13.8KV BATANG GFPC | Fair | Tree | 0 | Checked and found Batang GFPC T/R 1X Counter 852-853. Patrolled the line and found high palm tree on pole 36-AL-09. Cause : Tree. |  | 1 | 5:48 | Morning | Sunday | 2017 | 12
6934 | 2017-12-10 08:17 | 2017-12-10 08:17 | 13.8KV NEW KOTABATAK FEEDER #5 | Fair | Lightning | 0 | NKBS fdr #5 load dropped 190A (229-39A). NKBS fdr #4 load dropped 150A (169-19A). NKBS fdr #3 load dropped 9A (145-136A). NKBS GFPC T/R 1x. Not checked yet. |  | 1 | 8:17 | Morning | Sunday | 2017 | 12
6935 | 2017-12-10 08:17 | 14/10/2017 08:17 | 13.8KV NEW KOTABATAK FEEDER #5 | Fair | Lightning | 0 | Checked & found Recl. T/R 1x Ctr:154-155. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 8:17 | Morning | Sunday | 2017 | 12
6936 | 2017-12-10 11:47 | 2017-12-10 11:47 | 13.8KV BATANG FEEDER #3 | Fair | Construction Job | 0 | 11:47 Manually opened Batang OCB fdr #3. due to opened visual opening of Recloser: 36-AL-13. for Tie in new well at Candi area. 4 wells were off during the job execution. 12:02 Manually blocked and closed Batang OCB fdr #3 --> OK and released the block. Cause: Construction job. |  | 1 | 11:47 | Morning | Sunday | 2017 | 12
6937 | 2017-12-10 14:35 | 2017-12-10 14:35 | 13.8KV 6D FEEDER #2 | Fair | Planned Maintenance | 1 | 14:35 Manually opened LBS 6D-68 D/S 6D fdr #2. due to replaced bus fuse switch board on location 6D-62N by SPS team. 14:40 Manually closed LBS 6D-68. Cause: Planned Maintenance. |  | 1 | 14:35 | Afternoon | Sunday | 2017 | 12
6938 | 2017-10-13 10:52 | 2017-10-13 10:52 | 13.8KV 3D FEEDER #8 | Fair | Construction Job | 0 | 10:52 Manually open LBS 3D-41 d/s 3D fdr #8 (Loaad :38A) due to energized HPS Pump at GS #5 (2X1500 Kva & 300 Kva Tx). 11:21 Manually closed LBS 3D-41. Cause : Construction job. |  | 1 | 10:52 | Morning | Friday | 2017 | 10
6939 | 2017-10-13 14:21 | 2017-10-13 14:21 | 13.8KV CENTRAL DURI FEEDER #14 | Heavy Rain | Animal | 17 | 14:21 C.Duri fdr#14 T/R 7X Counter: 357-364 R/F 51 @1 & @2. 14:43 It was reported no power on pole 05-P7-02. 15:44 Patrolled the line found Recloser: 05-P7-02 T/LO counter: 505-509. Manually blocked and closed Recloser: 05-P7-02 --> Ok and then released the block. Cause: Animal (snake). |  | 1 | 14:21 | Afternoon | Friday | 2017 | 10
6940 | 2017-10-13 16:17 | 2017-10-13 16:17 | 13.8KV MENGGALA FEEDER #1 | Drizzle | Animal | 98 | Menggala fdr #1 load dropped 101A (193-92A). Not checked yet. |  | 1 | 16:17 | Afternoon | Friday | 2017 | 10
6941 | 2017-10-13 16:17 | 2017-10-15 16:24 | 13.8KV MENGGALA FEEDER #1 | Drizzle | Animal | 98 | Checked and Found Recloser: 19-AN-04 T/R 1x Counter: 344 – 345. Patrolled the line found @1,@2 b/o fuse at well Meno #38. Cause: Animal (monkey). |  | 1 | 16:17 | Afternoon | Friday | 2017 | 10
6942 | 2017-10-14 02:23 | 2017-10-14 02:23 | MINAS SWITCH YARD | Cloudy | Under investigation | 0 | 02:23 115Kv Minas SY GCB#53 T/O Ctr:162-163 R/F:86T, 87T. 115Kv Minas SY GCB#55 T/O Ctr:75-76. MGT#8 Open Generator Breaker, Freq>59.90 (No load shedding). 03:25 Checked Tx-8 Winding temp 65C, Oil Temp. 65C. Checked visual Tx-8 Normal condition. 03:45 S/D MGT#8 for maintenance. (Tx-8 Continued checked tomorrow morning). 10:12 Manually closed 115 Kv GCB #55 --> OK. 10:15 Manually closed 115 Kv GCB #53 --> OK. Monitoring Power Tx #8. 13:45 S/U MGT #8 and On Line the unit at 14:10. Cause:: Under Investigation. |  | 1 | 2:23 | Night | Saturday | 2017 | 10
6943 | 2017-10-14 02:23 | 2017-10-14 02:23 | MINAS POWER PLANT |  |  | - | 02:23 MGT#8 Open Generator Breaker, Freq:59.90 (No load shedding). By: 115Kv GCB#53 & GCB#55 T/O. 03:45 S/D MGT#8, for maintenance. Cause: Under Investigation. |  | 1 | 2:23 | Night | Saturday | 2017 | 10
6944 | 2017-10-14 08:37 | 2017-10-14 08:37 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Planned Maintenance | 0 | 08:37 Manually opened ACB #27 (CD fdr #14) due to dismantle animal (Snake) from power line o/p 06-P7-02. 08:38 Manually blocked and closed ACB #27 (CD fdr #14) and then released the block. Cause : Animal. |  | 1 | 8:37 | Morning | Saturday | 2017 | 10
6945 | 2017-10-14 09:50 | 2017-10-14 09:50 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 234 | 09:50 It was reported b/o fuse o/p 08-M4-04 d/s CD fdr #2. Not checked yet. |  | 1 | 9:50 | Morning | Saturday | 2017 | 10
6946 | 2017-10-14 09:50 | 2017-10-15 13:27 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Animal | 234 | Checked and found @1,@2 b/o fuse for 112.5 Kva TX. Perform TTR & megger found good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (bird). |  | 1 | 9:50 | Morning | Saturday | 2017 | 10
6947 | 2017-10-14 09:54 | 2017-10-14 09:54 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 144 | 09:54-10:06 Manually opened So Balam fdr #4 due to : Closed HLC for reactive well Balam #157. Adjusted voltage at well So Balam #302. Replaced b/o fuse at well So Balam #78. Cause : Animal. |  | 1 | 9:54 | Morning | Saturday | 2017 | 10
6948 | 2017-10-14 10:20 | 2017-10-14 10:20 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 115 | 10:20 Manually opened So Balam OCB fdr #1 due to: C/O Transformer at well So Balam #364. Tx : 150 Kva Sec.voltage : 466 10:45 Manually blocked and Closed So Balam OCB fdr #1. Cause : Plan Maintenance. |  | 1 | 10:20 | Morning | Saturday | 2017 | 10
6949 | 2017-10-14 10:52 | 2017-10-14 10:52 | 13.8KV RANGAU FEEDER #1 | Fair | Planned Maintenance | 41 | 10:52 Manually opened Rangau fdr #1 due to C/O Transformer at well Rangau #04. 12:17 Manually blocked and closed Rangau OCB fdr #1. Cause : Plan Maintenace. |  | 1 | 10:52 | Morning | Saturday | 2017 | 10
6950 | 2017-10-14 11:18 | 2017-10-14 11:18 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 169 | 11:18 Manually opened 8C OCB fdr #3 due to: 1. Replaced Tx due to Leakage at well 8C #68. 2.Troubled shoot at S/B by SPS Team at well. 11:52 Manually blocked and closed 8C OCB fdr #3. Cause : Plan Maintenace. |  | 1 | 11:18 | Morning | Saturday | 2017 | 10
6951 | 2017-10-14 13:45 | 2017-10-14 13:45 | MINAS POWER PLANT |  |  | - | 13:45 S/U MGT #8 and then On Line the unit at 14:10. |  | 1 | 13:45 | Afternoon | Saturday | 2017 | 10
6952 | 2017-10-14 14:00 | 2017-10-14 14:00 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 4 | 14:00 Manually opened recleser 39-CX-24 d/s OKB fdr #2 due to : 1. Adjusted voltage 300 Kva Tx at well KB #231. 2. Repaired secondary cable at well KB #455. 14:14 Manually blocked and closed reclose 38-CX-25. Cause : Construction job. |  | 1 | 14:00 | Afternoon | Saturday | 2017 | 10
6953 | 2017-10-14 15:26 | 2017-10-14 15:26 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified (Fuse) | 125 | It was reported b/o fuse at well Menggala North #38 D/S Menggala fdr #1. Not checked yet. |  | 1 | 15:26 | Afternoon | Saturday | 2017 | 10
6954 | 2017-10-14 15:26 | 2017-10-15 09:52 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified (Fuse) | 125 | 09:52 Manually opened recl. 19-AN-04 d/s Manggala fdr #1 due to replaced @1 b/o fuse at well Meno #38 09:57 Manually blocked & closed recl. 19-AN-04 and then released the block. Cause : Plan Maintenance. |  | 1 | 15:26 | Afternoon | Saturday | 2017 | 10
6955 | 2017-10-14 20:25 | 2017-10-14 20:25 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Recloser | 0 | 20:25 C.Duri fdr#14 T/R 3x Ctr:364-367 R/F:51@1@2. 22:11 Checked & found Recl. 05-P7-02 T/R 3x Ctr:509-512. Not patrolled yet. |  | 1 | 20:25 | Night | Saturday | 2017 | 10
6956 | 2017-10-14 20:25 | 2017-10-15 17:06 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Recloser | 0 | Checked and found C.Duri ACB #27 (fdr #14) T/R3x Counter: 364-367 R/F:51@1,@2. Checked & found Recl. 06-P7-02 T/R 3x Counter:509-512. Patrolled the line found @1,@2 broken By Pass switch Recloser on pole : 06-P7-02. Cause: Broken By Pass Recloser. |  | 1 | 20:25 | Night | Saturday | 2017 | 10
6957 | 2017-10-15 08:38 | 2017-10-15 08:38 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Planned Maintenance | 47 | 08:38 Manually open recl. 09-N6-06 d/s CD #8. due to replaced Transformer on pole 09-P1-01 & @2 fuse o/p 09-P1-07. 10:00 Manually blocked & closed recl. 09-N6-06 and then release the block. Cause : Plan Maintenance. |  | 1 | 8:38 | Morning | Sunday | 2017 | 10
6958 | 2017-10-15 09:29 | 2017-10-15 09:29 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 26 | Ketigul VCB fdr #1 T/R 1x. Not Checked yet. |  | 1 | 9:29 | Morning | Sunday | 2017 | 10
6959 | 2017-10-15 09:29 | 2017-10-16 09:29 | 13.8KV KETIGUL FEEDER#1 | Fair | Dead End Insulator | 26 | Checked & found, Ketigul VCB fdr #1 T/R 1x ctr: 189-190 R/F: 51 @2. Patrolled the line & found, @2 Flash over Dead-end Insulator on Pole 32-AK-74. Cause: Dead-end Insulator. |  | 1 | 9:29 | Morning | Sunday | 2017 | 10
6960 | 2017-10-15 13:50 | 2017-10-15 13:50 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 37 | 13:50 Manually open recl.36-CT-10 d/s CKBS fdr #1 due to: 1. Replaced 300Kva Tx to 250 Kva Tx at well KB #439. and voltage = 1220 volt. 2. Replaced 150Kva Tx to 300 Kva Tx at well KB #276. and voltage = 450 volt. 14:25 Manually blocked & closed recl.36-CT-10 and then release the block. Cause : Plan Maintenance. |  | 1 | 13:50 | Afternoon | Sunday | 2017 | 10
6961 | 2017-10-16 09:53 | 2017-10-16 09:53 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 33 | 09:53 Manually open recl.16-AB-03 d/s Balam fdr #4 due to: External conection Tx at well Balam #53 10:07 Manually blocked & closed recl.16-AB-03 and then release the block. Cause : Plan Maintenance. |  | 1 | 9:53 | Morning | Monday | 2017 | 10
6962 | 2017-10-16 10:05 | 2017-10-16 10:05 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 227 | 10:05 It was reported b/o fuse o/p 07-V5-07 d/s DF fdr #4. 11:30 Checked and found @3 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (monkey). |  | 1 | 10:05 | Morning | Monday | 2017 | 10
6963 | 2017-10-16 11:34 | 2017-10-16 11:34 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 3 | 11:34 Manually open LBS.32-AJ-01 d/s Katigul fdr #1 due to : Dismantle recloser o/p 33-AK-09. 12:36 Manually closed LBS.32-AJ-01. Cause : Plan Maintenance. |  | 1 | 11:34 | Morning | Monday | 2017 | 10
6964 | 2017-10-16 15:20 | 2017-10-16 15:20 | 13.8KV 6DN FEEDER #1 | Fair | Planned Maintenance | 96 | 15:20 Manually opened 6DN fdr #1 due to : Installed 300 Kva Tx at well 5B 38 (Reactive well). 16:07 Manually blocked and closed 6DN fdr #1 and then release the block. Cause : Plan Maintenance. |  | 1 | 15:20 | Afternoon | Monday | 2017 | 10
6965 | 2017-10-16 15:26 | 2017-10-16 15:26 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 5 | 15:26 It was reported no power at well Kulim #32 d/s CD fdr #1. Checked & founded recl. 40-AW-17 T/SO. Ctr.636-637. 16:30 Blocked and closed recl. 40-AW-17 then released the block. Cause : Unidentified. |  | 1 | 15:26 | Afternoon | Monday | 2017 | 10
6966 | 2017-10-16 15:30 | 2017-10-16 15:30 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 5 | 15:30 Manually open LBS.34-CT-58 d/s CKBS fdr #5 due to : 1. Adjusted voltage at well KB #226. Sec. voltage : 1060 - 960Volt, R/M 80 - 60Hp. 2. Replaced @1 bus fuse on S/B at well KB #384. 15:38 Manually closed LBS.34-CT-58 . Cause : Plan Maintenance. |  | 1 | 15:30 | Afternoon | Monday | 2017 | 10
6967 | 2017-10-16 16:19 | 2017-10-16 16:19 | 13.8KV BATANG FEEDER #3 | Fair | Construction Job | 0 | 16:19 Manually open Batang fdr #3 due to: Closed isolation switch of recloser 36-AL-13. 16:28 Manually blocked & closed Batang fdr #3 and then release the block. |  | 1 | 16:19 | Afternoon | Monday | 2017 | 10
6968 | 2017-10-16 16:47 | 2017-10-16 16:47 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | 16:47 CD fdr #3 T/R 1X. ctr.202-203 and R/F 50 @2, 51G. Not patroleld yet. |  | 1 | 16:47 | Afternoon | Monday | 2017 | 10
6969 | 2017-10-16 16:47 | 2017-10-20 16:47 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | Checked & found, Central Duri ACB #13 fdr #3 T/R 1x ctr: 202-203 R/F: 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:47 | Afternoon | Monday | 2017 | 10
6970 | 2017-10-16 18:36 | 2017-10-16 18:36 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 14 | Ketigul VCB fdr #3 T/R 1x. Not checked yet. |  | 1 | 18:36 | Afternoon | Monday | 2017 | 10
6971 | 2017-10-16 18:36 | 2017-10-22 18:36 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 14 | Checked & found, Ketigul VCB fdr #3 T/R 1x ctr: 188-189 R/F: 51N. Patrolled the line but found nothing. Cause: unidentified. |  | 1 | 18:36 | Afternoon | Monday | 2017 | 10
6972 | 2017-10-17 05:56 | 2017-10-17 05:56 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 32 | Pinang VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 5:56 | Morning | Tuesday | 2017 | 10
6973 | 2017-10-17 05:56 | 2017-10-19 05:56 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 32 | Checked & found, Pinag VCB fdr #1 T/R 1x ctr: 422-423 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. . |  | 1 | 5:56 | Morning | Tuesday | 2017 | 10
6974 | 2017-10-17 07:08 | 2017-10-17 07:08 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 91 | Sintong VCB fdr#2 T/R 1x. Not Patrolled yet. |  | 1 | 7:08 | Morning | Tuesday | 2017 | 10
6975 | 2017-10-17 08:09 | 2017-10-17 08:09 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Dead End Insulator | 0 | C.Duri ACB #13 fdr#3 T/R 1x. Not Patrolled yet. |  | 1 | 8:09 | Morning | Tuesday | 2017 | 10
6976 | 2017-10-17 08:09 | 2017-10-20 08:09 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Dead End Insulator | 0 | Checked & found, Central Duri ACB #13 fdr #3 T/R 1x ctr: 203-204 R/F: 51N. Patrolled the line & found, @1 broken Dead-end Insulator on Pole 01-01-32. Cause : Dead End Insulator |  | 1 | 8:09 | Morning | Tuesday | 2017 | 10
6977 | 2017-10-17 09:42 | 2017-10-17 09:42 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Planned Maintenance | 58 | 09:42 Manually open recl. 08-M3-38 and then opened LBS 08-M3-01 d/s C.Duri fdr #2 due to : C/O recloser 06-M6-02. 12:30 Closed LBS 08-M3-01. Cause : Plan Maintenance. |  | 1 | 9:42 | Morning | Tuesday | 2017 | 10
6978 | 2017-10-17 11:21 | 2017-10-17 11:21 | 44KV NORTH DURI - DUMAI LINE | Fair | Accident | 0 | 11:21 N.Duri 44Kv GCB #1 T/LO ctr.114-120. 11:30 Blocked & closed N.Duri 44Kv GCB #1 but failure. Patrolled the line found public foco truck tooch to power line on pole DD #261 at KM 14 Bagan Besar. 11:58 Blocked & closed N.Duri 44Kv GCB #1, ok and then release the block. Cause : Others (Foco truck). |  | 1 | 11:21 | Morning | Tuesday | 2017 | 10
6979 | 2017-10-17 11:31 | 2017-10-17 11:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 52 | 11:31 Man. Opened LBS 37.AQ.08 (C.Duri fdr#1) to Replace 300KVA TX at well Puncak#30 12:17 Man. Closed back the LBS after finished the jobs Cause: Planed Maintenance. |  | 1 | 11:31 | Morning | Tuesday | 2017 | 10
6980 | 2017-10-17 14:00 | 2017-10-17 14:00 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 137 | It was reported B/O fuse at well Bangko #245 (Bangko fdr#1). Not checked yet |  | 1 | 14:00 | Afternoon | Tuesday | 2017 | 10
6981 | 2017-10-17 14:00 | 2017-10-18 15:54 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified (Fuse) | 137 | 15:54 Man.Open Bangko fdr#4 to replace b/o fuse at well BKO#245. 16:02 Man.close Bangko fdr#4. Cause : Unidentified (Fuse). See PIDOD 18-10-2017 15:54:00 |  | 1 | 14:00 | Afternoon | Tuesday | 2017 | 10
6982 | 2017-10-17 14:00 | 2017-10-17 14:00 | 13.8KV SINTONG FEEDER #2 | Fair | Broken Fuse Cut Out | 30 | It was reported B/O fuse at well Benar#37 (Sintong fdr#2). Not checked yet. |  | 1 | 14:00 | Afternoon | Tuesday | 2017 | 10
6983 | 2017-10-17 14:00 | 2017-10-18 14:45 | 13.8KV SINTONG FEEDER #2 | Fair | Broken Fuse Cut Out | 30 | 14:45 Man.Opened recl 28 AF 02 (d/s Sintong fdr#2). to replace b/o fuse & FCO at Well Benar#37 14:51 Man.Closed back the Recloser after finished the Job. Cause : Broken Fuse Cut Out. See PIDOD at 18-10-2017 14:45:00 |  | 1 | 14:00 | Afternoon | Tuesday | 2017 | 10
6984 | 2017-10-17 14:41 | 2017-10-17 14:41 | 13.8KV BATANG FEEDER #3 | Fair | Planned Maintenance | 59 | 14:41 Manually opened Batang OCB fdr #3 ctr.353, due to : C/O 300Kva Tx at Candi #12. Cause : Plan Maintenance. |  | 1 | 14:41 | Afternoon | Tuesday | 2017 | 10
6985 | 2017-10-18 07:14 | 2017-10-18 07:14 | NEW PETAPAHAN SUBSTATION | Fair | Under investigation | 684 | 07:14 New Petapahan 115KV GCB#2 T/O, (GCB #3 Open status) New PTH TX#1 De energized, R/F: 86T, 87T @1@3. New Petapahan Substation no power (Black Out). New Petapahan RTU Fail 07:20 Man. Opened New PTH Fdr#2,#3,#4,#6,#7,#8 those are Energized before. 07:47 Man. Closed New PTH 115KV GCB #2, (GCB #3 Open status) after reset the relays. New PTH TX#1 has Energized. 07:49 Man. Closed New PTH ACB fdr#7, #8, #2, #3, #4, #6 Cause: Under investigation. | 12345 | 1 | 7:14 | Morning | Wednesday | 2017 | 10
6986 | 2017-10-18 10:22 | 2017-10-18 10:22 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Planned Maintenance | 549 | 10:22 Man. Opened C.Duri ACB fdr#4. SP. to replace Bypass switch and Recloser unit o/p 09.Q1.06. 14:05 Man Closed back C.Duri ACB fdr#4, after Finished the Jobs. Cause: Planed Maintenance. | 12345 | 1 | 10:22 | Morning | Wednesday | 2017 | 10
6987 | 2017-10-18 10:46 | 2017-10-18 10:46 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 506 | 10:46 Man. Opened Bekasap OCB fdr#2. SP. to Replace TX at Well BKS#130 and Adjust Voltage at Well Bks#89 12:56 Man Closed back Bks OCB fdr#2, after finished the Jobs. Cause: Planned Maintenance. | 12345 | 1 | 10:46 | Morning | Wednesday | 2017 | 10
6988 | 2017-10-18 10:52 | 2017-10-18 10:52 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 124 | 10:52 Man. Opened S.Balam VCB fdr#1. SP to Adjust Voltage at Well Balam#358. 10:54 Man Closed S.Balam VCB fdr#1, After finished the Jobs. Cause : Planned Maintenance. |  | 1 | 10:52 | Morning | Wednesday | 2017 | 10
6989 | 2017-10-18 11:55 | 2017-10-18 11:55 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 46 | 11:55 Man. Open LBS 34.CT.58 (CKB fdr#5). to Replace TX at Well KB#139. 12:43 Man. Closed back the LBS after finished the Jobs. Cause: Planned maintenance. |  | 1 | 11:55 | Morning | Wednesday | 2017 | 10
6990 | 2017-10-18 14:45 | 2017-10-18 14:45 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 10 | 14:45 Man.Opened recl 28 AF 02 (d/s Sintong fdr#2). to replace b/o fuse at Well Benar#37 14:51 Man.Closed back the Recloser after finished the Job. Cause : Planned maintenance. See PIDOD at 17-10-2017 14:00:01 |  | 1 | 14:45 | Afternoon | Wednesday | 2017 | 10
6991 | 2017-10-18 15:54 | 2017-10-18 15:54 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 58 | 15:54 Man.Open Bangko fdr#4 to replace b/o fuse at well BKO#245. 16:02 Man.close Bangko fdr#4. Cause : Planned maintenance. See PIDOD 17-10-2017 14:00:00 |  | 1 | 15:54 | Afternoon | Wednesday | 2017 | 10
6992 | 2017-10-18 17:59 | 2017-10-18 17:59 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 17 | Ketigul Fdr # 1 T/R 1X Not checked yet. |  | 1 | 17:59 | Afternoon | Wednesday | 2017 | 10
6993 | 2017-10-18 17:59 | 2017-10-22 17:59 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 17 | Checked & found, Ketigul VCB fdr #1 T/R 1x ctr: 190-191 R/F: 51 @1, @2 Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:59 | Afternoon | Wednesday | 2017 | 10
6994 | 2017-10-18 20:08 | 2017-10-18 20:08 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 20:08 Opened Gen Breaker CDGT #5 , and then On Line the unit at 20:14. Freq: 59:92. |  | 1 | 20:08 | Night | Wednesday | 2017 | 10
6995 | 2017-10-18 23:30 | 2017-10-18 23:30 | CENTRAL DURI POWER PLANT |  |  | - | 23:30 S/U CDGT #2 and then On Line the unit at 23:50. |  | 1 | 23:30 | Night | Wednesday | 2017 | 10
6996 | 2017-10-18 23:51 | 2017-10-18 23:51 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 23:51 CDGT #1 Trip by alarm: Mvar Low , freq:59:88. |  | 1 | 23:51 | Night | Wednesday | 2017 | 10
6997 | 2017-10-19 00:21 | 2017-10-19 00:21 | CENTRAL DURI POWER PLANT |  |  | - | 00:21 S/U CDGT #1 and then On Line the unit at 00:37. |  | 1 | 0:21 | Night | Thursday | 2017 | 10
6998 | 2017-10-19 01:30 | 2017-10-19 01:30 | CENTRAL DURI POWER PLANT |  |  | - | 01:30 S/D CDGT #5 and then Off Line the unit at 01:31 for Stan By. |  | 1 | 1:30 | Night | Thursday | 2017 | 10
6999 | 2017-10-19 07:11 | 2017-10-19 07:11 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 17 | 07:11 Libo OCB fdr#1 T/R 1x. 16:00 Checked & found, Libo OCB fdr #1 T/R 1x ctr: 562-563 R/F: 51 @1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:11 | Morning | Thursday | 2017 | 10
7000 | 2017-10-19 09:46 | 2017-10-19 09:46 | 13.8KV SINTONG FEEDER #1 | Fair | Planned Maintenance | 132 | 09:46 Man. Opened LBS 26.AE.06 (Sintong fdr#1). to Adjust Voltage at Well Seruni #30. 10:08 Man. Closed back the LBS after finished the Jobs. Cause: Planned Maintenance. |  | 1 | 9:46 | Morning | Thursday | 2017 | 10
7001 | 2017-10-19 09:59 | 2017-10-19 09:59 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Planned Maintenance | 0 | 09:59 Man Opened Petapahan ACB fdr#4. to repair Fencing Transformer at Well PTH#138. 10:10 Man.Closed back the Feeder after finished the jobs. Cause: Planned Maintenance. |  | 1 | 9:59 | Morning | Thursday | 2017 | 10
7002 | 2017-10-19 10:10 | 2017-10-19 10:10 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 48 | 10:10 Man Opened LBS 45.BS.05 (Pungut fdr#2). to Replace Recl.43.BY.25. 13:38 Man Closed back the LBS, after finished the Jobs. 10:31 Man Opened LBS 45.BR.01 (Pungut fdr#2). to Adjust Voltage transformer at Well Tandun #2. 10:52 Man Closed bcak the LBS after finished the Jobs. Causes: Planned Maintenance. |  | 1 | 10:10 | Morning | Thursday | 2017 | 10
7003 | 2017-10-19 10:58 | 2017-10-19 10:58 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 218 | 10:58 Man Opened 4D ACB fdr#2. to Replace Recl. 3D.119. 14:16 Man Closed the OCB after finished the jobs. Cause: Planned Maintenance |  | 1 | 10:58 | Morning | Thursday | 2017 | 10
7004 | 2017-10-19 13:58 | 2017-10-19 13:58 | 13.8KV DARLING VCB FEEDER #6 | Fair | Planned Maintenance | 0 | 13:58 Man Opened Darling VCB fdr#6 to replace @3 b/o 7.8 sf fuse with the same size o/p 05.M7.13 14:10 Man Closed the Feeder after finished the jobs. Cause : Planned Maintenance. See PIDOD 05-10-2017 10:41:00 |  | 1 | 13:58 | Afternoon | Thursday | 2017 | 10
7005 | 2017-10-19 14:22 | 2017-10-19 14:22 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Planned Maintenance | 0 | 14:22 Man Opened D.Comm. ACB fdr#1. to Energized 1MVA & 100KVA TXs at WDC & Golf cours. 14:32 Man Closed the Feeder after finished the jobs. Cause: Planned Maintenance. |  | 1 | 14:22 | Afternoon | Thursday | 2017 | 10
7006 | 2017-10-19 14:22 | 2017-10-19 14:22 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 48 | 14:22 Man Opened Sintong OCB fdr#2. to Replace b/o fuse at well Benar #37. 14:48 Man Closed the Feeder after finished the jobs. Cause: Planned Maintenance. |  | 1 | 14:22 | Afternoon | Thursday | 2017 | 10
7007 | 2017-10-19 14:42 | 2017-10-19 14:42 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 36 | 14:42 Man Opened LBS 7C.33 (Mns fdr#3). to replace Vaccum breaker Switch board at well 7D.42N. 14:45 Man Closed the LBS after finished the jobs. Cause: Planned construction. |  | 1 | 14:42 | Afternoon | Thursday | 2017 | 10
7008 | 2017-10-19 17:04 | 2017-10-19 17:04 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 17:04 C.Duri fdr#1 Load dropped 44A(108-64A). Not checked yet. |  | 1 | 17:04 | Afternoon | Thursday | 2017 | 10
7009 | 2017-10-19 17:04 | 2017-10-20 17:04 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recl. 41-AW-62 T/R 1x ctr: 261-262. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:04 | Afternoon | Thursday | 2017 | 10
7010 | 2017-10-20 06:17 | 2017-10-20 06:17 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | D Field ACB #51 (feeder#4) T/R 1x ctr: 510-511 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:17 | Morning | Friday | 2017 | 10
7011 | 2017-10-20 06:47 | 2017-10-20 06:47 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | N.Duri VCB #13 (feeder#1) T/R 1x. Not checked yet. |  | 1 | 6:47 | Morning | Friday | 2017 | 10
7012 | 2017-10-20 06:47 | 2017-10-24 14:00 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found N. Duri 13.8KV VCB fdr #1 normal operation. Patrolled the line but found nothing. Cause: Un identified. |  | 1 | 6:47 | Morning | Friday | 2017 | 10
7013 | 2017-10-20 10:29 | 2017-10-20 10:29 | 13.8KV 6D FEEDER #2 | Fair | Planned Maintenance | 26 | 10:29 Man open Recl 6D-78 D/S 6D-2 To Replace transformer at loc 6C-49N 11:11 Blocked and Closed Recl 6D-78 D/S 6D-2, then release the block. Caused : Plan maintenance. |  | 1 | 10:29 | Morning | Friday | 2017 | 10
7014 | 2017-10-20 10:31 | 2017-10-20 10:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 0 | 10:31 Man open recl 39 AV 36 D/S CD Fdr#1 Replace switch boar at Kulim # 8 10:35 Bloked and Close Recl. 39 AV 36 D/S CD Fdr#1 then release the block. Caused: planned maintenance. |  | 1 | 10:31 | Morning | Friday | 2017 | 10
7015 | 2017-10-20 10:38 | 2017-10-20 10:38 | 13.8KV BATANG FEEDER #3 | Fair | Planned Maintenance | 113 | 10:38 Man open OCB Batang Fdr#3 Relocated Guy wire at Candy #12 for Rig service 11:50 Close OCB Caused : Planned Maintenance. |  | 1 | 10:38 | Morning | Friday | 2017 | 10
7016 | 2017-10-20 10:56 | 2017-10-20 10:56 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 45 | 10:56 Sintong VCB Fdr #2 T/R 1x 16:00 Checked & found, Sintong OCB fdr #2 T/R 1x ctr: 465-466 R/F: 51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 10:56 | Morning | Friday | 2017 | 10
7017 | 2017-10-20 14:04 | 2017-10-20 14:04 | 13.8KV LIBO FEEDER #1 | Fair | Planned Maintenance | 0 | 14:04 Man open LBS 34 CC 01 D/S Libo Fdr #1 Adjusted voltage at SE Libo 09 14:45 Blocked and Close LBS 34 CC 01 D/S Libo Fdr #1 then release the block. Caused Planned maintenance. |  | 1 | 14:04 | Afternoon | Friday | 2017 | 10
7018 | 2017-10-20 15:20 | 2017-10-20 15:20 | 13.8KV MINAS FEEDER #4 | Fair | Planned Maintenance | 46 | 15:20 Man open LBS 7C-33 D/S Minas Fdr#4 Replace vacuum switch boar at 7D-42N 15:23 Blocked and Closed LBS 7C-33 D/S Minas Fdr#4, then release the block. Caused: Planned Maintenance. |  | 1 | 15:20 | Afternoon | Friday | 2017 | 10
7019 | 2017-10-20 18:19 | 2017-10-20 18:19 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | 18:19 C.Duri Fdr # 14 T/R 1X Not Checked yet. |  | 1 | 18:19 | Afternoon | Friday | 2017 | 10
7020 | 2017-10-20 18:19 | 2017-10-24 18:00 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | Checked and found C. Duri 13.8KV fdr #14 T/R 1X ctr:367-368 R/F:51N. Patrolled the line but found nothing. Cause: Un identified. |  | 1 | 18:19 | Afternoon | Friday | 2017 | 10
7021 | 2017-10-21 09:12 | 2017-10-21 09:12 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 42 | 09:12 Man open Reclose 39 AV 36 D/S C.Duri Fdr# 1 Replace switch boar at loc Kulim #8 09:14 Closed Recloser Cause: Planned Maintenace. |  | 1 | 9:12 | Morning | Saturday | 2017 | 10
7022 | 2017-10-21 14:14 | 2017-10-21 14:14 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Tree | 0 | 14:14 Duri Community Fdr # 2 T/R 1X Not Checked yet. |  | 1 | 14:14 | Afternoon | Saturday | 2017 | 10
7023 | 2017-10-21 14:14 | 2017-10-22 14:14 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Tree | 0 | Checked & found, Duri Community ACB #30 fdr #2 T/R 1x ctr: 085-086 R/F: 51N. Patrolled the line & found, high trees touched powerline on Pole behind House Merapi #111. Cause: Tree. |  | 1 | 14:14 | Afternoon | Saturday | 2017 | 10
7024 | 2017-10-21 16:06 | 2017-10-21 16:06 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 26 | 16:06 Rangau Fdr#2 load drop 102 Amp ( 116 - 14 ) Not Checked Yet. |  | 1 | 16:06 | Afternoon | Saturday | 2017 | 10
7025 | 2017-10-21 16:06 | 2017-10-27 16:06 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 26 | Checked & found 23.BD.01 T/R 5x, Ctr: 305 - 310, R/F: 51 @2 Patrolled the Line, found nothing. Cause : Unidentified |  | 1 | 16:06 | Afternoon | Saturday | 2017 | 10
7026 | 2017-10-22 06:33 | 2017-10-22 06:33 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 61 | Sitong VCB fdr #1 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 6:33 | Morning | Sunday | 2017 | 10
7027 | 2017-10-22 10:48 | 2017-10-22 10:48 | 13.8KV 8D FEEDER #5 | Fair | Planned Maintenance | 0 | 10:48 Manually open 8D Fdr#5 SPS crew trouble shot at switch board loc 8E - 42 11:15 Closed 8D Fdr#5 Planned maintenance. |  | 1 | 10:48 | Morning | Sunday | 2017 | 10
7028 | 2017-10-22 11:46 | 2017-10-22 11:46 | 13.8KV 6D FEEDER #2 | Fair | Unidentified | 37 | 11:46 6D Fdr #2 Load drop 163 Amp ( 233 - 70 ) Not Checked yet. |  | 1 | 11:46 | Morning | Sunday | 2017 | 10
7029 | 2017-10-22 11:46 | 2017-10-27 08:00 | 13.8KV 6D FEEDER #2 | Fair | Unidentified | 37 | Checked and found Recloser 6D-298 T/R Ctr:68-69 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 11:46 | Morning | Sunday | 2017 | 10
7030 | 2017-10-22 12:00 | 2017-10-22 12:00 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Secondary Cable | 88 | It was reported Broken secondary cable o/p 01-07-17 D/S DF Fdr#1. Not checked Yet. |  | 1 | 12:00 | Afternoon | Sunday | 2017 | 10
7031 | 2017-10-22 12:00 | 2017-10-24 10:34 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Secondary Cable | 88 | 10:34 Manually open Recloser 01 07 01, -----> Closed at 10:58. 16:11 Manually open Recloser 01 07 01, -----> Closed at 16:15. Repaired Scondary Cable o/p 01 07 17. Cause: Broken Secondary Cable. See PIDOD on 24 Oct 10:34 |  | 1 | 12:00 | Afternoon | Sunday | 2017 | 10
7032 | 2017-10-22 14:31 | 2017-10-22 14:31 | 13.8KV 8D FEEDER #10 | Fair | Planned Maintenance | 0 | 14:31 Manually open Recl 7E-21 D/S 8D-10 Adjusted voltage at Loc 7E-42E 14:45 Closed Recloser. Caused : Planned Maintenance. |  | 1 | 14:31 | Afternoon | Sunday | 2017 | 10
7033 | 2017-10-22 14:51 | 2017-10-22 14:51 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 9 | 14:51 Man open Rec 23BW02 D/S Libo Fdr#2 Adjusted voltage at loc Hitam #03 15:06 Closed Rec Cause : Planned Maintenance. |  | 1 | 14:51 | Afternoon | Sunday | 2017 | 10
7034 | 2017-10-22 15:45 | 2017-10-22 15:45 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 0 | 15:45 Man open rec 9D-25 D/S 8C Fdr#1 Adjusted voltage at loc 9D-19N 15:49 Closed recloser Caused : planned maintenance. |  | 1 | 15:45 | Afternoon | Sunday | 2017 | 10
7035 | 2017-10-23 02:03 | 2017-10-23 02:03 | MINAS POWER PLANT | Fair | Under investigation | 0 | 02:03 MGT #7 Open Generator Breaker. By alarm: Cooling fan from exiciter failure. 02:27 S/D MGT #7 for not stand by. |  | 1 | 2:03 | Night | Monday | 2017 | 10
7036 | 2017-10-23 09:59 | 2017-10-23 09:59 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Planned Maintenance | 75 | 09:59 Man open Rec 22 CX 05 D/S Pth Fdr# 4 Instal VSD at Loc Pth#12 and Tpz#11 11:32 Closed Rec Caused: Construction job. |  | 1 | 9:59 | Morning | Monday | 2017 | 10
7037 | 2017-10-23 10:45 | 2017-10-23 10:45 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 0 | 10:45 Man open Rec: 45 BR 01 D/S Pungut Fdr#2 Adjusted voltage at loc Tandun #12 11:15 Closed Recloser Caused : Planned Maintenance. |  | 1 | 10:45 | Morning | Monday | 2017 | 10
7038 | 2017-10-23 14:32 | 2017-10-23 14:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 90 | 14:32 Man open Rec 36 AV 36 D/S CD Fdr# 1 To changed breaker at Kulim #08 15:25 Closed Rec Caused : planned maintenance. |  | 1 | 14:32 | Afternoon | Monday | 2017 | 10
7039 | 2017-10-23 14:43 | 2017-10-23 14:43 | 13.8KV 6DN FEEDER #5 | Fair | Unidentified | 55 | 14:43 6DN OCB Fdr#5 T/R 1X Not Checked yet. |  | 1 | 14:43 | Afternoon | Monday | 2017 | 10
7040 | 2017-10-23 14:43 | 2017-10-28 08:00 | 13.8KV 6DN FEEDER #5 | Fair | Unidentified | 55 | Checked and found 13.8 KV OCB fdr #5 T/R 1x Ctr:234-235 R/F: - Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:43 | Afternoon | Monday | 2017 | 10
7041 | 2017-10-23 14:52 | 2017-10-23 14:52 | 13.8KV 6DN FEEDER #6 | Fair | Planned Maintenance | 0 | 14:52 Man open LBS 6D-142 D/S 6DN Fdr#6 To checked switch board at Loc 6D-26 15:10 Closed LBS Caused : Construction job. |  | 1 | 14:52 | Afternoon | Monday | 2017 | 10
7042 | 2017-10-23 15:05 | 2017-10-23 15:05 | MINAS POWER PLANT |  |  | - | 15:05 S/U MGT#7 and On Line at 15:23. |  | 1 | 15:05 | Afternoon | Monday | 2017 | 10
7043 | 2017-10-23 15:33 | 2017-10-23 15:33 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 15 | 15:33 Man open LBS 4D-229E D/S 4D Fdr#2 Adjusted voltage at loc 4D-35 15:50 Closed LBS Caused:Planned Maintenance. |  | 1 | 15:33 | Afternoon | Monday | 2017 | 10
7044 | 2017-10-23 16:06 | 2017-10-23 16:06 | 13.8KV 3D FEEDER #8 | Fair | Planned Maintenance | 32 | 16:06 Man open 3D Fdr#8 PT SGN Check switch board at loc 3D-42 16:40 Closed Caused : Construction job. |  | 1 | 16:06 | Afternoon | Monday | 2017 | 10
7045 | 2017-10-23 17:30 | 2017-10-23 17:30 | 13.8KV 5B FEEDER #2 | Fair | Planned Maintenance | 46 | 17:30 Man open 5B OCb Fdr#2 ( +4D Fdr#4 ) PT SGN check switch board at loc 6C-15N. 17:33 Closed OCB Caused:Construction job. |  | 1 | 17:30 | Afternoon | Monday | 2017 | 10
7046 | 2017-10-24 07:34 | 2017-10-24 07:34 | 13.8KV BANGKO GFPC | Fair | Unidentified | 0 | 13.8KVBKO GFPC T/R 1X. No Laod dropped. Not checked yet. |  | 1 | 7:34 | Morning | Tuesday | 2017 | 10
7047 | 2017-10-24 10:34 | 2017-10-24 10:34 | 13.8KV DURI FIELD FEEDER #3 | Fair | Planned Maintenance | 6 | 10:34 Manually open Recloser 01 07 01, -----> Closed at 10:58. 16:11 Manually open Recloser 01 07 01, -----> Closed at 16:15. Repaired Scondary Cable o/p 01 07 17. Cause: Plan Maintenance. See 22-OCT-2017 12:00:00 |  | 1 | 10:34 | Morning | Tuesday | 2017 | 10
7048 | 2017-10-24 11:03 | 2017-10-24 11:03 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 527 | 11:03 Manually open 13.8KV Nella fdr #1, ----->Closed at 13:12. Replaced Recloser o/p 21 V 01. Cause: Plan Maintenance. | 12345 | 1 | 11:03 | Morning | Tuesday | 2017 | 10
7049 | 2017-10-24 11:10 | 2017-10-24 11:10 | 13.8KV BANGKO FEEDER #2 | Fair | Planned Maintenance | 0 | 11:10 Manually Open LBS # 04, ----->Closed at 12:45. Repaired Hot Spot of TX #1, 2 & 3 at EOR. Cause: Plan Maintenance. |  | 1 | 11:10 | Morning | Tuesday | 2017 | 10
7050 | 2017-10-24 11:37 | 2017-10-24 11:37 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 70 | 11:37 Manually Open 13.8KV Minas fdr #3, ----->Closed at 11:56. Adjusted Voltage for 300KVA TX at well 7D-72. Cause: Plan Maintenance. |  | 1 | 11:37 | Morning | Tuesday | 2017 | 10
7051 | 2017-10-24 13:50 | 2017-10-24 13:50 | 13.8KV 6DN FEEDER #5 | Fair | Planned Maintenance | 76 | 13:50 Manually Open LBS 6D-16A, ----->Closed at 14:20. Replaced Vacuum Switch Board at well # 1C-19 & 6D-94E. Plan Maintenance. |  | 1 | 13:50 | Afternoon | Tuesday | 2017 | 10
7052 | 2017-10-24 14:37 | 2017-10-24 14:37 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 7 | 14:37 Manually Open Reclosed 16 Z 25, ----->Closed at 14:39. Adjusted voltage for 150KVA TX at well So. Balam #437. Plan Maintenance. |  | 1 | 14:37 | Afternoon | Tuesday | 2017 | 10
7053 | 2017-10-24 15:35 | 2017-10-24 15:35 | KETIGUL SUBSTATION | Fair | Planned Maintenance | 247 | 15:35 Manually Open 13.8KV Ketigul fdr #1, ---->Closed at 16:25 Ctr:192. 15:36 Manually Open 13.8KV Ketigul fdr #2, ---->Closed at 16:27 Ctr:251. 15:37 Manually Open 13.8KV Ketigul fdr #3, ---->Closed at 16:28 Ctr:190. 15:40 Manually Open 115KV Ketigul GCB #2, ---->Closed at 16:23 Ctr:172. 15:40 Manually Open 115KV Ketigul GCB #3, ---->Closed at 16:21 Ctr:161. (Repair Ketigul Transformer Grounding System). Plan Maintenance. |  | 1 | 15:35 | Afternoon | Tuesday | 2017 | 10
7054 | 2017-10-24 22:52 | 2017-10-24 22:52 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Lightning Arrester | 0 | C.Duri ACB #27 (feeder #14) T/R 1x Counter: 368-369 R/F: 51 @1,2. Not patrolled yet. |  | 1 | 22:52 | Night | Tuesday | 2017 | 10
7055 | 2017-10-24 22:52 | 2017-10-25 18:00 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Lightning Arrester | 0 | Checked and found C. Duri 13.8KV fdr #14 T/LO ctr:369-373 R/F:51@1. Patrolled the line and found broken LA o/p:06 P7 02. Cause: Broken LA. |  | 1 | 22:52 | Night | Tuesday | 2017 | 10
7056 | 2017-10-24 23:03 | 2017-10-24 23:03 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 105 | CKBS VCB fdr #5 T/R 1x. CKBS fdr #6 Load dropped 137A (169-32A). Not checked yet. |  | 1 | 23:03 | Night | Tuesday | 2017 | 10
7057 | 2017-10-24 23:03 | 2017-10-25 08:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 105 | Checked and found CKBS 13.8KV VCB fdr #5 T/R 1X ctr:156-157 R/F:51@2. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 23:03 | Night | Tuesday | 2017 | 10
7058 | 2017-10-25 04:26 | 2017-10-25 04:26 | 13.8KV CENTRAL DURI FEEDER #14 | Drizzle | Recloser | 320 | 04:26 C. Duri 13.8KC ACB 27 fdr#14 T/LO Ctr:369-373 R/F: 51 @1@2.51N. 06:19 Patrolled the Line, but found nothing. 06:23 Block & Closed CD ACB#27 but failed. 06:27 Opened LBS 06.Q1.02----->Closed at 06:59. 06:20 Block & Closed CD ACB#27, Success. Patrolled again the Line. 06:52 Man Opened C. Duri ACB 27 fdr#14, ----->Closed at 07:15. Open Bypass Recloser 06.P8.02, ----->Closed at 08:52. 08:45 Open HLC o/p 06 P7 02 to isolated Recloser 06 P7 02. 08:51 Man Opened C. Duri ACB 27 fdr#14, ----->Closed at 08:54. Cause: Recloser. |  | 1 | 4:26 | Morning | Wednesday | 2017 | 10
7059 | 2017-10-25 08:10 | 2017-10-25 08:10 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Tree | 0 | Duri Comy 13.8KV ACB#26 fdr#3 T/R 1X. Not checked yet. |  | 1 | 8:10 | Morning | Wednesday | 2017 | 10
7060 | 2017-10-25 08:10 | 2017-10-28 08:10 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Tree | 0 | Checked and found 13.8 KV ACB fdr#6 T/R 1x Ctr: 62-63 R/F: 51N Patrolled the line and found high trees near pole DK-04. Cause: Tree. |  | 1 | 8:10 | Morning | Wednesday | 2017 | 10
7061 | 2017-10-25 11:39 | 2017-10-25 11:39 | 13.8KV 8C FEEDER #4 | Fair | Planned Maintenance | 24 | 11:39 Manually Open 8C 13.8KV fdr #4, ----->Closed at 11:40. 16:05 Manually Open 8C 13.8KV fdr #4, ----->Closed at 16:06. Repaired switch Board at well 8D-62. Plan Maintenance. |  | 1 | 11:39 | Morning | Wednesday | 2017 | 10
7062 | 2017-10-25 14:25 | 2017-10-25 14:25 | 13.8KV 6DN FEEDER #2 | Fair | Planned Maintenance | 55 | 14:25 Manually Open LBS 5D-57, ----->Closed at 15:00. (De feed from 6D fdr #5). Replaced 150 KVA - 300 KVA at well 6C-29N. Adjusted voltage at well 6D-42 Plan Maintenance. |  | 1 | 14:25 | Afternoon | Wednesday | 2017 | 10
7063 | 2017-10-25 17:05 | 2017-10-25 17:05 | CENTRAL DURI POWER PLANT |  |  | - | 17:05 S/U CDGT #5 online at 17:30. |  | 1 | 17:05 | Afternoon | Wednesday | 2017 | 10
7064 | 2017-10-25 17:54 | 2017-10-25 17:54 | CENTRAL DURI POWER PLANT |  |  | - | 17:54 S/D CGT #1 and shutdown. |  | 1 | 17:54 | Afternoon | Wednesday | 2017 | 10
7065 | 2017-10-26 10:05 | 2017-10-26 10:05 | 4 BRAVO SUBSTATION | Fair | Planned Maintenance | 589 | 10:18 Open LBS 3C-03 (Sparated load 4B fdr #1 and 5B fdr #4). 10:22 Manually Open 4B fdr #6, ----->Closed at 17:42. 10:31 Manually Open 4B fdr #4, ----->Closed at 17:22. 11:01 Manually Open 4B fdr #5, ----->Closed at 17:37. 11:07 Manually Open 115KV 4B C/S, ----->Closed at 14:49. 11:18 Open LBS 5B-128 (Sparated load 4B fdr #2 and 5B fdr #1). Open LBS 4B-175 (Sparate 4B fdr #3 and 4B fdr #5) 17:00 Closed 4B fdr #2. 17:04 Closed 4B fdr #3. 18:02 Closed 4B fdr #1. Cause: Planned Maintenance. | 1111 | 1 | 10:05 | Morning | Thursday | 2017 | 10
7066 | 2017-10-26 10:06 | 2017-10-26 10:06 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Planned Maintenance | 23 | 10:06 Manually Open Petapahan 13.8KV VCB fdr #6, ----->Closed at 11:24. Replaced 150KVA TX to 300KVA TX at well Petapahan #25. Adjusted voltage for 300KVA TX at well Petapahan # 09. Plan Maintenance. |  | 1 | 10:06 | Morning | Thursday | 2017 | 10
7067 | 2017-10-26 10:07 | 2017-10-26 10:07 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 81 | 10:07 Manually Open Recloser 16 Z 25, ----->Closed at 10:19. Replaced @1, @2 b/o fuse for 150KVA TX at well So. Balam # 140. Cause: Animal (Bird). Plan Maintenance. |  | 1 | 10:07 | Morning | Thursday | 2017 | 10
7068 | 2017-10-26 11:17 | 2017-10-26 11:17 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning | 12 | Ketigul 13.8KV VCB fdr #3 T/R 1X. Not checked yet. |  | 1 | 11:17 | Morning | Thursday | 2017 | 10
7069 | 2017-10-26 11:17 | 2017-10-28 08:00 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning | 12 | Checked and found 13.8KV VCB #3 T/R 1x Ctr: 190-191 R/F: @2 51N. Patrolled the line and found Flash over dead end insulator o/p 31-AR-25. Cause: Lightning. |  | 1 | 11:17 | Morning | Thursday | 2017 | 10
7070 | 2017-10-27 10:38 | 2017-10-27 10:38 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 104 | 10:30 Manually open 13.8 KV Nella VCB fdr #1. due to : Replaced 150 KVA Tx to 100 KVA Tx at well Bangko #63. Replaced 150 KVA Tx and @2 b/o fuse at well Bangko #35. 11:02 Blocked and closed 13.8 KV VCB fdr #1. then release the block. Cause : Plan Maintenance. |  | 1 | 10:38 | Morning | Friday | 2017 | 10
7071 | 2017-10-27 14:55 | 2017-10-27 14:55 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | 35 | 14:55 Manual open Bangko 13,8 KV OCB fdr #1. Replaced b/o Fuse @2, @3, 300 Kva TX at Bangko #62 15:02 Closed Bangko 13.8 KV OCB fdr #1. Cause: Plant Maintenance. |  | 1 | 14:55 | Afternoon | Friday | 2017 | 10
7072 | 2017-10-28 09:07 | 2017-10-28 09:07 | 13.8KV MENGGALA FEEDER #1 | Fair | Planned Maintenance | 5 | 09:07 Manually opened recl.19-OA-01 d/s Menggala Fdr #1 due to : Replaced @1, @2 b/o fuse for 300 Kva Tx at well Meso #08. 09:08 Manually closed 19-OA-01 d/s Menggala Fdr #1. Cause : Plan Maintenace. |  | 1 | 9:07 | Morning | Saturday | 2017 | 10
7073 | 2017-10-28 14:40 | 2017-10-28 14:40 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 56 | 14:40 Manually opened recl.36-CT-10 d/s CKB Fdr #1 due to : Replaced Switchboard at well KB #377. 15:22 Manually blocked and closed recl.36-CT-10 and then release the blocked. Cause : Plan Maintenace. |  | 1 | 14:40 | Afternoon | Saturday | 2017 | 10
7074 | 2017-10-29 14:37 | 2017-10-29 14:37 | 13.8KV 8D FEEDER #1 | Fair | Unidentified | 0 | 8D 13.8 Kv OCB fdr #1 T/R 1x Not checked yet. |  | 1 | 14:37 | Afternoon | Sunday | 2017 | 10
7075 | 2017-10-29 14:37 | 2017-01-11 14:37 | 13.8KV 8D FEEDER #1 | Fair | Unidentified | 0 | Checked & found, 8D OCB fdr #1 T/R 1x ctr: 301-302 R/F: None. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:37 | Afternoon | Sunday | 2017 | 10
7076 | 2017-10-29 14:37 | 2017-10-29 14:37 | MINAS SWITCH YARD | Fair | Unidentified | 0 | 14:37 Minas 115 Kv GCB #31 T/R 1 X . Minas 115 Kv GCB #33 T/R 1 X . (115KV Line Minas-Lukut T/R) Not checked yet. |  | 1 | 14:37 | Afternoon | Sunday | 2017 | 10
7077 | 2017-10-29 14:37 | 2017-03-11 14:37 | MINAS SWITCH YARD | Fair | Unidentified | 0 | Checked & found, Minas 115 Kv GCB #31 T/R 1 X ctr: 188-189 R/F: 76. Minas 115 Kv GCB #33 T/R 1 X ctr: 325-326 R/F: 76. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:37 | Afternoon | Sunday | 2017 | 10
7078 | 2017-10-29 15:27 | 2017-10-29 15:27 | 13.8KV 8D FEEDER #11 | Fair | Planned Maintenance | 0 | 15:27 Manual opened 13.8 Kv VCB 8 D fdr #11 ,----->Closed at 15:33. adjusted Tapping 300 KVA TX , Tap.B to E R/M: 150 HP to 120 HP. Voltage:1050 Volt. to 1230 Volt. at well 9 D - 14 E. Plan maintenance. |  | 1 | 15:27 | Afternoon | Sunday | 2017 | 10
7079 | 2017-10-30 04:23 | 2017-10-30 04:23 | NORTH RUMBAI SUBSTATION | Fair | Under investigation | 0 | 04:23 N.Rumbai C/S T/O 05:38 Open Fdr#1 and 2 05:38 Try to closed GCB 44Kv ( Trip ) R/f 86T/87T ( Reset ) Checked but found nothing 05:47 Closed GCB 44 Kv ( success ) 05:48 Closed 4,16 Kv Fdr # 2 and Fdr #1 Caused : Under investigation . |  | 1 | 4:23 | Morning | Monday | 2017 | 10
7080 | 2017-10-30 09:00 | 2017-10-30 09:00 | 13.8KV DARLING VCB FEEDER #3 | Fair | Animal | 41 | 09:00 It was reported no power o/p 05 N3 14. 10:08 Checked and found Recloser 05 N3 02 T/SO ctr:120-121. Blocked and closed the Recloser. OK then released the block. Not patrolled yet. |  | 1 | 9:00 | Morning | Monday | 2017 | 10
7081 | 2017-10-30 09:00 | 2017-05-11 09:00 | 13.8KV DARLING VCB FEEDER #3 | Fair | Animal | 41 | Patrolled the line & found an animal (Monkey) on Pole 05-N3-14. Cause: Animal (Monkey). |  | 1 | 9:00 | Morning | Monday | 2017 | 10
7082 | 2017-10-30 09:26 | 2017-10-30 09:26 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Planned Maintenance | 159 | 09:26 O/C Petapahan 13.8 KV VCB fdr #3. Adjusted voltage for 300 KVA TX , 80 HP - 40 HP at Petapahan #062. Adjusted voltage for 300 KVA TX , 100 HP - 50 HP at well Petapahan #93. 14:56 C/O USD to SWB at well Petapahan #088. 15:03 O/C fuse to C/O step up VST TX at well Petapahan #112. Plan maintenance. |  | 1 | 9:26 | Morning | Monday | 2017 | 10
7083 | 2017-10-30 15:30 | 2017-10-30 15:30 | 13.8KV BATANG FEEDER #2 | Fair | Planned Maintenance | 20 | 15:30 Manually Opec Batang 13.8KV OCB fdr #2,---->Closed at 16:38. Disconnected and connected H&P Units from RBS 069 to RBS 050. Plan Maintenance. |  | 1 | 15:30 | Afternoon | Monday | 2017 | 10
7084 | 2017-10-30 21:38 | 2017-10-30 21:38 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Tree | 328 | 21:38 Minas ACB fdr#4 T/LO, Ctr: 79-81, R/F: 51N, 51 @1@3. Patrolled the Line, but found nothing. (Recl. 7D.150 in bypass status). 24:20 Man. Closed Minas ACB fdr#4, but failed. Continued re patrolled the Line. 02:34 Open By Pass Recloser 7D.150, to isolate the problem. Man. Closed Minas ACB fdr#4 Cause: Unidentified (Will Continued re patrol) |  | 1 | 21:38 | Night | Monday | 2017 | 10
7085 | 2017-10-30 21:38 | 2017-10-31 08:14 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Tree | 328 | 08:14 Patrolled the line & found Dangers tree at well 8D-32. Broken @1,@2,@3 B/O fuse for 300KVA TX at well 8D-32. 08:16 Open LBS 8D-32. 08:17 Closed LBS 8D-151 (feed 8D fdr #7). 8 Well off ( 8D-31,22,19,21,32,33,42) waiting trimming Danger Trees. |  | 1 | 21:38 | Night | Monday | 2017 | 10
7086 | 2017-10-30 21:38 | 2017-02-11 16:21 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Tree | 328 | Manually opened Minas ACB fdr #4 due to : - Re-Energized 8 wells d/s LBS : 8D-32. - Do Normalize Part Load 8D fdr #7 to Minas fdr #4. - Blocked and Closed Minas fdr #4. - Closed LBS : 8D-32 (Paraler 8D fdr#7 to Minas fdr #4) Load : 8D fdr #7 257A Minas fdr #4 = 110A. - Closed LBS : 8D-151 (Sparated 8D fdr#7 and Minas fdr #4) Load : 8D fdr #7 230A Minas fdr #4 = 155A. |  | 1 | 21:38 | Night | Monday | 2017 | 10
7087 | 2017-10-30 22:05 | 2017-10-30 22:05 | 115KV DURI - KOTABATAK JUNCTION LINE | Rain and Lightning | Lightning | 0 | 22:05 115KV Line KBJ-DRB T/SO, (KBJ R/F: .......) 115KV KBJ GCB# 43 T/SO, 115KV KBJ GCB# 45 T/SO, Not checked yet 115KV Line DRB-KBJ T/SO, (DRB R/F: L90, D60). 115KV DRB OCB#26 T/SO, Cttr: N/A. 115KV DRB OCB #28 T/SO, Ctr: 174-175. 23:37 Checked & found 115KV Line DRB-KBJ T/SO, (DRB R/F: L90, D60). Man Closed 115KV DRB OCB#26 &#28, after reseted the Relay. Not Patrolled yet. |  | 1 | 22:05 | Night | Monday | 2017 | 10
7088 | 2017-10-30 22:05 | 2017-10-31 09:05 | 115KV DURI - KOTABATAK JUNCTION LINE | Rain and Lightning | Lightning | 0 | 09:50 Checked & foud 115 KV Line KBJ -DRB, GCB #43 T/SO ctr:423-424 R/F:87 LC. GCB #45 T/SO ctr:307-308 @1,@2. 10:00 Closed 115 KV line KBJ - DRB, GCB #43. Closed 115 KV Line KBJ - DRB, GCB #45. Not Patrolled yet, |  | 1 | 22:05 | Night | Monday | 2017 | 10
7089 | 2017-10-30 22:05 | 26/11/2017 08:05 | 115KV DURI - KOTABATAK JUNCTION LINE | Rain and Lightning | Lightning | 0 | Patrolled the line & found Sawit touch the line pole DK-46. @1 Broken Suspention Insulator o/p DK-56. @1 Broken Dead End Insulator o/p DK-58. @2 Flashed over Suspention Insulator o/p DK-59. Danger trees touch line Pole. DK-65. Cause; Lightning. |  | 1 | 22:05 | Night | Monday | 2017 | 10
7090 | 2017-10-31 10:06 | 2017-10-31 10:06 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 91 | 10:04-10:06 Open & Closed 13.8 KV S.Balam fdr#4. Set voltage for 150 TX at well S.Balam #424. Planned maintenance. |  | 1 | 10:06 | Morning | Tuesday | 2017 | 10
7091 | 2017-10-31 14:46 | 2017-10-31 14:46 | 13.8KV 8D FEEDER #10 | Fair | Planned Maintenance | 90 | 14:46 Manually opened 13.8 KV 8D VCB fdr #10. Replaced 150KVA with 300KVA Tx at well 7F-51. 15:05 Manually Blocked and Closed 13.8Kv 8D fdr #10, then release the block. Planned Maintenannce. |  | 1 | 14:46 | Afternoon | Tuesday | 2017 | 10
7092 | 2017-10-31 15:10 | 2017-10-31 15:10 | 13.8KV BEKASAP FEEDER #3 | Fair | Planned Maintenance | 0 | 15:10-15:12 Manually Open & Closed Recl. 38-BD-18 )Bekasap fdr#3). Set Voltage for 300Kva Tx at well Bekasap #17. (Tap. 1-3 . Voltage:920-970V). Planned Maintenance. |  | 1 | 15:10 | Afternoon | Tuesday | 2017 | 10
7093 | 2017-01-11 02:37 | 2017-01-11 02:37 | MINAS POWER PLANT | Fair | Under investigation | 0 | 02:37 MGT #10 Tripped off by Auto reboot Computer (R) Trip. Cause: Under investigation. |  | 1 | 2:37 | Night | Wednesday | 2017 | 1
7094 | 2017-01-11 03:28 | 2017-01-11 03:28 | MINAS POWER PLANT |  |  | - | 03:28 MGT #5 S/U and On line to the system at 03:39 to restore load. |  | 1 | 3:28 | Night | Wednesday | 2017 | 1
7095 | 2017-01-11 11:27 | 2017-01-11 11:27 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 174 | 11:27 Manually Open 4D 13.8KV OCB fdr #2, -----> Closed at 13:40. Manually Open LBS 3D-66, -----> Closed at 13:56. 13:59 Manually Open 4D 13.8KV OCB fdr #5. (Transfer all Load 4D fdr #5 to 4D fdr #2). Plan Maintenance. Production Loss: 199Bbls / 27 Wells. |  | 1 | 11:27 | Morning | Wednesday | 2017 | 1
7096 | 2017-01-11 11:38 | 2017-01-11 11:38 | KETIGUL SUBSTATION | Fair | Planned Maintenance | 3152 | 11:38 Started to Shut down 115KV Line Rokan - Ketigul. Shut Down Rokan Subtation. Shut down Ketigul Substation. 11:49 Manually Open 13.8KV Rokan fdr #2. ----->Closed at 18:04. 11:51 Manually Open 13.8KV Rokan fdr #3. ----->Closed at 18:04. 11:52 Manually Open 13.8KV Rokan fdr #4. ----->Closed at 17:55. 11:54 Manually Open 13.8KV Ketigul fdr #1. ----->Closed at 18:07. 11:55 Manually Open 13.8KV Ketigul fdr #2. ----->Closed at 18:07. 11:56 Manually Open 13.8KV Ketigul fdr #3. ----->Closed at 18:08. 12:13 Manually Open 115KV Ketigul GCB #1. ----->Closed at 17:49. 12:14 Manually Open 115KV Ketigul GCB #3. ----->Closed at 18:01. 13:00 Manually Open 115KV Rokan GCB #12. ----->Closed at 17:58. Plan Maintenance. (Service/repair 115KV Isolation Switch of GCB #11 Rokan Substation.) (Change out Neutral Grounding Resistor of Substation). 12:27 115KV CDSY OCB #31 T/R 3x. 115KV CDSY OCB #33 T/R 3x. (115KV CDSY - Batang Line) Frequency up to : 60:41. Respectively over Voltage at Bangko area. 1. Sintong VCB fdr #1 T/O Manually blocked and closed at 12:40. 2. Sintong VCB fdr #2 T/O Manually blocked and closed at 12:40. 3. Pinang VCB fdr #1 T/O Manually blocked and closed at 12:37. 4. Menggala VCB fdr #1 T/O Manually blocked and closed at 12:38. 5. Bangko VCB fdr #1 T/O Manually blocked and closed at 12:41. 6. Nella fdr #1 Load dropped 171A (257-86A). 7. Nella fdr #2 Load dropped 70A (92-22A). 14:05 Manually Rangau 13.8KV OCB fdr #2, -----> Closed at 14:47. 14:05 Manually Pematang 13.8KV OCB fdr #2, -----> Closed at 14:51. 14:06 Manually Pematang 13.8KV OCB fdr #1, -----> Closed at 14:48. 14:07 Manually Rangau 13.8KV OCB fdr #1, -----> Closed at 14:47. 14:21 Manually Open Pematang Main 44KV OCB #1, ----->Closed at 14:50 (44KV line to Petani Substation) 14:39 Manually Open 115KV C. Duri GCB #43, ----->Closed at 14:44. 14:40 Manually Open 115KV C. Duri GCB #45, ----->Closed at 14:44. Plan Maintenance. (Due to Rokan 115KV GCB #12 Isolation Switch Can Not Fully Open) 17:30 Manually Rangau 13.8KV OCB fdr #2, -----> Closed at 17:36. 17:31 Manually Pematang 13.8KV OCB fdr #2, -----> Closed at 17:35.. 17:32 Manually Pematang 13.8KV OCB fdr #1, -----> Closed at 17:34. 17:30 Manually Rangau 13.8KV OCB fdr #1, -----> Closed at 17:35. 17:30 Manually Open Pematang Main 44KV OCB #1, ----->Closed at ...... Plan Maintenance. (To Closed Line Switch o/p PPR 44). Production loss: Sintong fdr #1 : 41 Bbls / 24 Wells. Sintong fdr #2 : 117 Bbls / 56 Wells. Pinang fdr #1 : 31 Bbls / 26 Wells. Menggala fdr #1 : 58 Bbls / 34 Wells. Bangko fdr #1 : 106 Bbls / 60 Wells. S. Balam fdr #1 : 131 Bbls / 98 Wells. Petani fdr #1 : 90 bbls / 37 wells. Petani fdr #2 : 51 bbls / 23 wells. Rokan fdr #2 : 123 bbls / 8 wells. Ketigul fdr #1 : 312 bbls / 20 wells. Ketigul fdr #2 : 1140 bbls / 49 wells. Ketigul fdr #3 : 149 bbls / 4 wells. Rangau fdr #1 : 4 bbls / 5 wells. Rangau fdr #2 : 59 bbls / 10 wells. Pematang fdr#1 : 101 bbls / 19 wells. Pematang fdr#2 : 115 Bbls / 14 wells. Grand Total Prod. Loss : 2628 Bbls / 487 Wells. | 1111 | 1 | 11:38 | Morning | Wednesday | 2017 | 1
7097 | 2017-01-11 14:16 | 2017-01-11 14:16 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning Arrester | 0 | Bangko 13.8KVOCB fdr #4 T/R 1X. Bangko GFPC T/R 1X. Not checked yet. |  | 1 | 14:16 | Afternoon | Wednesday | 2017 | 1
7098 | 2017-01-11 14:16 | 2017-03-11 08:00 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning Arrester | 0 | Checked and found 13.8 KV OCB #4 T/R 1x Ctr: 15-16 R/F: @1 51N. Patrolled the line and found Broken L/A o/p 28-Y-04. Cause: Lightning Arrester. |  | 1 | 14:16 | Afternoon | Wednesday | 2017 | 1
7099 | 2017-01-11 15:18 | 2017-01-11 15:18 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Planned Maintenance | 19 | 15:18 Manually opened Petapahan VCB fdr #6 due to : 1. Install 300 Kva Tx at well PH #49 (reactive well). 2. Changed out 500 Kva to 550 Kva at well PH #23. 3. Adjust voltage due to changed R/M from 300 to 200 HP at well PH #32. 16:23 Manually blocked and closed Petapahan VCB fdr #6 and then released the block. Cause: Plan maintenance. |  | 1 | 15:18 | Afternoon | Wednesday | 2017 | 1
7100 | 2017-01-11 15:28 | 2017-01-11 15:28 | 13.8KV NELLA FEEDER #1 | Fair | Transformer Failure | 0 | 15:28 Nella 13.8KV VCB fdr #1 T/O (On Block Position), then closed at 15:34. Nella GFPC T/R 1X. Not checked yet. Prod. Loss sudah digabung dengan even at 11:38 (01/11/2017). | 11111 | 1 | 15:28 | Afternoon | Wednesday | 2017 | 1
7101 | 2017-01-11 15:28 | 2017-02-11 16:00 | 13.8KV NELLA FEEDER #1 | Fair | Transformer Failure | 0 | Checked All Recl. D/S Nella fdr#1 Not operated. Patrolled the line & found, @3,@2 B/O fuse for 150Kva Tx at well Bangko#128. Performed TTR & Megger test, found the Tx was failure. Replaced the failure Transformer above with the same size then energized the Tx. Cause: Transformer Failure. | 11111 | 1 | 15:28 | Afternoon | Wednesday | 2017 | 1
7102 | 2017-01-11 15:46 | 2017-01-11 15:46 | 13.8KV 8D FEEDER #2 | Fair | Planned Maintenance | 72 | 15:46 Manually opened 8D OCB fdr #2 due to: 1. Install Tx at well 8E 45 (reactive well). 2. Changed out VSD to Switch board at well 8E 45N. 3. Trouble shoot switch board at well 8E 45N. 4. Install Scada monitor at well 8E 53N. Manually blocked and closed 8D OCB fdr #2 and then released the block. Cause: Plan Maintenance. |  | 1 | 15:46 | Afternoon | Wednesday | 2017 | 1
7103 | 2017-01-11 20:35 | 2017-01-11 20:35 | MINAS POWER PLANT |  |  | - | 20:35 MGT #10 S/U and On line to the system at 20:57 to restore load. |  | 1 | 20:35 | Night | Wednesday | 2017 | 1
7104 | 2017-01-11 22:25 | 2017-01-11 22:25 | MINAS POWER PLANT |  |  | - | 22:25 S/D CGT #1 and shutdown. |  | 1 | 22:25 | Night | Wednesday | 2017 | 1
7105 | 2017-02-11 06:03 | 2017-02-11 06:03 | CENTRAL DURI POWER PLANT |  |  | - | 06:03 Off line and then S/D CGT #5 for S/B. |  | 1 | 6:03 | Morning | Saturday | 2017 | 2
7106 | 2017-02-11 09:55 | 2017-02-11 09:55 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 20 | 09:55 Manually opened recl. 22-V-01 d/s Nella fdr #1 due to : 1. Replaced b/o fuse at well Bangko #164. 2. Replaced b/o fuse at well Bangko #184. 1. Replaced b/o fuse at Station #C 10:43 Manually blocke and closed Recloser 22-V-01, then realease the block. Cause : Planed Maintenance. |  | 1 | 9:55 | Morning | Saturday | 2017 | 2
7107 | 2017-02-11 10:34 | 2017-02-11 10:34 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Construction Job | 0 | 10:34 Manually opened Petpahan VCB fdr #4 due to : Tie In new well at PTH #140. 10:40 Manually blocke and closed PTH VCB fdr #4 then release the blocked. Cause : Construction Job. |  | 1 | 10:34 | Morning | Saturday | 2017 | 2
7108 | 2017-02-11 10:44 | 2017-02-11 10:44 | 13.8KV BEKASAP FEEDER #6 | Fair | Planned Maintenance | 132 | 10:44 Manually opened So Bekasap OCB fdr #6 due to : Replaced b/o fuse at well Bekasap #94 and Bekasap #127. 11:55 Manually blocked and closed So Bekasap fdr #6, then release the block. Cause : Plan MAintenance. |  | 1 | 10:44 | Morning | Saturday | 2017 | 2
7109 | 2017-02-11 10:53 | 2017-02-11 10:53 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 44 | 10:53 Manually opened recloser 21-V-01 d/s Nella fdr #1 due to : Replaced 150 KVa Tx at with 225 KVa Tx at well Bangko #128. 11:05 Manually blocke and closed 21-V-01, then release the block . Cause : Plan Maintenance. |  | 1 | 10:53 | Morning | Saturday | 2017 | 2
7110 | 2017-02-11 13:21 | 2017-02-11 13:21 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | 13:21 It was reported b/o fuse at near Talang #50 o/p 2.DG.12. 17:05 Manually Opened LBS :1F.27.3 d/s Duri Community fdr #3. 17:09 Replaced @2 b/o fuse for 50 KVa Tx o/p 2.DG.12. 17:16 Manually block and Closed LBS :1F.27.3 d/s Duri Community fdr #3. then release the blocked. Cause : Animal (Snake). |  | 1 | 13:21 | Afternoon | Saturday | 2017 | 2
7111 | 2017-02-11 16:43 | 2017-02-11 16:43 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified (Fuse) | 243 | It was reported b/o fuse at well Neno #21 d/s Manggala fdr #1 Not checked yet. |  | 1 | 16:43 | Afternoon | Saturday | 2017 | 2
7112 | 2017-02-11 16:43 | 2017-04-11 09:26 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified (Fuse) | 243 | Checked and found @2 b/o fuse for 500 Kva Tx at well Meno #21. Replaced b/o fuse above and energized the Tx. Cause: Unidentified (fuse). (See Outage on 4 Nov at 09:26) |  | 1 | 16:43 | Afternoon | Saturday | 2017 | 2
7113 | 2017-02-11 19:17 | 2017-02-11 19:17 | 13.8KV 6DN FEEDER #6 | Rain | Lightning | 73 | 19:17 6DN fdr #6 T/R 1X. 19:23 6DN FDR #6 T/R again 1X. Not checked yet. |  | 1 | 19:17 | Night | Saturday | 2017 | 2
7114 | 2017-02-11 19:17 | 2017-04-11 19:17 | 13.8KV 6DN FEEDER #6 | Rain | Lightning | 73 | Checked & found, 6DN OCB fdr #6 T/R 1x ctr: 355 (did not operate) R/F: 50N. Patrolled the line & found, @2 broken Pin insulator on Pole 6D-47N. Cause: Lightning. |  | 1 | 19:17 | Night | Saturday | 2017 | 2
7115 | 2017-02-11 19:47 | 2017-02-11 19:47 | MINAS POWER PLANT | Rain | Under investigation | 0 | 19:47 MGT #10 Tripped off by alarm Hight Vibration Trip. Cause: Under investigation. |  | 1 | 19:47 | Night | Saturday | 2017 | 2
7116 | 2017-02-11 20:15 | 2017-02-11 20:15 | MINAS POWER PLANT |  |  | - | 20:15 MGT #5 S/U and On line to the system at 20:25 to restore load. |  | 1 | 20:15 | Night | Saturday | 2017 | 2
7117 | 2017-03-11 06:27 | 2017-03-11 06:27 | 13.8KV 6D FEEDER #5 | Fair | Unidentified | 85 | 6D fdr #5 load dropped 155A (219-64A) 6D fdr #6 load dropped 239A (247-8A). ---->WIP. Not checked yet. |  | 1 | 6:27 | Morning | Saturday | 2017 | 3
7118 | 2017-03-11 06:27 | 2017-04-11 06:27 | 13.8KV 6D FEEDER #5 | Fair | Unidentified | 85 | Checked & found, 6D OCB fdr #5 T/R 1x ctr: 778-779 R/F: 51 @2, @3 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:27 | Morning | Saturday | 2017 | 3
7119 | 2017-03-11 09:48 | 2017-03-11 09:48 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 72 | 09:48 Manually opened Bangko OCB fdr #4 due to : - Replaced @1,2 b/o fuse for 150 KVa Tx at well BKO #321. - Replaced @1,3 b/o fuse for 150 KVa Tx at well BKO #137. 09:53 Manually blocked and closed Bangko OCB fdr #4, then release the blocked. Cause : Plan Maintenance. |  | 1 | 9:48 | Morning | Saturday | 2017 | 3
7120 | 2017-03-11 14:40 | 2017-03-11 14:40 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 22 | 14:40 Manually opened Recloser:36-CT-10 D/S CKBS #1 due to : - Opened and closed FCO due to replaced vacuum on switch board at well KB #337. - Opened and closed FCO due to repaired Bus Fuse at well KB # 395. 15:03 Manually blocked and closed Recloser:36-CT-10 then release the blocked. Cause : Plan Maintenance. |  | 1 | 14:40 | Afternoon | Saturday | 2017 | 3
7121 | 2017-03-11 14:48 | 2017-03-11 14:48 | 13.8KV PETANI FEEDER #2 | Fair | Planned Maintenance | 86 | 14:48 Manually opened Petani OCB fdr #2 due to: - Changed out 150 Kva Tx failure with 225 Kva Tx at well Petani #80. 15:53 Manually blocked and closed Petani OCB fdr #2 then release the blocked. Cause : Plan Maintenance. |  | 1 | 14:48 | Afternoon | Saturday | 2017 | 3
7122 | 2017-03-11 15:01 | 2017-03-11 15:01 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 15 | 15:01 Manually opened Recloser:26-AK-02 D/S Ketigul fdr #2 due to : - Adjust voltage for 300 Kva Tx at well UBI #37 (VSD to Switch board). 15:05 Manually blocked and closed Recloser:26-AK-02 then release the blocked. Cause : Plan Maintenance. |  | 1 | 15:01 | Afternoon | Saturday | 2017 | 3
7123 | 2017-03-11 16:15 | 2017-03-11 16:15 | 13.8KV 6D FEEDER #5 | Fair | Planned Maintenance | 55 | 16:15 Manually opened LBS:5D-57 D/S 6D OCB fdr #5 due to : - Changed out 300 Kva Tx with 250 Kva at well 6D-31E. 16:40 Manually closed Recloser:LBS:5D-57. Cause : Plan Maintenance. |  | 1 | 16:15 | Afternoon | Saturday | 2017 | 3
7124 | 2017-03-11 16:17 | 2017-03-11 16:17 | 13.8KV PETANI FEEDER #1 | Fair | Planned Maintenance | 72 | 16:17 Manually opened Recloser: 33-AY-47 D/S Petani fdr #1 due to: - Replaced VSD to S3witch board at well Petani #46. 17:18 Manually closed LBS: 33-AX-36 due to Recloser 33-AY-47 failed to closed. (Part load Petani fdr #1 transfer to Petani fdr #2) Cause: Plan Maintenance. |  | 1 | 16:17 | Afternoon | Saturday | 2017 | 3
7125 | 2017-03-11 17:20 | 2017-03-11 17:20 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 0 | 17:20 Rangau fdr#2 load drooped 102A(117-15A). Cause : Not checked yet. |  | 1 | 17:20 | Afternoon | Saturday | 2017 | 3
7126 | 2017-03-11 17:20 | 2017-05-11 17:20 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recloser 23-BD-01 T/R 1x ctr: 310-311. Patrolled the line & found, @1 broken Pin Insulator on Pole NN to Well Jorang #11. Cause: Lightning. |  | 1 | 17:20 | Afternoon | Saturday | 2017 | 3
7127 | 2017-03-11 17:56 | 2017-03-11 17:56 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | 17:56 Menggala fdr#1 load dropped 41A (192 - 151 A). Menggala GFPC T/R 1X. Cause : Not checked yet. |  | 1 | 17:56 | Afternoon | Saturday | 2017 | 3
7128 | 2017-03-11 17:56 | 2017-04-11 17:56 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recloser 19-AO-01 T/R 1x ctr: 481-482. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:56 | Afternoon | Saturday | 2017 | 3
7129 | 2017-03-11 20:15 | 2017-03-11 20:15 | MINAS POWER PLANT |  |  | - | 20:15 S/U MGT#6 at online 20:49. |  | 1 | 20:15 | Night | Saturday | 2017 | 3
7130 | 2017-04-11 07:05 | 2017-04-11 07:05 | 13.8KV MINAS FEEDER #6 | Fair | Unidentified | 79 | Minas ACB #18 (fdr #6) T/R 1x. Not checked yet. |  | 1 | 7:05 | Morning | Tuesday | 2017 | 4
7131 | 2017-04-11 07:05 | 2017-06-11 07:05 | 13.8KV MINAS FEEDER #6 | Fair | Unidentified | 79 | Checked & found, Minas ACB #18 T/R 1x ctr: 169-170 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:05 | Morning | Tuesday | 2017 | 4
7132 | 2017-04-11 09:26 | 2017-04-11 09:26 | 13.8KV MENGGALA FEEDER #1 | Fair | Planned Maintenance | 51 | 09:26 Manually open recl 19 AN 04 d/s Menggala fdr#1 due to: 1.Replace @1 b/o fuse at well Meno # 21 for 500Kva Tx. 2.Replace @3 b/o fuse at well Meno # 12 for 150Kva Tx. 09:35 Manually blocked and close recl. 19 AN 04. Cause : Plan maintenance. (See PIDOD on 02 Nov at 16:43) |  | 1 | 9:26 | Morning | Tuesday | 2017 | 4
7133 | 2017-04-11 11:07 | 2017-04-11 11:07 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 31 | Pinang OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 11:07 | Morning | Tuesday | 2017 | 4
7134 | 2017-04-11 11:07 | 2017-05-11 11:07 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 31 | Checked & found, Pinang OCB fdr #1 T/R ctr: 423-425 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 11:07 | Morning | Tuesday | 2017 | 4
7135 | 2017-04-11 14:00 | 2017-04-11 14:00 | MINAS POWER PLANT |  |  | - | Off line MGT#4 then S/D the unit for S/B. |  | 1 | 14:00 | Afternoon | Tuesday | 2017 | 4
7136 | 2017-04-11 14:30 | 2017-04-11 14:30 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 54 | 14:30 Manually open recl. 22 V 01 d/s Nella fdr#1 due to: Replace @2 b/o fuse for 300Kva Tx at well Bangko#59. 14:38 Manually blocked and close recl.22 V 01. Cause : Plan maintenance. |  | 1 | 14:30 | Afternoon | Tuesday | 2017 | 4
7137 | 2017-04-11 14:34 | 2017-04-11 14:34 | MINAS POWER PLANT |  |  | - | 14:34 S/U MGT#10 then online the unit at 15:03. (Running test). 16:12 MGT#10 Trip by Vibration test at 24Mw. (No load shedding). |  | 1 | 14:34 | Afternoon | Tuesday | 2017 | 4
7138 | 2017-05-11 14:08 | 2017-05-11 14:08 | 13.8KV SINTONG FEEDER #1 | Fair | Planned Maintenance | 9 | 14:08 Manually opened Recl :26-AE-22 d/s Sintong fdr#1 due to Adjust voltage at well Kerang#08. 14:10 Manually closed recl.26 AE 22. Cause : Plan maintenance. |  | 1 | 14:08 | Afternoon | Thursday | 2017 | 5
7139 | 2017-05-11 16:13 | 2017-05-11 16:13 | 13.8KV BANGKO FEEDER #4 | Cloudy | Lightning | 54 | Bangko VCB fdr#4 T/R 1x. Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 16:13 | Afternoon | Thursday | 2017 | 5
7140 | 2017-05-11 16:13 | 2017-06-11 10:41 | 13.8KV BANGKO FEEDER #4 | Cloudy | Lightning | 54 | Checked & found, Bangko OCB fdr #4 T/R 1x ctr: 017-018 R/F: 51N. Patrolled the line & found @3 broken Lightning Arrester on Pole 27-Y-13. Cause: Lightning. |  | 1 | 16:13 | Afternoon | Thursday | 2017 | 5
7141 | 2017-05-11 16:13 | 2017-05-11 16:13 | 13.8KV BANGKO FEEDER #1 | Cloudy | Lightning | 100 | Bangko fdr#1 load dropped 158A(222-64). Not checked yet. |  | 1 | 16:13 | Afternoon | Thursday | 2017 | 5
7142 | 2017-05-11 16:13 | 2017-06-11 10:13 | 13.8KV BANGKO FEEDER #1 | Cloudy | Lightning | 100 | Checked & found, Recloser 23-X-08 T/R 1x ctr: 278-279. Patrolled the line & found @3 broken Lightning Arrester on Terminal Pole of Bangko #89. Cause: Lightning. |  | 1 | 16:13 | Afternoon | Thursday | 2017 | 5
7143 | 2017-05-11 16:13 | 2017-05-11 16:13 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 14 | So.Balam fdr#4 load dropped 83A(206-123A). So.Balam fdr#1 load dropped 33A(131-98A). Not checked yet. |  | 1 | 16:13 | Afternoon | Thursday | 2017 | 5
7144 | 2017-05-11 16:13 | 2017-07-11 14:41 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 14 | Checked & found, no Recloser operated under Balam fdr #1 & #4. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:13 | Afternoon | Thursday | 2017 | 5
7145 | 2017-05-11 16:42 | 2017-05-11 16:42 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 85 | Ketigul VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 16:42 | Afternoon | Thursday | 2017 | 5
7146 | 2017-05-11 16:42 | 20/11/2017 16:42 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 85 | Checked & found, Ketigul VCB fdr #2 T/R 1x ctr: did not change R/F: None. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:42 | Afternoon | Thursday | 2017 | 5
7147 | 2017-05-11 17:57 | 2017-05-11 17:57 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 0 | 4B VCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 17:57 | Afternoon | Thursday | 2017 | 5
7148 | 2017-05-11 17:57 | 2017-06-11 17:57 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, 4B OCB fdr #5 T/R 1x ctr: 120-121 R/F: 50N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:57 | Afternoon | Thursday | 2017 | 5
7149 | 2017-06-11 10:27 | 2017-06-11 10:27 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Secondary Cable | 0 | 10:27 It was reported @1 Secondary cable break o/p 06-Q1-13 d/s CD #14. near loc.: 7P-83C. 15:17 Checked and founded @1 broken jumper o/p 06-Q1-13. Cause : Broken Jumper. |  | 1 | 10:27 | Morning | Sunday | 2017 | 6
7150 | 2017-06-11 11:28 | 2017-06-11 11:28 | 13.8KV PINANG FEEDER #1 | Fair | Planned Maintenance | 40 | 11:28 Manually opened Pinang VCB fdr #1 due to : Setting voltage for 150 Kva Tx at well Pinang #32. from 460 - 980 volt, (42HP - 105HP). 11:37 Manually blocked and closed Pinang VCB fdr #1, then release the block. Cause : Plan Maintenance. |  | 1 | 11:28 | Morning | Sunday | 2017 | 6
7151 | 2017-06-11 12:00 | 2017-06-11 12:00 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 147 | 12:00 Manually opened So Balam fdr #4 due to : Replace @2,@3 fuse for 150 Kva Tx witch the same size at well #302. 12:04 Manually blocked and closed So Balam fdr #4, then release the blockek Cause : Plan Maintenance. |  | 1 | 12:00 | Afternoon | Sunday | 2017 | 6
7152 | 2017-06-11 18:58 | 2017-06-11 18:58 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 36 | 4B VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 18:58 | Afternoon | Sunday | 2017 | 6
7153 | 2017-06-11 18:58 | 2017-09-11 18:58 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 36 | Checked & found, 4B OCB fdr #2 T/R 1x ctr: 265-266 R/F: 51 @2. Patrolled the line & found, @2 broken Lightning Arrester on Pole to Well 4B-94 (OBS Well). Cause: Lightning. |  | 1 | 18:58 | Afternoon | Sunday | 2017 | 6
7154 | 2017-06-11 20:08 | 2017-06-11 20:08 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 48 | 20:08 8C fdr #1 load dropped 139A ( 184-45A ). 8C fdr #2 load dropped 10A ( 74-64A ). 8C fdr #3 load dropped 13A ( 199-186A ) Not Checked yet. |  | 1 | 20:08 | Night | Sunday | 2017 | 6
7155 | 2017-06-11 20:08 | 20/11/2017 08:08 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 48 | Checked and found 13.8KV VCB #1 T/R 2x Ctr: 674-676. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 20:08 | Night | Sunday | 2017 | 6
7156 | 2017-06-11 20:39 | 2017-06-11 20:39 | 13.8KV BEKASAP FEEDER #3 | Heavy Rain | Lightning | 0 | 20:39 Bekasap 13,8KV ACB fdr #3 load dropped 92A ( 152-61A ). Bekasap 13,8KV ACB fdr #6 load dropped 58A ( 83-25A ). S.Bekasap 13.8KV OCB fdr #1 load dropped 41A ( 130-82A ). Not Checked yet. |  | 1 | 20:39 | Night | Sunday | 2017 | 6
7157 | 2017-06-11 20:39 | 14/11/2017 08:00 | 13.8KV BEKASAP FEEDER #3 | Heavy Rain | Lightning | 0 | Checked and found Recloser 38-BD-18 T/R 3x Ctr:82-85 Patrolled the line and found @1 Chipping Dead end insulator o/p 38-BD-23. Cause: Lightning. |  | 1 | 20:39 | Night | Sunday | 2017 | 6
7158 | 2017-06-11 21:36 | 2017-06-11 21:36 | 13.8KV 3D FEEDER #2 | Rain | Lightning | 37 | 21:36 3D 13.8 KV OCB #2 T/R 1X. 3D 13.8 KV OCB #4 Load dropped 10A ( 25-245A ). Not Checked yet. Prod.loss: 43 bbls / 18 Wells, -----> 3D fdr #2 11 bbls / 8 Wells, ------> 3D fdr #4 ---------------------------------------- + Total : 54 bbls / 26 Wells. |  | 1 | 21:36 | Night | Sunday | 2017 | 6
7159 | 2017-06-11 21:36 | 2017-09-11 21:36 | 13.8KV 3D FEEDER #2 | Rain | Lightning | 37 | Checked & found, 3D OCB fdr #2 T/R 1x ctr: 245-246 R/F: 51@1. Patrolled the line & found, @1 broken Dead-end Insulator on Pole 3E-02 (Near Well 3E-85). Cause: Lightning. |  | 1 | 21:36 | Night | Sunday | 2017 | 6
7160 | 2017-06-11 21:55 | 2017-06-11 21:55 | 13.8KV DURI FIELD FEEDER #2 | Rain and Lightning | Transformer Failure | 213 | 21:55 D.Field fdr#2 load dropped 94 A (274-180 A ). 00:22 It was reported no power o/p 07 T1 06,07 T5 07,and 06 S7 11. Not checked yet. |  | 1 | 21:55 | Night | Sunday | 2017 | 6
7161 | 2017-06-11 21:55 | 2017-07-11 07:40 | 13.8KV DURI FIELD FEEDER #2 | Rain and Lightning | Transformer Failure | 213 | 07:40 Checked and found Recloser 07-U3-21 T/SO Ctr: 197-198 Patrolled the line found at @2,3 b/o fuse on pole 06-S3-05 Perform TTR & megger found Loe Megger reading Manually opened LBS 06-53-02 to opened FCO ( isolated tx ) 09:57 Block & closed Recloser 07-U3-21 oK Close LBS 06-53-02 Cause Tx Failure. |  | 1 | 21:55 | Night | Sunday | 2017 | 6
7162 | 2017-06-11 22:00 | 2017-06-11 22:00 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Lightning | 0 | C.Duri 13.8 Kv ACB fdr#4 T/R. R/f : 51N. Count :505-506. Not checked yet. |  | 1 | 22:00 | Night | Sunday | 2017 | 6
7163 | 2017-06-11 22:00 | 2017-07-11 16:00 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found, C. Duri ACB #21 fdr #4 T/R ctr: 505-506 R/F: 51 @1. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 22:00 | Night | Sunday | 2017 | 6
7164 | 2017-06-11 22:13 | 2017-06-11 22:13 | 13.8KV BEKASAP FEEDER #5 | Rain and Lightning | Circuit Breaker | 8270 | 22:13 Bekasap 13.8KV ACB fdr #5 T/LO ctr:..... R/F: 51N & F60. 07-Nov-2017 ---------------------------- 00:09 Manually Open Bekasap fdr #2. --------> Closed at 10:24 00:10 Manually Open Bekasap fdr #3. --------> Closed at 04:19 00:11 Manually Open Bekasap fdr #6. --------> Closed at 06:06 01:39 Manually Open SO. Bekasap fdr #1. -----> Closed at 06:04 00:41 Patrooled the lina and found Broken LA of TX-01B. Isolated broken LA. Blocked and closed Bekasap frd #5, but T/O again. Open Recloser of TX-01B. Blocked and closed Bekasap frd #5, but T/O again. Isolated LA of TX-01A. Blocked and closed Bekasap frd #5, but T/O again. Open Recloser of TX-01A. Blocked and closed Bekasap frd #5, but T/O again. Open LBS 4/5. Blocked and closed Bekasap frd #5, but T/O again Open Disconnect switch of Bekasap fdr #5. Blocked and closed Bekasap frd #5, but T/O again. (Suspected Breaker failure).\ Restore to closed Recloser 04:12 Open LBS 37 BE 21 and Closed LBS 38 BD 36. (Load Bekasap feeder #3 transferred to Bekasap feeder #2) Closed LBS 3/5 and LBS 4/5. (Transfer load Bekasap feeder #4 & #5 to Bekasap feeder #3) 04:19 Closed 13.8KV ACB feeder #3. 04:23 Closed Recloser TX-01A and TX-01B. Cause: Circuit Breaker Failure. | 111 | 1 | 22:13 | Night | Sunday | 2017 | 6
7165 | 2017-06-11 22:32 | 2017-06-11 22:32 | CENTRAL DURI SWITCH YARD | Rain and Lightning | Under investigation | 815 | 22:32 C. Duri 115KV GCB #43 T/R 1X. C. Duri 115KV GCB #45 T/R 1X. (115KV Line to Pematang Main T/R) Rokan 13.8KV VCB fdr #2 T/R 1X. So. Balam fdr #1 load dropped 64A (132-68A). So. Balam fdr #4 load dropped 64A (203-39A). Nella fdr #1 load dropped 222A (262-40A). Nella fdr #2 load dropped 66A (86-20A). Bangko fdr #1 load dropped 140A (222-82A). Bangko fdr #4 load dropped 163A (215-52A). Menggala fdr #1 Load dropped 81A (207-126A). Sintong fdr #1 load dropped 29A (78-49A). Sintong fdr #2 load dropped 131A (196-65A). Pematang fdr #1 load dropped 124A (200-76A). Pematang fdr #2 load dropped 76A (84-8A). Rangau fdr #1 load dropped 30A (60-30A). Rangau fdr #2 load dropped 91A (117-26A). Petani fdr #1 load dropped 149A (155-6A). Ketigul fdr #1 load dropped 86A (92-6A). Prod.loss: 128 bbls / 80 Wells, -----> Nella fdr #1 37 bbls / 23 Wells, -----> Nella fdr #2 143 bbls / 77 Wells, -----> Bangko fdr #1 59 bbls / 34 Wells, -----> Bangko fdr #4 5 bbls / 2 Wells, -----> Menggala fdr #1 75 bbls / 24 Wells, -----> Sintong fdr #1 117 bbls / 61 Wells, -----> Sintong fdr #2 45 bbls / 20 Wells, ----->Pematang fdr #1 52 bbls /18 Wells, -----> Pematang fdr #2 2 bbls /4 Wells, -----> Rangau fdr #1 26 bbls /11 Wells, -----> Rangau fdr #2 65 bbls /37 Wells, -----> Petani fdr #1 22 bbls /9 Wells, -----> Rokan fdr #2 ---------------------------------------- + Total : 776 bbls / 400 Wells. | 11111 | 1 | 22:32 | Night | Sunday | 2017 | 6
7166 | 2017-06-11 22:48 | 2017-06-11 22:48 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | 22:48 Off Line NDC CT #3 and then S/D at 22:51. *Reduced load 16MW from BOB. 14:14 Shut Down Pusaka Substation and Pedada Substation (6MW). 18:10 Shut Down Beruk Substation and Zamrut Substation (12MW). 18:35 Manually Open 115KV GCB Lukut. *MGT Activity: 09:25 S/U MGT CT #10 and On LIne at 09:40. 15:25 S/U MGT #2 and then On Line at 15:4. 15:51 Manually Open Tie Breaker 13.8KV ACB #16. 16:34 S/U MGT #3 and then On Line at 16:52. 16:55 Manually Open Tie Breaker 13.8KB ACB #25. 17:05 S/U MGT #1 and On LIne at 17:30. S/U MGT $4 but failed. * CGT Activity: 17:16 S/U CGT #5 then On Line at 17:32. 17:44 Emegency S/D CGT #5 due to Fire on ACC Compartment (Fire on load gear) 01:49 MGT #10 tripped off by IGV Trouble. 02:19 S/U MGT #10 and then On line at 02:30. |  | 1 | 22:48 | Night | Sunday | 2017 | 6
7167 | 2017-06-11 22:54 | 2017-06-11 22:54 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 0 | Petani 13.8KV OCB fdr #2 T/R 2X. Not checked yet. |  | 1 | 22:54 | Night | Sunday | 2017 | 6
7168 | 2017-06-11 22:54 | 14/11/2017 08:00 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked and found 13.8 KV Petani fdr #2 T/R 2x Ctr:227-229 R/F: @3 50N. Patrolled the line but found nothing. Cause: suspect Lightning. |  | 1 | 22:54 | Night | Sunday | 2017 | 6
7169 | 2017-07-11 06:45 | 2017-07-11 06:45 | 13.8KV 8C FEEDER #1 | Drizzle | Unidentified | 240 | 06:45 It was reported no power under Recloser 9D-25 (d/ 8C fdr #1). 09:25 Checked and found Recloser: 9D-25 T/SO Counter: 55-56. Blocked and closed the Recloser, then released the blocked. Cause: Unidentified. |  | 1 | 6:45 | Morning | Tuesday | 2017 | 7
7170 | 2017-07-11 06:50 | 2017-07-11 06:50 | 13.8KV CENTRAL DURI FEEDER #15 | Drizzle | Powerline - Jumper | 398 | 06:50 It was reported no power on pole 06-Q3-03 (d/s C Duri fdr #15). 09:00 Checked and found Recloser: 06-Q3-02 T/LO Counter: 45-49. R/F: 51 @2 Patrolled the line found @2 broken Lightning Arrester touching cross arm on pole 06-Q3-11. Dismantled broken jumper on pole 06-Q3-11. Manually blocked and closed Recloser: 06-Q3-02, then released the block. Cause: Broken LA. |  | 1 | 6:50 | Morning | Tuesday | 2017 | 7
7171 | 2017-07-11 14:09 | 2017-07-11 14:09 | SO BEKASAP SUBSTATION | Fair | Planned Maintenance | 16 | 14:09 Manually Opened SoBek fdr and 44KV GCB#2. to By Pass Voltage Regulator for repair. 14:13 Manually Closed back SoBek fdr#1 and 44KV GCB #2. Cause: Maintenance |  | 1 | 14:09 | Afternoon | Tuesday | 2017 | 7
7172 | 2017-07-11 14:14 | 2017-07-11 14:14 | 230KV NORTH DURI SWITCH YARD | Fair | Under investigation | 603 | 14:14 N. Duri 230 KV Bus#1 T/O. When NDC Operator Selected the Synchron selector from CPI Mode to NDC Local Modes N. Duri 230 KV GCB#43 T/O, -------> Closed at 15:52 N. Duri 230 KV GCB#15 T/O, -------> Closed at 15:56 N. Duri 230 KV GCB#25 T/O, -------> Closed at 15:53 N. Duri 230 KV GCB#23 T/R, N. Duri 230 KV GCB#33 T/O, keep Open, CT#3 TX Under Investigate N. Duri 230 KV GCB#35 T/O, keep Open, CT#3 TX Under Investigate Checked & Found Bus#1 R/F: Neutral Over Current & 86 Bus#1. At That time, Respectively Tripping Off Petapahan Feeders. PTH 13.8KV VCB fdr#2 T/O, -------> Closed at 14:43 PTH 13.8KV VCB fdr#3 T/O, -------> Closed at 14:43 PTH 13.8KV VCB fdr#4 T/O, -------> Closed at 14:42 PTH 13.8KV VCB fdr#6 T/O, -------> Closed at 14:41 PTH 13.8KV VCB fdr#7 T/O, -------> Closed at 14:40 PTH 13.8KV VCB fdr#8 T/O, -------> Closed at 14:39 Cause: Under Investigate. | 12345 | 1 | 14:14 | Afternoon | Tuesday | 2017 | 7
7173 | 2017-07-11 16:41 | 2017-07-11 16:41 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Tree | 0 | 16:41 Duri Community fdr#5 T/R 1x. Not checked yet. |  | 1 | 16:41 | Afternoon | Tuesday | 2017 | 7
7174 | 2017-07-11 16:41 | 2017-12-11 15:41 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Tree | 0 | Checked & found, Duri Community ACB #33 fdr #5 T/R 1x ctr: 112-113 R/F: 51@3. Patrolled the line & found, Tree trouched power line on Pole 39-BE-14. Cause: Tree. |  | 1 | 16:41 | Afternoon | Tuesday | 2017 | 7
7175 | 2017-07-11 18:30 | 2017-07-11 18:30 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Circuit Breaker | 56 | Minas ACB #14 (feeder#1) T/SO Counter: 72-73 R/F: 51@2. Not checked yet. |  | 1 | 18:30 | Afternoon | Tuesday | 2017 | 7
7176 | 2017-07-11 18:30 | 2017-08-11 08:30 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Circuit Breaker | 56 | Checked and found Minas ACB #14 (feeder#1) T/SO Counter: 72-73 R/F: 51@2. Function test ACB #14 (feeder#1) found failed to close. Transfer Minas ACB fdr #1 to Minas ACB fdr #2 by: 1. Opened LBS: M5B-5 and Opened LBS: 6D-28. 2. Closed LBS: 7D-17A (parallel Minas Fdr #1 and Minas Fdr #2) 3. Closed LBS: M5B-5 and Closed LBS: 6D-28. Cause: Circuit breaker. |  | 1 | 18:30 | Afternoon | Tuesday | 2017 | 7
7177 | 2017-07-11 19:08 | 2017-07-11 19:08 | 230KV NORTH DURI SWITCH YARD | Rain and Lightning | Equipment Failure | 18488 | 19:08 230 KV GCB #13 T/O the Closed at :21:24. GCB #15 T/O GCB #21 T/O the Closed at :23:05. GCB #23 T/O the Closed at :21:41. GCB #25 T/O GCB #43 T/O NDC #1 T/O NDC #2 T/O , 22:29 S/U NDC #2 then online the unit at :23:01 Freq. 59.84 Hz. Suram fdr #1 T/O , Closed at : 00:05 3D OCB fdr #2 T/O ,then closed at 23:16 3D OCB fdr #3 T/O ,then closed at 3D OCB fdr #5 T/O ,then closed at 00:11 3D OCB fdr #6 T/O ,then closed at 00:19 4D OCB fdr #2 T/O ,then closed at 00:08 4D OCB fdr #3 T/O ,then closed at 00:14 4D OCB fdr #5 T/O ,then closed at 00:12 4B OCB fdr #1 T/O ,then closed at 23:22 4B OCB fdr #4 T/O ,then closed at 23:08 4B OCB fdr #5 T/O ,then closed at 23:09 4B OCB fdr #6 T/O ,then closed at 00:06 5B OCB fdr #1 T/O ,then closed at 23:31 5B OCB fdr #3 T/O ,then closed at 00:18 5B OCB fdr #4 T/O ,then closed at 00:10 5B OCB fdr #5 T/O ,then closed at 00:14 5B OCB fdr #7 T/O ,then closed at 00:17 8D OCB fdr #1 T/O ,then closed at 23:50 8D OCB fdr #3 T/O ,then closed at 00:00 8D OCB fdr #10 T/O ,then closed at 23:27 8C OCB fdr #1 T/O ,then closed at 23:16 8C OCB fdr #2 T/O ,then closed at 00:01 SURAM fdr #1 T/O ,then closed at 00:05 19:20 ROKAN fdr #2 M/O , then closed at 00:04 19:29 6D fdr #1 M/O , then closed at 23:34 19:30 6D fdr #2 M/O , then closed at 23:34 19:28 6D fdr #5 M/O , then closed at 23:36 19:29 PEMATANG fdr #2 M/O , then closed at 23:35 19:31 6DN fdr #1 M/O , then closed at 23:32 19:32 6DN fdr #5 M/O , then closed at 23:33 19:42 6DN fdr #6 M/O , then closed at 23:14 19:35 KETIGUL fdr #2 M/O , then closed at 23:37 19:39 BATANG fdr #3 M/O , then closed at 23:19 19:40 3D fdr #4 M/O , then closed at 23:17 19:40 BEKASAP fdr #2 M/O , then closed at 23:16 19:41 5B fdr #1 M/O , then closed at 23:15 19:43 NELLA fdr #2 M/O , then closed at 23:14 19:43 8D fdr #11 M/O , then closed at 23:14 19:43 BEKASAP fdr #6 M/O , then closed at 23:13 19:44 MINAS fdr #3 M/O , then closed at 23:14 19:08 PETAPAHAN fdr #2 M/O , then closed at 22:17 19:08 PETAPAHAN fdr #3 M/O , then closed at 23:05 19:08 PETAPAHAN fdr #4 M/O , then closed at 23:06 19:08 PETAPAHAN fdr #6 M/O , then closed at 23:07 19:08 PETAPAHAN fdr #7 M/O , then closed at 22:11 19:08 PETAPAHAN fdr #8 M/O , then closed at 22:11 | 1234 | 1 | 19:08 | Night | Tuesday | 2017 | 7
7178 | 2017-07-11 19:08 | 2017-08-11 02:00 | 230KV NORTH DURI SWITCH YARD | Rain and Lightning | Equipment Failure | 18488 | 02:01 Manually opened 5B fdr#5,then closed 06:16. 02:02 Manually opened 4D fdr#3,then closed at 06:15. 02:02 Manually opened 4D fdr#5, then closed at 06:14. 02:16 Manually opened 5B fdr#2 (Req. GS#4), then closed at 15:18 02:32 Manually opened 8D fdr#10 (Req. GS#1), then closed at 06:12. HO Team Req, manually open fdrs by over flow water CGS#10. 03:41 Manually opened N.Duri fdr#1 closed at 22:54. 04:54 Manually opened N.Duri fdr#6 closed at 15:10. 04:00 NDC Operator reported Supplay Gas for NDC lower 290Psi. NDW lower load at 60MW.Freq. 59.70 Hz. 04:18 Manually opened 5B fdr#5, then closed at 04:52. 04:19 Manually opened 4D fdr#2, then closed at 04:50. 04:22 Manually opened Suram fdr#1, then closed at 04:49. 04:23 Manually opened Suram fdr#2, then closed at04:48. 04:23 Manually opened Rokan fdr#2, then closed at 04:47. 04:23 Manually opened 3D fdr#3, then closed at 04:46. 04:24 Manually opened 8C fdr#2, then closed at 04:49. 04:24 Manually opened 8D fdr#3, then closed at 04:45. 04:24 Manually opened 8D fdr#1, then closed at 04:44. 04:27 Manually opened 8C fdr#1, closed at 04:44. 04:26 Manually opened 6D fdr#5, the closed at 04:43. 04:26 Manually opened Pematang fdr#2, then closd at 04:43. 04:27 Manually opened 5B fdr#3, then closed at 04:40. Production Loss: 1. Production loss Heavy Oil (HO) = 1449 Bbls / 200 wells. 2. Production loss SLN Petani GS = 31 Bbls / 8 wells. Pematang GS = 51 Bbls / 19 wells. 3. Production loss SLS GS #1 = 120 Bbls / 93 Wells. GS #2 = 56 Bbls / 45 wells. GS #3 = 0 Bbls / 0 well. GS #4 = 4 Bbls / 8 wells. GS #5 = 331 Bbls / 84 wells. GS #6 = 0 Bbls / 0 well. -------------------------------------------- + Grand total = 2042 Bbls / 457 wells. | 1234 | 1 | 19:08 | Night | Tuesday | 2017 | 7
7179 | 2017-07-11 19:08 | 2017-08-11 19:00 | 230KV NORTH DURI SWITCH YARD | Rain and Lightning | Equipment Failure | 18488 | Checked and found: N. Duri 230KV GCB #21 T/O Counter : 123 - 124 Relay Flag : 86. N. Duri 230KV GCB #25 T/O Counter : 203 - 204. N. Duri 230KV GCB #23 T/O Counter : 242 - 243. N. Duri 230KV GCB #43 T/O Counter : 195 - 196. N. Duri 230KV GCB #15 T/O Counter : 144 - 145. N. Duri 230KV GCB #13 T/O Counter : 278 - 279. Patrolled the line and found failure @2 of GCB #35. Cause: Under investigation. | 1234 | 1 | 19:08 | Night | Tuesday | 2017 | 7
7180 | 2017-07-11 20:48 | 2017-07-11 20:48 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Tree | 0 | Duri Community fdr#5 T/R 1x. Not checked yet. |  | 1 | 20:48 | Night | Tuesday | 2017 | 7
7181 | 2017-07-11 20:48 | 2017-12-11 20:48 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Tree | 0 | Checked & found, Duri Community ACB #33 fdr #5 T/R 1x ctr: 112-113 R/F: 51@3. Patrolled the line & found, Tree trouched power line on Pole 39-BE-14. Cause: Tree. |  | 1 | 20:48 | Night | Tuesday | 2017 | 7
7182 | 2017-08-11 09:36 | 2017-08-11 09:36 | 13.8KV CENTRAL DURI FEEDER #8 | Rain | Recloser | 993 | 09:36 C Duri ACB #32 (feeder #8) T/LO Counter: 436-439 R/F: 51@2. Patrolled the line found @2 broken bushing on Recloser 04-06-40. By pass Recloser 04-06-40 and then dismantled the Recloser. 14:35 Manually blocked and closed C Duri ACB #32 (feeder #8) --> Ok and then released the block. Cause: Broken bushing Recloser. | 12345 | 1 | 9:36 | Morning | Friday | 2017 | 8
7183 | 2017-08-11 14:17 | 2017-08-11 14:17 | NORTH DURI POWER PLANT |  |  | - | 14:17 S/U NDC CT #1 and then On line the unit at 14:54. |  | 1 | 14:17 | Afternoon | Friday | 2017 | 8
7184 | 2017-09-11 03:11 | 2017-09-11 03:11 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Cloudy | Recloser - Control Recloser | 230 | 03:11 CKBS fdr#6 load dropped 130 A (155-25A). 08:17 Checked & found Recl 34-CU3-4 T/SO Ctr:NN. Patrolled the line but found nothing. Blocked & Closed Recl 34-CU-34, then release the block. Cause: Control Recloser. |  | 1 | 3:11 | Night | Monday | 2017 | 9
7185 | 2017-09-11 09:10 | 2017-09-11 09:10 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified | 128 | 09:10 Nella fdr#1 T/R 1X Ctr : 507 - 508 R/F 51N , 51@1 Not Checked Yet. |  | 1 | 9:10 | Morning | Monday | 2017 | 9
7186 | 2017-09-11 09:10 | 2017-11-11 09:00 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified | 128 | Checked & found Nella ACB fdr#1 T/R 1x, Ctr: 507-508, R/F: 51N. Patrolled the Line, but fond nothing. Cause : Unidentified |  | 1 | 9:10 | Morning | Monday | 2017 | 9
7187 | 2017-09-11 11:48 | 2017-09-11 11:48 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 99 | 11:48 Manual open Pematang OCB Fdr#2 to Replace 150KVATX at Well Pematang #13 12:54 Manual Closed back Pematang OCB fdr#2, after finished the Jobs. Cause: Planned Maintenance. |  | 1 | 11:48 | Morning | Monday | 2017 | 9
7188 | 2017-09-11 13:15 | 2017-09-11 13:15 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 155 | 13:15 S.Balam Fdr# 4 T/R 1x GFPC TX T/R 1x Ground fault alarm at fdr #4. S.Balam Fdr# 1 load drop 70 A (128 - 58 A) S.Balam Fdr# 2 load drop 100 A (131 - 31 A) S.Balam Fdr# 3 load drop 70 A (70 - 0 A) Not Checked yet. |  | 1 | 13:15 | Afternoon | Monday | 2017 | 9
7189 | 2017-09-11 13:15 | 2017-11-11 13:00 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 155 | Checked & found S.Balam VCB fdr#4 T/R 1x, Ctr: 348-349, R/F: 51. Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 13:15 | Afternoon | Monday | 2017 | 9
7190 | 2017-09-11 18:40 | 2017-09-11 18:40 | CENTRAL DURI POWER PLANT |  |  | - | 18:40 S/U CGT#5, then on line the unit at 19:00. |  | 1 | 18:40 | Afternoon | Monday | 2017 | 9
7191 | 2017-09-11 20:21 | 2017-09-11 20:21 | NORTH DURI POWER PLANT |  |  | - | 20:21-22:14 Do Switching to Energized 13.8/230Kv TXP#3 at NDSY. 21:05 S/U NDC#3, then on line the unit at 22:18. NDC Operator reported spark at @1 Line Switch TXP#3 load 20MW. 22:29 Off Line NDC#3, then S/D the unit for Exercise Line switch TXP#3. 22:50 S/U NDC#3, then on line the unit at 23:18. TDO Crew monitor intermittent spark at @1 Line switch TXP#3. 00:00 Off line NDC#3, then S/D the unit for repaired @1 Line switch TXP#3. (Continued tomorrow morning). |  | 1 | 20:21 | Night | Monday | 2017 | 9
7192 | 2017-10-11 05:33 | 2017-10-11 05:33 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Substation Failure (LA) | 1363 | 05:33 Manually opened 44 KV OCB #1. (44 Kv line to Petani Substation). due to b/o L/A at structure of Petani SS. 1. Manually opened Petani OCB fdr #1 2. Manually opened Petani OCb fdr #2 ( Local ) 06:00 Manually opened Rokan OCB fdr #2. 10:24 Open Line switch incoming line at Petani substation , Closed Grounding system Replace Burn out 13.8 kV L/A @2 on structure. 10:32 Manually blocked and closed 44 KV OCB # 1. 10:42 Manually blocked and closed Petani OCB fdr #1 and then released the block. Manually blocked and closed Petani OCB fdr #2 and then released the block. 11:19 Manually blocked and closed Rokan OCB fdr #2 and then released the block. Caused :Lightning Arrester. | 11111 | 1 | 5:33 | Morning | Wednesday | 2017 | 10
7193 | 2017-10-11 07:21 | 2017-10-11 07:21 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr#1 load dropped 30A (130-100A) Not checked yet. |  | 1 | 7:21 | Morning | Wednesday | 2017 | 10
7194 | 2017-10-11 07:21 | 24/11/2017 07:21 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found Recloser 38 AS 09 T/R 1x ctr:226-227 R/F:51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:21 | Morning | Wednesday | 2017 | 10
7195 | 2017-10-11 07:38 | 2017-10-11 07:38 | 13.8KV 3D FEEDER #8 | Fair | Unidentified | 23 | 3D fdr#8 load dropped 118A (203-85A) Not checked yet. |  | 1 | 7:38 | Morning | Wednesday | 2017 | 10
7196 | 2017-10-11 07:38 | 19/11/2017 08:38 | 13.8KV 3D FEEDER #8 | Fair | Unidentified | 23 | Checked and found 3D fdr #8 dropped 118 A. Patrolled the line and found no Recloser under this feeder. Cause: Unidentified. |  | 1 | 7:38 | Morning | Wednesday | 2017 | 10
7197 | 2017-10-11 10:29 | 2017-10-11 10:29 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 0 | 10:29 Open LBS 27 AL 03 (d/s Ketigul Fdr #2) To adjust voltage at Well UBI #24 and UBI #27. 10:34 Closed the LBS back, after finished the Jobs. Cause: Planned Maintenance. |  | 1 | 10:29 | Morning | Wednesday | 2017 | 10
7198 | 2017-10-11 10:40 | 2017-10-11 10:40 | MINAS POWER PLANT |  |  | - | Off line MGT#2, then S/D the unit for S/B. |  | 1 | 10:40 | Morning | Wednesday | 2017 | 10
7199 | 2017-10-11 14:24 | 2017-10-11 14:24 | 13.8KV MENGGALA FEEDER #1 | Fair | Construction Job | 0 | 14:24 Man open Recloser 19.AN.04 (d/s Manggala Fdr#1). Due to project team working at Well Meno #44 and #45 17:10 Normalized Recloser 19.AN.04, after finisehed the construction Jobs Cause: Construction Job. |  | 1 | 14:24 | Afternoon | Wednesday | 2017 | 10
7200 | 2017-10-11 15:12 | 2017-10-11 15:12 | 13.8KV BEKASAP FEEDER #6 | Fair | Planned Maintenance | 105 | 15:12 Man open Bekasap ACB Fdr#6 To install t150KVATX at lWell Bekasap #94 and adjusted tapping at Well Bekasap #50 16:08 Normalized Bekasap ACB Fdr #6, after finished the Jobs. Cause: Planned maintenance |  | 1 | 15:12 | Afternoon | Wednesday | 2017 | 10
7201 | 2017-10-11 18:50 | 2017-10-11 18:50 | NORTH DURI POWER PLANT |  |  | - | 18:50 S/U NDC#3, then on line the unit at 19:35. After Off line Wash maintenance program. |  | 1 | 18:50 | Afternoon | Wednesday | 2017 | 10
7202 | 2017-10-11 22:25 | 2017-10-11 22:25 | NORTH DURI POWER PLANT |  |  | - | Off line NDC#2, then S/D the unit for Maintenance. |  | 1 | 22:25 | Night | Wednesday | 2017 | 10
7203 | 2017-11-11 14:07 | 2017-11-11 14:07 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 670 | 14:07 Manually opened Bekasap OCB fdr# 2 to Replace Transformer at Well Bekasap #100 , #67 and #154 Adjusted tapping at location Bekasap #107, #184 and #101 16:37 Manually blocked and closed Bekasap OCB fdr# 2 and then released the block. Cause: Planned Maintenance. | 12345 | 1 | 14:07 | Afternoon | Saturday | 2017 | 11
7204 | 2017-11-11 18:00 | 2017-11-11 18:00 | NORTH DURI POWER PLANT |  |  | - | 18:00 S/U NDC #2 and then On line the unit at 18:30. |  | 1 | 18:00 | Afternoon | Saturday | 2017 | 11
7205 | 2017-11-11 20:40 | 2017-11-11 20:40 | MINAS POWER PLANT |  |  | - | 20:40 Off Line MGT #4 and then S/D the unit for Stand By. |  | 1 | 20:40 | Night | Saturday | 2017 | 11
7206 | 2017-11-11 20:50 | 2017-11-11 20:50 | CENTRAL DURI POWER PLANT |  |  | - | 20:50 Off Line CDGT #5 and then S/D the unit for Stand By. |  | 1 | 20:50 | Night | Saturday | 2017 | 11
7207 | 2017-11-11 21:00 | 2017-11-11 21:00 | MINAS POWER PLANT |  |  | - | 21:00 Off Line MGT #3 and then S/D the unit for Stand By. |  | 1 | 21:00 | Night | Saturday | 2017 | 11
7208 | 2017-11-11 21:10 | 2017-11-11 21:10 | MINAS POWER PLANT |  |  | - | 21:10 Off Line MGT #1 and then S/D the unit for Stand By. |  | 1 | 21:10 | Night | Saturday | 2017 | 11
7209 | 2017-11-11 21:48 | 2017-11-11 21:48 | MINAS POWER PLANT |  |  | - | Off line MGT#6, then S/D the unit for S/B. |  | 1 | 21:48 | Night | Saturday | 2017 | 11
7210 | 2017-11-11 23:28 | 2017-11-11 23:28 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning | 7 | Ketigul VCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 23:28 | Night | Saturday | 2017 | 11
7211 | 2017-11-11 23:28 | 14/11/2017 23:28 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning | 7 | Checked & found, Ketigul 13.8KV VCB fdr #3 T/R 1X ctr:193-194 R/F:51N. Patrolled the line and found, @2 Dead end flash over o/p 31AR 25. Also found @2 broken Pin Insulator and @1, @2 broken LA o/p 31 AR 17. Cause: Lightning. |  | 1 | 23:28 | Night | Saturday | 2017 | 11
7212 | 2017-12-11 01:50 | 2017-12-11 01:50 | SINABUNG MINI SUBSTATION | Fair | Unidentified (Fuse) | 0 | 01:50 It was reported unbalance at WTP Camp. 02:15 Checked and found @3 b/o fuse for 500 Kva Tx at WTP Camp. 09:00 Replaced @3 B/O fuse for 500 Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 1:50 | Night | Monday | 2017 | 12
7213 | 2017-12-11 17:24 | 2017-12-11 17:24 | MINAS POWER PLANT | Fair |  | - | Off line MGT #10, and then S/D the unit for S/B. |  | 1 | 17:24 | Afternoon | Monday | 2017 | 12
7214 | 2017-12-11 23:35 | 2017-12-11 23:35 | MINAS POWER PLANT | Fair |  | - | 23:35 S/U MGT#1 and then On line the unit at 23:52 |  | 1 | 23:35 | Night | Monday | 2017 | 12
7215 | 2017-11-13 08:05 | 2017-11-13 08:05 | 13.8KV MINAS FEEDER #6 | Fair | Equipment Failure | 0 | 08:05 Minas Fdr # 6 load drop 92 A ( 178 - 86 A) Checked & found, Recloser 6E-23A T/LO ctr:... Also found, @3 broken isolation switch of Recl. 6E-23A. 16:30 Opened LBS:7E-54 D/S Minas Fdr# 6 due to: Repair broken isolation switch on Recloser 6E-23A. 17:36 Close LBS:7E-54. Cause: Equipment Failure. See PIDOD 13-NOV at 16:30. |  | 1 | 8:05 | Morning | Monday | 2017 | 11
7216 | 2017-11-13 14:45 | 2017-11-13 14:45 | 13.8KV DURI FIELD FEEDER #2 | Fair | Planned Maintenance | 16 | 14:45 Opened LBS:06-S3-02 D/S D.Field fdr #2 due to: Replaced 112.5 Kva Transformer failure with same size and then energized the Tx o/p 06-S3-05. 16:10 Closed LBS: 06-S3-02. Cause: Plan Maintenance. |  | 1 | 14:45 | Afternoon | Monday | 2017 | 11
7217 | 2017-11-13 15:05 | 2017-11-13 15:05 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Planned Maintenance | 0 | 15:05 Opened Fuse due to perform TTR and Megger at well PTH #80. 5 wells Off (PTH 73,74,75,76,77) during this job. 16:00 Closed Fuse for energizing wells above. Cause: Plan Maintenance. |  | 1 | 15:05 | Afternoon | Monday | 2017 | 11
7218 | 2017-11-13 16:30 | 2017-11-13 16:30 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 429 | 16:30 Opened LBS:7E-54 D/S Minas Fdr# 6 due to: Repair broken isolation switch on Recloser 6E-23A. 17:36 Close LBS:7E-54. Cause: Plan Maintenance. See PIDOD 13 Nov at 08:05 | 12345 | 1 | 16:30 | Afternoon | Monday | 2017 | 11
7219 | 2017-11-13 16:50 | 2017-11-13 16:50 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 73 | 16:50 Manually opened Recloser: 16-Z-25 D/S S.Balam fdr #1 due to: Reeplaced @2 , @3 broken Fuse Cut Out at well Balam #396. 16:59 Manually blocked and closed Recloser: 16-Z-25 and then released the block. Cause: Plan Maintenance. |  | 1 | 16:50 | Afternoon | Monday | 2017 | 11
7220 | 2017-11-13 16:57 | 2017-11-13 16:57 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified | 0 | N.Duri VCB fdr#8 T/R 1x. Not checked yet. |  | 1 | 16:57 | Afternoon | Monday | 2017 | 11
7221 | 2017-11-13 16:57 | 2017-11-20 16:57 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified | 0 | Checked and found N. Duri 13.8KV VCB fdr #8 T/R 1X Ctr:83-84 R/F:51@1. Cause: Unidentified. |  | 1 | 16:57 | Afternoon | Monday | 2017 | 11
7222 | 2017-11-14 10:54 | 2017-11-14 10:54 | 13.8KV MINAS FEEDER #4 | Fair | Planned Maintenance | 490 | 10:54 Manually Open 13.8KV Minas ACB fdr #4,----> Closed at 16:00. Replaced TX at well 7D-96N. Replaced Recloser 7D-150. Cause: Planned Maintenance. |  | 1 | 10:54 | Morning | Tuesday | 2017 | 11
7223 | 2017-11-14 11:21 | 2017-11-14 11:21 | 13.8KV PINANG FEEDER #1 | Fair | Planned Maintenance | 36 | 11:21 Manually open Pinang 13.8KV OCB fdr #1, ----->Closed at 11:24. Replaced @2, @3 fuses for 150KVA TX at well Pinang #42. Adjusted voltage for 300KVA TX at well Pinang #41. Plan Maintenance. |  | 1 | 11:21 | Morning | Tuesday | 2017 | 11
7224 | 2017-11-14 13:48 | 2017-11-14 13:48 | CENTRAL DURI POWER PLANT |  |  | - | 13:48 S/U CGT #5 and On Line at 13:04. |  | 1 | 13:48 | Afternoon | Tuesday | 2017 | 11
7225 | 2017-11-14 14:21 | 2017-11-14 14:21 | 13.8KV PUNGUT FEEDER #1 | Fair | Planned Maintenance | 83 | 14:21 Manually Open 13.8KV Pungut OCB fdr #1, -----> Closed at 14:46 Adjusted Voltage for TX at well Pungut #08. Plan Maintenance. |  | 1 | 14:21 | Afternoon | Tuesday | 2017 | 11
7226 | 2017-11-14 14:24 | 2017-11-14 14:24 | MINAS POWER PLANT |  |  | - | 14:24 Off line and then S/D MGT #1 for S/B. |  | 1 | 14:24 | Afternoon | Tuesday | 2017 | 11
7227 | 2017-11-15 03:39 | 2017-11-15 03:39 | 4.16KV MINAS IND FEEDER | Fair | Unidentified | 0 | 03:39 Minas fdr #2 load dropped 14A (121-107A). 04:00 Checked and found 4160 V ACB Industrial T/LO Counter: 648-650 R/F: 51N. Patrolled the line found nothing. 05:02 Blocked and closed 4160 V ACB Industrial --> Ok and then released the block. Cause: Unidentified. |  | 1 | 3:39 | Night | Wednesday | 2017 | 11
7228 | 2017-11-15 07:41 | 2017-11-15 07:41 | 13.8KV PEMATANG FEEDER #1 | Fair | Lightning | 50 | Pematang 13.8 KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 7:41 | Morning | Wednesday | 2017 | 11
7229 | 2017-11-15 07:41 | 2017-11-20 08:00 | 13.8KV PEMATANG FEEDER #1 | Fair | Lightning | 50 | Checked and found 13.8KV OCB #1 T/R 1x Ctr: 144-145 R/F: @1, @2 51N. Patrolled the line and found L/A broken o/p 35-BC-14. Cause: Lightning. |  | 1 | 7:41 | Morning | Wednesday | 2017 | 11
7230 | 2017-11-15 10:25 | 2017-11-15 10:25 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 245 | 10:25 Manually open S.Balam 13.8KV OCB fdr #4. Install the TX at well SE.Balam #22. 150 KVA ,79 HP ,480 VOLT. Plant maintenance. |  | 1 | 10:25 | Morning | Wednesday | 2017 | 11
7231 | 2017-11-15 11:31 | 2017-11-15 11:31 | 13.8KV 8C FEEDER #1 | Rain | Planned Maintenance | 43 | 11:31 Manually open Recloser 9D-111 d/s 8C fdr #1. Replaced dead end ,Pin insulator ,and Tie in new location. (PDKB Category 2) 15:41 Manually Closed Recloser 9D-111. Plant maintenance. |  | 1 | 11:31 | Morning | Wednesday | 2017 | 11
7232 | 2017-11-15 14:28 | 2017-11-15 14:28 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 0 | 14:28 Manually open Bekasap 13.8 KV OCB FDR #2 ----->Closed at 15:55. Relocated Powerline at well Bekasap #162 & Bks #89. Shut off 5 Wells ( Bekasap #184, #69, #162, #26, #89 ) Plant maintenance (Construction). |  | 1 | 14:28 | Afternoon | Wednesday | 2017 | 11
7233 | 2017-11-16 08:18 | 2017-11-16 08:18 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 38 | 08:19 Ground fault alarm Bangko fdr #4. Bangko fdr #4 load dropped 15A ( 218-203A ). Not checked yet. |  | 1 | 8:18 | Morning | Thursday | 2017 | 11
7234 | 2017-11-16 08:18 | 2017-11-17 08:18 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 38 | Chceked & found, Bangko GFPC T/R 1x ctr:.... Patrolled the line & found, @2 b/o Fuse for 150Kva Tx at well Bangko #245. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal (Monkey) |  | 1 | 8:18 | Morning | Thursday | 2017 | 11
7235 | 2017-11-16 10:47 | 2017-11-16 10:47 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 130 | 10:47 Manual Opened S.Balam VCB fdr #1. to Replaced switch board at Well S.Balam #150. 11:00 Manual Closed back after finished the jobs Cause: Planned maintenance. |  | 1 | 10:47 | Morning | Thursday | 2017 | 11
7236 | 2017-11-16 12:10 | 2017-11-16 12:10 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 170 | 12:10 Manual open Rangau 13.8 KV OCB fdr #2. to Tie in Well Jurong #42, check Voltage at Well Jurong #36. 15:09 Manual Closed back after finished the Jobs Cause: Planned maintenance. |  | 1 | 12:10 | Afternoon | Thursday | 2017 | 11
7237 | 2017-11-16 13:13 | 2017-11-16 13:13 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | 553 | 13:13 Manual Opened Bangko 13.8 Kv OCB fdr#1. to replace Recl.23 W 12. 15:10 Manual Closed Bangko 13.8 Kv OCB fdr#1. after finished the jobs Cause : Planned maintenance. | 1234 | 1 | 13:13 | Afternoon | Thursday | 2017 | 11
7238 | 2017-11-16 13:39 | 2017-11-16 13:39 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 23 | 13:39 Manual Open Recloser 44-BX-06, d/s Pungut #22. to Disconnect X-0 150KVATX at well Ami #002. 13:46 Manual Closed Recloser 44.BX.06 After finished the Jobs Cause: Planned maintenance. |  | 1 | 13:39 | Afternoon | Thursday | 2017 | 11
7239 | 2017-11-16 13:58 | 2017-11-16 13:58 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 28 | 13:58 Manually Open Recloser 9D-111 (d/s 8C fdr #1). Continued Replaced dead end ,Pin insulator ,and Tie in new Well. (PDKB Category 2) 16:50 Manually Closed Recloser 9D-111. after finished the Jobs Cause: Planned maintenance. |  | 1 | 13:58 | Afternoon | Thursday | 2017 | 11
7240 | 2017-11-16 15:24 | 2017-11-16 15:24 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 158 | 15:24 Nella 13.8 KV VCB fdr #1 T/R 1X. Nella 13.8 KV VCB fdr #2 dropped 55A ( 90-35A ). Not checked yet |  | 1 | 15:24 | Afternoon | Thursday | 2017 | 11
7241 | 2017-11-16 15:24 | 2017-11-17 08:24 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 158 | Checked and found 13.8KV VCB #1 T/R 1x Ctr: 508-509 R/F: 51N Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 15:24 | Afternoon | Thursday | 2017 | 11
7242 | 2017-11-16 15:24 | 2017-11-16 15:24 | MINAS POWER PLANT |  |  | - | 15:24 S/U MGT #8 and Online at 15:28. to back up power due to CGT#3 Will Down. |  | 1 | 15:24 | Afternoon | Thursday | 2017 | 11
7243 | 2017-11-16 16:48 | 2017-11-16 16:48 | CENTRAL DURI POWER PLANT |  |  | - | 16:48 CDGT #3 0ff line and S/D the unit at 16:49. to Repair CD TX#3 |  | 1 | 16:48 | Afternoon | Thursday | 2017 | 11
7244 | 2017-11-16 22:19 | 2017-11-16 22:19 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 46 | 22:19 8D 13.8 KV VCB fdr#7 T/R 1x. 8D fdr#8 load dropped 178A(182-4A). 8D fdr#9 load dropped 64A(184-120A).WIP. 8D fdr#6 load dropped 69A(189-120A).WIP. Cause : Not checked yet. |  | 1 | 22:19 | Night | Thursday | 2017 | 11
7245 | 2017-11-16 22:19 | 2017-05-12 08:00 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 46 | Checked and found 8D fdr #7 T/R 1x Ctr: 661-662 R/F: 51 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 22:19 | Night | Thursday | 2017 | 11
7246 | 2017-11-17 04:12 | 2017-11-17 04:12 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Rain and Lightning | Lightning | 0 | 04:12 Dumai 4.16 kV VCB # 12 ( Fdr#1 Warf ) T/LO Not checked yet. |  | 1 | 4:12 | Morning | Friday | 2017 | 11
7247 | 2017-11-17 04:12 | 2017-11-20 18:00 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked and found 4.16kV DUMAI (WHARF FEEDER) FEEDER #01 T/LO ctr:278-279 R/F:51 @1, @2. Patrolled the line but found nothing. Cause:Lightning. |  | 1 | 4:12 | Morning | Friday | 2017 | 11
7248 | 2017-11-17 04:22 | 2017-11-17 04:22 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 48 | 04:22 Nella fdr #1 load drop 100 A ( 250 - 150 A ) 06:01 Checked & found, Recl. 22V.01 T/SO, Ctr: 807-808, R/F : None Blocked & Closed the Recloser, OK. then released the Block. Patrolled the Line, but found nothing. Cause: Suspected by Lightning. |  | 1 | 4:22 | Morning | Friday | 2017 | 11
7249 | 2017-11-17 07:34 | 2017-11-17 07:34 | 13.8KV DARLING VCB FEEDER #4 | Heavy Rain | Unidentified | 0 | Darling 13.8KV VCB fdr #4 T/R 1X. Darling 13.8KV GFPC TX-1 T/R 1x. No checked yet. |  | 1 | 7:34 | Morning | Friday | 2017 | 11
7250 | 2017-11-17 07:34 | 2017-11-20 07:34 | 13.8KV DARLING VCB FEEDER #4 | Heavy Rain | Unidentified | 0 | Checked and found Darling 13.8KV VCB fdr #4 T/R 1X ctr:138-139 R/F:51@2. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 7:34 | Morning | Friday | 2017 | 11
7251 | 2017-11-17 12:39 | 2017-11-17 12:39 | 13.8KV BANGKO FEEDER #3 | Drizzle | Unidentified | 0 | Bangko 13.8KV OCB fdr #3 T/R 1X. Ctr: 99943 - 99944, R/F: 50N, 50@2 Bangko fdr #2 Load dropped 88A (257-169A). Bangko GFPC T/R 1X. Patrolled the Line, but found nothing Cause: Unidentified |  | 1 | 12:39 | Afternoon | Friday | 2017 | 11
7252 | 2017-11-17 14:39 | 2017-11-17 14:39 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 239 | 14:39 Manually Open So. Bekasap fdr #1, ----->Closed at 16:34. Adjusted voltage for TX at wells Ampuh #15 and Ampuh #21. Plan Maintenance. |  | 1 | 14:39 | Afternoon | Friday | 2017 | 11
7253 | 2017-11-18 08:53 | 2017-11-18 08:53 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 08:53 It was reported b/o fuse at o/p 07-U7-07 d/s D. Field fdr #4. 14:30 Checked found, @1, @2 b/o fuse for 112.5 KVA TX. Replaced b/o fuse above with the same size then energized the Tx. Cause: Unidentified (fuse ). |  | 1 | 8:53 | Morning | Saturday | 2017 | 11
7254 | 2017-11-18 09:41 | 2017-11-18 09:41 | 13.8KV PETANI FEEDER #2 | Fair | Planned Maintenance | 83 | 09:41 Manual opened 13.8 KV Petani OCB fdr #2 Adjusted voltage at well Petani #013. 10:42 Closed Plant maintenance. Prod loss 77 bbls and 23 wells |  | 1 | 9:41 | Morning | Saturday | 2017 | 11
7255 | 2017-11-18 10:59 | 2017-11-18 10:59 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 95 | 10:59 Manual opened 13.8 KV Pematang OCB fdr #2. 11:51 C/O 150 KVA - 300 KVA TX , at well Pematang #07. R/M :105 HP - 225 HP. Plant maintenance. |  | 1 | 10:59 | Morning | Saturday | 2017 | 11
7256 | 2017-11-18 14:40 | 2017-11-18 14:40 | 13.8KV NORTH DURI FEEDER #7 | Fair | Planned Maintenance | 0 | 14:40 Manually Opened Fuses for 112.5 Kva TX o/p 10-J6-16A. due to replaced Secondary cable. Cause: Planned Maintenance. |  | 1 | 14:40 | Afternoon | Saturday | 2017 | 11
7257 | 2017-11-18 15:25 | 2017-11-18 15:25 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 15:25 Replaced @1, @2 b/o fuse for 112.5 Kva TX o/p 04-06-23 d/s C. Duri fdr #9. Cause: Unidentified (Fuse). |  | 1 | 15:25 | Afternoon | Saturday | 2017 | 11
7258 | 2017-11-18 15:30 | 2017-11-18 15:30 | 13.8KV DARLING VCB FEEDER #4 | Fair | Animal | 0 | 15:30 Replaced @2 b/o fuse for 1500 Kva Tx at CSS #6, d/s Darling fdr #4. Cause: Animal ( Snake ). |  | 1 | 15:30 | Afternoon | Saturday | 2017 | 11
7259 | 2017-11-19 08:40 | 2017-11-19 08:40 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | 08:40 Menggala 13.8 Kv fdr #1 load dropped 131A ( 196-65A ). Menggala GFPC #1 T/R 1X. Not Checked yet. |  | 1 | 8:40 | Morning | Sunday | 2017 | 11
7260 | 2017-11-19 08:40 | 2017-11-20 08:40 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recloser 19 AN 04 T/R 1x ctr: 348-349 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 8:40 | Morning | Sunday | 2017 | 11
7261 | 2017-11-19 10:48 | 2017-11-19 10:48 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 0 | 10:48 Shutdown Travo 3000 Kv at Benar GS , d/s Bangko fdr #4. ----->Closed at 11:20. Plant maintenance. |  | 1 | 10:48 | Morning | Sunday | 2017 | 11
7262 | 2017-11-19 11:39 | 2017-11-19 11:39 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | 13;39 Sintong fdr#1 load dropped 23A (74-51A) Sintong GFPC T/R 1X. Not checked yet. |  | 1 | 11:39 | Morning | Sunday | 2017 | 11
7263 | 2017-11-19 11:39 | 2017-11-20 10:00 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recloser 25-AD-26 T/R 1x ctr: 117-118 R/F: 51 @2, 51N. also found, Sintong GFPC T/R 1X ctr: 1008-1012 R/F : 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 11:39 | Morning | Sunday | 2017 | 11
7264 | 2017-11-19 17:52 | 2017-11-19 17:52 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 135 | 17:52 3D 13.8KV OCB fdr #3 T/SO. 3D fdr #2 load dropped 135A (176-41A). 3D fdr #4 load dropped 190A (255-65A). 3D fdr #5 Load dropped 58A (150-92A). WIP 3D GFPC T/R 1X. 18:53 Blocked and closed 3D fdr #3, OK then released the block. Not checked yet. |  | 1 | 17:52 | Afternoon | Sunday | 2017 | 11
7265 | 2017-11-19 17:52 | 2017-11-21 17:52 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 135 | Checked & found, 3D OCB fdr #3 T/SO ctr: 443-444 R/F: 50 @1, @2. Patrolled the line & found high palm trees touched Powerline on Pole 4B24A. Cause: Suspected by Lightning. |  | 1 | 17:52 | Afternoon | Sunday | 2017 | 11
7266 | 2017-11-19 17:57 | 2017-11-19 17:57 | 13.8KV 3D FEEDER #2 | Lightning | Lightning | 0 | 3D 13.8KV OCB fdr #2 T/R. Not checked yet. |  | 1 | 17:57 | Afternoon | Sunday | 2017 | 11
7267 | 2017-11-19 17:57 | 2017-11-21 17:57 | 13.8KV 3D FEEDER #2 | Lightning | Lightning | 0 | Checked & found, 3D OCB fdr #2 T/R 1x ctr: 248-249 R/F: 51 @2. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:57 | Afternoon | Sunday | 2017 | 11
7268 | 2017-11-19 18:02 | 2017-11-19 18:02 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 25 | 4D fdr#5 T/R 1X. 4D fdr#4 load dropped 133A (241-108A) Not checked yet. |  | 1 | 18:02 | Afternoon | Sunday | 2017 | 11
7269 | 2017-11-19 18:02 | 2017-11-20 18:02 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 25 | Checked & found, 4D OCB fdr #5 T/R 1x ctr: 307-308 R/F: 51 @2, @3. Patrolled the line & found, @2, @3 broken Pin Insulator on Pole 4D-102. Cause: Lightning. |  | 1 | 18:02 | Afternoon | Sunday | 2017 | 11
7270 | 2017-11-19 18:10 | 2017-11-19 18:10 | 13.8KV 8C FEEDER #2 | Rain and Lightning | Lightning | 8 | 18:10 8C fdr#2 T/R 1x ctr: R/F: 50@3. Checked and found 8C fdr#2 T/R 1x Not Patrolled yet. |  | 1 | 18:10 | Afternoon | Sunday | 2017 | 11
7271 | 2017-11-19 18:10 | 2017-11-27 08:10 | 13.8KV 8C FEEDER #2 | Rain and Lightning | Lightning | 8 | Checked and found 13.8KV VCB #2 T/R 1x Ctr: 516-517 R/F: @3 50. Patrolled the line and found Broken Pin Insulator o/p 9D-50. Cause: Lightning. |  | 1 | 18:10 | Afternoon | Sunday | 2017 | 11
7272 | 2017-11-19 18:10 | 2017-11-19 18:10 | 13.8KV 8C FEEDER #6 | Lightning | Lightning | 65 | 18:10 8C fdr#6 T/R 1x ctr: R/F 51@2. Checked and found 8C fdr#6 T/R 1x. Not Patrooled yet. |  | 1 | 18:10 | Afternoon | Sunday | 2017 | 11
7273 | 2017-11-19 18:10 | 2017-11-27 08:10 | 13.8KV 8C FEEDER #6 | Lightning | Lightning | 65 | Checked and found 13.8KV VCB #6 T/R 1x Ctr: 583-584 R/F: @2 51 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 18:10 | Afternoon | Sunday | 2017 | 11
7274 | 2017-11-19 19:11 | 2017-11-19 19:11 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Unidentified | 0 | 19:11 Duri Community ACB fdr#1 Checked & found D.Comm fdr#1 T/LO, Ctr: 105-109, R/F 51N, 51@1 Patrolled the Line, but found nothing. 20:30 Open LBS KT61, (to Split the Feeder to ward Gor FM facility ) Man. Closed D.Comm fdr#1, but T/O again. 20:40 Closed LBS BKS12 (Transfer part Load to D.Comm fdr#2, Energized Sibayak Complex) Opened LBS KT18 to Split the Feeder and Trouble Shoot at around New Krakatau Complex Man Closed D Comm fdr#1, OK. 21:21 Open LBS 2DF8, (to Isolate Old Krakatau Complex and trouble shoot) Closed LBS KT18, but D.Comm fdr#1 T/O again. 22:06 Closed LBS MR01, (Energized Old Krakatau complex from D.Comm fdr#2) 22:49 Continued Patrolled the Line, but found nothing Closed LBS KT18 (toward new Krakatau complex) Man Closed D.Comm fdr#1, OK. Cause: Unidentified (Continued Re patrolled and Normalize Load tomorrow) |  | 1 | 19:11 | Night | Sunday | 2017 | 11
7275 | 2017-11-20 08:50 | 2017-11-20 08:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 39 | C. Duri fdr #1 load dropped 49A (125-76A). (Informed power Outage at Puncak GS). Not checked yet. |  | 1 | 8:50 | Morning | Monday | 2017 | 11
7276 | 2017-11-20 08:50 | 2017-11-27 08:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 39 | Checked and found C. Duri fdr #1 load dropped. Patrolled the line and found Recloser 39-AV-36 T/R 1x Ctr: 236-237 R/F: @2 51. Cause: Unidentified. |  | 1 | 8:50 | Morning | Monday | 2017 | 11
7277 | 2017-11-20 10:33 | 2017-11-20 10:33 | 13.8KV BEKASAP FEEDER #6 | Fair | Planned Maintenance | 171 | 11:50 Manually open Bekasap Bekasap fdr #6. -----> Closed at :11:50. Replaced TX at well Bekasap #124. Adjusted Voltage at well Aman #11. Plant maintenance. |  | 1 | 10:33 | Morning | Monday | 2017 | 11
7278 | 2017-11-20 13:25 | 2017-11-20 13:25 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | 60 | Minas fdr#3 T/R 1X. Not checked yet. |  | 1 | 13:25 | Afternoon | Monday | 2017 | 11
7279 | 2017-11-20 13:25 | 15/12/2017 08:00 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | 60 | Checked and found Minas fdr #3 T/R 1x Ctr: 229-230 R/F: 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 13:25 | Afternoon | Monday | 2017 | 11
7280 | 2017-11-20 13:53 | 2017-11-20 13:53 | 13.8KV BEKASAP FEEDER #3 | Fair | Planned Maintenance | 350 | 13:53 Manually opened 13.8 Kv Bekasap #3. ----->Closed at :15:26. Setting Voltage at well Bekasap #33. Plant maintenance. |  | 1 | 13:53 | Afternoon | Monday | 2017 | 11
7281 | 2017-11-20 16:06 | 2017-11-20 16:06 | NORTH RUMBAI SUBSTATION | Fair | Under investigation | 0 | 16:06 It was reported No Power at Oliander Comp, Sawit Comp, Randu Comp 16:32 Checked and found 44 Kv N.Rumbai OCB #1 T/O. Counter: 70-71. ( No indication at DSC ). relay flag: 86T , 87 @3. 17:00 Manually Open N.Rumbai fdr #1 ,----->Closed at : 17:06. 17:00 Manually Open N.Rumbai fdr #2 ,----->Closed at : 17:09. 17:04 Manually Closed 44 Kv N.Rumbai OCB #1. Cause: Under Investigation. |  | 1 | 16:06 | Afternoon | Monday | 2017 | 11
7282 | 2017-11-20 19:42 | 2017-11-20 19:42 | 13.8KV PETAPAHAN FEEDER #8 | Rain | Unidentified | 103 | 19:42 Petapahan Fdr# 8 T/R 1X Not Checked yet. |  | 1 | 19:42 | Night | Monday | 2017 | 11
7283 | 2017-11-20 19:42 | 2017-11-22 19:42 | 13.8KV PETAPAHAN FEEDER #8 | Rain | Unidentified | 103 | Checked & found, Petapahan VCB fdr #8 T/R 1x ctr: 356-357 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 19:42 | Night | Monday | 2017 | 11
7284 | 2017-11-20 20:53 | 2017-11-20 20:53 | 13.8KV DURI COMMUNITY FEEDER #3 | Cloudy | Planned Maintenance | 0 | 20:53 Manually opened Recl. 2 F 07 d/s D. Comm Fdr#3 to replaced @3 b/o fuse o/p... & cut palm high trees o/p..... 21:16 Closed Recl. 2 F07. Cause: Planned Maintenance. |  | 1 | 20:53 | Night | Monday | 2017 | 11
7285 | 2017-11-21 11:05 | 2017-11-21 11:05 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | 954 | 11:05 Manual Opened 13.8 KV Bangko fdr #1. Replaced B/O Recl. 23-W-12. 13:30 Blocked & closed Bangko VCB fdr#1, then release the block. 15:03 Manual Opened Again 13.8 KV Bangko fdr #1. Closed bypass switch of Recl. 23W12 (Recloser pumping). 15:13 Blocked & closed Bangko VCB fdr#1, then release the block. Cause: Planned Maintenance. | 11111 | 1 | 11:05 | Morning | Tuesday | 2017 | 11
7286 | 2017-11-21 11:23 | 2017-11-21 11:23 | MINAS POWER PLANT |  |  | - | 11:23 S/U MGT#10, then on line the unit at 12:40. (Running test). |  | 1 | 11:23 | Morning | Tuesday | 2017 | 11
7287 | 2017-11-21 11:38 | 2017-11-21 11:38 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 203 | 11:38-12:00 Manually Opened 13.8 KV Nella fdr #1. Replaced Secondary Cable at Well Bangko#34. Cause: Plant Maintenance. |  | 1 | 11:38 | Morning | Tuesday | 2017 | 11
7288 | 2017-11-21 15:05 | 2017-11-21 15:05 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 26 | It was reported B/O fuse O/P 12-E7-04 (ND fdr #1). Not checked yet. |  | 1 | 15:05 | Afternoon | Tuesday | 2017 | 11
7289 | 2017-11-21 15:05 | 2017-11-22 11:20 | 13.8KV NORTH DURI FEEDER #1 | Fair | Animal | 26 | Replaced @1 @2 B/O fuse for 112.5 KVA Tx with the same size. Cause : Animal ( Bird ). |  | 1 | 15:05 | Afternoon | Tuesday | 2017 | 11
7290 | 2017-11-21 15:12 | 2017-11-21 15:12 | 13.8KV BATANG FEEDER #2 | Fair | Lightning | 0 | 15:12 Batang fdr#2 T/O 1X (In blocked position for PT. KRS Pilling Pipe). 15:21 Closed Batang VCB fdr#2, then release the block. Not checked yet. |  | 1 | 15:12 | Afternoon | Tuesday | 2017 | 11
7291 | 2017-11-21 15:12 | 2017-11-26 08:12 | 13.8KV BATANG FEEDER #2 | Fair | Lightning | 0 | Checked & found Batang OCB fdr#2 T/O Ctr:151-152 R/F:51N. Patrolled the line & found @1 Broken Pin insulator o/p 39-AI-31. Cause : Lightning. |  | 1 | 15:12 | Afternoon | Tuesday | 2017 | 11
7292 | 2017-11-22 08:12 | 2017-11-22 08:12 | MINAS POWER PLANT |  |  | - | 08:12 S/U MGT #10, Then Online the unit at.08:55 (Running Test). |  | 1 | 8:12 | Morning | Wednesday | 2017 | 11
7293 | 2017-11-22 11:05 | 2017-11-22 11:05 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 77 | 11:05 Manually opened LBS 30-AN-38. d/s Katigul fdr #2. Due to Replace @1@2 b/o fuse for 300 KVA Tx at well Pagar #27. 11:08 Manually closed LBS 30-AN-38. Cause : Plan Maintenance. |  | 1 | 11:05 | Morning | Wednesday | 2017 | 11
7294 | 2017-11-22 16:25 | 2017-11-22 16:25 | MINAS POWER PLANT |  |  | - | 16:25 MGT #10 Opened Gen.Breaker then S/D the unit after Running Test. |  | 1 | 16:25 | Afternoon | Wednesday | 2017 | 11
7295 | 2017-11-23 05:30 | 2017-11-23 05:30 | MINAS POWER PLANT |  |  | - | 05:30 S/U MGT #10, Then Online the unit at.05:50 (Check Vibration ). |  | 1 | 5:30 | Morning | Thursday | 2017 | 11
7296 | 2017-11-23 11:06 | 2017-11-23 11:06 | 13.8KV BEKASAP FEEDER #3 | Fair | Planned Maintenance | 654 | 11:06 Manually opened Bekasap VCB fdr #3 due to: Replaced Recloser #01A at Bekasap EOR. 14:06 Manually blocked and closed Bekasap VCB fdr #3 --> OK and then released the block. Cause: Plan Maintenance. | 1111 | 1 | 11:06 | Morning | Thursday | 2017 | 11
7297 | 2017-11-23 14:31 | 2017-11-23 14:31 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Recloser | 321 | 10:57 3D OCB fdr #4 T/R 1x. 14:31 3D OCB fdr #4 T/LO. 19:00 Checked and found 3D 13.8KV OCB fdr #4 T/LO ctr:712-765 R/F:51 @1, @2. Patrolled the line and found Reclose 2D-38 T/LO ctr:..... Also found @1 broken Isolation switch of Recl. 2D-38. Isolated Recloser 2D-38 and Closer By Pass switch. 19:52 Blocked and closed 3D fdr #4, OK then released the block. Cause: Recloser. |  | 1 | 14:31 | Afternoon | Thursday | 2017 | 11
7298 | 2017-11-23 14:33 | 2017-11-23 14:33 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse on pole 02-08-04 D/S C Duri fdr #3. Not checked yet. |  | 1 | 14:33 | Afternoon | Thursday | 2017 | 11
7299 | 2017-11-23 14:33 | 2017-02-12 14:25 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified (Fuse) | 0 | Checked & found, B/O @1@2 fuse o/p 02-08-04 for 112.5 KVATX (d/s CD fdr#3) Replaced the Fuse with the same size, then Energized the TX Cause : Unidentified (fuse) |  | 1 | 14:33 | Afternoon | Thursday | 2017 | 11
7300 | 2017-11-23 15:30 | 2017-11-23 15:30 | MINAS POWER PLANT |  |  | - | 15:30 S/U MGT #1 and then On Line the unit at 16:00. |  | 1 | 15:30 | Afternoon | Thursday | 2017 | 11
7301 | 2017-11-23 16:45 | 2017-11-23 16:45 | CENTRAL DURI POWER PLANT |  |  | - | 16:45 S/U CDGT #3 and then On Line the unit at 17:02. |  | 1 | 16:45 | Afternoon | Thursday | 2017 | 11
7302 | 2017-11-23 16:48 | 2017-11-23 16:48 | 13.8KV 6DN FEEDER #6 | Fair | Planned Maintenance | 58 | 16:48 Manually opened Recloser: 6E-30 due to: Replaced @ broken Fuse Cut Out on terminal pole well:6E-73. Manually closed Recloser: 6E-30. Cause: Plan Maintenance. |  | 1 | 16:48 | Afternoon | Thursday | 2017 | 11
7303 | 2017-11-23 16:55 | 2017-11-23 16:55 | MINAS POWER PLANT |  |  | - | 16:55 S/U MGT #3 and then On Line the unit at 17:10. |  | 1 | 16:55 | Afternoon | Thursday | 2017 | 11
7304 | 2017-11-23 17:13 | 2017-11-23 17:13 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy and Lightning | Lightning | 42 | SO.Bekasap OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 17:13 | Afternoon | Thursday | 2017 | 11
7305 | 2017-11-23 17:13 | 2017-11-27 17:13 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy and Lightning | Lightning | 42 | Checked & found Recloser 34-BI-18 T/R, Ctr: 163-164, R/F: None. Patrolled the Line, found @1 Broken LA O/P 32-BG-13 Cause : Lightning |  | 1 | 17:13 | Afternoon | Thursday | 2017 | 11
7306 | 2017-11-23 18:05 | 2017-11-23 18:05 | SINABUNG MINI SUBSTATION | Fair | Planned Maintenance | 0 | 18:05 Manually opened Recloser 4160 V Singgalang Mini Substation due to: Repair spark on Hot Line Clamp on pole 11-52 in front of Gading Office. 18:17 Manually closed Recloser 4160 V Singgalang Mini Substation. Cause: Plan Maintenance. |  | 1 | 18:05 | Afternoon | Thursday | 2017 | 11
7307 | 2017-11-23 20:26 | 2017-11-23 20:26 | NORTH DURI POWER PLANT |  |  | - | 20:26 NDC #3 Open Generator Breaker and S/D the unit at : 20:29. |  | 1 | 20:26 | Night | Thursday | 2017 | 11
7308 | 2017-11-24 03:05 | 2017-11-24 03:05 | NORTH RUMBAI SUBSTATION | Rain | Under investigation | 0 | 03:05 N.Rumbai 44KV OCB #1 T/O. 04:16 Checked & found N.Rumbai 44KV OCB #1 T/R Counter:........ R/F :86T , 87@1. 04:19 Open N.Rumbai 4.16 KV VCB #1. Open N.Rumbai 4.16 KV VCB #2. 04:24 Closed N.Rumbai 44 KV OCB #1. ----->Ok. 04:26 Closed N.Rumbai 4.16 KV VCB #1. Counter: 407. 04:27 Closed N.Rumbai 4.16 KV VCB #2. Counter: 359. Couse: Under investigation. |  | 1 | 3:05 | Night | Friday | 2017 | 11
7309 | 2017-11-24 08:45 | 2017-11-24 08:45 | MINAS POWER PLANT |  |  | - | 08:45 S/U MGT #2 and then On Line the unit at 09:12. |  | 1 | 8:45 | Morning | Friday | 2017 | 11
7310 | 2017-11-24 09:06 | 2017-11-24 09:06 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Broken Fuse Cut Out | 78 | It was reported b/o fuse o/p : 08-L3-15 d/s CD fdr #1. Not checked yet |  | 1 | 9:06 | Morning | Friday | 2017 | 11
7311 | 2017-11-24 09:06 | 2017-02-12 15:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Broken Fuse Cut Out | 78 | Checked & found, Broken @1 FCO o/p 08-L3-15 (d/s CD fdr#1) Patrolled the Line found nothing, Will Replace FCO soon. Cause : Broken Fuse Cut Out |  | 1 | 9:06 | Morning | Friday | 2017 | 11
7312 | 2017-11-24 09:07 | 2017-11-24 09:07 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Transformer Failure | 365 | It was reported b/o fuse o/p : 04-07-29 d/s CD fdr #9. Not checked yet |  | 1 | 9:07 | Morning | Friday | 2017 | 11
7313 | 2017-11-24 09:07 | 2017-02-12 14:51 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Transformer Failure | 365 | Checked & found, b/o @1@3 Fuse o/p 04-07-29 for 112.5KVATX (d/s CD fdr#9) Perform TTR & Megger, found the TX was Low Reading., will replaced soon. Cause : Transformer Failure |  | 1 | 9:07 | Morning | Friday | 2017 | 11
7314 | 2017-11-24 10:14 | 2017-11-24 10:14 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 0 | 10:14 Manually opened Bekasap OCB fdr #2 due to : Tie In well Bekasap #162 and #89. 11:36 Manually blocked and closed Bekasap OCB fdr #2 then release the blocked. Cause : Construction Job. Loss: 335 bbls/46 well |  | 1 | 10:14 | Morning | Friday | 2017 | 11
7315 | 2017-11-24 10:33 | 2017-11-24 10:33 | 13.8KV 3D FEEDER #4 | Fair | Unidentified | 129 | 10:33 It was reported no power at well. 1D-85 d/s 3D fdr #4 15:00 Checked and founded recloser 2D-33 T/SO Ctr.45-46. Blocked and closed recloser 2D-33, ok then release the block. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:33 | Morning | Friday | 2017 | 11
7316 | 2017-11-24 14:19 | 2017-11-24 14:19 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 21 | 14:19 Manually opened Bangko OCB fdr #4 due to : Adjusted voltage at well BKO #221. Tx=150KVa R/M=140-40. Sec. Voltage : 960-900Volt. 14:26 Manually blocked and closed Bangko OCB fdr #4 and then released the block.. Cause : Plan Maintenance. |  | 1 | 14:19 | Afternoon | Friday | 2017 | 11
7317 | 2017-11-24 14:23 | 2017-11-24 14:23 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 155 | 14:23 Manually opened Nella OCB fdr #1 due to : Internal connection at well KB #92. Tx=150KVa R/M=140-38HP, Sec.Voltage : 960-480Volt. 14:30 Manually blocked and closed Nella OCB fdr #1 and then released the block. Cause : Plan Maintenance. |  | 1 | 14:23 | Afternoon | Friday | 2017 | 11
7318 | 2017-11-24 16:23 | 2017-11-24 16:23 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 55 | 16:23 Manually open Pematang OCB fdr #2 due to : Adjusted voltage at well Pematang #32. Tx : 150KVa R/M : 105-125HP Sec. Voltage : 1005-1044 Voltage. 16:29 Manually blocked and closed Pematang OCB fdr #2 and then released the block. Cause : Plan Maintenance. |  | 1 | 16:23 | Afternoon | Friday | 2017 | 11
7319 | 2017-11-24 22:01 | 2017-11-24 22:01 | 13.8KV PUNGUT FEEDER #2 | Fair | Broken Fuse Cut Out | 27 | 22:01 Pungut fdr #2 load dropped 14A (57-43A). It was reported no power at Sebanga GS and Intan GS. 23:20 Checked and found Recloser 46 BP 12 T/O (On Block). Blocked and closed Recloser 45 BP 12, burt trip again. Patrolled the line and found @1, @3 broken FCO at well Intan #08, then Isolated. Blocked and closer the Recloser, OK. Cause: Broken FCO. |  | 1 | 22:01 | Night | Friday | 2017 | 11
7320 | 2017-11-25 01:07 | 2017-11-25 01:07 | 13.8KV BANGKO FEEDER #4 | Rain | Unidentified | 218 | 01:07 Bangko 13.8KV OCB fdr #4 T/O ctr:0019-0020 R/F: F35. Bangko GFPC T/O. 02:00 Checked and found Bangko fdr #4 T/O. Also found Bangko GFPC T/O. 02:04 Blocked and Closed Bangko GFPC, OK then realsed the block. Blocked and Closed Bangko fdr #4, OK then realsed the block. Not Patrolled yet. |  | 1 | 1:07 | Night | Saturday | 2017 | 11
7321 | 2017-11-25 01:07 | 2017-11-27 08:00 | 13.8KV BANGKO FEEDER #4 | Rain | Unidentified | 218 | Checked and found Bangko fdr #4 T/O Ctr: 0019-0020 R/F: 64. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 1:07 | Night | Saturday | 2017 | 11
7322 | 2017-11-25 13:18 | 2017-11-25 13:18 | 13.8KV 3D FEEDER #8 | Fair | Unidentified | 30 | 13:18 3D OCB fdr#8 T/O (Block position). 13:24 Blocked & closed 3D OCB fdr#8, then release the block. Not checked yet. |  | 1 | 13:18 | Afternoon | Saturday | 2017 | 11
7323 | 2017-11-25 13:18 | 2017-05-12 08:00 | 13.8KV 3D FEEDER #8 | Fair | Unidentified | 30 | Checked and found 3D fdr #8 T/O Ctr: 306-307 R/F: 50N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 13:18 | Afternoon | Saturday | 2017 | 11
7324 | 2017-11-25 14:48 | 2017-11-25 14:48 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 47 | 14:48 Manually Open Recl 28AF02 (Sintong fdr#2). Relocated Line well Benar#45 for Tie in new Loc at Benar. 15:17 Blocked & closed Recl. 28AF02, then release the block. Cause: Planned Maintenance. |  | 1 | 14:48 | Afternoon | Saturday | 2017 | 11
7325 | 2017-11-25 15:50 | 2017-11-25 15:50 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 28 | It was reported B/O fuse o/p 09-S4-04 (C.Duri fdr#4). Not checked yet. |  | 1 | 15:50 | Afternoon | Saturday | 2017 | 11
7326 | 2017-11-25 15:50 | 2017-02-12 16:13 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 28 | Checked & found, b/o @1 fuse o/p 09-S4-04 for 112.5KVATX (d/s CD fdr#4) Replaced the Fuse with the Same size, then Energized the TX Cause : Unidentified (Fuse) |  | 1 | 15:50 | Afternoon | Saturday | 2017 | 11
7327 | 2017-11-26 13:28 | 2017-11-26 13:28 | 13.8KV SINTONG FEEDER #1 | Cloudy | Unidentified (L/A) | 0 | Sintong fdr #1 load dropped 23A (74-51A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 13:28 | Afternoon | Sunday | 2017 | 11
7328 | 2017-11-27 10:30 | 2017-11-27 10:30 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 55 | 10:30 Manually opened Bangko VCB fdr #4 due to : Replaced @1,3 b/o fuse for 150 KVaTx with the same size at Bangko #221. 10:33 Manually blocked and closed Bangko VCB fdr #4 then release the block. Cause : Plan Maintenance. |  | 1 | 10:30 | Morning | Monday | 2017 | 11
7329 | 2017-11-27 14:15 | 2017-11-27 14:15 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified | 121 | 14:15 CKBS VCB fdr #6 T/R. Cause : Not checked yet. |  | 1 | 14:15 | Afternoon | Monday | 2017 | 11
7330 | 2017-11-27 14:35 | 2017-11-27 14:35 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Tree | 260 | 14:35 Batang VCB fdr#3 T/O. 15:37 Checked & found Batang VCB fdr#3 T/LO Ctr:356-360 R/F:51@1. Patrolled the line found Akasia tree touching powerline at Terminal pole Pemburu #14. Dismantle the tree from powerline. 17:24 Blocked and closed Batang VCB fdr#3 --> OK and then released the block. Cause: Tree. |  | 1 | 14:35 | Afternoon | Monday | 2017 | 11
7331 | 2017-11-27 15:55 | 2017-11-27 15:55 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 30 | 15:55 4B OCB fdr#1 T/R 1x. 16:12 4B OCB fdr#1 T/R 1x Ctr:319-320 R/F:51@2. Not patrolled yet. |  | 1 | 15:55 | Afternoon | Monday | 2017 | 11
7332 | 2017-11-27 15:55 | 2017-05-12 08:00 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 30 | Checked and found 4B fdr #1 T/R Ctr: 294-296 R/F: 50 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 15:55 | Afternoon | Monday | 2017 | 11
7333 | 2017-11-27 17:12 | 2017-11-27 17:12 | NORTH DURI POWER PLANT |  |  | - | 17:12 S/U NDC #3 , online at : 19:04. |  | 1 | 17:12 | Afternoon | Monday | 2017 | 11
7334 | 2017-11-27 20:04 | 2017-11-27 20:04 | MINAS POWER PLANT |  |  | - | 20:04 MGT #2 offline & S/D for Standby. |  | 1 | 20:04 | Night | Monday | 2017 | 11
7335 | 2017-11-27 21:04 | 2017-11-27 21:04 | CENTRAL DURI POWER PLANT |  |  | - | 21:04 CDGT #5 offline & S/D for standby. |  | 1 | 21:04 | Night | Monday | 2017 | 11
7336 | 2017-11-27 21:25 | 2017-11-27 21:25 | MINAS POWER PLANT |  |  | - | 21:25 MGT #1 offline & S/D for Standby. |  | 1 | 21:25 | Night | Monday | 2017 | 11
7337 | 2017-11-27 21:42 | 2017-11-27 21:42 | MINAS POWER PLANT |  |  | - | 21:42 MGT #3 offline & S/D for Standby. |  | 1 | 21:42 | Night | Monday | 2017 | 11
7338 | 2017-11-28 08:47 | 2017-11-28 08:47 | CENTRAL KOTABATAK SUBSTATION | Fair | Construction Job | 0 | 08:47 Manually opened 115 KV Line CKB-Petapahan GCB #1. Installed bus pipe conector at Petapahan Subst. and modification pole. 17:05 Blocked and closed 115 KV Line CKB-Petapahan GCB #1, then release the block. Cause : Construction Job. |  | 1 | 8:47 | Morning | Tuesday | 2017 | 11
7339 | 2017-11-28 10:10 | 2017-11-28 10:10 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Others | 0 | It was reported b/o fuse on pole 09-N4-02 D/S C. Duri fdr #16. Not checked yet. |  | 1 | 10:10 | Morning | Tuesday | 2017 | 11
7340 | 2017-11-28 10:10 | 2017-02-12 10:10 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Others | 0 | Checked & found B/O Fuse o/p 09-N4-02 for 112.5KVATX (d/s C. Duri fdr #16) Replaced the fuse with the same size, then energized the TX. Cause : Other. |  | 1 | 10:10 | Morning | Tuesday | 2017 | 11
7341 | 2017-11-28 10:55 | 2017-11-28 10:55 | MINAS POWER PLANT | Fair |  | - | 10:55 S/U MGT#3 and then On line the Unit at 11:15. |  | 1 | 10:55 | Morning | Tuesday | 2017 | 11
7342 | 2017-11-28 11:23 | 2017-11-28 11:23 | MINAS POWER PLANT | Fair |  | - | 11:23 S/U MGT# 1 and then On line the unit at 11:50. |  | 1 | 11:23 | Morning | Tuesday | 2017 | 11
7343 | 2017-11-28 13:55 | 2017-11-28 13:55 | MINAS POWER PLANT | Fair |  | - | 13:55 S/U MGT#2 at then On line Unit at 14:14. |  | 1 | 13:55 | Afternoon | Tuesday | 2017 | 11
7344 | 2017-11-28 17:10 | 2017-11-28 17:10 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 28 | 3DOCB fdr#3 T/R 1X. Not checked yet. |  | 1 | 17:10 | Afternoon | Tuesday | 2017 | 11
7345 | 2017-11-28 17:10 | 2017-05-12 08:10 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 28 | Checked and found 3D fdr #3 T/R 1x Ctr: 444-444 (counter not working) R/F: 51 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 17:10 | Afternoon | Tuesday | 2017 | 11
7346 | 2017-11-28 17:10 | 2017-11-28 17:10 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Unidentified | 0 | 3D fdr# 2 load dropped 35A (186-151A). Not checked yet. |  | 1 | 17:10 | Afternoon | Tuesday | 2017 | 11
7347 | 2017-11-28 17:10 | 2017-04-12 08:10 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found 3D fdr #2 load dropped. Patrolled the line but found nothing. Cause: Unidentified |  | 1 | 17:10 | Afternoon | Tuesday | 2017 | 11
7348 | 2017-11-28 17:10 | 2017-11-28 17:10 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | 3D fdr#4 load dropped 68A (237-169A). Not checked yet. |  | 1 | 17:10 | Afternoon | Tuesday | 2017 | 11
7349 | 2017-11-28 17:10 | 2017-05-12 08:10 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found 3D fdr #4 load dropped. Patrolled the line and found Recloser 2D-14 T/R 4x Ctr: 54-58. Cause: Lightning. |  | 1 | 17:10 | Afternoon | Tuesday | 2017 | 11
7350 | 2017-11-28 17:42 | 2017-11-28 17:42 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Rangau fdr#2 load dropped 90A (97-7A). Not checked yet. |  | 1 | 17:42 | Afternoon | Tuesday | 2017 | 11
7351 | 2017-11-28 17:42 | 2017-11-30 17:42 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 23-BD-01 T/R, Ctr: 311-312, R/F: SGF Patrolled the Line, found Broken @1 @3 Dead End O/P 22-BD-03 Cause : Lightning |  | 1 | 17:42 | Afternoon | Tuesday | 2017 | 11
7352 | 2017-11-29 05:25 | 2017-11-29 05:25 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Lightning | 122 | 44KV PEMATANG MAIN - PETANI LINE GCB#1 T/R 1x. Petani fdr#1 load dropped 165A (165-0A). Petani fdr#2 load dropped 60A (60-0A). Pematang fdr#1 load dropped 141A (197-56A). Pematang fdr#2 load dropped 16A (94-83A). Not checked yet. |  | 1 | 5:25 | Morning | Wednesday | 2017 | 11
7353 | 2017-11-29 05:25 | 2017-11-30 05:25 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Lightning | 122 | Checked & found, Pematang 44KV OCB#1 T/R 1x, Ctr: 4006-4007, R/F: 51N. Patrolled the Line, found Broken @3 Dead End O/P 22-BD-03 Cause : Lightning |  | 1 | 5:25 | Morning | Wednesday | 2017 | 11
7354 | 2017-11-29 05:25 | 2017-11-30 05:25 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Lightning | 122 | Checked & found, Pematang 44KV OCB#1 T/R 1x, Ctr: 4006-4007, R/F: 51N. Patrolled the Line, found Broken @3 Dead End O/P 22-BD-03 Cause : Lightning |  | 1 | 5:25 | Morning | Wednesday | 2017 | 11
7355 | 2017-11-29 07:22 | 2017-11-29 07:22 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | C.Duri 13.8KV ACB#27 fdr#14 T/R 1X Ctr:378-379 R/F: 51 @1@2 Not Patrolled yet. |  | 1 | 7:22 | Morning | Wednesday | 2017 | 11
7356 | 2017-11-29 07:22 | 2017-04-12 07:22 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:22 | Morning | Wednesday | 2017 | 11
7357 | 2017-11-29 10:47 | 2017-11-29 10:47 | 13.8KV NELLA FEEDER #2 | Fair | Planned Maintenance | 95 | 10:47 Manually opened Bangko Fdr#2 to Replace 300-300 kVATx at Well Bangko #50 for VSD 480 V. 11:40 Manually Closed Back after finished the jobs. Cause : Planned Maintenance |  | 1 | 10:47 | Morning | Wednesday | 2017 | 11
7358 | 2017-11-29 11:00 | 2017-11-29 11:00 | MINAS POWER PLANT | Fair |  | - | 11:00 MGT#8 Off line then S/D to Replace card of Computer S. 14:15 MGT#8 S/U, then On Line at 14:39 after success Card Replacement |  | 1 | 11:00 | Morning | Wednesday | 2017 | 11
7359 | 2017-11-29 13:21 | 2017-11-29 13:21 | 13.8KV NORTH DURI FEEDER #6 | Fair | Unidentified | 0 | N.Duri VCB fdr#6 T/R 1X. Not checked yet. |  | 1 | 13:21 | Afternoon | Wednesday | 2017 | 11
7360 | 2017-11-29 13:21 | 2017-04-12 08:00 | 13.8KV NORTH DURI FEEDER #6 | Fair | Unidentified | 0 | Checked and found N. Duri VCB #6 T/R 1x Ctr: 295-296 R/F: 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 13:21 | Afternoon | Wednesday | 2017 | 11
7361 | 2017-11-29 17:23 | 2017-11-29 17:23 | MINAS POWER PLANT | Fair |  | - | MGT#10 Off line then S/D for S/B Waiting Generator balance cuing. |  | 1 | 17:23 | Afternoon | Wednesday | 2017 | 11
7362 | 2017-11-30 09:57 | 2017-11-30 09:57 | 13.8KV SINTONG FEEDER #2 | Fair | Construction Job | 0 | 09:57 Man. Opened Recl. 28-AF-02 (Sintong fdr#2) Project, Tie In New Well Benar #45. 15:08 Man Closed back the recloser after finished the Jobs. Cause : Planned Construction. |  | 1 | 9:57 | Morning | Thursday | 2017 | 11
7363 | 2017-11-30 10:07 | 2017-11-30 10:07 | 13.8KV PETANI FEEDER #1 | Fair | Planned Maintenance | 182 | 10:07 Transfer Part Load Petani fdr#1 to fdr#3 by Closed LBS 34-AZ-13, then Man. Opened PTN fdr#1 (Load PTN fdr#1 Off, Except Ptn GS) to Replace 150-300 KVATX at Well PTN#120. 11:35 Man Closed & Normalized back PTN fdr#1 & PTN fdr#3. Cause : Planned Maintenance. |  | 1 | 10:07 | Morning | Thursday | 2017 | 11
7364 | 2017-11-30 11:45 | 2017-11-30 11:45 | 13.8KV PETANI FEEDER #2 | Fair | Planned Maintenance | 65 | 11:45 Man.Opened Petani OCB fdr#2. to Replace 150-500KVATX at Well PTN#19. 12:36 Man Closed back the OCB after finished the Jobs. Cause: Planned Maintenance. |  | 1 | 11:45 | Morning | Thursday | 2017 | 11
7365 | 2017-11-30 17:51 | 2017-11-30 17:51 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 16 | 17:53 Ketigul VCB fdr#1 T/O. (In BLock Status, Rig Jobs). 18:04 Man Closed Ketigul VCB fdr#1, after got Clearence from RIG ACS#05 and TDO on duty. Cause : Not Checked yet. |  | 1 | 17:51 | Afternoon | Thursday | 2017 | 11
7366 | 2017-11-30 17:51 | 2017-04-12 17:51 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 16 | Checked & found, Ketigul VCB fdr #1 T/O ctr: 193-194 R/F: 51N @1 @2. Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 17:51 | Afternoon | Thursday | 2017 | 11
7367 | 2017-01-12 05:59 | 2017-01-12 05:59 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Recloser | 0 | 05:59 Duri Community ACB #30 (feeder #2) T/R 1x. 09:00 Got Information Any Explosion at . Checked & found Broken Bushing of Recloser for MSS Mini Substation Perform Switching to Replace the Recloser. 14:22 Closed LBS LKT 24, ------> Closed at 16:56 14:30 Opened LBS KRC 20, ------> Opened at 16:55 14:40 Closed LKT 61, ------> Opened at 16:46 14:47 Opened ACB# 30 fdr#2----> Closed at 16:45 14:55 Opened LBS 2F 151 ------> Closed at 16:29 Finished Replace Recloser,--> Closed at 16:36 Cause : Recloser (broken Bushing) |  | 1 | 5:59 | Morning | Thursday | 2017 | 1
7368 | 2017-01-12 08:08 | 2017-01-12 08:08 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | N.Duri VCB fdr#11 T/R 1x. Not checked yet. |  | 1 | 8:08 | Morning | Thursday | 2017 | 1
7369 | 2017-01-12 08:08 | 2017-05-12 08:00 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | Checked and found N Duri fdr #1 T/R 1x Ctr: 158-159 R/F: 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 8:08 | Morning | Thursday | 2017 | 1
7370 | 2017-01-12 09:01 | 2017-01-12 09:01 | 13.8KV LIBO FEEDER #1 | Fair | Animal | 76 | 09:01 Libo OCB fdr#1 T/O. Checked & found Libo OCB fdr#1 T/LO, Ctr: 563-566, R/F 51N & 51@1. Patrolled the Line, found Dead Monkey o/p 34-CC-34 Dismantled the Animal, then Tried to Close from DSC, but Fail. 10:51 Blocked & Closed from Local, OK. then released the Block. Cause: Animal (monkey). |  | 1 | 9:01 | Morning | Thursday | 2017 | 1
7371 | 2017-01-12 10:00 | 2017-01-12 10:00 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 23 | It was reported B/O fuse for 112.5KVATx O/P 08-M1-06 (d/s C.Duri fdr#2) Not checked yet. |  | 1 | 10:00 | Morning | Thursday | 2017 | 1
7372 | 2017-01-12 10:00 | 2017-02-12 15:33 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 23 | Checked & found, b/o @1 Fuse o/p 08-M1-06, for 112.4KVATX (d/s CD fdr#2) Replaced the fuse with the same size, then Energized the TX Cause : Unidentified (Fuse) |  | 1 | 10:00 | Morning | Thursday | 2017 | 1
7373 | 2017-02-12 09:50 | 2017-02-12 09:50 | 13.8KV BEKASAP FEEDER #3 | Fair | Planned Maintenance | 96 | 09:50 Perform by OP. Manually Open Bekasap OCB fdr#3 to Replace Transformer at Well BKS #54 10:57 Manually Closed back Bekasap OCB fdr#3 after finished replace Transformer. Cause: Planned Maintenance |  | 1 | 9:50 | Morning | Sunday | 2017 | 2
7374 | 2017-02-12 11:03 | 2017-02-12 11:03 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 1119 | 11:03 By OP, Manually Opened Bekasap OCB fdr#2 to Replace Transformer at Well BKS#41 and BKS#47. 14:03 Manually Closed Bekasap OCB fdr#2 after finished the Jobs replace Transformers. Cause: Planned Maintenance | 12345 | 1 | 11:03 | Morning | Sunday | 2017 | 2
7375 | 2017-02-12 15:37 | 2017-02-12 15:37 | 13.8KV 4D FEEDER #2 | Fair | Unidentified | 0 | 15:37 4D fdr#2 Load dropped 112A (154-42A). Not checked yet |  | 1 | 15:37 | Afternoon | Sunday | 2017 | 2
7376 | 2017-02-12 15:37 | 2017-05-12 08:00 | 13.8KV 4D FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recloser 2D-204 T/R 4x. Patrolled the line and found nothing. Cause: Unidentified. |  | 1 | 15:37 | Afternoon | Sunday | 2017 | 2
7377 | 2017-02-12 16:07 | 2017-02-12 16:07 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | C.Duri ACB fdr#15 T/R 1x, Ctr: 373-374, R/F: 51 @2 Not checked yet. |  | 1 | 16:07 | Afternoon | Sunday | 2017 | 2
7378 | 2017-02-12 16:07 | 2017-04-12 16:07 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | Checked & found, Central Duri ACB #18 fdr #15 T/R 1x ctr: 373-374 R/F: 51. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 16:07 | Afternoon | Sunday | 2017 | 2
7379 | 2017-03-12 09:36 | 2017-03-12 09:36 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 39 | 09:36 Man. Opened Recl. 46 BP 12 (d/s Pungut fdr#2) to Replace Broken @1@2@3 FCO at Well Intan# 8 11:54 Man Closed Back the Recloser after finished the Jobs. Cause: Planned Maintenance. |  | 1 | 9:36 | Morning | Sunday | 2017 | 3
7380 | 2017-03-12 10:37 | 2017-03-12 10:37 | 13.8KV 4B FEEDER #1 | Cloudy | Tree | 159 | 10:37 4B VCB fdr#1 T/LO, Ctr: 320-324, R/F: 51 @1@2 4B fdr#2 Load dropped 32A(98-67A) 4B fdr#3 Load dropped 132A (188-56A) WIP GS6. Patrolled the line, found Fall down Tree touching the Line and Broken LA at Well 4A-62 Dismantled and isolate the Tree and LA 13:20 Blocked & Closed 4B VCB fdr#1, then released the Block Cause: Tree. |  | 1 | 10:37 | Morning | Sunday | 2017 | 3
7381 | 2017-03-12 10:56 | 2017-03-12 10:56 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning Arrester | 13 | 10:56 Rokan OCB fdr#2 T/R 1x. 16:00 Checked & found, Rokan VCB fdr #2 T/R 1x ctr: 1257-1258 R/F: 51N. Patrolled the line & found, @2 broken Lightning Arrester on Pole 31-AV-27. Cause: Lightning Arrester. |  | 1 | 10:56 | Morning | Sunday | 2017 | 3
7382 | 2017-03-12 15:24 | 2017-03-12 15:24 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy | Unidentified | 54 | 15:24 SOBEK OCB fdr#1 T/R 1x Not checked yet. |  | 1 | 15:24 | Afternoon | Sunday | 2017 | 3
7383 | 2017-03-12 15:24 | 2017-05-12 15:24 | 13.8KV SO BEKASAP FEEDER #1 | Cloudy | Unidentified | 54 | Checked & found, South Bekasap OCB fdr #1 T/R 1x ctr: 416-417 R/F: 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:24 | Afternoon | Sunday | 2017 | 3
7384 | 2017-04-12 23:59 | 2017-04-12 23:59 | CPI POWER SYSTEM |  | Normal Condition | - | Normal System Condition. |  | 1 | 23:59 | Night | Wednesday | 2017 | 4
7385 | 2017-05-12 09:40 | 2017-05-12 09:40 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 225 | 09:40 Manually Open 13.8KV S. Balam VCB fdr #1. Replaced PT of Recloser 17 Z 01. 10:36 Closed 13.8KV S. Balam VCB fdr #1. Plan Maintenance. |  | 1 | 9:40 | Morning | Friday | 2017 | 5
7386 | 2017-05-12 15:34 | 2017-05-12 15:34 | 13.8KV 3D FEEDER #4 | Fair | Lightning Arrester | 462 | 15:34 3D GFPC T/R 1X. 3D fdr #4 load 129A (237-108A). 16:00 It was reported no Power at area 1E. 17:30 Checked and found Recl. 2D-14 T/LO ctr:158-164. Patrolled the line but found nothing. Blocked and closed Recloser 2D-14 tripped again. 18:00 Continued patrol the line and found Recl. 2D-44 T/SO Counter:13-14 Blocked and closed Recloser 2D-14, OK the released the block. 19:00 Opened Recloser 2D-14. By pass Recloser 2D-44. 19:30 Blocked and closed Recloser 2D-14 but trip again and 3D GFPC #1 Trip. Isolated Recloser 2D-44. 19:37 Blocked and closed Recloser 2D-14, OK and then released the block. Cause: Not patrolled yet. |  | 1 | 15:34 | Afternoon | Friday | 2017 | 5
7387 | 2017-05-12 15:34 | 2017-06-12 10:47 | 13.8KV 3D FEEDER #4 | Fair | Lightning Arrester | 462 | 10:47 Patrolled the line and found @3 Broken LA of Cap. Bank o/p 1E-02. Isolated @3 Broken LA of Cap. Bank o/p 1E-02. 10:48 Blocked and close Recloser 2D-44, OK then released the block. Cause: Lightning Arrestor. |  | 1 | 15:34 | Afternoon | Friday | 2017 | 5
7388 | 2017-05-12 15:56 | 2017-05-12 15:56 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 15:56 Manually Open Recloser 26 AK 02 d/s Menggala fdr #2 (transfer to Ketigul fdr #2). Installed 300Kva TX for New well at UBI #40. 15:56 Manually Open Recloser 26 AK 02. 16:27 Closed Recloser 26 AK 02. Cause: Construction job (Project). |  | 1 | 15:56 | Afternoon | Friday | 2017 | 5
7389 | 2017-05-12 16:36 | 2017-05-12 16:36 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified (Fuse) | 56 | 16:39 It was reported b/o fuse o/p 11 h5 20. Not checked yet. |  | 1 | 16:36 | Afternoon | Friday | 2017 | 5
7390 | 2017-05-12 16:36 | 2017-07-12 16:36 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified (Fuse) | 56 | Checked and found @1, @2 b/o fuse for 112.5Kva TX o/p 11-H5-20. Replaced the b/o fuse above with same size, then energized the TX, OK. Cause: Unidentified (fuse). |  | 1 | 16:36 | Afternoon | Friday | 2017 | 5
7391 | 2017-06-12 06:55 | 2017-06-12 06:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr#1 Load dropped 41A (126-85A). Not checked yet |  | 1 | 6:55 | Morning | Monday | 2017 | 6
7392 | 2017-06-12 06:55 | 2017-10-12 06:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Central Duri ACB #11 fdr #1 T/R 2x ctr: 262-264 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:55 | Morning | Monday | 2017 | 6
7393 | 2017-06-12 08:04 | 2017-06-12 08:04 | 13.8KV LIBO FEEDER #2 | Fair | Animal | 35 | 08:04 Lbo 13.8KV OCB fdr #2 T/R 1X. Libo fdr #1 load dropped 31A (67-36A). 08:08 Libo 13.8KV OCB fdr #2 T/R again. 16:00 Lbo 13.8KV OCB fdr #2 T/R AGAIN. Libo fdr #1 load dropped 22A (67-45A). Checked & found, Libo OCB fdr #2 T/R 5x ctr: 471-476 R/F: 50N Patrolled the line & found, an animal (Dead Monkey) on Pole KW 98B. 17:20 Manually Opened Libo OCB fdr #2 for removing the animal. 17:30 Closed Libo OCB fdr #2. Cause: Animal (Monkey). See PIDOD on 06 Dec at 17:20. |  | 1 | 8:04 | Morning | Monday | 2017 | 6
7394 | 2017-06-12 08:30 | 2017-06-12 08:30 | 13.8KV 4D FEEDER #5 | Fair | Pin Insulator | 35 | 08:30 4D 13.8 KV fdr #5 T/R 2X 4D 13.8 KV fdr #3 load dropped 8A ( 70-62A ) Not checked yet. |  | 1 | 8:30 | Morning | Monday | 2017 | 6
7395 | 2017-06-12 08:30 | 2017-07-12 08:30 | 13.8KV 4D FEEDER #5 | Fair | Pin Insulator | 35 | Checked & found, 4D OCB fdr #5 T/R 1x ctr: 308-309 R/F: 50 @2. Patrolled the line & found, @2 broken Pin Insulator on Pole 4D-102. Cause: Pin Insulator. |  | 1 | 8:30 | Morning | Monday | 2017 | 6
7396 | 2017-06-12 08:30 | 2017-06-12 08:30 | 13.8KV 4D FEEDER #4 | Fair | Unidentified | 0 | 08:30 4D 13.8 KV fdr #4 load dropped 132A ( 233-101A ) Not checked yet. |  | 1 | 8:30 | Morning | Monday | 2017 | 6
7397 | 2017-06-12 08:30 | 19/12/2017 08:30 | 13.8KV 4D FEEDER #4 | Fair | Unidentified | 0 | Checked and found 4D fdr #4 load dropped. Patrolled the line but no found Recloser opearated. Cause: Unidentifed. |  | 1 | 8:30 | Morning | Monday | 2017 | 6
7398 | 2017-06-12 09:45 | 2017-06-12 09:45 | 13.8KV PETANI FEEDER #2 | Fair | Construction Job | 0 | 09:45 Manual opened 13.8 KV Petani fdr #2. Repaired pipe line leak at Pematang . 18:01 Closed Petani 13.8 KV fdr #2. Cause: Planned Construction |  | 1 | 9:45 | Morning | Monday | 2017 | 6
7399 | 2017-06-12 09:57 | 2017-06-12 09:57 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 141 | 09:57 Manually Open Minas 13.8KV OCB fdr #2. Repaired Hot Spot of Recloser 7D-81. 11:58 Closed Minas 13.8KV OCB fdr #2. Plan Maintenance. |  | 1 | 9:57 | Morning | Monday | 2017 | 6
7400 | 2017-06-12 10:10 | 2017-06-12 10:10 | 13.8KV NORTH DURI FEEDER #9 | Fair | Construction Job | 0 | 10:10 Manually Open Recloser 11 J2 05 d/s N. Duri fdr #9. Replaced 112.5Kva TX to 150Kva TX o/p 11 H7 18. 14:45 Closed Recloser 11 J2 05 d/s N. Duri fdr #9. Cause: Planned Construction (Project) |  | 1 | 10:10 | Morning | Monday | 2017 | 6
7401 | 2017-06-12 15:11 | 2017-06-12 15:11 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Lightning | 76 | Old Kota Batak 13.8KV OCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 15:11 | Afternoon | Monday | 2017 | 6
7402 | 2017-06-12 15:11 | 2017-07-12 15:11 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Lightning | 76 | Checked & found, Kotabatak OCB fdr #2 T/R ctr: 1304-1305 R/F: 51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 15:11 | Afternoon | Monday | 2017 | 6
7403 | 2017-06-12 17:20 | 2017-06-12 17:20 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 36 | 17:20 Manually Open Libo 13.8KV OCB fdr #2. Removed Animal (Monkey) at power line o/p KW 38B. 17:30 Closed Libo 13.8KV OCB fdr #2. Cause: Planned Maintenance. See PIDOD on 6 Dec at 08:04 |  | 1 | 17:20 | Afternoon | Monday | 2017 | 6
7404 | 2017-06-12 18:34 | 2017-06-12 18:34 | 13.8KV DARLING VCB FEEDER #3 | Cloudy | Unidentified | 0 | 18:34 Darling 13.8KV VCB fdr #3 T/SO (On block). 18:38 Blocked and closed Darling fdr #3, OK then released the block. Not checked yet. |  | 1 | 18:34 | Afternoon | Monday | 2017 | 6
7405 | 2017-06-12 18:34 | 2017-10-12 18:34 | 13.8KV DARLING VCB FEEDER #3 | Cloudy | Unidentified | 0 | Checked & found, Darling VCB fdr #3 T/SO ctr: 247-248 R/F: 51 @3. Patrolled the line but found nothing. Cause: Unidentified |  | 1 | 18:34 | Afternoon | Monday | 2017 | 6
7406 | 2017-07-12 09:52 | 2017-07-12 09:52 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 527 | 09:52 Manually Open S. Bekasap 13.8KV OCB fdr #1. Repair Hot Spot and replaced Recloser o/p 36-BI-04, Replaced FCO at well Pudu #03. 15:19 Manually Closed back S.Bekasap OCB fdr#1 after finished the Jobs Cause: Planned Maintenance. | 1234 | 1 | 9:52 | Morning | Wednesday | 2017 | 7
7407 | 2017-07-12 11:20 | 2017-07-12 11:20 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse o/p 10-K2A-08. (d/s N.Duri fdr#8) Not checked yet. |  | 1 | 11:20 | Morning | Wednesday | 2017 | 7
7408 | 2017-07-12 11:20 | 2017-08-12 10:00 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified (Fuse) | 0 | 10:00 Checked and found @1 b/o fuse for TX 112.5 Kv o/p 10 K2A 08. Replaced @1 b/o fuse for above with same size then energize the TX. OK. Cause: Unidentified. |  | 1 | 11:20 | Morning | Wednesday | 2017 | 7
7409 | 2017-07-12 11:50 | 2017-07-12 11:50 | 13.8KV PUNGUT FEEDER #2 | Fair | Low mega-ohm reading | 0 | It was reported b/o fuse at well Intan #8 (d/s Pungut #2). Not checked yet. |  | 1 | 11:50 | Morning | Wednesday | 2017 | 7
7410 | 2017-08-12 09:26 | 2017-08-12 09:26 | 13.8KV BATANG FEEDER #3 | Fair | Planned Maintenance | 240 | 09:36 Manually Open Batang 13.8KV OCB fdr #3. Manually Open Batang 13.8KV OCB fdr #1. Replaced LBS o/p 39 AL 01. Replaced 206Kva TX to 300Kva TX at well CANDI #03. 11:51 Manually blocked and Close Batang 13.8KV OCB fdr #3, then release the block Manually blocked and Close Batang 13.8KV OCB fdr #1, then release the block Plan Maintenance. |  | 1 | 9:26 | Morning | Saturday | 2017 | 8
7411 | 2017-08-12 10:00 | 2017-08-12 10:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 17 | 10:20 Checked and found @1 b/o fuse for TX 112.5 Kv o/p 08 27 28. Replaced @1 b/o fuse for above with same size then energize the TX. OK. Cause: Unidentified. |  | 1 | 10:00 | Morning | Saturday | 2017 | 8
7412 | 2017-08-12 11:29 | 2017-08-12 11:29 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Unidentified | 0 | 11:29 Batang 13.8KV OCB fdr #2 T/R. Not checked yet. |  | 1 | 11:29 | Morning | Saturday | 2017 | 8
7413 | 2017-08-12 11:29 | 19/12/2017 08:29 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found Batang fdr #2 T/R 1x Ctr: 152-153 R/F: 51N. Patrolled the line but found nothing. cause: Unidentified. |  | 1 | 11:29 | Morning | Saturday | 2017 | 8
7414 | 2017-08-12 14:20 | 2017-08-12 14:20 | MINAS POWER PLANT |  |  | - | 14:20 S/U MGT #1 and online at 14:35 to restore load. Due to MGT #8 will be Transfer fuel test to Distillate. 16:55 S/D MGT #1 FOR Standby. |  | 1 | 14:20 | Afternoon | Saturday | 2017 | 8
7415 | 2017-08-12 16:20 | 2017-08-12 16:20 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified (Fuse) | 156 | 16:20 It was reported b/o fuse o/p 10-k4-17 d/s N.duri fdr #8. 17:20 Checked and found @1 b/o fuse for 112.5Kva TX o/p 10-K2A-08. Replaced the b/o fuse above with same size, then energized the TX, OK. Cause: Unidentified (fuse). Not checked yet. |  | 1 | 16:20 | Afternoon | Saturday | 2017 | 8
7416 | 2017-09-12 09:42 | 2017-09-12 09:42 | 13.8KV 8D FEEDER #11 | Fair | Planned Maintenance | 19 | 09:36 Manualiy opened Recl 9E-02 (d/s 8D fdr#11) to replace 500Kva to 150KvaTx, at Well 9E-53. 10:35 Manually back and Closed Recl 9E-02, then energized the Tx. Cause : Planned maintenance. |  | 1 | 9:42 | Morning | Tuesday | 2017 | 9
7417 | 2017-09-12 10:11 | 2017-09-12 10:11 | 13.8KV DURI FIELD FEEDER #2 | Fair | Planned Maintenance | 7 | 10:11 Manually opened Recl 07-U5-32 (d/s D.field fdr#2) to repaired @2 broken jumper, the Recloser above 10:34 Manually closed back the Recloser, after finished the job. Cause : Planned maintenance. |  | 1 | 10:11 | Morning | Tuesday | 2017 | 9
7418 | 2017-09-12 12:16 | 2017-09-12 12:16 | 44KV NORTH DURI - DUMAI LINE | Fair | Unidentified | 0 | N.Duri 44Kv GCB#1 T/r. Not checked yet. |  | 1 | 12:16 | Afternoon | Tuesday | 2017 | 9
7419 | 2017-09-12 12:16 | 2017-10-12 12:16 | 44KV NORTH DURI - DUMAI LINE | Fair | Unidentified | 0 | Checked & found, 44KV North Duri GCB #44 T/R 1x ctr: 120-121 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 12:16 | Afternoon | Tuesday | 2017 | 9
7420 | 2017-09-12 13:38 | 2017-09-12 13:38 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Rain and Lightning | Lightning | 0 | 13:38 Dumai 4160 Kv VCB fdr # 1 T/LO Checked & found, 4.16KV Dumai ACB #12 fdr #1 T/LO ctr: 279-280 R/F: 51 @2, @3. Patrolled the line but found nothing. 14:54 Blocked and closed Dumai 4160Kv Vcb fdr#1. Cause : Suspected by Lightning. |  | 1 | 13:38 | Afternoon | Tuesday | 2017 | 9
7421 | 2017-09-12 13:49 | 2017-09-12 13:49 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Lightning | Lightning | 0 | 13:49 Dumai 4160 Kv VCB #FDR #4 T/R 1X. Checked and found no thing , relay flag @A,@B Counter:269-270. Cause:Lightning. |  | 1 | 13:49 | Afternoon | Tuesday | 2017 | 9
7422 | 2017-09-12 13:49 | 2017-10-12 13:49 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Lightning | Lightning | 0 | Checked & found, 4.16KV Dumai ACB #22 fdr #4 T/R 1x ctr: 269-270 Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 13:49 | Afternoon | Tuesday | 2017 | 9
7423 | 2017-09-12 15:13 | 2017-09-12 15:13 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Lightning | 0 | 15:13 Duri Community 13.8 Kv ACB fdr #3 T/R 1X. Not Checked yet. |  | 1 | 15:13 | Afternoon | Tuesday | 2017 | 9
7424 | 2017-09-12 15:13 | 2017-12-12 08:00 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found Duri Community fdr #3 T/R 1x Ctr: 65-66 R/F: 51N Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 15:13 | Afternoon | Tuesday | 2017 | 9
7425 | 2017-09-12 15:28 | 2017-09-12 15:28 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Lightning | 0 | 15:28 Duri Community 13.8 Kv ACB fdr #1 T/R 1X. Not Checked yet. |  | 1 | 15:28 | Afternoon | Tuesday | 2017 | 9
7426 | 2017-09-12 15:28 | 2017-12-12 08:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked and found Duri Community fdr #3 T/R 1x Ctr: 110-111 R/F: 51N Patrolled the line and found @1 Pin Insulator broken o/p 1-KT-35, @1 Deadend Insulator broken o/p 3D-E4. Cause: Lightning. |  | 1 | 15:28 | Afternoon | Tuesday | 2017 | 9
7427 | 2017-09-12 17:00 | 2017-09-12 17:00 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 31 | It was reported b/o fuse o/p 03-07-11 d/s CD Fdr #7. Cause : Not Checked yet. |  | 1 | 17:00 | Afternoon | Tuesday | 2017 | 9
7428 | 2017-09-12 17:00 | 2017-10-12 10:35 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 31 | Checked and found @3 b/o fuse for 112.5Kva TX o/p 03-07-11. Replaced b/o fuse above with same size, then energized the TX, OK. Cause: Animal (Monkey). |  | 1 | 17:00 | Afternoon | Tuesday | 2017 | 9
7429 | 2017-10-12 08:23 | 2017-10-12 08:23 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified (Fuse) | 0 | 08:23 It was reported b/o fuses o/p 03-06=25A (d/s CDuri fdr#5) 10:20 Checked and found @1, @2 b/o fuse for 112.5Kva TX. Replaced b/o fuse with same size, then energized the TX. OK. Cause: Unidentified (fuse). |  | 1 | 8:23 | Morning | Thursday | 2017 | 10
7430 | 2017-10-12 14:30 | 2017-10-12 14:30 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Broken Fuse Cut Out | 0 | 14:30 It was reported Hot Spot o/p 04-05 27A (d/s C.Duri fdr#8) 15:10 Checked and found @2 broken FCO o/p 04-05 27A. Cause: Broken FCO. |  | 1 | 14:30 | Afternoon | Thursday | 2017 | 10
7431 | 2017-10-12 14:30 | 2017-11-12 14:37 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Broken Fuse Cut Out | 0 | 14:37 Blocked Recloser 04-05-32, ---->released block at 15:50. Replaced all broken FCO o/p 04-0527A. Cause: Fuse Cut Out (broken). |  | 1 | 14:30 | Afternoon | Thursday | 2017 | 10
7432 | 2017-10-12 18:01 | 2017-10-12 18:01 | 13.8KV BATANG FEEDER #2 | Fair | Dead End Insulator | 0 | 18:01 & 19:33 Batang 13.8KV OCB fdr #2 T/R 1x. Batang GFPC T/R 1X. Not checked yet. |  | 1 | 18:01 | Afternoon | Thursday | 2017 | 10
7433 | 2017-10-12 18:01 | 19/12/2017 08:01 | 13.8KV BATANG FEEDER #2 | Fair | Dead End Insulator | 0 | Checked and found Batang fdr #2 T/R 2x Ctr: 153-155 R/F: @2 51N. Patrolled the line and found broken Dead End Insulator near STG #04. Cause: Dead End Insulator. |  | 1 | 18:01 | Afternoon | Thursday | 2017 | 10
7434 | 2017-10-12 18:42 | 2017-10-12 18:42 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 99 | Bangko 13.8KV OCB fdr#4 T/O, Ctr: 21-22, R/F: 51 @b@c In Block status, due to Rig job. Bangko fdr#2 load dropped 122A (250-118A). Bangko fdr#1 load dropped 114A (190-76A). Not patrolled yet. |  | 1 | 18:42 | Afternoon | Thursday | 2017 | 10
7435 | 2017-10-12 18:42 | 2017-11-12 18:42 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 99 | Checked & found Bangko OCB fdr#4 TO, Cttr: 21-22, R/F: 51N, 51 @b@c Patrolled the Line, found nothing. Cause : Lightning |  | 1 | 18:42 | Afternoon | Thursday | 2017 | 10
7436 | 2017-10-12 20:14 | 2017-10-12 20:14 | 13.8KV NELLA FEEDER #1 | Lightning | Construction Job | 0 | 20:14 Manual Opened Nella OCB fdr#1. To Maintain tank level at Bangko GS. 22:53 Manual Closed Nella OCB fdr#1. Cause: Maintain tank level. |  | 1 | 20:14 | Night | Thursday | 2017 | 10
7437 | 2017-10-12 22:47 | 2017-10-12 22:47 | 13.8KV NELLA FEEDER #2 | Lightning | Construction Job | 0 | 22:47 Manual Opened Nella OCB fdr#2. To Maintain tank level at Bangko GS. 22:53 Manual Closed Nella OCB fdr#2. Cause: Maintain tank level. |  | 1 | 22:47 | Night | Thursday | 2017 | 10
7438 | 2017-11-12 23:59 | 2017-11-12 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | CPI Power system Normal Operation |  | 1 | 23:59 | Night | Sunday | 2017 | 11
7439 | 2017-12-12 10:00 | 2017-12-12 10:00 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 122 | It was reported B/O fose o/p 04-8-24 (C.Duri fdr#6). Not checked yet. |  | 1 | 10:00 | Morning | Tuesday | 2017 | 12
7440 | 2017-12-12 10:00 | 14/12/2017 15:44 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 122 | 15:44 Checked and found @1 b/o fuse for 12.5 Kva on pole 04-08-24. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (fuse). |  | 1 | 10:00 | Morning | Tuesday | 2017 | 12
7441 | 2017-12-12 10:15 | 2017-12-12 10:15 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 125 | 10:15 Manualy opened Bangko VCB fdr#4. Replaced B/O 150Kva Tx with the same size at well Bangko#179, 11:00 Blocked & closed Bangko VCB fdr#4, then release the block. Cause: Plant maintenance. |  | 1 | 10:15 | Morning | Tuesday | 2017 | 12
7442 | 2017-12-12 10:20 | 2017-12-12 10:20 | 13.8KV RANGAU FEEDER #2 | Fair | Lightning | 29 | Rangau fdr#2 Load dropped 95A (113-18A). Not checked yet. |  | 1 | 10:20 | Morning | Tuesday | 2017 | 12
7443 | 2017-12-12 10:20 | 19/12/2017 10:20 | 13.8KV RANGAU FEEDER #2 | Fair | Lightning | 29 | Checked & found, Recl 23-BD-01 T/R 3x, Ctr: 311-314, R:F None. Patrolled the Line, but found nothing. Cause : Lightning |  | 1 | 10:20 | Morning | Tuesday | 2017 | 12
7444 | 2017-12-13 07:11 | 2017-12-13 07:11 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | C.Duri ACB #22 (feeder #5) T/R 1x. Not checked yet. |  | 1 | 7:11 | Morning | Wednesday | 2017 | 12
7445 | 2017-12-13 07:11 | 2017-12-18 07:11 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | Check and found C. Duri #5 T/R 1x Ctr: 257-258 R/F: @3 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:11 | Morning | Wednesday | 2017 | 12
7446 | 2017-12-13 07:11 | 2017-12-13 07:11 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | C.Duri ACB #33 (feeder #7) T/R 1x. Not checked yet. |  | 1 | 7:11 | Morning | Wednesday | 2017 | 12
7447 | 2017-12-13 07:11 | 2017-12-18 08:00 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | Checked and found C. Duri fdr #7 T/R 1x Ctr: 519-520 R/F: @3 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:11 | Morning | Wednesday | 2017 | 12
7448 | 2017-12-14 03:04 | 2017-12-14 03:04 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Dead End Insulator | 974 | 03:04 C.Duri 13.8 Kv ACB fdr #11 Load dropped 51A (122-71A ) 03:11 It was reported Explosive sound beside Gate #127 Puncak. 04:30 Checked and found Recloser 39-AV-36 T/LO R/F: 51@3 Counter: 240-244. Patrolled the line and found @1 broken Dead end, and conductor o/p NN ( beside Gate #127 Puncak ). Open visual opening and unplug Recloser 39-AV-36. 08:51 Blocked C. Duri fdr #1. Replaced @1 broken dead end insulator on pole 39-AV-08. 11:05 Blocked and closed Recloser 39-AV-36 and then released the block. Cause: Broken Dead end insulator. | 123 | 1 | 3:04 | Night | Thursday | 2017 | 12
7449 | 2017-12-14 06:10 | 2017-12-14 06:10 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | 06:10 Batang 13.8Kv GFPC T/R 1X. 13:15 Checked & found @1 B/O fuse for 150Kva Tx at well RB#52 (Batang fdr#2) Replaced @1 B/O fuse for 150Kva Tx with the same size. Cause: Animal (Monkey). |  | 1 | 6:10 | Morning | Thursday | 2017 | 12
7450 | 2017-12-14 08:25 | 2017-12-14 08:25 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Animal | 0 | 08:25 It was reported b/o fuse for Tx at Krakatau complex no #283. 09:58 Checked and found @2 b/o fuse for 75 Kva Tx on pole KT #35. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (Squirrel). |  | 1 | 8:25 | Morning | Thursday | 2017 | 12
7451 | 2017-12-14 09:19 | 2017-12-14 09:19 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Secondary Cable | 182 | 09:19 It was reported broken secondary cable from Tx on pole 03-06-06. Not checked yet. |  | 1 | 9:19 | Morning | Thursday | 2017 | 12
7452 | 2017-12-14 09:19 | 2017-12-17 15:04 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Secondary Cable | 182 | Replaced broken secondary cable on pole 03-06-06 D/S C Duri fdr #5, and then energized the Tx. Cause: Secondary cable. |  | 1 | 9:19 | Morning | Thursday | 2017 | 12
7453 | 2017-12-14 10:38 | 2017-12-14 10:38 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 78 | 10:38 Manually opened Recloser 28-AF-02 D/S Sintong fdr #2 due to : Replaced 100 Kva Tx with 150 Kva Tx at well Benar #05. 11:05 Blocked and closed Recloser 28-AF-02 and then released the block. Cause: Plan Maintenance. |  | 1 | 10:38 | Morning | Thursday | 2017 | 12
7454 | 2017-12-14 12:01 | 2017-12-14 12:01 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 29 | 12:01 Manually opened Recloser 23-BD-01 D/S Rangau fdr #2 due to: Replaced b/o fuse for 150 Kva at well Jurong #13. 12:18 Blocked and closed Recloser Recloser 23-BD-01 and then released the block. Cause: Plan Maintenance. |  | 1 | 12:01 | Afternoon | Thursday | 2017 | 12
7455 | 2017-12-14 22:25 | 2017-12-14 22:25 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 205 | It was reported b/o fuse on pole 13-H11-10 D/S N Duri fdr #2. Not checked yet. |  | 1 | 22:25 | Night | Thursday | 2017 | 12
7456 | 2017-12-14 22:25 | 2017-12-16 09:45 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 205 | 09:45 Manually opened Recloser: 13-H11-08 D/S N Duri fdr #2. due to replaced b/o fuse for 112.5 Kva Tx on pole 13-H11-10. 09:47 Manually blocked and closed Recloser: 13-H11-08 and then released the block. Cause: Plan Maintenance / Unidentified (fuse). |  | 1 | 22:25 | Night | Thursday | 2017 | 12
7457 | 2017-12-15 08:44 | 2017-12-15 08:44 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Recloser - Control Recloser | 71 | 08:44 So Bekasap fdr #1 Load dropped 98A (123-25A). 09:20 Checked and found Recloser 36-BE-04 T/O Counter: 832-1357 (524x). 09:25 Blocked and closed Recloser 36-BE-04 and then released the block. Cause: Control Recloser. |  | 1 | 8:44 | Morning | Friday | 2017 | 12
7458 | 2017-12-15 10:15 | 2017-12-15 10:15 | 13.8KV BEKASAP FEEDER #3 | Fair | Planned Maintenance | 6 | 10:15 Manually opened Recloser:1-TL-06 D/S Bekasap fdr #3 due to: 1. Isolate line toward well Bekasap #72 by opened HLC on pole: 37-BE-58 (Cancel) 2. Adjust voltage at well Bekasap #183. Tx: 150 Kva R/M: 120 HP Sec Voltage: 960 V 11:05 Manually blocked and closed Recloser:1-TL-06 --> OK and then released the block. Cause: Construction Job. |  | 1 | 10:15 | Morning | Friday | 2017 | 12
7459 | 2017-12-15 11:00 | 2017-12-15 11:00 | 230KV NORTH DURI SWITCH YARD | Fair | Under investigation | 0 | N.Duri 230 KV GCB#15 T/O Closed at 14:10 Ctr:146. N.Duri 230 KV GCB#25 T/O Closed at 14:40 Ctr:204. N.Duri 230 KV GCB#43 T/O Closed at 14:10 Ctr:197. R/F 86 Bus 1 50BF @1@2@3. Cause: Under Investigasi. No load dropped. |  | 1 | 11:00 | Morning | Friday | 2017 | 12
7460 | 2017-12-15 16:06 | 2017-12-15 16:06 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Lightning | 66 | Ketigul VCB fdr#2 T/R 1X. Not checked yet. |  | 1 | 16:06 | Afternoon | Friday | 2017 | 12
7461 | 2017-12-15 16:06 | 2017-12-19 16:06 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Lightning | 66 | Checked & found Ketigul VCB fdr#2 T/R, 2x, Ctr: 255-257, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 16:06 | Afternoon | Friday | 2017 | 12
7462 | 2017-12-15 16:09 | 2017-12-15 16:09 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 99 | It was reported B/O fuse on pole 13-H4-03 D/S N.Duri#2. Not checked yet. |  | 1 | 16:09 | Afternoon | Friday | 2017 | 12
7463 | 2017-12-15 16:09 | 2017-12-16 10:10 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 99 | Checked and found @1 b/o fuse for 112.5 Kva Tx on pole 13-H4-03. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (fuse). |  | 1 | 16:09 | Afternoon | Friday | 2017 | 12
7464 | 2017-12-15 16:41 | 2017-12-15 16:41 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse on pole 07-V3-05 D/S DF fdr#2. Not checked yet. |  | 1 | 16:41 | Afternoon | Friday | 2017 | 12
7465 | 2017-12-15 16:41 | 2017-12-16 15:05 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | Checked & found @2@3 B/O fuse for 112.5Kva Tx. Replaced @2@3 B/O fuse above with the same size and energized the Tx. Cause: Unidentified Fuse. |  | 1 | 16:41 | Afternoon | Friday | 2017 | 12
7466 | 2017-12-15 17:00 | 2017-12-15 17:00 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse on pole 12-E3-20 D/S ND fdr#1. Not checked yet. |  | 1 | 17:00 | Afternoon | Friday | 2017 | 12
7467 | 2017-12-15 17:00 | 2017-12-16 09:53 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked and found @1 b/o fuse for 112.5 Kva Tx on pole 12-E3-20. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (fuse). |  | 1 | 17:00 | Afternoon | Friday | 2017 | 12
7468 | 2017-12-16 09:40 | 2017-12-16 09:40 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Planned Maintenance | 0 | 09:40 Manually opened LBS 1F-27-3 at Talang D/S D.Comm. fdr#3. Repaired broken static wire o/p 2DG-09 near Talang#31. 10:12 Closed LBS 1F-27-3 at Talang. Cause: Plant maintenance. |  | 1 | 9:40 | Morning | Saturday | 2017 | 12
7469 | 2017-12-16 10:00 | 2017-12-16 10:00 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 11 | It was reported B/O fuse o/p 05-N3-17 (C.Duri fdr#14). Not checked yet. |  | 1 | 10:00 | Morning | Saturday | 2017 | 12
7470 | 2017-12-16 10:00 | 2017-12-18 10:00 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 11 | Checked & found, @1 b/o fuse for 112.5KVA TX on Pole 05-N3-17. Replaced b/o Fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 10:00 | Morning | Saturday | 2017 | 12
7471 | 2017-12-16 10:35 | 2017-12-16 10:35 | 13.8KV DURI FIELD FEEDER #2 | Fair | Secondary Cable | 0 | 10:35 It was reported broken secondary on pole 06-S1-13 (D.Field fdr#2). 17:10 Replaced broken secondary cable on pole 06-S1-13. Cause: Broken secondary. |  | 1 | 10:35 | Morning | Saturday | 2017 | 12
7472 | 2017-12-16 14:58 | 2017-12-16 14:58 | 13.8KV PUNGUT FEEDER #2 | Heavy Rain | Unidentified | 18 | 14:58 Pungut fdr #2 Load dropped 11A (60-49A). 18:00 Checked and found Recloser: 44-BX-06 T/SO Counter: 363-364 R/F:51N. Blocked and closed Recloser: 44-BX-06 --> Ok and then released the block. Cause: Not patrolled yet. |  | 1 | 14:58 | Afternoon | Saturday | 2017 | 12
7473 | 2017-12-16 14:58 | 2017-12-17 16:58 | 13.8KV PUNGUT FEEDER #2 | Heavy Rain | Unidentified | 18 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 14:58 | Afternoon | Saturday | 2017 | 12
7474 | 2017-12-17 01:15 | 2017-12-17 01:15 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified | 0 | N. Duri 13.8KV VCB fdr #8 T/R 1X. Not checked yet. |  | 1 | 1:15 | Night | Sunday | 2017 | 12
7475 | 2017-12-17 01:15 | 2017-12-19 08:00 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified | 0 | Checked and found N. Duri fdr #8 T/R 1x Ctr: 84-85 R/F: @1 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 1:15 | Night | Sunday | 2017 | 12
7476 | 2017-12-17 09:40 | 2017-12-17 09:40 | 13.8KV 8D FEEDER #1 | Fair | Planned Maintenance | 64 | 09:40 Manually opened 8D OCB fdr #1 due to : Replaced 550 Kva Tx with 300 Kva Tx at well 8E-13. Tx: 300 Kva R/M: 160 HP Sec Voltage: 1060 Volt. 10:20 Manually blocked and closed 8D OCB fdr #1 --> OK and then released the block. Cause: Plan maintenance. |  | 1 | 9:40 | Morning | Sunday | 2017 | 12
7477 | 2017-12-17 10:05 | 2017-12-17 10:05 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Planned Maintenance | 0 | 10:05 Manually opened LBS: SD-01 D/S D Community fdr #1. 10:13 Manually opened LBS: 2DF-08 D/S D Community fdr #3. Due to replaced broken LBS:3DE-24. 11:38 Manually closed LBS: SD-01 D/S D Community fdr #1. 11:47 Manually closed LBS: 2DF-08 D/S D Community fdr #3. Cause: Plan maintenance. |  | 1 | 10:05 | Morning | Sunday | 2017 | 12
7478 | 2017-12-17 11:09 | 2017-12-17 11:09 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 10 | 11:09 It was reported b/o fuse on pole 01-03-06 D/S C.Duri fdr #6. 13:50 Checked & found @3 b/o fuse for 112.5 Kva Tx o/p 01-3-06. Replaced @3 B/O fuse above with the same size & energized the Tx. Cause: Unidentified Fuse. |  | 1 | 11:09 | Morning | Sunday | 2017 | 12
7479 | 2017-12-17 11:54 | 2017-12-17 11:54 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 0 | 11:54 Manually opened Recloser 9D-25 D/S 8C fdr #1 due to : Replaced 550 Kva Tx with 300 Kva Tx at well 9E-91. Tx: 300 Kva R/M: 120 HP Sec Voltage: 960 Volt. 12:20 Manually blocked and closed Recloser 9D-25 --> OK and then released the block. Cause: Plan maintenance. |  | 1 | 11:54 | Morning | Sunday | 2017 | 12
7480 | 2017-12-18 10:43 | 2017-12-18 10:43 | 13.8KV DARLING VCB FEEDER #6 | Fair | Unidentified | 0 | 10:43 Darling ACB fdr #6 T/O. Darling GFPC Tx #2 T/O. 10:54 Checked and found Darling ACB fdr #6 T/O Ctr: Do not change R/F: Not appear. Darling GFPC Tx-2 T/O Ctr:161-162. 10:55 Blocked & closed Darling GFPC Tx-2. then release the block. Blocked and closed Darling ACB fdr #6, then released the block. Cause: Not patrolled yet. |  | 1 | 10:43 | Morning | Monday | 2017 | 12
7481 | 2017-12-18 10:43 | 2017-12-19 08:00 | 13.8KV DARLING VCB FEEDER #6 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:43 | Morning | Monday | 2017 | 12
7482 | 2017-12-18 13:50 | 2017-12-18 13:50 | MINAS POWER PLANT |  |  | - | 13:50 S/U MGT #1 and then On line the unit at 14:20. |  | 1 | 13:50 | Afternoon | Monday | 2017 | 12
7483 | 2017-12-18 13:50 | 2017-12-18 13:50 | MINAS POWER PLANT |  |  | - | 13:50 S/U MGT #1 and then On line the unit at 14:20. |  | 1 | 13:50 | Afternoon | Monday | 2017 | 12
7484 | 2017-12-18 14:27 | 2017-12-18 14:27 | MINAS POWER PLANT |  |  | - | 14:27 S/U MGT #3 and then On line the unit at 14:50. |  | 1 | 14:27 | Afternoon | Monday | 2017 | 12
7485 | 2017-12-18 15:05 | 2017-12-18 15:05 | MINAS POWER PLANT |  |  | - | 15:05 S/U MGT #2 and then On line the unit at 15:25. |  | 1 | 15:05 | Afternoon | Monday | 2017 | 12
7486 | 2017-12-18 17:00 | 2017-12-18 17:00 | CENTRAL DURI POWER PLANT |  |  | - | 17:00 S/U CGT#5, then on line the unit at 17:30. |  | 1 | 17:00 | Afternoon | Monday | 2017 | 12
7487 | 2017-12-18 22:32 | 2017-12-18 22:32 | NORTH DURI POWER PLANT |  |  | - | NDC #1 offline and S/D the unit. |  | 1 | 22:32 | Night | Monday | 2017 | 12
7488 | 2017-12-19 07:14 | 2017-12-19 07:14 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 45 | 07:14 Sintong fdr#2 T/R 1x. Sintong GFPC T/R 1x. 16:45 Checked & found Sintong VCB fdr#2 T/R 1x Ctr:467-468 R/F:51N. Sintong GFPC T/R 1x Ctr:1014-1915. Patrolled the line but found noting. Cause : Unidentified. |  | 1 | 7:14 | Morning | Tuesday | 2017 | 12
7489 | 2017-12-19 09:10 | 2017-12-19 09:10 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Dead End Insulator | 0 | Duri Community Fdr# 1 T/r 1x. Not checked yet. |  | 1 | 9:10 | Morning | Tuesday | 2017 | 12
7490 | 2017-12-19 09:10 | 2017-12-20 09:10 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Dead End Insulator | 0 | Checked & found, D.Comm ACB fdr#1 T/R 1x, Ctr: 111-112, R/F: 51N Patrolled the Line, found @2 Broken Dead end Insulator o/p 1-KT-35 Cause : Dead End Insulator |  | 1 | 9:10 | Morning | Tuesday | 2017 | 12
7491 | 2017-12-19 09:42 | 2017-12-19 09:42 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 0 | C Duri Fdr#8 T/R 1x. Not checked yet. |  | 1 | 9:42 | Morning | Tuesday | 2017 | 12
7492 | 2017-12-19 09:42 | 2017-12-30 14:42 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 0 | Checked & found C.Duri ACB fdr#8 T/R 1x Ctr:393-394 R/F:51. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 9:42 | Morning | Tuesday | 2017 | 12
7493 | 2017-12-19 11:30 | 2017-12-19 11:30 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 40 | 11:30 Manually open LBS 32 AK 02B D/S KETIGUL Fdr#1 Replaced broken Recl.32 AK 04 Dismantle 150 KVA TX At Well KELOK #9. Dismantle 150 KVA TX At Well KELOK #8. 13:22 Closed LBS 32 AK 02B Cause Plan Maintenance. |  | 1 | 11:30 | Morning | Tuesday | 2017 | 12
7494 | 2017-12-19 14:19 | 2017-12-19 14:19 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 0 | 14:19 Darling Fdr #3 T/O on block position. 14:22 Blocked and closed Darling fdr#3 then release the blocked. 16:50 Checked & found Darling VCB fdr#3 T/O (block position) Ctr:247-248 R/F:51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:19 | Afternoon | Tuesday | 2017 | 12
7495 | 2017-12-19 16:42 | 2017-12-19 16:42 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Unidentified | 0 | Menggala fdr#1 Load dropped 72A (168-96A). Not checked yet. |  | 1 | 16:42 | Afternoon | Tuesday | 2017 | 12
7496 | 2017-12-19 16:42 | 2017-12-21 16:42 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Unidentified | 0 | Checked & found, Recloser 19-AO-01 T/R 1x ctr: 482-483. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:42 | Afternoon | Tuesday | 2017 | 12
7497 | 2017-12-20 02:03 | 2017-12-20 02:03 | 13.8KV DARLING VCB FEEDER #3 | Rain and Lightning | Lightning | 0 | Darling VCB fdr #3 T/R 1x. Darling GFPC Tx #1 T/R 1x. Not checked yet. |  | 1 | 2:03 | Night | Wednesday | 2017 | 12
7498 | 2017-12-20 02:03 | 2017-12-22 02:03 | 13.8KV DARLING VCB FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found, Darling VCB fdr #3 T/R 1x ctr: did not change R/F: 51N. Patrolled the line & found, @1 broken Lightning Arrester on Pole NN Near CGS #5. Cause: Lightning. |  | 1 | 2:03 | Night | Wednesday | 2017 | 12
7499 | 2017-12-20 14:15 | 2017-12-20 14:15 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 14:15 Manually opened Recloser: 26-AK-02 D/S Ketigul fdr #2 due to: Tie in new well UBI #41. 17:20 Manually blocked and closed Recloser: 26-AK-02 --> OK and then released the block. Cause: Construction job (Project). |  | 1 | 14:15 | Afternoon | Wednesday | 2017 | 12
7500 | 2017-12-20 14:30 | 2017-12-20 14:30 | 13.8KV KETIGUL FEEDER#1 | Fair | Construction Job | 0 | 14:30 Manually opened LBS: 32-AJ-01 D/S Ketigul fdr #1 due to: Tie in static wire at well Kelok North East. Cause: Construction job (Project). |  | 1 | 14:30 | Afternoon | Wednesday | 2017 | 12
7501 | 2017-12-21 10:37 | 2017-12-21 10:37 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 26 | 10:37 Man Opened Recloser: 46-BP-12 (d/s Pungut fdr#2) due to: Change out 150 Kva Tx with the same size and energized the Tx at well Intan #08. 12:25 Manually blocked and closed Recloser: 46-BP-12 --> OK and then released the block. Cause: Planned Maintenance. |  | 1 | 10:37 | Morning | Thursday | 2017 | 12
7502 | 2017-12-21 10:43 | 2017-12-21 10:43 | 13.8KV LIBO FEEDER #1 | Fair | Planned Maintenance | 48 | 10:43 Manually opened Libo OCB fdr#1 due to: Adjust Voltage 300 Kva Tx at Well SEL#49. Tx: 300 Kva R/M: 175 Hp Sec volptage: 1100 Volt. 11:40 Manually blocked and closed Libo OCB fdr#1. Cause Planned Maintenance. |  | 1 | 10:43 | Morning | Thursday | 2017 | 12
7503 | 2017-12-21 10:47 | 2017-12-21 10:47 | 13.8KV 6DN FEEDER #6 | Fair | Construction Job | 0 | 10:47 Manually opened 6DN OCB fdr#6 due to: Shut down WIP & WELLS for installing 20" Valve. 14:27 Manually blocked and closed 6DN OCB fdr#6 --> Ok and then released the block. Cause: Construction job (Project). |  | 1 | 10:47 | Morning | Thursday | 2017 | 12
7504 | 2017-12-21 11:35 | 2017-12-21 11:35 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 561 | It was reported b/o Fuse at Well Pagar#40 D/S Ketigul Fdr#2. Not Checked yet. | 123 | 1 | 11:35 | Morning | Thursday | 2017 | 12
7505 | 2017-12-21 11:35 | 2017-12-26 11:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 561 | Checked & found, @1, @2 b/o Fuse for 300KVA Tx at Well Pagar #40. Replaced b/o Fuses above with the same size then energized the Tx. Cause: Unidentified (Fuse). | 123 | 1 | 11:35 | Morning | Thursday | 2017 | 12
7506 | 2017-12-22 05:49 | 2017-12-22 05:49 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 30 | 05:49 Rangau fdr #2 load dropped 99A (115-16A). 14:00 Checked & found Recl 23-BD-01 T/R 1x, Ctr: 314-315, R/F: 51G @2 Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 5:49 | Morning | Friday | 2017 | 12
7507 | 2017-12-22 10:24 | 2017-12-22 10:24 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 79 | 10:24 Manually Opened Pematang OCB fdr#2. to Adjust Voltage at Well PMT#41. and Replace Transformer at Well PMT#17 11:02 Manually Blocked & Closed Pematang OCB fdr#2, then Released the Block after finished the Jobs. Cause: Planned Maintenance. |  | 1 | 10:24 | Morning | Friday | 2017 | 12
7508 | 2017-12-22 10:30 | 2017-12-22 10:30 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Planned Maintenance | 133 | 10:30 Manually Opened Petapahan VCB fdr#4 to Replace Transformer at well PTH#122 and #135 11:17 Manually Block & Closed Petapahan VCB fdr#4, then released the Block After finished the jobs. Cause: Planned Maintenance. |  | 1 | 10:30 | Morning | Friday | 2017 | 12
7509 | 2017-12-22 10:40 | 2017-12-22 10:40 | 13.8KV RANGAU FEEDER #2 | Fair | Construction Job | 0 | 10:40 Manually Closed Rangau OCB fdr#2 to install Transformer at Well Obor #3 reactive Well. and Project Tie In power for New Well Jurong S1-O-23A. 17:50 Manually Block & Closed Rangau OCB fdr#2, then released the Block. After finished the Jobs. Cause : Planned Construction Job. |  | 1 | 10:40 | Morning | Friday | 2017 | 12
7510 | 2017-12-22 15:48 | 2017-12-22 15:48 | NEW PETAPAHAN SUBSTATION | Fair | Planned Maintenance | 69 | Perform to Energize Petapahan TX#2 & VR#2 15:48 By Opened TIE Breaker VCB #9 between Bus#1 & Bus#2, separate the Buses also Petapahan Feeder#6,#7,#8 be Off. 17:19 Manually Block & Closed Petapahan VCB fdr#6 17:17 Manually Block & Closed Petapahan VCB fdr#7 17:08 Manually Block & Closed Petapahan VCB fdr#8. Cause: Planned Maintenance. |  | 1 | 15:48 | Afternoon | Friday | 2017 | 12
7511 | 2017-12-23 06:16 | 2017-12-23 06:16 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri 13.8 KV ACB#26 Fdr#16 T/R 1X Ctr:304-305 R/F:50@1@2. Not Patrolled Yet. |  | 1 | 6:16 | Morning | Saturday | 2017 | 12
7512 | 2017-12-23 06:16 | 2017-12-30 15:16 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 6:16 | Morning | Saturday | 2017 | 12
7513 | 2017-12-23 10:50 | 2017-12-23 10:50 | 13.8KV 8C FEEDER #2 | Fair | Planned Maintenance | 0 | 10:50 Manually Opened 8D OCB fdr#2 to Replace 150-300KVATX at Well 9D-16N 11:03 Manually Block & Closed 8D OCB fdr#2, then released the block. After finished the Jobs. Cause: Planned Maintenance |  | 1 | 10:50 | Morning | Saturday | 2017 | 12
7514 | 2017-12-23 11:08 | 2017-12-23 11:08 | NORTH DURI POWER PLANT |  |  | - | 11:08 NDC CT##1 S/U, Then On Line to Power System at 12:05 to restore power after solve High Vibration |  | 1 | 11:08 | Morning | Saturday | 2017 | 12
7515 | 2017-12-23 11:30 | 2017-12-23 11:30 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 33 | 11:30 Manually Opened Bekkasap OCB fdr#2 to Adjust Voltage 150KVATX at well BKS #89 11:54 Manually Block & Closed Back BKS OCB fdr#2, then released the block. after finished the Jobs. Cause: Planned Maintenance |  | 1 | 11:30 | Morning | Saturday | 2017 | 12
7516 | 2017-12-23 14:22 | 2017-12-23 14:22 | 13.8KV 3D FEEDER #3 | Fair | Planned Maintenance | 35 | 14:22 Manually Opened 3D Ocb fdr #3 to Replace 150-300Kva Tx at well 4C 38N and Install 150Kva at Well 4C 44 Reactive Well 15:51 Manually Blocked & Closed 3D Ocb Fdr #3 After Finished the Jobs Cause: planned Maintenance |  | 1 | 14:22 | Afternoon | Saturday | 2017 | 12
7517 | 2017-12-23 14:22 | 2017-12-23 14:22 | 13.8KV 3D FEEDER #3 | Fair | Planned Maintenance | 35 | 14:22 Manually Opened 3D Ocb fdr #3 to Replace 150-300Kva Tx at well 4C 38N and Install 150Kva at Well 4C 44 Reactive Well 15:51 Manually Blocked & Closed 3D Ocb Fdr #3 After Finished the Jobs Cause: planned Maintenance |  | 1 | 14:22 | Afternoon | Saturday | 2017 | 12
7518 | 2017-12-23 16:05 | 2017-12-23 16:05 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Broken Fuse Cut Out | 874 | It Was Reported B/O Fuse o/p 03-01-19 (CD Fdr #7) Not checked yet | 123 | 1 | 16:05 | Afternoon | Saturday | 2017 | 12
7519 | 2017-12-23 16:05 | 2017-12-24 16:05 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Broken Fuse Cut Out | 874 | Checked & found, @1, @2 b/o Fuses for 112.5KVA Tx on Pole 03-01-19. Also Found, @1, @2 broken FCO for the Tx. Cause: Broken Fuse Cut Out. (Will be replaced soon). Prod Loss: 735 Bbls to 02 Jan 2018 | 123 | 1 | 16:05 | Afternoon | Saturday | 2017 | 12
7520 | 2017-12-23 16:05 | 2018-03-01 14:29 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Broken Fuse Cut Out | 874 | Replaced @1@2@3 Broken Fuse Cut Out for 112.5 Kva Tx o/p 03-1-19. Cause: Broken Fuse Cut Out. | 123 | 1 | 16:05 | Afternoon | Saturday | 2017 | 12
7521 | 2017-12-23 19:10 | 2017-12-23 19:10 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 87 | Ketigul VCB fdr#2 T/R 1x Not checked yet. |  | 1 | 19:10 | Night | Saturday | 2017 | 12
7522 | 2017-12-23 19:10 | 2018-02-01 07:10 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 87 | Checked & found Ketigul VCB fdr#2 T/R 1x Ctr;257-258 R/F:51@1@2. Patrolled the line & found Dead Monkey at bushing Tx Pagar#14. Cause : Animal (Monkey). |  | 1 | 19:10 | Night | Saturday | 2017 | 12
7523 | 2017-12-24 08:22 | 2017-12-24 08:22 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Unidentified | 0 | 08:22 Menggala fdr#1 load dropped 110A (165-52A). 16:40 Checked & found Recl. 19-AO-01 T/R 1x, Ctr: 482-483, R/F 51N. Patrolled the Line, but found nothing. Cause: Unidentified. |  | 1 | 8:22 | Morning | Sunday | 2017 | 12
7524 | 2017-12-24 15:15 | 2017-12-24 15:15 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified (Fuse) | 158 | 15:15 It was reported B/O fuse on pole 09-N2-01A (C.Duri fdr#16). Not checked yet. |  | 1 | 15:15 | Afternoon | Sunday | 2017 | 12
7525 | 2017-12-24 15:15 | 2017-12-28 15:15 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified (Fuse) | 158 | Replaced @1 B/O fuse for 112.5 Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 15:15 | Afternoon | Sunday | 2017 | 12
7526 | 2017-12-24 16:00 | 2017-12-24 16:00 | 13.8KV CENTRAL DURI FEEDER #16 | Heavy Rain | Unidentified | 0 | C.Duri 13.8KV ACB fdr#16 T/R 1x, Ctr:305-306. R/F:51@1 ,@2. Not Patrolled yet. |  | 1 | 16:00 | Afternoon | Sunday | 2017 | 12
7527 | 2017-12-24 16:00 | 2017-12-30 16:00 | 13.8KV CENTRAL DURI FEEDER #16 | Heavy Rain | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:00 | Afternoon | Sunday | 2017 | 12
7528 | 2017-12-24 21:25 | 2017-12-24 21:25 | MINAS POWER PLANT |  |  | - | 21:25 MGT #1 Off Line then S/D the unit for S/B. |  | 1 | 21:25 | Night | Sunday | 2017 | 12
7529 | 2017-12-24 21:45 | 2017-12-24 21:45 | CENTRAL DURI POWER PLANT |  |  | - | 21:45 CDGT #5 Off Line then S/D the unit at.21:50. for S/B |  | 1 | 21:45 | Night | Sunday | 2017 | 12
7530 | 2017-12-24 21:55 | 2017-12-24 21:55 | MINAS POWER PLANT |  |  | - | 21:55 MGT #2 Off Line then S/D the unit for S/B. |  | 1 | 21:55 | Night | Sunday | 2017 | 12
7531 | 2017-12-24 22:00 | 2017-12-24 22:00 | MINAS POWER PLANT |  |  | - | 22:00 MGT #3 Off Line then S/D the unit for S/B. |  | 1 | 22:00 | Night | Sunday | 2017 | 12
7532 | 2017-12-25 06:50 | 2017-12-25 06:50 | 13.8KV 8D FEEDER #6 | Cloudy | Lightning | 0 | 8D 13.8 KV OCB Fdr#6 T/R 1X. Not checked yet. |  | 1 | 6:50 | Morning | Monday | 2017 | 12
7533 | 2017-12-25 06:50 | 2017-12-30 06:50 | 13.8KV 8D FEEDER #6 | Cloudy | Lightning | 0 | Checked & found, 8D OCB fdr #6 T/R 1x ctr: 2063-2064 R/F: 50N@1. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 6:50 | Morning | Monday | 2017 | 12
7534 | 2017-12-25 09:27 | 2017-12-25 09:27 | 13.8KV CENTRAL DURI FEEDER #3 | Cloudy | Unidentified | 0 | C.Duri ACB fdr#3 T/R 1x Ctr:204-205 R/F:51N. Not Patrolled Yet. |  | 1 | 9:27 | Morning | Monday | 2017 | 12
7535 | 2017-12-25 09:27 | 2017-12-30 14:27 | 13.8KV CENTRAL DURI FEEDER #3 | Cloudy | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:27 | Morning | Monday | 2017 | 12
7536 | 2017-12-25 21:21 | 2017-12-25 21:21 | NEW PETAPAHAN SUBSTATION | Cloudy | Under investigation | 90 | 21:21 New Petapahan 115KV GCB#3 T/O, Ctr: 172-173 New Petapahan 115KV GCB#5 T/O, Ctr: 68-69 New Petapahan TX-2 T/O, R/F : 87T @1@2, & 50 @A@B Checked & found, Broken LA TX for WTP, but the Fuse still good, and Recl 30-CZ-23 is Normal. Checked Visually GCBs and TX,VR saws Normal. 22:38 Isolate the TX-2 by Opened MOD Line Switch and VR Source side. 22:39 Manually Closed 13.KV MV Cable Tie Line for TIE breaker. 22:40 Manually Opened PTH VCB fdr#6,#7,#8 22:42 Manually Closed 13.8KV TIE breaker for Bus1-Bus2. 22:55 Manually Blocked & Closed VCB fdr#8, then released the block 22:58 Manually Blocked & Closed VCB fdr#6, then released the block 22:59 Manually Blocked & Closed VCB fdr#7, then released the block Cause: Under Investigation. |  | 1 | 21:21 | Night | Monday | 2017 | 12
7537 | 2017-12-26 08:22 | 2017-12-26 08:22 | MINAS POWER PLANT |  |  | - | 08:22 S/U MGT#3 the online the unit at 08:45. |  | 1 | 8:22 | Morning | Tuesday | 2017 | 12
7538 | 2017-12-26 08:40 | 2017-12-26 08:40 | CENTRAL DURI POWER PLANT | Fair |  | - | 08:40 S/U CGT#5 then on line the unit at 09:00. |  | 1 | 8:40 | Morning | Tuesday | 2017 | 12
7539 | 2017-12-26 09:30 | 2017-12-26 09:30 | MINAS POWER PLANT |  |  | - | 09:30 Off line MGT#9 Then S/D for Maintenance. |  | 1 | 9:30 | Morning | Tuesday | 2017 | 12
7540 | 2017-12-26 10:40 | 2017-12-26 10:40 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 52 | 10:40 It was reported B/O fuse on pole 08-L3-23 (C.Duri fdr#1). 15:05 Replaced @1@2 B/O fuse for 112.5 Kva Tx with the same size. Cause: Animal (Bird). |  | 1 | 10:40 | Morning | Tuesday | 2017 | 12
7541 | 2017-12-26 10:53 | 2017-12-26 10:53 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 0 | Rangau fdr#2 load dropped 100A (115-15A). Not checked yet. |  | 1 | 10:53 | Morning | Tuesday | 2017 | 12
7542 | 2017-12-26 10:53 | 2018-04-01 06:49 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Recloser 23 BD 01 T/R 1x ctr: 315-316. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:53 | Morning | Tuesday | 2017 | 12
7543 | 2017-12-26 11:30 | 2017-12-26 11:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 274 | 11:30 Manually Open LBS 30AN38 (Ketigul fdr#2). Replaced 300Kva Tx with 150Kva Tx at well Pagar#40. 12:35 Closed LBS 30AN38. Cause: Plan maintenance. |  | 1 | 11:30 | Morning | Tuesday | 2017 | 12
7544 | 2017-12-26 13:43 | 2017-12-26 13:43 | 13.8KV 3D FEEDER #4 | Cloudy | Tree | 625 | 3D fdr#4 load dropped 111A (225-114A). 3D GFPC Tx-1 T/R 1x. Not checked yet. | 123 | 1 | 13:43 | Afternoon | Tuesday | 2017 | 12
7545 | 2017-12-26 13:43 | 2017-12-28 13:01 | 13.8KV 3D FEEDER #4 | Cloudy | Tree | 625 | 13:01 It was reported no power 10 wells d/s 3D fdr#4. inform :Maridun. 14:45 Checked and found recl. 2D 33 T/o ctr:46 not operated. Patrolled the line & found fall down trees near T/p 1D 74. 15:00 Blocked & closed recl. 2D 33,the releas the block. Cause : Tree. (See PIDOD on 28 Dec at 13:43). | 123 | 1 | 13:43 | Afternoon | Tuesday | 2017 | 12
7546 | 2017-12-26 17:02 | 2017-12-26 17:02 | 13.8KV SINTONG FEEDER #2 | Cloudy | Pin Insulator | 0 | Sintong fdr#2 load dropped 138A (188-50A). Sintong fdr#1 load dropped 18A (76-58A). Not checked yet. |  | 1 | 17:02 | Afternoon | Tuesday | 2017 | 12
7547 | 2017-12-26 17:02 | 2017-12-31 07:02 | 13.8KV SINTONG FEEDER #2 | Cloudy | Pin Insulator | 0 | Checked & found Recl.. 19-Z-13A T/R 1x Ctr:175-176. Patrolled the line @2 Broken Pin Insulator o/p 29Z27. Cause : Pin Insulator. |  | 1 | 17:02 | Afternoon | Tuesday | 2017 | 12
7548 | 2017-12-27 06:49 | 2017-12-27 06:49 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 33 | Rangau fdr#2 Load dropped 103A (119-16A). Not checked yet. |  | 1 | 6:49 | Morning | Wednesday | 2017 | 12
7549 | 2017-12-27 06:49 | 2018-04-01 06:49 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 33 | Checked & found, Recloser 23 BD 01 T/R 1x ctr: 316-317. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:49 | Morning | Wednesday | 2017 | 12
7550 | 2017-12-27 11:10 | 2017-12-27 11:10 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Unidentified | 96 | 11:10 CKBS VCB fdr#5 T/R 1x. CKBS fdr#6 Load dropped 100A (153-53A). 12:40 Checked & found CKBS VCB fdr#5 T/R 1x Ctr:147-148 R/F:51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 11:10 | Morning | Wednesday | 2017 | 12
7551 | 2017-12-27 11:20 | 2017-12-27 11:20 | 13.8KV BEKASAP FEEDER #3 | Cloudy | Planned Maintenance | 53 | 11:20 Manually opened Recl. 1TL06 (Bekasap fdr#6). Set Voltage at well BKS#17 & BKS#65. 11:40 Blocked & closed Recl. 1TL06, then release the block. Cause: Plan Maintenance. |  | 1 | 11:20 | Morning | Wednesday | 2017 | 12
7552 | 2017-12-27 14:55 | 2017-12-27 14:55 | 13.8KV 4B FEEDER #1 | Fair | Planned Maintenance | 0 | 14:55 Manually Opened LBS 3B-22 (4B fdr#1). Installed 100Kva Tx for Reactive well at 3B-74N. 16:00 Closed LBS 3B-22. Cause: Plan Maintenance. |  | 1 | 14:55 | Afternoon | Wednesday | 2017 | 12
7553 | 2017-12-27 16:35 | 2017-12-27 16:35 | MINAS POWER PLANT | Fair | Others | 0 | 16:35 MGT#5 Open Gen. Breaker, then S/D the unit by GCV Trouble. 16:52 Closed Tie Breaker ACB#16. Cause: Other (Gas fuel Low BTU, Bad Quality) |  | 1 | 16:35 | Afternoon | Wednesday | 2017 | 12
7554 | 2017-12-27 22:22 | 2017-12-27 22:22 | MINAS POWER PLANT |  |  | - | 22:22 MGT#3 S/U then on line the unit at 23:23. to Restore Power due to MGT#5 T/O.. |  | 1 | 22:22 | Night | Wednesday | 2017 | 12
7555 | 2017-12-28 06:40 | 2017-12-28 06:40 | MINAS POWER PLANT |  |  | - | 06:40 S/U MGT#5 then online the unit at 06:53. |  | 1 | 6:40 | Morning | Thursday | 2017 | 12
7556 | 2017-12-28 09:40 | 2017-12-28 09:40 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Planned Maintenance | 38 | 09:40 Manually open Recl: 29 CX 05 (Petapahan Fdr#4). Replaced 150 Kva TX with 300 Kva TX at well Petapahan #21. RM 80HP to 180HP. Dismantle 300 Kva VSD TX at well Petapahan #52. Replaced 350 Kva TX with the same size at well Topas#06. 11:04 Blocked & Closed Recl: 29 CX 05 then release the Block Cause: Plan Maintenance. |  | 1 | 9:40 | Morning | Thursday | 2017 | 12
7557 | 2017-12-28 10:34 | 2017-12-28 10:34 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | 46 | It was reported B/O Fuse o/p 06-R1-11 (C.Duri Fdr#15). Not checked yet. |  | 1 | 10:34 | Morning | Thursday | 2017 | 12
7558 | 2017-12-28 10:34 | 2017-12-30 10:35 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | 46 | Replaced @1 B/O fuse for 112.5Kva Tx with the same size o/p 06-R1-11. Cause: Unidentified Fuse. |  | 1 | 10:34 | Morning | Thursday | 2017 | 12
7559 | 2017-12-28 10:35 | 2017-12-28 10:35 | 13.8KV PINANG FEEDER #1 | Fair | Transformer Failure | 0 | It was reported B/O Fuse at well Pinang #14 (Pinang Fdr#1). Checed TTR & Megger 150 Kva Tx failure. (would be changed tomorrow). Cause TX Failure. |  | 1 | 10:35 | Morning | Thursday | 2017 | 12
7560 | 2017-12-28 10:35 | 2017-12-30 15:35 | 13.8KV PINANG FEEDER #1 | Fair | Transformer Failure | 0 | Replaced 150Kva Tx with the same size above. Cause: Tx Failure. |  | 1 | 10:35 | Morning | Thursday | 2017 | 12
7561 | 2017-12-28 13:01 | 2017-12-28 13:01 | 13.8KV 3D FEEDER #4 | Fair | Tree | 0 | 13:01 It was reported no power 10 wells d/s 3D fdr#4. inform :Maridun. 14:45 Checked and found recl. 2D 33 T/SO ctr:46 not operated. Patrolled the line & found fall down trees near T/p 1D 74. 15:00 Blocked & closed recl. 2D 33,the releas the block. Cause : Tree. See Outage 26 Dec at 13:43:00 |  | 1 | 13:01 | Afternoon | Thursday | 2017 | 12
7562 | 2017-12-28 13:30 | 2017-12-28 13:30 | MINAS POWER PLANT | Fair |  | - | 13:30 S/U MGT#9, then online the unit at 14:26. |  | 1 | 13:30 | Afternoon | Thursday | 2017 | 12
7563 | 2017-12-28 16:35 | 2017-12-28 16:35 | MINAS POWER PLANT |  |  | - | Off line MGT#5, the S/D the unit for S/B. 16:25 Close Tie Breaker ACB#16. 16:28 Open Tie Breaker ACB#8 |  | 1 | 16:35 | Afternoon | Thursday | 2017 | 12
7564 | 2017-12-28 16:54 | 2017-12-28 16:54 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | 16:54 Darling 13.8Kva VCB#7 T/O. 16:54 Darling GFPC-TX#2 T/O. 16:57 Blocked & Closed Darling GFPC TX#2 the release the Block. 16:58 Blocked & Closed Darling Fdr#7 But not operate. 18:05 Checked & found Darling VCB Fdr#7 T/O Ctr:162(Not operated) R/F: NN. Block & Closed Darling Fdr#7, the release the Block. Not Patrolled Yet. |  | 1 | 16:54 | Afternoon | Thursday | 2017 | 12
7565 | 2017-12-28 16:54 | 2018-01-01 07:54 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 16:54 | Afternoon | Thursday | 2017 | 12
7566 | 2017-12-28 17:15 | 2017-12-28 17:15 | CENTRAL DURI POWER PLANT |  |  | - | 17:15 Off line CDGT#3 the S/D the unit for replace flame scanner 17:16 Closed Tie Breaker ACB#39, then closed at 18:53. 18:44 S/U CGT#3, then on line the unit at 18:58. |  | 1 | 17:15 | Afternoon | Thursday | 2017 | 12
7567 | 2017-12-28 19:42 | 2017-12-28 19:42 | CENTRAL DURI POWER PLANT |  |  | - | 19:42 Off Line CDGT #5 The S/D the unit at.19:45 for S/B. |  | 1 | 19:42 | Night | Thursday | 2017 | 12
7568 | 2017-12-28 20:28 | 2017-12-28 20:28 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Unidentified | 15 | Libo 13.8KV OCB fdr#2 T/R 1X. Libo fdr#1 load dropped 13A (62-49A). Not checked yet. |  | 1 | 20:28 | Night | Thursday | 2017 | 12
7569 | 2017-12-28 20:28 | 2018-02-01 07:28 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Unidentified | 15 | Checked & found Libo fdr#2 T/R 1x Ctr:477-478 R/F:51@1. Patrolled the line not found nothing. Cause : Unidentified. |  | 1 | 20:28 | Night | Thursday | 2017 | 12
7570 | 2017-12-28 21:55 | 2017-12-28 21:55 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Unidentified | 50 | Bekasap fdr #2 Load dropped 46A (99-53A). Not checked yet. |  | 1 | 21:55 | Night | Thursday | 2017 | 12
7571 | 2017-12-28 21:55 | 2018-02-01 07:55 | 13.8KV BEKASAP FEEDER #3 | Rain and Lightning | Unidentified | 50 | Checked & found 38BD18 T/R 1x Ctr:85-86. Patrolled the line @2 Broken LA o/p 38BE19. Cause : Unidentified. |  | 1 | 21:55 | Night | Thursday | 2017 | 12
7572 | 2017-12-28 22:03 | 2017-12-28 22:03 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Unidentified | 0 | 22:02 OKB Fdr #2 Load dropped 159A (259-100A). Not checked yet. |  | 1 | 22:03 | Night | Thursday | 2017 | 12
7573 | 2017-12-28 22:03 | 2017-12-31 17:03 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found Recl. 38CW08 T/R 1x Ctr:97-98. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 22:03 | Night | Thursday | 2017 | 12
7574 | 2017-12-29 07:10 | 2017-12-29 07:10 | 13.8KV MINAS FEEDER #3 | Fair | Animal | 64 | Minas Fdr#3 T/R 1X Ctr:131-132 R/F: 51N. Not patrolled yet. |  | 1 | 7:10 | Morning | Friday | 2017 | 12
7575 | 2017-12-29 07:10 | 2017-12-30 07:10 | 13.8KV MINAS FEEDER #3 | Fair | Animal | 64 | Checked & found, Minas ACB #02 fdr #3 T/R 1x ctr: 131-132 R/F: 51 @3. Patrolled the line & found, b/o fuse for PT of Recloser 7D-93. Cause: Animal (Bird). |  | 1 | 7:10 | Morning | Friday | 2017 | 12
7576 | 2017-12-29 10:05 | 2017-12-29 10:05 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | 68 | 10:05 Manually open Recl. 23X08 (Bangko Fdr#1). Replaced 225 Kva TX with 150 Kva TX at Well Bangko #219. 10:27 Blocked & Closed Recl:23 X 08,then release the Block. Cause: Plan Maintenance. |  | 1 | 10:05 | Morning | Friday | 2017 | 12
7577 | 2017-12-29 10:50 | 2017-12-29 10:50 | 13.8KV RANGAU FEEDER #2 | Fair | Construction Job | 0 | 10:50 Manually Opened Rangau VCB fdr#2. Relocated & Tie In New well Jurong#42. 18:40 Blocked & closed Rangau VCB fdr#2, then release the block. Cause: Construction Job. |  | 1 | 10:50 | Morning | Friday | 2017 | 12
7578 | 2017-12-29 14:12 | 2017-12-29 14:12 | MINAS POWER PLANT |  |  | - | 14:12 S/U MGT#5, then on line the unit at 14:23. ( Running test ) 16:15 Off line MGT#5, then S/D the unit for S/B. |  | 1 | 14:12 | Afternoon | Friday | 2017 | 12
7579 | 2017-12-29 15:00 | 2017-12-29 15:00 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 250 | 15:00 Manually open LBS 20V01 (Nella Fdr#1). Repaired hot spot Recl:20V01 & Cap Bank on T/P Bangko#175. 15:30 Closed LBS 20V01. Cause: Plan Maintenance. |  | 1 | 15:00 | Afternoon | Friday | 2017 | 12
7580 | 2017-12-29 15:34 | 2017-12-29 15:34 | 13.8KV DURI COMMUNITY FEEDER #2 | Cloudy | Lightning | 0 | Duri Community Fdr#2 T/R 1x. Not checked yet. |  | 1 | 15:34 | Afternoon | Friday | 2017 | 12
7581 | 2017-12-29 15:34 | 2018-04-01 15:34 | 13.8KV DURI COMMUNITY FEEDER #2 | Cloudy | Lightning | 0 | Checked & found, Duri Community ACB #30 fdr #2 T/R 1x ctr: 88-89 R/F: 51 @3. Patrolled the line & found, @3 broken Pin Insulator on Pole SLI-1A-05A. Cause: Lightning. |  | 1 | 15:34 | Afternoon | Friday | 2017 | 12
7582 | 2017-12-30 04:10 | 2017-12-30 04:10 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Tree | 0 | 04:10 It was reported no power at Wisma Mutiara. 09:00 Checked & found @2@3 B/O fuse for 300Kva Tx at W.Mutiara. Danger tree Touch Bushing 300Kva Tx at W.Mutiara. 16:45 Replaced @2@3 B/O fuse for 300Kva Tx with the same size and Energized Tx. Cause: Tree. |  | 1 | 4:10 | Morning | Saturday | 2017 | 12
7583 | 2017-12-30 13:20 | 2017-12-30 13:20 | 13.8KV CENTRAL DURI FEEDER #16 | Rain | Unidentified | 0 | C.Duri ACB fdr#16 T/R 1x Ctr:306-307 R/F:51@1@2. Not patrolled yet. |  | 1 | 13:20 | Afternoon | Saturday | 2017 | 12
7584 | 2017-12-30 13:20 | 2018-01-01 08:20 | 13.8KV CENTRAL DURI FEEDER #16 | Rain | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 13:20 | Afternoon | Saturday | 2017 | 12
7585 | 2017-12-30 13:28 | 2017-12-30 13:28 | 13.8KV PINANG FEEDER #1 | Fair | Planned Maintenance | 63 | 13:38 Manually open Pinang VCB fdr#1. Replaced 150Kva Tx with the same size at well Pinang#14. Replaced 150Kva Tx with 100Kva Tx at well Pinang#30. Replaced@1 B/O fuse for 150Kva Tx wit the same size at well Pinang#23. 14:48 Blocked & closed Pinang VCB fdr#1, then release the block. Cause: Plan Maintenance. |  | 1 | 13:28 | Afternoon | Saturday | 2017 | 12
7586 | 2017-12-30 15:30 | 2017-12-30 15:30 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 33 | Ketigul VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 15:30 | Afternoon | Saturday | 2017 | 12
7587 | 2017-12-30 15:30 | 2018-04-01 15:30 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 33 | Checked & found, Ketigul VCB fdr #1 T/R 1x ctr: 194-195 R/F: 51 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:30 | Afternoon | Saturday | 2017 | 12
7588 | 2017-12-30 17:07 | 2017-12-30 17:07 | 13.8KV DURI FIELD FEEDER #2 | Rain | Animal | 44 | 05:51 DF Fdr #2 Load drop 67A (179-130A). 07:15 Checked & found Recl. 07-U3-21 T/SO Ctr:200-201 R/F:51@2. Blocked & closed Recl. 07-U3-21, then release the block. By pass Recl. 07-U3-21 by unplug cable control Recl. 09:20 Patrolled the line & found Dead Squirrel at pole 07-3-15. Cause: Animal (Squirrel) |  | 1 | 17:07 | Afternoon | Saturday | 2017 | 12
7589 | 2017-12-30 21:12 | 2017-12-30 21:12 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Transformer Failure | 31 | Pinang fdr #1 T/R 1X, Not checked yet. |  | 1 | 21:12 | Night | Saturday | 2017 | 12
7590 | 2017-12-30 21:12 | 2018-03-01 07:12 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Transformer Failure | 31 | Checked & found Pinang VCB fdr#1 T/R 1x Ctr::429-430 R/F:51N. Patrolled the line & Found @2@3 B/O fuse for 150Kva Tx at well Pinang#12. Cause : Transformer Failure. |  | 1 | 21:12 | Night | Saturday | 2017 | 12
7591 | 2017-12-30 21:12 | 2018-04-01 14:30 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Transformer Failure | 31 | Replaced 150Kva Tx with the same size at well Pinang #12. Cause: Transformer Failure. |  | 1 | 21:12 | Night | Saturday | 2017 | 12
7592 | 2017-12-31 01:30 | 2017-12-31 01:30 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 93 | 01:30 5BOCB fdr#3 T/R 1x. 5B fdr#1 Load dropped 84A (88-4A) 5B fdr#2 Load dropped 163A (175-11A) 17:00 Checked & found, 5B OCB fdr #3 T/R 1x ctr: 382-385 R/F: 51N @2, @3. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 1:30 | Night | Sunday | 2017 | 12
7593 | 2017-12-31 05:46 | 2017-12-31 05:46 | 13.8KV DURI FIELD FEEDER #1 | Drizzle | Transformer Failure | 0 | 05:46 Duri Field Fdr #1 T/R 1x. 14:00 Checked & found, Duri Field ACB #41 fdr #1 T/R 2x ctr: 683-685 R/F: 51. Patrolled the line & found, 2500KVA TX #8 at CGS #1 on Pole 01-05-19A was Failure. Cause: Transformer Failure. |  | 1 | 5:46 | Morning | Sunday | 2017 | 12
7594 | 2017-12-31 05:51 | 2017-12-31 05:51 | 13.8KV DURI FIELD FEEDER #2 | Drizzle | Animal | 31 | 05:51 DF Fdr #2 Load drop 67A (179-130A). 07:15 Checked & found Recl. 07-U3-21 T/SO Ctr:200-201 R/F:51@2. Blocked & closed Recl. 07-U3-21, then release the block. By pass Recl. 07-U3-21 by unplug cable control Recl. 09:20 Patrolled the line & found Dead Squirell at pole 07-3-15. Cause: Animal (Squirrel). |  | 1 | 5:51 | Morning | Sunday | 2017 | 12
7595 | 2017-12-31 06:10 | 2017-12-31 06:10 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Recloser - Control Recloser | 240 | 06:10 Manggala Fdr #1 Load drop 89A (159-70A). 08:45 Checked & found Recl. 19AN04 Pumping. Service Control Recl. 19AN04. 09:22 Blocked & closed Recl. 19AN04, then bypass Recl. with unplug control Recl. Cause: Control Recloser. |  | 1 | 6:10 | Morning | Sunday | 2017 | 12
7596 | 2017-12-31 07:00 | 2017-12-31 07:00 | 13.8KV DURI FIELD FEEDER #1 | Drizzle | Transformer Failure | 0 | 07:00 It was reported no power at CGS#1. 07:50 Checked & found @1 B/O fuse for 2500Kva Tx-8 at CGS#1 (D.Field fdr#1). @1 Broken LA o/p 01-5-19. 08:52 Open LBS 01-5-32. Replaced @1 B/O fuse for 2500Kva Tx-8 with the same size. 08:54 Closed LBS 01-5-32. Cause: Suspected Lightning. 14:00 It was reported unbalance voltage for 2500Kva Tx-8 at CGS#1. 14:20 Checked & found @1 B/O fuse for 2500Kva Tx-8 at CGS#1. 15:08 Opened LBS 01-5-32, then closed at 15:09. Open @2@3 fuse for 2500 Kva Tx-8 at CGS#1. Checked TTR & Megger 2500Kva Tx-8 at CGS#1 is Failure. Cause; Transformer Failure. |  | 1 | 7:00 | Morning | Sunday | 2017 | 12
7597 | 2017-12-31 07:00 | 2018-06-01 11:44 | 13.8KV DURI FIELD FEEDER #1 | Drizzle | Transformer Failure | 0 | Energized 2500 Kva Tx #8 at CGS #1. Cause: Transformer failure. |  | 1 | 7:00 | Morning | Sunday | 2017 | 12
7598 | 2017-12-31 09:05 | 2017-12-31 09:05 | CENTRAL DURI POWER PLANT |  |  | - | 09:05 S/U CGT#5, then on line the unit at 09:20. 14:00 Off line CGT#5, then S/D the unit for S/B. |  | 1 | 9:05 | Morning | Sunday | 2017 | 12
7599 | 2017-12-31 09:50 | 2017-12-31 09:50 | CENTRAL DURI POWER PLANT |  |  | - | 09:50 Off Line CGT#2, the S/D the unit for Maintenance. 09:51 Closed Tie Breaker ACB#19. 13:22 S/U CGT#2, then on line the unit at 13:37. 13:35 Open Tie Breaker ACB#19. |  | 1 | 9:50 | Morning | Sunday | 2017 | 12
7600 | 2017-12-31 10:00 | 2017-12-31 10:00 | 13.8KV BEKASAP FEEDER #3 | Cloudy | Powerline - Jumper | 396 | 10:00 Bekasap fdr#3 Load dropped 73A (95-22A). Bekasap fdr#2 Load dropped 8A (250-242A). Bekasap fdr#5 Load dropped 245A (296-51A) Pump Off. Bekasap fdr#6 Load dropped 37A (89-52A). 10:30 Checked & found Recl. 1TL06 T/LO Ctr:58-62. Patrolled the line & found @2 Broken LA o/p 37BE16. 11:17 Blocked & closed Recl. 1TL06, but failed. Patrolled the line & found @2 Broken Jumper of Recl 38BD18. 13:55 Closed bypass switch of Recl.38BD18. 14:07 Blocked & closed Recl 1TL06, then release the block. Cause: Broken Jumper. |  | 1 | 10:00 | Morning | Sunday | 2017 | 12
7601 | 2017-12-31 13:54 | 2017-12-31 13:54 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 16 | It was reported B/O fuse o/p 01-6-15 (D,Field fdr#1). Not checked yet. |  | 1 | 13:54 | Afternoon | Sunday | 2017 | 12
7602 | 2017-12-31 13:54 | 2018-02-01 11:00 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 16 | Replaced @1@2 B/O fuse for 112.5Kva Tx with the same size o/p 01-6-15. Cause: Unidentified Fuse. |  | 1 | 13:54 | Afternoon | Sunday | 2017 | 12
7603 | 2017-12-31 15:10 | 2017-12-31 15:10 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 0 | 15:10 Duri Field fdr#1 T/R 1x. 16:33 Checked & found D.Field fdr#1 T/R 2x Ctr:283-285 R/F 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:10 | Afternoon | Sunday | 2017 | 12
7604 | 2017-12-31 16:54 | 2017-12-31 16:54 | 13.8KV SINTONG FEEDER #2 | Cloudy | Pin Insulator | 44 | Sintong VCB fdr#2 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 16:54 | Afternoon | Sunday | 2017 | 12
7605 | 2017-12-31 18:51 | 2017-12-31 18:51 | 13.8KV SO BEKASAP FEEDER #1 | Rain | Lightning | 0 | So.Bekasap fdr#1 Load dropped 80A (122-42A). Not checked yet. |  | 1 | 18:51 | Afternoon | Sunday | 2017 | 12
7606 | 2017-12-31 18:51 | 2018-04-01 18:51 | 13.8KV SO BEKASAP FEEDER #1 | Rain | Lightning | 0 | Checked & found, Recloser 34-BI-18 T/R 1x ctr: 164-165 Patrolled the line & found, @3 broken Lightning Arrester on Pole 32-BE-08. Cause: Lightning. |  | 1 | 18:51 | Afternoon | Sunday | 2017 | 12
7607 | 2018-01-01 02:38 | 2018-01-01 02:38 | KOTABATAK JUNCTION SW STA | Heavy Rain | Substation Failure (LA) | 3283 | 02:38 KBJ 115KV GCB#27 T/R 1x. at that time respectively 3D substation RTU was Failed. Got Inform that Minas GS#5 was no power. 04:13 Checked and founded 115KV GCB #21 T/SO, Ctr:154-157 R/F:87B@B. Checked and founded 115KV GCB #22 T/SO, Ctr:111-112. Manually Opened TX-1 C/S. Manually Opened TX-2 C/S but fail (Breaker pumping). 04:50 Manually Opened 13.8KV OCB 5B Fdr #4.(GS #5 ) Manually Opened 13.8KV OCB 4D Fdr #6 (GS #5 ) 05:18 Manually Opened Line switch of C/S TX-2. Manually Opened 13.8KV OCB Fdr #2, 3, 4, 5, 6, 7, 8. 05:20 Manually Closed 115KV GCB #21. 05:22 Manually Closed C/S TX-1. 05:25 Manually Closed 3D Fdr #5. 07:36 Closed breaker power of station service from 3D Bus-1 (RTU On). 08:00 Closed LBS 3D-144 transfer load 3D fdr#7 to 3D fdr#5. 08:14 Opened LBS 3D-41. 08:16 Closed LBS 3D-148 transfer part load 3D fdr#8 to 3D fdr#5. 09:14 Blocked & closed 4D fdr#6, then release the block. 09:45 Function tes 3D C/S-2, ok. 09:55 Closed Line Switch 3D C/S-2. 09:56 Closed 3D C/S-2 but failed. 115Kv KBJ GCB#27 T/R 1x. 115Kv KBJ GCB#23 T/O. 115Kv 3D GCB#21 T/O, then closed at 10:00. 09:57 Open 3D fdr#5, then closed at 10:06. 09:58 Opened 3D C/S-1, then closed at 10:05. Checked & found @2 Broken 115Kv LA at 3D Tx-2. 10:26 Closed LBS "A" GS#5, transfer load 3D fdr#6 to 4D fdr#1. 11:08 Blocked & closed 3D fdr#4, then release the block. 11:09 Blocked & closed 5B fdr#4, the release the block. 11:24 Closed LBS 3D-208 transfer part load 3d fdr#8 to 4D fdr#6. 11:53 Blocked & closed 3D fdr#3, then release the block. 10:07 Blocked & closed 3D fdr#2, then release the block. 13:24 4D OCB fdr#1 T/R 1x (Over load S/U pump). 15:48 Closed 115 Kv 3D GCB#22. Cause: Under investigation. Production Loss of Minas GS#5 3D fdr#2 : 18 Wells, 412 Bbls 3D fdr#3 : 15 Wells, 260 Bbls 3D fdr#4 : 27 Wells, 518 Bbls 3D fdr#7 : 11 Wells, 143 Bbls 3D fdr#8 : 14 Wells, 244 Bbls 5B fdr#4 : 6 Wells, 126 Bbls 4D fdr#6 : 2 Wells, 24 Bbls ------------------------------------- Total : 79 Wells, 1727 Bbls | 1234 | 1 | 2:38 | Night | Monday | 2018 | 1
7608 | 2018-02-01 10:10 | 2018-02-01 10:10 | 13.8KV BEKASAP FEEDER #3 | Fair | Planned Maintenance | 5 | 10:10 Manually Opened Recl 1TL06 (Bekasap fdr#3). Replaced 100Kva Tx with 150Kva Tx at well Bekasap#166. 11:15 Blocked & Closed Recl: 1TL06, then release the block. Cause: Plan Maintenance. |  | 1 | 10:10 | Morning | Thursday | 2018 | 2
7609 | 2018-02-01 15:28 | 2018-02-01 15:28 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | 15:28 It was reported B/O fuse o/p 01-2-24 (C.Duri fdr#3). 16:40 Replaced @2 B/O fuse for 112.5Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 15:28 | Afternoon | Thursday | 2018 | 2
7610 | 2018-03-01 05:59 | 2018-03-01 05:59 | 13.8KV 4D FEEDER #1 | Fair | Unidentified | 0 | 05:59 4D OCB fdr#1 T/R 1x. 06:18 4D OCB fdr#1 T/R 1x. While S/U WIP unit GS#5. Not checked yet |  | 1 | 5:59 | Morning | Thursday | 2018 | 3
7611 | 2018-03-01 05:59 | 2018-05-01 05:59 | 13.8KV 4D FEEDER #1 | Fair | Unidentified | 0 | Checked & found, 4D OCB fdr #1 T/R 2x ctr: 179-181 R/F: 50. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 5:59 | Morning | Thursday | 2018 | 3
7612 | 2018-03-01 06:25 | 2018-03-01 06:25 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 0 | 06:25 Manually Opened 4D OCB fdr#2 Well Feeder. GS #5 to to Maintain Tank Level. 06:51 Manually Block & Closed 4D OCB fdr#2, then released the Block. Cause: Planned Construction.. |  | 1 | 6:25 | Morning | Thursday | 2018 | 3
7613 | 2018-03-01 10:37 | 2018-03-01 10:37 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Planned Maintenance | 31 | 10:37 Manually Opened Petapahan fdr#4. Replaced 300Kva VCD SGN wit Tx with 300Kva Tx . 11:07 Blocked & Closed Petapahan fdr#4, then release the block. Cause: Planned Maintenance |  | 1 | 10:37 | Morning | Thursday | 2018 | 3
7614 | 2018-03-01 11:15 | 2018-03-01 11:15 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 30 | 10:10 Manually Opened Recl. 34 B1 18 (So. Bekasap fdr#1). Replaced 300Kva Tx with 150Kva Tx at well Hiu#09. 11:15 Blocked & Closed Recl: 34 B1 18, then release the block. Cause: Plan Maintenance. |  | 1 | 11:15 | Morning | Thursday | 2018 | 3
7615 | 2018-03-01 17:21 | 2018-03-01 17:21 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Lightning | 0 | Duri Field 13.8KV VCB fdr#4 T/R 1X. Not checked yet. |  | 1 | 17:21 | Afternoon | Thursday | 2018 | 3
7616 | 2018-03-01 17:21 | 2018-07-01 17:20 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found Duri Field VCB #51 (feeder#4) T/R 1x Counter: 511-512 R/F: 51@1. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 17:21 | Afternoon | Thursday | 2018 | 3
7617 | 2018-03-01 19:57 | 2018-03-01 19:57 | 13.8KV KETIGUL FEEDER#3 | Cloudy | Lightning | 15 | Ketigul 13.8KV VCB fdr #3 T/R 1X. Not checked yet. |  | 1 | 19:57 | Night | Thursday | 2018 | 3
7618 | 2018-03-01 19:57 | 2018-07-01 19:57 | 13.8KV KETIGUL FEEDER#3 | Cloudy | Lightning | 15 | Checked & found, Ketigul VCB fdr # T/R 1x ctr: 194-195 R/F: 51N. Patrolled the line & found, @2 broken Pin Insulator on TP of Well Gulamo #3. Also found, @1, @2 broken Lightning Arrester on TP of Well Gulamo #3. Cause: Lightning. |  | 1 | 19:57 | Night | Thursday | 2018 | 3
7619 | 2018-04-01 09:58 | 2018-04-01 09:58 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Planned Maintenance | 0 | 09:58 Manually Opened CKBS fdr#6. Replaced 300Kva Tx VSD SGN with 300Kva Tx VSD EJP. 11:11 Blocked & Closed CKBS fdr#6 , then release the block. Cause: Contraction. |  | 1 | 9:58 | Morning | Sunday | 2018 | 4
7620 | 2018-04-01 10:01 | 2018-04-01 10:01 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 0 | Ketigul fdr#1 load dropped 96A (106-10A). Ketigul fdr#2 load dropped 24A (176-152A). Not checked yet. |  | 1 | 10:01 | Morning | Sunday | 2018 | 4
7621 | 2018-04-01 10:01 | 2018-07-01 10:01 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 0 | Checked & found, Ketigul VCB fdr #1 T/R 1x ctr: 195-196 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:01 | Morning | Sunday | 2018 | 4
7622 | 2018-04-01 13:10 | 2018-04-01 13:10 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Low mega-ohm reading | 0 | It was reported B/O fuse at wells SoE.Balam22 (Balam fdr#4). Not checked yet. |  | 1 | 13:10 | Afternoon | Sunday | 2018 | 4
7623 | 2018-04-01 13:10 | 2018-05-01 10:12 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Low mega-ohm reading | 0 | Checked and found @1,@3 b/o fuse for 150 Kva Tx at well South East Balam #22. Performed TTR and megger test the Tx and found Low megger reading. Cause: Tx failure (Low mega ohm reading). |  | 1 | 13:10 | Afternoon | Sunday | 2018 | 4
7624 | 2018-04-01 13:10 | 2018-06-01 11:30 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Low mega-ohm reading | 0 | Replaced transformer failure with the same size (150 Kva). and then energized the Transformer. Cause: Tx failure. |  | 1 | 13:10 | Afternoon | Sunday | 2018 | 4
7625 | 2018-04-01 14:46 | 2018-04-01 14:46 | 13.8KV 8C FEEDER #2 | Fair | Planned Maintenance | 12 | 14:46 Manually Opened 8C fdr#2 . Replaced @1, @2, @3 broken pin insulator O/P 9D-50. 15:15 Blocked & Closed 8C fdr#2, then release the block. Cause: Plan Maintenance. |  | 1 | 14:46 | Afternoon | Sunday | 2018 | 4
7626 | 2018-04-01 14:47 | 2018-04-01 14:47 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Planned Maintenance | 0 | 09:58 Manually Opened Petapahan fdr#3. Replaced 300Kva Tx VSD SGN with 300Kva Tx VSD EJP. 15:25 Blocked & Closed CKBS fdr#6, then release the block. Cause: Contraction. |  | 1 | 14:47 | Afternoon | Sunday | 2018 | 4
7627 | 2018-04-01 14:50 | 2018-04-01 14:50 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 60 | OKB OCB fdr#2 T/R 1X. Not checked yet. |  | 1 | 14:50 | Afternoon | Sunday | 2018 | 4
7628 | 2018-04-01 14:50 | 2018-05-01 14:50 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 60 | Checked & found, Kotabatak OCB fdr #2 T/R 1x ctr: 1305-1306 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:50 | Afternoon | Sunday | 2018 | 4
7629 | 2018-05-01 09:54 | 2018-05-01 09:54 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 0 | 09:54 Manually opened Pematang OCB feeder #2 due to: 1. Adjust voltage at well Pematang #29. Tx: 300 Kva R/M: 50 Hp Sec Voltage:927 Volt. 2. Adjust voltage at well Pematang #73. Tx: 225 Kva R/M: 105 Hp Sec Voltage:1009 Volt. 10:34 Manually blocked and closed Pematang OCB feeder #2 and then released the block. Cause: Plan Maintenance. |  | 1 | 9:54 | Morning | Tuesday | 2018 | 5
7630 | 2018-05-01 09:56 | 2018-05-01 09:56 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 45 | It was reported b/o fuse for Tx on pole 04-02-10 D/S C. Duri feeder # 9. Not checked yet. |  | 1 | 9:56 | Morning | Tuesday | 2018 | 5
7631 | 2018-05-01 09:56 | 2018-06-01 14:10 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 45 | Checked and found @3 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (fuse). |  | 1 | 9:56 | Morning | Tuesday | 2018 | 5
7632 | 2018-05-01 10:39 | 2018-05-01 10:39 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 160 | 10:39 Manually opened Minas ACB #2 (feeder #3) due to: 1. Changed out Tx at well 7C-79 Tx: 550 - 300 Kva R/M: 200 Hp Sec Voltage:1060 Volt. 2. Repaired jumper of Recloser on pole 7D-81 due to Hot. 3. Repaired LBS on pole 7D-23 (one way feeder) due to stack. 11:30 Manually blocked and closed Minas ACB #2 (feeder #3) and then released the block. Cause: Plan Maintenance. |  | 1 | 10:39 | Morning | Tuesday | 2018 | 5
7633 | 2018-05-01 15:51 | 2018-05-01 15:51 | 13.8KV 5B FEEDER #4 | Fair | Planned Maintenance | 0 | 15:51 Manually opened LBS: 4B5B-11 D/S 5B fdr #4 due to: 1. Installed Tx and VSD by PT SGN at well 4C-11. 2. Installed Tx at well 4B-99 due to reactivated well. 18:12 Manually closed LBS: 4B5B-11. Cause: Plan Maintenance. |  | 1 | 15:51 | Afternoon | Tuesday | 2018 | 5
7634 | 2018-05-01 18:15 | 2018-05-01 18:15 | 13.8KV DURI FIELD FEEDER #1 | Fair | Circuit Breaker | 0 | Duri Field SW GR VCB #41 (feeder #1) T/R 1x. Not checked yet. |  | 1 | 18:15 | Afternoon | Tuesday | 2018 | 5
7635 | 2018-05-01 18:15 | 2018-07-01 17:15 | 13.8KV DURI FIELD FEEDER #1 | Fair | Circuit Breaker | 0 | Checked and found Duri Field SW GR VCB #41 (feeder #1) T/R 1x Counter: 685-686 R/F: 51N. Patrolled the line found Breaker 13.8 Kv failure on pole 01-05-19. Cause: Circuit breaker. |  | 1 | 18:15 | Afternoon | Tuesday | 2018 | 5
7636 | 2018-06-01 09:21 | 2018-06-01 09:21 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 26 | 09:21 Manually opened LBS: 34-CT-58 D/S CKBS fdr #5 due to: 1. Open / close fuse for trouble shooting by PT EJP at well KB #180. 2. Installed Tx at well KB #404 due to reactivated well. Tx: 300 Kva R/M: 120 Hp Sec Voltage: 980 Volt. 10:10 Manually closed LBS: 34-CT-58. Cause: Plan Maintenance. |  | 1 | 9:21 | Morning | Friday | 2018 | 6
7637 | 2018-06-01 10:10 | 2018-06-01 10:10 | 13.8KV 8D FEEDER #10 | Fair | Planned Maintenance | 230 | 10:10 Manually opened Recloser: 7E-21 D/S 8D fdr #10 due to: 1. Changed out transformer at well 7E-84N. Tx: R/M: Sec Voltage: Manually blocked and closed Recloser: 7E-21 and then released the block. Cause: Plan Maintenance. |  | 1 | 10:10 | Morning | Friday | 2018 | 6
7638 | 2018-07-01 07:22 | 2018-07-01 07:22 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 45 | Minas ACb #13 (feeder #2) T/R 1x Counter:71-72 R/F: 51N. Not patrolled yet. |  | 1 | 7:22 | Morning | Sunday | 2018 | 7
7639 | 2018-07-01 07:22 | 18/01/2018 07:22 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 45 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:22 | Morning | Sunday | 2018 | 7
7640 | 2018-08-01 06:18 | 2018-08-01 06:18 | 13.8KV MENGGALA FEEDER #1 | Fair | Low mega-ohm reading | 0 | 06:18 It was reported b/o fuse for Tx at Menggala GS D/S Menggala fdr #1. 10:00 Checked and found @1,@3 b/o fuse for 1000 Kva Tx (for chemical pump and compressor). Performed TTR and Megger test found Low megger reading. Cause: Tx failure (Low mega ohm reading). |  | 1 | 6:18 | Morning | Wednesday | 2018 | 8
7641 | 2018-08-01 09:50 | 2018-08-01 09:50 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Planned Maintenance | 0 | 09:50 Manually opened LBS.2F-15-1 d/s Duri Community Fdr #2 Replaced Pin Insulator o/p FL1-05A @1, @2 and LA @1, @2. 10:57 Manually closed LBS.2F-15-1. after replaced Pin Insulator o/p FL1-05A @1, @2 and LA @1, @2. Cause Plan Mantenance. |  | 1 | 9:50 | Morning | Wednesday | 2018 | 8
7642 | 2018-08-01 10:42 | 2018-08-01 10:42 | 13.8KV MINAS FEEDER #2 | Fair | Planned Maintenance | 15 | 10:42 Manually opened LBS.7D-96 and Closed LBS.7D-23 due to : Serviced recloser o/p 7D#20. 12:35 Manually Closed LBS.7D-96 and Opened LBS.7D-23 after finish Serviced recloser o/p 7D#20. Cause : Plan Maintenance. |  | 1 | 10:42 | Morning | Wednesday | 2018 | 8
7643 | 2018-08-01 11:00 | 2018-08-01 11:00 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Animal | 0 | 10:00 It was reported b/o fuse o/p 03-06-16B d/s CD Fdr #5. 13:52 Checked and found @2 b/o fuse for TX 300KVA Replaced b/o fuse aboved with same size and then energize the TX. Cause : Animal (Monkey).. |  | 1 | 11:00 | Morning | Wednesday | 2018 | 8
7644 | 2018-08-01 14:41 | 2018-08-01 14:41 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 91 | 14:41 Manually opened Recloser 9D-25 D/S 8C feeder #1 due to: 1. Changed out Transformer at well 9D-57. Tx: 550-550 Kva R/M: 450 Hp Sec Voltage: 2400 Volt. 15:50 Manually blocked and closed Recloser 9D-25. Cause: Plan Maintenance. |  | 1 | 14:41 | Afternoon | Wednesday | 2018 | 8
7645 | 2018-08-01 15:26 | 2018-08-01 15:26 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 92 | 15:26 Manually opened LBS:32-AJ-01 d/s Katigul fdr #1 due to : Adjusted voltage at well Tilan NE#01, S/B to VSD TX: 300 KVA, R/M:133 Hp, Sec. voltage : 480 Volt. 16:33 Manually closed LBS:32-AJ-01 Cause : Plan Maintenance. |  | 1 | 15:26 | Afternoon | Wednesday | 2018 | 8
7646 | 2018-09-01 09:36 | 2018-09-01 09:36 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Planned Maintenance | 61 | 09:36 Manually opened CD Fdr #9 due to : 1. Repl. dead end insulator @1, @2, @3 o/p.04-07-04, 04-07-09, 04-07-10. 2. C/O Transformer on pole 04-07-29. TX : 112.5Kva. 13:18 Manually blocked and closed CD Fdr #8 and then release the block. Cause : Plan Maintenance. |  | 1 | 9:36 | Morning | Saturday | 2018 | 9
7647 | 2018-09-01 10:57 | 2018-09-01 10:57 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 9 | 10:57 Manually opened recl.34-BI-18 d/s Sobek fdr #1 due to : Adjusted voltage at well Ampuh #23. TX: 150 KVA, R/M:63Hp-42Hp, Sec. voltage : 873-496Volt. 11:10 Manually blocke and closed recl.34-BI-18. then release the blocked. Cause : Plan Maintenance. |  | 1 | 10:57 | Morning | Saturday | 2018 | 9
7648 | 2018-09-01 13:23 | 2018-09-01 13:23 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 592 | 13:23 C.Duri ACB #11 ( Fdr #1 ) T/LO Counter : 208-211, R/F 51 @1, @2 and 51.G. 13:53 Checked and found @1, @2, @3 broken bushung of Recloser.41-AW-62. and @1 broken Pin Insulator o/p 41-AW-61. Dismantled all jumpers of Recloser 41-AW-62 and bypass the Recloser, Replaced @1 broken Pin Insulator o/p 41-AW-61. 15:48 Manually blocked and close C.Duri ACB #11 ( Fdr #1 ) and then release the block. Cause : Animal (Monkey). | 123 | 1 | 13:23 | Afternoon | Saturday | 2018 | 9
7649 | 2018-09-01 14:00 | 2018-09-01 14:00 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Construction Job | 0 | 14:00 Manually blocked Recloser 28-CX-05 d/s PTP Fdr #3 due to : Installed TX 300Kva at New well PTP #142 by opened disconnect switch N/N. Well were off: PTP #128, 129, 130, 131, 132, 133, 134. 17:06 Renormally blocked Recloser 28-CX-05. Cause : Job Construction. |  | 1 | 14:00 | Afternoon | Saturday | 2018 | 9
7650 | 2018-09-01 14:32 | 2018-09-01 14:32 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 6 | 14:32 Manually opened recl.445-BR-01, d/s Pungut Fdr #2 due to : Adjusted voltage at well Tandun #04. TX: 150 KVA, R/M:42 Hp, Sec. voltage : 460 Volt. 16:33 Manually blocked and closed recl.445-BR-01, then release the blocked. Cause : Plan Maintenance. |  | 1 | 14:32 | Afternoon | Saturday | 2018 | 9
7651 | 2018-09-01 15:35 | 2018-09-01 15:35 | 13.8KV 3D FEEDER #2 | Fair | Planned Maintenance | 10 | 15:35 Manually opened LBS.3E-64 d/s 3D Fdr #2 due to : Reactive well at 4D-57. Well were off : 3D-63, 3D-65N, 4D-49, 4D-58, 4D-59N, 4E-21R, 4E-23, 4E-41, 2F-71, 2F-82, 2F-82N, 2F-92, 2E-79. 16:30 Manually CLOSED lbs.3E-64. Cause : Plan Maintenance. |  | 1 | 15:35 | Afternoon | Saturday | 2018 | 9
7652 | 2018-09-01 16:10 | 2018-09-01 16:10 | 13.8KV PUNGUT FEEDER #1 | Fair | Planned Maintenance | 0 | 16:10 Manually opened Pungut Fdr #1 due to : External conection for replacing VSD to SB at well Pungut #46. Tx : 300Kva, R/M:73 Hp, Sec.Voltage : 800Volt. 16:29 Manually blocked and closed Pungut Fdr #1 and then release the block. Cause : Construction Job. (Requested by SPS Team). |  | 1 | 16:10 | Afternoon | Saturday | 2018 | 9
7653 | 2018-09-01 18:12 | 2018-09-01 18:12 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 81 | OKB Fdr #2 T/R 1x. Not checked yet. |  | 1 | 18:12 | Afternoon | Saturday | 2018 | 9
7654 | 2018-09-01 18:12 | 2018-11-01 20:12 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 81 | Checked & found OKB fdr#2 T/R 1x Ctr:1306-1307 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 18:12 | Afternoon | Saturday | 2018 | 9
7655 | 2018-10-01 08:07 | 2018-10-01 08:07 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 44 | 08:07 CKB Fdr #5 T/R 1x. CKB Fdr #6 Load drop 135A (161-26A). 11:30 Checked & found CKB VCB fdr#5 T/R 1x Ctr:158-159 R/F:51N @1. Patrolled the Line, but found nothing. Cause : Unidentified |  | 1 | 8:07 | Morning | Monday | 2018 | 10
7656 | 2018-10-01 14:06 | 2018-10-01 14:06 | 13.8KV 6DN FEEDER #6 | Fair | Planned Maintenance | 12 | 14:06 Opened HLC o/p 6D-154 to c/o @2 Pin Insulator at well 6D-74N (d/s 6DN Fdr #6) 15:36 Closed back the HLC after finished change the Pin above Cause Planned Maintenance. |  | 1 | 14:06 | Afternoon | Monday | 2018 | 10
7657 | 2018-10-01 16:08 | 2018-10-01 16:08 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified (Fuse) | 108 | It was reported b/o fuse o/p 13-F1-01F (d/s ND Fdr #11). Not Checked yet |  | 1 | 16:08 | Afternoon | Monday | 2018 | 10
7658 | 2018-10-01 16:08 | 2018-11-01 16:00 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified (Fuse) | 108 | Checked & found, @1 b/o Fuse for 112.5KVA Tx on Pole 13-F1-01. Replaced b/o Fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 16:08 | Afternoon | Monday | 2018 | 10
7659 | 2018-10-01 18:03 | 2018-10-01 18:03 | 13.8KV RANGAU FEEDER #2 | Cloudy | Broken Fuse Holder | 30 | Rangau fdr#2 Load dropped 102A (118-16A) Not checked yet. |  | 1 | 18:03 | Afternoon | Monday | 2018 | 10
7660 | 2018-10-01 18:03 | 2018-11-01 18:03 | 13.8KV RANGAU FEEDER #2 | Cloudy | Broken Fuse Holder | 30 | Checked & found, Recloser 23 BD 01 T/R ctr: 317-318. Patrolled the line & found, @2, @3 broken fuse link for 300KVA Tx at well Pelita #4. Replaced b/o fuses above then energized the Tx. Cause : Broken Fuse Holder |  | 1 | 18:03 | Afternoon | Monday | 2018 | 10
7661 | 2018-11-01 06:30 | 2018-11-01 06:30 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified (Fuse) | 16 | 06:30 It was reported b/o fuse at well Pelita #04 d/s Rangau Fdr #2. 11:15 Replaced Fuse TX:300 KVA @2. Cause : Unidentified. |  | 1 | 6:30 | Morning | Thursday | 2018 | 11
7662 | 2018-11-01 09:37 | 2018-11-01 09:37 | 13.8KV BEKASAP FEEDER #6 | Fair | Planned Maintenance | 40 | 09:37 Manually opened recloser.38-BE-10 d/s BKS #6 due to : Adjusted voltage at well Aman #05. 300 KVA TX, Voltage:1025 - 786 Volt, R/M:125-76Hp. 10:20 Manually blocked and closed recloser 30-BE-10 then release the block. Cause : Plan Maintenance. |  | 1 | 9:37 | Morning | Thursday | 2018 | 11
7663 | 2018-11-01 12:45 | 2018-11-01 12:45 | 13.8KV PUNGUT FEEDER #2 | Fair | Unidentified | 55 | 12:45 It was reported no power at well Ami #3, Asih #2, NAsih #2 & Gading #1,#2 (d/s Pungut Fdr #2) 16:40 Checked and found recl.44-BX-6 T/SO, R/F : 51G, Ctr:264-265. 17:00 Blocked & closed Recloser 44-BX-06, ok, then release the block. Cause : Unidentified. |  | 1 | 12:45 | Afternoon | Thursday | 2018 | 11
7664 | 2018-11-01 12:45 | 2018-12-01 12:45 | 13.8KV PUNGUT FEEDER #2 | Fair | Unidentified | 55 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 12:45 | Afternoon | Thursday | 2018 | 11
7665 | 2018-11-01 18:18 | 2018-11-01 18:18 | 13.8KV DURI FIELD FEEDER #4 | Drizzle | Lightning | 0 | Duri field 13.8KV ACB-51 fdr#4 T/R 1X. Not checked yet. |  | 1 | 18:18 | Afternoon | Thursday | 2018 | 11
7666 | 2018-11-01 18:18 | 16/01/2018 18:18 | 13.8KV DURI FIELD FEEDER #4 | Drizzle | Lightning | 0 | Checked & found, Duri Fields ACB #51 fdr #4 T/R 1x ctr: 512-513 R/F: 51N. Patrolled the line & found, @2 broken Lightning Arrester on Pole 07-U1-06. Cause: Lightning. |  | 1 | 18:18 | Afternoon | Thursday | 2018 | 11
7667 | 2018-11-01 22:08 | 2018-11-01 22:08 | 4.16KV NO RUMBAI FEEDER #1 | Cloudy | Lightning | 0 | N Rumbai 4.16 KV VCB #1 T/R 1x. Not checked yet. |  | 1 | 22:08 | Night | Thursday | 2018 | 11
7668 | 2018-11-01 22:08 | 18/01/2018 22:08 | 4.16KV NO RUMBAI FEEDER #1 | Cloudy | Lightning | 0 | Checked & found, North Rumbai VCB fdr #1 T/R 1x ctr: 407-408 R/F: 51N. Patrolled the line & found, @2 broken Dead end Insulator on Pole 2RD-5. Cause: Lightning. |  | 1 | 22:08 | Night | Thursday | 2018 | 11
7669 | 2018-12-01 09:40 | 2018-12-01 09:40 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 100 | 09:40 Manually opened Recl.34-CT-58 d/s CKB Fdr #5 due to : Replaced Switchboard to VSD at well KB #414, R/M:225 Hp. 11:56 Manually blocked and close Recl.34-CT-58 Then release the block. Cause : Contruction Job. |  | 1 | 9:40 | Morning | Saturday | 2018 | 12
7670 | 2018-12-01 09:45 | 2018-12-01 09:45 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 09:45 Manually opened Recl.27-AL-03 d/s Katigul Fdr #2 due to : Opened T-Type jumper o/p 25-AL-13, Near well UBI #10 to insolate Well UBI #10 for Drilling Job. 10:17 Manually blocked and close Recl.27-AL-03 then release the block. Cause : Job Construction. |  | 1 | 9:45 | Morning | Saturday | 2018 | 12
7671 | 2018-12-01 10:08 | 2018-12-01 10:08 | 13.8KV 6D FEEDER #2 | Fair | Planned Maintenance | 22 | 10:08 Manually opened Recl.6D-78 d/s 6D Fdr #2 due to : Installed TX 300KVA, R/M: 160Hp, Volt: 1170 Volt at well 6C-28. 10:30 Manually blocked and close Recl.6D-78 then release the block. Cause : Job Construction. |  | 1 | 10:08 | Morning | Saturday | 2018 | 12
7672 | 2018-12-01 13:26 | 2018-12-01 13:26 | 13.8KV RANGAU FEEDER #2 | Drizzle | Unidentified | 30 | 13:26 Rangau Fdr #2 Load dropped 100A (116-16). Cause : Not Checked Yet. |  | 1 | 13:26 | Afternoon | Saturday | 2018 | 12
7673 | 2018-12-01 13:26 | 13/01/2018 16:09 | 13.8KV RANGAU FEEDER #2 | Drizzle | Unidentified | 30 | 16:09 Checked & found Recl. 23-BD-01 Counter : 18-19, R/F: None Patrolled the Line found fishing rope hang up at @2 near well Pelita #4. Cause : Others. |  | 1 | 13:26 | Afternoon | Saturday | 2018 | 12
7674 | 2018-12-01 14:40 | 2018-12-01 14:40 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 231 | 09:40 Manually opened Recl.8D-18A d/s 8C Fdr #3 due to : Replaced Switchboard to VSD at well 8D #41E, TX.300KVA. 15:50 Manually blocked and close Recl.8D-18A Then release the block. Cause : Contruction Job. |  | 1 | 14:40 | Afternoon | Saturday | 2018 | 12
7675 | 2018-01-13 08:50 | 2018-01-13 08:50 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 419 | 08:50 It was reported b/o fuse at Benar #11 d/s Sintong Fdr #2. Cause : Not Checked yet. |  | 1 | 8:50 | Morning | Saturday | 2018 | 1
7676 | 2018-01-13 08:50 | 2018-01-14 10:00 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 419 | Checked & found, @1, @2 b/o Fuses for 150KVA Tx at well Benar #11. Replaced b/o Fuses above with the same size then energized the Tx. Cause: Animal. |  | 1 | 8:50 | Morning | Saturday | 2018 | 1
7677 | 2018-01-13 09:15 | 2018-01-13 09:15 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Pin Insulator | 0 | 09:15 Duri Community Fdr #5 T/R: 1X, R/F: ........ .Counter: ...... Cause : Not Checked yet. |  | 1 | 9:15 | Morning | Saturday | 2018 | 1
7678 | 2018-01-13 09:15 | 2018-01-18 09:15 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Pin Insulator | 0 | Checked and found Duri Community Fdr #5, Counter : 113 - 114, Relay Flag : 51N. Paterol the line founded Phase 1 Pin Insulator Flash over on Pole TP 18. Cause : Pin Insulator. |  | 1 | 9:15 | Morning | Saturday | 2018 | 1
7679 | 2018-01-14 14:25 | 2018-01-14 14:25 | 13.8KV NELLA FEEDER #2 | Fair | Planned Maintenance | 0 | 14:25 Manually opened Nella Fdr #2 due to : BKO GS - Maintain Level. Cause : Planned Maintenance. |  | 1 | 14:25 | Afternoon | Sunday | 2018 | 1
7680 | 2018-01-14 14:50 | 2018-01-14 14:50 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Animal | 142 | It was reported b/o fuse for Tx on pole 04-04-14 d/s C. Duri fdr #8. Not checked yet. |  | 1 | 14:50 | Afternoon | Sunday | 2018 | 1
7681 | 2018-01-14 14:50 | 2018-01-16 14:30 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Animal | 142 | Checked & found @3 b/o Fuse for 112.5KVATX o/p 04-04-14 (d/s CD fdr#8) Replaced the Fuse with the same size, the Energized the TX. Patrolled the Line, found Animal (Monkey) near the TX Pole. Cause : Animal (Monkey) |  | 1 | 14:50 | Afternoon | Sunday | 2018 | 1
7682 | 2018-01-15 10:00 | 2018-01-15 10:00 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 9 | It was reported B/O Fuse o/p 09-T1-03 (CD fdr#4) Not checked yet (Not Exist on drawing) |  | 1 | 10:00 | Morning | Monday | 2018 | 1
7683 | 2018-01-15 10:00 | 2018-01-16 15:00 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 9 | Checked & found @2 b/o fuse for 112.5KVATX o/p 09-T1-03 (d/s CD fdr#4) Replaced the fuse with the same size, then energized the TX. Patrolled the Line, but found nothing Cause: Unidentified (Fuse) |  | 1 | 10:00 | Morning | Monday | 2018 | 1
7684 | 2018-01-16 07:00 | 2018-01-16 07:00 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | 511 | 07:00 Minas ACB #2 (feeder #3) T/LO ctr:132-135 R/F: 51 @1, @2. Minas fdr #4 load dropped 152A (196-44 A). Minas fdr #6 load dropped 125A (165-40 A). Patrolled the line but found nothing. 08:28 Blocked and closed Minas ACB fdr #3, but tripped again ctr:132-135 R/F: 51 @1, @2 & @3. 10:20 Manually Open Recloser 7D-93, -----> Closed at 10:40. 10:20 Manually Open Recloser 7D-81, -----> Closed at 10:33. 10:30 Blocked and closed Minas ACB fdr #3, OK then released the block. Cause: Unidentified. | 123 | 1 | 7:00 | Morning | Tuesday | 2018 | 1
7685 | 2018-01-16 08:28 | 2018-01-16 08:28 | EAST RUMBAI SUBSTATION | Fair | Under investigation | 0 | 08:28 East Rumbai 44KV OCB S/C T/O. (No power to Eats Rumbai fdr #1, #2 and #3). 09:24 Checked and found East Rumbai 44KV OCB S/C T/O ctr:35-36 R/F: 24 and 86. 09:28 Closed East Rumbai 44KV OCB S/C. Manually Open East Rumbai fdr #1, ------> Closed at 09:30. Manually Open East Rumbai fdr #2, ------> Closed at 09:30. Manually Open East Rumbai fdr #3, ------> Closed at 09:30. Cause: Under investigation. |  | 1 | 8:28 | Morning | Tuesday | 2018 | 1
7686 | 2018-01-16 09:17 | 2018-01-16 09:17 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 12 | Minas ACB fdr#2 T/R 1x. Ctr: 72-73, R/F: 51N. Not checked yet. |  | 1 | 9:17 | Morning | Tuesday | 2018 | 1
7687 | 2018-01-16 09:17 | 2018-01-18 09:17 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 12 | Checked & found, Minas ACB #13 fdr #2 T/R 1x ctr: 71-72 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:17 | Morning | Tuesday | 2018 | 1
7688 | 2018-01-16 10:30 | 2018-01-16 10:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 0 | 10:30 Opened LBS 31 AN 32C (d/s Ketigul fdr#2) to Replaced 6pcs @1 @2 Dead End insulator o/p 29 AL 01 and Repair LBS o/p No Name. 13:30 Closed the LBS above, after finished the jobs. Cause: Planned maintenance |  | 1 | 10:30 | Morning | Tuesday | 2018 | 1
7689 | 2018-01-16 15:00 | 2018-01-16 15:00 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Planned Maintenance | 80 | 15:00 Manually Opened New Petapahan VCB fdr#6 to Replace 300KVATX at Well PTH#07. 15:30 Manually Block & Closed New Petapahan VCB fdr#6 after Finished the Jobs above. Cause: Planned Maintenance. |  | 1 | 15:00 | Afternoon | Tuesday | 2018 | 1
7690 | 2018-01-16 20:33 | 2018-01-16 20:33 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 16 | 20:33 So Balam fdr #1 load dropped 14A (113-99 A). So Balam fdr #4 load dropped 24A (189-165 A). So Balam GFPC T/R 1x (fault alarm on So Balam fdr #1). 22:45 Checked and found Recloser: 17-Z-01 T/SO Counter: 58-59. Patrolled the line found Owl (burung hantu) hang on Recloser: 17-Z-01. Manually blocked and closed Recloser: 17-Z-01 Ok and then released the block. Cause: Animal (Owl ). |  | 1 | 20:33 | Night | Tuesday | 2018 | 1
7691 | 2018-01-17 06:39 | 2018-01-17 06:39 | 13.8KV 8C FEEDER #5 | Cloudy | Lightning | 0 | 8C VCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 6:39 | Morning | Wednesday | 2018 | 1
7692 | 2018-01-17 06:39 | 2018-01-18 06:39 | 13.8KV 8C FEEDER #5 | Cloudy | Lightning | 0 | Checked & found, 8C VCB fdr #5 T/R 1x ctr: 500-501 R/F: 50N Patrolled the line & found, @3 Flash over Pin Insulator on Pole 8D-247. Cause: Lightning. |  | 1 | 6:39 | Morning | Wednesday | 2018 | 1
7693 | 2018-01-17 06:49 | 2018-01-17 06:49 | 13.8KV NORTH DURI FEEDER #6 | Cloudy | Unidentified | 0 | N Duri VCB fdr #6 T/R 1x. Not checked yet. |  | 1 | 6:49 | Morning | Wednesday | 2018 | 1
7694 | 2018-01-17 06:49 | 2018-01-24 08:00 | 13.8KV NORTH DURI FEEDER #6 | Cloudy | Unidentified | 0 | North Duri fdr #6 T/R 1x R/F: @2 51 Ctr: 297-298 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:49 | Morning | Wednesday | 2018 | 1
7695 | 2018-01-17 08:37 | 2018-01-17 08:37 | CENTRAL DURI POWER PLANT |  |  | - | 08:37 S/U CGT #5 and On line to system at 09:02. (Replaced CGT #4 will be S/D for Certification of Gas Scrubber PSV). |  | 1 | 8:37 | Morning | Wednesday | 2018 | 1
7696 | 2018-01-17 09:18 | 2018-01-17 09:18 | CENTRAL DURI POWER PLANT |  |  | - | Off Line CGT #4 and S/D at 09:19 for Gas Scrubber PSV Certification. |  | 1 | 9:18 | Morning | Wednesday | 2018 | 1
7697 | 2018-01-17 10:54 | 2018-01-17 10:54 | 13.8KV PETANI FEEDER #2 | Fair | Planned Maintenance | 78 | 10:54 Manually Open 13.8KV Petani OCB fdr #2. Replaced 150Kva to 300Kva TX at well Petani #55. 11:56 Closed 13.8KV Petani OCB fdr #2. Cause: Plan Maintenance. |  | 1 | 10:54 | Morning | Wednesday | 2018 | 1
7698 | 2018-01-17 11:03 | 2018-01-17 11:03 | 13.8KV 6D FEEDER #5 | Fair | Construction Job | 0 | 11:03 Manually Opened Rcl 5D-10 (d/s 6D fdr#5) to Install 150KVATX at Well 5D25. 12:00 Manually Block & Closed the Recloser above after finished the Jobs. Cause: Planned Construction (Reactive Well) |  | 1 | 11:03 | Morning | Wednesday | 2018 | 1
7699 | 2018-01-17 11:07 | 2018-01-17 11:07 | 13.8KV DURI FIELD FEEDER #3 | Fair | Planned Maintenance | 6 | 11:07 It was reported Broken Scondary cable o/p 01 07 27. 11:25 Checked and found @2 broken Scondary cable for 112.5Kva TX. (Not replaced yet). |  | 1 | 11:07 | Morning | Wednesday | 2018 | 1
7700 | 2018-01-17 11:07 | 2018-01-19 11:05 | 13.8KV DURI FIELD FEEDER #3 | Fair | Planned Maintenance | 6 | Repaired Hot Spot o/p 01 07 27. Plan Maintenance. |  | 1 | 11:07 | Morning | Wednesday | 2018 | 1
7701 | 2018-01-17 19:43 | 2018-01-17 19:43 | MINAS POWER PLANT |  |  | - | 19:43 MGT #4 Start Up then Online to system at 20:20 For Running test after M.O. |  | 1 | 19:43 | Night | Wednesday | 2018 | 1
7702 | 2018-01-18 09:25 | 2018-01-18 09:25 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 42 | 09:25 It was reported b/o fuse o/p 04 01 19. Not checked yet. |  | 1 | 9:25 | Morning | Thursday | 2018 | 1
7703 | 2018-01-18 09:25 | 2018-01-19 10:31 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 42 | 10:31 Checked and found @1, @2 b/o fuse for 112.5Kva TX. Replaced the b/o fuse above with same size, then energized the TX. OK. Cause: Un identified fuse. |  | 1 | 9:25 | Morning | Thursday | 2018 | 1
7704 | 2018-01-18 10:00 | 2018-01-18 10:00 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 0 | 10:00 Manually Open Recloser 7E-67A. Repair Hot Spot at Recl. 6E-23A. Cause: Plan Maintenance. |  | 1 | 10:00 | Morning | Thursday | 2018 | 1
7705 | 2018-01-18 10:14 | 2018-01-18 10:14 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 0 | 10:14 Manually Open Recl. 46 PB 12, -----> Closed at 10:35. Adjusted voltage for 100Kva TX at well INTAN # 003. Cause: Plan Maintenance. |  | 1 | 10:14 | Morning | Thursday | 2018 | 1
7706 | 2018-01-18 10:25 | 2018-01-18 10:25 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Planned Maintenance | 0 | 10:25 Manually Open LBS 34 CT 68, -----> Closed at 10:56. Rmoved TX for LTC wells at KB #416 and KB # 398. Cause: Plan Maintenance. |  | 1 | 10:25 | Morning | Thursday | 2018 | 1
7707 | 2018-01-18 14:24 | 2018-01-18 14:24 | MINAS POWER PLANT |  |  | - | 14:24 S/U MGT #4 and On line to system at 15:00. (Running test ). |  | 1 | 14:24 | Afternoon | Thursday | 2018 | 1
7708 | 2018-01-18 14:43 | 2018-01-18 14:43 | 13.8KV MENGGALA FEEDER #1 | Heavy Rain | Pin Insulator | 114 | 14:43 Menggala 13.8KV OCB fdr #1 T/LO. 15:15 Checked and found Menggala 13.8KV OCB fdr #1 T/LO ctr: 314-318 R/F:51N. 16:15 Patrolled the line, bun found nothing. Blocked and closed Menggala fdr #1, tripped again. 17:10 Open By Pass recloser 19 AN 04. 17:15 Blocked and closed Menggala fdr #1, OK. Patrolled the line and found @2 Pin Support at Menu #13 broken then Replaceed. 19:06 Manually Opened Manggala Fdr #1 to By Pass Recloser 19-AN-04 to closed 19:10 Manually blocked and closed Manggala Fdr #1 then release the block. Cause : Pin Support. |  | 1 | 14:43 | Afternoon | Thursday | 2018 | 1
7709 | 2018-01-18 17:30 | 2018-01-18 17:30 | MINAS POWER PLANT |  |  | - | Off Line MGT #3 and S/D at 17:31 for Standby. |  | 1 | 17:30 | Afternoon | Thursday | 2018 | 1
7710 | 2018-01-19 09:30 | 2018-01-19 09:30 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 106 | 09:30 Open Recloser 36 BI 04. d/s S.Bekasap fdr #1. Replaced TX at Pudu #17. 11:07 Closed Recloser 36 BI 04. d/s S.Bekasap fdr #1. Cause:Planned maintenance. |  | 1 | 9:30 | Morning | Friday | 2018 | 1
7711 | 2018-01-19 10:00 | 2018-01-19 10:00 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified (Fuse) | 0 | Replaced @2 b/o fuse 112.5 KVA TX o/p 09 N4 08 d/s C,Duri fdr #16. Cause:Unidentified fuse. |  | 1 | 10:00 | Morning | Friday | 2018 | 1
7712 | 2018-01-19 10:35 | 2018-01-19 10:35 | 13.8KV BATANG FEEDER #2 | Fair | Planned Maintenance | 0 | 10:35 Opened FCO for 500 KVA TX at well Rantau Bais #14 (d/s Batang fdr #2). to Replaced secondary cable. 11:00 Closed the fuse after finished the job. Cause: Planned Maintenance |  | 1 | 10:35 | Morning | Friday | 2018 | 1
7713 | 2018-01-19 11:00 | 2018-01-19 11:00 | 13.8KV DURI FIELD FEEDER #3 | Fair | Animal | 110 | 11:00 It was reported b/o fuse o/p 01-07-23 (d/s D.field fdr #3). Checked and found @2 b/o fuse for 112.5 KVATX. 15:14 Replaced b/o fuse above with the same size then energized the TX. Cause: Animal (Squirrel) |  | 1 | 11:00 | Morning | Friday | 2018 | 1
7714 | 2018-01-19 11:15 | 2018-01-19 11:15 | 13.8KV BATANG FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 11:15 Checked & found @1,@2,@3 b/o fuse for 150 KVA TX at well Rantau Bais #57 (d/s Batang fdr #2). Replaced fuse with the same size, the energized the Cause :Un Identified fuse. |  | 1 | 11:15 | Morning | Friday | 2018 | 1
7715 | 2018-01-19 15:25 | 2018-01-19 15:25 | 13.8KV DURI FIELD FEEDER #3 | Fair | Animal | 7 | 15:25 It was reported b/o fuse o/p 01-9-20 (d/s D.Field fdr #3). Checked and found @2 b/o fuse for 112.5 KVA TX. 15:25 Replaced b/o fuse above with same size then energize the TX. Cause: Animal (Squirrel). |  | 1 | 15:25 | Afternoon | Friday | 2018 | 1
7716 | 2018-01-19 17:33 | 2018-01-19 17:33 | CENTRAL DURI POWER PLANT |  |  | - | 17:33 S/U CDGT #4 and online at 18:02. |  | 1 | 17:33 | Afternoon | Friday | 2018 | 1
7717 | 2018-01-19 18:18 | 2018-01-19 18:18 | CENTRAL DURI POWER PLANT |  |  | - | 18:18 Off line CDGT #5 and then S/D at 18:19. |  | 1 | 18:18 | Afternoon | Friday | 2018 | 1
7718 | 2018-01-20 08:20 | 2018-01-20 08:20 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Animal | 0 | 08:20 NKBS 13.8 KV fdr #3 T/R 1X. NKBS GFPC T/R 1X. Not checked yet. |  | 1 | 8:20 | Morning | Saturday | 2018 | 1
7719 | 2018-01-20 08:20 | 2018-01-21 08:00 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Animal | 0 | 08:00 Checked & found NKBS fdr #3 T/R 1X , ctr:315-316 . relay flag:51@1. Patrolled the line and found deat animal (squirrel) at Kotabatak#08. Cause:Animal (squirrel ). |  | 1 | 8:20 | Morning | Saturday | 2018 | 1
7720 | 2018-01-20 17:14 | 2018-01-20 17:14 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 0 | 17:14 Ketigul 13.8KV fdr#2 T/LO. Ctr: 258-264, R/F: 51N and Katigul GFPC T/R. Patrolled the line until LBS.29-AL-07 but found nothing. 19:35 Manually open LBS.29-AL-07 to splite the problem. 20:01 Manually blocked and close Katigul Fdr #2 from DSC but fail, Manually Block & Close from Local ok, then released the block. Patrolled the line from Manggala Fdr#2 and found The Monkey hung out o/p 29-AL-04. 21:40 Manually closed LBS.29-AL-07, after dismantle the monkey. Cause : Animal (Monkey). |  | 1 | 17:14 | Afternoon | Saturday | 2018 | 1
7721 | 2018-01-21 09:00 | 2018-01-21 09:00 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 0 | 09:00 O/C Recl 22-V-01 D/S Nella fdr#1. Replaced LA TO/P BKO# 170 & BKO#70. Replaced Pin Insulator at BKO#13. Cause : Plain Maintenance. |  | 1 | 9:00 | Morning | Sunday | 2018 | 1
7722 | 2018-01-22 09:45 | 2018-01-22 09:45 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Planned Maintenance | 309 | 09:45 Manually Open Petapahan VCB fdr #3. Dismantled Switch Board and TX at well PH-78 (LTC well). C/O VSD to Switch Board at wells PH-132 and PH-077. Cause: Plan Maintnance. |  | 1 | 9:45 | Morning | Monday | 2018 | 1
7723 | 2018-01-22 10:40 | 2018-01-22 10:40 | MINAS POWER PLANT |  |  | - | 10:40 Off line & S/D MGT#6 of S/B. |  | 1 | 10:40 | Morning | Monday | 2018 | 1
7724 | 2018-01-22 10:43 | 2018-01-22 10:43 | 13.8KV 5B FEEDER #8 | Fair | Planned Maintenance | 0 | 10:43 Open LBS 5C-107. Repaired Hot Spot Of TX-1 and TX-2 at GS-4. 11:39 Manually Open 5B fdr#3 Maintenance level Tank. 13:30 Manually Open 4D fdr#4 Maintenance level Tank. Cause: Plan Maintenance. |  | 1 | 10:43 | Morning | Monday | 2018 | 1
7725 | 2018-01-22 10:48 | 2018-01-22 10:48 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 0 | 10:48 Open Recloser 22 V 06. Replaced LA TO/P BKO # 287. Cause: Plan Maintenance. |  | 1 | 10:48 | Morning | Monday | 2018 | 1
7726 | 2018-01-22 11:39 | 2018-01-22 11:39 | 13.8KV 5B FEEDER #3 | Fair | Planned Maintenance | 93 | 11:39 Manually Open 5B fdr#3 Maintenance level Tank. Cause: Plan Maintenance |  | 1 | 11:39 | Morning | Monday | 2018 | 1
7727 | 2018-01-22 12:39 | 2018-01-22 12:39 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 0 | 12:39 Manually Open LBS 32 AK 02 D/S Ketigul fdr#1. Replaced Reclose 32 AK 04 Cuase: Plan maintenance. |  | 1 | 12:39 | Afternoon | Monday | 2018 | 1
7728 | 2018-01-22 13:30 | 2018-01-22 13:30 | 13.8KV 4D FEEDER #4 | Fair | Planned Maintenance | 273 | 13:30 Manually Open 4D fdr#4 Maintenance level Tank. Cause: Plan Maintenance |  | 1 | 13:30 | Afternoon | Monday | 2018 | 1
7729 | 2018-01-22 14:40 | 2018-01-22 14:40 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 73 | 14:40 Manually Open 8C fdr#3 Replaced TX at 8D-38E Cause: Plan Maintenance. |  | 1 | 14:40 | Afternoon | Monday | 2018 | 1
7730 | 2018-01-22 14:44 | 2018-01-22 14:44 | 13.8KV 6D FEEDER #2 | Fair | Planned Maintenance | 0 | 14:44 Manually Open Recl 6D-78A D/S 6D fdr#2. Replaced TX To VSD at well 6C-29. Cause: Plan Maintenance. |  | 1 | 14:44 | Afternoon | Monday | 2018 | 1
7731 | 2018-01-23 07:57 | 2018-01-23 07:57 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri ACB fdr#16 T/R 1x Ctr:307-308 R/F:51@1@2. Not patrolled yet. |  | 1 | 7:57 | Morning | Tuesday | 2018 | 1
7732 | 2018-01-23 07:57 | 2018-01-26 08:00 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked and found C. Duri fdr #16 T/R 1x R/F: @1, @2 51 Ctr: 307-308. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:57 | Morning | Tuesday | 2018 | 1
7733 | 2018-01-23 10:56 | 2018-01-23 10:56 | MINAS POWER PLANT |  |  | - | 10:56 S/U MGT#3, tene on line the unit at 11:24. |  | 1 | 10:56 | Morning | Tuesday | 2018 | 1
7734 | 2018-01-23 10:57 | 2018-01-23 10:57 | PUNGUT SUBSTATION | Fair | Planned Maintenance | 710 | 10:57 Manually Open Pungut VCB fdr #2. Closed at 15:50 11:01 Manually Open Pungut VCB fdr #1. Closed at 15:50 11:09 Manually Open 115Kv Pungut OCB-22. Tie in 13.8KV MSU fdr #1 & #2. Cause: Contruction JOB. | 1234 | 1 | 10:57 | Morning | Tuesday | 2018 | 1
7735 | 2018-01-23 11:24 | 2018-01-23 11:24 | MINAS POWER PLANT |  |  | - | Off line MGT#4, then S/D the unit for Maintenance. |  | 1 | 11:24 | Morning | Tuesday | 2018 | 1
7736 | 2018-01-23 16:36 | 2018-01-23 16:36 | 13.8KV BANGKO FEEDER #2 | Fair | Lightning Arrester | 0 | Bangko VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 16:36 | Afternoon | Tuesday | 2018 | 1
7737 | 2018-01-23 16:36 | 2018-01-25 08:00 | 13.8KV BANGKO FEEDER #2 | Fair | Lightning Arrester | 0 | Checked and found Bangko Fdr #2 T/R 1x R/F: None Ctr: 99958-99959. Patrolled the line and found broken Lightning Arrester @3 o/p LBS 4. Cause: Lightning Arrester. |  | 1 | 16:36 | Afternoon | Tuesday | 2018 | 1
7738 | 2018-01-23 16:36 | 2018-01-23 16:36 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning Arrester | 0 | 16:36 Bangko VCB fdr#4 T/LO. 16:53 Checked & found Bangko VCb fdr#4 T/LO Ctr:23-27 R/F:51@1@2@3. 17:45 Patrolled the line & found @1@2@3 Broken LA on T/P Bangko#271. 17:57 Blocked &Closed Bangko VCB fdr#4, then release the block. Cause: Lightning Aresster. |  | 1 | 16:36 | Afternoon | Tuesday | 2018 | 1
7739 | 2018-01-23 19:20 | 2018-01-23 19:20 | 13.8KV KOTABATAK FEEDER #2 | Fair | Lightning Arrester | 57 | 19:20 OKB 13.8KV OCB#2 T/R. 20:02 OKB 13.8KV OCB#2 T/R. Not checked yet. |  | 1 | 19:20 | Night | Tuesday | 2018 | 1
7740 | 2018-01-23 19:20 | 2018-01-25 08:00 | 13.8KV KOTABATAK FEEDER #2 | Fair | Lightning Arrester | 57 | Checked and found OKB Fdr #2 T/R 2x R/F: @3 51N Ctr: 1307-1309. Patrolled the line and found broken Lightning Arrester o/p 38-CX-05. Cause: Lightning Arrester. |  | 1 | 19:20 | Night | Tuesday | 2018 | 1
7741 | 2018-01-24 09:32 | 2018-01-24 09:32 | 13.8KV NORTH DURI FEEDER #7 | Fair | Secondary Cable | 80 | It was reported b/o fuse for Tx on pole 10-K2-12 D/S N Duri fdr #7. Not checked yet. |  | 1 | 9:32 | Morning | Wednesday | 2018 | 1
7742 | 2018-01-24 09:32 | 2018-01-27 10:35 | 13.8KV NORTH DURI FEEDER #7 | Fair | Secondary Cable | 80 | Checked and found the secondary cable was found missing. Replaced secondary cable and energized the Tx. Cause: Secondary cable. |  | 1 | 9:32 | Morning | Wednesday | 2018 | 1
7743 | 2018-01-24 09:32 | 2018-01-24 09:32 | 13.8KV NORTH DURI FEEDER #7 | Fair | Secondary Cable | 79 | It was reported b/o fuse for Tx on pole 10-K2-27 D/S N Duri fdr #7. Not checked yet. |  | 1 | 9:32 | Morning | Wednesday | 2018 | 1
7744 | 2018-01-24 09:32 | 2018-01-27 10:35 | 13.8KV NORTH DURI FEEDER #7 | Fair | Secondary Cable | 79 | Checked and found the secondary cable was found missing. Replaced secondary cable and energized the Tx. Cause: Secondary cable. |  | 1 | 9:32 | Morning | Wednesday | 2018 | 1
7745 | 2018-01-24 14:47 | 2018-01-24 14:47 | 13.8KV NELLA FEEDER #1 | Cloudy | Lightning | 105 | 14:47 Nella VCB fdr #1 T/R 1x. 14:49 Nella VCB fdr #1 T/R 1x. Nella GFPC T/R 2x. Not checked yet. |  | 1 | 14:47 | Afternoon | Wednesday | 2018 | 1
7746 | 2018-01-24 14:47 | 2018-01-27 17:51 | 13.8KV NELLA FEEDER #1 | Cloudy | Lightning | 105 | Checked and found Nella VCB fdr #1 T/R 3x Counter: 513-516 R/F: 51N. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 14:47 | Afternoon | Wednesday | 2018 | 1
7747 | 2018-01-25 23:59 | / | CPI POWER SYSTEM | Fair | Normal Condition | - | - |  | 1 | 23:59 | Night | Thursday | 2018 | 1
7748 | 2018-01-26 09:45 | 2018-01-26 09:45 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 4 | 09:45 It was reported b/o fuse on pole 03-07-05 D/S C Duri fdr #7. 15:15 Replaced @1@2 B/O fuse for 112.5Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 9:45 | Morning | Friday | 2018 | 1
7749 | 2018-01-26 14:00 | 2018-01-26 14:00 | MINAS POWER PLANT |  |  | - | 14:00 S/U MGT#5, then on line the unit at 14:14. 14:40 Closed Tie breaker ACB#8. 14:44 Opened Tie breaker ACB#16. |  | 1 | 14:00 | Afternoon | Friday | 2018 | 1
7750 | 2018-01-26 15:10 | 2018-01-26 15:10 | MINAS POWER PLANT |  |  | - | 15:10 S/U MGT#5, then on line the unit at 15:23. |  | 1 | 15:10 | Afternoon | Friday | 2018 | 1
7751 | 2018-01-26 15:32 | 2018-01-26 15:32 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 15:32 Manually Opened LBS.27AL03 (Ketigul fdr#2). Tie In New well UBI#42. 16:30 Manually Closed LBS.27AL03. Cause: Construction Job. |  | 1 | 15:32 | Afternoon | Friday | 2018 | 1
7752 | 2018-01-26 15:38 | 2018-01-26 15:38 | MINAS POWER PLANT |  |  | - | Off line MGT#6, then S/D the unit for Maintenance. |  | 1 | 15:38 | Afternoon | Friday | 2018 | 1
7753 | 2018-01-26 17:29 | 2018-01-26 17:29 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 9 | It was reported B/O fuse o/p 05-P3-11 (C.Duri fdr#14). Not checked yet. |  | 1 | 17:29 | Afternoon | Friday | 2018 | 1
7754 | 2018-01-26 17:29 | 2018-01-27 14:50 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 9 | Replaced @1@2@3 B/O fuse for 112.5Kva Tx with the same size. Cause: Animal (Monkey). |  | 1 | 17:29 | Afternoon | Friday | 2018 | 1
7755 | 2018-01-26 18:55 | 2018-01-26 18:55 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 39 | OKB fdr #2 load dropped 118A 9 (244 - 126A) Not checked yet. |  | 1 | 18:55 | Afternoon | Friday | 2018 | 1
7756 | 2018-01-26 18:55 | 2018-01-29 07:00 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 39 | Checked & found Recl. 38-CW-08 T/R 1x Ctr:88-89. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 18:55 | Afternoon | Friday | 2018 | 1
7757 | 2018-01-26 22:40 | 2018-01-26 22:40 | 13.8KV 8C FEEDER #3 | Fair | Others | 211 | 22:40 8C fdr #3 load dropped 141A (202 - 61A) 23:30 It was reported explosive sound around 8c-48E. 01:02 Checked and found Recl. 8D-18A T/SO ctr:47-48. Patrolled the line and found a Kite hang on power line around 8D-29. Blocked and closed the Recl. Ok the released the block. Cause: Other (Kite). |  | 1 | 22:40 | Night | Friday | 2018 | 1
7758 | 2018-01-27 09:35 | 2018-01-27 09:35 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Recloser | 69 | 09:35 It was reported no power at road M 5 & M 6 at Area #8 D/S C Duri ACB fdr #2. 10:50 Checked and found Recloser:08-M5-13 T/SO Counter: 57-58. Manually blocked and closed Recloser:08-M5-13 but failed (Suspect Recloser fail) 11:16 Manually opened C Duri ACB fdr #2 due to: - By pass Recloser:08-M5-13. 11:18 Manually blocked and closed C Duri ACB fdr#2 and then released the block. Cause: Recloser. |  | 1 | 9:35 | Morning | Saturday | 2018 | 1
7759 | 2018-01-27 10:36 | 2018-01-27 10:36 | 13.8KV 8D FEEDER #3 | Fair | Construction Job | 0 | 10:36 Manually opened 8D OCB fdr #3 due to: - Install 225 Kva at well 8D-76 (reactive well). 11:07 Manually blocked and closed 8D OCB fdr #3 and then released the block. Cause: Construction Job. |  | 1 | 10:36 | Morning | Saturday | 2018 | 1
7760 | 2018-01-27 11:30 | 2018-01-27 11:30 | 13.8KV SINTONG FEEDER #2 | Fair | Transformer Failure | 82 | 11:30 It was reported b/o fuse at well Benar #36 D/S Sintong fdr #2. 14:10 Checked and found @3 b/o fuse for 150 Kva Tx. Perform TTR and megger found Low megger reading. Cause: Tx failure (Low mega ohm reading). This Tx is not replaced yet. |  | 1 | 11:30 | Morning | Saturday | 2018 | 1
7761 | 2018-01-27 11:30 | 2018-01-28 10:22 | 13.8KV SINTONG FEEDER #2 | Fair | Transformer Failure | 82 | Replaced 150 Kva Tx failure with 150 Kva Tx. And energized the Transformer. Cause: Tx failure. |  | 1 | 11:30 | Morning | Saturday | 2018 | 1
7762 | 2018-01-27 16:41 | 2018-01-27 16:41 | 13.8KV 8D FEEDER #2 | Fair | Construction Job | 0 | 16:41 Manually opened 8D OCB fdr #2 due to: - Install 300 Kva at well 8D-26 (reactive well). 17:41 Manually blocked and closed 8D OCB fdr #2 and then released the block. Cause: Construction Job. |  | 1 | 16:41 | Afternoon | Saturday | 2018 | 1
7763 | 2018-01-27 17:34 | 2018-01-27 17:34 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Lightning Arrester | 102 | Pematang Main 44 KV OCB #1 (To Petani) T/R 1x. Not checked yet. |  | 1 | 17:34 | Afternoon | Saturday | 2018 | 1
7764 | 2018-01-27 17:34 | 2018-01-30 17:34 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Lightning Arrester | 102 | Checked & found, 44 KV Pematang Main OCB #1 T/R 1x ctr: 4007-4008 R/F: 50N. (44KV Pematang Main-Petani Line) Patrolled the line & found @1 broken Lightning Arrester on Pole PTN #05. Cause: Lightning Arrester. |  | 1 | 17:34 | Afternoon | Saturday | 2018 | 1
7765 | 2018-01-28 09:30 | 2018-01-28 09:30 | 13.8KV 5B FEEDER #1 | Fair | Planned Maintenance | 241 | 09:30 Manually opened 5B OCB fdr #1 due to : 1. Squeezed jumpers on pole 5C-171. 2. Replaced Recloser on pole 5B-06. 12:33 Manually blocked and closed 5B OCB fdr #1 and then released the block. Cause: Plan Maintenance. |  | 1 | 9:30 | Morning | Sunday | 2018 | 1
7766 | 2018-01-28 10:02 | 2018-01-28 10:02 | 13.8KV 4B FEEDER #1 | Fair | Lightning Arrester | 0 | 4B fdr#1 Load dropped 211A (274-63A). 4B fdr#2 Load dropped 45A (89-44A). 4B fdr#3 Load dropped 236A (244-8A)(Pump off). Not checked yet. |  | 1 | 10:02 | Morning | Sunday | 2018 | 1
7767 | 2018-01-28 10:02 | 2018-01-29 16:50 | 13.8KV 4B FEEDER #1 | Fair | Lightning Arrester | 0 | 14:05 Checked and found Recloser 4B-101 T/LO Counter: 614-619. Patrolled the line found @1 and @2 broken Lightning Arrester on Recloser 4B-101. Replaced broken Lightning Arrester above. 16:50 Manually blocked and closed Recloser 4B-101 --> Ok and then released the block. Cause: Broken Lightning Arrester. |  | 1 | 10:02 | Morning | Sunday | 2018 | 1
7768 | 2018-01-29 06:49 | 2018-01-29 06:49 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Animal | 0 | C.Duri ACB fdr#1 T/R 1x Ctr:211-212 R/F:51N. Not patrolled yet. |  | 1 | 6:49 | Morning | Monday | 2018 | 1
7769 | 2018-01-29 06:49 | 2018-01-30 06:49 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Animal | 0 | Checked & found, Central Duri ACB #11 fdr #1 T/R 1x ctr: 211-212 R/F: 51 @2. Patrolled the line & found dead bird around Pole 40 AW 17. Cause : Animal |  | 1 | 6:49 | Morning | Monday | 2018 | 1
7770 | 2018-01-29 14:52 | 2018-01-29 14:52 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 14:52 It was reported b/o fuse at well Kulim #53 D/S C Duri Fdr #1. 16:46 Checked and found @2 b/o fuse for 75 Kva Tx. Replaced b/o fuse above and then energized the Tx. Cause: Unidentified (fuse). |  | 1 | 14:52 | Afternoon | Monday | 2018 | 1
7771 | 2018-01-29 16:44 | 2018-01-29 16:44 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Sintong fdr #2 load dropped 16A (221-205). Sintong GFPC T/R 1x , fault alarm on Sintong fdr #2. Not checked yet. |  | 1 | 16:44 | Afternoon | Monday | 2018 | 1
7772 | 2018-01-29 21:59 | 2018-01-29 21:59 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Unidentified (Fuse) | 21 | 21:59 It was reported b/o fuse at well PTP #032 d/s PTP fdr #6. Not checked yet. |  | 1 | 21:59 | Night | Monday | 2018 | 1
7773 | 2018-01-29 21:59 | 2018-01-30 08:30 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Unidentified (Fuse) | 21 | Checked & found, @1, @2 b/o fuses for 350KVA Tx at Well Petapahan #32. Replaced b/o Fuses above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 21:59 | Night | Monday | 2018 | 1
7774 | 2018-01-30 07:09 | 2018-01-30 07:09 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 0 | Petani OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 7:09 | Morning | Tuesday | 2018 | 1
7775 | 2018-01-30 07:09 | 2018-01-31 07:09 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Petani OCB fdr #2 T/R 1x ctr: 239-240 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:09 | Morning | Tuesday | 2018 | 1
7776 | 2018-01-30 07:16 | 2018-01-30 07:16 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Dead End Insulator | 0 | 07:16 C Duri ACB #11 (feeder #1) T/R 3x Counter: 212-215 R/F: 51@3 , 51N. 16:00 Patrolled the line & found @2 Flashed over Dead End Insulator o/p 40AW16. Cause : Dead End Insulator. |  | 1 | 7:16 | Morning | Tuesday | 2018 | 1
7777 | 2018-01-30 12:18 | 2018-01-30 12:18 | 13.8KV PINANG FEEDER #1 | Fair | Construction Job | 0 | 12:18 Manually opened Pinang OCB Fdr #1 due to : Dismantle conductor and static at Pinang #29 due to new well Pinang #43. Crt: 431. 13:00 Manually blocked and closed Pinang OCB Fdr #1 and then released the block. Cause : Counstruction Job. |  | 1 | 12:18 | Afternoon | Tuesday | 2018 | 1
7778 | 2018-01-31 00:24 | 2018-01-31 00:24 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | N.Duri fdr#7 T/R 1x. Not checked yet. |  | 1 | 0:24 | Night | Wednesday | 2018 | 1
7779 | 2018-01-31 00:24 | 2018-02-02 10:24 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | Checked & found, North Duri Fdr #7 T/R 1x ctr: 101-102 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 0:24 | Night | Wednesday | 2018 | 1
7780 | 2018-01-31 07:34 | 2018-01-31 07:34 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | 07:34 Duri Field Fdr #4 T/R:2X, Ctr:...... R/F:........... Not checked yet. |  | 1 | 7:34 | Morning | Wednesday | 2018 | 1
7781 | 2018-01-31 07:34 | 2018-02-02 07:34 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Checked & found, Duri Field ACB #51 fdr #4 T/R 1x ctr: 513-514 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:34 | Morning | Wednesday | 2018 | 1
7782 | 2018-01-31 10:00 | 2018-01-31 10:00 | 13.8KV PEMATANG FEEDER #1 | Fair | Planned Maintenance | 0 | 10:00 Opened fuse at well Pematang #86 d/s Pematang Fdr #1 To Adjusted voltage 150 KVA TX 10:40 Closed the Fuse of well Pematang #86. Cause : Planned Maintenance. |  | 1 | 10:00 | Morning | Wednesday | 2018 | 1
7783 | 2018-01-31 10:20 | 2018-01-31 10:20 | 115KV BATANG - SINTONG LINE | Fair | Tree | 893 | 10:20 Batang 115KV line OCB#1 T/R 1X. Menggala 115KV line GCB#28 T/R 1X. Ctr:342-343, R/F:21G. Bangko Substation No power. Nella Substation No power. S Balam Substation No power. Pinang Subst.13.8KV VCB fdr#1 T/O--> Closed 10:35.(Prod. Loss:28Bbls/25 wells) Ctr: 430-432, R/F: 81 Sintong Substation 13.8KV VCB fdr#1 T/O--> Closed 11:41.(Prod. Loss: ................ ) Ctr: 389-390, R/F: 81. Sintong Substation 13.8KV VCB fdr#2 T/O--> Closed 11:42.(Prod. Loss: ................ ) Ctr: 469-470, R/F: 81. Cause : Under Investigation. | 123 | 1 | 10:20 | Morning | Wednesday | 2018 | 1
7784 | 2018-01-31 15:05 | 2018-01-31 15:05 | 13.8KV 8C FEEDER #1 | Fair | Transformer leakage | 0 | It was reported TX leak at 9E-91 d/s 8C Fdr #1. Cause : Not Checked yet. |  | 1 | 15:05 | Afternoon | Wednesday | 2018 | 1
7785 | 2018-01-31 15:05 | 2018-01-02 15:05 | 13.8KV 8C FEEDER #1 | Fair | Transformer leakage | 0 | Replaced Leakage Transformer with the same size at well 9E-91 then energized the Tx. Cause: Transformer Leakage. |  | 1 | 15:05 | Afternoon | Wednesday | 2018 | 1
7786 | 2018-01-31 20:45 | 2018-01-31 20:45 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 55 | It was reported B/O fuse at well Bangko#164 (Nella fdr#1). Not checked yet. |  | 1 | 20:45 | Night | Wednesday | 2018 | 1
7787 | 2018-01-31 20:45 | 2018-01-02 08:00 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 55 | Checked and found @2 B/O fuse for 150 KVA TX at Well BKO #164. Replaced B/O fuse above with the same size then energized the TX. Cause: Unidentified (Fuse). |  | 1 | 20:45 | Night | Wednesday | 2018 | 1
7788 | 2018-01-02 05:41 | 2018-01-02 05:41 | 13.8KV MINAS FEEDER #2 | Cloudy | Lightning | 0 | 05:41 Minas fdr#2 Load dropped 61A (126-61A). 05:50 It was reported no power at Minas WTP. 06:12 Checked & found Recl. M2-01 T/SO Ctr:46-47. Blocked & closed Recl M2-01, then release the block. 17:00 Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 5:41 | Morning | Tuesday | 2018 | 1
7789 | 2018-01-02 08:30 | 2018-01-02 08:30 | CENTRAL DURI POWER PLANT |  |  | - | 08:30 S/U CDGT #5 and Online to the system at.08:30. |  | 1 | 8:30 | Morning | Tuesday | 2018 | 1
7790 | 2018-01-02 09:35 | 2018-01-02 09:35 | MINAS POWER PLANT |  |  | - | 09:35 Open Gen Breaken and than S/D the unit for S/B. |  | 1 | 9:35 | Morning | Tuesday | 2018 | 1
7791 | 2018-01-02 10:00 | 2018-01-02 10:00 | 13.8KV BEKASAP FEEDER #5 | Fair | Planned Maintenance | 2383 | 10:00 Manually open Bekasap Main ACB Fdr #5. SP to De/Re Energize Line Bks Main Fdr #5. (TX-01B Bks EOD). Purpose: Repl. Hot Spot at Isolation switch Recl. 01-Bks-EOR. Change out recl. 01B-Bks-EOR. Up grate Relay. 09:08 Manually 0pened Bekasap Main Fdr #6 to Maintenance Tank Level. 15:55 Close Bekasap Main Fdr #6 11:40 Manually opened Bekasap Main Fdr #2. 15:36 Close Bekasap Main Fdr #2 12:54 Manually opened Petani Fdr #2. 15:46 Close Petani Fdr #2 13:10 Manually Opened Rokan Fdr #2. 15:48 Close RokanFdr #2 Cause:Plan Maintenance. | 12134 | 1 | 10:00 | Morning | Tuesday | 2018 | 1
7792 | 2018-01-02 10:45 | 2018-01-02 10:45 | 13.8KV BATANG FEEDER #2 | Fair | Construction Job | 0 | 10:45 Manually opened Batang Fdr #2 due to : Tie-in New Boster Pump. 14:30 Manually blocked and closed Batang Fdr #2, then release the block. Cause : Construction Job. |  | 1 | 10:45 | Morning | Tuesday | 2018 | 1
7793 | 2018-01-02 13:55 | 2018-01-02 13:55 | 13.8KV PUNGUT FEEDER #2 | Rain | Unidentified | 26 | 13:55 Pungut Fdr#2 Load dropped 17A (59-42A) Got Inform No Power at OKI, AMI,ASI,GADING. 18:05 Checked & Found Recl 44BX-06 T/SO, Ctr: 375-376 Block & Closed the Recloser. the released the block. Cause: Unidentified. |  | 1 | 13:55 | Afternoon | Tuesday | 2018 | 1
7794 | 2018-01-02 14:20 | 2018-01-02 14:20 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 57 | 14:20 Manually opened Recl.9D-25 d/s 8C Fdr#1 due to: C/O 300 Kva Tx due to leak at .9E 91. 15:30 Manually Block and Close Recl.9D-25 then release the block. Cause: Plan Maintenance. |  | 1 | 14:20 | Afternoon | Tuesday | 2018 | 1
7795 | 2018-01-02 15:00 | 2018-01-02 15:00 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 214 | 15:00 Manually Open LBS.32 AK 02 D/S Ketigul Fdr#1 C/O 150Kva Tx at well Kelok #11. Dismantle 150 Kva Tx at Well Kelok #06. 16:55 Close LBS.32 AK 02. Cause: Planned Maintenance. |  | 1 | 15:00 | Afternoon | Tuesday | 2018 | 1
7796 | 2018-01-02 15:27 | 2018-01-02 15:27 | 13.8KV DURI FIELD FEEDER #1 | Rain and Lightning | Tree | 151 | 15:27 Duri Field 13.8KV VCB Fdr#1 T/SO, Ctr:688 - 689, R/F: 51N, 51G. 17:37 Patrolled the Line, found Fall down Tree, O/P 01 07 15, Dismantled the Tree. Block & Closed D Field VCB fdr#1. Cause: TREE. |  | 1 | 15:27 | Afternoon | Tuesday | 2018 | 1
7797 | 2018-01-02 15:27 | 2018-01-02 15:27 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain and Lightning | Lightning | 0 | Duri Community fdr#2 T/R 1x. Not checked yet. |  | 1 | 15:27 | Afternoon | Tuesday | 2018 | 1
7798 | 2018-01-02 15:27 | 2018-05-02 15:27 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Duri Community ACB #30 fdr #2 T/R 1x ctr: 54-55 R/F: 50G. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 15:27 | Afternoon | Tuesday | 2018 | 1
7799 | 2018-01-02 16:10 | 2018-01-02 16:10 | 13.8KV 3D FEEDER #2 | Rain | Lightning | 36 | 16:10 3D VCB fdr#2 T/R 1x ctr: 252-253 R/F: N/A. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:10 | Afternoon | Tuesday | 2018 | 1
7800 | 2018-01-02 18:19 | 2018-01-02 18:19 | 44KV PEMATANG MAIN - PETANI LINE | Rain | Lightning | 113 | 18:19 44KV Line OCB #1 T/R 1x. Petani Substation NO power, (PTN fdr#1, Fdr#2). Pematang fdr#1 Load dropped 104A(196-88A) Rangau Fdr#1 Load dropped 141A(128-72A) Not Checked Yet. |  | 1 | 18:19 | Afternoon | Tuesday | 2018 | 1
7801 | 2018-01-02 18:19 | 2018-05-02 18:19 | 44KV PEMATANG MAIN - PETANI LINE | Rain | Lightning | 113 | Checked & found, 44 KV Pematang OCB #1 (to Petani) T/R 1x ctr: 4008-4009 R/F: 50N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 18:19 | Afternoon | Tuesday | 2018 | 1
7802 | 2018-02-02 01:37 | 2018-02-02 01:37 | 13.8KV NORTH DURI FEEDER #7 | Rain | Unidentified | 0 | N Duri VCB fdr #7 T/R 1x ctr: 101-102 R/F: 51N, 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 1:37 | Night | Friday | 2018 | 2
7803 | 2018-02-02 01:37 | 2018-02-02 01:37 | 13.8KV NORTH DURI FEEDER #8 | Rain | Unidentified | 0 | N Duri VCB fdr #8 T/R 1x. Not checked yet. |  | 1 | 1:37 | Night | Friday | 2018 | 2
7804 | 2018-02-02 01:37 | 2018-05-02 01:37 | 13.8KV NORTH DURI FEEDER #8 | Rain | Unidentified | 0 | Checked & found VCB Fdr#8 T/R 1x, Ctr: 85-86, R/F: 51N. Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 1:37 | Night | Friday | 2018 | 2
7805 | 2018-02-02 02:32 | 2018-02-02 02:32 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain | Tree | 0 | 02:32 Duri Community fdr#5 T/LO Ctr:114-116 R/F:51@1. 03:37 Patrolled the line but found nothing. Blocked & closed Duri Comm fdr#5, but trip again. 03:45 Patrolled the line & found @1 tree touch jumper LA o.p NN Near Medical then isolated. @1@2 B/O fuse for 112.5 Kva Tx for Limbah Medical. 04:15 Blocked & closed Duri Comm fdr#5, then release the block. Cause: Tree. |  | 1 | 2:32 | Night | Friday | 2018 | 2
7806 | 2018-02-02 11:08 | 2018-02-02 11:08 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 5 | It was reported b/o fuse o/p.09.S4.04 d/s CD Fdr #4. Not checked yet. |  | 1 | 11:08 | Morning | Friday | 2018 | 2
7807 | 2018-02-02 11:08 | 2018-03-02 11:44 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 5 | Checked & found @2 b/o fuse for 112.5KVATX Perform TTR & Megger the TX, was good result Replaced the fuse with the same size, then energized the TX Cause : Unidentified. |  | 1 | 11:08 | Morning | Friday | 2018 | 2
7808 | 2018-02-02 15:06 | 2018-02-02 15:06 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked & found N.Duri VCB fdr #4 T/R 1x Ctr: 513-514, R/F: 51N @1,@2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:06 | Afternoon | Friday | 2018 | 2
7809 | 2018-02-02 15:35 | 2018-02-02 15:35 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Others | 0 | Duri Community 13.8KV ACB-33 fdr #5 T/R 1x. Ctr:,,,,,,, R/F: ,,,,,,, Not checked yet. |  | 1 | 15:35 | Afternoon | Friday | 2018 | 2
7810 | 2018-02-02 15:35 | 2018-05-02 15:35 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Others | 0 | Checked & found, Duri Community ACB #33 fdr #5 T/R 1x ctr: 116-118 R/F: 51N @2. Patrolled the line & found, @2 spark at LBS on Pole 1 SG 14. Cause: Others. |  | 1 | 15:35 | Afternoon | Friday | 2018 | 2
7811 | 2018-02-02 15:42 | 2018-02-02 15:42 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Lightning | 0 | N Duri fdr #8 T/R 1x. Not checked yet. |  | 1 | 15:42 | Afternoon | Friday | 2018 | 2
7812 | 2018-02-02 15:42 | 2018-05-02 15:42 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Lightning | 0 | Checked & found N.Duri VCB fdr#8 T/R 1x, Ctr: 86-87, R/F 51N. Patrolled the Line, but Found nothing Cause : Lightning |  | 1 | 15:42 | Afternoon | Friday | 2018 | 2
7813 | 2018-02-02 15:54 | 2018-02-02 15:54 | 13.8KV CENTRAL DURI FEEDER #8 | Rain and Lightning | Unidentified | 0 | Central Duri fdr #8 T/R 1x. Ctr:441-442, R/F: 51@1. Not checked yet. |  | 1 | 15:54 | Afternoon | Friday | 2018 | 2
7814 | 2018-02-02 15:54 | 2018-05-02 15:54 | 13.8KV CENTRAL DURI FEEDER #8 | Rain and Lightning | Unidentified | 0 | Checked & found C.Duri AVB fdr#8 T/R 1x, Ctr:441-442, R/F : 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 15:54 | Afternoon | Friday | 2018 | 2
7815 | 2018-02-02 15:54 | 2018-02-02 15:54 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Lightning | 0 | Central Duri fdr #9 T/R 1x. Ctr:379-380, R/F: 51@1. Not checked yet. |  | 1 | 15:54 | Afternoon | Friday | 2018 | 2
7816 | 2018-02-02 15:54 | 2018-05-02 15:54 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Lightning | 0 | Checked & found C.Duri ACB fdr#9 T/R 1z, Ctr: 441-442, R/F : 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 15:54 | Afternoon | Friday | 2018 | 2
7817 | 2018-02-02 16:00 | 2018-02-02 16:00 | MINAS POWER PLANT |  |  | - | 16:00 Open Gen.Breaker and S/D the unit for repai leaks at bearing #2 |  | 1 | 16:00 | Afternoon | Friday | 2018 | 2
7818 | 2018-02-02 16:09 | 2018-02-02 16:09 | 13.8KV CENTRAL DURI FEEDER #15 | Rain and Lightning | Lightning | 0 | Central Duri ACB #18 fdr #15 T/R 1x. Ctr:374-375, R/F: 51N, 51@2. Not checked yet. |  | 1 | 16:09 | Afternoon | Friday | 2018 | 2
7819 | 2018-02-02 16:09 | 2018-05-02 16:09 | 13.8KV CENTRAL DURI FEEDER #15 | Rain and Lightning | Lightning | 0 | Checked & found C.Duri ACB fdr#15 T/R 1x, Ctr:374-375, R/F: 51N Patrolled the Line, found @2 Broken LA O/P 06-Q5-02 Cause : Lightning |  | 1 | 16:09 | Afternoon | Friday | 2018 | 2
7820 | 2018-02-02 16:09 | 2018-02-02 16:09 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain and Lightning | Lightning | 0 | Duri Community 13.8KV ACB-30 fdr #2 T/R 1x. Ctr:,,,,,,, R/F: ,,,,,,, Not checked yet. |  | 1 | 16:09 | Afternoon | Friday | 2018 | 2
7821 | 2018-02-02 16:09 | 2018-05-02 16:09 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Duri Community ACB #30 fdr #2 T/R 1x ctr: 89-90 R/F: 50G. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:09 | Afternoon | Friday | 2018 | 2
7822 | 2018-02-02 19:36 | 2018-02-02 19:36 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Broken Fuse Cut Out | 0 | 19:30 It was reported b/o fuse o/p.04-4A d/s CD Fdr #8. Checked and found @3 broken FCO o/p at CGS #4. |  | 1 | 19:36 | Night | Friday | 2018 | 2
7823 | 2018-02-02 19:36 | 2018-03-02 10:02 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Broken Fuse Cut Out | 0 | 10:03 Manually opened recl.04.05.32 (d/s CD Fdr #8) to Replace @3 broken Fuse cut out. Cause : Unidentified. |  | 1 | 19:36 | Night | Friday | 2018 | 2
7824 | 2018-03-02 09:15 | 2018-03-02 09:15 | 13.8KV DARLING VCB FEEDER #8 | Fair | Unidentified | 108 | 09:15 It was reported b/o fuse o/p.08.M3.01 d/s CD Fdr #8. 14:35 Checked and found recl.08.M7A.01 T/SO. Ctr:74-75. Manually blocked and closed the recloser then release the block. Patrolled the Line, but found nothing Cause : Unidentified. |  | 1 | 9:15 | Morning | Friday | 2018 | 3
7825 | 2018-03-02 09:15 | 2018-03-02 09:15 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 20 | It was reported b/o fuse o/p.04.7.29 (d/s CD Fdr #9). Not checked yet. |  | 1 | 9:15 | Morning | Friday | 2018 | 3
7826 | 2018-03-02 09:15 | 2018-04-02 10:00 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 20 | Checked & found @1 b/o fuse for 112.5KVATX perform TTR & Megger, was good result Replaced the fuse with the same size, then Energized the TX Cause: Unidentified (Fuse). |  | 1 | 9:15 | Morning | Friday | 2018 | 3
7827 | 2018-03-02 09:28 | 2018-03-02 09:28 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 77 | 09:28 Manually opened Recl.37.BD.40 d/s Bekasp Fdr #2. due to: Replaced TX from 150KVA to 225KVA at well BKS #184. 10:05 Manually blocked and closed Recl.37.BD.40 then release the block. Cause : Plan Maintenance. |  | 1 | 9:28 | Morning | Friday | 2018 | 3
7828 | 2018-03-02 10:05 | 2018-03-02 10:05 | 13.8KV BANGKO FEEDER #1 | Fair | Construction Job | 0 | 10:05 Manually opened Recl.23.X.08 (d/s Bangko Fdr #1) to Open HLC at T/O/P well BKO #4 for new Well at Bangko #91. 10:27 Manually blocked and closed Recl.23.X.08 then release the block. Cause : Construction Job. |  | 1 | 10:05 | Morning | Friday | 2018 | 3
7829 | 2018-03-02 11:11 | 2018-03-02 11:11 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 36 | 11:11 Manually opened recl.36.BI.04 d/s Sobek Fdr #1 due to: Replaced TX.150KVA to 225KVA at well Ampuh #19 (Reactive well). 12:20 Manually blocked and closed recl.36.BI.04 then release the block. Cause : Plan Maintenance. |  | 1 | 11:11 | Morning | Friday | 2018 | 3
7830 | 2018-03-02 17:50 | 2018-03-02 17:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse o/p 39-AV-9 Well Kulin#07 (d/s C Duri fdr#1) not checked yet. |  | 1 | 17:50 | Afternoon | Friday | 2018 | 3
7831 | 2018-03-02 17:50 | 2018-04-02 17:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked & found @3 b/o fuse at Well Kulim#7 (d/s CD fdr#1). Perform TTR & Megger the TX, was Good Result. Replaced the Fuse with the same size, the energized the TX. Cause : Unidentified (Fuse) |  | 1 | 17:50 | Afternoon | Friday | 2018 | 3
7832 | 2018-04-02 07:44 | 2018-04-02 07:44 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 53 | 07:44 4B Fdr #1 T/R, Ctr:......... R/F:............ 4B Fdr #2 Load drop 11A (88-77A). 4B Fdr #3 Load drop 185A (24-59A). Cause : Not checked yet. |  | 1 | 7:44 | Morning | Monday | 2018 | 4
7833 | 2018-04-02 07:44 | 13/02/2018 17:44 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 53 | Checked & found, 4B OCB fdr #1 T/R 1x ctr: 324-325 R/F: 50 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:44 | Morning | Monday | 2018 | 4
7834 | 2018-04-02 09:08 | 2018-04-02 09:08 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 9 | It was reported b/o fuse o/p.04-7-12 (d/s CD FDR #9). Not checked yet. |  | 1 | 9:08 | Morning | Monday | 2018 | 4
7835 | 2018-04-02 09:08 | 2018-05-02 09:08 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 9 | Checked & found @3 B/O fuse for 112.5KVATX Perform TTR & Megger the TX, was Good result Replaced the Fuse with the same size, then energized the TX. Cause : Unidentified (Fuse) |  | 1 | 9:08 | Morning | Monday | 2018 | 4
7836 | 2018-04-02 11:15 | 2018-04-02 11:15 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 0 | 11:15 Manually opened recloser 5C.42 d/s 6D Fdr #1 due to : Replace 150 KVATX with the same size due to change of VSD to Switchboard. 11:30 Manually block and closed 5C.42 then release the block. Cause : Plan Maintenance. |  | 1 | 11:15 | Morning | Monday | 2018 | 4
7837 | 2018-04-02 11:45 | 2018-04-02 11:45 | 13.8KV NORTH DURI FEEDER #9 | Fair | Lightning | 0 | ND Fdr #9 T/R 1X, Checked and found Ctr:47-48, R/F:51N, 51@A. Patrolled the Line, but found nothing Cause: Lightning |  | 1 | 11:45 | Morning | Monday | 2018 | 4
7838 | 2018-04-02 12:20 | 2018-04-02 12:20 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 149 | ND Fdr #9 T/SO 1X, Checked and found Ctr:48-489 R/F:51N, 51@A,B & Spring VCB #9 Discharge Patrolled the Line, but found nothing Cause: Unidentified |  | 1 | 12:20 | Afternoon | Monday | 2018 | 4
7839 | 2018-05-02 11:12 | 2018-05-02 11:12 | MINAS POWER PLANT | Fair |  | - | 11:12 S/U MGT #6 and Online to the system at.15:40 for Increase Voltage. |  | 1 | 11:12 | Morning | Wednesday | 2018 | 5
7840 | 2018-05-02 14:10 | 2018-05-02 14:10 | CENTRAL DURI POWER PLANT |  |  | - | 14:10 Open Gen.Breaker CDGT #5 and S/D at.14:12 for S/B. |  | 1 | 14:10 | Afternoon | Wednesday | 2018 | 5
7841 | 2018-05-02 15:16 | 2018-05-02 15:16 | 13.8KV 3D FEEDER #2 | Fair | Planned Maintenance | 26 | 15:16 Manually opened 3D Fdr #2 due to : Replaced 300 KVATX b/o with the same size. Installed New 300 KVATX, reactive well 3E.64. 15:40 Manually blocked and closed 3D Fdr #2 then release the block. Cause : Plan Maintenance. |  | 1 | 15:16 | Afternoon | Wednesday | 2018 | 5
7842 | 2018-05-02 15:20 | 2018-05-02 15:20 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Animal | 0 | It was reported b/o fuse o/p.09.TL.02 d/s CD Fdr #4. Cause : Not checked yet. |  | 1 | 15:20 | Afternoon | Wednesday | 2018 | 5
7843 | 2018-05-02 15:20 | 2018-06-02 15:20 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Animal | 0 | Checked & found @1 B/O fuse For 112.5KVATX o/p 09-T5-02 (d/s CD Fdr#4) Perform TTR & Megger the TX was good result Replaced the Fuse with the same size, then energized the TX patrolled the Line found Animal, monkey below the TX Pole. Cause : Animal (monkey) |  | 1 | 15:20 | Afternoon | Wednesday | 2018 | 5
7844 | 2018-05-02 17:00 | 2018-05-02 17:00 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 8 | It was reported b/o fuse at @1. o/p.11.G7.20 d/s ND Fdr #9. Not checked yet. |  | 1 | 17:00 | Afternoon | Wednesday | 2018 | 5
7845 | 2018-05-02 17:00 | 2018-07-02 16:30 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 8 | Checked and found @2 B/O fuse for 112.5KVA TX o/p 11-G7-20. Perform TTR & Megger , the TX was good result Replaced B/O fuse with the same size, then Energized the TX Cause : Animal (Monkey). |  | 1 | 17:00 | Afternoon | Wednesday | 2018 | 5
7846 | 2018-06-02 06:39 | 2018-06-02 06:39 | 8 CHARLIE SUBSTATION | Fair | Control Voltage Regulator Problem | 1602 | 06:39 115 Kv 8C C/S TX #2 T/O. 07:00 Manually opened 8C OCB fdr #4 Closed at: 07:39 (GS2 WIP) 07:01 Manually opened 8C OCB fdr #5 Closed at: 07:40 (GS2 WIP) 07:02 Manually opened 8C OCB fdr #6 Closed at: 16:48 (GS2 WIP& Some Wells) GS2 Requested to maintain level 07:06 Manually opened Minas ACB Fdr #3 Closed at: 10:51 (Caried Part Of Minas Fdr#1,GS3) 07:06 Manually opened Minas ACB Fdr #4 Closed at: 10:42 (GS2 & 1) 07:18 Manually opened 8C OCB fdr #1 Closed at: 11:48 (GS2 & 1) 07:19 Manually opened 8C OCB fdr #2 Closed at: 13:03 (GS2 & 1) 07:19 Manually opened 8C OCB fdr #3 Closed at: 17:40 (GS2 & 1) 07:23 Manually opened 8D OCB fdr #3 Closed at: 10:48 - 18:55 (GS2 ) Checked and found 8C C/S T/SO, Ctr:520, R/F: 51G. Trouble shoot 8C TX-2 & VR 07:35 Manually opened Isolation swith TX-2 to Bus 07:36 Manually Closed Tie Bus 1&2 . 07:38 Installed Temporary Gdround at TX-2. 07:40 Manually Closed C/S 8C.TX-2. Transfer part Load 8C Fdr #6 to 8C Fdr #4 to backed up Power GS2 10:20 Opened LBS.8C.102 and Closed LBS.8D.114 Continued Trouble shoot 8C TX-2 & VR 11:00 Manually opened C/S 8C TX-2 11:10 Manually opened Isolation switch TX-2. 11:30 Manually Closed C/S 8C TX-2 Normalized Load 8C substation, without VR. 13:55 Manually opened 8D Fdr #3 Closed at. 17:20 14:00 Manually opened Minas ACB Fdr #3 Closed at: 17:02. 16:30 Manually opened 8C OCB fdr #4 Closed at: 16:46. Ctr.602 16:30 Manually opened 8C OCB fdr #5 Closed at: 16:47. Ctr.503 16:31 Manually Opened Tie Bus 1&2 at 8C. 16:32 Removed out Temporary Gdround at TX-2. 16:33 Manually Closed Isolation swith TX-2. 16:35 Manually Closed Bypass VR 8C TX-2. 16:40 Manually Closed Isolation switch 8C Fdr #6. 16:43 Manually Close C/S 8C TX-2. Ctr:164. 16:46 Manually Closed 8C Fdr #4, Ctr:602 16:47 Manually Closed 8C Fdr #5, Ctr:503 16:48 Manually Closed 8C Fdr #6, Ctr:584. 17:02 Manually Closed Minas Fdr #3, Ctr:136-138. 17:06 Manually Closed LBS.8C.102 d/s 8C Fdr #6. 17:07 Manually Opened LBS.8D.114 d/s 8C Fdr #4. 17:20 Manually Closed 8D OCB Fdr#3, but Fail, from DSC & Local. 18:55 Transfer Load 8D fdr#3 to 8C fdr#2, by Closed LBS 8DC-05. Cause : VR Problem | 12345 | 1 | 6:39 | Morning | Saturday | 2018 | 6
7847 | 2018-06-02 08:38 | 2018-06-02 08:38 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Over voltage | 0 | It Was reported high voltage o/p 08.M4.04. d/s CD Fdr #2. Not checked yet. |  | 1 | 8:38 | Morning | Saturday | 2018 | 6
7848 | 2018-06-02 08:38 | 15/02/2018 10:00 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Over voltage | 0 | Adjust tapping 112.5 Kva Transformer from 5 to 3. Cause: Over voltage. |  | 1 | 8:38 | Morning | Saturday | 2018 | 6
7849 | 2018-06-02 10:02 | 2018-06-02 10:02 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 10:02 CDGT #2 Trip by alarm Liquid Level High due to HCT Pigging Job. 10:06 Closed Tie Breaker #19 10:40 S/U CDGT #2 and Online at.11:16 to restore power. 11:16 Manually Opened Tie Breaker #19. |  | 1 | 10:02 | Morning | Saturday | 2018 | 6
7850 | 2018-06-02 10:07 | 2018-06-02 10:07 | 13.8KV BATANG FEEDER #2 | Fair | Construction Job | 0 | 10:07 Manually opened Batang Fdr #2 due to : Tie-In New Boster Pump at Rantau Bais GS. 16:....Manually blocked and closed Batang Fdr #2, then release the block. Cause : Construction job. |  | 1 | 10:07 | Morning | Saturday | 2018 | 6
7851 | 2018-06-02 10:40 | 2018-06-02 10:40 | CENTRAL DURI POWER PLANT |  |  | - | 10:40 S/U CDGT #2 and Online at.11:16 to restore power, 11:05 Manually Opened Tie Breaker #19. |  | 1 | 10:40 | Morning | Saturday | 2018 | 6
7852 | 2018-06-02 15:56 | 2018-06-02 15:56 | 13.8KV 5B FEEDER #1 | Fair | Planned Maintenance | 21 | 15:56 Manually opened 5B Fdr #1 due to : Replaced 300 KVATX with the same size and Change VSD to Switchboard. 16:45 Manually blocked and closed 5B Fdr#1 then release the block. Cause : Planned Maintenance. |  | 1 | 15:56 | Afternoon | Saturday | 2018 | 6
7853 | 2018-06-02 20:20 | 2018-06-02 20:20 | CENTRAL DURI POWER PLANT |  |  | - | 20:20 CDGT #4 Off Line (Open Generator Breaker). Alarm DC ground. 20:25 On Line CDGT #4. |  | 1 | 20:20 | Night | Saturday | 2018 | 6
7854 | 2018-06-02 21:00 | 2018-06-02 21:00 | MINAS POWER PLANT |  |  | - | 21:00 Off Line MGT #4 and then S/D the unit for Stand By. |  | 1 | 21:00 | Night | Saturday | 2018 | 6
7855 | 2018-07-02 05:53 | 2018-07-02 05:53 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Duri Field fdr#4 T/R 1x. Not checked yet. |  | 1 | 5:53 | Morning | Monday | 2018 | 7
7856 | 2018-07-02 05:53 | 2018-11-02 05:53 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Checked and found D.Field 13.8 KV ACB fdr #4 T/R 1X ctr: 515 - 516 R/F: 51@1. Patrol the line and found nothing. cause : Unidentified. |  | 1 | 5:53 | Morning | Monday | 2018 | 7
7857 | 2018-07-02 07:50 | 2018-07-02 07:50 | 13.8KV KETIGUL GFPC | Fair | Unidentified | 0 | 07:50 Ketigul & GFPC T/R 1X ( on Blocked ) Ketigul fdr #1 load dropped 11A (117-106A ) Not checked yet. |  | 1 | 7:50 | Morning | Monday | 2018 | 7
7858 | 2018-07-02 07:50 | 13/02/2018 07:50 | 13.8KV KETIGUL GFPC | Fair | Unidentified | 0 | Checked and found Ketigul 13.8KV GFPC T/R 1X ctr: 732-733 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:50 | Morning | Monday | 2018 | 7
7859 | 2018-07-02 10:20 | 2018-07-02 10:20 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Animal | 0 | 10;20 It was reported B/O fuse O/P 09 T5 02 D/S C.Duri fdr#4. 14:00 Replace b/o fuse @2. Cause :Animal (squirrel). |  | 1 | 10:20 | Morning | Monday | 2018 | 7
7860 | 2018-07-02 10:37 | 2018-07-02 10:37 | 13.8KV PETANI FEEDER #1 | Fair | Planned Maintenance | 100 | 10:37 Manual opened Petani fdr #1 , and Closed at 11:24. Replaced Travo 100 KVA at Petani #125. Cause: Planned maintenance . |  | 1 | 10:37 | Morning | Monday | 2018 | 7
7861 | 2018-07-02 14:21 | 2018-07-02 14:21 | MINAS POWER PLANT |  |  | - | 14:21 S/U MGT#10 and online at 16:30, running test. |  | 1 | 14:21 | Afternoon | Monday | 2018 | 7
7862 | 2018-07-02 16:32 | 2018-07-02 16:32 | 13.8KV NORTH DURI FEEDER #7 | Fair | Secondary Cable | 0 | 16:32 It was reported vandalism secondary cable at O/P 10 k2 32 D/S N. Duri fdr#7 at well 4K-20C. Not checked yet. |  | 1 | 16:32 | Afternoon | Monday | 2018 | 7
7863 | 2018-07-02 16:32 | 2018-10-02 10:35 | 13.8KV NORTH DURI FEEDER #7 | Fair | Secondary Cable | 0 | 10:35 Open and closed fuse for 112.5Kva TX o/p 10 K2 32. Replaced Scondary Cable. Cause: Scondary Cable. |  | 1 | 16:32 | Afternoon | Monday | 2018 | 7
7864 | 2018-07-02 19:09 | 2018-07-02 19:09 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | 19:09 DF Fdr #4 T/R, Ctr: ...... R/F: ............ 19:50 DF Fdr #4 T/R, Ctr: ...... R/F: ............ 19:51 DF Fdr #4 T/R, Ctr: ...... R/F: ............. Cause : Not Checked yet |  | 1 | 19:09 | Night | Monday | 2018 | 7
7865 | 2018-07-02 19:09 | 2018-11-02 19:09 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Checked and found D.Field 13.8 KV ACB fdr #4 T/R 2X ctr: 516 - 518 R/F: 51@1, 51N. Patrol the line and found nothing. cause : Unidentified. |  | 1 | 19:09 | Night | Monday | 2018 | 7
7866 | 2018-07-02 19:37 | 2018-07-02 19:37 | 13.8KV 6D FEEDER #5 | Fair | Planned Maintenance | 0 | 19:37 Manually opened 6D Fdr #5 due to GS #4 Maintain Tank Level. 21:05 Manually blocked and closed 6D Fdr #5 then release the block. Cause: Planned Construction (Maintain tank level) |  | 1 | 19:37 | Night | Monday | 2018 | 7
7867 | 2018-07-02 20:00 | 2018-07-02 20:00 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 20:00 CGT #4 Generator Breaker T/O, by Alarm Exciter trouble. 20:27 CGT #4 Online Back to System. Cause: Under Investigation |  | 1 | 20:00 | Night | Monday | 2018 | 7
7868 | 2018-07-02 21:40 | 2018-07-02 21:40 | CENTRAL DURI POWER PLANT |  |  | - | 21:40 CGT #5 S/U, then On line to system at 21:5. to restore Power & Backup CGT#4. |  | 1 | 21:40 | Night | Monday | 2018 | 7
7869 | 2018-08-02 06:27 | 2018-08-02 06:27 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | 06:27 C.Duri 13.8 KV fdr #16 T/R 1x, Cttr: 308-309, R/F: 51N. Not checked yet. |  | 1 | 6:27 | Morning | Thursday | 2018 | 8
7870 | 2018-08-02 06:27 | 2018-11-02 06:27 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked and found C.Duri 13.8 KV ACB fdr #16 T/R 1X ctr: 308 - 309 R/F: 51@1, 51N Patrol the line and found nothing. cause : Unidentified. |  | 1 | 6:27 | Morning | Thursday | 2018 | 8
7871 | 2018-08-02 08:15 | 2018-08-02 08:15 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | 08:15 D.field 13.8 KV fdr #4 T/R 1X. Not checked yet. |  | 1 | 8:15 | Morning | Thursday | 2018 | 8
7872 | 2018-08-02 08:15 | 2018-11-02 08:15 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Checked and found D.Field 13.8 KV ACB fdr #4 T/R 1X ctr: 519 - 520 R/F: 51@1, 51N Patrol the line and found nothing. cause : Unidentified. |  | 1 | 8:15 | Morning | Thursday | 2018 | 8
7873 | 2018-08-02 09:35 | 2018-08-02 09:35 | 13.8KV MINAS FEEDER #3 | Fair | Transformer Failure | 0 | 09:35 It was reported TX Lube Oil leak at well 8C 17. Not checked yet. |  | 1 | 9:35 | Morning | Thursday | 2018 | 8
7874 | 2018-08-02 09:35 | 21/02/2018 08:00 | 13.8KV MINAS FEEDER #3 | Fair | Transformer Failure | 0 | Checked and found Leakage transformer at location 8C-17. Open the fuse to isolate it. Cause: Transformer Failure. |  | 1 | 9:35 | Morning | Thursday | 2018 | 8
7875 | 2018-08-02 09:36 | 2018-08-02 09:36 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | 09:36 C.Duri 13.8 KV VCB #28 fdr #16 T/R 1X. R/F: 51@1,@2 ctr:309-311. Not checked yet. |  | 1 | 9:36 | Morning | Thursday | 2018 | 8
7876 | 2018-08-02 09:36 | 2018-11-02 09:36 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked and found C.Duri 13.8 KV ACB fdr #16 T/R 2X ctr: 309 - 311 R/F: 51@1. Patrol the line and found nothing. cause : Unidentified. |  | 1 | 9:36 | Morning | Thursday | 2018 | 8
7877 | 2018-08-02 10:00 | 2018-08-02 10:00 | MINAS POWER PLANT | Fair | Under investigation | 0 | 10:00 MGT #7 Tripp off by alarm Gas scrubber liquid level hight trip. |  | 1 | 10:00 | Morning | Thursday | 2018 | 8
7878 | 2018-08-02 10:28 | 2018-08-02 10:28 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified (Fuse) | 0 | 10:28 It was reported b/o fuse o/p 09 N2 01A. Not checked yet. |  | 1 | 10:28 | Morning | Thursday | 2018 | 8
7879 | 2018-08-02 10:28 | 2018-09-02 09:40 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified (Fuse) | 0 | 09:40 Checked and found @2 b/o fuse for 112.5 KVA TX 09-N2-01A d/s C.Duri fdr #16. Replaced b/o fuse above with same size than energize the TX. Cause:unidentified (fuse). |  | 1 | 10:28 | Morning | Thursday | 2018 | 8
7880 | 2018-08-02 13:46 | 2018-08-02 13:46 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Unidentified | 72 | Menggala 13.8 KV OCB #1 fdr #1 T/R 1X Not checked yet. |  | 1 | 13:46 | Afternoon | Thursday | 2018 | 8
7881 | 2018-08-02 13:46 | 2018-12-02 13:46 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Unidentified | 72 | Checked and found Menggala 13.8 KV OCB fdr #1 T/R 1X ctr: 320 - 321 R/F: 51N Patrol the line and found nothing. cause : Unidentified. |  | 1 | 13:46 | Afternoon | Thursday | 2018 | 8
7882 | 2018-08-02 13:47 | 2018-08-02 13:47 | KETIGUL SUBSTATION | Fair | Equipment Failure | 1387 | 13:47 Ketigul RTU Failed . It was reported no Power at Tilan Booster. 15:45 Checked and found: Ketigul 115 KV GCB #2 T/O. and Closed at 17:27 ctr:172-173. Ketigul 115 KV GCB #3 T/O. and Closed at 17:28 ctr:162-163. Ketigul GFPC T/R 1X ctr:773. 17:24 Checked and found Ketigul TX Normal Condition R/F:87 T. Manual open Ketigul fdr #1 and Closed at 17:29. ctr:197-198. Manual open Ketigul fdr #2 and Closed at 17:32 ctr: 221 - 264. (Can not Closed from DSC). Manual open Ketigul fdr #3 and Closed at 17:30 ctr: 196 - 197. Cause: Under investigation. | 11111 | 1 | 13:47 | Afternoon | Thursday | 2018 | 8
7883 | 2018-08-02 14:36 | 2018-08-02 14:36 | MINAS POWER PLANT |  |  | - | 14:36 S/U MGT #7 online at 14:54. |  | 1 | 14:36 | Afternoon | Thursday | 2018 | 8
7884 | 2018-08-02 16:15 | 2018-08-02 16:15 | CENTRAL DURI POWER PLANT |  |  | - | 16:15 S/D CDGT #4 for Standby. |  | 1 | 16:15 | Afternoon | Thursday | 2018 | 8
7885 | 2018-09-02 10:14 | 2018-09-02 10:14 | 13.8KV PETANI FEEDER #2 | Fair | Tree | 88 | 10:14 Petani fdr #2 T/LO ctr:241-245 r/f:51@1. Checked and found the Tree Touch Power line o/p 33-AX-37, then remove the tree. 10:22 Closed Petani fdr #2. ok. Petani fdr #1 dropped 126A ( 162-36A ). Cause:Tree. |  | 1 | 10:14 | Morning | Sunday | 2018 | 9
7886 | 2018-09-02 15:54 | 2018-09-02 15:54 | 13.8KV SINTONG FEEDER #2 | Fair | Construction Job | 0 | 15:54 Manually Open Recl. 28-AF-02, ----->Closed at 16:44. Installed TX for new well at Benar #52. Cause:Consruction. |  | 1 | 15:54 | Afternoon | Sunday | 2018 | 9
7887 | 2018-10-02 06:39 | 2018-10-02 06:39 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 06:39 C.Duri 13.8KV ACB-11 (C.Duri Fdr #1) T/R, Ctr: 215-216 R/F: 51N-51G. Cause : Not Checked yet. |  | 1 | 6:39 | Morning | Tuesday | 2018 | 10
7888 | 2018-10-02 06:39 | 2018-11-02 06:39 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found C.Duri 13.8 KV ACB fdr #1 T/R 1X ctr: 215 - 216 R/F: 51@1. Patrol the line and found nothing. cause : Unidentified. |  | 1 | 6:39 | Morning | Tuesday | 2018 | 10
7889 | 2018-10-02 16:18 | 2018-10-02 16:18 | MINAS POWER PLANT |  |  | - | 16:18 S/D MGT #10 and off line. |  | 1 | 16:18 | Afternoon | Tuesday | 2018 | 10
7890 | 2018-10-02 18:41 | 2018-10-02 18:41 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 50 | 18:41 Old Kotabatak13.8 KV OCB #2 T/R 1X. Not checked yet. |  | 1 | 18:41 | Afternoon | Tuesday | 2018 | 10
7891 | 2018-10-02 18:41 | 13/02/2018 18:41 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 50 | Checked & found OKB OCB fdr#2 T/R, Ctr: 1309-1310, R/F: 51N. Patrolled the line, but found nothing. Cause : Others |  | 1 | 18:41 | Afternoon | Tuesday | 2018 | 10
7892 | 2018-11-02 09:48 | 2018-11-02 09:48 | 13.8KV SINTONG FEEDER #1 | Fair | Construction Job | 0 | 09:48 Manually Open Recl. 25 AD 26 d/s Sintong fdr #1 -----> Closed at 12:17. Installed TX at New well Seruni #47. Cause: Consruction. |  | 1 | 9:48 | Morning | Friday | 2018 | 11
7893 | 2018-11-02 11:06 | 2018-11-02 11:06 | 13.8KV PINANG FEEDER #1 | Fair | Planned Maintenance | 49 | 11:06 Manually Open Pinang 13.8 KV OCB-1 fdr #1 -----> Closed at 12:08. Replaced TX 150 KVA - 300 KVA at Pinang #47 R/M: 57HP - 147HP, Voltage:800 - 1000. Cause:Consruction. |  | 1 | 11:06 | Morning | Friday | 2018 | 11
7894 | 2018-11-02 15:26 | 2018-11-02 15:26 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 15:35 C.Duri 13.8KV ACB-11 (C.Duri Fdr #1) T/R, Ctr: 216 R/F: 51N-51G. Cause : Not Checked yet. |  | 1 | 15:26 | Afternoon | Friday | 2018 | 11
7895 | 2018-11-02 15:26 | 15/02/2018 10:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found C.Duri 13.8KV ACB-11 (C.Duri Fdr #1) T/R, Ctr: 216 R/F: 51N-51G. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 15:26 | Afternoon | Friday | 2018 | 11
7896 | 2018-11-02 15:42 | 2018-11-02 15:42 | 13.8KV KETIGUL GFPC | Fair | Unidentified | 0 | 15:42 Ketigul GFPC T/R, ( on blocked ). No load dropped. Cause : Not Checked yet. |  | 1 | 15:42 | Afternoon | Friday | 2018 | 11
7897 | 2018-11-02 15:42 | 27/02/2018 08:00 | 13.8KV KETIGUL GFPC | Fair | Unidentified | 0 | Checked and found 13.8 KV Ketigul GFPC T/R Ctr: - R/F: None Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:42 | Afternoon | Friday | 2018 | 11
7898 | 2018-11-02 17:36 | 2018-11-02 17:36 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | 17:36 C.Duri 13.8 KV VCB #28 fdr #16 T/R 1X. R/F: 51N @1,@2 ctr:311-312. Not checked yet. |  | 1 | 17:36 | Afternoon | Friday | 2018 | 11
7899 | 2018-11-02 17:36 | 13/02/2018 17:36 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked & found, Central Duri ACB #28 fdr#16 T/R 1x ctr: 311-312 R/F: 51 @1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:36 | Afternoon | Friday | 2018 | 11
7900 | 2018-12-02 10:47 | 2018-12-02 10:47 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 10:47 CDGT #2 Tripp off by alarm Gas scrubber liquid level hight trip. |  | 1 | 10:47 | Morning | Sunday | 2018 | 12
7901 | 2018-12-02 11:46 | 2018-12-02 11:46 | MINAS POWER PLANT |  |  | - | 11:46 S/U MGT #5 and on line at : 12:30. |  | 1 | 11:46 | Morning | Sunday | 2018 | 12
7902 | 2018-12-02 13:32 | 2018-12-02 13:32 | CENTRAL DURI POWER PLANT |  |  | - | 13:32 S/U CDGT #2 and on line at :14:15. |  | 1 | 13:32 | Afternoon | Sunday | 2018 | 12
7903 | 2018-12-02 14:25 | 2018-12-02 14:25 | CENTRAL DURI POWER PLANT |  |  | - | 14:25 CDGT #2 Trip off by alarm Gas Scrubber liquid level hight trip. |  | 1 | 14:25 | Afternoon | Sunday | 2018 | 12
7904 | 2018-12-02 15:15 | 2018-12-02 15:15 | CENTRAL DURI POWER PLANT |  |  | - | 15:15 S/U CDGT #4 and on line at :15:37. |  | 1 | 15:15 | Afternoon | Sunday | 2018 | 12
7905 | 2018-12-02 18:03 | 2018-12-02 18:03 | 13.8KV DURI FIELD FEEDER #4 | Fair | Lightning Arrester | 0 | 18:03 D.Field 13.8KV VCB-51 Fdr #4 T/R 1X Cause : Not Checked yet. |  | 1 | 18:03 | Afternoon | Sunday | 2018 | 12
7906 | 2018-12-02 18:03 | 16/02/2018 16:05 | 13.8KV DURI FIELD FEEDER #4 | Fair | Lightning Arrester | 0 | Checked and found D.Field 13.8KV VCB-51 Fdr #4 T/R 1x R/F: 51@2 Counter: 520-521. Patrolled the line found @2 broken L Arrester on pole 07-U1-06. Cause: Broken L Arrester. |  | 1 | 18:03 | Afternoon | Sunday | 2018 | 12
7907 | 2018-12-02 22:23 | 2018-12-02 22:23 | CENTRAL DURI POWER PLANT |  |  | - | 22:23 CDGT #4 Open gen. Breaker the S/D the unit due to L/O leaks at Acc. Gear. 22:24 Closed Tie Breaker ACB #39. |  | 1 | 22:23 | Night | Sunday | 2018 | 12
7908 | 2018-02-13 08:37 | 2018-02-13 08:37 | CENTRAL DURI POWER PLANT |  |  | - | 08:37 S/U CGT #2 and On Line the Unit at 09:03 |  | 1 | 8:37 | Morning | Tuesday | 2018 | 2
7909 | 2018-02-13 14:30 | 2018-02-13 14:30 | 13.8KV 8D FEEDER #10 | Fair | Planned Maintenance | 0 | 14:30 Manually Open LBS 8E-40 (all wells under 8D dfr #10 down). Replaced 300KVA TX at well 2D-38 ( reactive well ) 15:00 Closed LBS 8E-40. Cause: Plan Maintenance. |  | 1 | 14:30 | Afternoon | Tuesday | 2018 | 2
7910 | 2018-02-14 08:32 | 2018-02-14 08:32 | 13.8KV PEMATANG FEEDER #1 | Fair | Tree | 50 | Pematang OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 8:32 | Morning | Wednesday | 2018 | 2
7911 | 2018-02-14 08:32 | 2018-02-19 08:00 | 13.8KV PEMATANG FEEDER #1 | Fair | Tree | 50 | Checked and found 13.8 KV OCB #1 T/R 1x Ctr: 156-157 R/F: 51 @2 Patrolled the line and found High Trees o/p 35-BC-28 Cause: Tree. |  | 1 | 8:32 | Morning | Wednesday | 2018 | 2
7912 | 2018-02-14 10:10 | 2018-02-14 10:10 | 13.8KV PETAPAHAN FEEDER #8 | Fair | Planned Maintenance | 0 | Opened FCO at well Petapahan #13 due to: -C/O VCD to switch board by SPS Crew. Cause: Planned maintenance. To be continued tomorrow. |  | 1 | 10:10 | Morning | Wednesday | 2018 | 2
7913 | 2018-02-15 16:58 | 2018-02-15 16:58 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 31 | C Duri ACB #11 (Feeder #1) T/R 1x R/F : 51@2. Not patrolled yet. |  | 1 | 16:58 | Afternoon | Thursday | 2018 | 2
7914 | 2018-02-15 16:58 | 2018-02-16 09:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 31 | Checked and found C Duri ACB #11 (Feeder #1) T/R 1x R/F : 51@2 Counter: 216 (did not changed). Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 16:58 | Afternoon | Thursday | 2018 | 2
7915 | 2018-02-15 17:30 | 2018-02-15 17:30 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning | 59 | Bangko OCB fdr #4 T/R 1x. Not checked yet. |  | 1 | 17:30 | Afternoon | Thursday | 2018 | 2
7916 | 2018-02-15 17:30 | 2018-02-18 13:30 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning | 59 | Checked & found Bangko VCB fdr#4 T/R 1x Ctr:27-28 R/F:51@1. Patrolled the line & found @1 Broken LA o/p 25AB17. Cause : Lightning. |  | 1 | 17:30 | Afternoon | Thursday | 2018 | 2
7917 | 2018-02-16 05:23 | 2018-02-16 05:23 | DARLING SUBSTATION | Fair | Under investigation | 72 | 05:23 Darling 115KV GCB #1 T/O Darling 115KV GCB #3 T/O (No power to Darling fdr #6, #7 and #8) 06:25 Checked and found: Darling 115KV GCB #1 T/O ctr: 199-200 R/F : 51@1,@2,@3. Darling 115KV GCB #3 T/O ctr: 108-109. Checked Darling TX-2, OK. Manually Open Darling 13.8KV VCB fdr #6 Closed at : 06:59 Ctr : 229-230. Manually Open Darling 13.8KV VCB fdr #7 Closed at : 07:01 Ctr : 162-163. Manually Open Darling 13.8KV VCB fdr #8 Closed at : 07:03 Ctr : 381-382. 06:50 Closed Darling 115KV GCB #1, OK. 06:58 Closed Darling 115KV GCB #3, OK. 08:00 Patrolled the line nothing found. Cause : Under Investigation. |  | 1 | 5:23 | Morning | Friday | 2018 | 2
7918 | 2018-02-16 05:23 | 2018-02-19 05:23 | DARLING SUBSTATION | Fair | Under investigation | 72 | Checked and found : Darling 115KV GCB#! T/O Ctr : 199-200 R/F : 51 @1, @2 & @3. Darling 115KV GCB#3 T/O Ctr : 108-109. Patrolled the line but found nothing. Cause : Under investigation. |  | 1 | 5:23 | Morning | Friday | 2018 | 2
7919 | 2018-02-16 10:15 | 2018-02-16 10:15 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 115 | 10:15 Manually open LBS: 32-AK-02 D/S Ketigul fdr#1 due to: - C/O 100-225 Kva Tx at well Kelok #12. Tx: 225 Kva R/M : 175 Hp Sec Voltage : 1100 V. - Dismantled 500 Kva Tx due to LTC well at well Kelok #05. 11:20 Manually closed LBS: 32-AK-02 D/S Ketigul fdr#1. Cause : Plain Maintenance. |  | 1 | 10:15 | Morning | Friday | 2018 | 2
7920 | 2018-02-16 15:14 | 2018-02-16 15:14 | 13.8KV 4D FEEDER #4 | Fair | Planned Maintenance | 43 | 15:14 Manually open LBS: 36-DN-27 D/S 4D fdr#4 due to: - C/O 550-300 Kva Tx at well 4E-93. Tx: 300 Kva R/M : 225 Hp Sec Voltage : 1100 V. - Dismantled 300 Kva Tx due to LTC well at well 4E-83. 16:10 Manually blocked and closed 6DN OCB fdr #1 and then released block. (Part load 4D fdr 4 transfer to 6DN fdr #1 by open LBS: 36-DN-27). Cause : Plan Maintenance. |  | 1 | 15:14 | Afternoon | Friday | 2018 | 2
7921 | 2018-02-17 09:10 | 2018-02-17 09:10 | IT MINI SUBSTATION | Fair | Planned Maintenance | 0 | 09:10 Manually open Recl, 4160V IT Trimming tage at IT office 11:30 Closed recl, 4160V IT Ctr : 719 Cause : Plan Maintenance |  | 1 | 9:10 | Morning | Saturday | 2018 | 2
7922 | 2018-02-17 15:38 | 2018-02-17 15:38 | 13.8KV DURI FIELD FEEDER #4 | Fair | Pin Insulator | 0 | Duri Field 13.8KV VCB#51 fdr#4 T/R 1X. Not checked yet. |  | 1 | 15:38 | Afternoon | Saturday | 2018 | 2
7923 | 2018-02-17 15:38 | 2018-02-18 10:38 | 13.8KV DURI FIELD FEEDER #4 | Fair | Pin Insulator | 0 | Checked & found Duri Field fdr#4 T/R 1x Ctr:521-522 R/F:51@2. Patrolled the line & found @2 Broken Pin Insulator o/p 07-S8-01A. Cause : Pin Insulator. |  | 1 | 15:38 | Afternoon | Saturday | 2018 | 2
7924 | 2018-02-18 01:35 | 2018-02-18 01:35 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | 01:35 Duri Community 13.8 KV ACB fdr #3 T/R 1X. It was reported no power at HCT, Kutilang & Security office. 02:45 Checked and found Singgalang Mini Sub. 13.8 KV Recl. T/O, ctr: 236 - 237. And also found broken busing of the Recl. Open 4160 VOLT Recl. Singgalang Mini Sub. Closed LBS 1148 (from IT Mini Sub). Cause: Animal (Weasel). |  | 1 | 1:35 | Night | Sunday | 2018 | 2
7925 | 2018-02-18 06:53 | 2018-02-18 06:53 | 13.8KV BEKASAP FEEDER #5 | Fair | Unidentified | 113 | 06:53 Bekasap Main 13.8KV ACB fdr #5 T/R 1X. Bekasap fdr #3 dropped 97A (104-7A). Bekasap fdr #2 dropped 50A (223-183A). Bekasap fdr #6 dropped 69A (92-23A). 07:15 It was reported Spark at Recl.A for Tx.A EOR. 08:22 Checked & found Recl. A for Tx.-A T/O. 09:43 Checked Tx.-A 5Mva at EOR normal condition. 09:51 Opened LBS BKS4-5. 09:56 Closed bypass switch Recl.-A for Tx-A EOR. 09:57 Blocked Bekasap fdr#5, then release block at 10:17. 09:57 Closed LBS BKS4-5 feed power to TX-A EOR. (TX-A EOR back to normal). Cause: Unidentified. |  | 1 | 6:53 | Morning | Sunday | 2018 | 2
7926 | 2018-02-18 13:17 | 2018-02-18 13:17 | 13.8KV S. BALAM FEEDER #4 | Fair | Animal | 0 | 13:17 It was reported B/O fuse at well So.Balam#286 (So.Balam fdr#4). 15:05 Checked & found @1 B/O fuse for 100Kva Tx at well So.Balam #286. Replaced @1 B/O fuse above with the same size & Energized the Tx. Cause: Animal (Squirrel). |  | 1 | 13:17 | Afternoon | Sunday | 2018 | 2
7927 | 2018-02-18 15:56 | 2018-02-18 15:56 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 15:56 It was reported B/O fuse o/p MR-04D at Merapi Camp (D.Community fdr#2). 17:15 Replaced @1@2 B/O fuse for 50Kva Tx with the same size. Cause: Animal (monkey). |  | 1 | 15:56 | Afternoon | Sunday | 2018 | 2
7928 | 2018-02-19 08:03 | 2018-02-19 08:03 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Dead End Insulator | 0 | D Commy ACB #30 (feeder #2) T/R 1x. Not checked yet. |  | 1 | 8:03 | Morning | Monday | 2018 | 2
7929 | 2018-02-19 08:03 | 22/02/2018 08:03 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Dead End Insulator | 0 | Checked & found, Duri Community ACB #30 T/R 1x ctr: 92-93 R/F: 51N. Patrolled the line & found, @3 Flashed over Dead-end Insulator on Pole 2F 15. Cause: Dead-end Insulator. |  | 1 | 8:03 | Morning | Monday | 2018 | 2
7930 | 2018-02-19 09:08 | 2018-02-19 09:08 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified | 48 | 09:08 It was reported no power at 08-M3-08 D/S C Duri fdr#2 10:30 Checked & found Recl.08 M3 38 T/O Blocked position Ctr:NN. Patrolled the line but found nothing. 10:44 Blocked & Closed Recl.38 M3 38. Cause: Unidentified. |  | 1 | 9:08 | Morning | Monday | 2018 | 2
7931 | 2018-02-19 14:00 | 2018-02-19 14:00 | 13.8KV BEKASAP FEEDER #5 | Fair | Planned Maintenance | 0 | 14:00 Manually Opened LBS BKS4-5 (Bekasap fdr#5). Replaced B/O Broken Recl.-A for 5 Mva Tx-A at Bekasap EOR. 15:30 Closed LBS BKS4-5. Closed Isolation switch at Bekasap EOR. 15:40 Blocked & closed Recl-A for 5 Mva Tx-A at BKS EOR, then release the block. Cause: Plan Maintenance. |  | 1 | 14:00 | Afternoon | Monday | 2018 | 2
7932 | 2018-02-19 19:22 | 2018-02-19 19:22 | 115KV KOTABATAK JUNCTION - LIBO LINE | Rain and Lightning | Unidentified | 25 | KBJ- Libo 115KV GCB#53 T/R 1X. KBJ- Libo 115KV GCB#55 T/R 1X. Not checked yet. |  | 1 | 19:22 | Night | Monday | 2018 | 2
7933 | 2018-02-19 19:22 | 14/03/2018 08:20 | 115KV KOTABATAK JUNCTION - LIBO LINE | Rain and Lightning | Unidentified | 25 | 115KV Line KBJ - Libo T/R 1x by R/F: 67N. Checked & found- KBJSW-115KV GCB#53 T/R 1x, Ctr: 321 - 322 - KBJSW-115KV GCB#55 T/R 1x, Ctr: 235 - 236 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 19:22 | Night | Monday | 2018 | 2
7934 | 2018-02-20 13:48 | 2018-02-20 13:48 | CENTRAL DURI POWER PLANT |  |  | - | 13:48 S/U CGT#4, then on line the unit at 14:15. 14:14 Opened Tie breaker ACB#39. |  | 1 | 13:48 | Afternoon | Tuesday | 2018 | 2
7935 | 2018-02-20 14:38 | 2018-02-20 14:38 | MINAS POWER PLANT |  |  | - | 14:38 S/U MGT#10, then on line the unit at 14:55. (Running test). |  | 1 | 14:38 | Afternoon | Tuesday | 2018 | 2
7936 | 2018-02-20 16:12 | 2018-02-20 16:12 | CENTRAL DURI POWER PLANT |  |  | - | 16:12 Off line CGT#2, then S/D the unit for Maintenance. 16:17 Closed Tie Breaker ACB#19. |  | 1 | 16:12 | Afternoon | Tuesday | 2018 | 2
7937 | 2018-02-20 17:12 | 2018-02-20 17:12 | MINAS POWER PLANT |  |  | - | Off line MGT#8, then S/D the unit for Maintenance. |  | 1 | 17:12 | Afternoon | Tuesday | 2018 | 2
7938 | 2018-02-21 11:15 | 2018-02-21 11:15 | 13.8KV BATANG FEEDER #3 | Fair | Construction Job | 0 | 11:15 Manually opened recl.09-NG-06 d/s Batang Fdr #3 Installed 300KVATX for new wells at Candi 0.0.65B. 15:40 Manually blocked and Closed recl.09-NG-06 then release the blocked. Cause: Job Contruction. |  | 1 | 11:15 | Morning | Wednesday | 2018 | 2
7939 | 2018-02-21 14:14 | 2018-02-21 14:14 | 13.8KV 6DN FEEDER #1 | Fair | Unidentified | 45 | 14:14 6DN Fdr #1 T/R 1X. Not checked yet. |  | 1 | 14:14 | Afternoon | Wednesday | 2018 | 2
7940 | 2018-02-21 14:14 | 2018-05-03 14:14 | 13.8KV 6DN FEEDER #1 | Fair | Unidentified | 45 | Checked and found 6DN Fdr #1 T/R 1X Ctr: 159 - 160 R/F: 51 @3. Patrolled the line found nothing . Cause : Unidentified. |  | 1 | 14:14 | Afternoon | Wednesday | 2018 | 2
7941 | 2018-02-21 18:19 | 2018-02-21 18:19 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 0 | 18:19 Sintong GFPC T/R 1x. Sintong Fdr #2 Load drop 128A (216-82A). Ground fould alarm at Sintong Fdr #2. Not checked yet. |  | 1 | 18:19 | Afternoon | Wednesday | 2018 | 2
7942 | 2018-02-22 09:59 | 2018-02-22 09:59 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Construction Job | 0 | 09:59 Manually opened Recl.04.01.05 d/s CD Fdr #9 due to: Replace 112.5 KVATX to 150 KVATX o/p 04.01.14. Cause : Job Construction. |  | 1 | 9:59 | Morning | Thursday | 2018 | 2
7943 | 2018-02-22 11:40 | 2018-02-22 11:40 | NEW PETAPAHAN SUBSTATION | Fair | Planned Maintenance | 417 | SP Re-Energizing Power TX#1 New Petapahan. 11:56 Manually opened VCB Fdr #2 Closed at. 12:00 11:57 Manually opened VCB Fdr #3 Closed at. 11:59 11:58 Manually opened VCB Fdr #4 Closed at. 12:05. Cause : Plan Maintenance ( Service leakage TX #1). | 12345 | 1 | 11:40 | Morning | Thursday | 2018 | 2
7944 | 2018-02-22 16:26 | 2018-02-22 16:26 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 16:26 It was reported b/o fuse o/p 03.06.16 D/S C Duri fdr #7. 19:00 Checked and found @2 b/o fuse for 500 Kva Tx. Replaced b/o fuse above with the same size and energize the Tx. Cause: Unidentified. |  | 1 | 16:26 | Afternoon | Thursday | 2018 | 2
7945 | 2018-02-23 01:24 | 2018-02-23 01:24 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Unidentified | 0 | C Duri ACB #21 Fdr #4 T/R 1x Ctr:506-507 R/F: 51N. Not patrolled yet. |  | 1 | 1:24 | Night | Friday | 2018 | 2
7946 | 2018-02-23 01:24 | 2018-04-03 01:24 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked and found C. Duri ACB #21 Fdr #4 T/R 1x Ctr:506-507 R/F: 51N. Patrolled the line and found nothing. Cause : Unidentified. |  | 1 | 1:24 | Night | Friday | 2018 | 2
7947 | 2018-02-23 06:30 | 2018-02-23 06:30 | 13.8KV S. BALAM FEEDER #1 | Fair | Lightning Arrester | 7 | 06:30 So.Balam fdr#1 load dropped 81A (125-44A). So.Balam GFPC T/R 1x. 20:00 Checked & found Recl. 16Z25 T/R 1x Ctr:39-40. Patrolled the line & found @3 Broken LA on T/P So.Balam#136. Cause: Lightning. |  | 1 | 6:30 | Morning | Friday | 2018 | 2
7948 | 2018-02-23 09:20 | 2018-02-23 09:20 | NEW PETAPAHAN SUBSTATION | Fair | Planned Maintenance | 201 | SP De and Re-Energizing Power TX#2 New Petapahan. 09:48 Manually opened VCB Fdr #6 Closed at. 11:25 09:54 Manually opened VCB Fdr #7 Closed at. 11:26 09:52 Manually opened VCB Fdr #8 Closed at. 11:23. Cause : Plan Maintenance ( Service leakage TX #2). | 12345 | 1 | 9:20 | Morning | Friday | 2018 | 2
7949 | 2018-02-23 10:47 | 2018-02-23 10:47 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 109 | 10:47 Manually opened recl.36.BI.04 d/s Sobek Fdr #1 due to : Install 150 KVATX at Tagor #05 ( Reactive well ). 11:47 Manually blocked and closed recl.36.BI.04 then release the block. Cause : Planned Maintenance. |  | 1 | 10:47 | Morning | Friday | 2018 | 2
7950 | 2018-02-23 20:12 | 2018-02-23 20:12 | 13.8KV DURI FIELD FEEDER #4 | Fair | Others | 0 | 20:12 Duri Field SW Gear VCB #51 (feeder #4) T/R 1x. 20:55 It was reported spark on pole 07-V5-02 (Recloser in By pass position). 21:01 Duri Field SW Gear VCB #51 (feeder #4) T/R 1x again. 21:20 Patrolled the line found @1 by pass spark on Recloser 07-V5-02. 22:10 Manually open Duri Field VCB fdr #4 due to : - Opened by pass switch Recloser 07-V5-02. 22:17 Manually blocked and closed Duri Field VCB fdr #4 and then released the block. - Part of load Duri Field VCB fdr #4 (D/S Recloser 07-V5-02). transfer to Duri Fied fdr #2 by closed LBS 07-V5-21 at 22:25. Cause: Broken By pass switch. |  | 1 | 20:12 | Night | Friday | 2018 | 2
7951 | 2018-02-24 01:24 | 2018-02-24 01:24 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Powerline - Conductor | 257 | 01:24 C.Duri ACB#41 fdr#9 T/LO Ctr:380-383 R/F:51@1. 01:34 Blocked & Closed C.Duri ACB#41 fdr#9, but failed. 02:10 Patrolled the line & found @2 Broken Conductor between pole 04-5-13 -- 04-5-14. 02:19 Manually open Recl 04-5-02. Opened Visually opening Recl. 04-5-02. 02:31 Blocked & Closed C.Duri ACB#41 fdr#9, then release the block. 10:33 Manually closed Recl 04-5-02. After repaired @2 Broken Conductor between pole 04-5-13 -- 04-5-14. Cause: Broken conductor. |  | 1 | 1:24 | Night | Saturday | 2018 | 2
7952 | 2018-02-24 07:52 | 2018-02-24 07:52 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | 07:52 Duri Community Fdr #2 (13.8 KV ACB #25) T/R 1X Ctr: ............... R/F: ............... Cause : Not checked yet. |  | 1 | 7:52 | Morning | Saturday | 2018 | 2
7953 | 2018-02-24 07:52 | 2018-02-26 07:52 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB #30 fdr #2 T/R 1x ctr: 93-94 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:52 | Morning | Saturday | 2018 | 2
7954 | 2018-02-24 09:37 | 2018-02-24 09:37 | MINAS POWER PLANT |  |  | - | 09:37 S/U MGT #2 and Online at.09:55. due to NDC #2, 3 will be S/D for Offline wash and NDC #1 replaced Rotor until 20 March 2018. 10:35 Opened Tie 13.8 KV ACB #25 10:40 Closed Tie 13.8 KV ACB #8 10:46 Opened Tie 13.8 KV ACB #16 |  | 1 | 9:37 | Morning | Saturday | 2018 | 2
7955 | 2018-02-24 10:55 | 2018-02-24 10:55 | MINAS POWER PLANT |  |  | - | 10:55 S/U MGT #1 and Online at.11:20. due to NDC #2, 3 will be S/D for Offline wash and NDC #1 replaced Rotor until 20 March 2018 |  | 1 | 10:55 | Morning | Saturday | 2018 | 2
7956 | 2018-02-24 15:00 | 2018-02-24 15:00 | CENTRAL DURI POWER PLANT |  |  | - | 15:00 S/U CDGT #2 and Online at.15:27. due to NDC #2, 3 will be S/D for Offline wash and NDC #1 replaced Rotor until 20 March 2018. 15:23 Opened 13.8 KV ACB #19. |  | 1 | 15:00 | Afternoon | Saturday | 2018 | 2
7957 | 2018-02-24 17:07 | 2018-02-24 17:07 | MINAS POWER PLANT |  |  | - | 17:07 S/U MGT #2 and Online at.17:29. due to NDC #2, 3 will be S/D for Offline wash and NDC #1 . |  | 1 | 17:07 | Afternoon | Saturday | 2018 | 2
7958 | 2018-02-24 17:49 | 2018-02-24 17:49 | 13.8KV CENTRAL DURI FEEDER #14 | Cloudy | Unidentified | 0 | 17:49 ACB #27 (CD Fdr #14) T/R 1X, Ctr: 393-394 R/F: 51 @1, @2 Cause: Not checked yet. |  | 1 | 17:49 | Afternoon | Saturday | 2018 | 2
7959 | 2018-02-24 17:49 | 2018-04-03 17:49 | 13.8KV CENTRAL DURI FEEDER #14 | Cloudy | Unidentified | 0 | Checked and found C. Duri 13.8KV ACB Fdr #14 T/R 1X, Ctr: 393-394 R/F: 51@1, @2. Patrolled the line but nothing found. Cause : Unidentified. |  | 1 | 17:49 | Afternoon | Saturday | 2018 | 2
7960 | 2018-02-24 19:00 | 2018-02-24 19:00 | CENTRAL DURI POWER PLANT |  |  | - | 19:00 Offline CDGT #2 then S/D the unit for S/B 19:02 Closed Tie 13.8 KV ACB #19 |  | 1 | 19:00 | Night | Saturday | 2018 | 2
7961 | 2018-02-25 00:40 | 2018-02-25 00:40 | 13.8KV KOTABATAK FEEDER #2 | Fair | Animal | 71 | 00:40 OKB OCB fdr #2 T/R 1x. Not checked yet. 17:53 OKB OCB fdr #2 T/R 1x again. Not checked yet. |  | 1 | 0:40 | Night | Sunday | 2018 | 2
7962 | 2018-02-25 00:40 | 2018-02-26 00:40 | 13.8KV KOTABATAK FEEDER #2 | Fair | Animal | 71 | Checked & found, Kotabatak OCB fdr #2 T/R 1x ctr: 1310-1312 R/F: 51 @3. Patrolled the line & found, Death animal around Pole at Well KB #363. Cause: Animal. |  | 1 | 0:40 | Night | Sunday | 2018 | 2
7963 | 2018-02-25 10:46 | 2018-02-25 10:46 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse o/p 01.04.14 d/s DF Fdr #1,at Loc.5S-83D. Not checked yet. |  | 1 | 10:46 | Morning | Sunday | 2018 | 2
7964 | 2018-02-25 10:46 | 2018-02-26 10:00 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked & found, @3 B/O Fuse for 112.5KVA Tx on Pole 01-04-12. Replaced b/o Fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 10:46 | Morning | Sunday | 2018 | 2
7965 | 2018-02-25 14:00 | 2018-02-25 14:00 | CENTRAL DURI POWER PLANT |  |  | - | 14:00 S/U CDGT #2 and Online at.14:31. due to NDC #2, 3 will be S/D for Offline wash and NDC #1 replaced Rotor until 20 March 2018. 14:29 Opened 13.8 KV ACB #19. |  | 1 | 14:00 | Afternoon | Sunday | 2018 | 2
7966 | 2018-02-25 14:54 | 2018-02-25 14:54 | MINAS POWER PLANT |  |  | - | 14:54 S/U MGT #4 and Online at.15:05. due to NDC #2, 3 will be S/D for Offline wash and NDC #1 replaced Rotor until 20 March 2018. |  | 1 | 14:54 | Afternoon | Sunday | 2018 | 2
7967 | 2018-02-25 21:12 | 2018-02-25 21:12 | NORTH DURI POWER PLANT |  |  | - | Off line NDC#3, then S/D the unit for Maintenance. |  | 1 | 21:12 | Night | Sunday | 2018 | 2
7968 | 2018-02-25 21:47 | 2018-02-25 21:47 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse o/p 12-F9-07 (N.Duri fdr#5). Not checked yet. |  | 1 | 21:47 | Night | Sunday | 2018 | 2
7969 | 2018-02-25 21:47 | 2018-02-26 10:00 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified (Fuse) | 0 | Checked & found @1 B/O fuse for 225 KVA Tx O/P 12-F9-07 to AWT #12 (d/s ND fdr#5) Replaced b/o Fuse above with the same size then energized the Tx. Cause : Unidentified (Fuse) |  | 1 | 21:47 | Night | Sunday | 2018 | 2
7970 | 2018-02-25 22:42 | 2018-02-25 22:42 | 13.8KV 4D FEEDER #5 | Fair | Unidentified | 6 | 22:42 It was reported no power at well 3E-82, 3E-93, 3D-82, 3E91NP1 (4D fdr#5). 23:30 Checked & found Recl. 4D-14A T/SO Ctr:49-50. Blocked & closed Recl. 4D-14A, then release the block. Not patrolled yet. |  | 1 | 22:42 | Night | Sunday | 2018 | 2
7971 | 2018-02-25 22:42 | 2018-12-03 08:00 | 13.8KV 4D FEEDER #5 | Fair | Unidentified | 6 | Checked and found Recloser 4D-14A T/SO Ctr: 49-50 R/F: none. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 22:42 | Night | Sunday | 2018 | 2
7972 | 2018-02-26 15:05 | 2018-02-26 15:05 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 55 | It was reported b/o fuse o/p 05-P3-11 d/s CD Fdr #6. Not checked yet. |  | 1 | 15:05 | Afternoon | Monday | 2018 | 2
7973 | 2018-02-26 15:05 | 2018-02-27 14:50 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 55 | Checked & found @1 B/O fuse for 112.5KVATX. Replaced @1 B/O fuse with the same size then Energized the TX. Cause: unidentified |  | 1 | 15:05 | Afternoon | Monday | 2018 | 2
7974 | 2018-02-26 17:45 | 2018-02-26 17:45 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 5 | It was reported b/o fuse o/p 04-04-15A d/s CD Fdr #9. Not checked yet. |  | 1 | 17:45 | Afternoon | Monday | 2018 | 2
7975 | 2018-02-26 17:45 | 2018-04-03 17:45 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 5 | Checked and found @1, @2 and @3 b/o fuse for 112.5Kva TX. Replaced the b/o fuse above with same size then energized the TX. OK. Cause: Unidentified fuse. |  | 1 | 17:45 | Afternoon | Monday | 2018 | 2
7976 | 2018-02-26 19:25 | 2018-02-26 19:25 | NORTH DURI POWER PLANT |  |  | - | 19:25 S/U NDC #3 and then On line the unit at 22:13. |  | 1 | 19:25 | Night | Monday | 2018 | 2
7977 | 2018-02-26 23:30 | 2018-02-26 23:30 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Powerline - Hot Line Clamp | 0 | 23:30 Manually opened C Duri ACB #41 (feeder #9) due to: - Opened Fuse holder due to Spark on Hot Line Clamp on pole 04-05-10. 4 Wells were Off (5P-12A , 12C , 12E and 5P-21C). 23:39 Manually blocked and closed C Duri ACB #41 (feeder #9) and then released the block. Cause: Hot Line clamp. |  | 1 | 23:30 | Night | Monday | 2018 | 2
7978 | 2018-02-27 11:33 | 2018-02-27 11:33 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | NDC CT#1 Off line & S/D to Inspection, Repair Gen Rotor. |  | 1 | 11:33 | Morning | Tuesday | 2018 | 2
7979 | 2018-02-28 07:58 | 2018-02-28 07:58 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Pin Insulator | 0 | C. Duri 13.8KV ACB fdr #8 T/O ctr:442-443 R/F:51N, 51 @1. ( On block RIG BN #11 at well 3D 26B). Blocked and closed C. Duri |  | 1 | 7:58 | Morning | Wednesday | 2018 | 2
7980 | 2018-02-28 07:58 | 2018-04-03 07:58 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Pin Insulator | 0 | Checked and found C. Duri fdr #2 T/R 1X ctr: 442-443 R/F: 51N. Patrolled the line and found broken @2 Pin Insulator o/p: 04-08-25. Cause: Pin Insulator. |  | 1 | 7:58 | Morning | Wednesday | 2018 | 2
7981 | 2018-02-28 10:48 | 2018-02-28 10:48 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 0 | Petani 13.8KV OCB fdr #2 T/R 1X. Petani fdr #1 dropped 42A (202 - 160A). Not checked yet. |  | 1 | 10:48 | Morning | Wednesday | 2018 | 2
7982 | 2018-02-28 10:48 | 2018-05-03 10:48 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 0 | Checked & found, Petani fdr #2 T/R 1x ctr: 245-246 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:48 | Morning | Wednesday | 2018 | 2
7983 | 2018-02-28 16:59 | 2018-02-28 16:59 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri Community 13.8KV ACB fdr #2 T/R 1X. Not checked yet. |  | 1 | 16:59 | Afternoon | Wednesday | 2018 | 2
7984 | 2018-02-28 16:59 | 2018-05-03 16:59 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Chceked & found, Duri Community ACB #30 fdr #2 T/R 1x ctr: 93-94 R/F: - Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:59 | Afternoon | Wednesday | 2018 | 2
7985 | 2018-01-03 05:00 | 2018-01-03 05:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Theft | 0 | It was reported b/o fuse o/p.10.K6.33 d/s ND Fdr #2. Cause: Not checked yet. |  | 1 | 5:00 | Morning | Wednesday | 2018 | 1
7986 | 2018-01-03 05:00 | 2018-04-03 05:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Theft | 0 | Cecked and found @1, @2 &2@3 b/o fuse for 112.5Kva TX o/p 20 K6 33. Replaced Secondary cable then energized the TX. Cause: theft. |  | 1 | 5:00 | Morning | Wednesday | 2018 | 1
7987 | 2018-01-03 14:33 | 2018-01-03 14:33 | 13.8KV SINTONG FEEDER #2 | Fair | Construction Job | 0 | 14:33 Manually open Recl. 28 AF 02, --->and Closed at 15:45. Tie In Power line at well Benar #53 (New well). Cause: Project. |  | 1 | 14:33 | Afternoon | Wednesday | 2018 | 1
7988 | 2018-02-03 11:06 | 2018-02-03 11:06 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 41 | 11:06 Open Recloser 32-AK-04 , and Closed at: 11:58. Replaced 225KVA TX to 300KVA TX at well Kelok #12. Cause:Planned maintenance. |  | 1 | 11:06 | Morning | Saturday | 2018 | 2
7989 | 2018-02-03 14:50 | 2018-02-03 14:50 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Construction Job | 0 | 14:50 Open Recloser 28-CX-05 (d/s Petapahan fdr #3) To Tie in Power line at Well Petapahan #144 19:00 Closed Back the Recloser, after finished the Jobs Cause: Planned construction (Project). |  | 1 | 14:50 | Afternoon | Saturday | 2018 | 2
7990 | 2018-02-03 17:17 | 2018-02-03 17:17 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse o/p 01-4-14 (d/s C.Duri #6). Not checked yet. |  | 1 | 17:17 | Afternoon | Saturday | 2018 | 2
7991 | 2018-02-03 17:17 | 2018-04-03 17:17 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 0 | Checked and found @3 b/o fuse for 112.5Kva o/p: 01-04-14. Replaced the b/o fuse above with same size then energized the TX. Cause: Unidentified fuse. |  | 1 | 17:17 | Afternoon | Saturday | 2018 | 2
7992 | 2018-02-03 18:00 | 2018-02-03 18:00 | 13.8KV BANGKO FEEDER #1 | Fair | Low mega-ohm reading | 112 | 18:00 It was reported b/o fuse at well Bangko # 218. Not checked yet. |  | 1 | 18:00 | Afternoon | Saturday | 2018 | 2
7993 | 2018-02-03 18:00 | 2018-03-03 15:10 | 13.8KV BANGKO FEEDER #1 | Fair | Low mega-ohm reading | 112 | 15:10 Checked and found @1, @3 b/o fuse for 150KVA TX. Performed TTR test and Megger the TX and found Low Mega ohm reading TX. Replaced 150 KVA TX to 206KVA TX at well Bangko #218. Cause: TX Low Meg. Reading. |  | 1 | 18:00 | Afternoon | Saturday | 2018 | 2
7994 | 2018-03-03 04:07 | 2018-03-03 04:07 | 44KV MINAS - RUMBAI LINE | Drizzle | Unidentified | 0 | 04:07 13.8 KV ACB #21 ( Rumbai Fdr ) T/R 1X, R/F: 21 Ctr: 84-85. Cause : Not checked yet. |  | 1 | 4:07 | Morning | Saturday | 2018 | 3
7995 | 2018-03-03 04:07 | 2018-11-03 10:00 | 44KV MINAS - RUMBAI LINE | Drizzle | Unidentified | 0 | Checked and found ACB #21 ( Rumbai Fdr ) T/R 1X, R/F: 21 Ctr: 84-85. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 4:07 | Morning | Saturday | 2018 | 3
7996 | 2018-03-03 09:06 | 2018-03-03 09:06 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | 0 | 09:06 Manually Open Bangko OCB fdr #1, and closed at 09:07 Open Hot Line clamp to/p Bangko #240. Project. |  | 1 | 9:06 | Morning | Saturday | 2018 | 3
7997 | 2018-03-03 12:51 | 2018-03-03 12:51 | 13.8KV 4D FEEDER #2 | Drizzle | Unidentified | 47 | 4D 13.8KV OCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 12:51 | Afternoon | Saturday | 2018 | 3
7998 | 2018-03-03 12:51 | 2018-08-03 10:00 | 13.8KV 4D FEEDER #2 | Drizzle | Unidentified | 47 | Checked and found 4D 13.8KV OCB fdr #2 T/R 1X, CTR:255 - 256, R/F:51N. Patrol the line found nothing. Cause : Unidentified. |  | 1 | 12:51 | Afternoon | Saturday | 2018 | 3
7999 | 2018-03-03 13:06 | 2018-03-03 13:06 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 55 | 5B 13.8KV OCB fdr #2 T/R 1X. -----------> Prod Loss: 43 Bbls, 16 Wells 5B fdr #1 load dropped 70A (90-20A).----> Prod Loss: 29 Bbls, 12 Wells 5B fdr #3 load dropped 32A (44-12A).----> Prod Loss: 15 Bbls, 8 Wells 5B fdr #6 load dropped 183A (186-20A),-> WIP. Total Loss: 87 Bbls, 36 Wells Not checked yet. |  | 1 | 13:06 | Afternoon | Saturday | 2018 | 3
8000 | 2018-03-03 13:06 | 2018-07-03 13:06 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 55 | Checked & found, 5B OCB fdr #2 T/R 1x ctr: 385-386 R/F: 51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 13:06 | Afternoon | Saturday | 2018 | 3
8001 | 2018-03-03 14:03 | 2018-03-03 14:03 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | N. Duri 13.8KV VCB fdr #2 T/R 1X. not checked yet. |  | 1 | 14:03 | Afternoon | Saturday | 2018 | 3
8002 | 2018-03-03 14:03 | 2018-04-03 14:03 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | Checked and found N. Duri 13.8KV VCB fdr #2 T/R 1X ctr: 267-268 R/F: 51 @1, @2 & @3. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:03 | Afternoon | Saturday | 2018 | 3
8003 | 2018-03-03 14:39 | 2018-03-03 14:39 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Unidentified | 81 | C.Duri 13.8KV ACB fdr #1 T/R 1X. Ctr:216-217, R/F:51G, 51N Not checked yet. |  | 1 | 14:39 | Afternoon | Saturday | 2018 | 3
8004 | 2018-03-03 14:39 | 2018-05-03 08:00 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Unidentified | 81 | Checked and found 13.8 KV ACB #11 T/R 1x R/F: 51 @1 Ctr: 216-217 Patrolled the line but found nothing. Cuase: Unidentified. |  | 1 | 14:39 | Afternoon | Saturday | 2018 | 3
8005 | 2018-03-03 14:40 | 2018-03-03 14:40 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 39 | 14:40 Bangko 13.8KV OCB fdr #4 T/SO 1X. Bangko fdr #1 load dropped 8A (147-139A). Bangko fdr #2 load dropped 32A (251-219A),----->WIP. 14:50 Checked and found Bangko fdr #4 T/SO CTR:28-29. R/F:S35 Operate. 15:00 Blocked and Closed Bangko 13.8KV OCB fdr #4 , than release the blocked. Not Patrolled yet. |  | 1 | 14:40 | Afternoon | Saturday | 2018 | 3
8006 | 2018-03-03 14:40 | 2018-04-03 14:40 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 39 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:40 | Afternoon | Saturday | 2018 | 3
8007 | 2018-03-03 14:45 | 2018-03-03 14:45 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Switchboard Problem | 0 | D.field 13.8KV AVCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 14:45 | Afternoon | Saturday | 2018 | 3
8008 | 2018-03-03 15:44 | 2018-03-03 15:44 | 13.8KV MINAS FEEDER #1 | Lightning | Lightning | 8 | Minas 13.8KV ACB fdr #1 T/R 2X Ctr:75-77 R/F:51N. Not patrolled yet. |  | 1 | 15:44 | Afternoon | Saturday | 2018 | 3
8009 | 2018-03-03 15:44 | 2018-09-03 10:00 | 13.8KV MINAS FEEDER #1 | Lightning | Lightning | 8 | Checked and found Minas 13.8KV ACB fdr #1 T/R 2X Ctr:75-77 R/F:None. Patrolled the line found nothing. Cause : Lightning. |  | 1 | 15:44 | Afternoon | Saturday | 2018 | 3
8010 | 2018-03-03 15:50 | 2018-03-03 15:50 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 75 | 6DN 13.8KV OCB fdr #5 T/R 1X. --------> Prod Loss: 49 Bbls, 22 Wells 6DN fdr #6 dropped 156A (175-19A) ---> Prod Loss: 67 Bbls, 33 Wells 6DN fdr #4 dropped 212A (214-2A),----->WIP. 6DN fdr #3 dropped 122A (187-65A),---> WIP. 6DN fdr #2 dropped 142A (247-105A).-->Prod Loss: 92 Bbls, 39 Wells 6DN fdr #1 dropped 9A (128-119A). Total Loss: 208 Bbls, 94 Wells Not checked yet. |  | 1 | 15:50 | Afternoon | Saturday | 2018 | 3
8011 | 2018-03-03 15:50 | 2018-12-03 08:50 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 75 | Checked and found 13.8KV OCB #5 T/R Ctr: 782 (not change) R/F: None. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 15:50 | Afternoon | Saturday | 2018 | 3
8012 | 2018-03-03 16:02 | 2018-03-03 16:02 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 29 | 8D 13.8KV OCB fdr #5 T/R 1X. 8D fdr #1 dropped 102A (122-20A). 8D fdr #2 dropped 63A (102-39A). 8D fdr #3 dropped 34A (88-54A). 8D fdr #4 dropped 58A (168-110A),----->WIP. Not checked yet. |  | 1 | 16:02 | Afternoon | Saturday | 2018 | 3
8013 | 2018-03-03 16:02 | 2018-09-03 10:00 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 29 | Checked and found 8D OCB fdr #5 T/R 1X CTR:566-566 (Did not changed) R/F:51N. Patrol the line found nothing. Cause: Suspected Lightning. |  | 1 | 16:02 | Afternoon | Saturday | 2018 | 3
8014 | 2018-03-03 16:06 | 2018-03-03 16:06 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 55 | 8C 13.8KV VCB fdr #6 T/R 1X,----->WIP. 8C fdr #4 dropped 59A (168-109A),----->WIP. 8C fdr #5 dropped 58A (238-180A),----->WIP. Not checked yet. |  | 1 | 16:06 | Afternoon | Saturday | 2018 | 3
8015 | 2018-03-03 16:06 | 2018-12-03 08:06 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 55 | Checked and found 13.8KV VCB fdr #6 T/R 1x Ctr: 587-588 R/F: 50. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 16:06 | Afternoon | Saturday | 2018 | 3
8016 | 2018-03-03 16:10 | 2018-03-03 16:10 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning Arrester | 0 | 8C 13.8KV VCB fdr #4 T/R 1X, ---->WIP. Not checked yet. |  | 1 | 16:10 | Afternoon | Saturday | 2018 | 3
8017 | 2018-03-03 16:10 | 2018-09-03 10:00 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning Arrester | 0 | Checked and found 8C 13.8KV VCB fdr #4 T/R 1X, ---->WIP. CTR:602 - 603, R/F:51 Patrolled the line found nothing. Cause : Lightning. |  | 1 | 16:10 | Afternoon | Saturday | 2018 | 3
8018 | 2018-03-03 16:13 | 2018-03-03 16:13 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Lightning | 38 | Minas fdr #2 load dropped 128A (282-154). Not checked yet. |  | 1 | 16:13 | Afternoon | Saturday | 2018 | 3
8019 | 2018-03-03 16:13 | 2018-12-03 08:13 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Lightning | 38 | Checked and found Recloser M2-01 T/R 2x Ctr: 47-49 R/F: None. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 16:13 | Afternoon | Saturday | 2018 | 3
8020 | 2018-03-03 20:11 | 2018-03-03 20:11 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 233 | 20:11 ND Fdr #2 Load drop 30A (244-214A) 21:20 It was reported no power o/p 13.G7.1.06 Checked & found Recl. 13-G7.1-10 T/O, Without indication. 22:45 Block & Closed the Recloser, but Fail. RePatrolled the Line, but found nothing, 00:45 Blocked & Closed the Recloser, then Released the Block Cause : Unidentified. |  | 1 | 20:11 | Night | Saturday | 2018 | 3
8021 | 2018-04-03 10:35 | 2018-04-03 10:35 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Construction Job | 0 | 10:35 Opened Recl. 28-CX-05 (d/s Petapahan fdr#3) to Tie in New Conductor toward Well PTH #144. 12:45 Closed back the Recloser after finished the Jobs. Cause: Planned construction (Tie In). |  | 1 | 10:35 | Morning | Tuesday | 2018 | 4
8022 | 2018-04-03 14:27 | 2018-04-03 14:27 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 44 | 14:27 It was reported b/o fuse @2 at Puncak #8 d/s C.Duri fdr #1. Checked and found @2 b/o fuse for 100KVA TX. Replaced the b/o fuse above with same size then energize the TX. Cause:Unidentified (fuse ). |  | 1 | 14:27 | Afternoon | Tuesday | 2018 | 4
8023 | 2018-04-03 17:59 | 2018-04-03 17:59 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Animal | 153 | 17:59 NKBS 13.8 KV VCB fdr #3 T/R 1X. NKBS GFPC T/R 1X. It was reported stronger sound of TX at KBGS. 19:50 Checked and found NKBS fdr#3 T/R 1X ctr: 316-317 R/F: 51N, 51@1, @2 & @3. Also found @1,@2 b/o fuse for 300KVA TX at Kotabatak GS. Replace b/o fuse above with same size,then energize the TX. Cause: Animal (cat ). |  | 1 | 17:59 | Afternoon | Tuesday | 2018 | 4
8024 | 2018-05-03 11:28 | 2018-05-03 11:28 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Lightning | 0 | Duri Comm 13.8KV ACB fdr #5 T/R 1X. Not checked yet. |  | 1 | 11:28 | Morning | Thursday | 2018 | 5
8025 | 2018-05-03 11:28 | 13/03/2018 08:00 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked and found 13.8KV ACB #33 T/R 1x Ctr: 118-119 R/F: 51N. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 11:28 | Morning | Thursday | 2018 | 5
8026 | 2018-05-03 11:33 | 2018-05-03 11:33 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Tree | 0 | Duri Comm 13.8KV ACB fdr #3 T/R 1X. Not checked yet. |  | 1 | 11:33 | Morning | Thursday | 2018 | 5
8027 | 2018-05-03 11:33 | 2018-12-03 08:33 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Tree | 0 | Checked and found 13.8KV ACB #26 T/R 2x Ctr: 67-69 R/F: 51N @1. Patrolled the line and found danger high tree. Cause: Tree. |  | 1 | 11:33 | Morning | Thursday | 2018 | 5
8028 | 2018-05-03 11:40 | 2018-05-03 11:40 | 13.8KV BATANG FEEDER #2 | Fair | Construction Job | 0 | 11:40 Manually Open Batang 13.8KV OCB fdr #2 ctr:158-159. To Stopple plugging and Tapping at Batang Booster Pump. 17:19 Closed Batang 13.8KV OCB fdr #2. Cause: Project. |  | 1 | 11:40 | Morning | Thursday | 2018 | 5
8029 | 2018-05-03 14:05 | 2018-05-03 14:05 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 42 | Bangko 13.8KV OCB fdr #4 T/R 1X. Bangko fdr #1 load dropped 28A (146-118A). Bangko fdr #2 load dropped 110A (354-144A ) ---->EOR. Ground fault alarm from Bangko fdr #4. Nella fdr #1 load dropped 42A (209-167A). Nella fdr #2 load dropped 11A (67-56A). Not cheked yet. |  | 1 | 14:05 | Afternoon | Thursday | 2018 | 5
8030 | 2018-05-03 14:05 | 2018-06-03 14:05 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 42 | Checked & found, Bangko OCB fdr #4 T/R 1x ctr: 29-30 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:05 | Afternoon | Thursday | 2018 | 5
8031 | 2018-05-03 14:35 | 2018-05-03 14:35 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Animal | 81 | Ketigul 13.8KV VCB fdr #2 T/R 1X. Ketigul fdr #1 load dropped 12A (113-101A). Not checked yet. |  | 1 | 14:35 | Afternoon | Thursday | 2018 | 5
8032 | 2018-05-03 14:35 | 2018-12-03 08:35 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Animal | 81 | Checked and found 13.8KV VCB fdr #2 T/R 1x Ctr: 264-265 R/F: 51N @2, @3. Patrolled the line and found animal o/p Pagar #31. Cause: Animal. |  | 1 | 14:35 | Afternoon | Thursday | 2018 | 5
8033 | 2018-05-03 14:52 | 2018-05-03 14:52 | 13.8KV 6D FEEDER #2 | Fair | Tree | 143 | 14:52 6D 13.8KV #2 Load dropped 138A (206-68A). Not checked yet. 15:45 It was reported no power around well 6D-79, d/s 6D fdr #2. 16:50 Checked and found Recloser 6D-298 T/LO, CTR:69-74. Patrolled the line and found the true HLT Power line at well 6D-53. Remove the Tree from Power line. 16;58 Blocked and Closed Recloser 6D-298. Ok then released the block. Cause: Tree. (Prod Loss GS3: 166 Bbls, 22 Wells) (Prod Loss GS4: 25 Bbls, 13 Wells) |  | 1 | 14:52 | Afternoon | Thursday | 2018 | 5
8034 | 2018-05-03 15:36 | 2018-05-03 15:36 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 77 | 15:36 Manually Opened Recloser 37 BD 40 (d/s Bekasap fdr#2) to replace 150KVATX dueto Failure, at Well BKS#170 16:26 Manually Block & Closed the Recloser after finished the Jobs, then released the Block. Cause: Planned Maintenance. |  | 1 | 15:36 | Afternoon | Thursday | 2018 | 5
8035 | 2018-05-03 16:49 | 2018-05-03 16:49 | 13.8KV CENTRAL DURI FEEDER #3 | Cloudy | Unidentified | 0 | C.Duri 13.8KV ACB fdr #3 T/R 1X. Not checked yet. |  | 1 | 16:49 | Afternoon | Thursday | 2018 | 5
8036 | 2018-05-03 16:49 | 2018-07-03 16:49 | 13.8KV CENTRAL DURI FEEDER #3 | Cloudy | Unidentified | 0 | Checked & found, Central Duri ACB #13 fdr#3 T/R 1x ctr: 205-206 R/F: 51 @2, @3. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:49 | Afternoon | Thursday | 2018 | 5
8037 | 2018-06-03 10:05 | 2018-06-03 10:05 | 13.8KV BATANG FEEDER #2 | Fair | Construction Job | 0 | 10:05 Manually Open Batang 13.8KV OCB fdr #2 ctr:159-160. To Stopple plugging and Tapping at Batang Booster Pump. 17:46 Closed Batang 13.8KV OCB fdr #2. Cause: Project. |  | 1 | 10:05 | Morning | Sunday | 2018 | 6
8038 | 2018-06-03 10:23 | 2018-06-03 10:23 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 57 | 10:23 It was reported b/o fuse o/p # 03-03-23F. (4 wells off down). No checked yet. |  | 1 | 10:23 | Morning | Sunday | 2018 | 6
8039 | 2018-06-03 10:23 | 2018-07-03 10:00 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 57 | Checked & found, @2 B/O fuse for 112.5KVA Tx on Pole 03-03-23B. Replaced b/o Fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 10:23 | Morning | Sunday | 2018 | 6
8040 | 2018-06-03 17:19 | 2018-06-03 17:19 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Animal | 47 | 17:19 Ketigul 13.8KV VCB fdr #1 T/R 1X. Ketigul fdr #2 load dropped 53A (192-139A). Ketigul fdr #3 load dropped 21A (24-3A). Not checked yet. |  | 1 | 17:19 | Afternoon | Sunday | 2018 | 6
8041 | 2018-06-03 17:19 | 2018-12-03 08:19 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Animal | 47 | Checked and found 13.8KV VCB #1 T/R 1x Ctr: 198-199 R/F: 51N @1,@2. Patrolled the line and found dead animal around pole 32-AK-16. Cause: Animal. |  | 1 | 17:19 | Afternoon | Sunday | 2018 | 6
8042 | 2018-07-03 07:02 | 2018-07-03 07:02 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 0 | 07:02 Manually Open Rangau 13.8KV OCB fdr #2. Replaced 16” trunk line Rangau GS to Pematang GS. On March 08, 2018. 00:30 Closed Rangau 13.8KV OCB fdr #2. Project. |  | 1 | 7:02 | Morning | Tuesday | 2018 | 7
8043 | 2018-07-03 08:01 | 2018-07-03 08:01 | 13.8KV NORTH DURI FEEDER #9 | Fair | Theft | 0 | 08:00 It was reported no power o/p 11-J2-19 D/S ND#9. 15:00 Checked & found missing secondary cable. Will be replace Saturday morning. |  | 1 | 8:01 | Morning | Tuesday | 2018 | 7
8044 | 2018-07-03 08:01 | 2018-10-03 09:30 | 13.8KV NORTH DURI FEEDER #9 | Fair | Theft | 0 | Re-Installed Sec. Cable & Energized 112.5Kva Tx o/p 11-J2-11 (N.Duri fdr#9). Cause: Theft. |  | 1 | 8:01 | Morning | Tuesday | 2018 | 7
8045 | 2018-07-03 08:02 | 2018-07-03 08:02 | 13.8KV NORTH DURI FEEDER #9 | Fair | Theft | 0 | 08:02 It was reported no power o/p 11-J2-11 D/S ND#9. 15:15 Checked & found missing secondary cable. Will be replace Saturday morning. |  | 1 | 8:02 | Morning | Tuesday | 2018 | 7
8046 | 2018-07-03 08:02 | 2018-10-03 09:30 | 13.8KV NORTH DURI FEEDER #9 | Fair | Theft | 0 | Re-Installed Sec. Cable & Energized 112.5Kva Tx o/p 11-J2-19B (N.Duri fdr#9). Cause: Theft. |  | 1 | 8:02 | Morning | Tuesday | 2018 | 7
8047 | 2018-07-03 13:38 | 2018-07-03 13:38 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Lightning | 148 | So.Balam VCB fdr#4 T/R 1x. Not checked yet. |  | 1 | 13:38 | Afternoon | Tuesday | 2018 | 7
8048 | 2018-07-03 13:38 | 2018-09-03 07:38 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Lightning | 148 | Checked & found So.Balam fdr#4 T/R 1x Ctr:351-352 R/F:51N. Patrolled the line & found @2 Broken LA on T/P So.Balam#41. Cause : Lightning. |  | 1 | 13:38 | Afternoon | Tuesday | 2018 | 7
8049 | 2018-07-03 19:04 | 2018-07-03 19:04 | 13.8KV KOTABATAK FEEDER #2 | Fair | Animal | 160 | 19:04 OKB 13.8KV OCB fdr #2 T/SO. OKB 79CO Block position Appeared. 20:10 Checked and found OKB fdr #2 T/SO crt: 1313-1314 R/F: 51N. and also found 79CO on normal position. 20:15 Blocked and closed OKB fdr #2. OK (from local), then released the block (failed from DSC). (at DSC 79CO of OKB fdr #2 back to normal position). Not patrooled yet. |  | 1 | 19:04 | Night | Tuesday | 2018 | 7
8050 | 2018-07-03 19:04 | 2018-10-03 14:00 | 13.8KV KOTABATAK FEEDER #2 | Fair | Animal | 160 | Checked and found OKB OCB fdr #2 T/SO Counter: 1313-1314 R/F: 51N. Patrolled the line found animal (bird) under the terminal pole KB #345. Cause: Animal (Bird). |  | 1 | 19:04 | Night | Tuesday | 2018 | 7
8051 | 2018-08-03 03:11 | 2018-08-03 03:11 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 160 | 03:11 Bangko fdr#4 load dropped 105A (177-72A) Bangko fdr#1 Load dropped 97A (145-48A). Bangko GFPC T/R 1X. Fault alarm on fdr#4. 17:00 Checked & found Bangko fdr#4 T/R 1x Ctr:30-31 R/F:NN. Bangko GFPC T/R 1x Ctr:166-167. Patrolled the line & found @2@3 Flashed Over Dead End Insulator Near pole Catodic Batang Ibul. @2 Broken LA on T/P Bangko#178. @3 Broken Dead End Insulator o/p 25AA03. @1 Broken LA o/p 25AB17. Cause: Lightning. |  | 1 | 3:11 | Night | Friday | 2018 | 8
8052 | 2018-08-03 11:18 | 2018-08-03 11:18 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 16 | 11:18 Manually opened Recl.2D-38 D/S 3D Fdr#4. Replace B/O 250Kva Tx whit 300Kva Tx at well 2D-73. 11:59 Blocked and Closed Recl. 2D-38, then released the Block. Cause :Plan maintenance. |  | 1 | 11:18 | Morning | Friday | 2018 | 8
8053 | 2018-08-03 20:18 | 2018-08-03 20:18 | 13.8KV LIBO FEEDER #1 | Fair | Lightning Arrester | 277 | It was reported B/O fuse at well Se.Libo#56 (Libo fdr#1). Not checked yet. |  | 1 | 20:18 | Night | Friday | 2018 | 8
8054 | 2018-08-03 20:18 | 2018-10-03 15:25 | 13.8KV LIBO FEEDER #1 | Fair | Lightning Arrester | 277 | Checked & found @1@2@3 B/O fuse for 300Kva Tx at well Se.Libo#56 (Libo fdr#1). Te3sted TTR & Megger 300Kva Tx Low megger. (Would be changed tomorrow). Cause: Transformer Low Megger. |  | 1 | 20:18 | Night | Friday | 2018 | 8
8055 | 2018-08-03 20:18 | 2018-11-03 14:35 | 13.8KV LIBO FEEDER #1 | Fair | Lightning Arrester | 277 | Re-checked & found @1@2@3 Broken LA at 300Kva Tx at well Se.Libo#56. Replaced @1@2@3 Broken LA at well Se.Libo#56, then energized the Tx. Cause: Broken LA. |  | 1 | 20:18 | Night | Friday | 2018 | 8
8056 | 2018-09-03 13:38 | 2018-09-03 13:38 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 107 | It was reported B/O fuse at well Pagar#31 (Ketigul fdr#2). Not checked yet. |  | 1 | 13:38 | Afternoon | Monday | 2018 | 9
8057 | 2018-09-03 13:38 | 2018-10-03 10:27 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 107 | Checked & found@1@2 B/O fuse for 300Kva Tx at well Pagar#31. Replaced @1@2 B/O fuse above with the same size & Energized the Tx. Cause: Animal (Bird). |  | 1 | 13:38 | Afternoon | Monday | 2018 | 9
8058 | 2018-10-03 17:43 | 2018-10-03 17:43 | MINAS POWER PLANT | Fair | Under investigation | 0 | 17:43 MGT#10 Tripped by Computer Auto Reboot (Freq:59.84). No load shedding occurred. 18:17 S/U MGT#10, then on line the unit at 18:34. Cause: Under Investigation. |  | 1 | 17:43 | Afternoon | Wednesday | 2018 | 10
8059 | 2018-10-03 18:02 | 2018-10-03 18:02 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Animal | 37 | C.Duri ACB#11 fdr#1 T/R 1x Ctr:317-318 R/F:51N. Not patrolled yet. |  | 1 | 18:02 | Afternoon | Wednesday | 2018 | 10
8060 | 2018-10-03 18:02 | 2018-11-03 17:02 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Animal | 37 | Patrolled the line & found Dead Monkey near pole 40AU02. Cause : Animal (Monkey). |  | 1 | 18:02 | Afternoon | Wednesday | 2018 | 10
8061 | 2018-10-03 18:17 | 2018-10-03 18:17 | MINAS POWER PLANT |  |  | - | 18:17 S/U MGT#10, then on line the unit at 18:34. |  | 1 | 18:17 | Afternoon | Wednesday | 2018 | 10
8062 | 2018-11-03 00:02 | 2018-11-03 00:02 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 42 | Pinang 13.8KV OCB fdr#1 T/R 1X. Not checked yet. |  | 1 | 0:02 | Night | Saturday | 2018 | 11
8063 | 2018-11-03 00:02 | 2018-12-03 17:02 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 42 | Checked & found Pinang fdr#1 T/R 1x Ctr:433-434 R/F:51N. Patrolled the line & found @1 Broken Pin Insulator o/p 12E11. Cause : Lightning. |  | 1 | 0:02 | Night | Saturday | 2018 | 11
8064 | 2018-11-03 12:26 | 2018-11-03 12:26 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 0 | Ketigul fdr#2 Load dropped 168A (193-25A). Not checked yet. |  | 1 | 12:26 | Afternoon | Saturday | 2018 | 11
8065 | 2018-11-03 12:26 | 2018-12-03 17:26 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 0 | Checked & found Recl. 19AL03 T/R 1x Ctr:130-131. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 12:26 | Afternoon | Saturday | 2018 | 11
8066 | 2018-11-03 15:40 | 2018-11-03 15:40 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Animal | 11 | 15:40 It was reported B/O fuse o/p 03-4-05 (C.Duri fdr#3). 16:45 Replaced @1@2 B/O fuse for 112.5 Kva Tx with the same size. Cause: Animal (Monkey). |  | 1 | 15:40 | Afternoon | Saturday | 2018 | 11
8067 | 2018-12-03 06:54 | 2018-12-03 06:54 | 13.8KV RANGAU FEEDER #2 | Cloudy | Tree | 29 | Rangau fdr#2 load dropped 110A (128-18A). Not checked yet. |  | 1 | 6:54 | Morning | Monday | 2018 | 12
8068 | 2018-12-03 06:54 | 15/03/2018 06:54 | 13.8KV RANGAU FEEDER #2 | Cloudy | Tree | 29 | Checked & found, Recloser 23 BD 01 T/R 1x ctr: 321-322 R/F: 51N. Patrolled the line & found, high danger Tree under powerline toward Well Jurong #06. Cause: Tree. |  | 1 | 6:54 | Morning | Monday | 2018 | 12
8069 | 2018-12-03 10:12 | 2018-12-03 10:12 | MINAS POWER PLANT |  |  | - | Off line MGT#4, the S/D the unit for maintenance Bearing#2 Leak. |  | 1 | 10:12 | Morning | Monday | 2018 | 12
8070 | 2018-12-03 11:20 | 2018-12-03 11:20 | 13.8KV MENGGALA FEEDER #1 | Fair | Planned Maintenance | 26 | 11:20 Manually opened Rcl. 19AO01 So.Menggala (MGL fdr#1). Replaced 750Kva Tx with the same size at So.Menggala GS. 12:45 Blocked & closed Recl. 19AO01, then release the block. Cause: Plan Maintenance. |  | 1 | 11:20 | Morning | Monday | 2018 | 12
8071 | 2018-12-03 14:42 | 2018-12-03 14:42 | 13.8KV 8D FEEDER #7 | Fair | Planned Maintenance | 132 | 14:42 Manually opened 8D OCB fdr#7. Cut jumper o/p NN for replaced 2500 Kva Tx at GS#1. 15:00 Blocked & closed 8D OCB fdr#7, then release the block. Cause: Plan Maintenance. |  | 1 | 14:42 | Afternoon | Monday | 2018 | 12
8072 | 2018-03-13 09:20 | 2018-03-13 09:20 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 348 | 09:20 It was reported no power o/p 11-J2-05 (N.Duri fdr#9). 09:45 Checked & found Recl.11-J2-05 T/O (Block position) Ctr:45-46. Blocked & closed Recl. 11-J2-05. 10:00 Patrolled the line but found nothing. Cause: Unidentified |  | 1 | 9:20 | Morning | Tuesday | 2018 | 3
8073 | 2018-03-13 09:40 | 2018-03-13 09:40 | 13.8KV BANGKO FEEDER #1 | Fair | Construction Job | 0 | 09:40 Manually opened Bangko VCB fdr#1. Relocated Power line for Tie In new location Bangko field. 10:16 Blocked & closed Bangko VCb fdr#1, then release the block. Cause: Construction job. |  | 1 | 9:40 | Morning | Tuesday | 2018 | 3
8074 | 2018-03-13 11:27 | 2018-03-13 11:27 | 13.8KV DURI FIELD FEEDER #2 | Fair | Planned Maintenance | 0 | 11:27 Manually open LBS 07-V5-21 (D.Field fdr#2). Replaced @1 Broken Pin Insulator o/p 07-V5-11. 12:00 Manually closed LBS 07-V5-21. Cause: Plan Maintenance. |  | 1 | 11:27 | Morning | Tuesday | 2018 | 3
8075 | 2018-03-13 11:37 | 2018-03-13 11:37 | 13.8KV KETIGUL FEEDER#3 | Fair | Planned Maintenance | 38 | 11:37 Manually Opened LBS 32AN01 (Ketigul fdr#3). Repaired Hot Spot on T/P Gulamo#1. 12:56 Manually closed LBS 32AN01. Cause: Plan Maintenance. |  | 1 | 11:37 | Morning | Tuesday | 2018 | 3
8076 | 2018-03-13 14:09 | 2018-03-13 14:09 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Tree | 35 | Rangau fdr#2 Load dropped 91A 9108-17A). Not checked yet. |  | 1 | 14:09 | Afternoon | Tuesday | 2018 | 3
8077 | 2018-03-13 14:09 | 2018-03-15 14:09 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Tree | 35 | Checked & found, Recloser 23 BD 01 T/R 3x ctr: 322-325 R/F: 51N. Patrolled the line & found, high danger Tree under powerline toward Well Jurong #06. Cause: Tree. |  | 1 | 14:09 | Afternoon | Tuesday | 2018 | 3
8078 | 2018-03-13 14:12 | 2018-03-13 14:12 | 13.8KV 8D FEEDER #7 | Fair | Planned Maintenance | 276 | 14:12 Manually opened OCB 8D fdr#7. connect jumper o/p NN for energized 2500 Kva Tx at GS#1. 14:36 Blocked & closed OCB 8D fdr#7, then release the block. Cause: Plan Maintenance. |  | 1 | 14:12 | Afternoon | Tuesday | 2018 | 3
8079 | 2018-03-14 08:05 | 2018-03-14 08:05 | 13.8KV PEMATANG FEEDER #1 | Fair | Animal | 111 | 08:05 Pematang Fdr #1 T/R 1X. Pematang Fdr #2 Load drop 59A (76-17A). Not checked yet. |  | 1 | 8:05 | Morning | Wednesday | 2018 | 3
8080 | 2018-03-14 08:05 | 2018-03-15 08:05 | 13.8KV PEMATANG FEEDER #1 | Fair | Animal | 111 | Checked & found, Pematang OCB fdr #1 T/R 1x ctr: 157-158 R/F: 50P @1, @2. Patrolled the line & found, @1,@2 crossing Powerline shorted by a Bird on Pole in front of Pematang GS. Cause: Animal (Bird). |  | 1 | 8:05 | Morning | Wednesday | 2018 | 3
8081 | 2018-03-14 08:36 | 2018-03-14 08:36 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | 008:36 CD Fdr #7 Load drop 124A (148-24A). Not checked yet. |  | 1 | 8:36 | Morning | Wednesday | 2018 | 3
8082 | 2018-03-14 08:36 | 2018-03-24 08:36 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | Checked & found, Recl. 03-03-42 T/R 1x ctr: 160-161. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 8:36 | Morning | Wednesday | 2018 | 3
8083 | 2018-03-14 09:53 | 2018-03-14 09:53 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified (L/A) | 0 | 09:53 ND Fdr #5 T/R 1X. Not checked yet. |  | 1 | 9:53 | Morning | Wednesday | 2018 | 3
8084 | 2018-03-14 09:53 | 2018-03-24 09:53 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified (L/A) | 0 | Checked and found N. Duri 13.8KV VCB Fdr #5 T/R 1X ctr:113-114 R/F: 51 @1. Patrolled the line and found broken LA o/p 12-E1-01. Cause : Broken LA |  | 1 | 9:53 | Morning | Wednesday | 2018 | 3
8085 | 2018-03-14 10:07 | 2018-03-14 10:07 | 13.8KV BATANG FEEDER #2 | Fair | Construction Job | 0 | 10:07 Manually opened Batang OCB fdr #2 due to : - Dismantle Hot Tap Machine. 19:52 Manually blocked and closed Batang OCB fdr #2 and then released the block. Cause : Job Construction. |  | 1 | 10:07 | Morning | Wednesday | 2018 | 3
8086 | 2018-03-14 14:20 | 2018-03-14 14:20 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 229 | 14:20 Manually opened recl.23-BD-01 d/s Rangau Fdr #2 due to: Replaced 550 KVATX to 500 KVATX at Jurong #43. Replaced Secondary cable at Jurong #2. 18:00 Mannualy blocked and closed recl.23-BD-01 then release the blocked. Cause : Plan Maintenance. |  | 1 | 14:20 | Afternoon | Wednesday | 2018 | 3
8087 | 2018-03-14 14:30 | 2018-03-14 14:30 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 6 | 14:30 Manually opened recl.6E-23A d/s Minas Fdr #6 due to : Replaced 300KVATX with the same size. 14:45 Manually blocked and closed Recloser 6E-23A and then released the block. Cause : Plan Maintenance. |  | 1 | 14:30 | Afternoon | Wednesday | 2018 | 3
8088 | 2018-03-14 17:59 | 2018-03-14 17:59 | 13.8KV PETANI FEEDER #2 | Fair | Tree | 34 | 17:59 Petani Fdr #2 T/R 1X. Cause: Not checked yet. |  | 1 | 17:59 | Afternoon | Wednesday | 2018 | 3
8089 | 2018-03-14 17:59 | 2018-03-15 17:59 | 13.8KV PETANI FEEDER #2 | Fair | Tree | 34 | Checked & found, Petani OCB fdr #2 T/R 1x ctr: 246-247 R/F: 51N. Patrolled the line & found, high danger Palm tree under powerline toward well Petani #14. Cause: Tree. |  | 1 | 17:59 | Afternoon | Wednesday | 2018 | 3
8090 | 2018-03-15 09:45 | 2018-03-15 09:45 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 23 | 09:45 Manually opened recl.38.CX.25 d/s OKB Fdr #2 due to: Replaced 550 KVATX/Sec.2200A to 550 KVATX/Sec.1200/2200A at well KB #455. 10:18 Manually block and closed recl.38.CX.25 then release the block. Cause: Plan Maintenance. |  | 1 | 9:45 | Morning | Thursday | 2018 | 3
8091 | 2018-03-15 11:15 | 2018-03-15 11:15 | 13.8KV BATANG FEEDER #2 | Fair | Construction Job | 0 | 11:15 Manually open Batang OCB fdr #2 due to : Continued dismantle Hot Tap Machine. 17:10 Manually blocked and closed Batang OCB fdr #2 then release the block. Cause: Job Construction. |  | 1 | 11:15 | Morning | Thursday | 2018 | 3
8092 | 2018-03-15 11:22 | 2018-03-15 11:22 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 0 | 11:22 Manually open S,Balam Fdr #4 due to : Open / Close Hot Line Clamp to Reactive wells at Balam #72 and Balam #310. 11:50 Manually blocked and closed S.Balam Fdr #4 then release the block. Cause : Planned Maintenance. |  | 1 | 11:22 | Morning | Thursday | 2018 | 3
8093 | 2018-03-16 00:07 | 2018-03-16 00:07 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | N Duri VCB fdr #11 T/R 1x. Not checked yet. |  | 1 | 0:07 | Night | Friday | 2018 | 3
8094 | 2018-03-16 00:07 | 2018-03-24 00:07 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | Checked and found N Duri VCB fdr #11 T/R 1x ctr:159-160 R/F: 51 @1. Patrolled the line and found broken Bushing o/p 13-H5-27 Cause : Unidentified. |  | 1 | 0:07 | Night | Friday | 2018 | 3
8095 | 2018-03-16 10:50 | 2018-03-16 10:50 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 10:50 It was reported b/o fuse at Talang #296 d/s Duri Community Fdr #3. Not checked yet. |  | 1 | 10:50 | Morning | Friday | 2018 | 3
8096 | 2018-03-16 10:50 | 2018-03-18 15:30 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1 b/o Fuse for 100KVA Tx on Pole I F 34. Replaced b/o Fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 10:50 | Morning | Friday | 2018 | 3
8097 | 2018-03-17 07:20 | 2018-03-17 07:20 | NORTH DURI POWER PLANT |  |  | - | 07:20 S/U NDC#1 Then online the unit at 08:22. (Running test). 21:25 Off line NDC#1, then S/D the unit for Maintenance. |  | 1 | 7:20 | Morning | Saturday | 2018 | 3
8098 | 2018-03-17 08:15 | 2018-03-17 08:15 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 251 | 08:15 Bangko fdr#4 T/R 1x. Bangko fdr #1 load dropped 85A (134-49A). Bangko fdr#2 load dropped 234A (254-20A) WIP. Bangko fdr#3 load dropped 188A (210-20A) WIP. Nella fdr #1 load dropped 112A (223-111A). Nella fdr #2 load dropped 18A (68-50A). 16:00 Checked & found, Bangko OCB fdr #4 T/R 1x ctr: 31-32 R/F: None. Patrolled the line & found, @2 broken Pin Support Insulator on Pole 24 Z 35. Cause: Lightning. |  | 1 | 8:15 | Morning | Saturday | 2018 | 3
8099 | 2018-03-17 08:16 | 2018-03-17 08:16 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 0 | Sintong fdr#1 load dropped 36A (86-50A). Sintong fdr #2 load dropped 51A (234-183A). Sintong GFPC T/R Not checked yet. |  | 1 | 8:16 | Morning | Saturday | 2018 | 3
8100 | 2018-03-17 08:16 | 2018-03-18 08:16 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recloser 25AD26 T/R 1x ctr: 121-122 R/F: 50N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 8:16 | Morning | Saturday | 2018 | 3
8101 | 2018-03-17 09:37 | 2018-03-17 09:37 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 169 | 09:37 Manually open Pematang Fdr #2 due to : Open / Close Repair cover conductor line fdr#1. 11:20 Manually blocked and closed Pematang Fdr #2. Cause : Planned Maintenance. |  | 1 | 9:37 | Morning | Saturday | 2018 | 3
8102 | 2018-03-17 10:02 | 2018-03-17 10:02 | 13.8KV PEMATANG FEEDER #1 | Fair | Planned Maintenance | 105 | 10:02 Manually open Pematang Fdr #1 due to : - Modification jumper in front of Pematang GS. 11:20 Manually blocked and closed Pematang Fdr #1. Cause : Plan Maintenance. |  | 1 | 10:02 | Morning | Saturday | 2018 | 3
8103 | 2018-03-17 10:08 | 2018-03-17 10:08 | 13.8KV 4B FEEDER #1 | Fair | Planned Maintenance | 52 | 10:08 Manually opened recl.3A.28 d/s 4B Fdr #1 due to: Dismantled 300 KVATX from LTC well at well 3A-82 and 3W-28. 11:00 Manually blocked and closed recl.3A.28 then release the blocked. Cause : Plan Maintenance. |  | 1 | 10:08 | Morning | Saturday | 2018 | 3
8104 | 2018-03-17 10:32 | 2018-03-17 10:32 | 4.16KV SO RUMBAI FEEDER #3 | Fair | Unidentified | 0 | 10:32 S. Rumbai 4160V VCB fdr #3 T/SO ctr:132-133. Blocked & closed S. Rumbai fdr #3 then released the block. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:32 | Morning | Saturday | 2018 | 3
8105 | 2018-03-17 14:20 | 2018-03-17 14:20 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Lightning | 163 | 14:20 Pungut OCB fdr#1 T/R 6x, Ctr: 293-299, R/F: 50@1 (RTU Fail) 18:30 Checked and found, Recl.45.BP.9 T/LO Ctr: 130-134 R/F: none. Patrolled the Line and found, @3 b/o LA on Terminal Pole of well Pungut #35. Manually blocked and closed recl.45.BP.9 then release the block. Cause : Lightning. |  | 1 | 14:20 | Afternoon | Saturday | 2018 | 3
8106 | 2018-03-17 14:20 | 2018-03-17 14:20 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 43 | 14:20 Pungut OCB fdr#2 T/R 1x, Ctr:302-303, R/F : 51N (RTU Fail) Not patrolled yet |  | 1 | 14:20 | Afternoon | Saturday | 2018 | 3
8107 | 2018-03-17 14:20 | 2018-03-20 08:20 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 43 | Checked and found 13.8KV OCB #2 T/R 2x R/F: 51N @1 Ctr: 301-303 Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 14:20 | Afternoon | Saturday | 2018 | 3
8108 | 2018-03-17 14:52 | 2018-03-17 14:52 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Unidentified | 95 | 14:50 Duri field fdr#4 T/O 15:50 Checked and found DF Fdr #4 T/SO Ctr: 525 - 526 R/F: None. Manually blocked and closed DF Fdr #4 then release the block. Cause: Unidentified. |  | 1 | 14:52 | Afternoon | Saturday | 2018 | 3
8109 | 2018-03-17 14:52 | 2018-03-24 14:52 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Unidentified | 95 | Checked and found DF Fdr #4 T/SO Ctr: 525 - 526 R/F: 51 @1, @2. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 14:52 | Afternoon | Saturday | 2018 | 3
8110 | 2018-03-17 15:48 | 2018-03-17 15:48 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 0 | It was reported b/o fuse at well Benar #14 D/s Bangko fdr #4. Checked and found @2 b/o fuse for 300 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (mouse). |  | 1 | 15:48 | Afternoon | Saturday | 2018 | 3
8111 | 2018-03-17 16:23 | 2018-03-17 16:23 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 19 | 3D fdr#8 T/R 1X 3D fdr#7 load dropped 164A(175-11A) Not checked yet. |  | 1 | 16:23 | Afternoon | Saturday | 2018 | 3
8112 | 2018-03-17 16:23 | 2018-03-19 16:23 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 19 | Checked & found, 3D OCB fdr #8 T/R 1x ctr: 308-309 R/F: 51. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:23 | Afternoon | Saturday | 2018 | 3
8113 | 2018-03-17 21:25 | 2018-03-17 21:25 | NORTH DURI POWER PLANT |  |  | - | 21:25 Off Line NDC #1 and then S/D the Unit for balancing. |  | 1 | 21:25 | Night | Saturday | 2018 | 3
8114 | 2018-03-18 07:30 | 2018-03-18 07:30 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 07:30 It was reported b/o fuse o/p 10.K5.03 d/s ND Fdr #7. 14:00 Replaced @1 B/O fuse for 112.5Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 7:30 | Morning | Sunday | 2018 | 3
8115 | 2018-03-18 16:25 | 2018-03-18 16:25 | NORTH DURI POWER PLANT |  |  | - | 16:25 S/U NDC#1 Then online the unit at 17:05. (Running test). 22:17 Off line NDC#1, then S/D the unit for Maintenance. |  | 1 | 16:25 | Afternoon | Sunday | 2018 | 3
8116 | 2018-03-18 18:18 | 2018-03-18 18:18 | 13.8KV PINANG FEEDER #1 | Cloudy | Unidentified | 42 | Pinang VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 18:18 | Afternoon | Sunday | 2018 | 3
8117 | 2018-03-18 18:18 | 2018-03-20 08:18 | 13.8KV PINANG FEEDER #1 | Cloudy | Unidentified | 42 | Checked and found 13.8KV OCB #1 T/R 1x Ctr: 434-435 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 18:18 | Afternoon | Sunday | 2018 | 3
8118 | 2018-03-18 22:17 | 2018-03-18 22:17 | NORTH DURI POWER PLANT |  |  | - | 22:17 Off Line NDC #1 and then S/D the unit at 22:20 . For Balancing. |  | 1 | 22:17 | Night | Sunday | 2018 | 3
8119 | 2018-03-19 04:43 | 2018-03-19 04:43 | 13.8KV 6D FEEDER #1 | Fair | Lightning | 62 | 6D OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 4:43 | Morning | Monday | 2018 | 3
8120 | 2018-03-19 04:43 | 2018-03-20 08:43 | 13.8KV 6D FEEDER #1 | Fair | Lightning | 62 | Checked and found 13.8KV OCB #1 T/R Ctr: - R/F: None. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 4:43 | Morning | Monday | 2018 | 3
8121 | 2018-03-19 04:43 | 2018-03-19 04:43 | 13.8KV 6D FEEDER #2 | Fair | Lightning Arrester | 32 | 04:43 6D fdr #2 load dropped 198A (221-23A). 6D fdr #3 load dropped 135A (150-15A) --> WIP. 17:00 Checked & found, Recloser 6D298 T/R 1x ctr: 73-74. Patrolled the line & found, broken Lightning Arrester on Pole LBS 6D-68. Cause: Lightning Arrester Broken. |  | 1 | 4:43 | Morning | Monday | 2018 | 3
8122 | 2018-03-19 04:43 | 2018-03-19 04:43 | 13.8KV 6DN FEEDER #1 | Fair | Unidentified | 17 | 6DN fdr #1 load dropped 56A (153-97A). Not checked yet. |  | 1 | 4:43 | Morning | Monday | 2018 | 3
8123 | 2018-03-19 04:43 | 2018-03-20 16:43 | 13.8KV 6DN FEEDER #1 | Fair | Unidentified | 17 | Checked & found, no Recloser operated under this feeder. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 4:43 | Morning | Monday | 2018 | 3
8124 | 2018-03-19 04:47 | 2018-03-19 04:47 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 67 | Petani fdr #1 load dropped 89A (195-15A). Petani fdr #2 load dropped 11A (92-81A) Not checked yet. |  | 1 | 4:47 | Morning | Monday | 2018 | 3
8125 | 2018-03-19 04:47 | 2018-03-23 08:28 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 67 | Checked & found, no Breaker & Recloser operated under Petani fdr #1 & #2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 4:47 | Morning | Monday | 2018 | 3
8126 | 2018-03-19 13:15 | 2018-03-19 13:15 | NORTH DURI POWER PLANT |  |  | - | 13:15 S/U NDC#1 Then online the unit at 15:25. (Running test). |  | 1 | 13:15 | Afternoon | Monday | 2018 | 3
8127 | 2018-03-19 23:42 | 2018-03-19 23:42 | NORTH DURI POWER PLANT |  |  | - | 23:42 Off Line NDC #1. 23:46 S/D NDC #1 for balancing. |  | 1 | 23:42 | Night | Monday | 2018 | 3
8128 | 2018-03-20 04:17 | 2018-03-20 04:17 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Fair | Dead End Insulator | 14 | MSU #2 VCB fdr #2 (Pungut #2) T/R 1x. Not checked yet. |  | 1 | 4:17 | Morning | Tuesday | 2018 | 3
8129 | 2018-03-20 04:17 | 2018-03-21 16:17 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Fair | Dead End Insulator | 14 | Checked & found, MSU VCB fdr #2 (Pungut fdr #2) T/R 1x ctr: 303-304 R/F: 51@1. Patrolled the line & found, @1 broken Dead-end Insulator on Pole DK-131. Cause: Dead-end Insulator. |  | 1 | 4:17 | Morning | Tuesday | 2018 | 3
8130 | 2018-03-20 09:25 | 2018-03-20 09:25 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 0 | 3D Fdr #8 Load drop 133A (144-11A). Not checked yet. |  | 1 | 9:25 | Morning | Tuesday | 2018 | 3
8131 | 2018-03-20 09:25 | 2018-03-21 08:25 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 0 | Checked and found 13.8KV OCB #8 T/R 1x Ctr: 308-309 R/F: 51 @2. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 9:25 | Morning | Tuesday | 2018 | 3
8132 | 2018-03-20 10:19 | 2018-03-20 10:19 | 13.8KV PINANG FEEDER #1 | Fair | Construction Job | 0 | 10:19 Manually opened Pinang Fdr #1 due to: Tie In new Location Pinang #50. 14:23 Manually blocked and closed Pinang Fdr #1 then release the blocked. Cause: Job Construction. |  | 1 | 10:19 | Morning | Tuesday | 2018 | 3
8133 | 2018-03-20 10:56 | 2018-03-20 10:56 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Construction Job | 0 | 10:56 Manually opened recl.34.B1.18 d/s So,Bek Fdr #1 due to: Relocated facility Ampuh #16. 12:00 Manually blocked and closed recl.34.B1.18 then release the block. Cause : Construction job. |  | 1 | 10:56 | Morning | Tuesday | 2018 | 3
8134 | 2018-03-20 11:55 | 2018-03-20 11:55 | NORTH DURI POWER PLANT |  |  | - | 11:55 S/U NDC#1 and then O/L at 14:52. (Running test). |  | 1 | 11:55 | Morning | Tuesday | 2018 | 3
8135 | 2018-03-20 13:56 | 2018-03-20 13:56 | 44KV NORTH DURI - DUMAI LINE | Fair | Unidentified | 0 | N.Duri 44KV GCB #1 T/R 1X Not checked yet. |  | 1 | 13:56 | Afternoon | Tuesday | 2018 | 3
8136 | 2018-03-20 13:56 | 2018-03-24 13:56 | 44KV NORTH DURI - DUMAI LINE | Fair | Unidentified | 0 | 17;00 Checked and found Duri 44KV GCB #1 T/R 1X ctr:121-122 R/F:51 @1. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 13:56 | Afternoon | Tuesday | 2018 | 3
8137 | 2018-03-20 14:39 | 2018-03-20 14:39 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Rain and Lightning | Unidentified | 0 | Dumai 4.16 KV VCB #12 (Dumai Fdr #1) T/R 2X. Not checked yet. |  | 1 | 14:39 | Afternoon | Tuesday | 2018 | 3
8138 | 2018-03-20 14:39 | 2018-03-24 14:39 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Rain and Lightning | Unidentified | 0 | 17:00 Checked and found Dumai 4.16 KV VCB #12 (Dumai Fdr #1) T/R 2, ctr:270-271. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 14:39 | Afternoon | Tuesday | 2018 | 3
8139 | 2018-03-20 14:40 | 2018-03-20 14:40 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Rain and Lightning | Unidentified | 0 | Dumai 4.16 KV VCB #23 (Dumai Fdr #5) T/R 1X. Not checked yet. |  | 1 | 14:40 | Afternoon | Tuesday | 2018 | 3
8140 | 2018-03-20 14:40 | 2018-03-23 09:47 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Rain and Lightning | Unidentified | 0 | Checked & found, 4.16kV Dumai fdr #5 (Industrial Feeder) T/R 2x ctr: 279-281 R/F: 51 @2, @3. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:40 | Afternoon | Tuesday | 2018 | 3
8141 | 2018-03-21 00:49 | 2018-03-21 00:49 | NORTH DURI POWER PLANT |  |  | - | 00:49 Off line NDC #2 and then S/D the unit at 00:52. For stand by. |  | 1 | 0:49 | Night | Wednesday | 2018 | 3
8142 | 2018-03-21 06:22 | 2018-03-21 06:22 | 13.8KV NORTH DURI FEEDER #2 | Fair | Theft | 0 | It was reported no power on pole 10-J8-06 and 10-J8-07 D/S N Duri fdr #2. Checked and found Secondary Cable vandalism for 112.5KVA TX o/p 10-J8-06 and 10-J8-07. (Not Replaced yet). Cause: Theft. |  | 1 | 6:22 | Morning | Wednesday | 2018 | 3
8143 | 2018-03-21 07:21 | 2018-03-21 07:21 | NORTH DURI POWER PLANT | Fair | Under investigation | 371 | 07:21 NDC #1 Trip by..... ( under investigation ) Load shading level 2 followed by : 3D 13.8KV fdr #6 Tripped ,----->Closed at:09:37. 4D 13.8KV fdr #4 Tripped ,----->Closed at:09:43. 4D 13.8KV fdr #5 Tripped ,----->Closed at:09:43. 5B 13.8KV fdr #4 Tripped ,----->Closed at:09:38. 8D 13.8KV fdr #1 Tripped ,----->Closed at:09:43 8D 13.8KV fdr #3 Tripped ,----->Closed at:09:42. BOB Open , Beruk fdr #2 Tripped ,----->Closed at:09:58. Zamrud fdr #1 Tripped,----->Closed at:10:00. Zamrud fdr #3 Tripped,----->Closed at:10:00. 6DN 13.8KV fdr #1 load dropped 20A (126-106A). 4B 13.8KV fdr #1 load dropped 26A (256-230A). 6D 13.8KV fdr #6 load dropped 51A (184-133A). 8D 13.8KV fdr #8 load dropped 116A (183-66A). 8D 13.8KV fdr #9 load dropped 163A (174-11A). ----->Wip. 8C 13.8KV fdr #4 load dropped 46A (289-244A). ----->Wip. 8C 13.8KV fdr #5 load dropped 31A (197-166A). ----->Wip. Bangko 13.8KV fdr #3 load dropped 174A (240-66A). ----->Wip. Sintong 13.8KV fdr #2 load dropped 102A (254-152A). 08:38 S/U NDC#1 and online at 09:08. Production Loss GS#1 : 99 Bbls, 9 wells. GS#2 : 109 Bbls, 28 wells. GS#3 : 0 Bbls, 0 wells. GS#4 : 89 Bbls, 16 wells. GS#5 : 57 Bbls, 20 wells. GS#6 : 53 Bbls, 20 wells. Total Prod. Loss : 407 Bbls, 93 wells. |  | 1 | 7:21 | Morning | Wednesday | 2018 | 3
8144 | 2018-03-21 08:38 | 2018-03-21 08:38 | NORTH DURI POWER PLANT |  |  | - | 08:38 S/U NDC#1 and online at 09:08. |  | 1 | 8:38 | Morning | Wednesday | 2018 | 3
8145 | 2018-03-21 08:51 | 2018-03-21 08:51 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 42 | 08:51 4B 13.8KV VCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 8:51 | Morning | Wednesday | 2018 | 3
8146 | 2018-03-21 08:51 | 2018-03-27 08:51 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 42 | Checked & found, Recloser 4B-101 T/R 1x ctr: 621-622 R/F: -. Patrolled the line & found, @1, @2 broken Dead-end Insulator on Pole 3B-13. Cause: Unidentified. |  | 1 | 8:51 | Morning | Wednesday | 2018 | 3
8147 | 2018-03-21 10:36 | 2018-03-21 10:36 | 13.8KV MINAS FEEDER #6 | Fair | Construction Job | 0 | 10:36 Manually Open Recl. 6E-23A, ----->Closed at 16:15. Installed Jumper production line. Project. |  | 1 | 10:36 | Morning | Wednesday | 2018 | 3
8148 | 2018-03-21 15:11 | 2018-03-21 15:11 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Construction Job | 0 | 15:11 Blocked Recl. 04-02-22 ----->Closed at 17:50. O/C HLC o/p 04-02-12. Replaced 112KVA TX - 150KVA TX. o/p 04-02-12. Project. |  | 1 | 15:11 | Afternoon | Wednesday | 2018 | 3
8149 | 2018-03-21 19:10 | 2018-03-21 19:10 | NORTH DURI POWER PLANT |  |  | - | 19:10 S/U NDC#2, then on line the unit at 20:08. |  | 1 | 19:10 | Night | Wednesday | 2018 | 3
8150 | 2018-03-22 08:52 | 2018-03-22 08:52 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Pin Insulator | 83 | 08:52 CKB 13.8 KV fdr#1 T/R 1X. CKB 13.8 KV fdr #2 load dropped 239A (260-19A). Not checked yet. |  | 1 | 8:52 | Morning | Thursday | 2018 | 3
8151 | 2018-03-22 08:52 | 2018-03-23 08:52 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Pin Insulator | 83 | Checked & found, CKB VCB fdr #1 T/R 1x ctr: 222-223 R/F: 51@2. Patrolled the line & found, @2 broken Pin Insulator on T/P KB #287. Cause: Pin Insulator. |  | 1 | 8:52 | Morning | Thursday | 2018 | 3
8152 | 2018-03-22 09:30 | 2018-03-22 09:30 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Construction Job | 0 | 09:30 Manual open C. Duri 13.8KV ACB fdr #2, ---->Closed at 09:35. Open By Pas Recl. 08-M5-13. To rised Up 112.5Kva TX to 150KVA TX o/p# 08-M5-05 and 08-M5-07. Project. |  | 1 | 9:30 | Morning | Thursday | 2018 | 3
8153 | 2018-03-22 12:01 | 2018-03-22 12:01 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Unidentified | 11 | Libo 13.8KV VCB fdr #1 T/R 1X. No checked yet. |  | 1 | 12:01 | Afternoon | Thursday | 2018 | 3
8154 | 2018-03-22 12:01 | 2018-03-27 08:01 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Unidentified | 11 | Checked and found 13.8KV OCB #1 T/R 2x Ctr: 575-577 R/F: 50N @1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 12:01 | Afternoon | Thursday | 2018 | 3
8155 | 2018-03-22 12:15 | 2018-03-22 12:15 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 33 | Sintong fdr #2 load dropped 119A (209-90A). Sintong 13.8KV GFPC T/R 1X. No checked yet. |  | 1 | 12:15 | Afternoon | Thursday | 2018 | 3
8156 | 2018-03-22 13:20 | 2018-03-22 13:20 | NORTH DURI POWER PLANT |  |  | - | 13:20 Off line and then S/D NDC CT #3 for re wiring 230KV ND GCB #35. |  | 1 | 13:20 | Afternoon | Thursday | 2018 | 3
8157 | 2018-03-22 15:00 | 2018-03-22 15:00 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 36 | It was reported no power o/p 11-G7-13. No checked yet. |  | 1 | 15:00 | Afternoon | Thursday | 2018 | 3
8158 | 2018-03-22 15:00 | 2018-03-24 11:20 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 36 | 15:00 It was reported B/O fuse o/p 11-G7-13 d/s N.Duri fdr #9. 11:20 Checked and found @1,@2 b/o fuse for Tx o/p 11-G7-13 Replace b/o fuse above with same size then energized Tx. Cause: Animal (Monkey) |  | 1 | 15:00 | Afternoon | Thursday | 2018 | 3
8159 | 2018-03-22 15:26 | 2018-03-22 15:26 | 13.8KV 5B FEEDER #8 | Cloudy | Lightning | 0 | 5B 13.8KV OCB fdr #8 T/R 1X. No checked yet. |  | 1 | 15:26 | Afternoon | Thursday | 2018 | 3
8160 | 2018-03-22 15:26 | 2018-03-27 15:26 | 13.8KV 5B FEEDER #8 | Cloudy | Lightning | 0 | Checked & found, 5B OCB fdr #8 T/R 1x ctr: 99988-99989 R/F: 50N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 15:26 | Afternoon | Thursday | 2018 | 3
8161 | 2018-03-22 16:17 | 2018-03-22 16:17 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri Comm. 13.8KV ACB fdr #2 T/R 1X. No checked yet. |  | 1 | 16:17 | Afternoon | Thursday | 2018 | 3
8162 | 2018-03-22 16:17 | 2018-03-26 16:17 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Checked and found Duri Comm. 13.8KV ACB fdr #2 T/R 1X ctr:94-95 R/F: 51N , 51 @1. Patrolled the line but found nothing (Suspected the tree touch Power line). Couse: Unidentified. |  | 1 | 16:17 | Afternoon | Thursday | 2018 | 3
8163 | 2018-03-23 01:30 | 2018-03-23 01:30 | 13.8KV ROKAN FEEDER #2 | Fair | Animal | 89 | 01:30 It was reported b/o fuse at well Kopar #38 d/s Rokan Fdr #2 12:00 Checked and found @2, @3 b/o fuses for 150KVA TX at well Kopar #38. Replaced the b/o fuse above with same size, then energized the TX. OK. Cause: Animal (Monkey). |  | 1 | 1:30 | Night | Friday | 2018 | 3
8164 | 2018-03-23 10:31 | 2018-03-23 10:31 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified | 84 | 10:31 Nella 13.8 KV fdr#1 T/R 1X. Nella 13.8 KV fdr #2 load dropped 8A (68-60A). Not checked yet. |  | 1 | 10:31 | Morning | Friday | 2018 | 3
8165 | 2018-03-23 10:41 | 2018-03-23 10:41 | 13.8KV 3D FEEDER #2 | Fair | Planned Maintenance | 13 | 10:41 Manual open 3D 13.8KV fdr #2, ----->Closed at:11:04 Replaced TX 300 KVA at well 3E-62 (Reactive well). Cause:Plant maintenance. |  | 1 | 10:41 | Morning | Friday | 2018 | 3
8166 | 2018-03-23 11:38 | 2018-03-23 11:38 | 44KV NORTH DURI - DUMAI LINE | Fair | Unidentified | 0 | N.Duri-Dumai 44KV OCB #1 T/R 1X. No checked yet. |  | 1 | 11:38 | Morning | Friday | 2018 | 3
8167 | 2018-03-23 11:38 | 2018-03-24 17:00 | 44KV NORTH DURI - DUMAI LINE | Fair | Unidentified | 0 | 17:00 Checked and found N.Duri-Dumai 44KV OCB #1 T/R 1X ctr:122-123 R/F:51 @1. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 11:38 | Morning | Friday | 2018 | 3
8168 | 2018-03-23 14:20 | 2018-03-23 14:20 | NORTH DURI POWER PLANT |  |  | - | 14:20 NDC CT #3 S/U and O/L to the system at 16:41. |  | 1 | 14:20 | Afternoon | Friday | 2018 | 3
8169 | 2018-03-23 17:10 | 2018-03-23 17:10 | MINAS POWER PLANT |  |  | - | 17:10 MGT #7 Off line and then S/D for S/B. |  | 1 | 17:10 | Afternoon | Friday | 2018 | 3
8170 | 2018-03-23 17:30 | 2018-03-23 17:30 | MINAS POWER PLANT |  |  | - | 17:30 MGT #2 Off line and then S/D for S/B. |  | 1 | 17:30 | Afternoon | Friday | 2018 | 3
8171 | 2018-03-23 17:38 | 2018-03-23 17:38 | MINAS POWER PLANT |  |  | - | 17:38 MGT #1 Off line and then S/D for S/B. |  | 1 | 17:38 | Afternoon | Friday | 2018 | 3
8172 | 2018-03-23 17:46 | 2018-03-23 17:46 | 13.8KV 5B FEEDER #1 | Cloudy | Lightning | 23 | 5B 13.8KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 17:46 | Afternoon | Friday | 2018 | 3
8173 | 2018-03-23 17:46 | 2018-03-27 17:46 | 13.8KV 5B FEEDER #1 | Cloudy | Lightning | 23 | Checked & found, 5B OCB fdr #1 T/R 1x ctr: 254-255 R/F: 51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 17:46 | Afternoon | Friday | 2018 | 3
8174 | 2018-03-23 17:55 | 2018-03-23 17:55 | MINAS POWER PLANT |  |  | - | 17:55 MGT #10 Off line and then S/D for S/B. |  | 1 | 17:55 | Afternoon | Friday | 2018 | 3
8175 | 2018-03-23 18:20 | 2018-03-23 18:20 | CENTRAL DURI POWER PLANT |  |  | - | 18:20 Off line and then S/D CDGT #2. |  | 1 | 18:20 | Afternoon | Friday | 2018 | 3
8176 | 2018-03-24 06:31 | 2018-03-24 06:31 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified | 80 | CKBS VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 6:31 | Morning | Saturday | 2018 | 3
8177 | 2018-03-24 06:31 | 2018-03-25 06:31 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified | 80 | Checked & found, CKB VCB fdr #1 T/R 1x ctr: 223-224 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:31 | Morning | Saturday | 2018 | 3
8178 | 2018-03-24 08:32 | 2018-03-24 08:32 | MINAS POWER PLANT |  |  | - | 08:32 MGT #1 S/U and O/L to the system at 09:00. |  | 1 | 8:32 | Morning | Saturday | 2018 | 3
8179 | 2018-03-24 09:04 | 2018-03-24 09:04 | 13.8KV NORTH DURI FEEDER #7 | Fair | Theft | 0 | 09:04 It was reported B/O fuse o/p 10-J5-11 d/s N.Duri fdr #7. 11:00 Checked and found @2 b/o fuse for 112.5 KVA TX. Also found lost of ground cable. Cause:Vadalism. |  | 1 | 9:04 | Morning | Saturday | 2018 | 3
8180 | 2018-03-24 09:24 | 2018-03-24 09:24 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Animal | 2 | 09:24 It was reported b/o fuse o/p 05-P1-21 d/s C.Duri fdr#5 15:00 Checked and fund face @2,@3 b/o fuse for 1125Kva Tx Replace b/o fuse above with same size the energized the Tx Cause:Animal. |  | 1 | 9:24 | Morning | Saturday | 2018 | 3
8181 | 2018-03-24 09:28 | 2018-03-24 09:28 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Planned Maintenance | 0 | 09:28 Manual open LBS SN-01, (Duri Community fd #3 ----->Closed at:11:50. Cutting tress below line 13,8 KV Duri Community fdr #3 (near ex KKMC and Mutiara School). Cause:Plant maintenance. |  | 1 | 9:28 | Morning | Saturday | 2018 | 3
8182 | 2018-03-25 01:03 | 2018-03-25 01:03 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Recloser | 80 | 01:03 It was reported no power o/p 05.P3.18 d/s CD Fdr #14. 06:35 Checked & found Recl. 05-P3-02 T/SO Ctr: 593-594. Also found Broken Control of Recl. 05-P3-02. 07:52 Replaced broken Control Recl. 05-P3-02. Blocked and closed the Recloser, but failied. 08:17 Closed LBS 05-Pe-24 (d/s C. Duri fdr #15). 07:59 It was reported no power o/p 05.N7.23. 11:00 Checked & found Recl. 06-P7-02 T/O (on blocked) ctr: 79-80. Blocked and closed the Recloser. Ok then released the block. 14:58 Replaced broken Control Recl. 05-P3-02. Blocked and closed the Recloser, Ok then released the block. Open LBS 05-Pe-24 (C. Duri fdr #14 back to normal). Cause: Recloser. |  | 1 | 1:03 | Night | Sunday | 2018 | 3
8183 | 2018-03-26 23:59 | 2018-03-26 23:59 | CPI POWER SYSTEM |  | Normal Condition | - | Normal System Condition. |  | 1 | 23:59 | Night | Monday | 2018 | 3
8184 | 2018-03-27 11:11 | 2018-03-27 11:11 | 13.8KV SINTONG FEEDER #2 | Fair | Construction Job | 0 | 11:11 Manually Open Recl. 28AF-02, ----->Closed at 12:17. Tied in 300KV TX fo new well Benar #54, #55 and reactive wells Benar #34 & #44. Cause: Project. |  | 1 | 11:11 | Morning | Tuesday | 2018 | 3
8185 | 2018-03-27 11:53 | 2018-03-27 11:53 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified | 0 | 11:53 C. Duri 13.8KV ACB fdr #1 T/R 1X ctr:218-219 R/F: 51N, 51G. 13:49 C. Duri 13.8KV ACB fdr #1 T/R 1X again ctr:219-220 R/F: 51@1, 51G. Not patrolled yet. |  | 1 | 11:53 | Morning | Tuesday | 2018 | 3
8186 | 2018-03-27 11:53 | 2018-01-04 16:00 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified | 0 | 16:00 Checked and found C. Duri 13.8KV ACB fdr#1 T/R 1X @1, ctr:219-220 R/F: 51N, 51G. Patrolled the line no thing. Cause:Unidentified. |  | 1 | 11:53 | Morning | Tuesday | 2018 | 3
8187 | 2018-03-27 16:31 | 2018-03-27 16:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 19 | It was reported b/o fuse o/p 08-L5-08 d/s C.Duri fdr#1. Not checked yet. |  | 1 | 16:31 | Afternoon | Tuesday | 2018 | 3
8188 | 2018-03-27 16:31 | 2018-03-28 17:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 19 | Checked and found @2 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (Monkey). |  | 1 | 16:31 | Afternoon | Tuesday | 2018 | 3
8189 | 2018-03-27 17:15 | 2018-03-27 17:15 | 13.8KV S. BALAM FEEDER #4 | Fair | Transformer Failure | 18 | It was reported b/o fuse at well Balam # 386. Checked and found @1 b/o fuse for 150Kva TX. TTR test and megger the TX and found Low Mega Ohm reading TX. (will be replaced tomorrow). |  | 1 | 17:15 | Afternoon | Tuesday | 2018 | 3
8190 | 2018-03-27 17:15 | 2018-03-28 12:43 | 13.8KV S. BALAM FEEDER #4 | Fair | Transformer Failure | 18 | Replaced 150 Kva with same size and energized the Tx at well Balam #386. Cause: Tx failure. |  | 1 | 17:15 | Afternoon | Tuesday | 2018 | 3
8191 | 2018-03-28 07:25 | 2018-03-28 07:25 | MINAS POWER PLANT |  |  | - | 07:25 S/U MGT #7 , and then On Line the unit at 07:45. |  | 1 | 7:25 | Morning | Wednesday | 2018 | 3
8192 | 2018-03-28 10:17 | 2018-03-28 10:17 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 608 | 10:17 Manually opened Pematang OCB fdr #2 due to: - Sleeve pole on pole 34-BC-23 Take of pole of Pematang #41 / 75. 15:38 Manually blocked and close Pematang OCB fdr #2 and then released the block. Cause: Plan Maintenance. | 12345 | 1 | 10:17 | Morning | Wednesday | 2018 | 3
8193 | 2018-03-28 10:23 | / | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 73 | - |  | 1 | 10:23 | Morning | Wednesday | 2018 | 3
8194 | 2018-03-28 11:50 | 2018-03-28 11:50 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 11 | 11:50 Manually opened Recloser: 16-AB-03 D/S S Balam fdr #4 due to: - Open / close Hot line clamp on take of pole Balam #06. for reactive well Balam #06. 12:03 Manually blocked and closed Recloser: 16-AB-03 and then released the block. Cause: Plan maintenance. |  | 1 | 11:50 | Morning | Wednesday | 2018 | 3
8195 | 2018-03-28 15:10 | 2018-03-28 15:10 | MINAS POWER PLANT |  |  | - | 15:10 S/U MGT #4 and then On line the unit at 15:31. |  | 1 | 15:10 | Afternoon | Wednesday | 2018 | 3
8196 | 2018-03-28 16:20 | 2018-03-28 16:20 | MINAS POWER PLANT |  |  | - | 16:20 Off Line MGT #5 and then S/D the unit for Stand by. |  | 1 | 16:20 | Afternoon | Wednesday | 2018 | 3
8197 | 2018-03-28 17:45 | 2018-03-28 17:45 | MINAS POWER PLANT |  |  | - | 17:45 Off Line MGT #1 and then S/D the unit for Stand by. |  | 1 | 17:45 | Afternoon | Wednesday | 2018 | 3
8198 | 2018-03-28 23:11 | 2018-03-28 23:11 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Tree | 0 | 23:00 Duri Comy 13.8 KV ACB #25 fdr #1 T/R 1X. Not checked yet. |  | 1 | 23:11 | Night | Wednesday | 2018 | 3
8199 | 2018-03-28 23:11 | 2018-02-04 17:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Tree | 0 | Checked & found, Duri Community ACB #25 fdr #1 T/R 1x ctr: 116-117 R/F: 51N. Patrolled the line & found, high Palm tree touched powerline on Pole 3 DF 11. Cause: Tree. |  | 1 | 23:11 | Night | Wednesday | 2018 | 3
8200 | 2018-03-29 03:34 | 2018-03-29 03:34 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | 0 | 03:34 8C 13.8 KV OCB fdr #4 T/R 1X. 17:00 Checked & found, 8C VCB fdr #4 T/R 1x ctr: 603-604 R/F:50N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 3:34 | Night | Thursday | 2018 | 3
8201 | 2018-03-29 03:41 | 2018-03-29 03:41 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 86 | 03:41 8D 13.8 KV OCB fdr #1 T/R 1X. 17:00 Checked & found, 8C OCB fdr #1 T/R 1x ctr: 306-307 R/F: 51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 3:41 | Night | Thursday | 2018 | 3
8202 | 2018-03-29 10:56 | 2018-03-29 10:56 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 122 | 10:56 Manually opened Recloser: 23-BD-01 D/S Rangau fdr #2 due to: - Replaced @3 b/o fuse for 25 Kva Tx (For lighting area). 12:16 Manually blocked and closed Recloser: 23-BD-01 and then released the block. Cause: Plan Maintenance. |  | 1 | 10:56 | Morning | Thursday | 2018 | 3
8203 | 2018-03-29 11:27 | 2018-03-29 11:27 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 65 | 11:27 Manually opened LBS: 27-AL-03 D/S Ketigul fdr #2 due to : - Install 300 Kva Tx at well UBI #08 (reactive well). 12:12 Manually closed LBS: 27-AL-03. Cause: Plan Maintenance. |  | 1 | 11:27 | Morning | Thursday | 2018 | 3
8204 | 2018-03-29 14:06 | 2018-03-29 14:06 | 13.8KV PEMATANG FEEDER #1 | Fair | Planned Maintenance | 582 | 14:06 Manually opened Rangau OCB fdr #1 Closed at: 16:07. 14:07 Manually opened Rangau OCB fdr #2 Closed at: 16:08. 14:06 Manually opened Pematang OCB fdr #2 Closed at: 16:05. 14:06 Manually opened Pematang OCB fdr #1 Closed at: 16:04. Due to: 1. Repair hot spot on Recloser #B at Pematang GS (3 spots). 2. Repair hot spot on Recloser #A at Pematang GS (1 spot ). 3. Repair hot spot on 600 Kvar Cap Bank. 4. Repair hot spot on Take of pole Pematang #98 (Hot Line Clamp). Cause: Plan Maintenance. Prod.loss, Rangau fdr #1 =25 bbls/ 4wells. Rangau fdr #2 =172 bbls/ 13wells. Pematang fdr #1 =200 bbls/ 18wells. Pematang fdr #2 =275 bbls/ 20wells. ---------------------------------------- + Total =672 bbls/ 55wells. | 1234 | 1 | 14:06 | Afternoon | Thursday | 2018 | 3
8205 | 2018-03-29 14:32 | 2018-03-29 14:32 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 76 | Sintong fdr #2 load dropped 147A (246 - 99A) --> WIP. Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 14:32 | Afternoon | Thursday | 2018 | 3
8206 | 2018-03-29 14:32 | 2018-03-31 14:32 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 76 | Checked & found, Recloser 28-AF-02 T/R 1x ctr: 1530-1531. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:32 | Afternoon | Thursday | 2018 | 3
8207 | 2018-03-29 16:16 | 2018-03-29 16:16 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Fair | Unidentified | 0 | 16:16 Dumai 4.16 Kv VCB #23 (fdr #5) T/R. 16:27 Blocked Dumai 4.16 Kv VCB #23 (fdr #5) due to repeatedly trip / reclose. 17:26 Checked and found Dumai 4.16 Kv VCB #23 (fdr #5) T/R : 6x R/F: 50 @1,@2,@3. Patrolled the line but found nothing. 19:43 Blocked and closed Dumai fdr #5, OK then released the block. Cause: Unidentified . |  | 1 | 16:16 | Afternoon | Thursday | 2018 | 3
8208 | 2018-03-31 11:07 | 2018-03-31 11:07 | CENTRAL DURI POWER PLANT |  |  | - | 11:07 S/U CDGT #2 and then On Line the Unit at 11:49. |  | 1 | 11:07 | Morning | Saturday | 2018 | 3
8209 | 2018-03-31 11:55 | 2018-03-31 11:55 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Fair | Transformer Failure | 0 | Dumai 4.16 Kv VCB #23 ( Feeder #5 ) T/r 1x. Not checked yet. |  | 1 | 11:55 | Morning | Saturday | 2018 | 3
8210 | 2018-03-31 11:55 | 2018-01-04 19:00 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Fair | Transformer Failure | 0 | Checked and fond Dumai 4.16 Kv VCB #23 ( Feeder #5 ) T/r 1x ctr:286-288 R/F:51@1,@2. Patrolled the line and found TX failure at WTP. Cause:Transformer failure. |  | 1 | 11:55 | Morning | Saturday | 2018 | 3
8211 | 2018-03-31 13:16 | 2018-03-31 13:16 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | Central Duri VCB #18 ( fdr #15 ) T/R 1x. Not checked yet. |  | 1 | 13:16 | Afternoon | Saturday | 2018 | 3
8212 | 2018-03-31 13:16 | 2018-01-04 19:00 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | Checked and found Central Duri VCB fdr #15 T/R 1x ctr:375-376 R/F:50 @1,@2. Patrolled the line but found no thing. Cause:Unidentfied. |  | 1 | 13:16 | Afternoon | Saturday | 2018 | 3
8213 | 2018-03-31 14:25 | 2018-03-31 14:25 | CENTRAL DURI POWER PLANT |  |  | - | 14:25 Off Line CDGT #2 and then S/D the Unit at 14:26. |  | 1 | 14:25 | Afternoon | Saturday | 2018 | 3
8214 | 2018-03-31 14:52 | 2018-03-31 14:52 | 13.8KV S. BALAM FEEDER #4 | Fair | Animal | 0 | 14:52 It was reported b/o fuse at well So Balam #127 D/S Balam fdr #4. 16:15 Checked and found @2 b/o fuse for 45 Kva Transformer. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (monkey). |  | 1 | 14:52 | Afternoon | Saturday | 2018 | 3
8215 | 2018-03-31 16:55 | 2018-03-31 16:55 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 40 | Ketigul VCB fdr #1 T/R 1x. Ketigul fdr#2 load dropped 47A ( 205-158A). Not checked yet. |  | 1 | 16:55 | Afternoon | Saturday | 2018 | 3
8216 | 2018-03-31 16:55 | 2018-02-04 16:55 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 40 | Checked & found, Ketigul VCB fdr #1 T/R 1x ctr: 199-200 R/F: 51N. Patrolled the line & found, a death bird around Pole 32 AK 16. Cause: Animal. |  | 1 | 16:55 | Afternoon | Saturday | 2018 | 3
8217 | 2018-03-31 04:15 | 2018-03-31 04:15 | 13.8KV 6D FEEDER #6 | Fair | Unidentified | 15 | 04:15 6D 13.8 KV OCB fdr #6 T/R 1X. Not checked yet. |  | 1 | 4:15 | Morning | Saturday | 2018 | 3
8218 | 2018-03-31 04:15 | 2018-03-04 16:15 | 13.8KV 6D FEEDER #6 | Fair | Unidentified | 15 | Checked & found, 6D OCB fdr #6 T/R 1x ctr: 599-600 R/F: 50N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 4:15 | Morning | Saturday | 2018 | 3
8219 | 2018-03-31 10:21 | 2018-03-31 10:21 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Fair | Planned Maintenance | 0 | 10:21 Manually opened Dumai 4.16 Kv VCB #23 (feeder #5) due to: - Replaced 225 Kva - 300 Kva Transformer at WTP Dumai. 11:38 Manually blocked and closed Dumai 4.16 Kv VCB #23 (feeder #5) and then released the block. Cause: Plan Maintenance. |  | 1 | 10:21 | Morning | Saturday | 2018 | 3
8220 | 2018-03-31 11:38 | 2018-03-31 11:38 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 21 | 11:38 Pinang OCB fdr #1 T/O (in blocked position due to Rig HPS #08 activity at well Pinang #01). 11:55 Manually blocked and closed Pinang OCB fdr #1 and still in blocked position. ( After the approval of TL Bangko). Cause: Not checked yet. |  | 1 | 11:38 | Morning | Saturday | 2018 | 3
8221 | 2018-03-31 11:38 | 2018-01-04 11:38 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 21 | Checked & found, Pinang OCB fdr #1 T/O (On Blocked Position) ctr: 436-437 R/F: 51 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 11:38 | Morning | Saturday | 2018 | 3
8222 | 2018-03-31 16:40 | 2018-03-31 16:40 | 4.16KV SO RUMBAI FEEDER #4 | Fair | Planned Maintenance | 0 | 16:40 Manually opened S Rumbai 4.16 Kv Recl fdr #4 due to: - Opened FCO for replaced main breaker at HKBP Rumbai. 16:43 Manually blocked and closed S Rumbai 4.16 Kv Recl fdr #4 and then released the block. 17:36 Manually opened S Rumbai 4.16 Kv Recl fdr #4 due to: - Closed FCO after replaced main breaker at HKBP Rumbai. 17:40 Manually blocked and closed S Rumbai 4.16 Kv Recl fdr #4 and then released the block. Cause: Plan Maintenance. |  | 1 | 16:40 | Afternoon | Saturday | 2018 | 3
8223 | 2018-01-04 09:29 | 2018-01-04 09:29 | 13.8KV BATANG FEEDER #1 | Fair | Unidentified | 0 | Batang OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 9:29 | Morning | Thursday | 2018 | 1
8224 | 2018-01-04 09:29 | 2018-03-04 09:29 | 13.8KV BATANG FEEDER #1 | Fair | Unidentified | 0 | Checked and found 13.8KV OCB #1 T/R 1x Ctr: 141-142 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:29 | Morning | Thursday | 2018 | 1
8225 | 2018-01-04 11:45 | 2018-01-04 11:45 | 13.8KV BANGKO FEEDER #1 | Heavy Rain | Unidentified | 44 | Bangko fdr #1 load dropped 70A (148-78A). Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 11:45 | Morning | Thursday | 2018 | 1
8226 | 2018-01-04 11:45 | 2018-03-04 08:45 | 13.8KV BANGKO FEEDER #1 | Heavy Rain | Unidentified | 44 | Checked and found Bangko fdr #1 load dropped. Patrolled the line and found Recloser 23X-12 T/R 1x Ctr: 310-311. Cause: Unidentified. |  | 1 | 11:45 | Morning | Thursday | 2018 | 1
8227 | 2018-01-04 16:00 | 2018-01-04 16:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 7 | It was reported b/o fuse at well Pagar #42, d/s Ketigul fdr #2 . 16:00 Checked and found @1, @2 b/o fuse at well Pagar #42. Replaced b/o fuse above with the same size and energize the TX. Cause:Animal (Bird ). |  | 1 | 16:00 | Afternoon | Thursday | 2018 | 1
8228 | 2018-01-04 17:48 | 2018-01-04 17:48 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | N Duri VCB fdr #11 T/R 1x. Not checked yet. |  | 1 | 17:48 | Afternoon | Thursday | 2018 | 1
8229 | 2018-01-04 17:48 | 2018-02-04 19:00 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | Checked and found N Duri VCB fdr #11 T/R 1x ctr:160-161 R/F:51 @1,@2,@3. Patrolled the line but nothing found. Cause:Unidentified. |  | 1 | 17:48 | Afternoon | Thursday | 2018 | 1
8230 | 2018-02-04 06:04 | 2018-02-04 06:04 | 13.8KV PETANI FEEDER #1 | Fair | Tree | 80 | 06:04 Petani 13.8KV OCB fdr #1 T/R 1X. Petani fdr #2 load dropped 57A (86-29). 17:00 Checked & found, Petani OCB fdr #1 T/R 1x ctr; 56-57 R/F: 50N Patrolled the line & found, high Palm Tree touched powerline on Pole 34 AZ 29. Cause: Tree. |  | 1 | 6:04 | Morning | Sunday | 2018 | 2
8231 | 2018-02-04 11:12 | 2018-02-04 11:12 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified (Fuse) | 2 | 11:12 It was reported b/o fuse o/p 03-06-25 d/s CD Fdr #5. 15:57 Checked and found @1 b/o fufe for 112.5 KVA TX. Replaced b/o fuse with the same size and energized the TX. Cause : Unidentified (fuse). |  | 1 | 11:12 | Morning | Sunday | 2018 | 2
8232 | 2018-02-04 13:12 | 2018-02-04 13:12 | 13.8KV BEKASAP FEEDER #6 | Fair | Planned Maintenance | 41 | 13:12 Manually pen recloser 38-BE-10 d/s Bekasap Fdr #6 due to : C/O Transformer at well Bekasap #50. TX : 150-500 KVA, R/M 95-300 HP , Sec. volt : 1300 volt. 14:00 Manually blocked and closed recloser 38-BE-10 and then released the block, Ctr recloser : 595. Cause : Plan Maintenance. |  | 1 | 13:12 | Afternoon | Sunday | 2018 | 2
8233 | 2018-02-04 19:26 | 2018-02-04 19:26 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 54 | 19:26 8C 13.8 KV fdr #6 T/R 3X. 8C 13.8 KV fdr #5 load dropped 145A (146-1A). 8C 13.8 KV fdr #4 load dropped 229A (302-73A). 8C 13.8 KV fdr #1 load dropped 37A (221-184A). Not checked yet. |  | 1 | 19:26 | Night | Sunday | 2018 | 2
8234 | 2018-02-04 19:26 | 2018-03-04 17:26 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 54 | Checked & found, 8C VCB fdr #6 T/R 3x Ctr: 588-591 R/F: 51N. Patrolled the line & found, @1 Flash-over Dead-end Insulator on Pole 8D-81N. Cause: Lightning. |  | 1 | 19:26 | Night | Sunday | 2018 | 2
8235 | 2018-03-04 07:27 | 2018-03-04 07:27 | 13.8KV 4D FEEDER #5 | Cloudy | Lightning | 13 | 4D OCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 7:27 | Morning | Sunday | 2018 | 3
8236 | 2018-03-04 07:27 | 2018-10-04 08:27 | 13.8KV 4D FEEDER #5 | Cloudy | Lightning | 13 | Checked and found 13.8KV OCB #5 T/R 1x Ctr: 310-311 R/F: 51N. Patrolled the line but found nothing. Cause: Lughtning. |  | 1 | 7:27 | Morning | Sunday | 2018 | 3
8237 | 2018-03-04 09:15 | 2018-03-04 09:15 | 13.8KV NELLA FEEDER #1 | Fair | Construction Job | 0 | 09:15 Manually opened recl.22-V-01 d/s Nella Fdr #1 due to : Relocated terminal pool & dismantle power line towards well BKO #79. 09:58 Manually blocked and closed Recl.22-V-01 and then released the block. Cause : Construction Job. |  | 1 | 9:15 | Morning | Sunday | 2018 | 3
8238 | 2018-03-04 09:51 | 2018-03-04 09:51 | 13.8KV 3D FEEDER #4 | Fair | Construction Job | 0 | 09:51 Manually opened Recl.2D-14 d/s 3D Fdr #4 due to : -Replaced 6 " Production line near recl.2D-14. 17:03 Manually blocked and closed Recl.2D-14 and then released the block. Cause : Construction Job. |  | 1 | 9:51 | Morning | Sunday | 2018 | 3
8239 | 2018-03-04 10:23 | 2018-03-04 10:23 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Construction Job | 0 | 10:23 Manually opened Recl.34-B1-18 d/s So BEK fdr #1 due to : - Isolated line towards well Ampuh #22. 11:53 Manually blocked and closed Recl.34-B1-18 and then released the block. Cause : Construction Job. |  | 1 | 10:23 | Morning | Sunday | 2018 | 3
8240 | 2018-03-04 11:41 | 2018-03-04 11:41 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 111 | 11:41 Nella OCB fdr#1 T/R 1x . Nella GFPC T/R 1x. Nella fdr#2 load dropped 46A (67-21A) 17:00 Checked & found, Nella VCB fdr #1 T/R 1x ctr: 517-518 R/F: 51N. Also found, Recloser 22 V 01 T/R 2x ctr: 110-112. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 11:41 | Morning | Sunday | 2018 | 3
8241 | 2018-03-04 11:58 | 2018-03-04 11:58 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 38 | 11:58 Nella 13.8KV OCB fdr# 2 T/R 1x. Nella GFPC T/R 1x. 12:01 Nella 13.8KV OCB fdr# 2 T/R 1x. Nella GFPC T/R 1x. 17:00 Checked & found, Nella VCB fdr #2 T/R 1x ctr: 308-309 R/F: 51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 11:58 | Morning | Sunday | 2018 | 3
8242 | 2018-03-04 12:27 | 2018-03-04 12:27 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 96 | Ketigul VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 12:27 | Afternoon | Sunday | 2018 | 3
8243 | 2018-03-04 12:27 | 2018-09-04 08:27 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 96 | Checked and found 13.8KV VCB #2 T/R 1x Ctr: 265-266 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 12:27 | Afternoon | Sunday | 2018 | 3
8244 | 2018-03-04 12:42 | 2018-03-04 12:42 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | C.Duri ACB #11 (feeder #1) T/R 1x Counter: 220-221 R/F: 51N. Not patrolled yet. |  | 1 | 12:42 | Afternoon | Sunday | 2018 | 3
8245 | 2018-03-04 12:42 | 2018-09-04 08:42 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 12:42 | Afternoon | Sunday | 2018 | 3
8246 | 2018-03-04 13:23 | 2018-03-04 13:23 | 13.8KV CENTRAL DURI FEEDER #6 | Rain and Lightning | Unidentified | 0 | C.Duri ACB #23 (feeder#6 ) T/R 1x Counter:482-483 R/F: 51 @1,@2. Not patrolled yet. |  | 1 | 13:23 | Afternoon | Sunday | 2018 | 3
8247 | 2018-03-04 13:23 | 2018-09-04 09:23 | 13.8KV CENTRAL DURI FEEDER #6 | Rain and Lightning | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 13:23 | Afternoon | Sunday | 2018 | 3
8248 | 2018-03-04 13:27 | 2018-03-04 13:27 | 13.8KV DURI FIELD FEEDER #1 | Rain and Lightning | Unidentified | 0 | Duri field VCB #41 (feeder #1) T/R 1x. Not checked yet. |  | 1 | 13:27 | Afternoon | Sunday | 2018 | 3
8249 | 2018-03-04 13:27 | 2018-12-04 08:27 | 13.8KV DURI FIELD FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked and found 13.8KV ACB #41 T/R 1x Ctr: 690-691 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 13:27 | Afternoon | Sunday | 2018 | 3
8250 | 2018-03-04 14:46 | 2018-03-04 14:46 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 3 | 14:46 Manually opened Recloser: 23-BW-02 D/s Libo fdr #2 due to - Changed out Transformer at well Hitam #02. 15:35 Blocked and closed Recloser: 23-BW-02 and then released the block. Cause: Plan Maintenance. |  | 1 | 14:46 | Afternoon | Sunday | 2018 | 3
8251 | 2018-03-04 15:34 | 2018-03-04 15:34 | 13.8KV 4D FEEDER #2 | Cloudy | Lightning | 61 | 4D OCB fdr#2 T/R 1x. 4D fdr#3 load dropped 36A (61-25A) Not checked yet. |  | 1 | 15:34 | Afternoon | Sunday | 2018 | 3
8252 | 2018-03-04 15:34 | 2018-10-04 08:34 | 13.8KV 4D FEEDER #2 | Cloudy | Lightning | 61 | Checked and found 13.8KV OCB #3 T/R 2x Ctr: 256-258 R/F: 51. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 15:34 | Afternoon | Sunday | 2018 | 3
8253 | 2018-03-04 16:05 | 2018-03-04 16:05 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 65 | Bangko OCB fdr#4 T/R 1x. Bangko GFPC T/R 1x. Bangko fdr#1 load dropped 61A (148-87A) Bangko fdr#2 load dropped 115A (224-109A) --> WIP Not checked yet. Prod.loss, Bangko fdr #1 =38 bbls/ 21wells. Bangko fdr #4 =71 bbls/ 41wells. ---------------------------------------- + Total =109 bbls/ 62wells. |  | 1 | 16:05 | Afternoon | Sunday | 2018 | 3
8254 | 2018-03-04 16:05 | 2018-04-04 16:05 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 65 | Checked & found, Bangko VCB fdr #4 T/R 1x ctr: 33-34 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:05 | Afternoon | Sunday | 2018 | 3
8255 | 2018-04-04 10:14 | 2018-04-04 10:14 | 13.8KV PETANI FEEDER #2 | Fair | Construction Job | 0 | 10:14 Manually open petani OCB fdr#2 due to : - O/C HLC o/p 33 AE 04 at well Petani #37. 10:58 Manually blocked and closed Petani OCB fdr#2 and then released the block. Cause : Construction Job. |  | 1 | 10:14 | Morning | Wednesday | 2018 | 4
8256 | 2018-04-04 14:35 | 2018-04-04 14:35 | MINAS POWER PLANT | Fair |  | - | 14:35 S/U MGT#5 and then O/L at 14:47. |  | 1 | 14:35 | Afternoon | Wednesday | 2018 | 4
8257 | 2018-04-04 15:05 | 2018-04-04 15:05 | MINAS POWER PLANT |  |  | - | 15:05 MGT#4 Off line S/D for S/B (Will repair L/O leak bring#2) |  | 1 | 15:05 | Afternoon | Wednesday | 2018 | 4
8258 | 2018-04-04 15:05 | 2018-04-04 15:05 | 13.8KV KETIGUL FEEDER#2 | Fair | Secondary Cable | 0 | 15:05 It was reported B/O fuse at well UBI #10 D/S Ketigul fdr #2. Checked and found low megger secondary cable. 16:00 Replaced secondary cable above and energized the Tx. Cause: Secondary cable. |  | 1 | 15:05 | Afternoon | Wednesday | 2018 | 4
8259 | 2018-04-04 16:17 | 2018-04-04 16:17 | 13.8KV 6DN FEEDER #6 | Fair | Construction Job | 0 | 16:17 Manually opened Recloser: 6E-30 D/S 6DN fdr #6 due to: -Tie in new wells 6E-81 and 6E-51. 16:33 Manually blocked and closed Recloser: 6E-30 and then released the block. Cause: Construction job. |  | 1 | 16:17 | Afternoon | Wednesday | 2018 | 4
8260 | 2018-04-04 16:20 | 2018-04-04 16:20 | CENTRAL DURI POWER PLANT |  |  | - | 16:20 S/U CDGT#2 then on line the unit at 16:43. |  | 1 | 16:20 | Afternoon | Wednesday | 2018 | 4
8261 | 2018-04-04 17:12 | 2018-04-04 17:12 | PEMATANG MAIN SUBSTATION | Fair | Planned Maintenance | 775 | Program isolate and fix, add oil of Pematang 44KV OCB#1 17:12 Manually open Petani fdr#1--->Closed 19:20. Production loss = 362 Bbls / 35 wells. 17:17 Manually open Petani fdr#2--->Closed 19:24. Production loss = 166 Bbls / 24 wells. 17:06 Manually open Rokan fdr#2--->Closed 19:25. Production loss = 82 Bbls / 8 wells. 17:13 Manually open Rangau fdr#1--->Closed 17:29. Production loss = 6 Bbls / 4 wells. 17:09 Manually open Rangau fdr#2--->Closed 17:30. Production loss = 39 Bbls / 11 wells. 17:09 Manually open Pematang fdr#2--->Closed 17:40. Production loss = 68 Bbls / 10 wells. 17:11 Manually open Pematang fdr#1--->Closed 17:28. Production loss = 53 Bbls / 19 wells. ---------------------------------------------- Grand Total = 776 Bbls / 111 wells. 17:15 Manually open/closed Pematang main 44KV OCB#2--->17:25. 17:15 Manually open/closed Pematang main 44KV OCB#3--->17:26. 17:18 Manually open/closed Pematang main 44KV C/S--->17:24. 17:20 Manually open/closed Pematang main 44KV OCB#1 isolation switch --->19:18. Cause: Oil Leaks. | 12345 | 1 | 17:12 | Afternoon | Wednesday | 2018 | 4
8262 | 2018-04-04 17:45 | 2018-04-04 17:45 | CENTRAL DURI POWER PLANT | Fair |  | - | 17:45 CDGT#3 Off line then S/D for S/B. |  | 1 | 17:45 | Afternoon | Wednesday | 2018 | 4
8263 | 2018-05-04 04:20 | 2018-05-04 04:20 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 47 | Sintong OCB fdr #2 T/R 1x. Sintong fdr #1 load dropped 23A (83-60A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 4:20 | Morning | Friday | 2018 | 5
8264 | 2018-05-04 10:22 | 2018-05-04 10:22 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 26 | So BKS fdr#1 Load dropped 33A(106-73A) Not Checked yet |  | 1 | 10:22 | Morning | Friday | 2018 | 5
8265 | 2018-05-04 10:22 | 2018-09-04 07:22 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 26 | Checked & found Recl. 37BI01 T/R 1x Ctr:1314-1315. Patrolled the line & found @1 Broken Dea End Insulator o/p 37BI54. Cause : Unidentified. |  | 1 | 10:22 | Morning | Friday | 2018 | 5
8266 | 2018-05-04 13:50 | 2018-05-04 13:50 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 54 | 13:50 Pinang OCB fdr#1 T/SO, in Block Status (Rig Job) 14:05 Man Closed Pinang OCB fdr#1 Not checked yet |  | 1 | 13:50 | Afternoon | Friday | 2018 | 5
8267 | 2018-05-04 14:03 | 2018-05-04 14:03 | 13.8KV NELLA FEEDER #1 | Fair | Lightning Arrester | 148 | Nella OCB fdr#1 T/R 1x. Nella Fdr#2 Loa dropped 7A (67-60A) Not Checke3d yet |  | 1 | 14:03 | Afternoon | Friday | 2018 | 5
8268 | 2018-05-04 14:03 | 2018-09-04 07:03 | 13.8KV NELLA FEEDER #1 | Fair | Lightning Arrester | 148 | Checked & found Nella VCB fdr#2 T/R 1x Ctr:518-519 R/F:51N. Patrolled the line & found @2 Broken LA o/p 21V11. Cause : Lightning Arrester. |  | 1 | 14:03 | Afternoon | Friday | 2018 | 5
8269 | 2018-05-04 14:43 | 2018-05-04 14:43 | 13.8KV 3D FEEDER #3 | Fair | Construction Job | 0 | 14:43 Manually Opened 3D OCB fdr#3 to Install 300KVATX at reactive Well # 3C-99E. 14:58 Manually Closed back 3D OCB fdr#3, after finished the Jobs. Cause: Job Construction. |  | 1 | 14:43 | Afternoon | Friday | 2018 | 5
8270 | 2018-05-04 16:30 | 2018-05-04 16:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 103 | It was reported B/O fuse at well Kulin#70 (C.Duri fdr#1). Not checked yet. |  | 1 | 16:30 | Afternoon | Friday | 2018 | 5
8271 | 2018-05-04 16:30 | 2018-09-04 07:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 103 | Checked & found @1@2 B/O fuse for 75 Kva Tx at well Kulin#70. Checked TTR & Megger 75 Kva Tx failure. (Would be changed tomorrow). Cause : Transformer Failure. |  | 1 | 16:30 | Afternoon | Friday | 2018 | 5
8272 | 2018-05-04 16:30 | 21/04/2018 09:15 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Transformer Failure | 103 | Replaced transformer failure with the same size and then energized the Tx. Cause: Tx failure (low megger reading). |  | 1 | 16:30 | Afternoon | Friday | 2018 | 5
8273 | 2018-06-04 06:05 | 2018-06-04 06:05 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified | 0 | 06:05 C.Duri ACB#41 (ffeeder#9) T/LO Counter: 389-392 R/F: 51@1 08:15 Patrolled the line but found nothing. Blocked & closed C.Duri fdr#9, then release the block. Cause: Unidentified. |  | 1 | 6:05 | Morning | Monday | 2018 | 6
8274 | 2018-06-04 10:25 | 2018-06-04 10:25 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Planned Maintenance | 0 | 10:25 Manually Openend LBS 04-08-25 (d/s CD fdr#8) to Repair Hot spot at Source side of Recloser 03-01-39. 10:50 Manually Closed the LBS, after finished the Jobs. Cause: Planned Maintenance |  | 1 | 10:25 | Morning | Monday | 2018 | 6
8275 | 2018-06-04 14:32 | 2018-06-04 14:32 | MINAS POWER PLANT | Fair |  | - | 14:32 MGT #3 Off Line, then S/D for Stand By. |  | 1 | 14:32 | Afternoon | Monday | 2018 | 6
8276 | 2018-06-04 15:32 | 2018-06-04 15:32 | 13.8KV ROKAN FEEDER #4 | Fair | Planned Maintenance | 0 | 15:32 Manually Opened Rokan OCB fdr#4 to Repair Hot Spot HLC on To/P Well Kirana 16:25 Manually Block & Closed the Feeder after finished the Job, then released the Block Cause: Planed Maintenance |  | 1 | 15:32 | Afternoon | Monday | 2018 | 6
8277 | 2018-06-04 15:52 | 2018-06-04 15:52 | 13.8KV 6DN FEEDER #2 | Fair | Construction Job | 0 | 15:52 Manually Opened Recloser 6D-200 (d/s 6DN fdr#2) to install 300KVATX at Well 5D-76 as Reactive Well. 16:22 Manually Closed the Recloser after finished the job (Load dropped while Job done, 149A(247-98A) Cause: Planned Construction |  | 1 | 15:52 | Afternoon | Monday | 2018 | 6
8278 | 2018-06-04 17:05 | 2018-06-04 17:05 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse o/p 09-S4-04 (C.Duri fdr#4). Not checked yet. |  | 1 | 17:05 | Afternoon | Monday | 2018 | 6
8279 | 2018-06-04 17:05 | 2018-07-04 09:45 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified (Fuse) | 0 | Checked & found @1 b/o Fuse o/p 09-S4-04 for 112.5KVATX (C Duri fdr#4) Patrolled the Line, but found nothing. Replaced the fuse with the same size, then Energized the TX. Cause: Unidentified (Fuse). |  | 1 | 17:05 | Afternoon | Monday | 2018 | 6
8280 | 2018-07-04 07:25 | 2018-07-04 07:25 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | C Duri ACB # 18 (feeder #15) T/R 1x Ctr: 376-377 R/F: 51N. Not checked yet. |  | 1 | 7:25 | Morning | Wednesday | 2018 | 7
8281 | 2018-07-04 07:25 | 2018-11-04 08:25 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | Checked and found 13.8KV ACB #18 T/R 1x Ctr: 376-377 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:25 | Morning | Wednesday | 2018 | 7
8282 | 2018-07-04 11:15 | 2018-07-04 11:15 | 13.8KV PETANI FEEDER #2 | Fair | Construction Job | 0 | 11:15 Manually opened PTN OCB fdr#2. to Tie In New Well PTN #128. 11:45 Manually Block & Closed PTN OCB fdr#2, then released the Block. Cause: Planned Construction. |  | 1 | 11:15 | Morning | Wednesday | 2018 | 7
8283 | 2018-07-04 14:23 | 2018-07-04 14:23 | 13.8KV 4B FEEDER #2 | Fair | Tree | 57 | 14:23 4B OCB fdr#2 TL/O 15:08 Checked & found 4B OCB fdr#2 T/LO, Ctr: 266-277, R/F: 51 @1. 16:43 Patrolled the Line, found Fall down Tree and touch cross arm, causing Broken @1@2 Pin insulator and @1@2 FCO On T/P 4B-67. Dismantled the Tree, then Isolate the conductor, waiting to Replace the Broken Pin and FCO 17:08 Block & Closed 4B OCB fdr#2, the released the Block. Cause : Tree. |  | 1 | 14:23 | Afternoon | Wednesday | 2018 | 7
8284 | 2018-07-04 14:33 | 2018-07-04 14:33 | 13.8KV BANGKO FEEDER #1 | Fair | Construction Job | 0 | 14:33 Manually Opened Bangko OCB fdr#1. to Tie In New Well BKO#326. 16:18 Block & Closed BKO OCB fdr#1, then released the Block. After finished the Job. Cause: Planned Construction Job. |  | 1 | 14:33 | Afternoon | Wednesday | 2018 | 7
8285 | 2018-07-04 14:37 | 2018-07-04 14:37 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Animal | 70 | 14:37 Menggala fdr#1 Load dropped 104A (144-40A). Menggala GFPC TX T/R 1x. 16:25 was reported no power So Menggala field 18:10 Checked & found Recl. 19AO01 T/LO Ctr:484-488. Patrolled the line & found Dead Monkey on T/P So.Menggala#4. Blocked & Closed Recl. 19Ao01, then release the block. Cause: Animal (Monkey). |  | 1 | 14:37 | Afternoon | Wednesday | 2018 | 7
8286 | 2018-07-04 14:43 | 2018-07-04 14:43 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Tree | 38 | Rangau OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 14:43 | Afternoon | Wednesday | 2018 | 7
8287 | 2018-07-04 14:43 | 16/04/2018 08:43 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Tree | 38 | Checked and found 13.8KV OCB fdr #2 T/R 2x Ctr: 332-334 R/F: 51 @3. Patrolled the line and found palm tree touch the power line o/p 23-BC-03 Cause: others. |  | 1 | 14:43 | Afternoon | Wednesday | 2018 | 7
8288 | 2018-07-04 17:39 | 2018-07-04 17:39 | 13.8KV 8C FEEDER #6 | Fair | Pin Insulator | 54 | 17:39 8C RTU failed (freq. 60.28Hz). 8C OCB fdr#6 T/O. 18:10 Checked & found 8C OCB fdr#6 T/LO Ctr:591-595 R/F: 51 @1,2,3. Blocked & Closed 8C OCB fdr#6, then release the block. Not Patrolled yet. |  | 1 | 17:39 | Afternoon | Wednesday | 2018 | 7
8289 | 2018-07-04 17:39 | 2018-10-04 17:39 | 13.8KV 8C FEEDER #6 | Fair | Pin Insulator | 54 | Patrolled the line & found, @1, @2, @3 broken Pin Insulator on Pole Near GS-2. Cause: Pin Insulator. |  | 1 | 17:39 | Afternoon | Wednesday | 2018 | 7
8290 | 2018-08-04 08:00 | 2018-08-04 08:00 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 133 | 08:00 It was reported B/O fuse at well So.Balam#350 (So.Balam fdr#1). 09:20 Replaced @1 B/O fuse for 150Kva Tx with the same size. Cause: Animal (Squirrel). |  | 1 | 8:00 | Morning | Saturday | 2018 | 8
8291 | 2018-08-04 09:30 | 2018-08-04 09:30 | 13.8KV 8D FEEDER #2 | Fair | Construction Job | 0 | 09:30 Manually opened 8D OCB fdr#2. Installed Jumper for Reactive well 8E-43. 09:39 Blocked & Closed 8D OCB fdr#2, the release the block. Cause: Construction Job. |  | 1 | 9:30 | Morning | Saturday | 2018 | 8
8292 | 2018-08-04 13:55 | 2018-08-04 13:55 | 13.8KV 4B FEEDER #2 | Fair | Planned Maintenance | 29 | 13:55 Manually Opened LBS 4B-16 (4B fdr#2). Closed Jumper on T/P well 4B-69. 14:50 Manually closed 4B-16. Cause: Maintenance Job. |  | 1 | 13:55 | Afternoon | Saturday | 2018 | 8
8293 | 2018-08-04 14:41 | 2018-08-04 14:41 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 35 | 14:41 Manually Opened LBS 34CT-58 (CKBS fdr#5). Replaced 300Kva Tx with 250 Kva at well KB#42. 15:08 Closed LBS 34CT-58. Cause: Maintenance Job. |  | 1 | 14:41 | Afternoon | Saturday | 2018 | 8
8294 | 2018-08-04 16:24 | 2018-08-04 16:24 | 13.8KV 4D FEEDER #3 | Fair | Lightning | 18 | 4D OCB fdr#3 T/R 1x. 4D fdr#2 Load dropped47A (144-97A). Not checked yet. |  | 1 | 16:24 | Afternoon | Saturday | 2018 | 8
8295 | 2018-08-04 16:24 | 2018-10-04 08:24 | 13.8KV 4D FEEDER #3 | Fair | Lightning | 18 | Checked and found 13.8KV OCB #3 T/R 1x Ctr: 243-244 R/F: 51N @3. Patrolled the line and found Broken L/A o/p 3D-81. Cause: Lightning. |  | 1 | 16:24 | Afternoon | Saturday | 2018 | 8
8296 | 2018-08-04 18:48 | 2018-08-04 18:48 | 13.8KV KETIGUL FEEDER#3 | Fair | Animal | 7 | Ketigul VCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 18:48 | Afternoon | Saturday | 2018 | 8
8297 | 2018-08-04 18:48 | 16/04/2018 08:48 | 13.8KV KETIGUL FEEDER#3 | Fair | Animal | 7 | Checked and found 13.8KV VCB #3 T/R 1x Ctr: 376-377 R/F: 51N. Patrolled the line and found dead bird o/p 31-AR-31. Cause: Animal. |  | 1 | 18:48 | Afternoon | Saturday | 2018 | 8
8298 | 2018-09-04 12:19 | 2018-09-04 12:19 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Construction Job | 0 | 12:19 Manually opened Recl. 34BI18. Tie in new well at Ampuh Field. 15:50 Blocked & closed Recl.34BI18, then release the block. Cause: Construction Job. |  | 1 | 12:19 | Afternoon | Tuesday | 2018 | 9
8299 | 2018-09-04 12:39 | 2018-09-04 12:39 | 13.8KV NORTH DURI FEEDER #1 | Fair | Tree | 164 | 12:39 N.Duri fdr#1 Load dropped 32A (144-112A). 14:55t was reported no power at 10-J8-20. 15:20 Checked & found Recl. 10-J4-26 T/O (Block position) Ctr:85-86. 15:22 Block & Closed Recl. 10-J4-26, but failed. Patrolled the line & found Danger trees Near T/P at NA AWT Area 10. Trimming danger trees Near T/P AWT Area#10. 17:02 Blocked & clocked Recl. 10-J4-26, then release the block. Cause: Tree. |  | 1 | 12:39 | Afternoon | Tuesday | 2018 | 9
8300 | 2018-09-04 14:21 | 2018-09-04 14:21 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 10 | 14:21 8C fdr#3 Load dropped 116A (197-81A). 8C fdr#6 Load dropped 85A (150-65A). 16:10 Checked & found Recl.8D-18A T/O (Block position) Ctr;48-49). 16:16 Blocked & closed Recl.8D-18A, then release the block. Not patrolled yet. |  | 1 | 14:21 | Afternoon | Tuesday | 2018 | 9
8301 | 2018-09-04 14:21 | 2018-10-04 14:21 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 10 | Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 14:21 | Afternoon | Tuesday | 2018 | 9
8302 | 2018-09-04 14:22 | 2018-09-04 14:22 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 145 | 14:22 It was reported no power at well KB#434, KB#432 (OKB Fdr#2). 15:25 OKB OCB fdr#2 T/SO Ctr:1315-1316 R/F:51@2. 15:30 Blocked & Closed OKB OCB fdr#2, then release the block. Patrolled the line & found, @2, @3 broken Pin Insulator on Pole 38 CX 07. Cause: Lightning. |  | 1 | 14:22 | Afternoon | Tuesday | 2018 | 9
8303 | 2018-09-04 17:10 | 2018-09-04 17:10 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 864 | 17:10 Ketigul fdr#2 T/SO. Ketigul fdr#1 Load dropped 99A (144-15A). Ketigul fdr#3 Load dropped 15A (18-3A). 19:45 Checked & found Ketigul OCB fdr#2 T/LO, Ctr: 265-270, R/F: 51N. Patrolled the Line, found Dead Monkey Under Pole 29-AL-06. 20:30 Manually Block & Opened Ketigul OCB fdr#2, but T/O again. Any Spark Saws O/P Recl 29-AL-03,towad Menggala, other sides the River. 20:45 Manually Opened LBS 29-AL-07 toward Menggala. Manually Block & Closed Ketigul OCB fdr#2, OK, then released the block. 21:50 Checked & found, B/O Bushing Recl 29-AL-03, at Load sides. Isolate the Recloser, Open Visual opening, then Closed Bypass Recloser. 22:08 Closed LBS 29-AL-07 Ketigul Sides, (Ktg OCB fdr#2 in Block), then Released the block. Cause: Animal (Monkey) | 1234 | 1 | 17:10 | Afternoon | Tuesday | 2018 | 9
8304 | 2018-09-04 17:10 | 2018-10-04 08:10 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 864 | Checked and found Ketigul VCB #2 T/LO Ctr: 266-270 R/F: 51 @1,@2,@3. Patrolled the line and found broken Recloser bushing o/p 29-AL-03. Cause: Animal (monkey). | 1234 | 1 | 17:10 | Afternoon | Tuesday | 2018 | 9
8305 | 2018-10-04 18:00 | 2018-10-04 18:00 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 36 | It was reported B/O fuse at well Kelok#15 (Ketigul fdr#1). Not checked yet. |  | 1 | 18:00 | Afternoon | Thursday | 2018 | 10
8306 | 2018-10-04 18:00 | 2018-11-04 11:28 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 36 | Checked and found @1, @2 b/o fuse for 300KVA TX at well Kelok #15. Replaced the b/o fuse above with same size, then energized the TX. OK Cause: Animal (Bird). |  | 1 | 18:00 | Afternoon | Thursday | 2018 | 10
8307 | 2018-10-04 18:33 | 2018-10-04 18:33 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning Arrester | 7 | Ketigul VCB fdr#3 T/R 1x. Ketigul fdr#1 Load dropped 50A (113-63A). Not checked yet. |  | 1 | 18:33 | Afternoon | Thursday | 2018 | 10
8308 | 2018-10-04 18:33 | 17/04/2018 17:33 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning Arrester | 7 | Checked & found, Ketigul VCB fdr #3 T/R 2x ctr: 198-200 R/F: 51N. Patrolled the line & found, @1, @3 broken Lightning Arrester on Pole 31 AO 12. Cause: Lightning Arrester. |  | 1 | 18:33 | Afternoon | Thursday | 2018 | 10
8309 | 2018-11-04 01:22 | 2018-11-04 01:22 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 7 | Ketigul VCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 1:22 | Night | Sunday | 2018 | 11
8310 | 2018-11-04 01:22 | 17/04/2018 17:22 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 7 | Checked & found, Ketigul VCB fdr #3 T/R 2x ctr:198-200 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 1:22 | Night | Sunday | 2018 | 11
8311 | 2018-11-04 10:11 | 2018-11-04 10:11 | 13.8KV NORTH DURI FEEDER #11 | Fair | Planned Maintenance | 0 | 10:11 Manually Open N. Duri 13.8KV fdr #11. By Pass Recl. 12 E5-25 due to Lube Oil Leak. 10:14 Closed N. Duri 13.8KV fdr #11. Cause: Planned Maintenance (Recloser Leakage). |  | 1 | 10:11 | Morning | Sunday | 2018 | 11
8312 | 2018-11-04 13:40 | 2018-11-04 13:40 | MINAS POWER PLANT |  |  | - | 13:40 S/U MGT #10 and then online the unit at 14:28. |  | 1 | 13:40 | Afternoon | Sunday | 2018 | 11
8313 | 2018-11-04 15:28 | 2018-11-04 15:28 | MINAS POWER PLANT |  |  | - | 15:28 of line MGT #10 and then S/D the unit. |  | 1 | 15:28 | Afternoon | Sunday | 2018 | 11
8314 | 2018-11-04 15:53 | 2018-11-04 15:53 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified | 52 | Pematang fdr#2 T/R 1X Pematang fdr#1 load dropped 126A (190-64A) Not checked yet. |  | 1 | 15:53 | Afternoon | Sunday | 2018 | 11
8315 | 2018-11-04 15:53 | 20/04/2018 15:53 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified | 52 | Checked & found, Pematang OCB fdr #2 T/R 2x ctr: 483-485 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:53 | Afternoon | Sunday | 2018 | 11
8316 | 2018-11-04 16:16 | 2018-11-04 16:16 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 59 | OKB load dropped 200A (241-41A) Not checked yet. |  | 1 | 16:16 | Afternoon | Sunday | 2018 | 11
8317 | 2018-11-04 16:16 | 15/04/2018 08:16 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 59 | Checked and found, Recloser 38-CW-01 T/R 1x Ctr: 89-90. Patrolled the line but found nothing. Cause: suspected by Lightning. |  | 1 | 16:16 | Afternoon | Sunday | 2018 | 11
8318 | 2018-11-04 16:37 | 2018-11-04 16:37 | NEW PETAPAHAN SUBSTATION | Rain and Lightning | Under investigation | 1457 | 16:37 Petapahan 115KV GCB #3 T/O. Petapahan 115KV GCB #5 T/O. (No Power to Petapahan TX-2, fdr #6, #7 and Petapahan fdr #8). 16:46 Manually Open Petapahan fdr #3,---->Closed at 18:37. (Maintain level) 16:47 Manually Open Petapahan fdr #4,---->Closed at 18:36. (Maintain level) 16:58 Checked and found: Petapahan 115KV GCB #3 T/O ctr: R/F: 51N, 51 @ C, 50/51 W3, 86T Petapahan 115KV GCB #5 T/O ctr: Manually Open Petapahan fdr #6,---->Closed at 18:36. Manually Open Petapahan fdr #7,---->Closed at 18:02. Manually Open Petapahan fdr #8,---->Closed at 18:12. 17:59 Blocked and Closed Petapahan 115KV GCB #5, failed. Open Petapahan TX-2 isolation switch. Open Petapahan VR TX-2 isolation switch. Cause: Under investigation. | 123 | 1 | 16:37 | Afternoon | Sunday | 2018 | 11
8319 | 2018-12-04 09:08 | 2018-12-04 09:08 | MINAS POWER PLANT |  |  | - | 09:08 S/U MGT #3 and then online the unit at 09:20. |  | 1 | 9:08 | Morning | Tuesday | 2018 | 12
8320 | 2018-12-04 09:43 | 2018-12-04 09:43 | MINAS POWER PLANT |  |  | - | 09:43 Of line MGT #5 and then S/D the unit. |  | 1 | 9:43 | Morning | Tuesday | 2018 | 12
8321 | 2018-12-04 09:51 | 2018-12-04 09:51 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 22 | 09:51 Manually open LBS 38-CW-23 D/S Old Kotabatak fdr#2. Replaced Pin Insulator O/P 38-CX-7. 10:12 Manually closed LBS 38-CX-23. Cause: Planned maintenance. |  | 1 | 9:51 | Morning | Tuesday | 2018 | 12
8322 | 2018-12-04 10:58 | 2018-12-04 10:58 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 10:58 Manually open LBS 28-AL-05,----->Closed at 13:49. Tie in new power line at well Ubi #43. Cause: Project. |  | 1 | 10:58 | Morning | Tuesday | 2018 | 12
8323 | 2018-12-04 14:15 | 2018-12-04 14:15 | 13.8KV PETAPAHAN FEEDER #8 | Fair | Planned Maintenance | 90 | 14:15 Manually open LBS 30-CZ-03,----->Closed at 14:42. Replace 150Kva Tx to 550Kva Tx at well petapahan#01 Cause: Project. |  | 1 | 14:15 | Afternoon | Tuesday | 2018 | 12
8324 | 2018-12-04 16:08 | 2018-12-04 16:08 | 13.8KV MINAS FEEDER #3 | Fair | Lightning | 0 | Minas fdr #3 load dropped 166A (279-133A). Not checked yet. |  | 1 | 16:08 | Afternoon | Tuesday | 2018 | 12
8325 | 2018-12-04 16:08 | 2018-01-05 08:08 | 13.8KV MINAS FEEDER #3 | Fair | Lightning | 0 | Checked and found Recloser 7D-81 T/R 2x Ctr: 233-235 R/F: 51N @1. Patrolled the line and found Broken Dead End Insulator o/p 7D-99. Cause: Lightning. |  | 1 | 16:08 | Afternoon | Tuesday | 2018 | 12
8326 | 2018-04-13 05:11 | 2018-04-13 05:11 | NELLA SWITCHING STATION | Cloudy | Powerline - Jumper | 626 | 05:11 115KV Nella GCB#27 T/O, 115KV Line Nella Pinang T/O Pinang Substation No power 06:25 Checked & found 115KV Nella GCB#27 T/O, Ctr: 184-185, R/F: 21G @A Zona.1, 21G @A Zona.2 67N Instantinues, 67N Time. 08:30 Patrooled the line and found Broken Jumper (Connection) of X0 for Pinang TX. TTR Tested and Megger the TX, Good condition. Repaired jumper of X-0 Pinang TX. 11:42 Blocked and closed Pinang 115KV GCB #27, OK then released the block. 11:45 Blocked and closed Pinang fdr #1, OK then released the block. Cause: Broken Jumper. | 1234 | 1 | 5:11 | Morning | Friday | 2018 | 4
8327 | 2018-04-13 07:26 | 2018-04-13 07:26 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified | 0 | Duri Comm. 13.8KV ACB fdr #5 T/R 1X. Not checked yet. |  | 1 | 7:26 | Morning | Friday | 2018 | 4
8328 | 2018-04-13 07:26 | 2018-04-19 07:26 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB #33 fdr #5 T/R 1x ctr: 119-120 R/F: 50N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:26 | Morning | Friday | 2018 | 4
8329 | 2018-04-13 10:08 | 2018-04-13 10:08 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 121 | 10:08 Manually Oped Recl. 37-BD-12, ----->Closed at 11:14. Repaired Hot Spot o/p 38-BD-36. Cause: Plan Maintenance. |  | 1 | 10:08 | Morning | Friday | 2018 | 4
8330 | 2018-04-13 16:50 | 2018-04-13 16:50 | 13.8KV PETANI FEEDER #1 | Fair | Construction Job | 0 | 16:50 Manually open Petani 13.8 KV VCB fdr #1, ----->Closed at 17:39. Manually closed HLC at Petani #39. Install 150 KVA TX, 86Hp Reda motor at well Petani #39 (reactive well). Install 300 KVA TX, 100Hp Reda motor at well Petani #129 (New well). Cause: Construction Job. |  | 1 | 16:50 | Afternoon | Friday | 2018 | 4
8331 | 2018-04-13 23:11 | 2018-04-13 23:11 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 0 | Sintong GFPC T/R 1x Sintong Fdr#2 Load dropped 140A(240-100A) Not checked yet |  | 1 | 23:11 | Night | Friday | 2018 | 4
8332 | 2018-04-13 23:11 | 2018-04-16 17:00 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Recloser 26AK24 T/R 1x ctr: 23-24. Patrolled the line & found, @3 broken Pin Insulator on Pole 30-AJ-22. Cause: Pin Insulator. |  | 1 | 23:11 | Night | Friday | 2018 | 4
8333 | 2018-04-13 23:35 | 2018-04-13 23:35 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 62 | Bangko OCB fdr#4 T/R 1x Bangko GFPC TX T/R 1x Not checked yet |  | 1 | 23:35 | Night | Friday | 2018 | 4
8334 | 2018-04-13 23:35 | 2018-04-19 17:00 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 62 | Checked & found, Bangko VCB fdr #4 T/R 1x ctr: 35-36 R/F:51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 23:35 | Night | Friday | 2018 | 4
8335 | 2018-04-14 12:01 | 2018-04-14 12:01 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Construction Job | 0 | 12:01 Manually open LBS 34-CT-58 d/s CKBS fdr #5,----->Closed at 12:22. Re installed 150Kva TX , 60Hp, R/M at well KB #421 (reactive well). Cause: Project. |  | 1 | 12:01 | Afternoon | Saturday | 2018 | 4
8336 | 2018-04-14 14:00 | 2018-04-14 14:00 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Planned Maintenance | 0 | 14:00 Manually open LBS 1-SG-04 d/s Duri Community fdr #5,----->Closed at 16:04. Replaced FCO the TX-2 at Medical. Cause: Planned maintenance. |  | 1 | 14:00 | Afternoon | Saturday | 2018 | 4
8337 | 2018-04-14 17:07 | 2018-04-14 17:07 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Recloser - Control Recloser | 29 | C.Duri fdr #1 load dropped 36A (171 - 71A). Not checked yet. |  | 1 | 17:07 | Afternoon | Saturday | 2018 | 4
8338 | 2018-04-14 17:07 | 2018-04-19 16:56 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Recloser - Control Recloser | 29 | Checked and found Recloser: 38-AS-09 T/R 1x Counter: 272-273 R/F: 51 @1,2,3. Display of recloser can not read. Status Recloser Un plug. Patrolled the line but found nothing. Cause: Control recloser. |  | 1 | 17:07 | Afternoon | Saturday | 2018 | 4
8339 | 2018-04-14 17:41 | 2018-04-14 17:41 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 3 | 17:41 It was reported b/o fuse o/p 06-Q5-05 d/s C.Duri fdr #14. No checked yet. |  | 1 | 17:41 | Afternoon | Saturday | 2018 | 4
8340 | 2018-04-14 17:41 | 2018-04-16 08:41 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 3 | Checked and found @1 Burnt Out Fuse for 112.5 KVA TX o/p 06-Q5-05 D/S Central Duri Fdr #14. Replaced B/O Fuse above with the same size then energized the TX. Cause: Unidentified (Fuse). |  | 1 | 17:41 | Afternoon | Saturday | 2018 | 4
8341 | 2018-04-14 18:03 | 2018-04-14 18:03 | 13.8KV SINTONG FEEDER #1 | Fair | Dead End Insulator | 0 | Sintong fdr #1 load dropped 14A (83 - 69A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 18:03 | Afternoon | Saturday | 2018 | 4
8342 | 2018-04-14 18:03 | 2018-04-15 17:00 | 13.8KV SINTONG FEEDER #1 | Fair | Dead End Insulator | 0 | Checked & found, Recloser 26 AE 22 T/R 1x ctr: 249-250 Patrolled the line & found, @1 broken Dead-end Insulator on Pole 25 AF 38. Cause: Dead-end Insulator. |  | 1 | 18:03 | Afternoon | Saturday | 2018 | 4
8343 | 2018-04-14 19:15 | 2018-04-14 19:15 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Animal | 16 | Rokan VCB fdr#2 T/R Not checked yet. |  | 1 | 19:15 | Night | Saturday | 2018 | 4
8344 | 2018-04-14 19:15 | 2018-04-22 19:15 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Animal | 16 | Checked & found, Rokan VCB fdr #2 T/R 2x ctr: 1259-1261 R/F: 50N. Patrolled the line & found, a Dead Animal (Monkey) on Pole 32-AV-14. Cause: Animal. |  | 1 | 19:15 | Night | Saturday | 2018 | 4
8345 | 2018-04-15 09:17 | 2018-04-15 09:17 | 13.8KV NELLA FEEDER #1 | Fair | Construction Job | 0 | 09:17 Manually Open Recl. 22 V-01, ----->Closed at 15:23. Shuted down power line and TX at well Bangko #79 for RIG Activity. Cause: Plan Construction (Project) | 123 | 1 | 9:17 | Morning | Sunday | 2018 | 4
8346 | 2018-04-15 10:41 | 2018-04-15 10:41 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 0 | 10:41 Manually Open Minas fdr #6, ----->Closed at 12:00. Repaired Latch Line switc. Plan Maintenance. |  | 1 | 10:41 | Morning | Sunday | 2018 | 4
8347 | 2018-04-15 14:05 | 2018-04-15 14:05 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Unidentified | 0 | 14:05 Dumai 4.16KV ACB fdr #1 T/LO ctr:286-288 R/F: 51@1, @2. Patrolled the line and found nothing. 15:50 Blocked and closed Dumai 4160 Kv VCB fdr #1, but tripping again. Checked and patrolled again and found nothing. 17:18 Blocked and closed Dumai 4160 Kv VCB fdr #1 . ok. Cause: Unidentified. |  | 1 | 14:05 | Afternoon | Sunday | 2018 | 4
8348 | 2018-04-15 14:08 | 2018-04-15 14:08 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Tree | 0 | 14:08 It was reported b/o Fuse at Raw Water treating plan. 14:58 Checked and found @1, @1 b/o fuse for 225Kva TX. Replaced the b/o fuse above with same size,then energized the TX, OK. Cause: Tree (Lalang). |  | 1 | 14:08 | Afternoon | Sunday | 2018 | 4
8349 | 2018-04-15 15:05 | 2018-04-15 15:05 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 8 | Ketigul fdr #1 load dropped 87A (120-33A). Not checked yet. |  | 1 | 15:05 | Afternoon | Sunday | 2018 | 4
8350 | 2018-04-15 15:05 | 2018-04-23 15:05 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 8 | Checked & found, Recloser 32 AK 16 T/R 1x ctr: 131-132 R/F: None. Patrolled the line & found, @3 broken Lightning Arrester on Pole 32-AK-38. Cause: Lightning. |  | 1 | 15:05 | Afternoon | Sunday | 2018 | 4
8351 | 2018-04-15 15:26 | 2018-04-15 15:26 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 72 | Ketigul 13.8 Kv Fdr#2 T/R 1 X. Not checked yet. |  | 1 | 15:26 | Afternoon | Sunday | 2018 | 4
8352 | 2018-04-15 15:26 | 2018-04-17 15:26 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 72 | Checked & found, Ketigul VCB fdr #2 T/R 1x ctr: 272-273 R/F:51 @2, @3. Patrolled the line & found, @2, @3, broken Lightning Arrester on Pole 31 AN 08. Cause: Lightning. |  | 1 | 15:26 | Afternoon | Sunday | 2018 | 4
8353 | 2018-04-15 15:30 | 2018-04-15 15:30 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 11 | Sintong fdr #2 load dropped 179A (234-53A). Not checked yet. |  | 1 | 15:30 | Afternoon | Sunday | 2018 | 4
8354 | 2018-04-15 15:30 | 2018-04-16 15:30 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 11 | Checked & found, Recloser 29Z13A T/R 1x ctr: 181-182. Patrolled the line & found, @3 broken Pin Insulator on Pole 29 Z 27. Cause: Lightning. |  | 1 | 15:30 | Afternoon | Sunday | 2018 | 4
8355 | 2018-04-15 18:02 | 2018-04-15 18:02 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 61 | 4D 13.8kv OCB fdr#4 T/R. 4D 13.8Kv OCB fdr#6 load dropped 129A(129-0). Cause: Not Checked yet. |  | 1 | 18:02 | Afternoon | Sunday | 2018 | 4
8356 | 2018-04-15 18:02 | 2018-04-16 17:00 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 61 | Checked & found, 4D OCB fdr #4 T/R 3x ctr: 256-259 R/F: 50N Patrolled the line & found, @1 broken Dead-end Insulator on Pole NN. Cause: Lightning. |  | 1 | 18:02 | Afternoon | Sunday | 2018 | 4
8357 | 2018-04-15 18:24 | 2018-04-15 18:24 | 115KV KOTABATAK JUNCTION - 5B LINE | Rain and Lightning | Lightning | 2895 | 18:24 System Frequency Raise up to 61.19 Hz. Minas GT RTU failed and back normal RTU KBJ Failed and back normal RTU 8C Failed,-----------> Reset then On line at 19:19 RTU OKB,NKB,CKB,PTH,Suram are Failed, IT team will Checked 115Kv Line 5B-KBJ GCB#22 T/O 115Kv Line 5B-KBJ GCB#24 T/O 115Kv Line KBJ-5B GCB#21.....? 115Kv Line KBJ-5B GCB#23.....? NDC#1 Auto Open Gen. Breaker, then closed at 19:10. MGT#6 Auto Open Gen. Breaker, then closed at 18:39. MGT#7 Manually Opened Gen. Breaker, then Closed at 18:45 MGT#8 Manually Opened Gen. Breaker, then Closed at 18:46 18:48 Man. Opened 8D OCB fdr#3, -------> Closed at 19:22 18:57 Man. Opened Minas ACB fdr#3, ----> Closed at 20:00 18:54 3D OCB fdr#6 T/O, ------------------> Closed at 19:01 4D OCB fdr#4 T/O, -----------------.> Closed at 19:02 4D OCB fdr#5 T/O, ------------------> Closed at 19:02 20:30 Checked & found 5B 115KV GCB#22 T/O Ctr:661. 5B 115KV GCB#24 T/O Ctr:74-78 R/F: 87L @1@2@3, 21P Z1. 20:50 Man. Closed 115Kv 5B GCB#22. Man. Closed 115Kv 5B GCB#24. 21:30 It was reported No power Under 6D fdr#2 Checked & found Rec. 6D-298 T/LO, Ctr: 74-78 Man. Block & Closed the Recloser, but Failed. be Continued repatrol. Production Loss: Minas GS1: 0 Minas GS2: 284 Bbls, 101 Wells Minas GS3: 283 Bbls, 22 Wells Minas GS4: 146 Bbls, 42 Wells Minas GS5: 150 Bbls, 49 Wells Minas GS6: 26 Bbls, 14 Wells K.B GS : not yet PC Net work problen PTH GS : not yet PC net work problem ---------------------------------------------------- 889 Bbls, 228 Wells | 1234 | 1 | 18:24 | Afternoon | Sunday | 2018 | 4
8358 | 2018-04-15 18:24 | 2018-04-16 05:48 | 115KV KOTABATAK JUNCTION - 5B LINE | Rain and Lightning | Lightning | 2895 | 05:48 Re-patrolled Line Under Recloser 6D-298 (d/s 6D fdr#2) Found Fall down Tree On take off Pole Well 7C-25N, then Dismantled the Trees. Manually BLock & Closed Recloser 6D-298, Ok, then Released the block. | 1234 | 1 | 18:24 | Afternoon | Sunday | 2018 | 4
8359 | 2018-04-15 18:24 | 2018-04-18 09:25 | 115KV KOTABATAK JUNCTION - 5B LINE | Rain and Lightning | Lightning | 2895 | Checked & found, 5B 115KV GCB#22 T/O Ctr:661. 5B 115KV GCB#24 T/O Ctr:74-78 KBJ 115KV GCB #21 T/O ctr: 194-195 KBJ 115KV GCB #23 T/O ctr: 197-198 R/F: 87L @1@2@3, 21P Z1. Patrolled 115KV line KBJ-5B & found, @1 broken Dead-end Insulator on Pole K5B-02. Cause: Lightning. | 1234 | 1 | 18:24 | Afternoon | Sunday | 2018 | 4
8360 | 2018-04-16 02:40 | 2018-04-16 02:40 | 13.8KV BANGKO FEEDER #3 | Rain and Lightning | Lightning | 56 | Bangko OCB fdr#3 T/R 1x Bangko GFPC T/R 1x Not checked yet. |  | 1 | 2:40 | Night | Monday | 2018 | 4
8361 | 2018-04-16 02:40 | 2018-04-19 02:40 | 13.8KV BANGKO FEEDER #3 | Rain and Lightning | Lightning | 56 | Checked & found, Bangko VCB fdr #3 T/R 1x ctr: 99944-99945 R/F: 51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 2:40 | Night | Monday | 2018 | 4
8362 | 2018-04-16 12:46 | 2018-04-16 12:46 | NORTH DURI POWER PLANT | Fair | Under investigation | 326 | 12:46 NDC CT #1 Genarator Breaker Tripped Off. ---> Closed at 12:56. CPI System frequency dropped to 59:36Hz. (Followed Load Shedding Level-3): 3D fdr #2 Tripped Open,-----> Closed at 13:13. 3D fdr #3 Tripped Open,-----> Closed at 13:13. 3D fdr #5 Tripped Open,-----> Closed at 12:59. 3D fdr #6 Tripped Open,-----> Closed at 12:59. 4D fdr #2 Tripped Open,-----> Closed at 13:13. 4D fdr #3 Tripped Open,-----> Closed at 13:13. 4D fdr #4 Tripped Open,-----> Closed at 13:07. 4D fdr #5 Tripped Open,-----> Closed at 13:07. 4D fdr #6 Tripped Open,-----> Closed at 13:00. 4B fdr #1 Tripped Open,-----> Closed at 13:08. 5B fdr #1 Tripped Open,-----> Closed at 13:09. 5B fdr #3 Tripped Open,-----> Closed at 13:10. 5B fdr #4 Tripped Open,-----> Closed at 13:10. 8D fdr #1 Tripped Open,-----> Closed at 13:11. 8D fdr #3 Tripped Open,-----> Closed at 13:11. 8D fdr #10 Tripped Open,----> Closed at 13:11. 8C fdr #1 Tripped Open,-----> Closed at 13:12. Suram fdr #1 Tripped Open, ----->Closed at 13:08. Zamrud fdr #1 Triped Open, ----->Closed at 13:06. Zamrud fdr #2 Triped Open, ----->Closed at 13:06. Beruk fdr #1 Triped Open, ----->Closed at 13:06. Beruk fdr #2 Triped Open, ----->Closed at 13:06 Pusaka fdr #1 Triped Open, ----->Closed at 13:05. Pusaka fdr #2 Triped Open, ----->Closed at 13:05. Production Loss South Minas GS 1 : 0 Minas GS 2 : 49 Bbls, 23 Wells Minas GS 3 : 0 Minas GS 4 : 681 Bbls, 37 Wells Minas GS 5 : 234 Bbls, 75 Wells Minas GS 6 : 74 Bbls, 2 Wells --------------------------------------- Total : 1038 BBls, 137 Wells Cause : Under investigation | 1234 | 1 | 12:46 | Afternoon | Monday | 2018 | 4
8363 | 2018-04-16 13:38 | 2018-04-16 13:38 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 0 | S,Balam 13.8 Kv fdr#4 T/R 1X. Not checked yet. |  | 1 | 13:38 | Afternoon | Monday | 2018 | 4
8364 | 2018-04-16 13:38 | 2018-04-18 13:38 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 0 | Checked & found, S. Balam VCB fdr #4 T/R 1x ctr: 353-354 R/F: 51 @1, @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 13:38 | Afternoon | Monday | 2018 | 4
8365 | 2018-04-16 15:37 | 2018-04-16 15:37 | 13.8KV 6DN FEEDER #5 | Fair | Others | 0 | 15:37 Manually Open 6DN fdr #5, ----->Closed at 18:24. Maintenance Level Tank due to WIP Problem. Cause: Others (WIP Problem). |  | 1 | 15:37 | Afternoon | Monday | 2018 | 4
8366 | 2018-04-16 17:07 | 2018-04-16 17:07 | 13.8KV CENTRAL DURI FEEDER #16 | Rain | Unidentified | 0 | C. Duri 13.8KV ACB fdr #16 T/R 1X ctr:132-133 R/F: 51 @1, @2. Not checked yet. |  | 1 | 17:07 | Afternoon | Monday | 2018 | 4
8367 | 2018-04-16 17:07 | 2018-04-17 17:07 | 13.8KV CENTRAL DURI FEEDER #16 | Rain | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:07 | Afternoon | Monday | 2018 | 4
8368 | 2018-04-16 18:24 | 2018-04-16 18:24 | 13.8KV 6DN FEEDER #6 | Fair | Others | 0 | 18:24 Manually Open 6DN fdr #6, ----->Closed at 21:00. Maintenance Level Tank due to WIP Problem. Cause: Others (WIP Problem). |  | 1 | 18:24 | Afternoon | Monday | 2018 | 4
8369 | 2018-04-17 09:23 | 2018-04-17 09:23 | 13.8KV BANGKO FEEDER #1 | Fair | Construction Job | 0 | 09:23 Manually Open Bangko fdr #1, ----->Closed at 11:21. Tie in New well at Bangko #327 and reactive well at Bangko # 198. Project. |  | 1 | 9:23 | Morning | Tuesday | 2018 | 4
8370 | 2018-04-18 10:17 | 2018-04-18 10:17 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 82 | 10:17 Manually opened Recl: 2D-33 D/S 3D fdr #4 due to : - Replaced broken Pin & Dead end Insulator. 19:15 Manually Open Recl: 2D-14, ----->Close at 19:24. By Pass Recl: 2D-33 Cause: Plan Maintenance. |  | 1 | 10:17 | Morning | Wednesday | 2018 | 4
8371 | 2018-04-18 10:39 | 2018-04-18 10:39 | 13.8KV BANGKO FEEDER #1 | Fair | Construction Job | 0 | 10:39 Opened Hot Line Clamp on pole 23-X-72 due to : - Shut down well Bangko #241 and relocate pole for new well. Work will last until next week. Cause: Construction Job. |  | 1 | 10:39 | Morning | Wednesday | 2018 | 4
8372 | 2018-04-18 12:59 | 2018-04-18 12:59 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 60 | Sintong OCB fdr #1 T/R 1x and T/R again at 13:01. Sintong GFPC T/R 2x. Not checked yet. |  | 1 | 12:59 | Afternoon | Wednesday | 2018 | 4
8373 | 2018-04-18 12:59 | 2018-04-19 12:59 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 60 | Checked & found, Sintong OCB fdr #1 T/R 2x ctr: 390-392 R/F: 51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 12:59 | Afternoon | Wednesday | 2018 | 4
8374 | 2018-04-18 12:59 | 2018-04-18 12:59 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 67 | Sintong fdr #2 load dropped 180A (234-54A). Not checked yet. |  | 1 | 12:59 | Afternoon | Wednesday | 2018 | 4
8375 | 2018-04-18 12:59 | 2018-04-19 12:59 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 67 | Checked & found, Recloser 38AF17 T/R 3x ctr: 451-454. Patrolled the line & found, @3 broken Lightning Arrester on T/P of Well Mutiara #2. Cause: Lightning. |  | 1 | 12:59 | Afternoon | Wednesday | 2018 | 4
8376 | 2018-04-19 11:04 | 2018-04-19 11:04 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 126 | 11:04 Manually opened C.Duri ACB #11 (feeder #1) due to: - Repair @2 broken jumper Hot Line Clamp on Recloser: 41-AW-62. 11:54 Manually blocked and closed C.Duri ACB #11 (feeder #1) and then released the block. Cause: Plan maintenance. Production Loss: 47 Bbls / 60 Wells, -----> Kulin Area. 32 Bbls / 71 Wells, -----> Area 8. 48 Bbls / 18 Wells, -----> Balam Area. ---------------------------------------------+ TOTAL : 127 Bbs / 149 Wells. |  | 1 | 11:04 | Morning | Thursday | 2018 | 4
8377 | 2018-04-19 13:51 | 2018-04-19 13:51 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 4 | 13:51 Manually opened Recloser: 37-BD-40 D/S Bekasap fdr #2 due to: - Change out Transformer at well Bekasap #161. Tx : 225 Kva R/M : 175 HP Sec voltage: 1070 V. 14:43 Manually blocked and closed Recloser: 37-BD-40 and then released the block. Cause: Plan Maintenance. |  | 1 | 13:51 | Afternoon | Thursday | 2018 | 4
8378 | 2018-04-19 17:14 | 2018-04-19 17:14 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 69 | It was reported b/o fuse for Tx o/p 11-H5-31 D/S N Duri fdr #9. Not checked yet. |  | 1 | 17:14 | Afternoon | Thursday | 2018 | 4
8379 | 2018-04-19 17:14 | 2018-04-20 09:48 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 69 | Checked and found @2 b/o fuse for 112.5 Kva. Replaced b/o fuse above with the same size and then energized the Tx. Cause : Animal (Bird). |  | 1 | 17:14 | Afternoon | Thursday | 2018 | 4
8380 | 2018-04-19 17:37 | 2018-04-19 17:37 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 0 | It was reported b/o fuse at well Kulin #82 D/S C.Duri Fdr #1. Not checked yet. |  | 1 | 17:37 | Afternoon | Thursday | 2018 | 4
8381 | 2018-04-19 17:37 | 2018-04-20 15:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 0 | Checked and found @2 b/o fuse for 112.5 Kva. Replaced b/o fuse above with the same size and then energized the Tx. Cause : Others (Kite). |  | 1 | 17:37 | Afternoon | Thursday | 2018 | 4
8382 | 2018-04-19 19:17 | 2018-04-19 19:17 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | N.Duri 13.8 KV fdr #7 load dropped 83A (86-3A). Not checked yet. |  | 1 | 19:17 | Night | Thursday | 2018 | 4
8383 | 2018-04-19 19:17 | 2018-04-23 17:00 | 13.8KV NORTH DURI FEEDER #7 | Fair | Unidentified | 0 | Checked & found, Recloser 10-K2-18 T/R 1x ctr: 68-69. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 19:17 | Night | Thursday | 2018 | 4
8384 | 2018-04-20 06:35 | 2018-04-20 06:35 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 06:35 It was reported b/o fuse o/p 06-S7-04 D/S D Field fdr #4. 10:26 Checked and found @2 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above with the same size and energized the Tx. Cause: Unidentified (fuse). |  | 1 | 6:35 | Morning | Friday | 2018 | 4
8385 | 2018-04-20 06:55 | 2018-04-20 06:55 | 13.8KV MINAS FEEDER #6 | Fair | Lightning | 0 | Minas 13,8KV ACB fdr #6 T/R 1X. Not checked yet. |  | 1 | 6:55 | Morning | Friday | 2018 | 4
8386 | 2018-04-20 06:55 | 2018-04-26 08:55 | 13.8KV MINAS FEEDER #6 | Fair | Lightning | 0 | Checked and found 13.8KV Minas fdr #6 T/R 1x Ctr: 171-172 R/F: 51N @1. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 6:55 | Morning | Friday | 2018 | 4
8387 | 2018-04-20 14:57 | 2018-04-20 14:57 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Unidentified | 40 | Bangko fdr #1 Load dropped 80A (161-81A). Bangko fdr #2 load dropped 240A (262-22A). WIP. Bangko fdr #3 load dropped 188A (253-65A). WIP. Not checked yet. |  | 1 | 14:57 | Afternoon | Friday | 2018 | 4
8388 | 2018-04-20 14:57 | 2018-04-21 14:57 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Unidentified | 40 | Checked & found, no Recloser operated under this Feeder. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:57 | Afternoon | Friday | 2018 | 4
8389 | 2018-04-20 14:57 | 2018-04-20 14:57 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 6 | Bangko fdr #4 load dropped 61A (162-101A). Not checked yet. |  | 1 | 14:57 | Afternoon | Friday | 2018 | 4
8390 | 2018-04-20 14:57 | 2018-04-21 14:57 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 6 | Checked & found, no Recloser operated under this Feeder. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:57 | Afternoon | Friday | 2018 | 4
8391 | 2018-04-21 02:36 | 2018-04-21 02:36 | 115KV DURI - PUNGUT LINE | Rain and Lightning | Lightning | 49 | 02:36 Duri-Pungut 115KV OCB #21 T/R 1X. Duri-Pungut 115KV OCB #29 T/R 1X. (No Power to Pungut MSU). Not Checked yet. |  | 1 | 2:36 | Night | Saturday | 2018 | 4
8392 | 2018-04-21 02:36 | 2018-07-05 11:30 | 115KV DURI - PUNGUT LINE | Rain and Lightning | Lightning | 49 | Checked & found, Duri-Pungut 115KV OCB #21 T/R 1X ctr: 250-251 R/F: 87L Duri-Pungut 115KV OCB #29 T/R 1X ctr: 138-139 Patrolled the line but found nothing Cause: Suspected by Lightning. |  | 1 | 2:36 | Night | Saturday | 2018 | 4
8393 | 2018-04-21 07:58 | 2018-04-21 07:58 | 44KV NORTH DURI - DUMAI LINE | Fair | Unidentified | 0 | 07:58 N.Duri 44KV line GCB#1 T/R 17:00 Checked & found, 44 KV N. Duri GCB #1 (44KV N. Duri-Dumai) T/R 1x ctr: 123-124 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:58 | Morning | Saturday | 2018 | 4
8394 | 2018-04-21 09:43 | 2018-04-21 09:43 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Lightning Arrester | 0 | Duri commy ACB#30 (fdr#2) T/R Not checked yet |  | 1 | 9:43 | Morning | Saturday | 2018 | 4
8395 | 2018-04-21 09:43 | 2018-04-25 09:43 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Lightning Arrester | 0 | Checked & found, Duri Community ACB #30 fdr #2 T/R 2x ctr: 95-97 R/F: 51N. Patrolled the line & found, @1 broken Lightning Arrester on Pole SL 01. Cause: Lightning Arrester. |  | 1 | 9:43 | Morning | Saturday | 2018 | 4
8396 | 2018-04-21 10:21 | 2018-04-21 10:21 | DURI FIELD SWITCH GEAR | Fair | Under investigation | 2277 | 10:21 Duri Field SWGR RTU ----->Failed It was reported no power at CGS#1 11:27 Checked & faund DF 13.8KV VCB#45 (44) T/O, ----->Closed at 11:30. 11:27 Manually opened DF VCB fdr#1, ----->Closed at 11:32. Manually opened DF VCB fdr#2, ----->Closed at 11:32 Duri 115KV OCB #22 T/O ctr: 295-296. Duri 115KV OCB #26 T/O ctr: 916-Not change. (No Power to DF TX-3) Manually Open 13.8KV VCB #45. Manually opened DF VCB fdr#1. Manually opened DF VCB fdr#2. 12:15 Closed DF 13.8KV VCB #49 (TIE). (DF fdr #1 and DF fdr #2 supply from DF TX-5). 12:21 Blocked and Closed DF VCB fdr#1, then released the block. Blocked and Closed DF VCB fdr#2, then released the block. 12:23 DF RTU On Line. 12:26 DF Station Service A Energized. 12:31 DF 13.8KV VCB #54 T/O. (No Power to DF fdr #1, #2, #3 and #4). Manually opened DF VCB fdr#1. Manually opened DF VCB fdr#2. Manually opened DF VCB fdr#3. Manually opened DF VCB fdr#4. 12:39 Closed DF 13.8KV VCB #54, OK. 12:41 Blocked and Closed DF VCB fdr#3, then released the block. 12:43 Blocked and Closed DF VCB fdr#4, then released the block. 12:46 Duri 115KV OCB #28 T/O ctr: 178-179. Duri 115KV OCB #30 T/O ctr: 96-97. (No Power to DF TX-5) 12:57 Closed Duri 115KV OCB #30, OK. 15:27 Closed Duri 115KV OCB #28, OK. 16:46 Open Line Switch :252-73-02 . (To Isolated DF TX-3) 16:48 Closed Duri 115KV OCB #26, OK. 16:50 Closed Duri 115KV OCB #22, OK. *Transfer load DF fdr #1 and DF fdr #3 to C. Duri fdr #4. Un Plug Recloser : 01-08-31. 14:24 Closed LBS: 01-03-01. 14:30 Closed LBS: 01-05-01. 14:24 Closed LBS: 01-08-01. *Transfer load DF fdr #2 to C. Duri fdr #15. 14:22 Closed LBS: 06-R4-01. *Transfer load DF fdr #4to C. Duri fdr #14. Un Plug Recloser : 06-Q2-02. 15:01 Closed LBS: 06-R4-02. Cause: Under Investigation. | 12345 | 1 | 10:21 | Morning | Saturday | 2018 | 4
8397 | 2018-04-21 14:36 | 2018-04-21 14:36 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 0 | Menggala fdr#1 load dropped 89A (142-53A) Menggala GFPC T/R Not checked yet |  | 1 | 14:36 | Afternoon | Saturday | 2018 | 4
8398 | 2018-04-21 14:36 | 2018-04-22 14:36 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recloser 19-AN-04 T/R 2x ctr: 612-614. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 14:36 | Afternoon | Saturday | 2018 | 4
8399 | 2018-04-21 15:04 | 2018-04-21 15:04 | 13.8KV BEKASAP FEEDER #6 | Lightning | Others | 0 | Bekasap fdr#6 load dropped 64A (186-122A) Bekasap fdr#2 load dropped 11A (184-172A) Bekasap fdr#3 load dropped 23A (95-72A) Bekasap fdr#5 load dropped 80A (187-107A)WIP Not checked yet |  | 1 | 15:04 | Afternoon | Saturday | 2018 | 4
8400 | 2018-04-21 15:04 | 2018-04-25 15:04 | 13.8KV BEKASAP FEEDER #6 | Lightning | Others | 0 | Checked & found, Recloser 38BE10 T/R 2x ctr: 595-597. Patrolled the line & found, a Kite hang on @3 of Powerline on Pole 39-BE-23A. Cause: Others (Kite). |  | 1 | 15:04 | Afternoon | Saturday | 2018 | 4
8401 | 2018-04-21 15:56 | 2018-04-21 15:56 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 23 | 15:56 4B 13.8KV VCB fdr#1 T/R 1X. 21:17 Checked and found Recl. :4B-101 T/SO ctr:622-623. Blocked and closed the Recloser, OK then released the block. Not patrolled yet |  | 1 | 15:56 | Afternoon | Saturday | 2018 | 4
8402 | 2018-04-21 15:56 | 2018-04-26 08:56 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 23 | Checked and found 413.8KV 4B fdr #1 T/R 1x Ctr: 622-623 R/F: - Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 15:56 | Afternoon | Saturday | 2018 | 4
8403 | 2018-04-21 16:37 | 2018-04-21 16:37 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Transformer Failure | 20 | It was reported b/o fuse o/p 09-S4-04 D/S CD#4 Not checked yet |  | 1 | 16:37 | Afternoon | Saturday | 2018 | 4
8404 | 2018-04-21 16:37 | 2018-04-22 09:20 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Transformer Failure | 20 | Checked and found @2 b/o fuse for 112.5 Kva Tx. Replaced b/o fuse above but burnt out again. Perform TTR and Megger found low megger reading. Cause: Tx failure (low megger reading). |  | 1 | 16:37 | Afternoon | Saturday | 2018 | 4
8405 | 2018-04-22 10:14 | 2018-04-22 10:14 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 10:14 C.Duri fdr#1 load dropped 60A (106-46A) 15:45 C.Duri fdr#1 load dropped 43A (106-63A) Not checked yet |  | 1 | 10:14 | Morning | Sunday | 2018 | 4
8406 | 2018-04-22 10:14 | 2018-04-23 17:14 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recloser 41-AW-62 T/R 1x ctr: 267-268 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:14 | Morning | Sunday | 2018 | 4
8407 | 2018-04-22 11:56 | 2018-04-22 11:56 | 13.8KV LIBO FEEDER #2 | Fair | Recloser - Control Recloser | 15 | 11:56 Libo fdr#2 load dropped 25A (52-27A) 13:10 Checked & found reclosed 23-BW-02 T/O D/S Libo fdr#2 Blocked & closed reclosed 23-BW-02------->OK and then reclosed the block Cause :Control Reclosed |  | 1 | 11:56 | Morning | Sunday | 2018 | 4
8408 | 2018-04-22 13:56 | 2018-04-22 13:56 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Transformer Failure | 516 | 13:56 Petapahan fdr #3 load dropped 172A (172-0A). 14:18 Checked and found PTH fdr #3 Normal. Checked and found Recloser: 28-CX-05 T/O. (In blocked position due to RIG activity at well PTH #142). Also found 300KVA TX failure at well PTH #76. 14:22 Manually Open PTH fdr #3. By Pass Recloser: 28-CX-05. 14:57 Blocked and closed PTH fdr #3. Cause: TX failure (300KVA TX at well PTH #76). | 12134 | 1 | 13:56 | Afternoon | Sunday | 2018 | 4
8409 | 2018-04-22 15:55 | 2018-04-22 15:55 | NORTH DURI POWER PLANT | Rain and Lightning | Under investigation | 455 | 15:55 N. Duri 230KV GCB #33 T/O, ----->Closed at 16:14. N. Duri 230KV GCB #35 T/O, ----->Closed at 16:14. (NDC #3 Open Generator breaker) R/F: 86-1 (Generator field breaker tripped) System Frequency dropped to: 59.46 . *Load Shedding level : 3. 3D fdr#2 tripped Open, ----->Closed at 16:32 3D fdr#3 tripped Open, ----->Closed at 16:33 3D fdr#5 tripped Open, ----->Closed at 16:00 3D fdr#6 tripped Open, ----->Closed at 16:26 4B fdr#1 tripped Open, ----->Closed at 16:17 4D fdr#2 tripped Open, ----->Closed at 16:31 4D fdr#3 tripped Open, ----->Closed at 16:32 4D fdr#4 tripped Open, ----->Closed at 16:27 4D fdr#5 tripped Open, ----->Closed at 16:29 4D fdr#6 tripped Open, ----->Closed at 16:30 5B fdr#1 tripped Open, ----->Closed at 16:39 5B fdr#3 tripped Open, ----->Closed at 16:39 5B fdr#4 tripped Open, ----->Closed at 16:21 8C fdr#1 tripped Open, ----->Closed at 17:06 8D fdr#1 tripped Open, ----->Closed at 16:19 8D fdr#3 tripped Open, ----->Closed at 16:22 8D fdr#10 tripped Open, ----->Closed at 16:41 Suram fdr#1 tripped Open, ----->Closed at 16:53 Zamrud fdr #1 tripped Open, -----Closed at 16:31. Zamrud fdr #2 tripped Open, -----Closed at 16:31. Zamrud fdr #4 tripped Open, -----Closed at 16:31. Pusaka fdr #1 tripped Open, -----Closed at 16:27. Pusaka fdr #2 tripped Open, -----Closed at 16:27. Beruk fdr #2 tripped Open, -----Closed at 16:55. Bangko fdr#1 load dropped 115A (160-45A). Bangko fdr#2 load dropped 199A (226-27A). Bangko fdr#3 load dropped 58A (240-182A). Bangko fdr#4 load dropped 29A (160-131A). Sintong fdr#2 load dropped 80A (243-163A). SO.Balam fdr#1 load dropped 12A (132-120A). Nella fdr#1 load dropped 36A (226-190A). Nella fdr#2 load dropped 16A (65-49A). Cause: Under Investigation. *Production Loss: GS#1 : 176 Bbls / 38 Wells. GS#2 : 68 Bbls / 24 Wells. GS#6 : 212 Bbls / 75 Wells. GS#4 : 124 Bbls / 46 Wells. GS#5 : 113 Bbls / 40 Wells. Bangko fdr#1 : 25 Bbls / 8 Wells. Sintong fdr#2 : 12 Bbls / 6 Wells. Nella fdr#2 : 5 Bbls / 2 Wells. ------------------------------------------+ TOTAL : 735 Bbls / 239 Wells. | 1234 | 1 | 15:55 | Afternoon | Sunday | 2018 | 4
8410 | 2018-04-22 16:25 | 2018-04-22 16:25 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 72 | Bangko fdr#4 T/R 1X. Not checked yet |  | 1 | 16:25 | Afternoon | Sunday | 2018 | 4
8411 | 2018-04-22 16:25 | 2018-04-24 16:25 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 72 | Checked & found, Bangko OCB fdr #4 T/R 3x ctr: 36-39 R/F: 51. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 16:25 | Afternoon | Sunday | 2018 | 4
8412 | 2018-04-22 16:33 | 2018-04-22 16:33 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain and Lightning | Lightning | 0 | Duri Commy fdr#2 T/R 1x. Not checked yet |  | 1 | 16:33 | Afternoon | Sunday | 2018 | 4
8413 | 2018-04-22 16:33 | 2018-04-25 16:33 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Duri Community ACB #30 fdr #2 T/R 2x ctr: 95-97 R/F:51@1. Patrolled the line & found, @1 broken Lightning Arrester on Pole SL 2-01. Cause: Lightning. |  | 1 | 16:33 | Afternoon | Sunday | 2018 | 4
8414 | 2018-04-22 16:49 | 2018-04-22 16:49 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 13 | Nella fdr#1 T/R 1X Nella GFPC T/R 1X Not checked yet |  | 1 | 16:49 | Afternoon | Sunday | 2018 | 4
8415 | 2018-04-22 16:49 | 2018-04-23 16:49 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 13 | Checked & found, Nella VCB fdr #1 T/R 1x ctr: 519-520 R/F: 51N Patrolled the line & found, @2 broken Lightning Arrester on Pole 21 V 11. Cause: Lightning. |  | 1 | 16:49 | Afternoon | Sunday | 2018 | 4
8416 | 2018-04-22 17:19 | 2018-04-22 17:19 | 13.8KV CENTRAL DURI FEEDER #14 | Rain and Lightning | Unidentified | 0 | C.Duri 13.8KV VCB#27 fdr#14 T/R 1X Not checked yet |  | 1 | 17:19 | Afternoon | Sunday | 2018 | 4
8417 | 2018-04-22 17:19 | 2018-04-29 08:19 | 13.8KV CENTRAL DURI FEEDER #14 | Rain and Lightning | Unidentified | 0 | Checked and found C. Duri fdr #14 T/R 1x Ctr: 394-395 R/F: 51N @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:19 | Afternoon | Sunday | 2018 | 4
8418 | 2018-04-22 21:25 | 2018-04-22 21:25 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 78 | 21:25 It was reported no power around o/p 12-03-17. 23:20 Checked and found Recl: 12-03-27 T/O ctr: 23-24. (In blocked due to RIG activity AU #3518). Patrolled the line but found nothing. 23:35 Blocked and closed the Recloser, OK. Cause: Unidentified. | 1234 | 1 | 21:25 | Night | Sunday | 2018 | 4
8419 | 2018-04-23 09:41 | 2018-04-23 09:41 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 0 | 09:41 Manually opened recl: 37 B1 01 d/s So.Bek fgdr #1. Due to dismantle well Pematang Bow #11, #18, #25.Status LTC. 11:28 Manual blocked & closed recl: 37 B1 01. and then release the block. Ctr : 1316. Cause : Plan Maintenance. |  | 1 | 9:41 | Morning | Monday | 2018 | 4
8420 | 2018-04-23 11:56 | 2018-04-23 11:56 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 11:59 CD Fdr #1 Load drop 40A. Not checked yet. |  | 1 | 11:56 | Morning | Monday | 2018 | 4
8421 | 2018-04-23 11:56 | 2018-06-05 11:56 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found Recl.: 39-AV-36 T/R 1X ctr:248-249 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 11:56 | Morning | Monday | 2018 | 4
8422 | 2018-04-23 12:55 | 2018-04-23 12:55 | 230KV N. Duri-KBJ Line - 1 - TWR 129-192 | Rain and Lightning | Tree | 726 | 12:55 230 Kv N.Duri GCB # 23 T/SO 230 Kv N.Duri GCB # 25 T/SO 230 Kv KBJ GCB # 91 T/SO. 230 Kv KBJ GCB # 92 T/LO. 15:06 Checked and found: 230 Kv N.Duri GCB # 23 T/SO ctr: 243-244 R/F: 51@1 (D60). 230 Kv N.Duri GCB # 25 T/SO ctr: 205-206 R/F: 51@1 (L90). 14:21 Manually Open CKBS fdr #6, ----->Closed at 19:23. 16:34 Manually Open CKBS fdr #5, ----->Closed at 21:02. 18:30 Checked and found: 230 Kv KBJ GCB # 91 T/SO ctr: 294-295 R/F 21G@C, 67N (INST) & 51@C (D60). 230 Kv KBJ GCB # 92 T/LO ctr: 272-275 R/F 21G@C, 67N (INST), 51@C (D60). Also found R/F: 87L @C and 86L-1. 19:29 Closed 230KV KBJ GCB #91 (DL). 19:30 Closed 230KV ND GCB #23 (SC). 19:31 Closed 230KV KBJ GCB #92 (SC). 19:32 Closed 230KV ND GCB #25 (SC). Cause: Tree. | 123 | 1 | 12:55 | Afternoon | Monday | 2018 | 4
8423 | 2018-04-23 14:22 | 2018-04-23 14:22 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Planned Maintenance | 0 | 14:22 Menually opened PTH Fdr #6 due to : Replaced Transformer at well PTH #07. TX: R/M: Sec. voltage 15:10 Manually blocked and closed PTH Fdr #6 and then release the blocked. Cause : Plan Maintenance. |  | 1 | 14:22 | Afternoon | Monday | 2018 | 4
8424 | 2018-04-23 15:06 | 2018-04-23 15:06 | 13.8KV S. BALAM FEEDER #4 | Fair | Transformer Failure | 48 | It was reported b/o fuse at well Balam #54. Not checked yet. |  | 1 | 15:06 | Afternoon | Monday | 2018 | 4
8425 | 2018-04-23 15:06 | 2018-04-24 11:42 | 13.8KV S. BALAM FEEDER #4 | Fair | Transformer Failure | 48 | Replaced 100 Kva Transformer failure with the same size and energized the Tx. Cause: Tx failure (low megger reading). |  | 1 | 15:06 | Afternoon | Monday | 2018 | 4
8426 | 2018-04-23 15:07 | 2018-04-23 15:07 | 44KV NORTH DURI - DUMAI LINE | Rain | Unidentified | 0 | 44KV ND-DMI GCB #1 T/R 1X Not checked yet. |  | 1 | 15:07 | Afternoon | Monday | 2018 | 4
8427 | 2018-04-23 15:07 | 2018-04-29 08:07 | 44KV NORTH DURI - DUMAI LINE | Rain | Unidentified | 0 | Checked and found 44KV ND-Dumai GCB #44 T/R 1x Ctr: 124-125 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:07 | Afternoon | Monday | 2018 | 4
8428 | 2018-04-23 15:16 | 2018-04-23 15:16 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | 15:16 CD Fdr #1 Load drop 43A (106-63A). Checked & found, Recloser 41-AW-62 T/R 1x ctr: 168-169 R/F:51. Patrolled the line found broken secondary Cable on T/P Kulim#10. Cause: Unidentified (Suspected by Lightning). |  | 1 | 15:16 | Afternoon | Monday | 2018 | 4
8429 | 2018-04-23 15:52 | 2018-04-23 15:52 | 13.8KV SO BEKASAP FEEDER #1 | Rain | Unidentified | 155 | 15:52 So. Bekasap Fdr #1 load drop 60A (88-28A). Not checked yet. |  | 1 | 15:52 | Afternoon | Monday | 2018 | 4
8430 | 2018-04-23 15:52 | 2018-04-25 15:52 | 13.8KV SO BEKASAP FEEDER #1 | Rain | Unidentified | 155 | Checked & found, Recloser 34-BI-18 T/R 1x ctr: 170-171. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:52 | Afternoon | Monday | 2018 | 4
8431 | 2018-04-24 09:39 | 2018-04-24 09:39 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 0 | 09:39 It was reported b/o fuse at well Meno #26 d/s Manggala Fdr #1. 11:30 Checked and found @1 b/o fuse for 225 KVATX Replaced b/o fuse above with the same size and energized the Tx Cause : Animal ( Bird ). |  | 1 | 9:39 | Morning | Tuesday | 2018 | 4
8432 | 2018-04-24 10:25 | 2018-04-24 10:25 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Planned Maintenance | 153 | 10:24 Manually opened PTH VCB Fdr #4 due to: Replaced TX at well PTH #72. TX:300KVA, R/M: 180 , Sec.voltage: 1100 Volt. 10:36 Manually blocked and closed PTH VCB Fdr #4 and then released the block. Cause : Plan Maintenance. |  | 1 | 10:25 | Morning | Tuesday | 2018 | 4
8433 | 2018-04-24 11:01 | 2018-04-24 11:01 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Transformer Failure | 230 | 11:01 Manually opened PTH VCB Fdr #3 due to: Replaced TX at well PTH #76. TX: 260 KVA, R/M: 30 HP, Sec.voltage: 480 Volt. 11:33 Manually blocked and closed PTH VCB Fdr #3 and then released the block. Cause : TX Failure. |  | 1 | 11:01 | Morning | Tuesday | 2018 | 4
8434 | 2018-04-24 17:05 | 2018-04-24 17:05 | MINAS POWER PLANT |  |  | - | 17:05 S/U MGT #4 and then online the unit at 17:43. |  | 1 | 17:05 | Afternoon | Tuesday | 2018 | 4
8435 | 2018-04-25 10:05 | 2018-04-25 10:05 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 0 | 10:05 Manually Opened Recloser 28 AF 17 (d/s Sintong fdr#2) to Repair Lost Connection on T/Op well Sintong #32 10:55 Manually Block & Closed the Recloser, then released the block. after finished the Jobs. Cause: Planned maintenance |  | 1 | 10:05 | Morning | Wednesday | 2018 | 4
8436 | 2018-04-25 14:00 | 2018-04-25 14:00 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 43 | 14:00 Sintong Fdr#2 T/R 1x Sintong GFPC T/R 1x Ground Fault alarm at Sintong Fdr#2 Not Checked yet |  | 1 | 14:00 | Afternoon | Wednesday | 2018 | 4
8437 | 2018-04-25 14:00 | 2018-04-29 08:00 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 43 | Checked and found 13.8KV Sintong fdr #2 T/R 1x Ctr: 471-472 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:00 | Afternoon | Wednesday | 2018 | 4
8438 | 2018-04-25 16:31 | 2018-04-25 16:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 21 | 16:31 Manually Opened Recloser 41 AW 62 (d/s Cduri fdr#1) to Replace Secondary Cable Was loss before at Well KL#10 & KL#89 17:05 Manually Block & Closed the Recloser, then released the block, after Finished the Jobs. Cause: Planned Maintenance |  | 1 | 16:31 | Afternoon | Wednesday | 2018 | 4
8439 | 2018-04-26 08:38 | 2018-04-26 08:38 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 16 | Libo OCB Fdr#1 T/R 1x Not checked yet. |  | 1 | 8:38 | Morning | Thursday | 2018 | 4
8440 | 2018-04-26 08:38 | 2018-04-29 08:38 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 16 | Checked and found 13.8KV Libo Fdr #1 T/R 1x Ctr: 577-578 R/F: 51N @2, @3. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 8:38 | Morning | Thursday | 2018 | 4
8441 | 2018-04-26 09:21 | 2018-04-26 09:21 | MINAS POWER PLANT | Fair |  | - | 09:21 S/U MGT #11, then On line at 11:21 for Running tested, and took some data until 20 MW. |  | 1 | 9:21 | Morning | Thursday | 2018 | 4
8442 | 2018-04-26 10:20 | 2018-04-26 10:20 | 13.8KV PEMATANG FEEDER #2 | Fair | Construction Job | 0 | 10:20 Manually Opened Recloser 34-BC-08 (d/s Pematang fdr#2) to Dis Connect & Reconnected HLC and Insert Pole for New Well Pematang #101. 11:11 Manually Block & Closed the Recloser after finished the Jobs Cause: Planned (Construction) |  | 1 | 10:20 | Morning | Thursday | 2018 | 4
8443 | 2018-04-26 14:20 | 2018-04-26 14:20 | 13.8KV BANGKO FEEDER #1 | Fair | Construction Job | 0 | 14:20 Manually Opened Bangko OCB fdr#1 Reconnected HLC and Reenergized 300KVA TX at Well BKO#241 15:56 Manually Block & Closed the OCB, after Finished the Jobs Cause: Planned (Construction) |  | 1 | 14:20 | Afternoon | Thursday | 2018 | 4
8444 | 2018-04-26 15:23 | 2018-04-26 15:23 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Planned Maintenance | 77 | 15:23 Manually Opened Recloser 04-02-22 (d/s CDuri fdr#8) to Replace B/O 112.5KVATX o/p 04-02-12. 16:55 Manually Block & Closed the Recloser, then Released the block after finished the Jobs. Cause: Planned Maintenance |  | 1 | 15:23 | Afternoon | Thursday | 2018 | 4
8445 | 2018-04-27 09:50 | 2018-04-27 09:50 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 145 | 09:50 Manually Opened Recl. 28-AF-02 (d/s Sintong Fdr#2) to Repair B/O & lost Connection at VR O/P 29-AB-11 11:25 Manually Block & Closed the Recloser then released the block After finished the Jobs. Cause: Planned Manitenance. |  | 1 | 9:50 | Morning | Friday | 2018 | 4
8446 | 2018-04-27 10:33 | 2018-04-27 10:33 | 13.8KV PUNGUT FEEDER #2 | Fair | Low mega-ohm reading | 0 | 10:33 It was reported B/O fuse for 750 KVATX for Tandun GS WIP2. Not checked yet |  | 1 | 10:33 | Morning | Friday | 2018 | 4
8447 | 2018-04-27 10:33 | 2018-04-29 10:33 | 13.8KV PUNGUT FEEDER #2 | Fair | Low mega-ohm reading | 0 | Checked & found, @2 b/o Fuse for 750KVA Tx at Tandun GS. Performed TTR & Megger Test, found Low Mega-ohm Reading Tx. Cause: Low Mega-ohm Reading Tx. (Will be replaced soon). |  | 1 | 10:33 | Morning | Friday | 2018 | 4
8448 | 2018-04-27 10:33 | 2018-01-05 15:00 | 13.8KV PUNGUT FEEDER #2 | Fair | Low mega-ohm reading | 0 | Replaced 750KVA Tx with the same size for Tandun GS WIP2. Cause: Low Mega-ohm Reading Tx. |  | 1 | 10:33 | Morning | Friday | 2018 | 4
8449 | 2018-04-27 10:41 | 2018-04-27 10:41 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 76 | 10:41 Manually Opened LBS 36-CU-05 (d/s CKB fdr#1) to Change Out of Switch Board to VSD at Well KB#388 & #400 11:10 Manually Closed the LBS after finished the Jobs. Cause: Planned Construction. |  | 1 | 10:41 | Morning | Friday | 2018 | 4
8450 | 2018-04-27 11:18 | 2018-04-27 11:18 | MINAS POWER PLANT |  |  | - | 11:18 MGT #4 Off Line , then S/D for S/B |  | 1 | 11:18 | Morning | Friday | 2018 | 4
8451 | 2018-04-27 14:58 | 2018-04-27 14:58 | 44KV PEMATANG MAIN - PEMATANG LINE | Fair | Planned Maintenance | 767 | 14:46 Manually Opened Pematang OCB fdr#2,-------------> Closed at 18:00 14:48 Manually Opened Rangau OCB fdr#1,----------------> Closed at 17:58 14:57 Manually Opened Pematang OCB fdr#1,-------------> Closed at 17:36. 14:58 Manually Opened Pematang Main 44KB OCB #3,---> Closed at 17:33 14:59 Manually Opened Pematang 44KV OCB #1,---------> Closed at 17:35 Cause: Planned Maintenance. Work Over Well, Replaced 150 to 300 KVATX, adjust Voltge 480 to 1050V. Production loss : 1. Pematang fdr #1 = 194 Bbls / 16 wells. 2. Pematang fdr #2 = 284 Bbls / 18 wells. 3. Rangau fdr #2 = 188 Bbls / 10 wells. ------------------------------------------------ + Grand total = 666 Bbls / 44 wells. | 12345 | 1 | 14:58 | Afternoon | Friday | 2018 | 4
8452 | 2018-04-27 15:03 | 2018-04-27 15:03 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 58 | 15:03 Manually Opened Recloser 36-CT-10 (d/s CKB fdr#1) to Replace Switch Board to VSD at Well KB #388. 15:17 Manually Block & Closed the Recloser, the released the Block After finished the Jobs. Cause: Planned Construction |  | 1 | 15:03 | Afternoon | Friday | 2018 | 4
8453 | 2018-04-27 15:08 | 2018-04-27 15:08 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 32 | Bangko OCB fdr#4 T/R 1x. Bangko fdr#2 Load dropped 247A (266-19A), EOR Bangko Fdr#3 Load dropped 212A (239-27A), WIP Not checked yet. |  | 1 | 15:08 | Afternoon | Friday | 2018 | 4
8454 | 2018-04-27 15:08 | 2018-01-05 08:08 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 32 | Checked and found Recloser 25-Z-07 T/R 2x Ctr: 190-192 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:08 | Afternoon | Friday | 2018 | 4
8455 | 2018-04-27 15:08 | 2018-04-27 15:08 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Unidentified | 80 | Bangko fdr #1 load dropped 87A (161-74A). Not checked yet. |  | 1 | 15:08 | Afternoon | Friday | 2018 | 4
8456 | 2018-04-27 15:08 | 2018-01-05 15:08 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Unidentified | 80 | Checked and found Recloser 23-X-08 T/R 1x Ctr: 403-404 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:08 | Afternoon | Friday | 2018 | 4
8457 | 2018-04-27 15:33 | 2018-04-27 15:33 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Unidentified | 151 | Nella OCB fdr#1 T/R 1x Not Checked yet. |  | 1 | 15:33 | Afternoon | Friday | 2018 | 4
8458 | 2018-04-27 15:33 | 2018-01-05 15:33 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Unidentified | 151 | Checked & found, Nella VCB fdr #1 did not operated. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:33 | Afternoon | Friday | 2018 | 4
8459 | 2018-04-28 05:49 | 2018-04-28 05:49 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 36 | Bekasap VCB fdr #6 T/R 1x. Not checked yet. |  | 1 | 5:49 | Morning | Saturday | 2018 | 4
8460 | 2018-04-28 05:49 | 2018-05-05 17:00 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 36 | Checked & found, Bekasap VCB fdr #6 T/R 1x ctr: 367-368 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 5:49 | Morning | Saturday | 2018 | 4
8461 | 2018-04-28 09:28 | 2018-04-28 09:28 | 13.8KV BEKASAP FEEDER #6 | Fair | Construction Job | 0 | 09:28 Manually Opened Recl. 38-BD-18 (d/s Bekasap fdr#6) to Open T type jumper toward Well BKS#140, #141, #157, due to Insert Pole for New Well. 09:49 Manually Block & Closed the Recloser then released the block. after finished the Jobs. Cause: Planned Construction. |  | 1 | 9:28 | Morning | Saturday | 2018 | 4
8462 | 2018-04-28 12:15 | 2018-04-28 12:15 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Construction Job | 0 | 12:15 Manually Opened Recl. 34-BI-18 (So Bekasap fdr#1) to Tie In New Well Ampuh#16. 12:45 Manually Block & Closed the Recloser, then Released the Block After finished the Jobs. Cause: Planned Construction |  | 1 | 12:15 | Afternoon | Saturday | 2018 | 4
8463 | 2018-04-28 13:03 | 2018-04-28 13:03 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 39 | 13:03 Manually Opened Recl.23-BW-02 (Libo Fdr#2) to Replaced Failure TX; 500 to 300 KVA 14:40 Manually Block & Closed the Recloser, then Released the block. after finished the Jobs Cause: Planned Maintenance |  | 1 | 13:03 | Afternoon | Saturday | 2018 | 4
8464 | 2018-04-28 16:11 | 2018-04-28 16:11 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 84 | Ketigul OCB fdr#2 T/R 1x Not checked yet. |  | 1 | 16:11 | Afternoon | Saturday | 2018 | 4
8465 | 2018-04-28 16:11 | 2018-04-05 16:11 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 84 | Checked & found, Ketigul VCB fdr #2 T/R 1x ctr: 273-274 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:11 | Afternoon | Saturday | 2018 | 4
8466 | 2018-04-28 16:22 | 2018-04-28 16:22 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 8 | Ketigul OCB fdr#3 T/R 1x. Not Checked yet. |  | 1 | 16:22 | Afternoon | Saturday | 2018 | 4
8467 | 2018-04-28 16:22 | 2018-03-05 16:22 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 8 | Checked & found, Ketigul VCB fdr #3 T/R 1x ctr: 200-201 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:22 | Afternoon | Saturday | 2018 | 4
8468 | 2018-04-29 06:08 | 2018-04-29 06:08 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | 06:08 CDR Fdr #4 T/R 1X R/F: 51N Ctr: 507-508. Cause: Not Patrolled yet. |  | 1 | 6:08 | Morning | Sunday | 2018 | 4
8469 | 2018-04-29 06:08 | 2018-06-05 06:08 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | Checked and found C. Duri 13.8KV ACB fdr #4 T/R 1X ctr:507-508 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:08 | Morning | Sunday | 2018 | 4
8470 | 2018-04-29 10:48 | 2018-04-29 10:48 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Planned Maintenance | 0 | 10:48 Manually Opened CKB VCB fdr#6 to Open Close fuse, due to Replace VSD at Well KB #424, #407, #303. 11:14 Manually Block Closed CKB VCB fdr#6, then released the block After finished the Jobs Cause: Planned Maintenance. |  | 1 | 10:48 | Morning | Sunday | 2018 | 4
8471 | 2018-04-29 15:10 | 2018-04-29 15:10 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 73 | It was reported B/O fuse O/P 08-M1-20 (d/s CDuri fdr#2) Not checked yet |  | 1 | 15:10 | Afternoon | Sunday | 2018 | 4
8472 | 2018-04-29 15:10 | 2018-06-05 15:10 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Unidentified (Fuse) | 73 | Chekced and found @2 b/o fuse for 112.5KVA TX o/p 08-M1-20. Replaced the b/o fuse above wit same size, then energized the TX. Cause: Unidentified (fuse). |  | 1 | 15:10 | Afternoon | Sunday | 2018 | 4
8473 | 2018-04-29 15:28 | 2018-04-29 15:28 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 31 | 15:28 Manually open LBS 34 CT 58 (d/s CKBS fdr#5) to Replace 260 KvaTx with the same size, due to failure at well KB#180. 16:15 Manually Closed the LBS after finished jobs. Cause : Plain maintenance |  | 1 | 15:28 | Afternoon | Sunday | 2018 | 4
8474 | 2018-04-29 17:52 | 2018-04-29 17:52 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 7 | C.Duri fdr#1 load dropped 64A (109-55A) Not checked yet |  | 1 | 17:52 | Afternoon | Sunday | 2018 | 4
8475 | 2018-04-29 17:52 | 2018-06-05 17:52 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 7 | Checked and found Recl.: 39-AV-36 T/R 1X ctr:149-150 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:52 | Afternoon | Sunday | 2018 | 4
8476 | 2018-04-30 00:01 | 2018-04-30 00:01 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 140 | So Balam VCB fdr #4 T/R 1x. So Balam fdr #1 load dropped 77A (137-60A). So Balam fdr #2 Load dropped 130 A (130-0A). So Balam fdr #3 Load dropped 67 A (67-0A). So Balam GFPC T/R 1x. Not checked yet. |  | 1 | 0:01 | Night | Monday | 2018 | 4
8477 | 2018-04-30 00:01 | 2018-02-05 17:00 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 140 | Checked & found, S. Balam VCB fdr #4 T/R 1x ctr: 354-355 R/F: 51 @1, @2, @3. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 0:01 | Night | Monday | 2018 | 4
8478 | 2018-04-30 00:10 | 2018-04-30 00:10 | 13.8KV NELLA FEEDER #2 | Lightning | Pin Insulator | 157 | Nella VCB fdr #2 T/R 1x. Nella fdr #1 load dropped 136A (223-87A). Nella GFPC T/R 1x. Not checked yet. |  | 1 | 0:10 | Night | Monday | 2018 | 4
8479 | 2018-04-30 00:10 | 2018-02-05 00:10 | 13.8KV NELLA FEEDER #2 | Lightning | Pin Insulator | 157 | Checked and found 13.8KV Nella fdr #2 T/R 2x Ctr: 309-311 R/F: 51N @1, @2, @3. Patrolled the line and found Broken Pin Insulator o/p 21-V-07. Cause: Pin Insulator. |  | 1 | 0:10 | Night | Monday | 2018 | 4
8480 | 2018-04-30 00:30 | 2018-04-30 00:30 | 13.8KV BANGKO FEEDER #4 | Lightning | Lightning | 30 | Bangko fdr #4 load dropped 62A (161-99A). Not checked yet. |  | 1 | 0:30 | Night | Monday | 2018 | 4
8481 | 2018-04-30 00:30 | 2018-01-05 00:30 | 13.8KV BANGKO FEEDER #4 | Lightning | Lightning | 30 | Checked and found Recloser 25-Z-07 T/R 1x Ctr: 192-193 R/F: 51GN @2. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 0:30 | Night | Monday | 2018 | 4
8482 | 2018-04-30 13:37 | 2018-04-30 13:37 | MINAS POWER PLANT |  |  | - | 13:37 S/U MGT#10, then on line the unit at 15:20. |  | 1 | 13:37 | Afternoon | Monday | 2018 | 4
8483 | 2018-04-30 14:19 | 2018-04-30 14:19 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified | 84 | CKBS FDR#1 T/R 1X. Not checked yet |  | 1 | 14:19 | Afternoon | Monday | 2018 | 4
8484 | 2018-04-30 14:19 | 2018-03-05 14:19 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified | 84 | Checked & found, CKB VCB fdr #1 T/R 2x ctr: 224-226 R/F: None. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:19 | Afternoon | Monday | 2018 | 4
8485 | 2018-04-30 14:57 | 2018-04-30 14:57 | 13.8KV 8D FEEDER #5 | Cloudy | Unidentified | 29 | 8D fdr#5 T/R 1X. Not checked yet |  | 1 | 14:57 | Afternoon | Monday | 2018 | 4
8486 | 2018-04-30 14:57 | 2018-11-05 14:57 | 13.8KV 8D FEEDER #5 | Cloudy | Unidentified | 29 | Checked & found, 8C OCB fdr #5 T/R 1x ctr: 566-566 R/F: None. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:57 | Afternoon | Monday | 2018 | 4
8487 | 2018-04-30 14:57 | 2018-04-30 14:57 | 13.8KV 8D FEEDER #3 | Cloudy | Unidentified | 0 | 8D fdr#3 load dropped 98A (100-2A) Not checked yet |  | 1 | 14:57 | Afternoon | Monday | 2018 | 4
8488 | 2018-04-30 14:57 | 2018-11-05 14:57 | 13.8KV 8D FEEDER #3 | Cloudy | Unidentified | 0 | Checked & found, Recloser 8D-30 T/R 1x ctr: 16-17 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:57 | Afternoon | Monday | 2018 | 4
8489 | 2018-04-30 15:39 | 2018-04-30 15:39 | MINAS POWER PLANT |  |  | - | Off line MGT#11, then S/D the unit for Maintenance. |  | 1 | 15:39 | Afternoon | Monday | 2018 | 4
8490 | 2018-01-05 06:47 | 2018-01-05 06:47 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 31 | C Duri fdr #1 load dropped 44A (110-66A). Not checked yet. |  | 1 | 6:47 | Morning | Friday | 2018 | 1
8491 | 2018-01-05 06:47 | 2018-06-05 06:47 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 31 | Checked and found Recl.: 39-AV-36 T/R 1X ctr: 250-251 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified |  | 1 | 6:47 | Morning | Friday | 2018 | 1
8492 | 2018-01-05 07:27 | 2018-01-05 07:27 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 86 | OKB 13.8KV OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 7:27 | Morning | Friday | 2018 | 1
8493 | 2018-01-05 07:27 | 2018-03-05 07:27 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 86 | Checked and found OKB 13.8KV OCB fdr #2 T/R 1X ctr: 1316-1317 R/F: 51N. Patrolled the line but found nothing. Cause: unidentified . |  | 1 | 7:27 | Morning | Friday | 2018 | 1
8494 | 2018-01-05 12:58 | 2018-01-05 12:58 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | N.Duri VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 12:58 | Afternoon | Friday | 2018 | 1
8495 | 2018-01-05 12:58 | 2018-07-05 12:58 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked and found N.Duri VCB fdr#1 T/R 1x ctr: 287-287 (not changed) R/F: 51@3 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 12:58 | Afternoon | Friday | 2018 | 1
8496 | 2018-01-05 13:10 | 2018-01-05 13:10 | 13.8KV NORTH DURI FEEDER #7 | Rain and Lightning | Unidentified | 0 | N.Duri VCB fdr#7 T/R 1x. Not checked yet. |  | 1 | 13:10 | Afternoon | Friday | 2018 | 1
8497 | 2018-01-05 13:10 | 2018-07-05 13:10 | 13.8KV NORTH DURI FEEDER #7 | Rain and Lightning | Unidentified | 0 | Cehecked and found N.Duri VCB fdr #7 T/R 1X ctr:102-103, r/f:51@1 Patrolled the line but found nothing. Cause:Unidentified. |  | 1 | 13:10 | Afternoon | Friday | 2018 | 1
8498 | 2018-01-05 13:11 | 2018-01-05 13:11 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Unidentified | 0 | N.Duri VCB fdr#8 T/R 1x. Not checked yet. |  | 1 | 13:11 | Afternoon | Friday | 2018 | 1
8499 | 2018-01-05 13:11 | 2018-07-05 13:11 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Unidentified | 0 | Checked and found N.Duri VCB #8 T/R 1X ctr:87-88, R/F:51@1. Patrolled the line but found nothing. Cause:Unidentified. |  | 1 | 13:11 | Afternoon | Friday | 2018 | 1
8500 | 2018-01-05 13:45 | 2018-01-05 13:45 | 13.8KV PUNGUT FEEDER #2 | Fair | Planned Maintenance | 10 | 13:45 Manually Opened Recl. 45-BR-01 (d/s Pungut fdr#2) to Replace Failure 750KVATX with the same size at Tandun GS 14:36 Manually Block & Closed the Recloser, then released the Block After finished the Jobs Cause: Planned maintenance |  | 1 | 13:45 | Afternoon | Friday | 2018 | 1
8501 | 2018-01-05 13:48 | 2018-01-05 13:48 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Lightning | 0 | Duri Commy fdr#3 T/R 1X. Not checked yet |  | 1 | 13:48 | Afternoon | Friday | 2018 | 1
8502 | 2018-01-05 13:48 | 2018-03-05 13:48 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found, Duri Community ACB #26 fdr #3 T/R 1x ctr: 200-201 R/F: 51. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 13:48 | Afternoon | Friday | 2018 | 1
8503 | 2018-01-05 14:09 | 2018-01-05 14:09 | 13.8KV NORTH DURI FEEDER #6 | Fair | Recloser - Control Recloser | 99 | 14:09 N.Duri fdr#6 load dropped 10A (27-17A) It was reported No power At Road G2 d/s Recl 12-G2-02. 16:10 Checked & found Recl 12-G2-02 Controller Failure (d/s ND fdr#6) Opened Visual Opening to Isolate the Recloser Closed LBS 12-F9-40 (Road G2 of ND fdr#6 transfer to ND fdr#11) Cause : Control Recloser Failure |  | 1 | 14:09 | Afternoon | Friday | 2018 | 1
8504 | 2018-01-05 15:00 | 2018-01-05 15:00 | 13.8KV 3D FEEDER #4 | Drizzle | Tree | 483 | 15:00 It was reported No power at well Area 1D & 1E. (d/s 3D fdr#4) 17:00 Checked & found - Recl 2D14 T/O, Ctr: ......... R/F: ......... - Recl 2D33 in Bypass status Patrolled the Line, found Fall down Tree o/p 1D06 d/s Recl 2D33 18:05 Stay Open Recl 2-14, no power for Area 1D, the Tree Could not Dismantled due to Rain Manually Block & Closed Recl 2D14 for Area 1E, the released the block Cause: Tree |  | 1 | 15:00 | Afternoon | Friday | 2018 | 1
8505 | 2018-01-05 15:00 | 2018-02-05 15:00 | 13.8KV 3D FEEDER #4 | Drizzle | Tree | 483 | 09:00 Started to remove tree on power line under Recl. # 2D-14. 17:20 Blocked and closed Recl. # 2D-14, OK then released the block. Cause: Tree. |  | 1 | 15:00 | Afternoon | Friday | 2018 | 1
8506 | 2018-01-05 17:18 | 2018-01-05 17:18 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse o/p 08-N4_08 D/S C.Duri fdr #1. Not checked yet. |  | 1 | 17:18 | Afternoon | Friday | 2018 | 1
8507 | 2018-01-05 17:18 | 2018-02-05 12:48 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 12:48 Checked and found @2, b/o fuse for 112.5 KVA TX o/p 08-N4-08 d/s C.Duri fdr #1. Replaced b/o fuse above with the same size and energize the TX. Cause :Unidentified (fuse). |  | 1 | 17:18 | Afternoon | Friday | 2018 | 1
8508 | 2018-02-05 08:49 | 2018-02-05 08:49 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 86 | 08:49 Ketigul 13.8KV VCB fdr #2 T/R 1X. Ketigul fdr #1 dropped 25 (113-88A). Not checked yet. |  | 1 | 8:49 | Morning | Monday | 2018 | 2
8509 | 2018-02-05 08:49 | 2018-03-05 17:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 86 | Checked & found, Ketigul VCB fdr #2 T/R 2x ctr: 273-275 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 8:49 | Morning | Monday | 2018 | 2
8510 | 2018-02-05 11:21 | 2018-02-05 11:21 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 13 | 11:21 Manually Opened Recl. 38-CW-08 (d/s OKB fdr#2) -----> Closed at 11:40. Replace 250KVA TX - 300KVA TX , R/M 40HP at well Kotabatak #133. Cause: Planned maintenance. |  | 1 | 11:21 | Morning | Monday | 2018 | 2
8511 | 2018-02-05 12:38 | 2018-02-05 12:38 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | 12:38 C.Duri 13.8KV ACB fdr #4 T/R 1X. Not checked yet. |  | 1 | 12:38 | Afternoon | Monday | 2018 | 2
8512 | 2018-02-05 12:38 | 2018-06-05 12:38 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | Checked and found C. Duri 13.8KV ACB fdr #4 T/R 1X ctr: 163-164 R/F: 51@2. Patrooled the line but found nothing. Cause: Unidentified |  | 1 | 12:38 | Afternoon | Monday | 2018 | 2
8513 | 2018-02-05 13:00 | 2018-02-05 13:00 | 13.8KV DURI FIELD FEEDER #1 | Fair | Animal | 0 | 13:00 It was reported b/o fuse for TX at CGS #3 d/s D.Field fdr #1 . 14:00 Checked and found @1,@2,@3 b/o fuse TTR Test Megger the TX. Ok. 15:20 Opened LBS 01-05-32 and closed fuse for the TX. 15:23 Closed LBS 01-05-32. Cause:Animal (snake). |  | 1 | 13:00 | Afternoon | Monday | 2018 | 2
8514 | 2018-02-05 14:45 | 2018-02-05 14:45 | MINAS POWER PLANT | Fair | Under investigation | 0 | 14:45 MGT#10 Trip Generator breaker due to computer S Automatic reboot 14:55 MGT#10 on line the unit. |  | 1 | 14:45 | Afternoon | Monday | 2018 | 2
8515 | 2018-02-05 15:01 | 2018-02-05 15:01 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 0 | 15:01 Manually Opened LBS 34-CT-58 (d/s CKB fdr#5) -----> Closed at 16:01. Replace 300KVA TX , R/M 40HP at well Kotabatak #267 (reactive well). Cause: Planned maintenance. |  | 1 | 15:01 | Afternoon | Monday | 2018 | 2
8516 | 2018-02-05 18:28 | 2018-02-05 18:28 | PEMATANG MAIN SUBSTATION | Fair | Theft | 615 | Founding Problem : Lost of OIL at 44KV Pematang Main OCB#1 and Rangau Substation LTCTX 18:28 Manually opened 44KV Pematang Main OCB#2 open isolation switch----->Closed 20:16 19:30 Manually Opened Rangau fdr#1-------->Closed at 20:17. 19:30 Manually Opened Rangau fdr#2-------->Closed at 20:18. 19:32 Manually opened 115KV C/S Pematang Main------->Closed at 22:10. Manually opened isolation switch 44KV Pematang Main OCB#1----->Closed at 20:40. Manually opened 44KV Pematang Main OCB#1 to Petani SS---->Closed at 20:42. Manually opened Petani fdr#1------>Closed at 20:43. Manually opened Petani fdr#2------>Closed at 20:51. 19:32 Pematang substation no power due to 115KV C/S Pematang Main havikun opened Manually opened 44KV OCB#3 Pematang Main to Pematang Main SS----->Closed at 20:13. Manually opened Pematang fdr#1------>Closed at 20:13. Manually opened Pematang fdr#2------>Closed at 20:15. 20:30 Manually opened Rokan fdr#2------>Closed at 21:00 ( Petani GS level tank). Cause : Theft (Add oil at 44KV Pematang Main OCB#1 and Rangau LTCTX. Pematang fdr#1------> 99 BBLs/17 wells. Pematang fdr#2------> 85 BBLS/20 wells. -----------------------+ 184 BBLS/ 37 Wells. Rangau fdr#1---------> 16 BBLS/ 3 Wells. Rangau fdr#2---------> 141 BBLS/ 8 Wells. ------------------------+ 157 BBLS/ 11Wells Petani fdr#1----------> 234 BBLS/ 35 Wells. Petani fdr#2----------> 91 BBLS/ 25 Wells. -------------------------+ 325 BBLS/ 60Wells Grand Total ----------> 666 Bbls, 108 Wells | 1234 | 1 | 18:28 | Afternoon | Monday | 2018 | 2
8517 | 2018-03-05 08:35 | 2018-03-05 08:35 | MINAS POWER PLANT |  |  | - | MGT #6 Off line and then S/D the unit for S/B. |  | 1 | 8:35 | Morning | Monday | 2018 | 3
8518 | 2018-03-05 09:41 | 2018-03-05 09:41 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 0 | 09:41 Manually Open Recl.: 37-BD-40, Relocated Power line at well Bekasap # 176. Contruction. |  | 1 | 9:41 | Morning | Monday | 2018 | 3
8519 | 2018-03-05 09:41 | 2018-04-05 09:41 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 0 | 11:24 Closed Recl.: 37-BD-40. After Installed and energized 300KVA TX at well Bekasap #185 (New well ). Cause: Construction. |  | 1 | 9:41 | Morning | Monday | 2018 | 3
8520 | 2018-03-05 10:46 | 2018-03-05 10:46 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 31 | 10:46 Manually Open Recl. : 39-AV-36, ------>Closed at 10:51. By Pass Recl. : 38-AS-09 for trouble shoot. Cause: Plan Maintenance. |  | 1 | 10:46 | Morning | Monday | 2018 | 3
8521 | 2018-03-05 13:56 | 2018-03-05 13:56 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 62 | Bangko 13.8KV OCB fdr #4 T/R 1X. Bangko fdr #1 load dropped 100A (169-69A). Bangko fdr #2 load dropped 239A (260-21A) --->EOR. Bangko fdr #3 load dropped 190A (228-38A) --->EOR. Not checked yet. |  | 1 | 13:56 | Afternoon | Monday | 2018 | 3
8522 | 2018-03-05 13:56 | 2018-04-05 13:56 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 62 | Checked & found, Bangko OCB fdr #4 T/R 1x ctr: 40-41 R/F: 50N. Patrolled the line & found, @3 broken Pin Insulator on Pole 29 AA 9. Cause: Lightning. |  | 1 | 13:56 | Afternoon | Monday | 2018 | 3
8523 | 2018-03-05 14:14 | 2018-03-05 14:14 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified (Fuse) | 10 | 14:14 It was reportred b/o fuse at well SO. Balam #21. Checked and found @3 b/o fuse for 50KVA TX. TTR test and Megger the TX, OK. Replaced the b/o fuse above with same size, then energized the TX. OK. Cause: Un identified (fuse). |  | 1 | 14:14 | Afternoon | Monday | 2018 | 3
8524 | 2018-03-05 14:46 | 2018-03-05 14:46 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Unidentified | 0 | Sintong fdr #2 load dropped 160A (226-60A). Groun fault alarm from Sintong fdr #2, Not checked yet. |  | 1 | 14:46 | Afternoon | Monday | 2018 | 3
8525 | 2018-03-05 15:52 | 2018-03-05 15:52 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Secondary Cable | 0 | 15:52 It was reported broken secondary cable TX at SMP Cendana d/s Duri Comy. fdr #3. Checked and found @1 broken secondary cable for 150KVA TX. Repair the broken secondary cable above and then energize the TX. Cause:secondary cable (broken ). |  | 1 | 15:52 | Afternoon | Monday | 2018 | 3
8526 | 2018-04-05 09:44 | 2018-04-05 09:44 | 13.8KV MENGGALA FEEDER #1 | Fair | Construction Job | 0 | 09:44 Manually Open Recl. : 19-AN-04, ----->Closed at 09:53. Closed HLC for 1000 KVA TX at MENO GS. (CCTV). Cause: Construction JOB. |  | 1 | 9:44 | Morning | Thursday | 2018 | 4
8527 | 2018-04-05 11:31 | 2018-04-05 11:31 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 24 | 4B 13.8KV VCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 11:31 | Morning | Thursday | 2018 | 4
8528 | 2018-04-05 11:31 | 2018-11-05 11:31 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 24 | Checked & found, 4B OCB fdr #1 T/R 2x ctr: 330-332 R/F: 50N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 11:31 | Morning | Thursday | 2018 | 4
8529 | 2018-04-05 11:47 | 2018-04-05 11:47 | 13.8KV CENTRAL DURI FEEDER #1 | Rain | Unidentified | 0 | C. Duri fdr #1 load droped 57A (110-53A). Not checked yet. |  | 1 | 11:47 | Morning | Thursday | 2018 | 4
8530 | 2018-04-05 11:47 | 2018-06-05 19:47 | 13.8KV CENTRAL DURI FEEDER #1 | Rain | Unidentified | 0 | Checked & found Recl. 39AV36 T/R 1x Ctr:251-252 R/F:51@1. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 11:47 | Morning | Thursday | 2018 | 4
8531 | 2018-04-05 16:52 | 2018-04-05 16:52 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Planned Maintenance | 57 | 16:52 O/C Petapahan 13.8 KV VCB fdr #6,----->Closed at 17:25. Replaced 350 KVA TX at well Petapahan #32. Cause:Planned maintenance. |  | 1 | 16:52 | Afternoon | Thursday | 2018 | 4
8532 | 2018-05-05 07:42 | 2018-05-05 07:42 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 66 | 07:42 Bangko 13.8KV OCB fdr #4 T/R 1 Bangko fdr #1 load dropped 42A (169-127A). Bangko fdr #2 load dropped 31A (254-214A). Not checked yet. |  | 1 | 7:42 | Morning | Saturday | 2018 | 5
8533 | 2018-05-05 07:42 | 2018-06-05 07:42 | 13.8KV BANGKO FEEDER #4 | Fair | Pin Insulator | 66 | Checked & found, Bangko OCB fdr #4 T/R 1x ctr: 41-42 R/F: 51 @1. Patrolled the line & found, @1 broken Pin Insulator on Pole 24 Z 09. Cause: Pin Insulator. |  | 1 | 7:42 | Morning | Saturday | 2018 | 5
8534 | 2018-05-05 10:12 | 2018-05-05 10:12 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 93 | 10:12 Ketigul 13.8KV VCB fdr #2 T/SO. 10:40 Checked and found Ketigul fdr #2 T/SO ctr:175-276 R/F: 51 @1, @2. 11:10 Blocked and closed Ketigul fdr #2, OK then released the block. Not patrolled yet. |  | 1 | 10:12 | Morning | Saturday | 2018 | 5
8535 | 2018-05-05 10:12 | 2018-11-05 10:12 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 93 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:12 | Morning | Saturday | 2018 | 5
8536 | 2018-06-05 07:21 | 2018-06-05 07:21 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 0 | Minas 13.8KV ACB fdr #1 T/R 1X ctr: 77-78 R/F: 51N. Not patrolled yet. |  | 1 | 7:21 | Morning | Tuesday | 2018 | 6
8537 | 2018-06-05 07:21 | 2018-11-05 07:21 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:21 | Morning | Tuesday | 2018 | 6
8538 | 2018-06-05 09:39 | 2018-06-05 09:39 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 135 | 09:39 Manually Open LBS: 28-AL-05, ----->Closed at 10:44. Repaired Hot Spot o/p: 27-AL-21. Cause: Plan Maintenance. |  | 1 | 9:39 | Morning | Tuesday | 2018 | 6
8539 | 2018-06-05 10:48 | 2018-06-05 10:48 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Planned Maintenance | 267 | 10:48 Manually Open Petapahan 13.8KV VCB fdr #3, ----->Closed at 11:48. Replaced 260KVA TX at well Pe6tapahan #92. Also replaced 400KVA TX at well Pe6tapahan #113. Cause: Plan Maintenance. |  | 1 | 10:48 | Morning | Tuesday | 2018 | 6
8540 | 2018-06-05 15:42 | 2018-06-05 15:42 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 29 | C.Duri 13.8KV ACB fdr #1 T/R 1X ctr: 22-23 R/F: 51G/51N Time. Not checked yet. |  | 1 | 15:42 | Afternoon | Tuesday | 2018 | 6
8541 | 2018-06-05 15:42 | 2018-07-05 15:42 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 29 | Checked and found C.Duri 13.8 KV fdr #1 T/R 1X, ctr:22-23, R/F:51@1. Patrolled the line but found nothing. Cause:Unidentified. |  | 1 | 15:42 | Afternoon | Tuesday | 2018 | 6
8542 | 2018-06-05 17:23 | 2018-06-05 17:23 | 13.8KV NELLA FEEDER #1 | Heavy Rain | Lightning Arrester | 133 | Nella fdr #1 load dropped 187A (217-30A). Nella fdr #2 load dropped 22A (65-43A). Groun fault alarm from Nella fdr #2, Not checked yet. |  | 1 | 17:23 | Afternoon | Tuesday | 2018 | 6
8543 | 2018-06-05 17:23 | 2018-08-05 17:23 | 13.8KV NELLA FEEDER #1 | Heavy Rain | Lightning Arrester | 133 | Checked & found, Recloser 22V01 T/R 2x ctr: 114-116 R/F: 51N. Patrolled the line & found, @3 broken Lightning Arrester on Terminal Pole at Well BKO #193. Cause: Lightning Arrester. |  | 1 | 17:23 | Afternoon | Tuesday | 2018 | 6
8544 | 2018-07-05 11:24 | 2018-07-05 11:24 | MINAS POWER PLANT |  |  | - | 11:24 S/U MGT #5 and online the system at 11:35. |  | 1 | 11:24 | Morning | Thursday | 2018 | 7
8545 | 2018-07-05 14:51 | 2018-07-05 14:51 | 13.8KV BATANG FEEDER #2 | Fair | Planned Maintenance | 33 | 14:51 Manually Open Batang 13.8 KV OCB FDR#2 ----->Closed at 18:05. Replaced the TX 112.5 KVA at well Batang PSO. Replaced the TX 300 KVA at Rantau Bais #41. Cause:Planned maintenance. |  | 1 | 14:51 | Afternoon | Thursday | 2018 | 7
8546 | 2018-08-05 10:14 | 2018-08-05 10:14 | 13.8KV BEKASAP FEEDER #3 | Fair | Construction Job | 0 | 10:14 Manually Open Recl.: 38-BD-18, -----> Closed at 10:52. Closed Tie Tap at well Bekasap #140, #141 and #157 (Reactive well) Cause: Project. |  | 1 | 10:14 | Morning | Sunday | 2018 | 8
8547 | 2018-08-05 10:29 | 2018-08-05 10:29 | 13.8KV NEW KOTABATAK FEEDER #4 | Fair | Construction Job | 0 | 10:29 Manually Open New Petepahan fdr #4, ---->Closed at 11:16. Closed HLC at well #43 (Reactive well). Cause: Project. |  | 1 | 10:29 | Morning | Sunday | 2018 | 8
8548 | 2018-08-05 13:24 | 2018-08-05 13:24 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 127 | 13:24 Manually Open Pematang 13.8KV OCB fdr #2, ----->Closed at 14:15. Replaced 150KVA Tx at well Pematang # 23 (TX failure). Replaced Dead End Insulator o/p........ Cause: Plan Maintenance. |  | 1 | 13:24 | Afternoon | Sunday | 2018 | 8
8549 | 2018-08-05 15:03 | 2018-08-05 15:03 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 43 | 15:03 Manually Open Recl. 38-cw-08 d/s Kotabatak fdr #2, ----->Closed at 15:40. Replaced switch board to PSD at Kotabatak #356. Cause:Planned maintenance. |  | 1 | 15:03 | Afternoon | Sunday | 2018 | 8
8550 | 2018-08-05 16:48 | 2018-08-05 16:48 | MINAS POWER PLANT | Fair | Equipment Failure | 0 | 16:48 MGT #10 Trip by alarm Computer R problem. Frequency dropped to 59.89 hz. Cause: Equipment Failure. |  | 1 | 16:48 | Afternoon | Sunday | 2018 | 8
8551 | 2018-08-05 17:00 | 2018-08-05 17:00 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse O/P 04-04-11 d/s C.Duri fdr#8 Not checked yet. |  | 1 | 17:00 | Afternoon | Sunday | 2018 | 8
8552 | 2018-08-05 17:00 | 2018-10-05 09:50 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 0 | Checked and found @2 b/o fuse on pole 04-04-11 D/S C Duri fdr #8. Replaced @2 b/o fuse above and then energized the Tx. Cause: Unidentified (fuse). |  | 1 | 17:00 | Afternoon | Sunday | 2018 | 8
8553 | 2018-08-05 17:20 | 2018-08-05 17:20 | MINAS POWER PLANT |  |  | - | 17:20 MGT GT #11 was S/U and On Line to the system at 17:40 to restore the load. (After MGT GT #10 T/O by alarm Lig. Level High trip). |  | 1 | 17:20 | Afternoon | Sunday | 2018 | 8
8554 | 2018-09-05 06:47 | 2018-09-05 06:47 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 43 | 06:47 Ketigul fdr#1 T/R 1X Ketigul fdr#2 Load dropped 59A (206-147A) 17:00 Checked & found, Ketiguyl VCB fdr #1 T/R 1x ctr: 200-201 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:47 | Morning | Wednesday | 2018 | 9
8555 | 2018-09-05 17:05 | 2018-09-05 17:05 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | C Duri ACB #23 (feeder #6) T/R 1x Counter: 483-484 R/F: 51@2 , @3. Not patrolled yet. |  | 1 | 17:05 | Afternoon | Wednesday | 2018 | 9
8556 | 2018-09-05 17:05 | 13/05/2018 17:05 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:05 | Afternoon | Wednesday | 2018 | 9
8557 | 2018-09-05 17:56 | 2018-09-05 17:56 | 13.8KV NELLA FEEDER #2 | Cloudy | Lightning Arrester | 37 | Nella VCB fdr #2 T/R 1x. Nella GFPC T/R 1x. Not checked yet. |  | 1 | 17:56 | Afternoon | Wednesday | 2018 | 9
8558 | 2018-09-05 17:56 | 2018-11-05 17:56 | 13.8KV NELLA FEEDER #2 | Cloudy | Lightning Arrester | 37 | Checked & found, Nella VCB fdr #2 T/R 1x ctr: 311-312 R/F: 51N. Patrolled the line & found, @3 broken Lightning Arrester on Pole 20 V 12. Cause: Lightning Arrester. |  | 1 | 17:56 | Afternoon | Wednesday | 2018 | 9
8559 | 2018-10-05 04:28 | 2018-10-05 04:28 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | C.Duri 13.8 Kv fdr#7 load dropped 56A (149-93A). Not checked yet. |  | 1 | 4:28 | Morning | Friday | 2018 | 10
8560 | 2018-10-05 04:28 | 13/05/2018 17:28 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | Checked & found, Recloser 03-03-42 T/R 1x ctr: 163-164 R/F:51 @1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 4:28 | Morning | Friday | 2018 | 10
8561 | 2018-10-05 09:30 | 2018-10-05 09:30 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 30 | 09:30 Manually Open Recl.: 9D-25, ----->Closed at 10:05. Replaced 550KVA TX to 300KVA TX at well 9D-57. (Due to changed over 450HP to 50HP Reda Motor). Plan Maintenance. |  | 1 | 9:30 | Morning | Friday | 2018 | 10
8562 | 2018-10-05 15:30 | 2018-10-05 15:30 | 13.8KV NELLA FEEDER #1 | Fair | Construction Job | 0 | 15:30 Manually Open Recl.:22-V-01, ---->Closed at 16:21. Installed New TX at well Bangko #328 (New Well). Construction JOB. |  | 1 | 15:30 | Afternoon | Friday | 2018 | 10
8563 | 2018-11-05 14:00 | 2018-11-05 14:00 | MINAS POWER PLANT |  |  | - | 14:00 S/U MGT #10 and then Online the unit at.14:30. |  | 1 | 14:00 | Afternoon | Monday | 2018 | 11
8564 | 2018-11-05 14:32 | 2018-11-05 14:32 | NORTH DURI POWER PLANT | Fair | Others | 217 | 14:32 NDC #1 Trip, Freq.59.73 Hz (Load Seedding Level 2). 4D Fdr #4 Close at : 15:25. 4D Fdr #5 Close at : 15:26. 3D Fdr #6 Close at : 14:46 5B Fdr #5 Close at : ~"~ 5B Fdr #7 Close at : ~"~ 4B Fdr #4 Close at : ~"~ 8D Fdr #3 Close at : 15:22. 5B Fdr #4 Close at : ~"~ 8D Fdr #1 Close at : 15:20. Cause : NDC #1 Trip by Alarm Vibration high. Prod loss: GS#1---->19Wells / 118 BBLS GS#2---->17Wells / 36 BBLS GS#4---->18Wells / 25 BBLS GS#5---->12Wells / 22 BBLS GS#6---->16Wells / 23 BBLS -------------------------+ 82Wells / 224BBLS |  | 1 | 14:32 | Afternoon | Monday | 2018 | 11
8565 | 2018-11-05 14:32 | 2018-11-05 14:32 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 25 | 14:32 4B VCB Fdr #1 T/R 2x ctr: 330-332 R/F: 50N. 17:00 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:32 | Afternoon | Monday | 2018 | 11
8566 | 2018-11-05 15:02 | 2018-11-05 15:02 | MINAS POWER PLANT | Fair |  | - | 15:02 S/U MGT #6 and then Online the unit at.15:40 to restore power due to : NDC #1 Trip. |  | 1 | 15:02 | Afternoon | Monday | 2018 | 11
8567 | 2018-11-05 15:40 | 2018-11-05 15:40 | NORTH DURI POWER PLANT | Fair |  | - | 15:40 S/U NDC #1 and then On Line the unit at.16:16. |  | 1 | 15:40 | Afternoon | Monday | 2018 | 11
8568 | 2018-12-05 10:23 | 2018-12-05 10:23 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | 10:23 Manually opened recloser 16-AA-08 d/s So. Balam Fdr #4 due to : Opening HLC o/p 16-AA-111 Wells were off So Balam #49 and 326. 11:20 Manually blocked and closed recloser : 16-AA-08 and then released the block. Cause : Construction job. |  | 1 | 10:23 | Morning | Wednesday | 2018 | 12
8569 | 2018-12-05 10:24 | 2018-12-05 10:24 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Fair | Planned Maintenance | 0 | 10:24 Manually opened 4160V VCB #22 (Fdr #4) Housing Dumai due to : Closed By Pass Recloser H-33-07 and replaced control recloser. 10:27 Manually blocked and closed 4160V VCB #22 (Fdr #4) Housing Dumai and then released the block. Cause : Plan Maintenance. |  | 1 | 10:24 | Morning | Wednesday | 2018 | 12
8570 | 2018-12-05 11:09 | 2018-12-05 11:09 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Fair | Planned Maintenance | 0 | 11:09 Manually opened 4160V VCB #22 (Fdr #4) Housing Dumai due to : Cut high trees 11:36 Manually blocked and closed 4160V VCB #22 (Fdr #4) Housing Dumai and then released the block. Cause : Plan Maintenance. |  | 1 | 11:09 | Morning | Wednesday | 2018 | 12
8571 | 2018-12-05 14:23 | 2018-12-05 14:23 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 153 | 14:23 Bekasap OCB Fdr #2 T/R 1X. Bekasap GFPC T/R 1X. Cause : Not checked yet. |  | 1 | 14:23 | Afternoon | Wednesday | 2018 | 12
8572 | 2018-12-05 14:23 | 14/05/2018 17:00 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 153 | Checked & found, Bekasap Main OCB fdr #2 T/R 1x ctr: 891-892 R/F: 51. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 14:23 | Afternoon | Wednesday | 2018 | 12
8573 | 2018-12-05 14:23 | 2018-12-05 14:23 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 0 | Bekasap Fdr #6 Load drop 75A (165-90A). Not checked yet. |  | 1 | 14:23 | Afternoon | Wednesday | 2018 | 12
8574 | 2018-12-05 14:23 | 14/05/2018 17:00 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked & found, Recloser 1-TL-06 T/R 1x ctr: 64-65 R/F: 51N Patrolled the line & found, @2 broken Lightning Arrester on Pole for Bekasap Tool House. Cause: Lightning. |  | 1 | 14:23 | Afternoon | Wednesday | 2018 | 12
8575 | 2018-12-05 14:42 | 2018-12-05 14:42 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 42 | 44 Kv OVB #2 (Pematang Main - Rangau Line) T/R 1x. Not checked yet. |  | 1 | 14:42 | Afternoon | Wednesday | 2018 | 12
8576 | 2018-12-05 14:42 | 14/05/2018 17:00 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 42 | Checked & found, 44KV Pematang OCB fdr #2 T/R 1x ctr: 48883-48884 R/F:50@3. Patrolled the line & found, @3 Broken Suspension Insulator on Pole RGU-56. Cause: Lightning. |  | 1 | 14:42 | Afternoon | Wednesday | 2018 | 12
8577 | 2018-12-05 16:00 | 2018-12-05 16:00 | 13.8KV SINTONG FEEDER #2 | Rain | Transformer Failure | 0 | It was reported b/o fuse at Mutiara SBF d/s Sintong Fdr #2. Not checked yet. |  | 1 | 16:00 | Afternoon | Wednesday | 2018 | 12
8578 | 2018-12-05 16:00 | 13/05/2018 16:00 | 13.8KV SINTONG FEEDER #2 | Rain | Transformer Failure | 0 | Checked & found, @1 b/o Fuse for 50KVA Tx at Mutiara SBF. Performed TTR & Megger Test, found Transformer Failure. Cause: Transformer Failure. (Will be replaced soon). |  | 1 | 16:00 | Afternoon | Wednesday | 2018 | 12
8579 | 2018-12-05 16:00 | 14/05/2018 11:00 | 13.8KV SINTONG FEEDER #2 | Rain | Transformer Failure | 0 | Replaced The Failure Transformer with the same size then energized the Tx. Cause: Transformer Failure. |  | 1 | 16:00 | Afternoon | Wednesday | 2018 | 12
8580 | 2018-05-13 02:47 | 2018-05-13 02:47 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 0 | 02:47 S.Balam 13.8 KV VCB Fdr #4 load dropped 55A (177-122A). S.Balam GFPC T/R 1X. 17:00 Checked & found, Recloser 16AA08 T/R 1x ctr: 86-86. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 2:47 | Night | Sunday | 2018 | 5
8581 | 2018-05-13 05:38 | 2018-05-13 05:38 | 13.8KV 8D FEEDER #1 | Fair | Pin Insulator | 0 | 8D fdr # 1 Load Droped 47A (254-107A). 8D fdr # 3 Load Droped 15A (95-80A). Not checked yet. |  | 1 | 5:38 | Morning | Sunday | 2018 | 5
8582 | 2018-05-13 05:38 | 2018-05-20 05:38 | 13.8KV 8D FEEDER #1 | Fair | Pin Insulator | 0 | Checked & found Recl 8F-05 T/R 1x Ctr:73(Not operated). Patrolled the line & found @2 Broken Pin Insulator o/p 8D-136. Cause : Lightning. |  | 1 | 5:38 | Morning | Sunday | 2018 | 5
8583 | 2018-05-13 17:32 | 2018-05-13 17:32 | 13.8KV 6DN FEEDER #2 | Fair | Unidentified | 195 | 17:32 6DN fdr #2 load dropped 132A (229-97A). 18:45 Checked and found Recl: 5D-112 T/O (in block position) Counter: 29-30. Blocked and closed Recl: 5D-112, OK. then released the block. Cause: Not patrolled yet. |  | 1 | 17:32 | Afternoon | Sunday | 2018 | 5
8584 | 2018-05-13 17:32 | 2018-05-20 17:32 | 13.8KV 6DN FEEDER #2 | Fair | Unidentified | 195 | Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 17:32 | Afternoon | Sunday | 2018 | 5
8585 | 2018-05-13 21:55 | 2018-05-13 21:55 | 4.16KV SO RUMBAI FEEDER #2 | Rain and Lightning | Lightning | 0 | 21:55 S.Rumbai 4160V fdr#2 T/O (In block). 22:43 Checked and found S.Rumbai 4160V fdr#2 T/O Ctr: 796-797 R/F: 51N. Blocked and Closed S.Rumbai fdr#2, then released the block. Not Patrol yet. |  | 1 | 21:55 | Night | Sunday | 2018 | 5
8586 | 2018-05-13 21:55 | 2018-05-20 21:55 | 4.16KV SO RUMBAI FEEDER #2 | Rain and Lightning | Lightning | 0 | Patrolled the line but found nothing. Cause : Suspected by Lightning. |  | 1 | 21:55 | Night | Sunday | 2018 | 5
8587 | 2018-05-14 10:00 | 2018-05-14 10:00 | 13.8KV 8C FEEDER #6 | Fair | Planned Maintenance | 16 | 10:00 Manually opened HLC at well 8C #17 d/s 8C Fdr #6 due to : Replaced Pin to Pin Post Insulator at well 8C-74, 8C-84E. 13:00 Manually closed HLC at well 8C #17. Cause : Plan Maintenance. |  | 1 | 10:00 | Morning | Monday | 2018 | 5
8588 | 2018-05-14 17:12 | 2018-05-14 17:12 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 0 | 17:12 DF Fdr #1 (13.8KV VCB-41) T/R 1X Not checked yet. |  | 1 | 17:12 | Afternoon | Monday | 2018 | 5
8589 | 2018-05-14 17:12 | 2018-05-15 17:12 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 0 | Checked & found, Duri Field ACB #41 fdr #1 T/R 1x ctr: 694-695 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:12 | Afternoon | Monday | 2018 | 5
8590 | 2018-05-14 19:33 | 2018-05-14 19:33 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning Arrester | 8 | Rokan 13.8 KV VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 19:33 | Night | Monday | 2018 | 5
8591 | 2018-05-14 19:33 | 2018-05-22 08:33 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning Arrester | 8 | Checked and found 13.8KV Rokan fdr #2 T/R 1x Ctr: 161-162 R/F: 51N @2. Patrolled the line and found Broken L/A o/p Kopar #02 Cause: Lightning Arrester. |  | 1 | 19:33 | Night | Monday | 2018 | 5
8592 | 2018-05-14 20:50 | 2018-05-14 20:50 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | 0 | 20:50 Off Line NDC #1 and then S/D the unit at 20:53. |  | 1 | 20:50 | Night | Monday | 2018 | 5
8593 | 2018-05-15 03:07 | 2018-05-15 03:07 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | 4 | Minas 13.8 KV ACB fdr #4 load dropped 91A (180-89A). Not checked yet. |  | 1 | 3:07 | Night | Tuesday | 2018 | 5
8594 | 2018-05-15 03:07 | 2018-05-20 09:07 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | 4 | Checked & found Recl.7D-150 T/R 1x Ctr:1765-1766 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 3:07 | Night | Tuesday | 2018 | 5
8595 | 2018-05-15 07:45 | 2018-05-15 07:45 | 13.8KV MINAS FEEDER #6 | Fair | Unidentified | 279 | 07:45 Minas fdr #6 load dropped 100A (149-49A). 11:45 Checked and found Recloser 6E 23A T/O Counter: did not change. Blocked and closed Recloser: 6E 23A and then released the block. Cause: Not patrolled yet. |  | 1 | 7:45 | Morning | Tuesday | 2018 | 5
8596 | 2018-05-15 07:45 | 2018-05-20 07:45 | 13.8KV MINAS FEEDER #6 | Fair | Unidentified | 279 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 7:45 | Morning | Tuesday | 2018 | 5
8597 | 2018-05-15 10:00 | 2018-05-15 10:00 | MINAS POWER PLANT |  |  | - | 10:00 S/U MGT #4 and Online at.11:15 to restore power. |  | 1 | 10:00 | Morning | Tuesday | 2018 | 5
8598 | 2018-05-15 13:29 | 2018-05-15 13:29 | 13.8KV 3D FEEDER #2 | Fair | Construction Job | 0 | 13:29 Manually opened 3D Fdr #2 due to : Tie In 10" pipe at well 3D-02. 14:57 Manually blocked and closed 3D Fdr #2 then release the block. Cause : Construction job. |  | 1 | 13:29 | Afternoon | Tuesday | 2018 | 5
8599 | 2018-05-15 17:15 | 2018-05-15 17:15 | 13.8KV 8C FEEDER #3 | Cloudy | Lightning | 96 | 8C fdr #3 load dropped 169A (178-9A). Not checked yet. |  | 1 | 17:15 | Afternoon | Tuesday | 2018 | 5
8600 | 2018-05-15 17:15 | 2018-05-20 17:15 | 13.8KV 8C FEEDER #3 | Cloudy | Lightning | 96 | Checked & found Recl. 8D-18A T/R 2x Ctr:50-52. R/F:51N. Patrolled the line & Found @1 Broken Dead End Insulator o/p 8D-16. Cause : Lightning. |  | 1 | 17:15 | Afternoon | Tuesday | 2018 | 5
8601 | 2018-05-15 17:16 | 2018-05-15 17:16 | 13.8KV MINAS FEEDER #4 | Cloudy | Lightning | 15 | Minas ACB #1 (feeder #4) load dropped 96A (180-84A). Not checked yet. |  | 1 | 17:16 | Afternoon | Tuesday | 2018 | 5
8602 | 2018-05-15 17:16 | 2018-05-17 17:16 | 13.8KV MINAS FEEDER #4 | Cloudy | Lightning | 15 | Checked & found, Recloser 7D-121 T/R 1x ctr: 14-15. Patrolled the line & found, #3 broken Lightning Arrester on Pole 7D-99N. Cause: Lightning. |  | 1 | 17:16 | Afternoon | Tuesday | 2018 | 5
8603 | 2018-05-15 17:24 | 2018-05-15 17:24 | 13.8KV BATANG FEEDER #2 | Cloudy | Unidentified | 0 | Batang OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 17:24 | Afternoon | Tuesday | 2018 | 5
8604 | 2018-05-15 17:24 | 2018-05-20 17:24 | 13.8KV BATANG FEEDER #2 | Cloudy | Unidentified | 0 | Checked & found Batang fdr#2 T/R 1x R/F:51N. Patrolled the line & found Danger Trees at pole 37AH11. Cause : Unidentified. |  | 1 | 17:24 | Afternoon | Tuesday | 2018 | 5
8605 | 2018-05-15 17:24 | 2018-05-15 17:24 | 13.8KV BATANG FEEDER #3 | Cloudy | Unidentified | 0 | Batang fdr #3 load dropped 22A (32-10A). Not checked yet. |  | 1 | 17:24 | Afternoon | Tuesday | 2018 | 5
8606 | 2018-05-15 17:24 | 2018-05-22 08:24 | 13.8KV BATANG FEEDER #3 | Cloudy | Unidentified | 0 | Checked and found Recloser 36-AL-13 T/R 1x Ctr: 124-125 R/F: 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:24 | Afternoon | Tuesday | 2018 | 5
8607 | 2018-05-15 18:01 | 2018-05-15 18:01 | 13.8KV BEKASAP FEEDER #6 | Fair | Others | 39 | Bekasap fdr #6 load dropped 79A (182-103A). Bekasap fdr #5 load dropped 116A (218-102A) --> WIP. Not checked yet. |  | 1 | 18:01 | Afternoon | Tuesday | 2018 | 5
8608 | 2018-05-15 18:01 | 2018-05-22 08:01 | 13.8KV BEKASAP FEEDER #6 | Fair | Others | 39 | Checked and found : Recloser 38-BE-10 T/R 1x Ctr: 597-598 R/F: 51N @1 : Recloser 34-BI-18 T/R 1x Ctr: 597-598 R/F: 51N @1, @2. Patrolled the line and found kite o/p 39-BE-13C. Cause: Others. |  | 1 | 18:01 | Afternoon | Tuesday | 2018 | 5
8609 | 2018-05-15 18:11 | 2018-05-15 18:11 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 10 | Bangko fdr #1 load dropped 82A (160-78A). Bangko fdr #4 load dropped 72A (168-96A). Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 18:11 | Afternoon | Tuesday | 2018 | 5
8610 | 2018-05-15 18:11 | 2018-05-16 17:11 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 10 | Checked & found, Recloser 23W12 T/R 1x ctr: 311-312. Also found, Recloser 23X08 T/R 1x ctr: 404-405. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 18:11 | Afternoon | Tuesday | 2018 | 5
8611 | 2018-05-15 18:27 | 2018-05-15 18:27 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 60 | 18:27 Ketigul VCB fdr #2 T/R 1x. 18:34 Ketigul VCB fdr #2 T/R again. 20:06 Ketigul VCB fdr #2 T/R again. 20:09 Ketigul GFPC T/R 1X. Not checked yet. Prod loss at 18:27 : 85 bbls . 54 wells 20:06 : 85 bbls . 54 wells Total ___________________________ + 170 bbls. 108 wells. |  | 1 | 18:27 | Afternoon | Tuesday | 2018 | 5
8612 | 2018-05-15 18:27 | 2018-05-20 18:27 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 60 | Checked & found Ketigul fdr#2 T/R 1x Ctr:290-291 R/F:51N. Patrolled the line & found @2 Broken Pin Support o/p 29AN04. Cause : Lightning. |  | 1 | 18:27 | Afternoon | Tuesday | 2018 | 5
8613 | 2018-05-15 18:34 | 2018-05-15 18:34 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 22 | 18:34 Ketigul fdr #1 load dropped 41A (106-65A). Ketigul fdr #3 load dropped 16A (18-2A). 20:06 Ketigul fdr #1 load dropped 71A (91-21A). Not checked yet. |  | 1 | 18:34 | Afternoon | Tuesday | 2018 | 5
8614 | 2018-05-15 18:34 | 2018-05-20 15:34 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Lightning | 22 | Checked & found, Recloser 32-AK-16 T/R 1x ctr: 132-133. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 18:34 | Afternoon | Tuesday | 2018 | 5
8615 | 2018-05-15 19:21 | 2018-05-15 19:21 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Lightning | 81 | 19:21 Petani 13.8KV OCV fdr #1 T/R 1X. 19:53 Petani 13.8KV OCV fdr #1 T/R 1X. Not checked yet. |  | 1 | 19:21 | Night | Tuesday | 2018 | 5
8616 | 2018-05-15 19:21 | 2018-05-20 19:21 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Lightning | 81 | Checked & found Petani VCB fdr#1 T/R 2x Ctr:60-62 R/F51N. Patrolled the line & found @1@2 Flashed over Pin insulator o/p 33AX16. Cause : Lightning. |  | 1 | 19:21 | Night | Tuesday | 2018 | 5
8617 | 2018-05-15 19:21 | 2018-05-15 19:21 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Tree | 81 | 19:21 Petani 13.8KV OCV fdr #2 T/R 1X. Not checked yet. |  | 1 | 19:21 | Night | Tuesday | 2018 | 5
8618 | 2018-05-15 19:21 | 2018-05-20 19:21 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Tree | 81 | Checked & found Petani fdr#2 T/R 1x Ctr:251-252 R/F:51N. Patrolled the line & found Danger trees at well Petani#14. Cause : Unidentified |  | 1 | 19:21 | Night | Tuesday | 2018 | 5
8619 | 2018-05-15 19:34 | 2018-05-15 19:34 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Recloser - Control Recloser | 0 | 19:34 It was reported no power at Complet Talang and Leuser. 20:52 Checke and found Recl.: 06-F7 T/SO ctr:164-165. And also found no power to Control Recloser. Un plug Recloser 06-F7. Patrolled the line but found nothing. 22:00 Blocked Community fdr #1. Closed LBS: 1F-25. (d/f Community fdr #1), then released the block. Cause: Control Recloser. |  | 1 | 19:34 | Night | Tuesday | 2018 | 5
8620 | 2018-05-16 06:23 | 2018-05-16 06:23 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri Comm. 1`3.8KV ACB fdr #2 T/R 1X. Not checked yet. |  | 1 | 6:23 | Morning | Wednesday | 2018 | 5
8621 | 2018-05-16 06:23 | 2018-05-20 09:23 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Checked & found Duri Community fdr#2 T/R 1x Ctr:97-98 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 6:23 | Morning | Wednesday | 2018 | 5
8622 | 2018-05-16 09:37 | 2018-05-16 09:37 | 44KV NORTH DURI - DUMAI LINE | Fair | Lightning | 0 | 44Kv Line Duri-Dumai GCB#1 T/R 1x Ctr:125-126 R/F:51N, 51@1@2. Not patrolled yet. |  | 1 | 9:37 | Morning | Wednesday | 2018 | 5
8623 | 2018-05-16 09:37 | 2018-05-27 09:37 | 44KV NORTH DURI - DUMAI LINE | Fair | Lightning | 0 | Checked and found Duri-dumai 44KV GCB #1 T/R 1X ctr: 125-126 R/F: 51N. Patrolled the line but found nothung. Cause: Lightning. |  | 1 | 9:37 | Morning | Wednesday | 2018 | 5
8624 | 2018-05-16 13:55 | 2018-05-16 13:55 | 13.8KV 8D FEEDER #3 | Fair | Lightning | 17 | 8D fdr#3 T/R 1x. 8D fdr#1 Load dropped 21A (112-89A). 8D fdr#2 Load dropped 34A (145-111A). Not checked yet. |  | 1 | 13:55 | Afternoon | Wednesday | 2018 | 5
8625 | 2018-05-16 13:55 | 2018-05-20 09:55 | 13.8KV 8D FEEDER #3 | Fair | Lightning | 17 | Checked & found 8D fdr#3 T/R 1x Ctr:216-217 R/F:50. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 13:55 | Afternoon | Wednesday | 2018 | 5
8626 | 2018-05-16 17:15 | 2018-05-16 17:15 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain | Dead End Insulator | 0 | Duri Community fdr#1 T/R 1x. Not checked yet. |  | 1 | 17:15 | Afternoon | Wednesday | 2018 | 5
8627 | 2018-05-16 17:15 | 2018-05-20 20:15 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain | Dead End Insulator | 0 | Checked & found Duri Community fdr#1 T/R 1x Ctr:117-118 R/F:51N. Patrolled the line & found @1 Flashed over Dead End Insulator o/p NN. Cause : Dead End Insulator |  | 1 | 17:15 | Afternoon | Wednesday | 2018 | 5
8628 | 2018-05-16 18:40 | 2018-05-16 18:40 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Pin Insulator | 87 | So.Bekasap fdr#1 Load dropped 55A (87-32A). Not checked yet. |  | 1 | 18:40 | Afternoon | Wednesday | 2018 | 5
8629 | 2018-05-16 18:40 | 2018-05-22 08:40 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Pin Insulator | 87 | Checked and found Recloser 34-BI-18 T/R 1x Ctr: 172-173 R/F: 51N @2. Patrolled the line and found Broken Pin Insulator o/p 32-BG-10. Cuase: Pin Insulator. |  | 1 | 18:40 | Afternoon | Wednesday | 2018 | 5
8630 | 2018-05-17 10:45 | 2018-05-17 10:45 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Planned Maintenance | 58 | 10:45 Manually opened Petapahan fdr#6 Replaced 300Kva Tx with the same size at well Petapahan#32 (After Rig) 11:10 Blocked & Closed Petapahan fdr#6 Cause : Planned Maintenance. |  | 1 | 10:45 | Morning | Thursday | 2018 | 5
8631 | 2018-05-18 04:50 | 2018-05-18 04:50 | 13.8KV S. BALAM FEEDER #3 | Rain and Lightning | Unidentified | 0 | 04:50 So Balam VCB fdr #3 T/R 1x. 14:00 Checked & found, No breaker, counter & R/F operated. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 4:50 | Morning | Friday | 2018 | 5
8632 | 2018-05-18 04:50 | 2018-05-18 04:50 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 0 | 04:50 So Balam fdr #4 load dropped 164 A (179-15A). So Balam fdr #1 load dropped 68A (118-50A). So Balam fdr #2 load dropped 125 A (129-4A). So Balam GFPC T/R 1x. 11:30 Checked & found, Recloser 16 AB 03 T/R 1x ctr: 447-448 R/F: 51 @2, @3. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 4:50 | Morning | Friday | 2018 | 5
8633 | 2018-05-18 04:59 | 2018-05-18 04:59 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 124 | So Balam VCB fdr #4 T/R 1x. So Balam GFPC T/R 1x. Not checked yet. |  | 1 | 4:59 | Morning | Friday | 2018 | 5
8634 | 2018-05-18 05:04 | 2018-05-18 05:04 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 82 | Bangko fdr #1 load dropped 146 A (169-23A). Bangko fdr #2 load dropped 167 A (218-51A). Bangko fdr #3 load dropped 39 A (240-209A). Not checked yet. |  | 1 | 5:04 | Morning | Friday | 2018 | 5
8635 | 2018-05-18 05:04 | 2018-05-20 07:04 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 82 | Checked & found Recl. 23X08 T/R 1x Ctr:405-406. Patrolled the line But found nothing. Cause : Lightning. |  | 1 | 5:04 | Morning | Friday | 2018 | 5
8636 | 2018-05-18 05:04 | 2018-05-18 05:04 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning Arrester | 35 | 05:04 Bangko fdr #4 load dropped 80 A (158-78A). 10:00 Checked and found Recloser: 25-Z-07 T/R 1x Counter: 194-195 R/F: 51N. Patrolled the line found @3 broken Lightning Arrester on pole 29-Y-17. Cause: Broken Lightning Arrester. |  | 1 | 5:04 | Morning | Friday | 2018 | 5
8637 | 2018-05-18 05:28 | 2018-05-18 05:28 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 37 | Nella VCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 5:28 | Morning | Friday | 2018 | 5
8638 | 2018-05-18 05:28 | 2018-05-20 08:28 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 37 | Checked & found Nella VCB fdr#2 T/R 1x Ctr:312-313 R/F:51N Patrolled the line & found @3 Broken LA o/p 21Y38. Cause : Lightning. |  | 1 | 5:28 | Morning | Friday | 2018 | 5
8639 | 2018-05-18 05:28 | 2018-05-18 05:28 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 105 | Nella fdr #1 load dropped 118 A (214-96A). Not checked yet. |  | 1 | 5:28 | Morning | Friday | 2018 | 5
8640 | 2018-05-18 05:28 | 2018-05-20 08:28 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 105 | Checked & found Recl. 22V06 T/R 1x Ctr:80-81. Patrolled the line & found @1 Broken LA on T/P well Bangko#95. Cause : Lightning. |  | 1 | 5:28 | Morning | Friday | 2018 | 5
8641 | 2018-05-19 06:07 | 2018-05-19 06:07 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Darling VCB fdr #7 T/R 1x. Not checked yet. |  | 1 | 6:07 | Morning | Saturday | 2018 | 5
8642 | 2018-05-19 06:07 | 2018-05-27 06:07 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Darling fdr #7 T/R 2X ctr: 163-165 R/F: 51@1. Patrolled the line but foud nothing. Cause: Unidentified. |  | 1 | 6:07 | Morning | Saturday | 2018 | 5
8643 | 2018-05-19 08:38 | 2018-05-19 08:38 | 13.8KV 3D FEEDER #3 | Fair | Tree | 32 | 3D fdr#3 T/R 1x. Not checked yet. |  | 1 | 8:38 | Morning | Saturday | 2018 | 5
8644 | 2018-05-19 08:38 | 2018-05-31 12:16 | 13.8KV 3D FEEDER #3 | Fair | Tree | 32 | Checked & found, 3D OCB fdr #3 T/R 1x ctr: 444 (did not change) R/F: 51N. Patrolled the line & found, High Palm Tree touched Power Line on Pole 4B-24B. Cause: Tree. |  | 1 | 8:38 | Morning | Saturday | 2018 | 5
8645 | 2018-05-19 09:10 | 2018-05-19 09:10 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Planned Maintenance | 0 | 09:10 Opened Recl,09-R8-08 d/s CD fdr#4 Replace Failure 1125 Kva Tx O/p 09 S4 04 11:00 Blocked & closed Recl.09-R8-08, then release the block. Cause: Plan Maintenance. |  | 1 | 9:10 | Morning | Saturday | 2018 | 5
8646 | 2018-05-19 09:20 | 2018-05-19 09:20 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 114 | 09:20 Manually opened 8C Fdr #3 Replaced 150Kva Tx with the same size at well 8D-65E 09:35 Blocked & closed 8C fdr#3, then release the block . Cause : Plan Maintenance. |  | 1 | 9:20 | Morning | Saturday | 2018 | 5
8647 | 2018-05-19 12:04 | 2018-05-19 12:04 | 13.8KV SINTONG FEEDER #2 | Cloudy | Unidentified | 41 | Sintong fdr#2 T/R 1x. Sintong fdr #1 load dropped 23 A (82-59A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 12:04 | Afternoon | Saturday | 2018 | 5
8648 | 2018-05-19 12:04 | 2018-05-21 08:04 | 13.8KV SINTONG FEEDER #2 | Cloudy | Unidentified | 41 | Checked and found Sintong fdr #2 T/R 1x Ctr: 472-473 R/F: 51N Patroll the line but found nothing. Cause: Unidentified. |  | 1 | 12:04 | Afternoon | Saturday | 2018 | 5
8649 | 2018-05-19 17:57 | 2018-05-19 17:57 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 38 | Rangau fdr#2 T/R 1X Rangau fdr#1 load dropped 26A(55-29A) Not checked yet. |  | 1 | 17:57 | Afternoon | Saturday | 2018 | 5
8650 | 2018-05-19 17:57 | 2018-05-25 08:57 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 38 | Checked and found 13.8KV OCB #2 T/R 1x Ctr: 336-337 R/F: 50. Patroll the line but found nothing. Cause: Unidentified. |  | 1 | 17:57 | Afternoon | Saturday | 2018 | 5
8651 | 2018-05-19 22:50 | 2018-05-19 22:50 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 12 | It was reported b/o fuse at well Petani # 29 D/S Petani #1. Not checked yet. |  | 1 | 22:50 | Night | Saturday | 2018 | 5
8652 | 2018-05-19 22:50 | 2018-05-20 10:00 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 12 | Checked & found, @2, @3 b/o fuse for 150KVA Tx at well Petani #29. Performed TTR & Megger Test, found Transformer Failure. Cause: Transformer Failure. (Will be replaced soon). |  | 1 | 22:50 | Night | Saturday | 2018 | 5
8653 | 2018-05-19 22:50 | 2018-05-31 15:00 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 12 | Replaced Failure Transformer with the same size at well Petani #29 then energized the Tx. Cause: Transformer Failure. |  | 1 | 22:50 | Night | Saturday | 2018 | 5
8654 | 2018-05-20 00:26 | 2018-05-20 00:26 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | D Field VCB #42 (feeder #2) T/R 1x. Not checked yet. |  | 1 | 0:26 | Night | Sunday | 2018 | 5
8655 | 2018-05-20 00:26 | 2018-05-27 00:26 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 0 | Checked and found D. Field fdr #2 T/R 1X ctr: 1000-1001 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 0:26 | Night | Sunday | 2018 | 5
8656 | 2018-05-20 08:04 | 2018-05-20 08:04 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 188 | 08:04 So. Balam VCB fdr#4 T/O (Blocked position for Rig Job). 08:18 Blocked & closed Balam VCB fdr #4. Ok. Not checked yet. |  | 1 | 8:04 | Morning | Sunday | 2018 | 5
8657 | 2018-05-20 08:04 | 2018-05-22 17:10 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 188 | Checked & found, S. Balam VCB fdr #4 T/R 1x ctr: 357-358 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 8:04 | Morning | Sunday | 2018 | 5
8658 | 2018-05-20 10:30 | 2018-05-20 10:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse o/p 08-L5-22 (C.Duri fdr#1). Not checked yet. |  | 1 | 10:30 | Morning | Sunday | 2018 | 5
8659 | 2018-05-20 10:30 | 2018-05-27 10:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked and found @2 b/o fuse for 112.5KVA TX o/p :08-L5-22. Replaced the b/o fuse above with same size, then energized the TX.OK. Cause: Unidentified (fuse). |  | 1 | 10:30 | Morning | Sunday | 2018 | 5
8660 | 2018-05-21 09:12 | 2018-05-21 09:12 | MINAS POWER PLANT |  |  | - | 09:12 S/U MGT#1 then on line the unit at 09:48 |  | 1 | 9:12 | Morning | Monday | 2018 | 5
8661 | 2018-05-21 10:58 | 2018-05-21 10:58 | 13.8KV NORTH DURI FEEDER #2 | Fair | Under investigation | 366 | 10:58 Perform SP transfer Load N.Duri fdr#11 to N.Duri fdr#2. 11:05 It was reported no power at NC Station Area#13. Checked & found Recl 13-G2013 T/O (failed). Open LBS 13-G61-06. 12:19 Unplug Recl. NC-04 and Rec; 13-G7-10. Closed LBS 13-G72-33. (Power back to normal). Cause: Under Investigation. |  | 1 | 10:58 | Morning | Monday | 2018 | 5
8662 | 2018-05-21 14:55 | 2018-05-21 14:55 | 13.8KV DURI FIELD FEEDER #4 | Fair | Powerline - Jumper | 0 | It was reported Lose Connection Of Secondary Cable fpr 112.5Kva Tx o/p 06-S3-03 (D.Field fdr#4). Not checked yet. |  | 1 | 14:55 | Afternoon | Monday | 2018 | 5
8663 | 2018-05-21 14:55 | 2018-05-27 14:55 | 13.8KV DURI FIELD FEEDER #4 | Fair | Powerline - Jumper | 0 | Checked and found @2 broken Jumper of TX o/p: 06-S3-03. Replaced the broken Jumper above with New one then energized the TX. OK. Cause: Jumper (broken). |  | 1 | 14:55 | Afternoon | Monday | 2018 | 5
8664 | 2018-05-21 15:06 | 2018-05-21 15:06 | MINAS POWER PLANT |  |  | - | 15:06 S/U MGT#2 then on line the unit at 15:25 15:31 Open Tie breaker ACB#25. |  | 1 | 15:06 | Afternoon | Monday | 2018 | 5
8665 | 2018-05-21 15:46 | 2018-05-21 15:46 | CENTRAL DURI POWER PLANT |  |  | - | 15:46 Off line CDGT#2 the s/D the unit for S/B. |  | 1 | 15:46 | Afternoon | Monday | 2018 | 5
8666 | 2018-05-21 16:16 | 2018-05-21 16:16 | NORTH DURI POWER PLANT |  |  | - | 16:16 S/U NDC#1, then on line the unit at 17:28. (Running Test). |  | 1 | 16:16 | Afternoon | Monday | 2018 | 5
8667 | 2018-05-21 16:44 | 2018-05-21 16:44 | 13.8KV PUNGUT FEEDER #1 | Lightning | Unidentified | 0 | MSU fdr#1 (Pungut fdr#1) T/R 1x. MSU fdr#2 (Pungut fdr#2) Load dropped 40A (52-12A). Not checked yet. |  | 1 | 16:44 | Afternoon | Monday | 2018 | 5
8668 | 2018-05-21 16:44 | 2018-05-24 08:44 | 13.8KV PUNGUT FEEDER #1 | Lightning | Unidentified | 0 | Checked and found 13.8KV OCB #1 not operated. Patrolled the line and found Recloser 45-BP-09 normal operation. Cause: Unidentified. |  | 1 | 16:44 | Afternoon | Monday | 2018 | 5
8669 | 2018-05-21 17:06 | 2018-05-21 17:06 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 0 | 17:06 So.Balam fdr#1 Load ropped 80A (107-27A). 17:31 So.Balam fdr#1 Load ropped 91A (107-18A). So.Balam fdr#4 Load ropped 27A (179-152A). Not checked yet. |  | 1 | 17:06 | Afternoon | Monday | 2018 | 5
8670 | 2018-05-21 17:06 | 2018-05-22 09:30 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 0 | Checked & found, Recloser 16 Z 41 T/R 1x ctr: 3180-3181 R/F: 51N Patrolled the line & found, dead Monkey around Pole 16 Z 41. Cause: Animal (monkey). |  | 1 | 17:06 | Afternoon | Monday | 2018 | 5
8671 | 2018-05-21 17:43 | 2018-05-21 17:43 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Others | 0 | 17:43 Emergency Transfer load C.Duri fdr#2 to Darling fdr#8. Opened C.Duri fdr#2. 17:45 Unplug Recl 08-M3-38. Closed LBS 08-M6-01. Feed Darling fdr#8. Cause: Other (Low Voltage). |  | 1 | 17:43 | Afternoon | Monday | 2018 | 5
8672 | 2018-05-22 06:53 | 2018-05-22 06:53 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 88 | So Balam VCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 6:53 | Morning | Tuesday | 2018 | 5
8673 | 2018-05-22 10:17 | 2018-05-22 10:17 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 0 | 10:17 Manually Opened Recl 16.Z41 (d/s S.Balam OCB fdr#1). to Dismantled Dead Monkey on Recloser Bushing 10:21 Manually Block & Closed the Recloser, then released the block Cause: Animal (Monkey) |  | 1 | 10:17 | Morning | Tuesday | 2018 | 5
8674 | 2018-05-22 11:27 | 2018-05-22 11:27 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 30 | 11:27 Manually Opened OKB OCB fdr#2 to Replaced VSD to Switch board at Well KB #358 12:06 Block & Closed the OKB OCB fdr#2, the released the block Cause: Planned construction |  | 1 | 11:27 | Morning | Tuesday | 2018 | 5
8675 | 2018-05-22 15:20 | 2018-05-22 15:20 | 13.8KV KETIGUL FEEDER#2 | Fair | ESP Failure | 0 | 15:20 It was reported B?O fuse at Well Sikladi #20 (d/s MGL/KTG fdr#2) 16:16 Checked & found @3 b/o fuse for 100KVATX. Perform TTR & Megger, the TX was Good, then Replaced the Fuse with the same size. Hold to Energize the TX, due to the Pump motor was Burnt Out. Cause: ESP Motor Failure |  | 1 | 15:20 | Afternoon | Tuesday | 2018 | 5
8676 | 2018-05-22 22:45 | 2018-05-22 22:45 | NORTH DURI POWER PLANT |  |  | - | 22:45 Off Line NDC #2 and then S/D the unit for Stand by. |  | 1 | 22:45 | Night | Tuesday | 2018 | 5
8677 | 2018-05-23 13:01 | 2018-05-23 13:01 | 13.8KV ROKAN FEEDER #2 | Cloudy | Animal | 0 | Rokan 13.8 KV VCB fdr #2 T/R 1X Not checked yet. |  | 1 | 13:01 | Afternoon | Wednesday | 2018 | 5
8678 | 2018-05-23 13:01 | 2018-03-06 08:25 | 13.8KV ROKAN FEEDER #2 | Cloudy | Animal | 0 | Checked & found, Rokan VCB fdr #2 T/R 2x ctr: 1262-1264 R/F: 51N @2, @3. Patrolled the line & found, a death Monkey around Terminal Pole of well Kopar #02. Cause: Animal. |  | 1 | 13:01 | Afternoon | Wednesday | 2018 | 5
8679 | 2018-05-23 14:31 | 2018-05-23 14:31 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | C.Duri 13.8 KV ACB fdr #7 load dropped 58A (148-90A). Not checked yet. |  | 1 | 14:31 | Afternoon | Wednesday | 2018 | 5
8680 | 2018-05-23 14:31 | 2018-05-28 14:31 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | Checked and found Recl.: 03-03-42 T/R 1X. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:31 | Afternoon | Wednesday | 2018 | 5
8681 | 2018-05-23 16:20 | 2018-05-23 16:20 | NORTH DURI POWER PLANT |  |  | - | 16:2- Started Up NDC CT #2 and On line to thre system at 17:27. After Off Line Wash. |  | 1 | 16:20 | Afternoon | Wednesday | 2018 | 5
8682 | 2018-05-23 17:38 | 2018-05-23 17:38 | 13.8KV NORTH DURI FEEDER #2 | Cloudy | Unidentified | 90 | N. Duri 13.8KV VCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 17:38 | Afternoon | Wednesday | 2018 | 5
8683 | 2018-05-23 17:38 | 2018-05-27 17:38 | 13.8KV NORTH DURI FEEDER #2 | Cloudy | Unidentified | 90 | Checked and found N. Duri fdr# 2 T/R 1X ctr: 268-269 R/F: 51 @1, @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:38 | Afternoon | Wednesday | 2018 | 5
8684 | 2018-05-23 18:36 | 2018-05-23 18:36 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Unidentified | 0 | 6D fdr #2 load dropped 79A (198-119A). Not checked yet. |  | 1 | 18:36 | Afternoon | Wednesday | 2018 | 5
8685 | 2018-05-23 18:36 | 2018-01-06 07:42 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found, Recloser 6D-87 T/R 1x ctr: 68-69. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 18:36 | Afternoon | Wednesday | 2018 | 5
8686 | 2018-05-24 00:08 | 2018-05-24 00:08 | NORTH DURI POWER PLANT | Fair | Under investigation | 0 | 00:08 NDC CT #2 Trip Off by Alarm FIRE AT GT ENCLOSURE Respectively Some Feeder T/O Level 1 8D VCB fdr#1 -----> Closed at 00:26 8D VCB fdr#3 -----> Closed at 00:26 3D OCB fdr#6 - -----> Closed at 00:21, WIP 4D OCB fdr#4 -----> Closed at 00:24 4B OCB fdr#4 -----> Closed at 00:18, WIP 5B OCB fdr#4 -----> Closed at 00:23 BOB Zamrud fdr#1 -----> Closed at 00:22 BOB Zamrud fdr#2 -----> Closed at 00:22 BOB Beruk fdr #2 -----> Closed at 00:22 Cause: Under Investigate. |  | 1 | 0:08 | Night | Thursday | 2018 | 5
8687 | 2018-05-24 08:06 | 2018-05-24 08:06 | 13.8KV KETIGUL GFPC | Fair | Unidentified | 0 | Ketigul 13.8 KV GFPC T/R 1X. Not checked yet. |  | 1 | 8:06 | Morning | Thursday | 2018 | 5
8688 | 2018-05-24 10:58 | 2018-05-24 10:58 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified (Fuse) | 0 | 10:58 It was reported b/o fuse at well Gulamo #3 d/s Ketigul fdr #3. Checked and found @1,@2,@3 b/o fuse for 300 KVA TX. Performed TTX and megger the TX. Ok. Replaced the fuse with same size. Cause:Unidentified (fuse). |  | 1 | 10:58 | Morning | Thursday | 2018 | 5
8689 | 2018-05-24 11:29 | 2018-05-24 11:29 | NORTH DURI POWER PLANT |  |  | - | 11:29 S/U NDC #2 and online the system at:12:28. |  | 1 | 11:29 | Morning | Thursday | 2018 | 5
8690 | 2018-05-24 14:29 | 2018-05-24 14:29 | 13.8KV BATANG FEEDER #2 | Fair | Construction Job | 0 | 14:29 Manually Open Batang fdr #2, ----->Closed at 17:07. Installed PIG Launcher at Contruction. |  | 1 | 14:29 | Afternoon | Thursday | 2018 | 5
8691 | 2018-05-24 16:23 | 2018-05-23 08:23 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Unidentified | 0 | Checked and found 13.8KV VCB #3 T/O Ctr: 367-368 R/F: None. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:23 | Afternoon | Thursday | 2018 | 5
8692 | 2018-05-24 16:23 | 2018-05-24 16:23 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Unidentified | 0 | 16:23 Petapahan 13.8KV VCB fdr #3 T/LO ctr:267-268 R/F: None. 16:44 Checked and found Petapahan fdr #3 T/LO. Also found Petapahan GFPC T/O (In block). 16:45 Closed Petapahan GFPC. OK. 16:48 Blocked and closed Petapahan fdr #3, Ok then released the block. Npt Patrolled yet. |  | 1 | 16:23 | Afternoon | Thursday | 2018 | 5
8693 | 2018-05-25 06:00 | 2018-05-25 06:00 | NORTH DURI POWER PLANT |  |  | - | 06:00 Off line NDC #3 then S/D the unit for maintenance. |  | 1 | 6:00 | Morning | Friday | 2018 | 5
8694 | 2018-05-25 06:21 | 2018-05-25 06:21 | 13.8KV MINAS FEEDER #6 | Fair | Lightning | 56 | Minas Fdr#6 Looad dropped 78A (150-72A) Checked and found Recloser 6E-23A T/SO Ctr: 527-527 (not change) R/F: None. Blocked & closed Recloser above, then released the block. Not patrolled yet. |  | 1 | 6:21 | Morning | Friday | 2018 | 5
8695 | 2018-05-25 06:21 | 2018-04-06 08:21 | 13.8KV MINAS FEEDER #6 | Fair | Lightning | 56 | Checked and found Minas fdr #6 load dropped. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 6:21 | Morning | Friday | 2018 | 5
8696 | 2018-05-25 09:21 | 2018-05-25 09:21 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 352 | 09:21 S.Balam 13.8 KV VCB fdr #1 load dropped 112A (122-110A) 10:00 Checked and found Recloser 16-Z-25 T/LO, ctr:41-45. Patrolled the line and found dead Monkey O/P 16-Z-41. Blocked and Closed Recloser 16-Z-25. Ok, then release the block. Cause:Animal (Monkey). |  | 1 | 9:21 | Morning | Friday | 2018 | 5
8697 | 2018-05-25 09:21 | 2018-05-25 09:21 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 0 | S.Balam 13.8 KV VCB fdr #4 load dropped 77A (179-102A). Not checked yet. |  | 1 | 9:21 | Morning | Friday | 2018 | 5
8698 | 2018-05-25 09:21 | 2018-05-25 09:21 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 0 | Checked and foud Recloser :16-AA-08 T/R 2X Ctr : 87 – 89 F/R: None Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:21 | Morning | Friday | 2018 | 5
8699 | 2018-05-25 22:22 | 2018-05-25 22:22 | 13.8KV PEMATANG FEEDER #2 | Fair | Emergency | 0 | It was reported Pipe 12" Production Line Leaks in front of Pematang Public market. 22:22 - Manually Opened Pematang OCB fdr#1 --------> Closed at 23:41 - Manually Opened Pematang OCB fdr#2 --------> Closed at 23:45 - Manually Opened Rangau OCB fdr#2 ---------> Closed at 23:45 Cause: Emergency |  | 1 | 22:22 | Night | Friday | 2018 | 5
8700 | 2018-05-26 09:17 | 2018-05-26 09:17 | 13.8KV DURI FIELD FEEDER #2 | Fair | Planned Maintenance | 0 | 09:17 Manually Open LBS : 06-S3-02. Replaced 112.5KVA TX O/P : 06-S3-03. Plan Maintenance. |  | 1 | 9:17 | Morning | Saturday | 2018 | 5
8701 | 2018-05-26 10:32 | 2018-05-26 10:32 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 0 | 10:32 It was reported b/o fuse o/p # 03-01-03. Checked and found @2 b/o fuse for 112.5Kva TX. Performed TTR test and Megger the TX. OK. Replaced the b/o fuse above with same size, then energized the TX. OK. Cause: Animal (Monkey). |  | 1 | 10:32 | Morning | Saturday | 2018 | 5
8702 | 2018-05-26 12:52 | 2018-05-26 12:52 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | Duri Comy 13.8KV ACB#26 fdr#3 T/R 1X. Not checked yet. |  | 1 | 12:52 | Afternoon | Saturday | 2018 | 5
8703 | 2018-05-26 12:52 | 2018-03-06 15:52 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | Checked & found, Duri Community ACB #26 fdr #3 T/R 1x ctr: 70-71 R/F: 51 @1, @2. Patrolled the line & found, @1, @2 b/o Fuse for 300KVA Tx at WTP Sebanga. Cause: Animal. |  | 1 | 12:52 | Afternoon | Saturday | 2018 | 5
8704 | 2018-05-26 14:57 | 2018-05-26 14:57 | 13.8KV CENTRAL DURI FEEDER #8 | Rain | Unidentified | 0 | C.Duri 13.8 KV ACB fdr #8 T/R 1X. ctr:443-444, R/f:51@1. Not checked yet. |  | 1 | 14:57 | Afternoon | Saturday | 2018 | 5
8705 | 2018-05-26 14:57 | 2018-05-27 14:57 | 13.8KV CENTRAL DURI FEEDER #8 | Rain | Unidentified | 0 | Checked and found C. Duri fdr #8 T/R 1X ctr: 443-444 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:57 | Afternoon | Saturday | 2018 | 5
8706 | 2018-05-26 16:08 | 2018-05-26 16:08 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 172 | 16:08 OKB 134.8KV OCB fdr #2 T/SO ctr:1318-1319 R/F: 51N. (Block indication appeared while OCB Tripped) 17:00 Checked and found OKB fdr #2 T/SO. 17:16 Blocked and closed OKB fdr #2, OK then released the block. Not patrolled yet. |  | 1 | 16:08 | Afternoon | Saturday | 2018 | 5
8707 | 2018-05-26 16:08 | 2018-05-27 16:08 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 172 | Checked and found OKB fdr #2 T/SO ctr: 318-319 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:08 | Afternoon | Saturday | 2018 | 5
8708 | 2018-05-26 20:34 | 2018-05-26 20:34 | NORTH DURI POWER PLANT |  |  | - | 20:34 NDC CT#3 Stat Up then On Line at 21:01 21;13 Closed ND 230 GCB#33. After Off Line Wash Maintenance programs. 21:47 NDC CT#3 Off Line the S/D due to High Vibration 22:34 Perform HOT S/U, the On Line at 23:05 23:06 Closed ND GCB#33 the Vibration saw normal 2.2 mils |  | 1 | 20:34 | Night | Saturday | 2018 | 5
8709 | 2018-05-26 23:36 | 2018-05-26 23:36 | 13.8KV PINANG FEEDER #1 | Cloudy | Unidentified | 26 | 23:36 Pinang OCB fdr#1 T/R 1x Not checked yet |  | 1 | 23:36 | Night | Saturday | 2018 | 5
8710 | 2018-05-26 23:36 | 2018-05-31 11:30 | 13.8KV PINANG FEEDER #1 | Cloudy | Unidentified | 26 | Checked & found, Pinang VCB fdr #1 T/R 1x ctr: 439-440 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 23:36 | Night | Saturday | 2018 | 5
8711 | 2018-05-27 08:15 | 2018-05-27 08:15 | MINAS POWER PLANT |  |  | - | 08:15 Off line MGT #1 then S/D for standby. |  | 1 | 8:15 | Morning | Sunday | 2018 | 5
8712 | 2018-05-27 08:30 | 2018-05-27 08:30 | MINAS POWER PLANT |  |  | - | 08:30 Off line MGT #2 then S/D for standby. |  | 1 | 8:30 | Morning | Sunday | 2018 | 5
8713 | 2018-05-27 08:43 | 2018-05-27 08:43 | MINAS POWER PLANT |  |  | - | 08:43:00 Off line MGT #4 then S/D for standby. |  | 1 | 8:43 | Morning | Sunday | 2018 | 5
8714 | 2018-05-27 09:07 | 2018-05-27 09:07 | MINAS POWER PLANT |  |  | - | 09:07 Off line MGT #6 then S/D for standby. |  | 1 | 9:07 | Morning | Sunday | 2018 | 5
8715 | 2018-05-27 14:49 | 2018-05-27 14:49 | 13.8KV DURI FIELD FEEDER #2 | Fair | Low mega-ohm reading | 0 | It was reported B/O fuse o/p 06-S7-17A (Duri Field fdr#4). Not checked yet. |  | 1 | 14:49 | Afternoon | Sunday | 2018 | 5
8716 | 2018-05-27 14:49 | 2018-05-29 14:49 | 13.8KV DURI FIELD FEEDER #2 | Fair | Low mega-ohm reading | 0 | Checked & found, @1, @2 b/o Fuse for 112.5KVA Tx on Pole 06-S7-17A. Performed TTR & Megger Test the TX, found Low-Mega Ohm Reading Tx. Cause: Low-Mega Ohm Reading Tx. (Will be replaced tomorrow). |  | 1 | 14:49 | Afternoon | Sunday | 2018 | 5
8717 | 2018-05-27 14:49 | 19/06/2018 14:49 | 13.8KV DURI FIELD FEEDER #2 | Fair | Low mega-ohm reading | 0 | 11:00 Replaced 112.5KVA TX o/p: 06-S7-17 then energized the TX. OK. Cause: Low Megga Ohm TX. |  | 1 | 14:49 | Afternoon | Sunday | 2018 | 5
8718 | 2018-05-27 17:27 | 2018-05-27 17:27 | MINAS POWER PLANT |  |  | - | Off line MGT#3, then S/D the unit for S/B. |  | 1 | 17:27 | Afternoon | Sunday | 2018 | 5
8719 | 2018-05-28 09:59 | 2018-05-28 09:59 | 13.8KV NORTH DURI FEEDER #11 | Fair | Planned Maintenance | 0 | 09:59 Manually Open Recl.: 12-F3-26, ----->Closed at 12:00. Replaced 6Pcs LA o/p: 12-F3-08 and 12-F3-21. Plan Maintenance. |  | 1 | 9:59 | Morning | Monday | 2018 | 5
8720 | 2018-05-28 15:10 | 2018-05-28 15:10 | MINAS POWER PLANT | Fair | Equipment Failure | 0 | 15:10 MGT#10 T/O By Computer ( S) Auto reboot (No load Shedding). |  | 1 | 15:10 | Afternoon | Monday | 2018 | 5
8721 | 2018-05-28 15:28 | 2018-05-28 15:28 | MINAS POWER PLANT |  |  | - | 15:28 MGT # 6 S/U and On Line to the system at 15:54 to restore the load. |  | 1 | 15:28 | Afternoon | Monday | 2018 | 5
8722 | 2018-05-28 16:45 | 2018-05-28 16:45 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 113 | 16:45 Bekasap 13,.8KV OCB fdr #2 T/R 1X. Bekasap GFPC T/R 1X. Bekasap fdr #1 load dropped 10A (12-2A). Not checked yet. |  | 1 | 16:45 | Afternoon | Monday | 2018 | 5
8723 | 2018-05-28 16:45 | 16/06/2018 12:33 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 113 | Checked & found, Bekasap Main OCB fdr #2 T/R 1x ctr: 392-393 R/F: 50@2. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 16:45 | Afternoon | Monday | 2018 | 5
8724 | 2018-05-28 19:57 | 2018-05-28 19:57 | MINAS POWER PLANT |  |  | - | MGT#6 Open Generator Breaker by Excitation Fan Trouble. Then S/D the unit. |  | 1 | 19:57 | Night | Monday | 2018 | 5
8725 | 2018-05-28 20:27 | 2018-05-28 20:27 | MINAS POWER PLANT |  |  | - | 20:57 S/U MGT#10, then On line the unit at 20:45. |  | 1 | 20:27 | Night | Monday | 2018 | 5
8726 | 2018-05-28 21:13 | 2018-05-28 21:13 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 21:13 It was reported B/O fuse at well Petani#117 (Petani fdr#1). 23:04 Checked & found @1 B/O fuse for 150Kva Tx at well Petani#117. Not Replaced Yet. |  | 1 | 21:13 | Night | Monday | 2018 | 5
8727 | 2018-05-28 21:13 | 2018-05-06 14:00 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Replaced @1 b/o Fuse for 150KVA Tx with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 21:13 | Night | Monday | 2018 | 5
8728 | 2018-05-29 09:15 | 2018-05-29 09:15 | 13.8KV SINTONG FEEDER #2 | Fair | Low mega-ohm reading | 171 | It was reported b/o fuse at well Sintong #37 d/s Sintong fdr #2. Checked and found @1 b/o fuse for 150 KVA TX, Performed TTR Test and Megger the TX and found low reading Megger TX. Cause: Low Megger Reading Tx. |  | 1 | 9:15 | Morning | Tuesday | 2018 | 5
8729 | 2018-05-29 09:15 | 2018-05-31 11:28 | 13.8KV SINTONG FEEDER #2 | Fair | Low mega-ohm reading | 171 | Replaced The Low Mega-ohm Reading Tx with the same size then energized the Tx. Cause: Low Mega-ohm Reading. |  | 1 | 9:15 | Morning | Tuesday | 2018 | 5
8730 | 2018-05-29 11:24 | 2018-05-29 11:24 | 13.8KV PUNGUT FEEDER #1 | Fair | Construction Job | 0 | 11:24 Manually Open Pungut 13.8 KV fdr #1 (MSU 2 fdr #1), ----->Closed at 11:53. Replaced 150-300 KVA TX at well Pungut #19 , R/M:167-175 HP ctr:299. Cause: Contruction Job (by SPS). |  | 1 | 11:24 | Morning | Tuesday | 2018 | 5
8731 | 2018-05-29 11:30 | 2018-05-29 11:30 | 13.8KV 6D FEEDER #1 | Fair | Tree | 0 | 11:30 Manually Open Recl.: 5C-42 d/s 6D fdr #1, ----->Closed at 12:19. Wood falling at o/p: 6B-36 , ctr:30. Plan Maintenance. |  | 1 | 11:30 | Morning | Tuesday | 2018 | 5
8732 | 2018-05-29 14:30 | 2018-05-29 14:30 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 0 | It was reported b/o fuse o/p: 03-04-09. Not checked yet. |  | 1 | 14:30 | Afternoon | Tuesday | 2018 | 5
8733 | 2018-05-29 14:30 | 2018-05-31 11:18 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Animal | 0 | Checked and found @2,@3 b/o fuse for 112.5 Kva Tx on pole 03-04-09. Perform TTR and megger found good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (monkey). |  | 1 | 14:30 | Afternoon | Tuesday | 2018 | 5
8734 | 2018-05-29 14:42 | 2018-05-29 14:42 | 13.8KV BANGKO FEEDER #1 | Drizzle | Construction Job | 0 | 14:42 Manually Open Bangko fdr #1, ----->Closed at 15:28. Tie in Power line at well Bangko # 329. Project. |  | 1 | 14:42 | Afternoon | Tuesday | 2018 | 5
8735 | 2018-05-29 15:46 | 2018-05-29 15:46 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 53 | 3D fdr #4 Load dropped 134A (240-106). 3D GFPC TX-1 T/R 1X. Not checked yet. |  | 1 | 15:46 | Afternoon | Tuesday | 2018 | 5
8736 | 2018-05-29 15:46 | 2018-02-06 18:16 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 53 | Checked & found, Recloser 2D-14 T/R 1x ctr: 78-79 Patrolled the line & found, @3 broken Lightning Arrester on Pole 2D-33. Cause: Lightning. |  | 1 | 15:46 | Afternoon | Tuesday | 2018 | 5
8737 | 2018-05-29 19:45 | 2018-05-29 19:45 | 13.8KV NELLA FEEDER #1 | Cloudy | Lightning | 62 | Nella Fdr#1 Load dropped 87A (220-133A) Nella GFPC T/R 1x Not checked yet. |  | 1 | 19:45 | Night | Tuesday | 2018 | 5
8738 | 2018-05-29 19:45 | 2018-05-31 11:26 | 13.8KV NELLA FEEDER #1 | Cloudy | Lightning | 62 | Checked & found, Recloser 22V01 T/R 1x ctr: 117-119 R/F: 51N. Patrolled the line & found, @1 broken Lightning Arrester on T/P well Bangko #193. Cause: Lightning. |  | 1 | 19:45 | Night | Tuesday | 2018 | 5
8739 | 2018-05-29 23:53 | 2018-05-29 23:53 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Powerline - Conductor | 0 | 23:53 C.Duri ACB#23 Fdr#8 T/LO, Ctr: 444-4447, R/F 51 @1@2@3 00:17 Manually BLock & Closed the Feeder, but Trip Again Patrolled the Line, found @2 Broken Conductor at Pole Recl 04-04-02. Isolated The Recloser above, No power Beet wen Pole 04-04-22 to pole 04-04-22 Cause: Conductor |  | 1 | 23:53 | Night | Tuesday | 2018 | 5
8740 | 2018-05-30 07:09 | 2018-05-30 07:09 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | N Duri VCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 7:09 | Morning | Wednesday | 2018 | 5
8741 | 2018-05-30 07:09 | 2018-01-06 17:10 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found N Duri VCB fdr #1 T/R 1x Counter: 287-288 R/F: 51 @2. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 7:09 | Morning | Wednesday | 2018 | 5
8742 | 2018-05-30 10:12 | 2018-05-30 10:12 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Planned Maintenance | 207 | 10:12 Manually opened CD Fdr #8 due to : Repaired broken conductor on pole 04-04-22. 12:00 Manually blocked and closed CD Fdr #8 and then released the blocked. Cause : Plan Maintenance. |  | 1 | 10:12 | Morning | Wednesday | 2018 | 5
8743 | 2018-05-30 10:57 | 2018-05-30 10:57 | 13.8KV DURI FIELD FEEDER #3 | Fair | Construction Job | 0 | 10:57 Manually opened recl.01-09-30 d/s DF Fdr #3 due to : Tie in 24" pipe to 12" near pole 01-05-01. 17:06 Manually blocked and closed Recl.01-09-30 and then release the blocked. Cause : Project Construction. |  | 1 | 10:57 | Morning | Wednesday | 2018 | 5
8744 | 2018-05-31 06:53 | 2018-05-31 06:53 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | C Duri ACB#18 (feeder #15) T/R 1x. Not checked yet. |  | 1 | 6:53 | Morning | Thursday | 2018 | 5
8745 | 2018-05-31 06:53 | 2018-01-06 17:10 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | Checked and found C Duri ACB#18 (feeder #15) T/R 2x Counter: 377-379 R/F: 51@1. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 6:53 | Morning | Thursday | 2018 | 5
8746 | 2018-05-31 12:30 | 2018-05-31 12:30 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning | 36 | Rokan VCB fdr #2 T/R 1x. Rokan fdr #4 load dropped 24A (37-13A). not checked yet. |  | 1 | 12:30 | Afternoon | Thursday | 2018 | 5
8747 | 2018-05-31 12:30 | 2018-03-06 08:27 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning | 36 | Checked & found, Rokan VCB fdr #2 T/R 1x ctr: 1264-1265 R/F: 51N @3. Patrolled the line & found, @3 broken Lightning Arrester on Pole 21 AU 03. Cause: Lightning. |  | 1 | 12:30 | Afternoon | Thursday | 2018 | 5
8748 | 2018-05-31 19:15 | 2018-05-31 19:15 | 13.8KV MINAS FEEDER #2 | Rain | Unidentified | 45 | 19:15 Minas fdr#2 Load dropped 61A (125-64A) Minas fdr#3 Load dropped 15A (179-164A) 20:15 It was reported no power at Minas WTP. 20:52 It was reported no power at wells 7D-34, 44, 45 and 7D-54. 21:25 Checked and found Recl. #M2-01 T/LO ctr: 50-54. Patrolled the line but found nothing. 23:42 Blocked and closed Recl. #M2-01, OK then released the block. Cause: Unidentified. |  | 1 | 19:15 | Night | Thursday | 2018 | 5
8749 | 2018-05-31 19:15 | 2018-05-31 19:15 | 13.8KV MINAS FEEDER #4 | Fair | Tree | 48 | Minas fdr#4 load dropped 90A (182-92A). Not checked yet. |  | 1 | 19:15 | Night | Thursday | 2018 | 5
8750 | 2018-05-31 19:15 | 2018-08-06 02:59 | 13.8KV MINAS FEEDER #4 | Fair | Tree | 48 | Checked & found, Recloser 7D-150 T/R 6x ctr: 1766-1772. Patrolled the line & found, High Palm Tree touched Power line between Pole 8D-126 to 8D-127. Cause: Tree. |  | 1 | 19:15 | Night | Thursday | 2018 | 5
8751 | 2018-01-06 08:32 | 2018-01-06 08:32 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | 08:32 Darling VCB Fdr #7 T/R 1X. Not checked yet. |  | 1 | 8:32 | Morning | Saturday | 2018 | 1
8752 | 2018-01-06 08:32 | 2018-03-06 07:21 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Checked & found, Darling VCB fdr #7 T/R 1x ctr: 165-166 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 8:32 | Morning | Saturday | 2018 | 1
8753 | 2018-01-06 09:29 | 2018-01-06 09:29 | 13.8KV DARLING VCB FEEDER #3 | Fair | Animal | 0 | 09:29 It was reported b/o fuse o/p 05-N1-19 d/s Darling Fdr #3 (5NE Station no power). 11:04 Checked and found @1, @2 b/o fuse for 500 KVA TX. Replaced b/o fuse aboved and then energized the TX. Cause : Animal (Monkey). |  | 1 | 9:29 | Morning | Saturday | 2018 | 1
8754 | 2018-02-06 07:53 | 2018-02-06 07:53 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | N Duri VCB fdr #9 T/R 1x. Not checked yet. |  | 1 | 7:53 | Morning | Tuesday | 2018 | 2
8755 | 2018-02-06 07:53 | 2018-03-06 13:31 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | Checked & found, North Duri VCB fdr #9 T/R 1x ctr: 57-58 R/F: 51 @1, @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:53 | Morning | Tuesday | 2018 | 2
8756 | 2018-02-06 08:21 | 2018-02-06 08:21 | 13.8KV SINTONG FEEDER #2 | Fair | Pin Insulator | 0 | Sintong fdr #2 load dropped 15A (235-220A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 8:21 | Morning | Tuesday | 2018 | 2
8757 | 2018-02-06 08:21 | 2018-04-06 07:42 | 13.8KV SINTONG FEEDER #2 | Fair | Pin Insulator | 0 | Checked & found, Recloser 29-Z-13A T/R 2x ctr: 183-185. Patrolled the line & found, @2 broken Pin Insulator on Pole 30-AA-04. Cause: Pin Insulator. |  | 1 | 8:21 | Morning | Tuesday | 2018 | 2
8758 | 2018-02-06 09:35 | 2018-02-06 09:35 | 13.8KV 4B FEEDER #5 | Fair | Planned Maintenance | 0 | 09:35 Manually opened LBS 4B-150 d/s 4B Fdr #6 due to: Cutting tree at pole 149-151. abd 4 weel off (4B-13, 16, 24, 35). 11:10 Manually closed LBS 4B-150. Cause Plan Maintenance. |  | 1 | 9:35 | Morning | Tuesday | 2018 | 2
8759 | 2018-02-06 15:18 | 2018-02-06 15:18 | NORTH DURI SUBSTATION | Fair | Under investigation | 579 | 15:18 N Duri Circuit Switcher #12 T/O N Duri VCB fdr #5 T/R 1x. No power down stream C/S Tx #12. Manually opened N Duri VCB fdr #4 at : 16:44 Blocked and closed at : 17:01. Manually opened N Duri VCB fdr #5 at : 16:44 Blocked and closed at : 17:08. Manually opened N Duri VCB fdr #6 at : 16:44 Blocked and closed at : 17:02. Manually opened N Duri VCB fdr #7 at : 16:44 Blocked and closed at : 17:03. Manually opened N Duri VCB fdr #8 at : 16:44 Blocked and closed at : 17:03. Checked and found N Duri Circuit Switcher #12 T/O Counter : R/F: Winding 2 N Time. N Duri VCB fdr #5 T/R 1x Counter: 114-115 R/F: 51@1. 16:56 Manually closed C/S #12 --> OK Manually blocked and closed all feeders down stream C/S #12. Cause: Under investigation. | 1234 | 1 | 15:18 | Afternoon | Tuesday | 2018 | 2
8760 | 2018-03-06 06:31 | 2018-03-06 06:31 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | 06:31 ND Fdr #1 T/R 1x Ctr: 288-289 R/F: 51 @1,2,3. 17:30 Checked and found ND Fdr #1 T/R 1x Counter: 288-289 R/F: 51 @1,2,3. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 6:31 | Morning | Tuesday | 2018 | 3
8761 | 2018-03-06 06:31 | 2018-03-06 06:31 | 13.8KV NORTH DURI FEEDER #6 | Fair | Unidentified | 0 | 06:31 ND Fdr #6 T/R 2x. 17:30 Checked and found ND Fdr #6 T/R 2x Counter: 298-300 R/F: 51 @1,2,3. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 6:31 | Morning | Tuesday | 2018 | 3
8762 | 2018-03-06 06:31 | 2018-03-06 06:31 | 13.8KV NORTH DURI FEEDER #4 | Fair | Unidentified | 0 | 06:31 N Duri VCB fdr #4 T/R 1x. 17:30 Checked and found N Duri VCB fdr #4 T/R 1x Counter: 165-166 R/F: 50@1. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 6:31 | Morning | Tuesday | 2018 | 3
8763 | 2018-03-06 16:56 | 2018-03-06 16:56 | MINAS POWER PLANT | Fair | Under investigation | 0 | MGT #11 Trip By Alarm: Switch Liquid Level High. Frequency: 59.3 No Load shedding. |  | 1 | 16:56 | Afternoon | Tuesday | 2018 | 3
8764 | 2018-04-06 00:34 | 2018-04-06 00:34 | 13.8KV 8D FEEDER #10 | Fair | Lightning | 49 | 8D 13.8KV OCB fdr #10 T/R 1X. Not checked yet. |  | 1 | 0:34 | Night | Friday | 2018 | 4
8765 | 2018-04-06 00:34 | 2018-04-06 08:34 | 13.8KV 8D FEEDER #10 | Fair | Lightning | 49 | Checked and found 13.8KV OCB #10 T/R 1x Ctr: 257-258 R/F: 51N. Patrolled the line and found Flash Over Pin Insulator @2 near location 8E-16. Cause: Lightning. |  | 1 | 0:34 | Night | Friday | 2018 | 4
8766 | 2018-04-06 06:00 | 2018-04-06 06:00 | 13.8KV KETIGUL GFPC | Fair | Unidentified | 0 | Ketigul 13.8 KV GFPC T/R IX (On Block). No load dropped. Not checked yet. |  | 1 | 6:00 | Morning | Friday | 2018 | 4
8767 | 2018-04-06 09:28 | 2018-04-06 09:28 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | 09:28 Manually opened Recl, 16 AB 03 d/s So. Balam fdr#4 Due to : Relocated terminal pole at New well (well of Balam#19,331) 10:48 Manually blocked and closed recl;16 AB 03 d/s balam fdr#4 then release the blocked. Cause : Job construction. |  | 1 | 9:28 | Morning | Friday | 2018 | 4
8768 | 2018-04-06 10:29 | 2018-04-06 10:29 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 0 | 10:29 Manually opened Recl, 37 BD 40 d/s Bekasap fdr#2 Due to : Infill Bekasap well 02 & 03 at Bekasap 27, 137, 144. 11:40 Manually blocked and closed recl;37 BD 04 d/s Bekasap fdr#2 then release the blocked. Cause : Job construction. |  | 1 | 10:29 | Morning | Friday | 2018 | 4
8769 | 2018-04-06 14:52 | 2018-04-06 14:52 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | C.Duri 13.8Kv VCB#18 fdr#15 T/R 1X. Ctr : 379-380, R/f 51 @1 & @2 Not checked yet. |  | 1 | 14:52 | Afternoon | Friday | 2018 | 4
8770 | 2018-04-06 14:52 | 2018-12-06 17:42 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:52 | Afternoon | Friday | 2018 | 4
8771 | 2018-04-06 15:00 | 2018-04-06 15:00 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified | 53 | 09:29 It was reported b/o fuse o/p 04 07 12 d/s C.duri fdr9. Not checked yet. |  | 1 | 15:00 | Afternoon | Friday | 2018 | 4
8772 | 2018-04-06 15:00 | 2018-05-06 09:30 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified | 53 | Checked & found @1@3 b/o fuse for 112.5KVATX O/P04-07-11 d/s CD fdr#9 Blocked CD fdr#9, Replaced Fuse with the Same size, then Energized the TX Patrolled the Line, but Found nothing Cause: Unidentified |  | 1 | 15:00 | Afternoon | Friday | 2018 | 4
8773 | 2018-05-06 09:10 | 2018-05-06 09:10 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 24 | 09:10 It was reported No power road 09 under Recl: 10-J4-19 d/s N.Duri fdr#2. Checked & Found Recl 10-J4-19 T/SO, Ctr : 130-131, R/F: N/A Patrolled the line, but faund nothing 10:10 Blocked & Closed the Recloser, then released the block Cause: unidentified |  | 1 | 9:10 | Morning | Sunday | 2018 | 5
8774 | 2018-05-06 09:20 | 2018-05-06 09:20 | 13.8KV DURI FIELD FEEDER #2 | Fair | Construction Job | 0 | 09:20 Manually Opened LBS 01-09-32 d/s DF fdr#3 to Tie In & Hot Tapping Production Line 12:30 Manually Closed back the LBS. after finished the Jobs. Cause: Planning Construction. |  | 1 | 9:20 | Morning | Sunday | 2018 | 5
8775 | 2018-05-06 13:41 | 2018-05-06 13:41 | 13.8KV NELLA FEEDER #1 | Fair | Lightning Arrester | 0 | Nella fdr#1 load dropped 80A (220-140A) Nella GFPC T/R 1X. Not checked yet. |  | 1 | 13:41 | Afternoon | Sunday | 2018 | 5
8776 | 2018-05-06 13:41 | 2018-07-06 07:15 | 13.8KV NELLA FEEDER #1 | Fair | Lightning Arrester | 0 | Checked & found, Recloser 22-V-01 T/R 1x ctr: 119-120. Patrolled the line & found, @1 broken Lightning Arrester on Terminal Pole of Well BKO#193. Cause: Lightning Arrester. |  | 1 | 13:41 | Afternoon | Sunday | 2018 | 5
8777 | 2018-05-06 14:18 | 2018-05-06 14:18 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 51 | 8C fdr#1 T/R 1X. Not checked yet. |  | 1 | 14:18 | Afternoon | Sunday | 2018 | 5
8778 | 2018-05-06 14:18 | 13/06/2018 07:37 | 13.8KV 8C FEEDER #1 | Fair | Unidentified | 51 | Checked & found, 8C OCB fdr #1 counter & R/F did not operate. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:18 | Afternoon | Sunday | 2018 | 5
8779 | 2018-05-06 15:21 | 2018-05-06 15:21 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | 15:21 It was reported b/o fuse o/p 06.S3.11 d/s DF Fdr #4. 16:30 Checked & found @3 b/o fuse for 112.5KVATX. Replaced Fuse with the same size, then Energized the TX Cause : Unidentified |  | 1 | 15:21 | Afternoon | Sunday | 2018 | 5
8780 | 2018-06-06 10:40 | 2018-06-06 10:40 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Planned Maintenance | 259 | 10:40 Open /Closed Petapahan fdr#4 Change out 300Kv Tx duo to replace S.bouad & VSD 11:03 Blocked & closed Petapahan fdr#4, then release the block. Cause: Construction Job. |  | 1 | 10:40 | Morning | Wednesday | 2018 | 6
8781 | 2018-06-06 12:08 | 2018-06-06 12:08 | 13.8KV NORTH DURI FEEDER #5 | Fair | Animal | 0 | It was reported B/O fuse o/p 12 F9 09 d/s N.Duri fdr#5 Not checked yet. |  | 1 | 12:08 | Afternoon | Wednesday | 2018 | 6
8782 | 2018-06-06 12:08 | 2018-08-06 12:08 | 13.8KV NORTH DURI FEEDER #5 | Fair | Animal | 0 | Replaced @2@3 B/O fse for 112.5 Kva Tx with the same size. Cause: Animal (Monkey). |  | 1 | 12:08 | Afternoon | Wednesday | 2018 | 6
8783 | 2018-06-06 12:56 | 2018-06-06 12:56 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 132 | Bekasap main 13.8Kv ACB fdr#6 T/R 1X. Not checked yet. |  | 1 | 12:56 | Afternoon | Wednesday | 2018 | 6
8784 | 2018-06-06 12:56 | 16/06/2018 12:26 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 132 | Checked & found, Bekasap VCB fdr #6 T/R 1x ctr: 368-369 R/F: 51 @1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 12:56 | Afternoon | Wednesday | 2018 | 6
8785 | 2018-06-06 14:39 | 2018-06-06 14:39 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Duri Commy 13.8Kv VCB#26 fdr#3 T/R 1X. Not checked yet. |  | 1 | 14:39 | Afternoon | Wednesday | 2018 | 6
8786 | 2018-06-06 14:39 | 13/06/2018 11:08 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Checked & found, Duri Community ACB #26 fdr #3 T/R 1x ctr: 71-72 R/F:51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:39 | Afternoon | Wednesday | 2018 | 6
8787 | 2018-06-06 18:17 | 2018-06-06 18:17 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 35 | Rangau fdr#2 Load dropped 109A (121-12A). Not checked yet. |  | 1 | 18:17 | Afternoon | Wednesday | 2018 | 6
8788 | 2018-06-06 18:17 | 20/06/2018 19:11 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 35 | Checked & found, Recloser 23-BD-01 T/R 1x ctr: 331-332. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 18:17 | Afternoon | Wednesday | 2018 | 6
8789 | 2018-07-06 02:23 | 2018-07-06 02:23 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 66 | 02:23 Bangko 13.8 KV OCB-4 (Fdr #4) T/R 1x. Ctr: R/F:\ Bangko fdr #1 load dropped 18A (173-155A). Bangko Fdr #2 drop 88A (257-168A). Bangko Fdr #3 drop 31A (213-182A). Cause : Not checked yet. |  | 1 | 2:23 | Night | Friday | 2018 | 7
8790 | 2018-07-06 02:23 | 2018-09-06 07:36 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 66 | Checked & found, Bangko OCB fdr #4 T/R 1x ctr: 43-44 R/F: 50N. Patrolled the line & found, @1 Flash-over Dead-end Insulator on Pole 24-Y-01. Cause: Lightning. |  | 1 | 2:23 | Night | Friday | 2018 | 7
8791 | 2018-07-06 04:07 | 2018-07-06 04:07 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Animal | 0 | It was reported b/o fuse on pole 04-07-02 D/S C Duri fdr #8. Not checked yet. |  | 1 | 4:07 | Morning | Friday | 2018 | 7
8792 | 2018-07-06 04:07 | 2018-08-06 10:00 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Animal | 0 | Checked & found, @,1, @2 b/o Fuse for 112.5 KVA Tx on Pole 04-07-02. Replaced b/o fuse above with the same size then energized the Tx. Cause: Animal (Monkey). |  | 1 | 4:07 | Morning | Friday | 2018 | 7
8793 | 2018-07-06 09:02 | 2018-07-06 09:02 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Unidentified | 0 | C.Duri 13.8Kv ACB#28 Feeder#16 T/R 1X Ctr:324-325 R/F:51@1@2. Not Patrolled yet. |  | 1 | 9:02 | Morning | Friday | 2018 | 7
8794 | 2018-07-06 09:02 | 2018-12-06 05:43 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:02 | Morning | Friday | 2018 | 7
8795 | 2018-07-06 10:13 | 2018-07-06 10:13 | 13.8KV S. BALAM FEEDER #1 | Fair | Construction Job | 0 | 10:13 Manually opened Recl. 16-Z-25 d/s Balam Fdr#1 Tie in for New Well at So.Balam#440. 14:29 Block & Closed Recl. 16-Z-25 the release the block. Cause: Construction Job. |  | 1 | 10:13 | Morning | Friday | 2018 | 7
8796 | 2018-07-06 10:45 | 2018-07-06 10:45 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 0 | 10:45 Manually open Reclocer.37 -BD- 40 d/s Bekasap Fdr#2 Tie in new well at Bekasap#186. 13:42 Block & Close Reclocer 37-BD-40, then release the block. Cause: Construction Job. |  | 1 | 10:45 | Morning | Friday | 2018 | 7
8797 | 2018-07-06 11:15 | 2018-07-06 11:15 | 13.8KV PETANI FEEDER #1 | Fair | Planned Maintenance | 0 | 11:15 Manually opened Recl. 33-AY-47 d/s Petani Fdr#1 Replace Pin Insulator at Petani #120 12:04 Blocked and Closed Recl. 33-AY-47, then release the block. Cause: Plane Maintenance. |  | 1 | 11:15 | Morning | Friday | 2018 | 7
8798 | 2018-07-06 14:10 | 2018-07-06 14:10 | CENTRAL DURI POWER PLANT |  |  | - | 14:10 S/U CGT#2, then online the Unit at 14:30. |  | 1 | 14:10 | Afternoon | Friday | 2018 | 7
8799 | 2018-07-06 17:28 | 2018-07-06 17:28 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | Rangau fdr#2 Load dropped 97A (111-14A). Not checked yet. |  | 1 | 17:28 | Afternoon | Friday | 2018 | 7
8800 | 2018-07-06 17:28 | 20/06/2018 08:28 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | Checked & found, Recloser 23-BD-01 T/R 3x ctr: 332-335. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:28 | Afternoon | Friday | 2018 | 7
8801 | 2018-08-06 00:36 | 2018-08-06 00:36 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 24 | 5B fdr#1 load dropped 98A (167-69A) Not checked yet. Prod loss : 24 Bbls / 13 wells --> GS #4. Prod loss : 0 --> GS #6. -------------------------------------------------- + Total : 24 Bbls / 13 wells. |  | 1 | 0:36 | Night | Monday | 2018 | 8
8802 | 2018-08-06 00:36 | 13/06/2018 15:22 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 24 | Checked & found RCL 5B -93 T/R 1x, Ctr: 92-93. R/F: 51N Patrolled the Line, found @3 Broken Pin Insulator O/P D-Pole 4B-81 Cause : Lightning |  | 1 | 0:36 | Night | Monday | 2018 | 8
8803 | 2018-08-06 00:49 | 2018-08-06 00:49 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Lightning | 44 | 4B VCB fdr#6 T/R 2x. Not checked yet. |  | 1 | 0:49 | Night | Monday | 2018 | 8
8804 | 2018-08-06 00:49 | 13/06/2018 07:47 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Lightning | 44 | Checked & found, 4B OCB fdr #6 T/R 2x ctr: 181-183 R/F: 50@2. Patrolled the line & found, @2 broken Lightning Arrester on Pole 4B-102. Cause: Lightning. |  | 1 | 0:49 | Night | Monday | 2018 | 8
8805 | 2018-08-06 00:55 | 2018-08-06 00:55 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 7 | 5B OCB fdr#3 T/R 2x. 5B fdr#2 load dropped 142A (166-24A) Not checked yet. |  | 1 | 0:55 | Night | Monday | 2018 | 8
8806 | 2018-08-06 00:55 | 13/06/2018 15:25 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 7 | Checked & found 5B OCB fdr#3 T/R 1x, Ctr: 388-390. R/F : 51N Patrolled the Line, found @1 Broken LA o/p 4C-43 Cause : Lightning |  | 1 | 0:55 | Night | Monday | 2018 | 8
8807 | 2018-08-06 01:06 | 2018-08-06 01:06 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 46 | 6D OCB fdr#1 T/R 1x. 6D fdr#2 load dropped 58A (197-139A). Not checked yet. |  | 1 | 1:06 | Night | Monday | 2018 | 8
8808 | 2018-08-06 01:06 | 13/06/2018 07:34 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 46 | Checked & found, 6D OCB fdr #1 T/R 1x ctr: 331-332 R/F: 51 @2. Patrolled the line & found, @2 broken Dead-end Insulator on Pole 5C-47. Cause: Lightning. |  | 1 | 1:06 | Night | Monday | 2018 | 8
8809 | 2018-08-06 09:46 | 2018-08-06 09:46 | 13.8KV PEMATANG FEEDER #2 | Cloudy | Unidentified | 48 | Pematang OCB fdr#2 T/R 1x Not checked yet. |  | 1 | 9:46 | Morning | Monday | 2018 | 8
8810 | 2018-08-06 09:46 | 16/06/2018 12:29 | 13.8KV PEMATANG FEEDER #2 | Cloudy | Unidentified | 48 | Checked & found, Pematang OCB fdr #2 T/R 2x ctr: 490-492 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:46 | Morning | Monday | 2018 | 8
8811 | 2018-08-06 10:07 | 2018-08-06 10:07 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 0 | 10:07 Manually Opened Balam OCB fdr#1 to CUt Jumperon TOP So.Balam #117 10:17 Manually Block & Closed Balam OCB fdr#1, released the block after finished the Jobs. Cause: Planned Maintenace |  | 1 | 10:07 | Morning | Monday | 2018 | 8
8812 | 2018-08-06 10:35 | 2018-08-06 10:35 | 13.8KV PEMATANG FEEDER #1 | Fair | Construction Job | 0 | 10:35 Manually Opened Pematang OCB fdr#1 due to GS Tank level too High, due Pump T/O 10:59 Manually Closed the Pematang OCB fdr#1, then released the block After the Pump back to normal Cause: Planned construction |  | 1 | 10:35 | Morning | Monday | 2018 | 8
8813 | 2018-08-06 11:15 | 2018-08-06 11:15 | 8 CHARLIE SUBSTATION | Fair | Under investigation | 642 | 11:15 8C C/S TX#2 T/O , Ctr:............., R/F:..... , ------> Closed at 12:11 8C OCB fdr#4 T/O, Ctr: 604-605, R/F: 81 , ------> Closed at 12:17 8C OCB fdr#5 T/O, Ctr: 503-504, R/F: 81 , ------> Closed at 12:18 8C fdr#6 no power (Opened at 11:45) ------> Closed at 12:45 Checked but found, no indication Visually & no Relay Flag appear Manually Closed the Circuit Switcher, then the Feeders as GS#2 requested Manually Opened OCB feeders Below As GS Requested to Maintain Tank Level 11:18 8C OCB fdr#1 M/O ------> Closed at 13:05 11:19 8C OCB fdr#2 M/O ------> Closed at 13:06 11:19 8C OCB fdr#3 M/O ------> Closed at 13:06 11:20 MNS OCB fdr#3 M/O ------> Closed at 12:40 11:21 MNS OCB fdr#4 M/O ------> Closed at 12:40 11:22 8D OCB fdr#3 M/O ------> Closed at 13:49 8C fdr #1 Prod loss : 36 Bbls / 7 wells. 8C fdr #2 Prod loss : 22 Bbls / 8 wells. 8C fdr #3 Prod loss :139 Bbls / 24 wells. 8C fdr #4 Prod loss : 51 Bbls / 11 wells. 8C fdr #6 Prod loss : 78 Bbls / 18 wells. Mns fdr #3 Prod loss : 121 Bbls / 29 wells. Mns fdr #4 Prod loss : 67 Bbls / 10 wells. 8D fdr #3 Prod loss: 69 Bbls / 17 wells. ---------------------------------------------------- + Grand Total : 583 Bbls / 124 wells. Cause : Under Investigation. | 12345 | 1 | 11:15 | Morning | Monday | 2018 | 8
8814 | 2018-08-06 14:28 | 2018-08-06 14:28 | 115KV N. DURI SUBST - DARLING SUB - LINE | Fair | Under investigation | 0 | 14:28 115Kv Line Darling- N.Duri GCG#3 T/O, then Closed at 15:52. 115Kv Line Darling- N.Duri GCG#4 T/O, then Closed at 15:52. 115Kv Line N.Duri-Darling GCG#2 T/O, then Closed at 15:52. 115Kv Tie Line 1 C.Duri GCG#21 T/O, then Closed at 14:49. 115Kv Tie Line 1 C.Duri GCG#23 T/O, then Closed at 14:50. N.Duri 13.8 KV Fdr#1 T/R 1x. N.Duri 13.8 Kv Fdr#2 T/O, then closed at 14:30. Cause: Under Investigation. |  | 1 | 14:28 | Afternoon | Monday | 2018 | 8
8815 | 2018-08-06 15:50 | 2018-08-06 15:50 | MINAS POWER PLANT |  |  | - | Off Line MGT#6, then S/D the unit for S/B. |  | 1 | 15:50 | Afternoon | Monday | 2018 | 8
8816 | 2018-08-06 16:53 | 2018-08-06 16:53 | 13.8KV 4D FEEDER #5 | Fair | Lightning | 47 | 16:53 It was reported no Power at Well 3E-93, 3E-82, 3E-91NP1 (d/s 4D fdr#5) 23:05 Checked & found Rcl: 4D-14A T/SO, Ctr: 50-51 Blocked & closed the Recloser, then relased the block Cause: Not Patrolled yet |  | 1 | 16:53 | Afternoon | Monday | 2018 | 8
8817 | 2018-08-06 16:53 | 13/06/2018 15:23 | 13.8KV 4D FEEDER #5 | Fair | Lightning | 47 | Checked & found Rcl: 4D-14A T/R 1x, Ctr: 50-51, R/F: 51N Patrolled the Line found @1 Broken Pin Insulator O/P 3E-18 Cause : Lightning |  | 1 | 16:53 | Afternoon | Monday | 2018 | 8
8818 | 2018-09-06 02:17 | 2018-09-06 02:17 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 88 | 02:17 It was reported no power o/p 10-J4-19 (N.Duri fdr#2). 05:58 Checked & found Recl. 10-J4-19 T/SO ctr:131. 06:10 Blocked & closed Recl. 10-J4-19, then release the block. Not patrolled yet. |  | 1 | 2:17 | Night | Thursday | 2018 | 9
8819 | 2018-09-06 02:17 | 2018-11-06 15:16 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 88 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 2:17 | Night | Thursday | 2018 | 9
8820 | 2018-09-06 05:49 | 2018-09-06 05:49 | 13.8KV 3D FEEDER #4 | Cloudy | Lightning | 62 | 05:49 3D fdr#4 Load dropped 48A (217-169A). 12:09 It was reported no power at well 1E-53, 1E-52N, 1E-73. 14:20 Checked & found Recl. 2D-44 T/SO Ctr:15-16. Blocked & closed Recl. 2D-44, then release the block. Not patrolled yet. |  | 1 | 5:49 | Morning | Thursday | 2018 | 9
8821 | 2018-09-06 05:49 | 13/06/2018 07:39 | 13.8KV 3D FEEDER #4 | Cloudy | Lightning | 62 | Patrolled the line & found, @1 broken Lightning Arrester on Terminal Pole of Well 1E-53. Cause: Lightning. |  | 1 | 5:49 | Morning | Thursday | 2018 | 9
8822 | 2018-10-06 11:10 | 2018-10-06 11:10 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 5 | It was reported B/O fuse o/p 04-00-08 (CD fdr#8) Not checked yet |  | 1 | 11:10 | Morning | Saturday | 2018 | 10
8823 | 2018-10-06 11:10 | 2018-11-06 14:00 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 5 | Checked & found, @3 b/o Fuse for 112.5KVA Tx on Pole 04-00-08. Replaced b/o Fuse above with the same size, then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 11:10 | Morning | Saturday | 2018 | 10
8824 | 2018-11-06 08:00 | 2018-11-06 08:00 | MINAS POWER PLANT | Fair |  | - | 08:00 MGT#8 S/U then On Line at 08:20 to Back Up CGT#5 being Rebooted the Computer Controller |  | 1 | 8:00 | Morning | Tuesday | 2018 | 11
8825 | 2018-11-06 10:23 | 2018-11-06 10:23 | 13.8KV KETIGUL FEEDER#1 | Fair | Construction Job | 0 | 10:23 Manually Opened LBS 32-AJ-01 (Ketigul fdr#1) for Project TILAN NE. 17:30 Manually Closed the LBS after finished the Jobs Cause: Planned Construction |  | 1 | 10:23 | Morning | Tuesday | 2018 | 11
8826 | 2018-11-06 11:30 | 2018-11-06 11:30 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified (Fuse) | 2 | 11:30 It was reported B?O fuse O/P 05-07-12 (CD fdr#8) Checked & found @1 b/o Fuse for 112.5KVATX. 14:45 Replaced the fuse with same size, then Energized the TX Cause: Unidentified |  | 1 | 11:30 | Morning | Tuesday | 2018 | 11
8827 | 2018-11-06 15:48 | 2018-11-06 15:48 | MINAS POWER PLANT | Fair |  | - | MGT#8 Off Line, then S/D for Stand by |  | 1 | 15:48 | Afternoon | Tuesday | 2018 | 11
8828 | 2018-12-06 04:35 | 2018-12-06 04:35 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 0 | It was reported b/o fuse on pole 11-J2-12A D/S N. Duri fdr #9. Not checked yet. |  | 1 | 4:35 | Morning | Thursday | 2018 | 12
8829 | 2018-12-06 04:35 | 13/06/2018 11:35 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 0 | Replaced @2@3 B/O fuse for 112.5 Kva Tx with the same size. Cause: Animal (Monkey). |  | 1 | 4:35 | Morning | Thursday | 2018 | 12
8830 | 2018-12-06 06:06 | 2018-12-06 06:06 | 13.8KV BATANG FEEDER #3 | Fair | Animal | 29 | Batang OCB Fdr #3 T/R 1x. Batang GFPC T/R 1x. Cause : Not checked yet. |  | 1 | 6:06 | Morning | Thursday | 2018 | 12
8831 | 2018-12-06 06:06 | 20/06/2018 19:13 | 13.8KV BATANG FEEDER #3 | Fair | Animal | 29 | Checked & found, Batang OCB fdr #3 T/R 1x ctr: 361-362 R/F: 51 @1. Patrolled the line & found a Dead Animal (Bird) around Pole toward Well Pemburu #07. Cause: Animal. |  | 1 | 6:06 | Morning | Thursday | 2018 | 12
8832 | 2018-12-06 10:55 | 2018-12-06 10:55 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 0 | 10:55 Manually Opened Rcl 37-BD-40 (d/s BKS fdr#2) to Pop New Well BKS 186 11:20 Manually Block and Closed the Recloser to Posponed the Jobs, due to Local Publick Demontration Cause: Planned Constuction |  | 1 | 10:55 | Morning | Thursday | 2018 | 12
8833 | 2018-12-06 14:15 | 2018-12-06 14:15 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 86 | CKB VCB fdr#5 T/R 1x. Not checked yet |  | 1 | 14:15 | Afternoon | Thursday | 2018 | 12
8834 | 2018-12-06 14:15 | 14/06/2018 14:14 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 86 | Checked & found, CKB VCB fdr #5 T/R 1x ctr: 160-161 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 14:15 | Afternoon | Thursday | 2018 | 12
8835 | 2018-12-06 17:38 | 2018-12-06 17:38 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 17:38 C.Duri Fdr#1 Load dropped 40A (88-44A) It was reported No Power at Puncak Area. 19:27 Checked and found Recl: 39-AV-36 T/SO Counter: 255-256. Blocked and closed Recl: 39-AV-36 --> OK and then released the block. Cause: Not patrolled yet. |  | 1 | 17:38 | Afternoon | Thursday | 2018 | 12
8836 | 2018-12-06 17:38 | 13/06/2018 17:38 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:38 | Afternoon | Thursday | 2018 | 12
8837 | 2018-06-13 15:00 | 2018-06-13 15:00 | 13.8KV PEMATANG FEEDER #2 | Fair | Construction Job | 0 | 15:00 Manually Opened Pematang OCB fdr#2. Tie in New well Pematang #102 & Pematang#103. 16:35 Blocked & closed Pematang OCB fdr#2, then release the block. Cause: Construction Job. |  | 1 | 15:00 | Afternoon | Wednesday | 2018 | 6
8838 | 2018-06-14 09:40 | 2018-06-14 09:40 | 13.8KV 8D FEEDER #3 | Fair | Planned Maintenance | 0 | 09:40 Manually Opened 8D OCB fdr#3. Installed Jumper on TOP well 8D-85. 10:00 Blocked & closed 8D OCB fdr#3, then release the block. Cause: Plan Maintenance. |  | 1 | 9:40 | Morning | Thursday | 2018 | 6
8839 | 2018-06-14 14:48 | 2018-06-14 14:48 | 13.8KV PEMATANG FEEDER #2 | Fair | Low mega-ohm reading | 275 | 14:48 It was reported B/O fuse at well Pematang #75 (Pematang fdr#2). Not checked yet. |  | 1 | 14:48 | Afternoon | Thursday | 2018 | 6
8840 | 2018-06-14 14:48 | 2018-06-15 16:45 | 13.8KV PEMATANG FEEDER #2 | Fair | Low mega-ohm reading | 275 | 16:45 Checked and found @1,@2and@3 b/o fuse for 100Kva Tx at pematang 75 d/s pematang fdr#2 For formed TTR test & Manger, found low Megger Tx Not Replaced yet. |  | 1 | 14:48 | Afternoon | Thursday | 2018 | 6
8841 | 2018-06-14 14:48 | 2018-06-25 13:00 | 13.8KV PEMATANG FEEDER #2 | Fair | Low mega-ohm reading | 275 | Replaced The Low Mega-ohm Reading Tx with the same size then energized the Tx. Cause: Low Mega-ohm Reading Tx |  | 1 | 14:48 | Afternoon | Thursday | 2018 | 6
8842 | 2018-06-14 17:04 | 2018-06-14 17:04 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | C.Duri ACB#13 Fdr#3 T/R 1x Ctr:206-207 R/F:51@2@3. Not Patrolled yet. |  | 1 | 17:04 | Afternoon | Thursday | 2018 | 6
8843 | 2018-06-14 17:04 | 2018-06-19 17:04 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | Checked and found C. Duri fdr #3 T/R 1X ctr:206-207 R/F: 51@2, @3. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:04 | Afternoon | Thursday | 2018 | 6
8844 | 2018-06-14 22:10 | 2018-06-14 22:10 | 13.8KV NORTH DURI FEEDER #2 | Rain | Recloser - Control Recloser | 250 | 22:04 ND fdr#2 Load dropped 24 A (273-249A) Not checked yet |  | 1 | 22:10 | Night | Thursday | 2018 | 6
8845 | 2018-06-14 22:10 | 2018-06-15 02:10 | 13.8KV NORTH DURI FEEDER #2 | Rain | Recloser - Control Recloser | 250 | 02:10 It was reported no power o/p: 10-J4-19. 11:20 Checked and found Recl.: 10-J4-19 T/O. Also found no power at Control Recloser. 11:35 Closed LBS: 10-J4-02, OK (transfer load to N. Duri fdr #7). Cause: Control Recloser. |  | 1 | 22:10 | Night | Thursday | 2018 | 6
8846 | 2018-06-15 03:10 | 2018-06-15 03:10 | 13.8KV CENTRAL DURI FEEDER #1 | Rain | Animal | 900 | 03:10 CD fdr#1 T/R 2x, Ctr: 223-225, R/F: 51G, 51N. 09:00 It was reported no power o/p: 08-L3-20. o/p: 08-L5-22. o/p: 09-L7-02. o/p: 09-M3-01. 11:50 Checked and found Recl.: SBB-07 T/SO ctr: 534-536. 12:05 Blocked and closed the Recloser, but failed. Checked and found b/o fuse for Control reclosing of Recl.: SBB-07. Also found, a Death Animal (Bird) at PT of the Recloser. 12:15 Blocked and closed the Recloser, OK tnen released the block. Casue: Animal (Bird). | 12345 | 1 | 3:10 | Night | Friday | 2018 | 6
8847 | 2018-06-15 03:10 | 2018-06-19 03:10 | 13.8KV CENTRAL DURI FEEDER #1 | Rain | Animal | 900 | C. Duri fdr#1 T/R 2x, Ctr: 223-225, R/F: 51G, 51N. Patrolled the line but found nothing. Cause: Animal (Bird). | 12345 | 1 | 3:10 | Night | Friday | 2018 | 6
8848 | 2018-06-15 10:50 | 2018-06-15 10:50 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 122 | It was reported B/O Fuse o/p 05-N7-14 (s/d CD fdr#14) not checked yet |  | 1 | 10:50 | Morning | Friday | 2018 | 6
8849 | 2018-06-15 10:50 | 2018-06-19 10:50 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 122 | Checked and found @1, @2 b/o fuse for 112.5KVA TX o/p: 05-N7-14. Replaced the b/o fuse above wit same size, then energized the TX.OK. Cause: Animal (Bird). |  | 1 | 10:50 | Morning | Friday | 2018 | 6
8850 | 2018-06-15 14:54 | 2018-06-15 14:54 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 10:54 It was reported b/o fuse o/p TL-2-29. Not checked yet. |  | 1 | 14:54 | Afternoon | Friday | 2018 | 6
8851 | 2018-06-15 14:54 | 2018-06-19 14:54 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified (Fuse) | 0 | Checked and found @2 b/o fuse for 112.5KVA tX o/p TL02-29. Replaced the b/o fuse above with same size, then energized the TX. OK. Cause: Unidentified (fuse). |  | 1 | 14:54 | Afternoon | Friday | 2018 | 6
8852 | 2018-06-15 16:09 | 2018-06-15 16:09 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 33 | Rangau fdr#2 load dropped 109A (121-12A) Not checked yet. |  | 1 | 16:09 | Afternoon | Friday | 2018 | 6
8853 | 2018-06-15 16:09 | 2018-06-20 08:26 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 33 | Checked & found, Recloser 23-BD-01 T/R 2x ctr: 335-337. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:09 | Afternoon | Friday | 2018 | 6
8854 | 2018-06-15 16:50 | 2018-06-15 16:50 | 13.8KV BATANG FEEDER #1 | Cloudy | Animal | 0 | 16:50 Batang 134.8KV OCB fdr #1 T/LO. 18:20 Patrolled the line and found dead Fox to/p Batang #06. (then removed dead FOX). 18:35 Checked and found Batang fdr #1 T/LO ctr:142-146 R/F 51 @1, @2. Blocked and closed Batang fdr #1, OK then released the block. Cause: Animal (FOX). |  | 1 | 16:50 | Afternoon | Friday | 2018 | 6
8855 | 2018-06-15 16:50 | 2018-06-15 16:50 | 13.8KV BATANG FEEDER #2 | Cloudy | Lightning | 0 | Batang 134.8KV OCB fdr #2 T/R. Not checked yet. |  | 1 | 16:50 | Afternoon | Friday | 2018 | 6
8856 | 2018-06-15 16:50 | 2018-06-20 19:15 | 13.8KV BATANG FEEDER #2 | Cloudy | Lightning | 0 | Checked & found, Batang OCB fdr #2 T/R 1x ctr: 165-166 R/F: 51@1. Patrolled the line & found, @1 broken Lightning Arrester on Terminal Pole of well Rantau Bais#10. Cause: Lightning. |  | 1 | 16:50 | Afternoon | Friday | 2018 | 6
8857 | 2018-06-15 16:50 | 2018-06-15 16:50 | 13.8KV BATANG FEEDER #3 | Cloudy | Animal | 13 | Batang fdr #3 load dropped 32A (35-3A). Not checked yet. |  | 1 | 16:50 | Afternoon | Friday | 2018 | 6
8858 | 2018-06-15 16:50 | 2018-06-20 19:16 | 13.8KV BATANG FEEDER #3 | Cloudy | Animal | 13 | Checked & found, Batang OCB fdr #3 T/R 1x ctr: 361-362 R/F: 51 @1. Patrolled the line & found, a Dead Animal (Bird) around Pole toward well Pemburu #07. Cause: Animal. |  | 1 | 16:50 | Afternoon | Friday | 2018 | 6
8859 | 2018-06-15 17:35 | 2018-06-15 17:35 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Animal | 0 | 17:35 It was reported b/o fuse at well Pematang Bow #19. Checked and found @2 b/o fuse for 300KVA TX. Performed TTR test and megger the TX, OK. Replaced the b/o fuse above with same size then energized the TX. Cause: Animal. |  | 1 | 17:35 | Afternoon | Friday | 2018 | 6
8860 | 2018-06-15 18:54 | 2018-06-15 18:54 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified | 556 | 18:59 Ground Fault Alarm at Nella Fdr#1 Nella fdr#1 Load dropped 80A (215-135A) 20:45 It was reported NO power at Nella Field Under Rcl 22-V-01 21:33 Checke3d & found Rcl 22_V-01 T/SO, Ctr: 120-123, R/F: Ground @A Patrolled the Line, but Found Nothing Block & Closed the Recloser, but Fail, Suspected the Recloser was Fail (Control Problem) 23:36 Manually Opened Nella OCB fdr#1 to Ensure Recloser Controller 23:55 Manually Block & CLosed Nella OCB fdr#1. Saturday June 16-2018 00:42 Manually Opened Nella OCB fdr#1. to By Pass the Recloser 22-V-01 00.50 Manually Block & Closed Nella OCB fdr#1, then released the block Cause : Unidentified. | 12345 | 1 | 18:54 | Afternoon | Friday | 2018 | 6
8861 | 2018-06-16 07:43 | 2018-06-16 07:43 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | C. Duri fdr #1 load dropped 17A (99-62A). Not checked yet. |  | 1 | 7:43 | Morning | Saturday | 2018 | 6
8862 | 2018-06-16 07:43 | 2018-06-19 07:43 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | Checked and found Recl.: 41-AW-62 T/R 2X ctr: 273-275 R/F: 51 @2. Patrolled the line and found broken Pin Insulator o/p: 39-AV-22. Cause: Broken Pin Insulator. |  | 1 | 7:43 | Morning | Saturday | 2018 | 6
8863 | 2018-06-17 06:55 | 2018-06-17 06:55 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse o/p 04-07-12 (d/s CD fdr#9) Not checked yet |  | 1 | 6:55 | Morning | Sunday | 2018 | 6
8864 | 2018-06-17 06:55 | 2018-06-19 06:55 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified (Fuse) | 0 | Checked and found @3 b/o fuse for 112.5KVA TX o/p: 04-07-12. Reblaced the b/o fuse above with same size the energized the TX.OK. Cause: Unidentified (fuse). |  | 1 | 6:55 | Morning | Sunday | 2018 | 6
8865 | 2018-06-17 11:31 | 2018-06-17 11:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 11:31 Central Duri 13.8 Kv ACB feeder#1 T/R 1x Ctr:225 - 226 R/F:51N & 51G Cause:Not checed yed |  | 1 | 11:31 | Morning | Sunday | 2018 | 6
8866 | 2018-06-17 11:31 | 2018-06-19 11:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C. Duri fdr #1 T/R 1X ctr: 225-226 R/F: 51G, 51N. Patrolled the line but found nothing. |  | 1 | 11:31 | Morning | Sunday | 2018 | 6
8867 | 2018-06-17 15:59 | 2018-06-17 15:59 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning Arrester | 35 | 15:59 Ground fault alarm from Bangko Fdr#4 Bangko feeder#4 drop 69 A(166-97) Bangko feeder#1 drop 125A(176-51) Cause.Not checed yet. |  | 1 | 15:59 | Afternoon | Sunday | 2018 | 6
8868 | 2018-06-17 15:59 | 2018-06-18 13:42 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning Arrester | 35 | Checked & found, Bangko OCB fdr #4 T/R 1x ctr: 44-45 R/F: 51N. Patrolle the line & found, @1 broken Lightning Arrester on Pole 25-AB-17. Cause: Lightning Arrester. |  | 1 | 15:59 | Afternoon | Sunday | 2018 | 6
8869 | 2018-06-18 01:56 | 2018-06-18 01:56 | 6 DELTA SUBSTATION | Fair | Under investigation | 187 | 01:56 6D 115Kv C/S T/O. 6D 13.8Kv OCB fdr#4 T/O. 6D 13.8Kv OCB fdr#5 T/O. 02:32 Manually Open 6DN OCB fdr#6, then closed at 04:15. 02:35 Checked & found 6D 115Kv C/S T/O Ctr:301-302 R/F:51G, then closed at 03:52. 6D 13.8Kv OCB fdr#4 T/O , then closed at 03:55. 6D 13.8Kv OCB fdr#5 T/O , then closed at 03:56. 02:48 Manually Opened 6D OCB fdr#6, then closed at 03:53. Cause: Under Investigation. |  | 1 | 1:56 | Night | Monday | 2018 | 6
8870 | 2018-06-18 06:03 | 2018-06-18 06:03 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 46 | Ketigul 13.8Kv VCB#1 T/R 1X. Ketigul fdr#2 load dropped 84A (221-137A) Ketigul fdr#3 load dropped 21A (27-6A) Not checked yet. |  | 1 | 6:03 | Morning | Monday | 2018 | 6
8871 | 2018-06-18 06:03 | 2018-06-20 08:19 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 46 | Checked & found Ketigul VCB fdr #1 T/R 1x ctr: 201-202 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:03 | Morning | Monday | 2018 | 6
8872 | 2018-06-18 07:00 | 2018-06-18 07:00 | 13.8KV 3D FEEDER #4 | Cloudy | Unidentified | 203 | 07:00 3D fdr#4 Load ropped 48A 9233-185A). 20:19 It was reported no power at well 1E-53, 1E-52N, 1E-73, 1E-83 (3D fdr#4). 21:25 Checked & found Recl. 2D-44 T/O Ctr:16-17. Blocked & closed Recl. 2d-44, then release the block. Not patrolled yet. |  | 1 | 7:00 | Morning | Monday | 2018 | 6
8873 | 2018-06-18 07:00 | 2018-06-20 08:57 | 13.8KV 3D FEEDER #4 | Cloudy | Unidentified | 203 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:00 | Morning | Monday | 2018 | 6
8874 | 2018-06-19 07:16 | 2018-06-19 07:16 | 13.8KV BANGKO FEEDER #3 | Fair | Animal | 0 | Bangko 13.8KV OCB fdr #3 T/R 1X. Bangko fdr #2 Dropped 139A (260-121A)----->WIP. Bangko fdr #4 Droped 66A (166-100). Bangko fdr #1 Dropped 7A (174-167A). Not checked yet. |  | 1 | 7:16 | Morning | Tuesday | 2018 | 6
8875 | 2018-06-19 07:16 | 2018-06-20 09:34 | 13.8KV BANGKO FEEDER #3 | Fair | Animal | 0 | Checked & found, Bangko OCB fdr #3 T/R 1x ctr: 99945-99946 R/F: 50N. Patrolled the line & found, @1, @2 broken Fuse Cut Out on Pole NN at Bangko Camp. Cause: Animal. |  | 1 | 7:16 | Morning | Tuesday | 2018 | 6
8876 | 2018-06-19 09:00 | 2018-06-19 09:00 | 13.8KV S. BALAM FEEDER #1 | Fair | Animal | 23 | 09:00 It was reported b/o fuse for TX at well Balam #61. 16:00 Checked & found, @3 b/o Fuse for 45KVA Tx at Well Balam #61. Replaced b/o Fuse above with the same size then energized the Tx. Cause: Animal. |  | 1 | 9:00 | Morning | Tuesday | 2018 | 6
8877 | 2018-06-19 10:15 | 2018-06-19 10:15 | 13.8KV DURI FIELD FEEDER #2 | Fair | Planned Maintenance | 0 | 10:15 Manually Open LBS: 06-S7-02, ----->Closed at 11:20. Replaced 112.5KVA TX o/p 06-s7-17. Plan Maintenance. |  | 1 | 10:15 | Morning | Tuesday | 2018 | 6
8878 | 2018-06-19 11:30 | 2018-06-19 11:30 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 0 | 11:30 It was reported b/o fuse o/p: 03-02-36. Checked and found @3 b/o fuse for 112.5KVA TX o/p: 03-02-36. Replaced the b/o fuse above with same size the energized the TX.OK. Cause: Unidentified (fuse). |  | 1 | 11:30 | Morning | Tuesday | 2018 | 6
8879 | 2018-06-19 23:52 | 2018-06-19 23:52 | 13.8KV 8C FEEDER #4 | Fair | Unidentified | 22 | 8C VCB fdr#4 T/R 1x. 8C GFPC Tx-2 T/R 1x. Not checked yet. |  | 1 | 23:52 | Night | Tuesday | 2018 | 6
8880 | 2018-06-19 23:52 | 2018-06-21 07:17 | 13.8KV 8C FEEDER #4 | Fair | Unidentified | 22 | Checked & found, 8C VCB fdr #4 T/R 1x ctr: 137-138 R/F:51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 23:52 | Night | Tuesday | 2018 | 6
8881 | 2018-06-20 06:20 | 2018-06-20 06:20 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 50 | 06:20 It was reported B/O fuse o/p 08-L3-23 (C.Duri fdr#1). 11:10 Checked and found @2, @3 b/o fuse o/p 08-L3-23. Replaced b/o fuse above with the same size and Energized the Tx. Cause: Animal (monkey). |  | 1 | 6:20 | Morning | Wednesday | 2018 | 6
8882 | 2018-06-20 10:45 | 2018-06-20 10:45 | 13.8KV NEW KOTABATAK FEEDER #4 | Fair | Planned Maintenance | 10 | 10:45 Manually opened LBS 37-CU-12 d/s NKBS Fdr #4 due to : Replaced TX at well KB #353. TX: 300 - 350 KVA, Sec. Voltage: 1100 - 2200 V. R/M: 180 - 200 Hp. Wells were off 9 wells. 11:30 Manually Closed LBS 37-CU-12 d/s NKBS Fdr #4. Cause : Plan Maintenance. |  | 1 | 10:45 | Morning | Wednesday | 2018 | 6
8883 | 2018-06-20 15:13 | 2018-06-20 15:13 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Unidentified (Fuse) | 0 | 15:13 It was reported b/o fuse o/p 05-M7-13 d/s CD Fdr #10. 16:00 Checked and found @1 b/o fuse o/p 05-M7-13 d/s CD Fdr #10. Replaced b/o fuse abovewith the same size then energized the Tx. Cause: Un Identified. |  | 1 | 15:13 | Afternoon | Wednesday | 2018 | 6
8884 | 2018-06-21 06:00 | 2018-06-21 06:00 | 13.8KV 3D FEEDER #4 | Fair | Recloser - Control Recloser | 71 | 06:00 3D Fdr #4 Load drop 48A (232-184A). 10:15 Checked & found recloser 2D-44 T/SO Ctr: 17-18. d/s 3D Fdr #4. Blocked & closed recloser 2D-44 ~ ok, and then release the block. Cause: Control Recloser. |  | 1 | 6:00 | Morning | Thursday | 2018 | 6
8885 | 2018-06-21 09:38 | 2018-06-21 09:38 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | 09:38 Manually opened Recloser 16-AA-08 d/s S.Balam fdr #4 due to: Tie In new wll So Balam#331 & Re POP So Balam #409. 17:00 Manually blocked and closed Recloser 16-AA-08 and then released the block. Cause: Construction Job. |  | 1 | 9:38 | Morning | Thursday | 2018 | 6
8886 | 2018-06-21 09:54 | 2018-06-21 09:54 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 0 | 09:54 Manually Open Recloser: 37-BD-40 d/s Bekasap fdr #2. Due to Tie in new well at BKS # 137. Installed TX at well VKS #186. 16:54 Blocked and closed Recloser 37-BD-40, OK then released the block. Cause: Construction Job. |  | 1 | 9:54 | Morning | Thursday | 2018 | 6
8887 | 2018-06-21 10:23 | 2018-06-21 10:23 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 22 | 10:23 Manually Open Recloser: 38-BD-39 d/s Bekasap fdr #2. Replaced Crack FCO well at BKS # 146. 16:54 Blocked and closed Recloser 38-BD-39, OK then released the block. Cause: Plan Maintenance. |  | 1 | 10:23 | Morning | Thursday | 2018 | 6
8888 | 2018-06-21 15:01 | 2018-06-21 15:01 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Post Pin Insulator | 21 | Rokan 13.8KV OCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 15:01 | Afternoon | Thursday | 2018 | 6
8889 | 2018-06-21 15:01 | 2018-03-07 08:01 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Post Pin Insulator | 21 | Checked and found Rokan fdr #2 T/R 1x Ctr: 1265-1266 R/F: 51 @1. Patrolled the line and found Broken Pin Post Insulator o/p 31-AV-26 Cause: Pin Post Insulator. |  | 1 | 15:01 | Afternoon | Thursday | 2018 | 6
8890 | 2018-06-21 16:36 | 2018-06-21 16:36 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 399 | 16:35 4D 13.8KV OCB fdr #2 T/R 1X. 20:40 It was reported no power 15 Wells under 4D fdr#2. (3D-73, 73A, 75, 75N, 86E, 86N, 97, 88, 88N, 67, 74NP1, 88 and 4D-15). 22:15 Checked and found Recl. : 4D-204 T/O ctr: 99 (Not changed). Closed Recl. : 4D-204. OK. Not Patrolled yet. |  | 1 | 16:36 | Afternoon | Thursday | 2018 | 6
8891 | 2018-06-21 16:36 | 2018-06-29 08:10 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 399 | Checked & found 4D OCB fdr#2 T/R 2x, Ctr: 260-262, R/F: 51 Patrolled the Line, found @2 broken dead end and pin O/P 36 DN 12 Cause : Lightning |  | 1 | 16:36 | Afternoon | Thursday | 2018 | 6
8892 | 2018-06-21 19:12 | 2018-06-21 19:12 | KOTABATAK SUBSTATION | Rain and Lightning | Under investigation | 328 | 19:12 OKB 13.8KV OCB fdr #2 T/O (appeared Block while OCB tripped). 19:20 Blocked and Closed OKB 13.8KV OCB fdr #2, OK then released block. Found OKB OCB fdr #2 load still Zero ( no load). 21:20 Checked and found OKB 115KB C/S T/O ctr: 297 R/F: 51G (86T Not real). 22:06 Close OKB 115KB C/S, OK. 22:20 Blocked and closed OKB fdr #2, OK then released the block. Cause: Under investigation. |  | 1 | 19:12 | Night | Thursday | 2018 | 6
8893 | 2018-06-21 19:30 | 2018-06-21 19:30 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 26 | 5B 13.8KV OCB fdr #4 T/R 1X. 5B fdr #1 load dropped 30A (167-137A). 5B fdr #8 load dropped 72A (176-104A) ----->WIP. Not checked yet. |  | 1 | 19:30 | Night | Thursday | 2018 | 6
8894 | 2018-06-21 19:30 | 2018-06-23 07:39 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 26 | Checked & found, 5B OCB fdr #4 T/R 1x ctr: 369-370 R/F: 51. Patrolled the line & found, @1 broken Dead-end Insulator on Pole 4B-146. Cause: Lightning. |  | 1 | 19:30 | Night | Thursday | 2018 | 6
8895 | 2018-06-21 19:33 | 2018-06-21 19:33 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 31 | 3D 13.8KV OCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 19:33 | Night | Thursday | 2018 | 6
8896 | 2018-06-21 19:33 | 2018-06-24 16:55 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 31 | Checked & found, 3D OCB fdr #2 T/R 1x ctr: 260-261 R/F: 51. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 19:33 | Night | Thursday | 2018 | 6
8897 | 2018-06-22 09:45 | 2018-06-22 09:45 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Planned Maintenance | 58 | 09:49 Manually opened recloser 29.CX.05 d/s PTH Fdr #4 due to : Changed out Tx at well PH #27. Tx : 150 - 500 KVA. Sec. voltage : 2250 Volt. R/M : 120 - 400 Hp. 11:10 Manually blocked and closed recloser 29.CX.05 and then release the blocked. Cause : Plan Maintenance. |  | 1 | 9:45 | Morning | Friday | 2018 | 6
8898 | 2018-06-22 14:41 | 2018-06-22 14:41 | 13.8KV 6D FEEDER #6 | Fair | Planned Maintenance | 0 | 14:41 Manually opened 6D OCB Fdr #6 due to : Replaced Pin Insulator o/p 6D-505 near well 6D-334. 15:06 Manually blocked and closed 6D OCB Fdr #6 and then release the blocked. Cause : Plan Maintenance. |  | 1 | 14:41 | Afternoon | Friday | 2018 | 6
8899 | 2018-06-22 15:28 | 2018-06-22 15:28 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 131 | 15:28 Manually opened 8C OCB Fdr #3 due to : Replace Tx at well 8D-47. Tx : 300 KVA. Sec. voltage : 1275 Volt. R/M : 120 Hp. 15:56 Manually blocked and closed 8C OCB Fdr #3 and then release the blocked. Cause : Plan Maintenance. |  | 1 | 15:28 | Afternoon | Friday | 2018 | 6
8900 | 2018-06-23 02:06 | 2018-06-23 02:06 | 13.8KV 3D FEEDER #4 | Fair | Recloser - Control Recloser | 174 | 02:06 3D Fdr #4 Load drop 48A (232-184A). 15:00 Checked & found recloser 2D-44 T/SO Ctr: 18-19. d/s 3D Fdr #4. 15:42 Manually open recloser 2D-14 die to by pass reclosed 2D-44. 15:45 Manually blocked & closed reclosed 2D-14 and then reclosed the block. Cause: Control Reclosed. |  | 1 | 2:06 | Night | Saturday | 2018 | 6
8901 | 2018-06-23 11:29 | 2018-06-23 11:29 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 0 | 11:29 It was reported b/o fuse at Kulim#70 d/s C.Duri fdr#1. Not checked yet. |  | 1 | 11:29 | Morning | Saturday | 2018 | 6
8902 | 2018-06-23 11:29 | 2018-06-24 10:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 0 | Checked & found, @2 b/o fuse for 112.5KVA Tx for Kulin #70 on Pole 40-AV-07. Also found, @2 loose connection on Terminal of TX & Hot line Clamp. (Need to replaced the Tx). Cause: Others. |  | 1 | 11:29 | Morning | Saturday | 2018 | 6
8903 | 2018-06-23 11:29 | 2018-06-25 15:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 0 | Replaced 112.5KVA Tx with the same size for well Kulin #70 then energized the Tx. Cause: Others. |  | 1 | 11:29 | Morning | Saturday | 2018 | 6
8904 | 2018-06-23 15:06 | 2018-06-23 15:06 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 3 | 15:06 It was reported b/o fuse at well Bangko#134 d/s Bangko fdr#1. 15:55 Checked & found @1 & @2 b/o fuse for 300Kv Tx. Perform TTR & Megger found good reading Replace b/o fuse above with the same size & energized the Tx. Cause: Animal (Monkey). |  | 1 | 15:06 | Afternoon | Saturday | 2018 | 6
8905 | 2018-06-23 15:48 | 2018-06-23 15:48 | 44KV NORTH DURI - DUMAI LINE | Fair | Accident | 0 | N.Duri 44Kv GCB#1 T/R 1x. Not checked yet. |  | 1 | 15:48 | Afternoon | Saturday | 2018 | 6
8906 | 2018-06-23 15:48 | 2018-06-24 10:28 | 44KV NORTH DURI - DUMAI LINE | Fair | Accident | 0 | Checked & found, 44KV GCB #44 T/R 1x ctr: 126-127 R/F: 51N @3. Patrolled the line but found nothing. It was reported that outsiders set up a tent & touched powerline on Pole DD 229 at this time. Cause: Accident by outsider. |  | 1 | 15:48 | Afternoon | Saturday | 2018 | 6
8907 | 2018-06-24 06:40 | 2018-06-24 06:40 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Animal | 0 | 06:40 It was reported b/o fuse o/p 03-04-40 d/s CD Fdr#5. 10:05 Checked and found @2, @3 b/o fuse o/p 03-04-40 Perform TTR & Megger good reading. Replaced b/o fuse above with the same size and Energized the Tx. Cause : Animal (Monkey). |  | 1 | 6:40 | Morning | Sunday | 2018 | 6
8908 | 2018-06-24 09:00 | 2018-06-24 09:00 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 261 | 09:00 Manually opened Recloser 22-V-06 d/s Nella Fdr #1 due to reactive well BKO #213. 10:34 Manually blocked and closed reclosed 22-V-06 and then release the blocked. Cause : Plan Maintenance. |  | 1 | 9:00 | Morning | Sunday | 2018 | 6
8909 | 2018-06-24 10:58 | 2018-06-24 10:58 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 38 | 10:59 Manually opened 4D OCB Fdr #2 due to : Replaced @2 broken Fuse Cut Out at well #3D-86Z. 11:33 Manually blocked and closed 4D OCB Fdr #2 and then release the blocked. Cause : Plan Maintenance. |  | 1 | 10:58 | Morning | Sunday | 2018 | 6
8910 | 2018-06-24 15:30 | 2018-06-24 15:30 | 13.8KV 8D FEEDER #2 | Fair | Planned Maintenance | 0 | 15:30 Manually opened 8D OCB Fdr #2 due to : Replaced Transformer at well #8E-45N. 16:00 Manually blocked and closed 8D OCB Fdr #2 and then release the blocked. Cause : Plan Maintenance. |  | 1 | 15:30 | Afternoon | Sunday | 2018 | 6
8911 | 2018-06-24 19:06 | 2018-06-24 19:06 | 13.8KV BATANG GFPC | Fair | Tree | 0 | Batang 13.8 KV GFPC T/R 1x. Batang 13.8 KV fdr #2 load dropped 13A (46-33A). Not checked yet. |  | 1 | 19:06 | Night | Sunday | 2018 | 6
8912 | 2018-06-24 19:06 | 2018-08-07 08:06 | 13.8KV BATANG GFPC | Fair | Tree | 0 | Checked and found GFPC T/R 4x Ctr: 279-283 R/F: 51N @1 @2. Patrolled the line and found high Tree around pole 35-AG-03, 37-AH-11, 36-AG-16. Cause: Tree |  | 1 | 19:06 | Night | Sunday | 2018 | 6
8913 | 2018-06-25 01:55 | 2018-06-25 01:55 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 36 | 8C 13.8KV OCB fdr #6 T/R 1X. 8C fdr #5 Load dropped 200A (237-37A). Not checked yet. |  | 1 | 1:55 | Night | Monday | 2018 | 6
8914 | 2018-06-25 01:55 | 2018-02-07 08:55 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 36 | Checked and found 13.8KV VCB #6 T/R 1x Ctr: 596-597 R/F: 50 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 1:55 | Night | Monday | 2018 | 6
8915 | 2018-06-25 01:55 | 2018-06-25 01:55 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 0 | 8C fdr #3 load dropped 87A (183-96A). Not checked yet. |  | 1 | 1:55 | Night | Monday | 2018 | 6
8916 | 2018-06-25 01:55 | 2018-04-07 01:55 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found Recloser: 8D-18A T/R 1X ctr: 52-53 R/F: 51N. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 1:55 | Night | Monday | 2018 | 6
8917 | 2018-06-25 04:42 | 2018-06-25 04:42 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Unidentified | 60 | Nella GFPC T/R 1X. Nella 13.8 KV Load dropped 108A (215-107A). Not checked yet. |  | 1 | 4:42 | Morning | Monday | 2018 | 6
8918 | 2018-06-25 04:42 | 2018-06-28 07:13 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Unidentified | 60 | Checked & found, Nella VCB fdr #1 T/R 1x ctr: 522-523 R/F: 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 4:42 | Morning | Monday | 2018 | 6
8919 | 2018-06-25 10:40 | 2018-06-25 10:40 | 13.8KV 8D FEEDER #3 | Fair | Planned Maintenance | 20 | 10:40 Manually opened 8D OCB Fdr #3 due to : C/O Transformer at well #8D-87. Tx; 550 KVa, Sec. voltage: 2150 volt. R/M: 375 Hp. 10:57 Manually blocked and closed 8D OCB Fdr #3 and then release the blocked. Cause : Plan Maintenance. |  | 1 | 10:40 | Morning | Monday | 2018 | 6
8920 | 2018-06-25 13:03 | 2018-06-25 13:03 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 254 | 13:03 Manually opened Pematang OCB Fdr #2 due to : C/O Transformer at well Pematang #73 & Pematang #75. Tx; 225-550 KVa/100-150 KVa, Sec.Voltage: volt. R/M: Hp. 14:22 Manually blocked and closed Pematang OCB Fdr #2 and then release the blocked. Cause : Plan Maintenance. |  | 1 | 13:03 | Afternoon | Monday | 2018 | 6
8921 | 2018-06-25 14:58 | 2018-06-25 14:58 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 0 | 14:58 Manually opened recloser 37-BI-01 d/s So Bek Fdr #1 due to : C/O Transformer at well Pematang bow #26. Tx; 150-225 KVa, Sec.Voltage: 1095 volt. R/M: 84-189 Hp. 14:22 Manually blocked and closed recloser 37-BI-01 and then release the blocked. Ctr:1317. Cause : Plan Maintenance. |  | 1 | 14:58 | Afternoon | Monday | 2018 | 6
8922 | 2018-06-25 16:34 | 2018-06-25 16:34 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Duri Community Fdr #1 T/R 1X. Cause: Not checked yet. |  | 1 | 16:34 | Afternoon | Monday | 2018 | 6
8923 | 2018-06-25 16:34 | 2018-03-07 08:34 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | 0 | Checked and found 13.8KV ACB #25 T/R 1x Ctr: 122-123 R/F: 50N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:34 | Afternoon | Monday | 2018 | 6
8924 | 2018-06-25 18:33 | 2018-06-25 18:33 | 115KV MINAS - LUKUT LINE | Fair | Unidentified | 0 | Minas 115Kv GCB#31 T/R 1X. Minas 115Kv GCB#33 T/R 1X. Not checked yet. |  | 1 | 18:33 | Afternoon | Monday | 2018 | 6
8925 | 2018-06-25 18:33 | 2018-05-07 18:33 | 115KV MINAS - LUKUT LINE | Fair | Unidentified | 0 | Checked and found: Minas - Lukut 115Kv GCB#31 T/R 1X ctr: 189-190 R/F: 67N. Minas - Lukut 115Kv GCB#33 T/R 1X ctr: 326-327 R/F: 67N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 18:33 | Afternoon | Monday | 2018 | 6
8926 | 2018-06-26 07:00 | 2018-06-26 07:00 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 0 | DF VCB Fdr #1 T/R 1X. Not checked yet |  | 1 | 7:00 | Morning | Tuesday | 2018 | 6
8927 | 2018-06-26 07:00 | 2018-06-29 08:00 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 0 | Checked and found 13.8KV ACB #41 T/R 1x R/F: 51N Ctr: 696-697 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:00 | Morning | Tuesday | 2018 | 6
8928 | 2018-06-26 09:40 | 2018-06-26 09:40 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | 09:40 Manually opened recloser 16-AA-18 d/s Balam Fdr #4. due to : Tie in new wll Balam #442. 12:00 Manually blocked and closed recloser 16-AA-18 then released the blocked. Cause : Construction job. | 1234 | 1 | 9:40 | Morning | Tuesday | 2018 | 6
8929 | 2018-06-26 10:02 | 2018-06-26 10:02 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 127 | 10:02 Manually opened LBS.5C-59 d/s 6D Fdr #1. due to : Replaced Dead end Insulator o/p 5C-43. Replaced Pin Insulater o/p .................... 11:05 Manually closed LBS.5C-59 Cause : Plant Maintenance. |  | 1 | 10:02 | Morning | Tuesday | 2018 | 6
8930 | 2018-06-26 10:14 | 2018-06-26 10:14 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Unidentified | 331 | 10:14 PTH VCB Fdr #4 T/SO. 10:51 Checked and found PTH VCB Fdr #4 T/O. Counter: 370-371. R/F: 51 @2, @3. Patrolled the line found normal. 11:03 Blocked and closed PTH VCB Fdr #4 then release the block. Cause: Not patrolled yet. |  | 1 | 10:14 | Morning | Tuesday | 2018 | 6
8931 | 2018-06-26 10:14 | 2018-06-29 10:20 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Unidentified | 331 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 10:14 | Morning | Tuesday | 2018 | 6
8932 | 2018-06-26 12:08 | 2018-06-26 12:08 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | N Duri VCB Fdr #5 T/R 1X. Cause: Not checked yet. |  | 1 | 12:08 | Afternoon | Tuesday | 2018 | 6
8933 | 2018-06-26 12:08 | 2018-06-29 08:08 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | Checked and found 13.8KV VCB #5 T/R 1x Ctr: 127-128 R/F: 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 12:08 | Afternoon | Tuesday | 2018 | 6
8934 | 2018-06-26 13:25 | 2018-06-26 13:25 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 38 | 13:25 Manually opened LBS: 37-AQ-07 D/S C Duri fdr #1. Due to changed out Transformer at well Puncak # 30. 14:07 Manually closed LBS: 37-AQ-07. Cause: Plan Maintenance. |  | 1 | 13:25 | Afternoon | Tuesday | 2018 | 6
8935 | 2018-06-26 13:30 | 2018-06-26 13:30 | 13.8KV BEKASAP FEEDER #6 | Fair | Construction Job | 0 | 13:30 Manually opened Recloser: 38-BD-18 D/S Bekasap fdr #6. Due to Installed new Transformer at well Bekasap #187. 16:15 Manually blocked and closed Recloser: 38-BD-18 , and then released the block. Cause: Construction job. |  | 1 | 13:30 | Afternoon | Tuesday | 2018 | 6
8936 | 2018-06-26 14:06 | 2018-06-26 14:06 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 10 | 14:06 Manually opened Recloser: 37-BD-12 D/S Bekasap fdr #2. Due to changed out Transformer at well Bekasap #133. 14:48 Manually blocked and closed Recloser: 37-BD-12 and then released the block. Cause: Plan Maintenance. |  | 1 | 14:06 | Afternoon | Tuesday | 2018 | 6
8937 | 2018-06-26 22:35 | 2018-06-26 22:35 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 7 | It was reported B/O fuse at well Bangko#291 (Bangko fdr#4). Not checked yet. |  | 1 | 22:35 | Night | Tuesday | 2018 | 6
8938 | 2018-06-26 22:35 | 2018-06-27 14:10 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 7 | Replaced @2@3 B/O fuse for 300 Kva Tx with the same size. Cause: Animal (Monkey). |  | 1 | 22:35 | Night | Tuesday | 2018 | 6
8939 | 2018-06-27 01:06 | 2018-06-27 01:06 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 41 | 8D fdr#3 T/R 1X. Not checked yet. |  | 1 | 1:06 | Night | Wednesday | 2018 | 6
8940 | 2018-06-27 01:06 | 2018-02-07 08:06 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 41 | Checked and found 13.8KV OCB #3 T/R 1x Ctr: 222-223 R/F: 51N. Patrolled the line but found nothing. cause: Lightning. |  | 1 | 1:06 | Night | Wednesday | 2018 | 6
8941 | 2018-06-27 01:06 | 2018-06-27 01:06 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 49 | 01:06 8D fdr#1 load dropped 100A (140-40A) 11:05 Checked & found Recl. 8F-05 T/R 1x Ctr: 74-75. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 1:06 | Night | Wednesday | 2018 | 6
8942 | 2018-06-27 14:25 | 2018-06-27 14:25 | 13.8KV LIBO FEEDER #2 | Fair | Construction Job | 0 | 14:25 Manually opened Recl. 23BW02 (Libo fdr#2). Disconnected X0 for 150Kva Tx at well Waduk#14. 14:40 Blocked & Closed Recl. 23BW02, then release the block. Cause: Construction Job. |  | 1 | 14:25 | Afternoon | Wednesday | 2018 | 6
8943 | 2018-06-28 07:00 | 2018-06-28 07:00 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 28 | 07:00 It was reported B/O Fuse At well Rantau Bais #50 (Batang fdr#2) 15:55 Checked & found, Dead monkey on the Bushing, and @1 b/o fuse for 300KVA TX. Took down Replaced the monkeys. Replaced Fuse with the same size, then energized the TX. Cause: Animal |  | 1 | 7:00 | Morning | Thursday | 2018 | 6
8944 | 2018-06-28 11:52 | 2018-06-28 11:52 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 255 | 11:52 Menggala Fdr#1 Load dropped 100A(158-58A) 15:39 Checked and found Recloser: 19-AN-04 T/LO ctr: 615-617 R/F: 51@3. Patrolled the Line, but found nothing. Block and Closed the Recloser, then released the block. Cause: Unidentified. |  | 1 | 11:52 | Morning | Thursday | 2018 | 6
8945 | 2018-06-28 12:40 | 2018-06-28 12:40 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 19 | C.Duri ACB fdr#1 T/R 1x. Not checked yet. |  | 1 | 12:40 | Afternoon | Thursday | 2018 | 6
8946 | 2018-06-28 12:40 | 2018-08-07 12:40 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 19 | Checked and found C.Duri ACB11 fdr#1 T/R 1x ctr: 226 - 227 R/F: 51 @1. Patrol the line but found nothing. Cause: Unidentified. |  | 1 | 12:40 | Afternoon | Thursday | 2018 | 6
8947 | 2018-06-28 14:20 | 2018-06-28 14:20 | 13.8KV S. BALAM FEEDER #1 | Fair | Construction Job | 0 | 14:20 Manually Open SO. Balam OCB fdr#1 Connected T.type Jumper for New Well (WFO-10 P01N1-0-83B) 15:03 Manually Block and Closed the OCB, after finished the Jobs. Cause: Planned Construction. |  | 1 | 14:20 | Afternoon | Thursday | 2018 | 6
8948 | 2018-06-28 15:50 | 2018-06-28 15:50 | 13.8KV 3D FEEDER #3 | Fair | Construction Job | 0 | 15:50 Manually Opened 3D OCB fdr#3 to Replace Switch board to VSD at well 3C-99E 16:07 Manually Block and Closed the OCB, then Released the block after finished the Jobs. Cause: Planned Construction |  | 1 | 15:50 | Afternoon | Thursday | 2018 | 6
8949 | 2018-06-28 23:34 | 2018-06-28 23:34 | 13.8KV MINAS FEEDER #2 | Fair | Recloser - Control Recloser | 0 | 23:34 Minas Fdr #2 Load drop 71A. 00:30 Checked and found Reclose M2-01 T/SO, Ctr : 54-55. Alarm: SGF (Sensitive ground fould). Manually blocked and closed Recloser M2-01 then release the blocked. Cause: Control Recloser. |  | 1 | 23:34 | Night | Thursday | 2018 | 6
8950 | 2018-06-29 08:50 | 2018-06-29 08:50 | MINAS POWER PLANT | Fair | Main breaker | 0 | MGT #11 Trip Off by Alarm Bearing header temperature high due to MCC 480 Volt was Triped Off System Frequency dropped to 59.89 Hz, no Load shedding. Cause: Main Breaker. |  | 1 | 8:50 | Morning | Friday | 2018 | 6
8951 | 2018-06-29 08:59 | 2018-06-29 08:59 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 0 | 08:59 CGT #4 Open Generator Breaker by Alarm Over excitation 09:05 CGT #4 On Line back to System. |  | 1 | 8:59 | Morning | Friday | 2018 | 6
8952 | 2018-06-29 09:26 | 2018-06-29 09:26 | MINAS POWER PLANT |  |  | - | 09:26 MGT #6 S/U, then On line at 11:13 to back up Power. |  | 1 | 9:26 | Morning | Friday | 2018 | 6
8953 | 2018-06-29 11:23 | 2018-06-29 11:23 | CENTRAL DURI POWER PLANT |  |  | - | 11:23 CGT #3 S/U , then On Line at 11:42 to restore power |  | 1 | 11:23 | Morning | Friday | 2018 | 6
8954 | 2018-06-29 14:00 | 2018-06-29 14:00 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | Rangau Fdr#2 Load dropped 100A (127-14A). Not checked yet |  | 1 | 14:00 | Afternoon | Friday | 2018 | 6
8955 | 2018-06-29 14:00 | 2018-08-07 08:00 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | Checed and found Recloser 23-BD-01 T/R 2x Ctr: 337-339 R/F: 51. Patrolled the line but found nothing. Cause: Unidenfied. |  | 1 | 14:00 | Afternoon | Friday | 2018 | 6
8956 | 2018-06-29 16:21 | 2018-06-29 16:21 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 5 | 4D OCB fdr#3 T/R 2x. 4D fdr#2 Load dropped 92A(132-40A) Not checked yet. |  | 1 | 16:21 | Afternoon | Friday | 2018 | 6
8957 | 2018-06-29 16:21 | 2018-03-07 08:21 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 5 | Checked and found 13.8KV OCB #3 T/R 2x Ctr: 246-248 R/F: 51. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 16:21 | Afternoon | Friday | 2018 | 6
8958 | 2018-06-29 17:00 | 2018-06-29 17:00 | MINAS POWER PLANT |  |  | - | 17:00 MGT #6 Off Line, then S/D for Stand by |  | 1 | 17:00 | Afternoon | Friday | 2018 | 6
8959 | 2018-06-30 09:11 | 2018-06-30 09:11 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Planned Maintenance | 0 | 09:11 Manually Opened LBS SD-01 (D.Comm fdr#3) Replaced Broken Dead end insulator o/p 4DD55 @2 & 4DD56 @1 10:48 Blocked the Feeder and Manually Closed the LBS, then released block Feeder. Cause: Planned Maintenance |  | 1 | 9:11 | Morning | Saturday | 2018 | 6
8960 | 2018-06-30 13:28 | 2018-06-30 13:28 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 115 | 13:28 Manualy Opened Recl. 23 BD 01 (Rangau Fdr#2) Replaced 150 KVATX with the same size at well RGU#15 15:24 Manually Block & Closed the Recloser, the released the block After finished the Jobs Cause: Planned Maintenance. |  | 1 | 13:28 | Afternoon | Saturday | 2018 | 6
8961 | 2018-06-30 14:25 | 2018-06-30 14:25 | 13.8KV 5B FEEDER #4 | Fair | Planned Maintenance | 14 | 14:25 Manually Opened 5B OCB fdr#4 Replaced @1 broken Dead end insulator o/p 4B-146 15:45 Manually Block & Closed the OCB, then released the block Cause: Planned Maintenance |  | 1 | 14:25 | Afternoon | Saturday | 2018 | 6
8962 | 2018-06-30 16:05 | 2018-06-30 16:05 | 13.8KV S. BALAM FEEDER #1 | Fair | Construction Job | 0 | 16:05 Manually Opened S.Balam OCB fdr#1 Tie In New Wells S.Blm #433, 414, 376, 358 16:35 Manually block & Closed the OCB, then released the bLock Cause: Planned Construction. |  | 1 | 16:05 | Afternoon | Saturday | 2018 | 6
8963 | 2018-01-07 07:14 | 2018-01-07 07:14 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 57 | Bangko VCB fdr#4 T/R 1x. Bangko fdr#1 Load dropped 91A (158-67A). Bangko GFPC T/R 1x. Fault alarm on fdr#4. Not checked yet. |  | 1 | 7:14 | Morning | Sunday | 2018 | 1
8964 | 2018-01-07 07:14 | 2018-05-07 08:14 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 57 | Checked and found 13.8KV OCB #4 T/R 1x Ctr: 45-46 R/F: 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:14 | Morning | Sunday | 2018 | 1
8965 | 2018-01-07 09:30 | 2018-01-07 09:30 | 13.8KV LIBO FEEDER #2 | Fair | Construction Job | 0 | 09:30 Manually opened Recl. 23BW02 (Libo fdr#2). Tie in new well at Waduk. 12:45 Blocked & closed Recl. 23BW02. then release the block. Cause: Construction Job. |  | 1 | 9:30 | Morning | Sunday | 2018 | 1
8966 | 2018-02-07 11:04 | 2018-02-07 11:04 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 14 | 11:04 Manually Opened Recl. 7D-81 (Minas fdr#3) Replaced @1 Deadend insulator O/P 7D-89 12:10 Manually Block & Closed the Recloser, then Released the block After finished the Jobs Cause: Planned maintenance |  | 1 | 11:04 | Morning | Wednesday | 2018 | 2
8967 | 2018-02-07 13:40 | 2018-02-07 13:40 | 4 DELTA SUBSTATION | Fair | Human Failure | 204 | 13:40 4D 13.8KV OCB fdr#3 T/O, R/F: 81, Ctr: 248-249 4D 115KV C/S TX#1 T/O, R/F: 86T, 87T, Ctr: 1768-1769 4D fdr#1 & #2 no power 14:00 Manually Opened 4D OCB fdr#5, to maintain GS5 tank level Checked & found, PT Indocomas perform Calibration Relay. 15:07 Manually Opened 4D OCB fdr#1, #2 15:13 Manually Closed 4D 115Kv C/S TX#1 15:18 Manually Closed 4D OCB fdr#1 15:26 Manually Closed 4D OCB fdr#2 15:26 Manually Closed 4D OCB fdr#3 15:27 Manually Closed 4D OCB fdr#5 15:00 3D fdr#3 Load dropped 60A(140-80A), GS5 S/D 10 Wells Cause: Human Error. Production Loss : 1. 4D feeder #1 = 0 --> WIP. 2. 4D feeder #2 = 138 Bbls / 25 wells. 3. 4D feeder #3 = 24 Bbls / 11 wells. 4. 4D feeder #5 = 36 Bbls / 10 wells. 5. 3D feeder #3 = 34 Bbls / 9 wells. -------------------------------------------- + Grand total = 232 Bbls / 55 wells. |  | 1 | 13:40 | Afternoon | Wednesday | 2018 | 2
8968 | 2018-02-07 16:51 | 2018-02-07 16:51 | MINAS POWER PLANT |  |  | - | 16:51 MGT #11 S/U, then On line at 17:13 to Back up Power due to CGT#5 Down for Maintance |  | 1 | 16:51 | Afternoon | Wednesday | 2018 | 2
8969 | 2018-02-07 17:00 | 2018-02-07 17:00 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Animal | 0 | It was reported B?O fuse O/P 01-02-27 (CD fdr#3) Not checked yet |  | 1 | 17:00 | Afternoon | Wednesday | 2018 | 2
8970 | 2018-02-07 17:00 | 2018-03-07 17:00 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Animal | 0 | Checked and found @2 b/o fuse for 112.5Kva Tx o/p: 01-02-27. Replaced the b/o fuse above with same size then energized the TX. OK. Cause: Animal (Squirrel). |  | 1 | 17:00 | Afternoon | Wednesday | 2018 | 2
8971 | 2018-02-07 18:00 | 2018-02-07 18:00 | CENTRAL DURI POWER PLANT |  |  | - | 18:00 CGT #5 Off Line then S/D for Maintenance |  | 1 | 18:00 | Afternoon | Wednesday | 2018 | 2
8972 | 2018-03-07 07:58 | 2018-03-07 07:58 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Lightning | 0 | C.Duri ACB fdr#15 T/R 1x, Ctr: 380-381, R/F: Relay Failure Not checked yet |  | 1 | 7:58 | Morning | Wednesday | 2018 | 3
8973 | 2018-03-07 07:58 | 2018-08-07 07:58 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Lightning | 0 | Checked and found C.Duri ACB fdr#15 T/R 1x Ctr: 380-381 R/F: Relay Failure. Patrolled the line and found @1, @2 broken LA O/P 06-Q5-02. Cause: Lightning. |  | 1 | 7:58 | Morning | Wednesday | 2018 | 3
8974 | 2018-03-07 10:30 | 2018-03-07 10:30 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse at well BKO#88 (Nella fdr#1) not checked yet |  | 1 | 10:30 | Morning | Wednesday | 2018 | 3
8975 | 2018-03-07 10:30 | 2018-04-07 08:00 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked and found B/O Fuse @1 o/p BKO-88. Change the Fuse with same size. Cause: Unidentified (Fuse). |  | 1 | 10:30 | Morning | Wednesday | 2018 | 3
8976 | 2018-03-07 10:32 | 2018-03-07 10:32 | 13.8KV NELLA FEEDER #1 | Fair | Powerline - Hot Line Clamp | 6 | It was reported Unbalance voltage at well BKO#23 (Nella fdr#1) Not checked yet |  | 1 | 10:32 | Morning | Wednesday | 2018 | 3
8977 | 2018-03-07 10:32 | 2018-04-07 08:00 | 13.8KV NELLA FEEDER #1 | Fair | Powerline - Hot Line Clamp | 6 | Checked and found Unbalance voltage. Patrolled the line and found Loss connection HLC @1 o/p BKO-23. Cause: Hot Line Clamp. |  | 1 | 10:32 | Morning | Wednesday | 2018 | 3
8978 | 2018-03-07 13:00 | 2018-03-07 13:00 | 13.8KV 6D FEEDER #5 | Fair | Tree | 64 | 13:00 6D OCB fdr5 T/LO, Ctr: 783-787), R/F: 51 @A @C Patrolled the line, found Fall down Tree & Touch the Conductor at @1 @3 O/P toward well 5D-75, Dismantled the Trees 14:33 Manually Block & Closed the OCBs, the released the block Cause: Tree.. |  | 1 | 13:00 | Afternoon | Wednesday | 2018 | 3
8979 | 2018-03-07 13:06 | 2018-03-07 13:06 | 13.8KV MINAS FEEDER #1 | Fair | Lightning | 32 | Minas 13.8KV ACB fdr#1 T/R 1x, Ctr: 78-79, R/F : 51N Not checked yet |  | 1 | 13:06 | Afternoon | Wednesday | 2018 | 3
8980 | 2018-03-07 13:06 | 2018-04-07 13:06 | 13.8KV MINAS FEEDER #1 | Fair | Lightning | 32 | Checked and found Minas 13.8KV ACB fdr#1 T/R 1x Ctr: 78-79 R/F : 51N. Patrolled the line but found nothing. Cause: Lightning Suspected). |  | 1 | 13:06 | Afternoon | Wednesday | 2018 | 3
8981 | 2018-03-07 13:52 | 2018-03-07 13:52 | MINAS SWITCH YARD | Fair | Under investigation | 0 | 13:52 Minas SWY 115KV GCB #35 T/LO, R/F: 87T @123, 50S @123, 86T, Ctr: 115-116 Checked & found, GCB#33 under Serviced by PT indocomas. 17:22 Manually Block & Closed the GCB, then released the block Cause: Under investigation |  | 1 | 13:52 | Afternoon | Wednesday | 2018 | 3
8982 | 2018-03-07 15:56 | 2018-03-07 15:56 | MINAS SWITCH YARD | Fair | Under investigation | 0 | 15:56 MNS SWY 115KV GCB#31 T/LO, R/F: 86L, 21Zone1 @1, 67N, Ctr: 190-194 NO Power to Lukut BOB Checked & found GCB #33 under serviced by PT indocomas 17:14 Manually Block & Closed the GCB, then released the block Cause: Under Investigation |  | 1 | 15:56 | Afternoon | Wednesday | 2018 | 3
8983 | 2018-03-07 16:40 | 2018-03-07 16:40 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Unidentified | 0 | S Balam GFPC T/R 1x Ground fault alarm at S.Blm fdr#1 S.Balam Fdr#1 Load dropped 42A(126-84A) Not checked yet |  | 1 | 16:40 | Afternoon | Wednesday | 2018 | 3
8984 | 2018-03-07 16:40 | 2018-08-07 08:40 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked and found Recloser 16Z-41 T/R 1x Ctr: 3182-3183 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:40 | Afternoon | Wednesday | 2018 | 3
8985 | 2018-03-07 16:40 | 2018-03-07 16:40 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Dead End Insulator | 0 | S Balam GFPC T/R 1x Ground fault alarm at S.Blm fdr#4 S.Balam Fdr#1 Load dropped 92A(191-89A) Not checked yet |  | 1 | 16:40 | Afternoon | Wednesday | 2018 | 3
8986 | 2018-03-07 16:40 | 2018-08-07 08:40 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Dead End Insulator | 0 | Checked and found Recloser 16-Z-57 T/R 1x Ctr: 19-20 R/F: 51N @1. Patrolled the line and found broken Dead End Insulator o/p 16-Y-36. Cause: Dead End Insulator. |  | 1 | 16:40 | Afternoon | Wednesday | 2018 | 3
8987 | 2018-03-07 18:33 | 2018-03-07 18:33 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain and Lightning | Unidentified | 0 | Dumai 4160V VCB Fdr#4 T/R 1x Not checked yet |  | 1 | 18:33 | Afternoon | Wednesday | 2018 | 3
8988 | 2018-03-07 18:33 | 2018-10-07 18:33 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked ad found Dumai 4160V VCB Fdr#4 T/R 2x ctr: 279-281 R/F: none. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 18:33 | Afternoon | Wednesday | 2018 | 3
8989 | 2018-04-07 06:06 | 2018-04-07 06:06 | 13.8KV MINAS FEEDER #3 | Fair | Pin Insulator | 102 | 06:06 Minas ACB #2 (feeder #3) T/R 1x. 06:15 Checked and found Minas ACB fdr #3 T/R 1x ctr: 140-141 R/F: 51@1,@2. 16:00 Patrolled the line found @2 broken Pin Insulator o/p: 7D-104. Cause: Broken Pin Insulator. |  | 1 | 6:06 | Morning | Saturday | 2018 | 4
8990 | 2018-04-07 09:03 | 2018-04-07 09:03 | 13.8KV DARLING VCB FEEDER #6 | Fair | Unidentified | 0 | 09:03 Darling 13.8 KV VCB fdr #6 T/R 1X. Not checked yet. |  | 1 | 9:03 | Morning | Saturday | 2018 | 4
8991 | 2018-04-07 09:03 | 2018-08-07 09:03 | 13.8KV DARLING VCB FEEDER #6 | Fair | Unidentified | 0 | Checked and found Darling 13.8 KV VCB fdr #6 T/R 1X ctr: 230 (not change) R/F: 51G , 51@2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:03 | Morning | Saturday | 2018 | 4
8992 | 2018-04-07 11:04 | 2018-04-07 11:04 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 198 | 11:04 Manualy Opened Recloser 2D 14, -----> Closed at :15:09. ctr:81-82. Replaced Recloser 2D 44 , -----> Closed at : 15:12 . ctr:108-109. Cause: Planned Maintenance. |  | 1 | 11:04 | Morning | Saturday | 2018 | 4
8993 | 2018-04-07 14:24 | 2018-04-07 14:24 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Planned Maintenance | 0 | 11:24 Manualy Opened Petapahan 13.8 KV VCB fdr #3 , -----> Closed at :15:24. Replaced the TX to Swich board at well Petapahan # 77, 76, 129. Cause: Planned Maintenance. |  | 1 | 14:24 | Afternoon | Saturday | 2018 | 4
8994 | 2018-04-07 15:19 | 2018-04-07 15:19 | 13.8KV BEKASAP FEEDER #6 | Fair | Construction Job | 0 | 15:19 Manualy Opened Recloser 37 BE 27 d/s Bekasap fdr #6 , -----> Closed at :17:06. Open HLC to relocated at Bekasap #152. 16:58 Manually Open Bekasap Main fdr #6, ---->Closed at 17:06. To By Pass Recloser 37 BE 27 (Control problem). Cause: Construction Job. |  | 1 | 15:19 | Afternoon | Saturday | 2018 | 4
8995 | 2018-04-07 17:17 | 2018-04-07 17:17 | 13.8KV BEKASAP FEEDER #6 | Fair | Construction Job | 0 | 17:17 Manualy Opened Recloser 1 TL 06, -----> Closed at :17:39. Open HLC to relocated Power line at well Bekasap #72. Cause: Construction Job. |  | 1 | 17:17 | Afternoon | Saturday | 2018 | 4
8996 | 2018-05-07 07:45 | 2018-05-07 07:45 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 20 | 07:45 Libo 13.8 KV OCB fdr #1 T/R 1x. Not Patrolled yet. |  | 1 | 7:45 | Morning | Monday | 2018 | 5
8997 | 2018-05-07 07:45 | 2018-08-07 08:45 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 20 | Checked and found 13.8KV OCB #1 T/R 1x Ctr: 578-579 R/F: 51N @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:45 | Morning | Monday | 2018 | 5
8998 | 2018-05-07 09:46 | 2018-05-07 09:46 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | 09:46 Manually Open So. Balam fdr #4, ----->Closed at 10:49. 15:56 Manually Open So. Balam fdr #4, ----->Closed at 16:12 Tie In 300KVA TX at Balam CMTF. Cause: Construction Job. | 1234 | 1 | 9:46 | Morning | Monday | 2018 | 5
8999 | 2018-05-07 15:31 | 2018-05-07 15:31 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | 15:31 Ground fault alarm from Sintong fdr #2. Sintong fdr #2 load dropped 11A (239-228A). Not checked yet. |  | 1 | 15:31 | Afternoon | Monday | 2018 | 5
9000 | 2018-05-07 15:31 | 2018-08-07 08:31 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Checked and found Recloser 26-AK-24 T/R 1x Ctr: 228-229 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:31 | Afternoon | Monday | 2018 | 5
9001 | 2018-06-07 05:15 | 2018-06-07 05:15 | ROKAN SUBSTATION | Rain | Animal | 72 | 05:15 Rokan 115Kv C/S T/O. 06:30 Checked and found Rokan 115KV C/S T/O ctr: 200-201 R/F: 51T @2, 51@1 & @2. Checked the TX, good condition. Also found dead Squirrel at VR load side. 06:30 Open Rokan fdr #2, and Closed at 07:43. Open Rokan fdr #3, and Closed at 07:41. Open Rokan fdr #4, and Closed at 07:42. Cause: Animal (Civet). |  | 1 | 5:15 | Morning | Thursday | 2018 | 6
9002 | 2018-06-07 09:37 | 2018-06-07 09:37 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 0 | 09:37 Ground fault alarm from S.Balam fdr #1. S.Balam fdr #1 load dropped 23A (129-106A). Not checked yet. |  | 1 | 9:37 | Morning | Thursday | 2018 | 6
9003 | 2018-06-07 09:37 | 2018-12-07 07:22 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 0 | Checked & found, Recloser 16-Z-41 T/R 1x ctr: 3182-3183 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:37 | Morning | Thursday | 2018 | 6
9004 | 2018-06-07 09:47 | 2018-06-07 09:47 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 69 | 09:47 Manually Open LBS: 5C-99, ----->Closed at 11:07. Replaced Dead End Insulator o/p: 5C-47 & 5C-43. Cause: Plan Maintenance. |  | 1 | 9:47 | Morning | Thursday | 2018 | 6
9005 | 2018-06-07 10:19 | 2018-06-07 10:19 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Construction Job | 0 | 10:19 Manually Open Recloser: 29-CX-05, ----->Closed at: 10:54. Replaced transformer at well Petapahan # 12. Cause: Project. |  | 1 | 10:19 | Morning | Thursday | 2018 | 6
9006 | 2018-07-07 09:44 | 2018-07-07 09:44 | 13.8KV S. BALAM FEEDER #4 | Fair | Animal | 30 | 09:44 It was reported b/o fuse at WELL S.Balam #23 d/s S.Balam fdr#4. 16:00 Checked & found @2 b/o fuse for 300 Kva Tx. Replace b/o fuse above with the same size & energized the TX. Cause: Animal (Monkey). |  | 1 | 9:44 | Morning | Saturday | 2018 | 7
9007 | 2018-07-07 10:45 | 2018-07-07 10:45 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Animal | 0 | 10:45 It was reported b/o fuse at o/p 05-P3-14 d/s C.Duri fdr#14. 14:40 Checked & found @2 & @3 b/o fuse for 112.5Kv Tx. Perform TTR & Megger found good reading Replace b/o fuse above with the same size & energized the Tx. Cause: Animal (Monkey). |  | 1 | 10:45 | Morning | Saturday | 2018 | 7
9008 | 2018-07-07 11:29 | 2018-07-07 11:29 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 550 | 11:129 Manually Open Recloser: 21-V-01, ----->Closed at: 14:21. Replaced Recloser 22-V-01 Cause: Project. | 123 | 1 | 11:29 | Morning | Saturday | 2018 | 7
9009 | 2018-07-07 17:26 | 2018-07-07 17:26 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 0 | 17:26 Pinang 13.8 KV OCB fdr #1 T/R 1x. Not Patrolled yet. |  | 1 | 17:26 | Afternoon | Saturday | 2018 | 7
9010 | 2018-07-07 17:26 | 2018-10-07 08:26 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 0 | Checked and found 13.8KV OCB #1 T/R 1x Ctr: 440-441 R/F: 51G. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:26 | Afternoon | Saturday | 2018 | 7
9011 | 2018-07-07 18:18 | 2018-07-07 18:18 | 13.8KV KETIGUL FEEDER#3 | Fair | Switchboard Problem | 4 | 18:18 Ketigul 13.8 KV OCB fdr #3 T/R 1x. Ketigul GFPC T/R 1X Ketigul 13,8 KV OCB fdr #1 Load dropped 41A (123-82A) Ketigul 13,8 KV OCB fdr #2 Load dropped 93A (238-145A) No checked yet. |  | 1 | 18:18 | Afternoon | Saturday | 2018 | 7
9012 | 2018-07-07 22:20 | 2018-07-07 22:20 | 13.8KV ROKAN FEEDER #2 | Fair | Animal | 13 | 22:20 It was reported B/O fuse at well Kopar #38 (Rokan fdr#2) July 08. 2018 00:45 Checked & found @2@3 b/o fuse for 150KVATX Allso found Dead monkey at near the TX Perform TTR & Megger, its good reading Replaced the Fuse with the same size, then energized the TX. Cause: Animal (Monkey) |  | 1 | 22:20 | Night | Saturday | 2018 | 7
9013 | 2018-08-07 11:53 | 2018-08-07 11:53 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 26 | 11:53 Manually Opened Recl. 23 BD 01 (Rangau fdr#2) Replaced 250KVA TX at well Jorang#24 12:23 Manually Block & Closed the Recloser, then released the block After finished the Jobs. Cause: Planned maintenance |  | 1 | 11:53 | Morning | Tuesday | 2018 | 8
9014 | 2018-09-07 07:11 | 2018-09-07 07:11 | 13.8KV RANGAU FEEDER #2 | Fair | Tree | 26 | 07:11 Rangau fdr #2 load dropped 141A (155-14A). Not checked yet. |  | 1 | 7:11 | Morning | Friday | 2018 | 9
9015 | 2018-09-07 07:11 | 18/07/2018 08:11 | 13.8KV RANGAU FEEDER #2 | Fair | Tree | 26 | Checked and found Recloser 23-BD-01 T/R 2x Ctr: 340-342 R/F: 51P @1 Patrolled the line and found tree touch the power line. Cause: Tree. |  | 1 | 7:11 | Morning | Friday | 2018 | 9
9016 | 2018-09-07 08:50 | 2018-09-07 08:50 | 13.8KV NORTH DURI FEEDER #9 | Fair | Recloser - Control Recloser | 0 | 08:50 N. Duri fdr #9 Load Dropped 20A (93-73A). 09:10 It was reported No Power one Road o/p: 11-H5-12. 10:25 Checked and found Recl.: 11-H5-03 T/O (Control Problem). 10:39 Closed LBS: 11-H5-34 to transfer load to d/s N. Duri fdr #10. N. Duri fdr #10 T/SO. 11:25 Checked and found N. Duri fdr #10 T/SO ctr:...... R/F: 51 @1, @2. Blocked and closed N. Duri fdr #10. Ok then release the block. 11:36 Manually Open N. Duri fdr #9, ----->Closed at 11:38. By Pass Recloser: 11-H5-03. Cause: Recloser (Control problem). |  | 1 | 8:50 | Morning | Friday | 2018 | 9
9017 | 2018-09-07 08:58 | 2018-09-07 08:58 | BATANG SUBSTATION | Fair | Powerline - Jumper | 76 | 08:58 Batang 115KV C/S T/O, No power to Batang Substation). 10:42 Checked and found Batang 115KV C/S T/O ctr:..... R/F: 51 @1, @2, @3. Also found @1, @2, @3 burn out Bus fuse Batang fdr #2. (Batang 13.8KV OCB fdr #2 in PM Service) Open Batang fdr #1, ----->Closed at 11:11. Open Batang fdr #3, ----->Closed at 11:14. Open All Burn Out Bus Fuse Batang fdr #2. 11:02 Close Batang 115KV C/S, OK. Patrolled the line under Batang fdr #2, but found nothing. 13:12 Blocked Batang fdr #1. Closed LBS: NN (transfer load Batang fdr #2 to Batang fdr #1). Batang fdr #1 T/O. Open LBS: NN (transfer load Batang fdr #2 to Batang fdr #1). Checked and found Batang 13.8KV OCB fdr #1 T/O ctr: 147-148 R/F: 51@1. Also found Batang GFPC T/R 3X ctr: 283-286. 13:13 Closed Batang fdr #1. OK ctr: 148. 13:42 Open Line Switch T/P: 36 AG 11. Closed LBS: NN (transfer load Batang fdr #2 to Batang fdr #1). Patrolled the line and found @1, @2 broken Jumper toutch Cross Arm O/P: 35 AD 19. Isolated @1, @2 broken Jumper toutch Cross Arm O/P: 35 AD 19. 16:47 Open LBS: NN (transfer load Batang fdr #2 to Batang fdr #1). Closed Both side Isolation Switch Batang OCB fdr #2. 16:54 Blocked Batang fdr #2, OK then released the block ctr: 174. Cause: Broken Jumper. |  | 1 | 8:58 | Morning | Friday | 2018 | 9
9018 | 2018-09-07 09:47 | 2018-09-07 09:47 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Planned Maintenance | 376 | 09:47 Manually Open Recloser: 04-03-02. Replaced TX o/p 04-03-07. Plan Maintenance. |  | 1 | 9:47 | Morning | Friday | 2018 | 9
9019 | 2018-09-07 14:20 | 2018-09-07 14:20 | 13.8KV NORTH DURI FEEDER #9 | Fair | Theft | 0 | It was reported Scondary Cable vandalism o/p: 10-J4A-14. Not checked yet. |  | 1 | 14:20 | Afternoon | Friday | 2018 | 9
9020 | 2018-09-07 14:20 | 2018-10-07 14:20 | 13.8KV NORTH DURI FEEDER #9 | Fair | Theft | 0 | Checked and found Scondary Cable of 112.5KVA TX was Chief o/p: 10-J4A-14. Replaced the Scondary Cablen with New one, then energized the TX. OK. Cause: Thieft. |  | 1 | 14:20 | Afternoon | Friday | 2018 | 9
9021 | 2018-09-07 16:13 | 2018-09-07 16:13 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Fair | Planned Maintenance | 0 | 16:13 Manually Open Dumai 41.6KV VCB fdr #4,---->Closed at 16:51. Replaced Security Light at CPS. Cause: Plan Maintenance. |  | 1 | 16:13 | Afternoon | Friday | 2018 | 9
9022 | 2018-10-07 13:01 | 2018-10-07 13:01 | 13.8KV BATANG GFPC | Fair | Unidentified | 0 | Batang 13.8KV GFPC T/R 1X. Ground fault alarm from Batang fdr #3. No load dropped. |  | 1 | 13:01 | Afternoon | Sunday | 2018 | 10
9023 | 2018-10-07 13:01 | 25/07/2018 08:01 | 13.8KV BATANG GFPC | Fair | Unidentified | 0 | Checked and found 13.8KV GFPC T/R 1x Ctr:173-174 R/F: 51N @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 13:01 | Afternoon | Sunday | 2018 | 10
9024 | 2018-10-07 13:50 | 2018-10-07 13:50 | 13.8KV CENTRAL DURI FEEDER #1 | Drizzle | Animal | 0 | C. Duri 13.8KV fdr #1 load dropped 33A (126-93A). Not checked yet. |  | 1 | 13:50 | Afternoon | Sunday | 2018 | 10
9025 | 2018-10-07 13:50 | 2018-12-07 13:50 | 13.8KV CENTRAL DURI FEEDER #1 | Drizzle | Animal | 0 | Checked and found Recl.: 41-AW-62 T/R 1X ctr: 274-275 E/F: 51 @2. Patrolled the line but found nothing. Cause: Animal (Snake). |  | 1 | 13:50 | Afternoon | Sunday | 2018 | 10
9026 | 2018-10-07 16:42 | 2018-10-07 16:42 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 0 | It was reported b/o fuse o/p: 07-V5-19. Not checked yet. |  | 1 | 16:42 | Afternoon | Sunday | 2018 | 10
9027 | 2018-10-07 16:42 | 2018-12-07 16:42 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 0 | Checked and found @2 b/o fuse for 112.5KVA TX o/p: 07-V5-19. Performed TTR test and Megger the TX, found good. Replaced the b/o fuse with same size, then energized the TX. Cause: Animal. |  | 1 | 16:42 | Afternoon | Sunday | 2018 | 10
9028 | 2018-11-07 07:26 | 2018-11-07 07:26 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Broken Fuse Holder | 0 | D Community ACB#30 (feeder #2) T/R 1x. Not checked yet. |  | 1 | 7:26 | Morning | Wednesday | 2018 | 11
9029 | 2018-11-07 07:26 | 18/07/2018 07:26 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Broken Fuse Holder | 0 | Checked & found Duri Community fdr#2 T/R 1x Ctr:98-99 R/F:51N. Patrolled the line & found @3 Broken Fuse Holder o/p 2F-17B. Cause : Broken Fuse Holder. |  | 1 | 7:26 | Morning | Wednesday | 2018 | 11
9030 | 2018-11-07 10:25 | 2018-11-07 10:25 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 145 | 10:25 Manually opened Recloser 2D-38 D/S 3d fdr#4 Due to replace pin insulator to pin post insulator. Manually blocked & closed Recloser 2D-38 and then released the block. cause : Plan Maintenance. |  | 1 | 10:25 | Morning | Wednesday | 2018 | 11
9031 | 2018-11-07 11:10 | 2018-11-07 11:10 | 13.8KV 4D FEEDER #3 | Fair | Planned Maintenance | 1 | 11:10 Manually opened 4D OCB fdr#3 due to Change out transformer at location 4C-29. 11:40 Manually blocked & closed 4D OCB fdr#3 then released the block. Cause : Plan Maintenance. |  | 1 | 11:10 | Morning | Wednesday | 2018 | 11
9032 | 2018-11-07 14:06 | 2018-11-07 14:06 | 13.8KV DURI FIELD FEEDER #4 | Fair | Planned Maintenance | 1 | 14:06 Manually opened LBS 07-U2-02 D/S DF fdr#4. Due to repair LBS 07-U2-01. 14:40 Manually closed LBS 07-U2-02 Cause : Plan Maintenance. |  | 1 | 14:06 | Afternoon | Wednesday | 2018 | 11
9033 | 2018-11-07 14:38 | 2018-11-07 14:38 | 13.8KV 6DN FEEDER #6 | Fair | Planned Maintenance | 55 | 14:38 Manually opened Recloser 6E-64 D/S 6DN fdr#6 Due to C/O transformer at well 6E-70. 15:16 Manually blocked & closed Recloser 6E-64 and then released the block Cause : Plan Maintenance. |  | 1 | 14:38 | Afternoon | Wednesday | 2018 | 11
9034 | 2018-11-07 15:26 | 2018-11-07 15:26 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 15:26 It was reported b/o fuse O/P 08-L8A-02 D/S C.Duri fdr#1. Not checked yet. |  | 1 | 15:26 | Afternoon | Wednesday | 2018 | 11
9035 | 2018-11-07 15:26 | 2018-12-07 15:26 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked and found @2 b/o fuse for 112.5KVA TX o/p: 08-L8A-02. Performed TTR test and Megger the TX, found good. Replaced the b/o fuse with same size, then energized the TX. Cause: Unidentified. |  | 1 | 15:26 | Afternoon | Wednesday | 2018 | 11
9036 | 2018-12-07 15:40 | 2018-12-07 15:40 | 13.8KV DARLING VCB FEEDER #7 | Cloudy | Unidentified | 0 | Darling VCB fdr #7 T/R 1x. Darling GFPC Tx #2 T/R 1x. Not checked yet. |  | 1 | 15:40 | Afternoon | Friday | 2018 | 12
9037 | 2018-12-07 15:40 | 15/07/2018 09:50 | 13.8KV DARLING VCB FEEDER #7 | Cloudy | Unidentified | 0 | Checked and found Darling VCB fdr #7 T/R 1x Counter: 166-167 R/F: 51N Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 15:40 | Afternoon | Friday | 2018 | 12
9038 | 2018-07-13 10:02 | 2018-07-13 10:02 | 13.8KV ROKAN FEEDER #3 | Fair | Planned Maintenance | 0 | 10:02 Manually opened Rokan VCB fdr #3. Due to PM calibration Relay Bussler on Rokan fdr #3. Manually blocked and closed Rokan VCB fdr #3. Cause: Plan maintenance. |  | 1 | 10:02 | Morning | Friday | 2018 | 7
9039 | 2018-07-13 14:39 | 2018-07-13 14:39 | 13.8KV MINAS FEEDER #1 | Fair | Planned Maintenance | 50 | 14:39 Manually opened LBS 7D-23 d/s Minas Fdr #1. Due to C/O S/B to VSD at well 7D-31. Tx : 300-260 KVA Sec Voltage: 960 Volt. R/M: 60 Hp. 16:16 Manually closed LBS 7D-23. Cause : Plant Maintenance. |  | 1 | 14:39 | Afternoon | Friday | 2018 | 7
9040 | 2018-07-13 15:11 | 2018-07-13 15:11 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Emergency | 0 | 15:11 Manually open Petapahan fdr#3. Maintenance level tank Due to pigging stack at PKM#21. Cause: Emergency. |  | 1 | 15:11 | Afternoon | Friday | 2018 | 7
9041 | 2018-07-13 15:11 | 2018-07-14 13:45 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Emergency | 0 | 13:45 Manually blocked & closed Petapahan fdr#3 then released block. Cause: Emergency. |  | 1 | 15:11 | Afternoon | Friday | 2018 | 7
9042 | 2018-07-13 17:01 | 2018-07-13 17:01 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Emergency | 0 | 15:11 Manually open Petapahan fdr#4. Maintenance level tank Due to pigging stack at PKM#21. Cause: Emergency. |  | 1 | 17:01 | Afternoon | Friday | 2018 | 7
9043 | 2018-07-13 17:01 | 2018-07-14 13:46 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Emergency | 0 | 13:46 Manually open Petapahan fdr#4. Maintenance level tank Due to pigging stack at PKM#21. Cause: Emergency. |  | 1 | 17:01 | Afternoon | Friday | 2018 | 7
9044 | 2018-07-14 06:13 | 2018-07-14 06:13 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Bangko fdr#4 load dropped 83A (183-100A) Bangko GFPC fdr#4 T/R. Not checked yet. |  | 1 | 6:13 | Morning | Saturday | 2018 | 7
9045 | 2018-07-14 06:13 | 2018-07-15 08:13 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Checked and found Recloser 25-Z-07 T/R 1x Ctr: 197-198 R/F: 51N @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:13 | Morning | Saturday | 2018 | 7
9046 | 2018-07-14 14:20 | 2018-07-14 14:20 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Emergency | 0 | 14:20 Manually open OKB fdr#2 Maintenance level tank Due to pigging stack at PKM#21. Cause: Emergency |  | 1 | 14:20 | Afternoon | Saturday | 2018 | 7
9047 | 2018-07-14 17:06 | 2018-07-14 17:06 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Emergency | 0 | 17:06 Manually open OKB fdr#2 Maintenance level tank Due to pigging stack at PKM#21. Cause: Emergency. |  | 1 | 17:06 | Afternoon | Saturday | 2018 | 7
9048 | 2018-07-14 19:18 | 2018-07-14 19:18 | 13.8KV KOTABATAK FEEDER #2 | Fair | Emergency | 0 | 19:18 Manually open OKB fdr#2 Maintenance level tank Due to pigging stack at PKM#21. Cause: Emergency |  | 1 | 19:18 | Night | Saturday | 2018 | 7
9049 | 2018-07-14 19:18 | 2018-07-26 14:06 | 13.8KV KOTABATAK FEEDER #2 | Fair | Emergency | 0 | 14:06 Manually Closed OKB 13.8KV OCB fdr #2. Emergency. |  | 1 | 19:18 | Night | Saturday | 2018 | 7
9050 | 2018-07-15 08:19 | 2018-07-15 08:19 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 77 | 08:19 Bangko fdr#4 load 147A (189-42A). Not checked yet. |  | 1 | 8:19 | Morning | Sunday | 2018 | 7
9051 | 2018-07-15 08:19 | 2018-07-18 08:19 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | 77 | Checked & found Recl. 25Z03 T/R 1x Ctr:198-202. Patrolled the line but found nothing. Cause : Animal. |  | 1 | 8:19 | Morning | Sunday | 2018 | 7
9052 | 2018-07-15 10:00 | 2018-07-15 10:00 | MINAS POWER PLANT |  |  | - | 10:00 Off Line MGT #7 and then S/D the unit . Status: Stand by. |  | 1 | 10:00 | Morning | Sunday | 2018 | 7
9053 | 2018-07-15 10:14 | 2018-07-15 10:14 | 13.8KV 4B FEEDER #1 | Fair | Planned Maintenance | 0 | 10:14 Manually opened Recloser: 3B-18 D/S 4B fdr #1. Changed out Transformer at well 3B-79. 11:10 Manually blocked and closed Recloser: 3B-18 and then released the block. Cause: Plan Maintenance. |  | 1 | 10:14 | Morning | Sunday | 2018 | 7
9054 | 2018-07-15 10:40 | 2018-07-15 10:40 | CENTRAL DURI POWER PLANT |  |  | - | 10:40 S/U CDGT# 5 , and then On Line the unit at 11:08. |  | 1 | 10:40 | Morning | Sunday | 2018 | 7
9055 | 2018-07-15 11:14 | 2018-07-15 11:14 | CENTRAL DURI POWER PLANT |  |  | - | 11:14 Off Line CDGT #4 and then S/D the unit. Status: Stand by. |  | 1 | 11:14 | Morning | Sunday | 2018 | 7
9056 | 2018-07-15 13:56 | 2018-07-15 13:56 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Emergency | 0 | Manually opened CKBS VCB fdr #6. Due to Piging stack on PKM #30. Cause: Emergency. |  | 1 | 13:56 | Afternoon | Sunday | 2018 | 7
9057 | 2018-07-15 22:11 | 2018-07-15 22:11 | 13.8KV MINAS FEEDER #6 | Fair | Lightning | 30 | Minas fdr#6 T/R 1x Ctr:172-173 R/F 51N. Not checked yet. |  | 1 | 22:11 | Night | Sunday | 2018 | 7
9058 | 2018-07-15 22:11 | 2018-07-25 08:11 | 13.8KV MINAS FEEDER #6 | Fair | Lightning | 30 | Checked and found 13.8KV ACB #18 T/R 1x Ctr: 172-173 R/F: 51N @3. Patrolled the line and found broken L/A o/p 7E-54. Cause: Lightning. |  | 1 | 22:11 | Night | Sunday | 2018 | 7
9059 | 2018-07-16 10:23 | 2018-07-16 10:23 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 0 | 10:23 Manually opened Recloser: 37-BD-40 D/S Bekasap OCB fdr #2 Due to Tie in new well Bekasap #190 and #191. 18:15 Manually blocked and closed Recloser:37-BD-40 and then released the block. Cause: Construction Job. |  | 1 | 10:23 | Morning | Monday | 2018 | 7
9060 | 2018-07-17 06:16 | 2018-07-17 06:16 | 13.8KV NORTH DURI FEEDER #9 | Fair | Theft | 0 | It was reported Secondary Cable vandalism o/p: 11-J2-09. Not checked yet. |  | 1 | 6:16 | Morning | Tuesday | 2018 | 7
9061 | 2018-07-17 06:16 | 2018-07-25 06:16 | 13.8KV NORTH DURI FEEDER #9 | Fair | Theft | 0 | Checked & found Missing Secondary cable o/p 11-J2-05 (N.Duri fdr#9). Re-installed secondary cable o/p 11-J2-05. Cause : Theft. |  | 1 | 6:16 | Morning | Tuesday | 2018 | 7
9062 | 2018-07-17 09:26 | 2018-07-17 09:26 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Construction Job | 0 | 09:26 Manually opened Recloser 04-01-02 D/S Central Duri fdr#9. Due to Tie in new wells at Area 4 Road 1 14:15 Manually blocked & closed Recloser: 04- 01-02 and then released the block. Cause : Construction job. |  | 1 | 9:26 | Morning | Tuesday | 2018 | 7
9063 | 2018-07-17 10:59 | 2018-07-17 10:59 | 13.8KV 6D FEEDER #5 | Fair | Planned Maintenance | 84 | 10:59 Manually opened 6D OCB fdr #5. Due to 1. Changed out Transformer at well 5D-67. 2. Replaced Recloser on pole 5D-64. 13:48 Manually blocked and closed 6D OCB fdr #5 and then released the block. Cause: Plan maintenance. |  | 1 | 10:59 | Morning | Tuesday | 2018 | 7
9064 | 2018-07-18 06:05 | 2018-07-18 06:05 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Duri Comy fdr #3 T/R 1x. Not checked yet. |  | 1 | 6:05 | Morning | Wednesday | 2018 | 7
9065 | 2018-07-18 06:05 | 2018-07-22 08:05 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Checked and found 13.8KV ACB #26 T/R 1x Ctr: 78-79 RF: 51N @2. Patrolled the line and found broken Pin Insulator o/p 6F-3. Cause: Pin Insulator. |  | 1 | 6:05 | Morning | Wednesday | 2018 | 7
9066 | 2018-07-18 09:47 | 2018-07-18 09:47 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | C.Duri ACB fdr#14 T/R 1x Ctr:395-396 R/F:51@1@2. Not Patrolled yet. |  | 1 | 9:47 | Morning | Wednesday | 2018 | 7
9067 | 2018-07-18 09:47 | 2018-07-25 09:47 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 9:47 | Morning | Wednesday | 2018 | 7
9068 | 2018-07-18 10:15 | 2018-07-18 10:15 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 10:15 It was reported B/O fuse o/p 07-U3-37 (D.Field fdr#2). 14:30 Replaced @2 B/O fuse for 112.5 Kva Tx with the same size. Cause: Unidentified Fuse. |  | 1 | 10:15 | Morning | Wednesday | 2018 | 7
9069 | 2018-07-19 07:02 | 2018-07-19 07:02 | 13.8KV 3D FEEDER #3 | Fair | Tree | 90 | 07:02 3D fdr#3 T/Lo (RTU failed) 3D fdr#4 load dropped 33A (239-206A) 3D fdr#5 load dropped 66A (100-44A) WIP Pump. 10:50 Checked & Found 3D fdr#3 Ctr: Not change R/F: 51 @1, @2 Patrolled the line found fall down tree o/p Near well 4C-24. 11:20 Blocked & Closed 3D fdr#3, then release the block. Cause: Tree. |  | 1 | 7:02 | Morning | Thursday | 2018 | 7
9070 | 2018-07-19 07:57 | 2018-07-19 07:57 | 13.8KV S. BALAM FEEDER #4 | Fair | Transformer Failure | 297 | 07:57 So.Balam fdr#4 load dropped 57A (187-130A) So.Balam GFPC T/R Ground fault alarm at S.Balam fdr#4 16:30 Checked & found Recloser 16 AB 03 T/O Ctr: 45-456. Patrolled the Line found, Failure 150KVATX at well Balam#300, isolated the TX. Block & Closed The Recloser, then released the block Cause: Transformer Failure |  | 1 | 7:57 | Morning | Thursday | 2018 | 7
9071 | 2018-07-19 14:58 | 2018-07-19 14:58 | NEW PETAPAHAN SUBSTATION | Fair | Planned Maintenance | 0 | Perform Switching to Open 13.8KV Tie Breaker Petapahan Bus, then Supplied by TX#2 & VR#2 14:58 Manually Opened PTH VCB fdr#6, #7, #8 and Bus Tie Breaker (separate from Bus #1) Manually Closed Isolation Switch Load Side of VR#2, to Supply Bus #2. 15:18 Manually Block & Closed PTH VCB fdr#6, #7, #8, then released the Block. Cause: Planned Maintenance |  | 1 | 14:58 | Afternoon | Thursday | 2018 | 7
9072 | 2018-07-19 15:02 | 2018-07-19 15:02 | 13.8KV 6DN FEEDER #2 | Fair | Planned Maintenance | 97 | 15:02 Manually opened 6DN fdr #2. Install Tx 500Kva at well 5D-78. 15:35 Manually blocked and closed 6DN fdr#2 and then released the block. Cause: Planned Maintenance. |  | 1 | 15:02 | Afternoon | Thursday | 2018 | 7
9073 | 2018-07-19 15:05 | 2018-07-19 15:05 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 15:05 It was reported b/o fuse o/p 01-06-20 (D Field#1) Not checked yet. |  | 1 | 15:05 | Afternoon | Thursday | 2018 | 7
9074 | 2018-07-19 15:05 | 2018-07-25 15:05 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Replaced @1 B/O fuse for 112.5Kva Tx with the same size o/p 01-06-20. Cause : Unidentified (Fuse). |  | 1 | 15:05 | Afternoon | Thursday | 2018 | 7
9075 | 2018-07-19 18:18 | 2018-07-19 18:18 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 26 | Ketigul fdr#1 Load dropped 70A(118-48A) Not checked yet |  | 1 | 18:18 | Afternoon | Thursday | 2018 | 7
9076 | 2018-07-19 18:18 | 2018-07-25 08:18 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 26 | Checked and found Recloser 32-AK-16 T/R 1x Ctr: 133-134 R/F: 51N @2. Patrolled the line but found nothing. CAuse: Unidentified. |  | 1 | 18:18 | Afternoon | Thursday | 2018 | 7
9077 | 2018-07-20 09:36 | 2018-07-20 09:36 | NEW PETAPAHAN SUBSTATION | Fair | Planned Maintenance | 63 | 09:36 Preform S/P shut off Petapahan Tx1 and Bus#A. 14:47 Open and close petapahan VCB fdr#2, fdr#3, fdr#4. Dismantle / install MV cable from Bus # A. To change its from single type terminal lug to Disable hole type. Cause: Plan Maintenance. Production loss : 1. Petapahan VCB feeder #2 = 0 --> WIP. 2. Petapahan VCB feeder #3 = 36 Bbls / 1 well. 3. Petapahan VCB feeder #4 = 28 Bbls / 3 wells. ------------------------------------------------------- + Grand total = 64 Bbls / 4 wells. |  | 1 | 9:36 | Morning | Friday | 2018 | 7
9078 | 2018-07-20 15:00 | 2018-07-20 15:00 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 5 | 15:00-15:15 Do Switching to transfer part load Minas fdr#6 to 6DN fdr#6. Dismantle Zig Zag at Mini subst. Cendrawasih Complek. 3 Well S/D during the job (6E-99, 6E-99E, 6E-98). Cause: Plan Maintenance. |  | 1 | 15:00 | Afternoon | Friday | 2018 | 7
9079 | 2018-07-20 19:01 | 2018-07-20 19:01 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | N. Duri VCB fdr #1 T/R 2x. Not checked yet. |  | 1 | 19:01 | Night | Friday | 2018 | 7
9080 | 2018-07-20 19:01 | 2018-07-25 19:01 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found N.Duri fdr#1 T/LO Ctr:291-296 R/F:51@2. Patrolled the line & found @2 Broken LA o/p 12-F9-15. Cause : Lightning. |  | 1 | 19:01 | Night | Friday | 2018 | 7
9081 | 2018-07-21 10:10 | 2018-07-21 10:10 | 13.8KV 6DN FEEDER #5 | Fair | Planned Maintenance | 79 | 10:10 Manually Open LBS 6D-16 (6DN fdr#5). Replaced 500Kva Tx with the same size at well 6D-96E1. Replaced Recl 6D-16A (6DN fdr#5). (S/D 10 wells during the job) 13:20 Closed LBS 6D-16. Cause: Plan Maintenance. |  | 1 | 10:10 | Morning | Saturday | 2018 | 7
9082 | 2018-07-21 22:35 | 2018-07-21 22:35 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Duri Field VCB #51 (feeder #4) T/R 1x. Not checked yet. |  | 1 | 22:35 | Night | Saturday | 2018 | 7
9083 | 2018-07-21 22:35 | 2018-07-29 22:35 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | hecked & found Duri Field fdr#4 T/LO Ctr:529-534 R/F:51@1. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 22:35 | Night | Saturday | 2018 | 7
9084 | 2018-07-22 15:00 | 2018-07-22 15:00 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 9 | It was reported B/O Fuse o/p 06 - Q3 -05 (CDuri Fdr#15). Not checked yet. |  | 1 | 15:00 | Afternoon | Sunday | 2018 | 7
9085 | 2018-07-22 15:00 | 2018-07-25 15:00 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 9 | Replaced @2 B/O fuse for 112.5 Kva Tx with the same size. Cause : Animal. |  | 1 | 15:00 | Afternoon | Sunday | 2018 | 7
9086 | 2018-07-22 17:21 | 2018-07-22 17:21 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | C.Duri ACB fdr#5 T/R 1x Ctr:258-259 R/F:51@2,51N. Not patrolled yet. |  | 1 | 17:21 | Afternoon | Sunday | 2018 | 7
9087 | 2018-07-22 17:21 | 2018-07-29 17:21 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:21 | Afternoon | Sunday | 2018 | 7
9088 | 2018-07-22 18:48 | 2018-07-22 18:48 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 23 | C.Duri ACB fdr#1 T/R 1x, Ctr: 227-228, R/F: 51 @1, 51N. Not checked yet. |  | 1 | 18:48 | Afternoon | Sunday | 2018 | 7
9089 | 2018-07-22 18:48 | 2018-07-25 21:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 23 | Checked & found CD ACB fdr#1 T/R 1x, Ctr: 227 - 228, R/F: 51N Patrolled the line, but found nothing Cause : Unidentified |  | 1 | 18:48 | Afternoon | Sunday | 2018 | 7
9090 | 2018-07-23 07:04 | 2018-07-23 07:04 | 13.8KV DARLING VCB FEEDER #6 | Fair | Unidentified | 0 | Darling VCB fdr#6 T/R 1x. Not checked yet. |  | 1 | 7:04 | Morning | Monday | 2018 | 7
9091 | 2018-07-23 07:04 | 2018-07-29 07:04 | 13.8KV DARLING VCB FEEDER #6 | Fair | Unidentified | 0 | Checked & found Darling VCB fdr#6 T/R 1x Ctr:230(not operated) R/F:51N,@1. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 7:04 | Morning | Monday | 2018 | 7
9092 | 2018-07-23 10:33 | 2018-07-23 10:33 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 90 | 10:33 Manually Opened Rcl. 8D-18A (8C fdr#3) Replaced 150KVA TX with 550KVATX at well 8D-43 10:43 Manually BLock & Closed the recloser, the released the block after finished the Jobs. Cause: Planned Maintenance |  | 1 | 10:33 | Morning | Monday | 2018 | 7
9093 | 2018-07-23 14:06 | 2018-07-23 14:06 | 13.8KV BEKASAP FEEDER #2 | Fair | Planned Maintenance | 36 | 14:06 Manually Opened RCL. 37-BD-12 (Bekasap fdr#2) Replaced 150KVATX with 300KVATX at well BKS#147 14:50 Manually Block & Closed the Recloser, the released the block after finished the jobs Cause: Planned Maintenance |  | 1 | 14:06 | Afternoon | Monday | 2018 | 7
9094 | 2018-07-23 14:40 | 2018-07-23 14:40 | 13.8KV S. BALAM FEEDER #1 | Fair | Construction Job | 0 | 14:40 Manually Opened S Balam VCB fdr#1 Tie In New well S Balam#445 15:53 Manually Block & Closed the Feeder, then released the Block After finished the Jobs Cause: Construction Job |  | 1 | 14:40 | Afternoon | Monday | 2018 | 7
9095 | 2018-07-23 16:00 | 2018-07-23 16:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | 16:00 It was reported B/O fuse O/P 13-G2-03 (Nduri fdr#2) Not checked yet. |  | 1 | 16:00 | Afternoon | Monday | 2018 | 7
9096 | 2018-07-23 16:00 | 2018-07-25 16:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified (Fuse) | 0 | Replaced @2 B/O fuse for 112.5 Kva Tx with the same size. Cause : Unidentified (Fuse). |  | 1 | 16:00 | Afternoon | Monday | 2018 | 7
9097 | 2018-07-23 16:04 | 2018-07-23 16:04 | 13.8KV NELLA FEEDER #1 | Rain | Powerline - Conductor | 1616 | 16:00 Nella VCB fdr#1 T/LO Nella GFPC TX T/LO 17:15 Checked & Found Nella VCB fdr#1 T/LO, Ctr: R/F: 51@1, 51N Patrolled the Line, Found Broken Conductor On Take Off Pole Well BKO#132 18:00 Isolated the broken Conductor O/P 21V. 09 (12 Wells OFF). Block & Closed Nella GFPC TX, then released the block Block & Closed Nella VCB Fdr#1, then released the block Cause: Conductor (broken). Prod loss : 946 Bbls / 73 wells. | 12345 | 1 | 16:04 | Afternoon | Monday | 2018 | 7
9098 | 2018-07-23 16:04 | 2018-07-24 10:38 | 13.8KV NELLA FEEDER #1 | Rain | Powerline - Conductor | 1616 | 10:30 Opened LBS: 21-U-01 D/S Nella fdr #1. Reconnected the broken conductor on pole 21-V-09. 10:38 Closed LBS: 21-U-01. Cause: Broken conductor. Prod loss: 670 Bbls / 74 wells. | 12345 | 1 | 16:04 | Afternoon | Monday | 2018 | 7
9099 | 2018-07-23 16:04 | 2018-07-23 16:04 | 13.8KV NELLA FEEDER #2 | Fair | Normal Condition | 28 | Nella fdr #2 load dropped 43A (75-22A). Not checked yet. |  | 1 | 16:04 | Afternoon | Monday | 2018 | 7
9100 | 2018-07-23 16:04 | 2018-07-26 16:04 | 13.8KV NELLA FEEDER #2 | Fair | Normal Condition | 28 | Checked & found Nella VCB fdr#2 not operated. Patrolled the line but found nothing. Cause : Normal Condition. |  | 1 | 16:04 | Afternoon | Monday | 2018 | 7
9101 | 2018-07-23 16:18 | 2018-07-23 16:18 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 48 | 16:18 It was reported B/O fuse at well Pagar #30 (Ketigul fdr#2) Not checked yet. |  | 1 | 16:18 | Afternoon | Monday | 2018 | 7
9102 | 2018-07-23 16:18 | 2018-07-29 08:18 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 48 | Checked and found Broken Fuse @1 at Pagar #30 Change the Fuse with new one. Cause: Unidentified (Fuse). |  | 1 | 16:18 | Afternoon | Monday | 2018 | 7
9103 | 2018-07-23 17:00 | 2018-07-23 17:00 | CENTRAL DURI POWER PLANT |  |  | - | 17:00 S/U CGT#4, then O/L the unit at 17:25. 17:24 Open Tie Breaker ACB#39. |  | 1 | 17:00 | Afternoon | Monday | 2018 | 7
9104 | 2018-07-23 17:40 | 2018-07-23 17:40 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT#2, then S/D the unit for Maintenance. |  | 1 | 17:40 | Afternoon | Monday | 2018 | 7
9105 | 2018-07-23 19:05 | 2018-07-23 19:05 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Unidentified | 0 | N Duri 44 KV GCB #1 ( N Duri - Dumai ) T/R 1x. Not checked yet. |  | 1 | 19:05 | Night | Monday | 2018 | 7
9106 | 2018-07-23 19:05 | 2018-07-25 19:05 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Unidentified | 0 | Checked and found @1 Duri 44 KV GCB #1 ( N Duri - Dumai ) T/R 1x, counter :058 - 059 R/F:51 Patrol the line but found nothing. Cause: Unidentified. |  | 1 | 19:05 | Night | Monday | 2018 | 7
9107 | 2018-07-24 06:40 | 2018-07-24 06:40 | 13.8KV 8D FEEDER #5 | Fair | Lightning | 19 | 8D OCB fdr#5 T/R 1x. Not Checked yet. |  | 1 | 6:40 | Morning | Tuesday | 2018 | 7
9108 | 2018-07-24 06:40 | 2018-07-29 08:40 | 13.8KV 8D FEEDER #5 | Fair | Lightning | 19 | Checked and found 13.8 KV OCB fdr #5 T/R 1x Ctr: 565-566 R/F: 51 Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 6:40 | Morning | Tuesday | 2018 | 7
9109 | 2018-07-24 06:56 | 2018-07-24 06:56 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 16 | 06:56 Duri Field VCB#51 (feeder #4) T/O. 07:41 Checked & found Duri Field fdr#4 T/LO Ctr:529-534 R/F:51@1@2@3. Patrolled the line but found nothing. 08:25 Blocked & closed Duri Field fdr#4, then release the block. Cause: Unidentified. |  | 1 | 6:56 | Morning | Tuesday | 2018 | 7
9110 | 2018-07-24 11:20 | 2018-07-24 11:20 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified (Fuse) | 0 | It was reported B/O Fuse o/p 05-N3-19 (Darling Fdr#3) Not checked yet |  | 1 | 11:20 | Morning | Tuesday | 2018 | 7
9111 | 2018-07-24 11:20 | 2018-07-26 11:20 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified (Fuse) | 0 | Checked & found, @1, @2 b/o Fuse for 112.5 KVA Tx on Pole 05-N3-19. Replaced b/o fuses above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 11:20 | Morning | Tuesday | 2018 | 7
9112 | 2018-07-24 14:02 | 2018-07-24 14:02 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning Arrester | 467 | 14:02 C.Duri Fdr#1 T/LO Ctr: 228-232 R/F: 51N, 51G. Patrolled the Line Found; - @1 broken LA o/p 41-AW-64 - Recloser 41.AW.62 T/O. - @2 Broken LA On Raiser Pole C.Duri SWY. 17:15 Racked Out Breaker CD ACB fdr#1, then Replaced the Broken LA. 18:30 Racked In Breaker CD fdr#1, then Closed the Breaker. Cause: Lightning Arrester. |  | 1 | 14:02 | Afternoon | Tuesday | 2018 | 7
9113 | 2018-07-24 14:02 | 2018-07-24 14:02 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri ACB fdr#16 T/R 1x Ctr:235-236 R/F:51@1@2. Not Patrolled yet. |  | 1 | 14:02 | Afternoon | Tuesday | 2018 | 7
9114 | 2018-07-24 14:02 | 2018-07-29 14:02 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Patrolled the line & found @1@2 Broken LA o/p 09-N4-10. Cause : Unidentified. |  | 1 | 14:02 | Afternoon | Tuesday | 2018 | 7
9115 | 2018-07-24 14:02 | 2018-07-24 14:02 | 115KV N. DURI SUBST - CD. SW. YARD LINE | Fair | Under investigation | 561 | 14:02 115Kv Line ND-C.Duri GCB#3 T/O. 115Kv Line C.Duri-ND GCB#53 T/R 1x. 115Kv Line C.Duri-ND GCB#55 T/R 1x. CGT#5 Open Generator Breaker, then Closed at 14:25. CGT#4 Open Generator Breaker, then Closed at 14:32. 15:40 Man.Open C.Duri GCB#53, then closed at 15:42. Man.Open C.Duri GCB#55, then closed at 15:43. 15:41 Man. Closed N.Duri GCB#3. Continued Adjust Voltage system. Cause : Under investigation Load dropped Bangko Field & GS Pinang fdr#1 : 7A (100-93A) Prod loss : 7 Bbls / 1 well. Nella fdr#2 : 11A (70 -59A) Prod loss : 36 Bbls / 4 wells. Bangko fdr#1: 20A (168-148A) Prod loss : 48 Bbls / 7 wells. Bangko fdr#3: 44A (240-196) WIP Bangko fdr#4: 70A (180-110A) Prod loss :141 Bbls / 17 wells. Sintong fdr#1: 13A (84-71A) Prod loss : 38 Bbls / 3 wells. Sintong Fdr#2: 121A (264-143A) Prod loss :292 Bbls / 40 wells. Load dropped Balam Field & GS Balam Fdr#1 : 39A (130-91A) Prod loss : 15 Bbls / 7 wells. Balam Fdr#4 : 98A (193-95A) Prod loss : 40 Bbls / 6 wells. Ketigul Fdr#1: 11A (118-110A) Prod loss : 3 Bbls / 1 well. Ketigul Fdr#2: 139A (241-202A) Prod loss :169 Bbls / 6 wells. Ketigul Fdr#3: 17A (368-190A) Load dropped Bekasap Field & GS Bekasap Fdr#3: 17A (36-19A) Prod loss : 0. Bekasap Fdr#6: 19A (196-177A) Prod loss : 0. Load dropped Pematang Field & GS Pematang Fdr#1: 63A(93-71A) Prod loss : 49 Bbls / 14 wells. Pematang Fdr#2: 9A (84-75A) Prod loss : 68 Bbls / 17 wells. Load dropped Petani Field & GS Petani Fdr#1 : 18A (250-232A) Prod loss : 16 Bbls / 1 well. Petani Fdr#2 : 10A (70-60A) Prod loss : 16 Bbls / 1 well. Load dropped MNS Field Area#1 & GS 8D Fdr#8 : 59A (184-125A) Prod loss : 0. 8D Fdr#9 : 52A (119-157A) Prod loss : 0. 8C Fdr#1 : 8A (318-210A) Prod loss : 0. Load dropped MNS Field Area#6 & GS 4B Fdr#1 : 15A (132-117A) Prod loss : 16 Bbls / 1 well. ---------------------------------------------------------------------------- + Grand Total = 954 Bbls / 126 wells. | 12345 | 1 | 14:02 | Afternoon | Tuesday | 2018 | 7
9116 | 2018-07-25 00:13 | 2018-07-25 00:13 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 0 | Batang 13.8Kv OCB fdr#2 T/R 1x. Batang GFPC T/R Not checked yet. |  | 1 | 0:13 | Night | Wednesday | 2018 | 7
9117 | 2018-07-25 00:13 | 2018-07-29 08:13 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked and found Batang fdr #2 T/R 1x Ctr: 174-175 R/F: 51 @1 Patrolled the line and found broken L/A o/p Rantau Bais @10. Cause: Lightning Arrester. |  | 1 | 0:13 | Night | Wednesday | 2018 | 7
9118 | 2018-07-25 05:09 | 2018-07-25 05:09 | 13.8KV NORTH DURI FEEDER #1 | Heavy Rain | Unidentified (L/A) | 0 | 05 09 N.Duri VCB fdr#1 T/R 1x 08:00 Checked & found N.Duri VCB fdr#1 T/R 1x, Ctr: 195-196, R/F: 51 @1@2@3 Patrolled the Line, found @1@2@3 Broken Bushing Recloser O/P 12 G2 02 Open & Closed LBS 12 G2 40, to Isolate Rcl. 12 G2 02. Cause : Unidentified (L/A) |  | 1 | 5:09 | Morning | Wednesday | 2018 | 7
9119 | 2018-07-25 05:09 | 2018-07-25 05:09 | 13.8KV NORTH DURI FEEDER #6 | Heavy Rain | Lightning Arrester | 228 | 05:09 N.Duri 13.8Kv VCB fdr#6 T/O. 06:12 Blocked and Closed N Duri fdr #6. OK. 06:15 N Duri fdr #6 Tripped again. 06:12 Checked and found N Duri fdr #6 T/LO ctr:300-305 R/F: 51 @1, @2 and 51N. 08:00 Patro;;ed the line and found Broken all Bushing for Recl: 12-G2-02. Un Plug and isolated Recl: 06-G2-02. 08:08 Blocked and closed N. Duri fdr #6. OK. then released the block. Continued to patrol the line and found Recl: 12-F5-02 T/SO ctr: 77-78. Also fpound @2 Broken LA o/p: 12-F5-18 and @3 broken LA o/p: 12-F5-21. 08:22 Blocked and closed Recl: 12-F7-02. OK then released the block. Continued to patrol the line and found Recl: 12-F5-02 T/LO ctr: 83-87 R/F: 52 @1. Also fpound @3 Broken LA o/p: 12-F7-27 and o/p: 12-F7-31. 08:30 Blocked and closed Recl: 12-F7-02. OK then released the block. Also found @1 Broken LA o/p: 12-F7-23. Cause: Broken LA. |  | 1 | 5:09 | Morning | Wednesday | 2018 | 7
9120 | 2018-07-25 05:09 | 2018-07-25 05:09 | 13.8KV NORTH DURI FEEDER #8 | Heavy Rain | Unidentified | 0 | 05:09 N.Duri 13.8Kv fdr#8 load dropped 20A (64-44A) N.Duri GFPC T/R. 21:05 Checked & found N.Duri fdr#8 T/R 1x Ctr:89 (Not operated) R/F:51@1. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 5:09 | Morning | Wednesday | 2018 | 7
9121 | 2018-07-25 05:09 | 2018-07-25 05:09 | 13.8KV NORTH DURI FEEDER #2 | Heavy Rain | Unidentified | 0 | 09:03 N.Duri fdr#2 load dropped 65A (258-193A) 21:09 Checked & found N.Duri fdr#2 T/R 1x Ctr:304-305 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 5:09 | Morning | Wednesday | 2018 | 7
9122 | 2018-07-25 05:10 | 2018-07-25 05:10 | 13.8KV NORTH DURI FEEDER #5 | Heavy Rain | Unidentified | 0 | 05:10 N.Duri 13.8Kv VCB fdr#5 T/R 1x. 21:10 Checked & found N.Duri fdr#5 T/R 1x Ctr:128-129 R/F:51@3. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 5:10 | Morning | Wednesday | 2018 | 7
9123 | 2018-07-25 08:14 | 2018-07-25 08:14 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Recloser - Control Recloser | 35 | 08:14 C. Duri fdr #14 load dropped 25A (124-99A). 09:08 It was reported no power o/p: 06-R3-16. 11:00 Checked and found Recl: 06-Q2-02 T/SO ctr: 47-48. Blocked and closed the Recloser, but failed. Un Plug and isolated the Recloser. 11:25 Open Recloser 06-R3-19, ----->Closed at 11:35. 11:27 Closed LBS: 06-R4-02 (Transfer load to D. Field fdr #4). Cause: Control Recloser (Mul function). |  | 1 | 8:14 | Morning | Wednesday | 2018 | 7
9124 | 2018-07-25 13:32 | 2018-07-25 13:32 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | 13:32 It was reported No power o/p: 06-S1-23 and o/p: 06-R8=04. 14:30 Checked and found Recl: 06-R3-23 T/SO ctr: 93-94. Blocked and Closed Recl: 06-R3-23, Ok then released the block. Cause: Unidentified. |  | 1 | 13:32 | Afternoon | Wednesday | 2018 | 7
9125 | 2018-07-25 13:33 | 2018-07-25 13:33 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified | 38 | 13:33 Ground fault alarm from Nella fdr #1. Nella fdr #1 load dropped 62A (201-139A). Not checked yet. |  | 1 | 13:33 | Afternoon | Wednesday | 2018 | 7
9126 | 2018-07-25 13:33 | 2018-07-26 13:33 | 13.8KV NELLA FEEDER #1 | Fair | Unidentified | 38 | Checked and found Recloser 22-V-01 T/R 1x Ctr: 131-132 R/F: 51N @1 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 13:33 | Afternoon | Wednesday | 2018 | 7
9127 | 2018-07-26 05:25 | 2018-07-26 05:25 | CENTRAL KOTABATAK SUBSTATION | Fair | Powerline - Jumper | 44 | 05:25 CKBS 115 KV C/S TX-1 T/O. 06:45 Checked & found CKBS 115 KV C/S TX-1 T/O, ctr:144-145, r/f:51G. Checked TX-2 normal condition. Opened CKBS fdr#1. 06:47 Closed CKBS 115 KV C/S TX-1.,ok. 06:50 Bloked & Closed CKBS fdr #1, but CKBS 115 KV C/S TX-1 T/O, ctr:145-146, r/f:51G. Opened CKBS VCB fdr #1. 06:54 Closed CKBS 115 KV C/S TX-1, ok. 10:12 Patrolled the line and found @2 broken jumper of FCO at well KB #324. 10:24 Blocked & Closed CKB 13.8 KV fdr #1 and then release the blocked, ok. Cause: Jumper |  | 1 | 5:25 | Morning | Thursday | 2018 | 7
9128 | 2018-07-26 08:51 | 2018-07-26 08:51 | 13.8KV LIBO FEEDER #2 | Fair | Construction Job | 0 | 08:51 Manually opened Recloser 23-BW-02 D/S Libo Duri fdr#2. Relocacated Power line at well HitamP-02. 09:47 Manually blocked & closed Recloser: 23- BW-02 and then released the block. Well off during the job location Hitam #01, Hitam #02, Hitam #03. Cause : Construction job. |  | 1 | 8:51 | Morning | Thursday | 2018 | 7
9129 | 2018-07-26 09:16 | 2018-07-26 09:16 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Construction Job | 0 | 09:16 Manually opened Recloser 04-04-22 D/S Central Duri fdr#8. Replaced 112.KVA TX to 150 KVA TX at well 04-04-14, 04-04-07A, 04-04-13B, 04-04-18A. 15:18 Manually blocked & closed Recloser: 04- 04-22 and then released the block. Cause : Construction job. |  | 1 | 9:16 | Morning | Thursday | 2018 | 7
9130 | 2018-07-26 10:24 | 2018-07-26 10:24 | 13.8KV DURI FIELD FEEDER #1 | Fair | Planned Maintenance | 0 | 10:24 Manually opened LBS 01-05-01A d/s Duri Field fdr#1. Replaced by pass Recloser 01-05-01. Cutting Jumper o/p: 01-05-32. 10:51 Manually blocked & closed LBS 01-05-01 d/s Duri Field fdr#1 then released the block. Cause : Plan Maintenance. |  | 1 | 10:24 | Morning | Thursday | 2018 | 7
9131 | 2018-07-26 10:24 | 2018-07-27 16:05 | 13.8KV DURI FIELD FEEDER #1 | Fair | Planned Maintenance | 0 | 16:05 Manually Open LBS: 01=-05-01, ---->Closed at 16:40. Re Connected Jumprt o/p: 01-05-32. Cause: Plan Maintenance. |  | 1 | 10:24 | Morning | Thursday | 2018 | 7
9132 | 2018-07-26 10:28 | 2018-07-26 10:28 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 6 | Sintong 13.8KV fdr #2 load dropped 174A (223-49A). Sintong 13.8 KV fdr #1 load dropped 10A (82-72A). Not checked yet. |  | 1 | 10:28 | Morning | Thursday | 2018 | 7
9133 | 2018-07-26 10:28 | 2018-07-29 10:28 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 6 | Checked & found Recl. 28AF17 T/R 1x Ctr:455-457 R/F:51N. Recl. 25AD26 T/R 1x Ctr:122-123 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 10:28 | Morning | Thursday | 2018 | 7
9134 | 2018-07-27 00:25 | 2018-07-27 00:25 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 87 | 00:25 Sintong VCB fdr#2 T/R 1x. SIntong GFPC T/R 1x. Ground fault at Sintong fdr#2 16:00 Checked and found Sintong 13.8KV VCB fdr #2 T/R 1 X ctr: 473-474 R./F: 51N. patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 0:25 | Night | Friday | 2018 | 7
9135 | 2018-07-27 16:18 | 2018-07-27 16:18 | 13.8KV BANGKO FEEDER #4 | Cloudy | Animal | 42 | 16:18 Bangko 13.8KV OCB fdr #4 T/R 1X. Bangko fdr #1 load dropped 125A (163-38A). Nella fdr #1 load dropped 12A (212-200A). Nella fdr #2 load dropped 21A (74-53A). Not checked yet. |  | 1 | 16:18 | Afternoon | Friday | 2018 | 7
9136 | 2018-07-27 16:18 | 2018-07-28 16:18 | 13.8KV BANGKO FEEDER #4 | Cloudy | Animal | 42 | Checked and found Bangko fdr #4 T/R 1X ctr: 46-49 R/F: 51N. Patrolled the line and found @1, @2 b/o fuse for 150KVA TX at well Bangko #269. Also found Dead Monkey at well Bangko #269. Cause: Animal (Monkey). |  | 1 | 16:18 | Afternoon | Friday | 2018 | 7
9137 | 2018-07-27 16:18 | 2018-07-27 16:18 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Unidentified | 0 | S.Balam Fdr#4 Load dropped 32A (187-15A) Not checked yet |  | 1 | 16:18 | Afternoon | Friday | 2018 | 7
9138 | 2018-07-28 06:10 | 2018-07-28 06:10 | 13.8KV MINAS FEEDER #6 | Cloudy | Lightning | 42 | Minas ACB fdr#6 T/R 1x Ctr:173-174 R/F:51N. Not patrolled yet. |  | 1 | 6:10 | Morning | Saturday | 2018 | 7
9139 | 2018-07-28 06:10 | 2018-02-08 08:10 | 13.8KV MINAS FEEDER #6 | Cloudy | Lightning | 42 | Checked and found 13.8KV ACB #18 T/R 1x Ctr: 279-280 R/F: 51N. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 6:10 | Morning | Saturday | 2018 | 7
9140 | 2018-07-28 08:58 | 2018-07-28 08:58 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Duri Field 13.8Kv ACB#52 (fdr#3) T/R Not checked yet. |  | 1 | 8:58 | Morning | Saturday | 2018 | 7
9141 | 2018-07-28 08:58 | 2018-07-29 08:58 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 0 | Checked & found Duri Field fdr#3 T/R: 1x Ctr:371-372 R/F:51@1. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 8:58 | Morning | Saturday | 2018 | 7
9142 | 2018-07-28 10:10 | 2018-07-28 10:10 | 13.8KV BANGKO FEEDER #1 | Fair | Animal | 38 | 10:10 It was reported b/o fuse at well Bangko#269 D/S Bangko fdr#4. 10:30 Checked and found @1, @2 b/o fuse for 150KVA TX at well Bangko #269. Performed TTS test and Megger the TX. OK. Replaced b/o fuse above with same size, then energized the TX. OK. Cause: Animal (Monkey). |  | 1 | 10:10 | Morning | Saturday | 2018 | 7
9143 | 2018-07-28 11:14 | 2018-07-28 11:14 | 13.8KV NORTH DURI FEEDER #7 | Fair | Animal | 14 | 11:14 It was reported b/o fuse o/p 10-K2-11 D/S N.Duri fdr#7. Not checked yet. |  | 1 | 11:14 | Morning | Saturday | 2018 | 7
9144 | 2018-07-28 11:14 | 2018-04-08 15:50 | 13.8KV NORTH DURI FEEDER #7 | Fair | Animal | 14 | Checked and found @1 burnt out fuse o/p 10-K2-11. Replaced b/o fuse above with the same size and energized the Tx. Cause : Animal (Monkey). |  | 1 | 11:14 | Morning | Saturday | 2018 | 7
9145 | 2018-07-28 12:30 | 2018-07-28 12:30 | 13.8KV LIBO FEEDER #2 | Fair | Construction Job | 0 | 12:30 Manually opened Recloser 23-BW-02, Closed at:12:49. Closed by pass Recloser 23-BW-41 (after relocated Power line at well Hitam P-02) Well off during the job, Hitam #01, #02, #03. Cause : Plan Maintenance. |  | 1 | 12:30 | Afternoon | Saturday | 2018 | 7
9146 | 2018-07-28 13:45 | 2018-07-28 13:45 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Planned Maintenance | 0 | 13:45 Manually open Duri Commy fdr#3. Rack out Duri Commy fdr#3. 16:30 Isolated recloser 2F 07 then Closed by pass switch. Rack in Duri Commy fdr#3. 16:40 Close Duri Commy fdr#3 Ctr: 79-80. (Cancel all Maintenance job for investigation). Cause : Plain maintenance. |  | 1 | 13:45 | Afternoon | Saturday | 2018 | 7
9147 | 2018-07-28 14:08 | 2018-07-28 14:08 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Recloser | 0 | 14:08 Duri Commy 13.8KV ACB#25 fdr#1 T/LO Ctr:124-126 R/F :......... 14:38 Patrolled the line and found LBS 1F-25 close. (Talang and Louser Camp till Recl: 6F7 de feed from Duri Community fdr #1) Open LBS 1F-25. 14:40 Close Duri Commy fdr#1, OK. Cause : Under Investigation. |  | 1 | 14:08 | Afternoon | Saturday | 2018 | 7
9148 | 2018-07-28 14:08 | 2018-07-29 08:08 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Recloser | 0 | Checked and found 13.8 KV ACB #25 T/O Ctr: 124-126 R/F: 51N Ptrolled the line and found @3 Burnt Out Bushing of Recloser o/p 6F-07 Cause: Recloser. |  | 1 | 14:08 | Afternoon | Saturday | 2018 | 7
9149 | 2018-07-29 09:38 | 2018-07-29 09:38 | 230KV NORTH DURI SWITCH YARD | Fair | Under investigation | 0 | 09:38 N.D uri 230Kv GCB#15 T/O. N. Duri 230Kv GCB#25 T/O. N .Duri 230Kv GCB#35 T/O. N. Duri 230Kv GCB#41 T/O. N.Duri 115Kv GCB# 3 T/O. 10:56 Checked and found N. Duri TX-5 Condition. OK R/F: 86 (GCB #43). Also found: N. Duri 230Kv GCB#15 T/O ------->Close at 10:59. N. Duri 230Kv GCB#25 T/O ------->Close at 11:01. N. Duri 230Kv GCB#35 T/O ------->Close at 11:28. N. Duri 230Kv GCB#41 T/O ------->Close at 11:40. N. Duri 230Kv GCB#43 Close, then Open at 10:58. N. Duri 115Kv GCB# 3 T/O ------->Close at 12:06. C. Durii 115Kv GCB# 53 Closed. C. Durii 115Kv GCB# 53 Closed. 11:42 Manually open 115Kv C.Duri to N.Duri GCB#53 ----->Close at 12:31. 11:43 Manually open 115Kv C.Duri to N.Duri GCB#55 ----->Close at 12:31. 11:54 Closed N. Duri 230KV GCB #43, but failed (From DSC and Local). Open both side Isolation switch of GCB #43. 12:59 Checked and function test N. Duri GCB #43. OK. 17:07 Closed both side Isolation switch of GCB#43. 17:08 Closed N.Duri 230Kv GCB#43. Ctr: 202. Cause: Under investigation. |  | 1 | 9:38 | Morning | Sunday | 2018 | 7
9150 | 2018-07-29 09:49 | 2018-07-29 09:49 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 0 | 09:49 Manually opened LBS 7E-46 D/S Minas fdr#6. Replace Dead and at well 6E-93. 12:45 closed LBS 7E-46. Ok. Cause :Plain Maintenance. |  | 1 | 9:49 | Morning | Sunday | 2018 | 7
9151 | 2018-07-29 09:57 | 2018-07-29 09:57 | 13.8KV 8D FEEDER #2 | Cloudy | Lightning | 38 | 8D fdr#2 T/R 1x. Not checked yet. |  | 1 | 9:57 | Morning | Sunday | 2018 | 7
9152 | 2018-07-29 09:57 | 2018-02-08 08:57 | 13.8KV 8D FEEDER #2 | Cloudy | Lightning | 38 | Checked and found 13.8KV OCB #2 T/R 1x Ctr: 279-280 R/F: 51N. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 9:57 | Morning | Sunday | 2018 | 7
9153 | 2018-07-29 10:00 | 2018-07-29 10:00 | 13.8KV BEKASAP FEEDER #5 | Fair | Planned Maintenance | 0 | 10:00 Manually opened recloser 37-BD-21 D/S Bekasap fdr#5. Refill oil trafo Tx-B ( Bekasap EOR) 14:11 Manually closed recloser Tx-B OK. Cause: Pain Maintenance. |  | 1 | 10:00 | Morning | Sunday | 2018 | 7
9154 | 2018-07-29 11:18 | 2018-07-29 11:18 | 13.8KV 6D FEEDER #3 | Fair | Static Wire | 115 | 11:18 It was reported No Power at well 6D-61, 6D-62N, 6D-62N, 6D-62, 6D-72, 6D-51N, 6D-51. 11:35 Checked and found recloser 6D-03 T/LO. Also found broken static wire touch back arm o/p 6D-11 Isolate broken static wire 11:55 Manually open LBS 6D-66 Closed LSB 6D-68 D/S 6D fdr#2 Cause : Static wire. |  | 1 | 11:18 | Morning | Sunday | 2018 | 7
9155 | 2018-07-29 12:08 | 2018-07-29 12:08 | 13.8KV 6DN FEEDER #5 | Fair | Static Wire | 0 | 12:08 Manually open LBS 6D-16A Repaired broken static wire o/p 6D-11A. 10 wells off during done the JOB. (6D-95N, 6D-84, 6D-85, 6D-96, 6D-99E1, 7D-11A 7C-19, 6D-64, 6D-94E, 6D-95). 16:12 Closed LBS 6D-16A (Failed). 16:16 Closed LBS 6D-15. 16:26 Closed recloser 6D-03 16:29 Closed LBS 6D-66 (parallel 6D fdr#2 & 6D fdr#3). 16:31 Opened LBS 6D-68 D/S 6D fdr#3. Cause : Static wire. |  | 1 | 12:08 | Afternoon | Sunday | 2018 | 7
9156 | 2018-07-30 23:59 | 2018-07-30 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | Normal System Condition. |  | 1 | 23:59 | Night | Monday | 2018 | 7
9157 | 2018-07-31 09:37 | 2018-07-31 09:37 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Planned Maintenance | 30 | 09:37 Manually Open Petapahan fdr #4. Replaced all Pin Insulator with New Type. Cause: Plan Maintenance. |  | 1 | 9:37 | Morning | Tuesday | 2018 | 7
9158 | 2018-07-31 10:04 | 2018-07-31 10:04 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | Manually Open Recl: 16-AB-03. Tie In New well at So. Balam # 19 and So. Balam #449. Replaced All FCO of Recl: 16-AB-03 (additional JOB). Project. |  | 1 | 10:04 | Morning | Tuesday | 2018 | 7
9159 | 2018-07-31 10:59 | 2018-07-31 10:59 | 13.8KV NORTH DURI FEEDER #2 | Fair | Secondary Cable | 31 | It was reported Secondary Cable vandalism o/p: 10-J6-13A. Not checked yet. |  | 1 | 10:59 | Morning | Tuesday | 2018 | 7
9160 | 2018-07-31 10:59 | 2018-04-08 15:58 | 13.8KV NORTH DURI FEEDER #2 | Fair | Secondary Cable | 31 | Checked and found Missing Secondary Cable o/p 10-J6-13A. Replaced secondary cable and energized the Tx. Cause : Secondary Cable. |  | 1 | 10:59 | Morning | Tuesday | 2018 | 7
9161 | 2018-01-08 08:00 | 2018-01-08 08:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Unidentified | 0 | CKBS VCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 8:00 | Morning | Monday | 2018 | 1
9162 | 2018-01-08 08:00 | 2018-02-08 08:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Unidentified | 0 | Checked and found 13.8KV VCB #5 T/R 1x Ctr: 162-163 R/F: 51. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 8:00 | Morning | Monday | 2018 | 1
9163 | 2018-01-08 14:34 | 2018-01-08 14:34 | 13.8KV MINAS FEEDER #2 | Fair | Recloser - Control Recloser | 0 | 14:34 Minas fdr #2 load dropped 50A (130-80A). 14:51 Checked and found Recloser: M2-01 T/SO Counter: 55-56. 14:55 Blocked and closed Recloser: M2-01 --> OK and then released the block. Cause: Not patrolled yet. |  | 1 | 14:34 | Afternoon | Monday | 2018 | 1
9164 | 2018-01-08 14:34 | 2018-02-08 08:34 | 13.8KV MINAS FEEDER #2 | Fair | Recloser - Control Recloser | 0 | Checked and found Recloser M2-01 T/SO Ctr: 55-56. Patrolled the line but found nothing. Cause: Control Recloser. |  | 1 | 14:34 | Afternoon | Monday | 2018 | 1
9165 | 2018-01-08 15:02 | 2018-01-08 15:02 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Rain and Lightning | Lightning | 0 | 15:02 Dumai VCB #12 (feeder #1) T/LO. 17:20 Checked and found Dumai VCB #12 (feeder #1) T/LO Counter: 293-295 R/F: 50 @1,2,3. Patrolled the line found nothing. 17:23 Manually blocked and closed Dumai VCB #12 (feeder #1) --> Ok and then released the block. Cause: Suspected Lightning. |  | 1 | 15:02 | Afternoon | Monday | 2018 | 1
9166 | 2018-01-08 15:38 | 2018-01-08 15:38 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Sintong fdr #2 load dropped 193A (282-89A). Sintong GFPC T/R 1x. Not checked yet. | 11111 | 1 | 15:38 | Afternoon | Monday | 2018 | 1
9167 | 2018-01-08 15:38 | 2018-05-08 08:38 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Checked and found Recloser 28-AF-02 T/R 1x Ctr: 1533-1534. Patrolled the line but found nothing. Cause: Unidentified. | 11111 | 1 | 15:38 | Afternoon | Monday | 2018 | 1
9168 | 2018-01-08 16:07 | 2018-01-08 16:07 | 13.8KV 5B FEEDER #4 | Fair | Planned Maintenance | 0 | 16:07 Manually opened Recloser: 4B-73 D/S 5B fdr #4. Due to Change out transformer at well 3C-93. 16:40 Manually blocked and closed Recloser: 4B-73 and then released the block. Cause: Plan Maintenance. |  | 1 | 16:07 | Afternoon | Monday | 2018 | 1
9169 | 2018-01-08 16:44 | 2018-01-08 16:44 | SURAM SUBSTATION | Fair | Under investigation | 0 | 16:44 It was reported no power at Kasikan BOB. Suram RTU failed at that time. 17:30 Checked and found Circuit Switcher T/O. R/F: 59 , 86T and then checked Power transformer good condition. Reset 86 T. 17:40 Manually opened Suram OCB fdr #1. 17:41 Manually opened Suram OCB fdr #2. 17:47 Closed Circuit Switcher --> OK. 17:49 Manually blocked and closed Suram OCB fdr #1 --> OK and then released the block. 17:50 Manually blocked and closed Suram OCB fdr #2 --> OK and then released the block. Cause: Under investigation. |  | 1 | 16:44 | Afternoon | Monday | 2018 | 1
9170 | 2018-02-08 14:47 | 2018-02-08 14:47 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | 14:47 Manually opened Recloser 16-AB-03 D/S Balam fdr#4 Due to installed new transformer at well Balam#446 15:35 Manually blocked and closed Recl 16-AB-03 and then release the block. Cause : Construction Job. |  | 1 | 14:47 | Afternoon | Thursday | 2018 | 2
9171 | 2018-02-08 17:59 | 2018-02-08 17:59 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Darling VCB fdr #7 T/R 1x. Not checked yet. |  | 1 | 17:59 | Afternoon | Thursday | 2018 | 2
9172 | 2018-02-08 17:59 | 2018-04-08 15:45 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Checked and found Darling VCB fdr #7 T/R 1x Counter: 167-168 R/F: 51@3 Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 17:59 | Afternoon | Thursday | 2018 | 2
9173 | 2018-02-08 18:44 | 2018-02-08 18:44 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 0 | Sintong fdr #2 load dropped 126A (237-111A). Sintong GFPC T/R 1X. Not checked yet. |  | 1 | 18:44 | Afternoon | Thursday | 2018 | 2
9174 | 2018-02-08 18:44 | 2018-05-08 08:44 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 0 | Checked and found GFPC T/R 4x Ctr: 1086-1090 R/F: 51N @2. Patrolled the line and found Dead Monkey o/p 27-Y-17. Cause: Animal. |  | 1 | 18:44 | Afternoon | Thursday | 2018 | 2
9175 | 2018-03-08 09:28 | 2018-03-08 09:28 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Construction Job | 0 | 09:28 Manually opened LBS: 04-08-27 D/S C. Duri fdr #8. Due to cut jumper on pole 03-00-05 for repairing bridge 5P-79A. Manually closed LBS: 04-08-27. Cause: Construction job. |  | 1 | 9:28 | Morning | Thursday | 2018 | 3
9176 | 2018-03-08 14:30 | 2018-03-08 14:30 | 13.8KV 8D FEEDER #3 | Fair | Planned Maintenance | 0 | 14:30 Manually poned Recloser: 8D-30 D/S 8D fdr #3. Due to Changed out transformer at well 9D-12E ( Switchboard to VCD ). 14:50 Manually blocked and closed Recloser: 8D-30 and then released the block. Cause: Plan Maintenance. |  | 1 | 14:30 | Afternoon | Thursday | 2018 | 3
9177 | 2018-03-08 15:43 | 2018-03-08 15:43 | 13.8KV 4B FEEDER #6 | Fair | Planned Maintenance | 0 | 15:43 Manually opened Recloser: 4B-148 D/S 4B fdr #6. Due to Changed out transformer at well 4B-46. 16:50 Manually blocked and closed Recloser: 4B-148 and then released the block. Cause: Plan Maintenance. |  | 1 | 15:43 | Afternoon | Thursday | 2018 | 3
9178 | 2018-03-08 16:45 | 2018-03-08 16:45 | MINAS POWER PLANT |  |  | - | 16:45 S/U MGT # 7 and then On Line the unit at 16:58. |  | 1 | 16:45 | Afternoon | Thursday | 2018 | 3
9179 | 2018-04-08 09:23 | 2018-04-08 09:23 | CENTRAL DURI POWER PLANT |  |  | - | 09:25 S/U CDGT #2 and then on line the unit at 09:45. |  | 1 | 9:23 | Morning | Sunday | 2018 | 4
9180 | 2018-04-08 10:13 | 2018-04-08 10:13 | 13.8KV LIBO FEEDER #1 | Fair | Planned Maintenance | 29 | 10:13 Manually opened LBS: 34-CC-1B D/S Libo fdr #1. Due to dismantled transformer at well SE Libo #08. (3 wells were Off during this job) 11:58 Manually closed LBS: 34-CC-1B. Cause: Plan maintenance. |  | 1 | 10:13 | Morning | Sunday | 2018 | 4
9181 | 2018-04-08 11:11 | 2018-04-08 11:11 | 13.8KV 6DN FEEDER #6 | Fair | Planned Maintenance | 39 | 11:11 Manually opned Recloser: 6E-30 D/S 6DN fdr #6. Due to Repair LBS on pole 6E-04 and changed out transformer at well 6E-51. 12:18 Manually blocked and closed Recloser: 6E-30 and then released the block. Cause: Plan maintenance. |  | 1 | 11:11 | Morning | Sunday | 2018 | 4
9182 | 2018-04-08 12:04 | 2018-04-08 12:04 | CENTRAL DURI POWER PLANT |  |  | - | 12:04 Off line CDGT #4 and then S/D the unit at 12:05. Status: Standby. |  | 1 | 12:04 | Afternoon | Sunday | 2018 | 4
9183 | 2018-04-08 14:46 | 2018-04-08 14:46 | MINAS POWER PLANT |  |  | - | 14:46 S/U MGT #6 and then On line the unit at 15:10. |  | 1 | 14:46 | Afternoon | Sunday | 2018 | 4
9184 | 2018-04-08 15:20 | 2018-04-08 15:20 | MINAS POWER PLANT |  |  | - | 15:20 Off line MGT #7 and then S/D the unit for Standby. |  | 1 | 15:20 | Afternoon | Sunday | 2018 | 4
9185 | 2018-04-08 21:00 | 2018-04-08 21:00 | MINAS POWER PLANT |  |  | - | 21:00 S/U MGT #8 and then On line the unit at 21:34. |  | 1 | 21:00 | Night | Sunday | 2018 | 4
9186 | 2018-04-08 22:51 | 2018-04-08 22:51 | 13.8KV DURI COMMUNITY FEEDER #3 | Drizzle | Tree | 0 | Duri Community ACB # 26 (feeder # 3) T/R 1x Not checked yet |  | 1 | 22:51 | Night | Sunday | 2018 | 4
9187 | 2018-04-08 22:51 | 2018-05-08 14:41 | 13.8KV DURI COMMUNITY FEEDER #3 | Drizzle | Tree | 0 | Checked and found Duri Community ACB # 26 (feeder # 3) T/R 1x R/F : 51 @ 1 Ctr : 80 - 81 . Patrolled the line found Ketapang Tree Touch at Primary jumper on Pole 3 DE 28 (trafo 50 kVA). Dismantle Ketapang Tree. Cause : Tree. |  | 1 | 22:51 | Night | Sunday | 2018 | 4
9188 | 2018-05-08 07:53 | 2018-05-08 07:53 | 13.8KV MINAS FEEDER #3 | Fair | Lightning | 39 | Minas ACB #2 ( Feeder #3) T/R 1x R/F: 51N Counter: 80141 - 80142. Cause: Not patrolled yet. |  | 1 | 7:53 | Morning | Tuesday | 2018 | 5
9189 | 2018-05-08 07:53 | 2018-09-08 08:53 | 13.8KV MINAS FEEDER #3 | Fair | Lightning | 39 | Checked and found 13.8KV ACB #2 T/R 1x Ctr: 80142-80143 R/F: 51N Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 7:53 | Morning | Tuesday | 2018 | 5
9190 | 2018-05-08 09:31 | 2018-05-08 09:31 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 30 | Bangko OCB fdr # 4 T?R 1x. Not checked yet. |  | 1 | 9:31 | Morning | Tuesday | 2018 | 5
9191 | 2018-05-08 09:31 | 2018-06-08 08:31 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 30 | Checked and found 13.8KV OCB #4 T/R 1x Ctr: 49-50 R/F: 51 @1 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:31 | Morning | Tuesday | 2018 | 5
9192 | 2018-05-08 11:10 | 2018-05-08 11:10 | 13.8KV MBL SUBSTATION 2 DURI FEEDER #2 | Fair | Planned Maintenance | 36 | 11:10 Manually opened MSU#2 fdr #2 (Pungut fdr #2) Due to changed out transformer at well South Piala #01. 12:03 Manually blocked and closed MSU#2 fdr #2 and then released the block. Cause: Plan maintenance. |  | 1 | 11:10 | Morning | Tuesday | 2018 | 5
9193 | 2018-05-08 13:40 | 2018-05-08 13:40 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | It was reported b/o fuse at well Rantau Bais #53 D/S Batang fdr #2. Not checked yet. |  | 1 | 13:40 | Afternoon | Tuesday | 2018 | 5
9194 | 2018-05-08 13:40 | 2018-07-08 12:41 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | Checked and found @1 ,@2 b/o fuse for 112.5 Kva Tx at well Rantau Bais #53. Performed TTR and Megger found good reading. Replaced b/o fuse above with the same size and energized the Tx. Cause: Animal (monkey). |  | 1 | 13:40 | Afternoon | Tuesday | 2018 | 5
9195 | 2018-05-08 19:59 | 2018-05-08 19:59 | 13.8KV 8D FEEDER #5 | Fair | Lightning | 0 | 8D OCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 19:59 | Night | Tuesday | 2018 | 5
9196 | 2018-05-08 19:59 | 14/08/2018 20:40 | 13.8KV 8D FEEDER #5 | Fair | Lightning | 0 | Checked and found 8D OCB fdr #5 T/R 1x R/F: None Counter: 566-566 ( Not changed ). Cause: Suspected Lightning. |  | 1 | 19:59 | Night | Tuesday | 2018 | 5
9197 | 2018-06-08 06:42 | 2018-06-08 06:42 | 13.8KV 8D FEEDER #3 | Fair | Lightning | 0 | 8D 13.8KV OCB fdr #3 T/R 1X. 8D fdr #1 load dropped 26A (138-112A). 8D fdr #2 load dropped 12A (95-83A). Not checked yet. |  | 1 | 6:42 | Morning | Friday | 2018 | 6
9198 | 2018-06-08 06:42 | 2018-09-08 08:42 | 13.8KV 8D FEEDER #3 | Fair | Lightning | 0 | Checked and found 13.8KV OCB #3 T/R 1x Ctr: 223-224 R/F: 50N @1 Patrolled the line and found broken LA o/p 8D-30 Cause: Lightning. |  | 1 | 6:42 | Morning | Friday | 2018 | 6
9199 | 2018-06-08 06:42 | 2018-06-08 06:42 | 13.8KV 8D FEEDER #5 | Fair | Lightning | 0 | 8D 13.8KV OCB fdr #5 T/R 1X. 8D fdr #4 load dropped 47A (168-121A). Not checked yet. |  | 1 | 6:42 | Morning | Friday | 2018 | 6
9200 | 2018-06-08 06:42 | 2018-09-08 08:42 | 13.8KV 8D FEEDER #5 | Fair | Lightning | 0 | Checked and found 8D fdr #5 T/R 1x Ctr: 565-566 R/F: 50 @2, @3 Patrolled the line and found broken LA Cause: Lightning. |  | 1 | 6:42 | Morning | Friday | 2018 | 6
9201 | 2018-06-08 11:00 | 2018-06-08 11:00 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 21 | It was reported b/o fuse on pole 06-R5-05 D/S Duri Field feeder # 2 . Not checked yet. |  | 1 | 11:00 | Morning | Friday | 2018 | 6
9202 | 2018-06-08 11:00 | 2018-06-08 17:15 | 13.8KV DURI FIELD FEEDER #2 | Fair | Animal | 21 | Checked and found B/O fuse transformer o/p 06-R5-05 @ 1. Cause : Animal |  | 1 | 11:00 | Morning | Friday | 2018 | 6
9203 | 2018-06-08 15:30 | 2018-06-08 15:30 | 13.8KV PUNGUT FEEDER #2 | Fair | Recloser - Control Recloser | 5 | 15:30 It was reported no power at well AMI #02 D/S Pungut fdr #2. 17:25 Checked and found Recloser: 43-BY-25 T/SO Counter: 272-273. Manually blocked and closed Recloser: 43-BY-25 --> OK and then released the block. Cause: Control Recloser. |  | 1 | 15:30 | Afternoon | Friday | 2018 | 6
9204 | 2018-06-08 20:01 | 2018-06-08 20:01 | 13.8KV MINAS FEEDER #3 | Rain | Unidentified | 39 | Minas 13.8KV ACB fdr #3 T/R 1X ctr: 42-43 R/F: 51@3. Not checked yet. |  | 1 | 20:01 | Night | Friday | 2018 | 6
9205 | 2018-06-08 20:01 | 2018-09-08 08:01 | 13.8KV MINAS FEEDER #3 | Rain | Unidentified | 39 | Checked and found Minas fdr #3 T/R 1x Ctr: 80142-80143 R/F: 51N Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 20:01 | Night | Friday | 2018 | 6
9206 | 2018-06-08 20:01 | 2018-06-08 20:01 | 13.8KV MINAS FEEDER #1 | Fair | Lightning | 0 | Minas fdr #1 load dropped 195A (195-0A). Not checked yet. |  | 1 | 20:01 | Night | Friday | 2018 | 6
9207 | 2018-06-08 20:01 | 17/08/2018 20:01 | 13.8KV MINAS FEEDER #1 | Fair | Lightning | 0 | Checked & found Minas ACB fdr#1 T/R 1x Ctr: 78-79 R/F:51N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 20:01 | Night | Friday | 2018 | 6
9208 | 2018-06-08 20:01 | 2018-06-08 20:01 | 13.8KV MINAS FEEDER #2 | Fair | Lightning Arrester | 0 | Minas fdr #2 load dropped 72A (129-57A). Not checked yet. |  | 1 | 20:01 | Night | Friday | 2018 | 6
9209 | 2018-06-08 20:01 | 2018-09-08 08:01 | 13.8KV MINAS FEEDER #2 | Fair | Lightning Arrester | 0 | Checked and found Recloser M2-01 T/R 1x Ctr: 55-56 Patrolled the line and found broken LA @2 Cause: Lightning Arrester. |  | 1 | 20:01 | Night | Friday | 2018 | 6
9210 | 2018-06-08 20:01 | 2018-06-08 20:01 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | 134 | 20:01 Minas 13.8KV ACB fdr #4 T/LO ctr:86-88 R/F: 51N, 51 @2 @3. 21:00 Patrolled the line, but found nothing. 21:01 Blocked and Closed Minas fdr #4, OK then released the block. Cause: Unidentified. |  | 1 | 20:01 | Night | Friday | 2018 | 6
9211 | 2018-07-08 07:51 | 2018-07-08 07:51 | 13.8KV BEKASAP FEEDER #2 | Fair | Animal | 75 | Bekasap Main fdr #2 load dropped 93A !74-81A). Not checked yet. |  | 1 | 7:51 | Morning | Sunday | 2018 | 7
9212 | 2018-07-08 07:51 | 16/08/2018 11:00 | 13.8KV BEKASAP FEEDER #2 | Fair | Animal | 75 | Checked & found, Recl. 37-BD-12 T/R 1x ctr: 1025-1026. Patrolled the line & found, a Dead Animal around Terminal Pole for Well BKS #38. Cause: Animal. |  | 1 | 7:51 | Morning | Sunday | 2018 | 7
9213 | 2018-07-08 10:50 | 2018-07-08 10:50 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 95 | 10:50 It was reported b/o fuse at well Menggala North # 45 D/S Menggala fdr #1. 14:50 Checked and found @3 b/o fuse for 300 Kva Tx. Replaced b/o fuse with the same size and energized the Tx. Cause: Animal (monkey). |  | 1 | 10:50 | Morning | Sunday | 2018 | 7
9214 | 2018-07-08 11:32 | 2018-07-08 11:32 | 13.8KV BATANG FEEDER #3 | Fair | Construction Job | 0 | 11:32 Manually opened Batang OCB fdr #3. Due to Open HLC for additional new Well. 14:16 Manually blocked and closed Batang OCB fdr #3 and then released the block. Cause: Construction Job. |  | 1 | 11:32 | Morning | Sunday | 2018 | 7
9215 | 2018-07-08 17:13 | 2018-07-08 17:13 | 13.8KV PETANI FEEDER #2 | Cloudy | Unidentified | 18 | Petani OCB fdr#2 T/R 1x. Petani fdr#1 load dropped 53A (248-195A). Not checked yet. |  | 1 | 17:13 | Afternoon | Sunday | 2018 | 7
9216 | 2018-07-08 17:13 | 16/08/2018 11:19 | 13.8KV PETANI FEEDER #2 | Cloudy | Unidentified | 18 | Checked & found, Petani OCB fdr #2 T/R 1x ctr: 252-253 R/F: 51N. Patrolled the line & found, @3 broken Fuse for Capacitor Bank on Pole 33-AY-28. Cause: Unidentified. |  | 1 | 17:13 | Afternoon | Sunday | 2018 | 7
9217 | 2018-08-08 09:45 | 2018-08-08 09:45 | CENTRAL DURI POWER PLANT |  |  | - | 09:45 S/U CDGT#4 the on line unit at 10:10. |  | 1 | 9:45 | Morning | Wednesday | 2018 | 8
9218 | 2018-08-08 10:25 | 2018-08-08 10:25 | CENTRAL DURI POWER PLANT |  |  | - | 10:25 Off line CDGT#3 the S/D the unit for maintenance. |  | 1 | 10:25 | Morning | Wednesday | 2018 | 8
9219 | 2018-08-08 10:30 | 2018-08-08 10:30 | MINAS POWER PLANT |  |  | - | MGT#6 Emergency S/D by bearing header temperature high. |  | 1 | 10:30 | Morning | Wednesday | 2018 | 8
9220 | 2018-08-08 10:40 | 2018-08-08 10:40 | 13.8KV S. BALAM FEEDER #4 | Fair | Construction Job | 0 | 10:40 Manually open Recloser 16-AB-03 d/s Balam fdr#4. Tie in new well So.Balam#446. 17:00 Blocked & closed Recloser 16-AB-03,Then release the blocked. Cause: Construction job. |  | 1 | 10:40 | Morning | Wednesday | 2018 | 8
9221 | 2018-08-08 11:45 | 2018-08-08 11:45 | MINAS POWER PLANT |  |  | - | 11:45 S/U MGT#7 then on line the unit at 12:04. |  | 1 | 11:45 | Morning | Wednesday | 2018 | 8
9222 | 2018-09-08 05:22 | 2018-09-08 05:22 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning Arrester | 9 | Rokan VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 5:22 | Morning | Saturday | 2018 | 9
9223 | 2018-09-08 05:22 | 16/08/2018 09:45 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning Arrester | 9 | Checked & found, Rokan VCB fdr #2 T/R 1x ctr: 1268-1269 R/F: 51N. Patrolled the line & found, @2 broken Lightning Arrester on Pole 31-AV-27. Cause: Lightning Arrester. |  | 1 | 5:22 | Morning | Saturday | 2018 | 9
9224 | 2018-09-08 11:12 | 2018-09-08 11:12 | 13.8KV 8D FEEDER #11 | Fair | Construction Job | 0 | 11:12 Manually Opened 8D VCB fdr#11 Replaced 50 to 300KVATX at well 8E 64, as SPS project. 11:47 Manually Closed the VCBs after finished the job. Cause: Planning Construction |  | 1 | 11:12 | Morning | Saturday | 2018 | 9
9225 | 2018-09-08 11:38 | 2018-09-08 11:38 | 13.8KV BATANG FEEDER #3 | Fair | Construction Job | 0 | 11:38 Manually Opened Batang Fdr#3 Open HLC at Well Pemburu#23 & 25 for Pilling new Pole, and Installation construction for TX mounting at well Pemburu P03 Cut power line for support RFD at well Pemburu P01 12:16 Manually Block & Closed the VCB after finished the Job. Cause: Planned Construction |  | 1 | 11:38 | Morning | Saturday | 2018 | 9
9226 | 2018-09-08 16:40 | 2018-09-08 16:40 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 28 | It was reported B/O fuse o/p 01-01-23 (CD fdr#6) Not checked yet |  | 1 | 16:40 | Afternoon | Saturday | 2018 | 9
9227 | 2018-09-08 16:40 | 15/08/2018 15:17 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified (Fuse) | 28 | Checked & found, @2 b/o Fuse for 112.5 KVA Tx on Pole 01-01-23. Replaced b/o Fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 16:40 | Afternoon | Saturday | 2018 | 9
9228 | 2018-10-08 06:35 | 2018-10-08 06:35 | 13.8KV 8D FEEDER #2 | Fair | Lightning | 30 | 8D OCB fdr# 2 T/R 1x Not checked yet |  | 1 | 6:35 | Morning | Monday | 2018 | 10
9229 | 2018-10-08 06:35 | 14/08/2018 08:45 | 13.8KV 8D FEEDER #2 | Fair | Lightning | 30 | Checked and patrolled 8D OCB fdr# 2 T/R 1x. R/F: 51N Counter: 280-281 Found F/O LA on pole 8E-15 @ 1. Cause : Lightning |  | 1 | 6:35 | Morning | Monday | 2018 | 10
9230 | 2018-10-08 09:10 | 2018-10-08 09:10 | 13.8KV LIBO FEEDER #2 | Fair | Construction Job | 0 | 09:10 Manually Opened Recl 23 BW 02B (Libo fdr#2) Project relocate TX at Well Hitam#01 impact 4Wells Down for One week. Cause: Planned construction. |  | 1 | 9:10 | Morning | Monday | 2018 | 10
9231 | 2018-10-08 09:35 | 2018-10-08 09:35 | 13.8KV S. BALAM FEEDER #1 | Fair | Construction Job | 0 | 09:35 Manually Opened Balam VCB fdr#1 Project Tie In new well Blm#447 09:50 Manually block & Closed the VCB after finished the jobs (impact well down 4 wells not Pop yet for 8 hrs ) Cause : Planned Construction |  | 1 | 9:35 | Morning | Monday | 2018 | 10
9232 | 2018-10-08 15:00 | 2018-10-08 15:00 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 10 | 15:00 Manually Opened LBS 7E-54 (Minas fdr#6) Installed TX at Mini Cewa Substation Impacted 3 wells Down 16:50 Manually Closed the LBS above after finished the jobs Cause: Planned Maintenance |  | 1 | 15:00 | Afternoon | Monday | 2018 | 10
9233 | 2018-11-08 06:31 | 2018-11-08 06:31 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 313 | 06:31 D.field VCB fdr#3 T/LO. Checked, Found Ctr: 372-276, R/F : 51 @123 Patrolled the Line, but found nothing 07:56 Transfer part load of DF fdr#3 to DF Fdr#1 to Supply CGS#1. (under Recloser 01.05.02 in bay pass status) Opened bay pass Recl.01.05.02, then Closed LBS 01.05.32, CGS1 back normal Continued Patrolled the Line under D.field fdr#3 08:45 Block & Closed D.Field VCB fdr#3, then released the block Cause: Unidentified |  | 1 | 6:31 | Morning | Thursday | 2018 | 11
9234 | 2018-11-08 06:31 | 2018-11-08 06:31 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | 132 | 06:31 D.field VCB Fdr#2 T/LO Checked & found Ctr: 11004-11008, R/F: 51 @123. Patrolled the Line, but found nothing 09:10 Manually Block & Closed the VCB, then released the block Cause: Unidentified |  | 1 | 6:31 | Morning | Thursday | 2018 | 11
9235 | 2018-11-08 10:35 | 2018-11-08 10:35 | CENTRAL DURI POWER PLANT |  |  | - | 10:35 CGT#3 S/U, the On line at 10:54 due to CGT#4 S/B for certification. |  | 1 | 10:35 | Morning | Thursday | 2018 | 11
9236 | 2018-11-08 11:08 | 2018-11-08 11:08 | CENTRAL DURI POWER PLANT |  |  | - | 11:08 CGT #4 On Line the S/D for S/B. for Certification Boiler. |  | 1 | 11:08 | Morning | Thursday | 2018 | 11
9237 | 2018-11-08 12:52 | 2018-11-08 12:52 | 13.8KV KOTABATAK FEEDER #2 | Fair | Recloser | 16 | 12:52 OKB fdr#2 Load dropped 93A (268-175A) 14:30 Checked & found Recl 38 CX 25 In Open status. Patrolled the Line, but found nothing Closed the Recloser but fail 14:40 Closed LBS 39.CY.01, to transfer load under Recl 38.CW.08 Cause: Recloser |  | 1 | 12:52 | Afternoon | Thursday | 2018 | 11
9238 | 2018-11-08 14:20 | 2018-11-08 14:20 | 13.8KV S. BALAM FEEDER #1 | Fair | Construction Job | 0 | 14:20 Manually Opened S Balam VCB fdr#1 to Connect HLC for Well Blm#447 14:34 Manually Block & Closed the VCB, then released the block Cause: Planned Construction |  | 1 | 14:20 | Afternoon | Thursday | 2018 | 11
9239 | 2018-11-08 16:18 | 2018-11-08 16:18 | 13.8KV 8D FEEDER #10 | Fair | Fire | 0 | 16:18 It was reported Fire under power line near well 7D 78E,stagging area (8D VCB fdr#10) 16:28 Manually Opened 8D VCB fdr#10, Fire team Fighting the fire. 17:20 Manually block & Closed the VCB, then released the block after the Fire has Cooling down. Cause: Fire. |  | 1 | 16:18 | Afternoon | Thursday | 2018 | 11
9240 | 2018-11-08 19:59 | 2018-11-08 19:59 | 13.8KV 8D FEEDER #5 | Fair | Unidentified | 25 | 8D 13.8Kv OCB#5 T/R 1x. Not checked yet. |  | 1 | 19:59 | Night | Thursday | 2018 | 11
9241 | 2018-11-08 19:59 | 27/08/2018 16:26 | 13.8KV 8D FEEDER #5 | Fair | Unidentified | 25 | Checked & found, the Breaker did not operated ctr: 566-566. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 19:59 | Night | Thursday | 2018 | 11
9242 | 2018-12-08 07:17 | 2018-12-08 07:17 | 13.8KV PEMATANG FEEDER #2 | Fair | Pin Insulator | 61 | 07:17 Pematang VCB fdr#2 T/R 1x Pematang Fdr#1 Load dropped 159A(198-39A) Not checked yet |  | 1 | 7:17 | Morning | Saturday | 2018 | 12
9243 | 2018-12-08 07:17 | 16/08/2018 10:12 | 13.8KV PEMATANG FEEDER #2 | Fair | Pin Insulator | 61 | Checked & found, Pematang OCB fdr #2 T/R 1x ctr: 494-495 R/F: 51N. Patrolled the line & found, @1 Broken Pin Insulator on Pole 34 BB 26. Cause: Pin Insulator. |  | 1 | 7:17 | Morning | Saturday | 2018 | 12
9244 | 2018-12-08 07:42 | 2018-12-08 07:42 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 46 | 07:42 Bangko Fdr#4 Load dropped 92A(174-82A) Bangko GFPC T/R 1x 08:30 Checked & found Recl 25.Z.07 T/O in Block position Ctr: 202-203 Patrolled the Line, but found Nothing 09:21 Manually block & Closed the Recloser, then released the block. Cause: Unidentified |  | 1 | 7:42 | Morning | Saturday | 2018 | 12
9245 | 2018-12-08 07:51 | 2018-12-08 07:51 | 13.8KV 6DN FEEDER #6 | Fair | Accident | 0 | 07:51 Mannually Opened 6DN VCB fdr#6 To Maintain level tank (Citizens Demonstration at GS#3) 12:30 Manually Block & Closed the VCB, then released the block after the Tank level back normal. Cause: Accident |  | 1 | 7:51 | Morning | Saturday | 2018 | 12
9246 | 2018-12-08 09:21 | 2018-12-08 09:21 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | 162 | 09:21 Minas VCB fdr#3 T/LO Minas Fdr#1 Load dropped 180A (219-21A) Minas Fdr#2 Load dropped 49A (125-79A) Minas Fdr#4 Load dropped 180 (196-36A) Checked & found Ctr: 80143-80145, R/F: 51 @2@3 Patrolled the Line, but found nothing 10:30 Manually Block & Closed the VCB, then Released the block Cause: Unidentified |  | 1 | 9:21 | Morning | Saturday | 2018 | 12
9247 | 2018-12-08 10:37 | 2018-12-08 10:37 | 13.8KV KETIGUL FEEDER#3 | Fair | Planned Maintenance | 39 | 10:37 Opened LBS 31.AV.01 (Ketigul fdr#3) to Replace 300 KVA TX at well Gulamo north #01 12:15 Closed Backthe LBS after finished install the TX. Cause: Planned Maintenance |  | 1 | 10:37 | Morning | Saturday | 2018 | 12
9248 | 2018-08-13 12:15 | 2018-08-13 12:15 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 82 | 12:15 Manually Opened OKB VCB fdr#2 To By Passed Rel. 38.CX.25, 60 Well Down. Manually Block & Closed back OKB VCB fdr#2 after Ensure the bypass were Full contact Cause: Planned maintenance |  | 1 | 12:15 | Afternoon | Monday | 2018 | 8
9249 | 2018-08-13 21:41 | 2018-08-13 21:41 | 13.8KV BEKASAP FEEDER #6 | Fair | Suspension Insulator | 25 | Bekasap fdr #6 load dropped 73A (194-121A). Not checked yet. |  | 1 | 21:41 | Night | Monday | 2018 | 8
9250 | 2018-08-13 21:41 | 2018-08-19 21:41 | 13.8KV BEKASAP FEEDER #6 | Fair | Suspension Insulator | 25 | Checked & found Recl. 38BE10 T/R 1x Ctr:599-600 R/F:51@1. Patrolled the line & found @1 Broken Suspension o/p 39BF17. Cause : Suspension Insulator. |  | 1 | 21:41 | Night | Monday | 2018 | 8
9251 | 2018-08-14 09:12 | 2018-08-14 09:12 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 5 | It was reported b/o fuse o/p 03-08-10A d/s C.Duri fdr#7. Not checked yet. |  | 1 | 9:12 | Morning | Tuesday | 2018 | 8
9252 | 2018-08-14 09:12 | 2018-08-15 15:48 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified (Fuse) | 5 | Checked & found, @3 b/o Fuse for 112.5KVA Tx on Pole 03-08A-10. Replaced b/o Fuse above with the same size then energized the Tx. Cause: Unidentified (Fuse). |  | 1 | 9:12 | Morning | Tuesday | 2018 | 8
9253 | 2018-08-14 10:19 | 2018-08-14 10:19 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 0 | 10:19 Manually opened line switch o/p 7D-76B (Minas fdr#3). Replace 300KvTx at well 7D-82E S/D well 7D-72 during the job. 11:11 Closed block the line switch ,after finniest the jobs. Cause : Plain maintenance. |  | 1 | 10:19 | Morning | Tuesday | 2018 | 8
9254 | 2018-08-14 12:00 | 2018-08-14 12:00 | 13.8KV S. BALAM FEEDER #1 | Fair | Planned Maintenance | 153 | 12:00 Manually opened So.Balam fdr#1. Replace recloser 16-Z-25. Repair hot sport terminal jumper recloser. HLC with type by past with. 14:45 Closed So.Balam fdr#1. Cause : Plain maintenance. |  | 1 | 12:00 | Afternoon | Tuesday | 2018 | 8
9255 | 2018-08-14 15:39 | 2018-08-14 15:39 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 39 | 15:39 Manually opened recloser 6E-23A (Minas fdr#6). Replace 600-550Kv Tx at well 6E-65 (same well down 18 Wells). 17:00 Closed recloser 6E-23A (Minas fdr#6). Cause : Plain maintenance. |  | 1 | 15:39 | Afternoon | Tuesday | 2018 | 8
9256 | 2018-08-14 19:04 | 2018-08-14 19:04 | 13.8KV KOTABATAK FEEDER #2 | Fair | Others | 166 | 19:04 OKB OCB fdr #2 T/O. 20:25 Checked and found OKB OCB fdr #2 T/SO Counter: 1323-1324 R/F: 51N. 20:32 Manually blocked and closed OKB OCB fdr #2 --> Ok and then released the block. Cause: Not patrolled yet. |  | 1 | 19:04 | Night | Tuesday | 2018 | 8
9257 | 2018-08-14 19:04 | 2018-08-18 19:04 | 13.8KV KOTABATAK FEEDER #2 | Fair | Others | 166 | Patrolled the line but found nothing. Cause : Others. |  | 1 | 19:04 | Night | Tuesday | 2018 | 8
9258 | 2018-08-15 06:56 | 2018-08-15 06:56 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified | 0 | C.Duri ACB#41 fdr#9 T/R 1x. Not checked yet. |  | 1 | 6:56 | Morning | Wednesday | 2018 | 8
9259 | 2018-08-15 06:56 | 2018-08-19 06:56 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified | 0 | Checked and found C.Duri 13.8KV ACB fdr#9 T/R 1x ctr: 393-394 R/F: 51G, 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 6:56 | Morning | Wednesday | 2018 | 8
9260 | 2018-08-15 09:06 | 2018-08-15 09:06 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Darling 13.8 KV VCB fdr#7 T/R 2x. Not checked yet. |  | 1 | 9:06 | Morning | Wednesday | 2018 | 8
9261 | 2018-08-15 09:06 | 2018-08-19 09:06 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Checked and found Darling 13.8 KV VCB fdr#7 T/R 2x ctr: 168-170 R/F: 51 @1, @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 9:06 | Morning | Wednesday | 2018 | 8
9262 | 2018-08-15 10:27 | 2018-08-15 10:27 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Others | 0 | CKBS 13.8 KV VCB fdr#1 T/R 1x ( The feeder trip while open LBS 37-CU-05 ). Not checked yet. |  | 1 | 10:27 | Morning | Wednesday | 2018 | 8
9263 | 2018-08-15 10:27 | 2018-08-18 10:27 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Others | 0 | Checked & found CKBS fdr#1 T/R 1x Ctr:230-231 R/F:51@2. Patrolled the line but found nothing. Cause : Others. |  | 1 | 10:27 | Morning | Wednesday | 2018 | 8
9264 | 2018-08-15 10:27 | 2018-08-15 10:27 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 84 | 10:27. Manual open LBS: 37-CU-05. (CKBS fdr #1 T/R while operate LBS: 37-CU-05). Replaced Pin insulator o/p 37-CT-09. 11:11 Manual Open CKBS 13.8 KV fdr #1,-----> Closed at :11:24. Closed LBS: 37-CU-05 but failed (Blade problem). 11:31 Closed LBS: 36-CU-35 (Transfer load to NKBS fdr #3). Cause: Planned Maintenance. |  | 1 | 10:27 | Morning | Wednesday | 2018 | 8
9265 | 2018-08-15 17:33 | 2018-08-15 17:33 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Duri Community ACB fdr #3 T/R 1X. Not checked yet. |  | 1 | 17:33 | Afternoon | Wednesday | 2018 | 8
9266 | 2018-08-15 17:33 | 2018-08-19 17:33 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Pin Insulator | 0 | Checked & found Duri Community fdr#3 T/R 1x Ctr:81-82 R/F:51@1. Patrolled the line & found @1 Broken Pin Insulator o/p 3DD10. Cause : Pin Insulator. |  | 1 | 17:33 | Afternoon | Wednesday | 2018 | 8
9267 | 2018-08-16 14:45 | 2018-08-16 14:45 | 13.8KV 6D FEEDER #5 | Fair | Planned Maintenance | 4 | 14:45 Manually open recl. 5D-64 (6D fdr#5). Installed 150Kva Tx for reactive well 5D-56. 15:38 Blocked & closed recl. 5D-64,then release the block. Cause : Plan Maintenance. |  | 1 | 14:45 | Afternoon | Thursday | 2018 | 8
9268 | 2018-08-16 17:41 | 2018-08-16 17:41 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Duri Field 13.8 Kv VCB fdr#4 T/R 1x. Not checked yet. |  | 1 | 17:41 | Afternoon | Thursday | 2018 | 8
9269 | 2018-08-16 17:41 | 2018-08-19 17:41 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Checked and found Duri Field 13.8 Kv VCB fdr#4 T/R 1x ctr: 534-535 R/F: 51 @1, @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 17:41 | Afternoon | Thursday | 2018 | 8
9270 | 2018-08-17 02:53 | 2018-08-17 02:53 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 5 | 5B VCB fdr#3 T/R 1x. Not checked yet |  | 1 | 2:53 | Night | Friday | 2018 | 8
9271 | 2018-08-17 02:53 | 2018-08-25 12:42 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 5 | Checked and found 5BSB-13.8OCB3 T/R 1x R/F 51N Counter 390-391. Patrolled and found Broken Dead end on pole 4C62 @3. Cause : Lightning |  | 1 | 2:53 | Night | Friday | 2018 | 8
9272 | 2018-08-17 03:00 | 2018-08-17 03:00 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 98 | 6DN fdr#6 T/R 1x Not checked yet |  | 1 | 3:00 | Night | Friday | 2018 | 8
9273 | 2018-08-17 03:00 | 2018-08-25 12:53 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 98 | Checked and found 6DNSB-13.8OCB6 T/R 1x R/F 50 @3 Counter 355 - 355. Patrolled and found Broken Pin on pole 6D147 @3. Cause : Lightning |  | 1 | 3:00 | Night | Friday | 2018 | 8
9274 | 2018-08-17 03:00 | 2018-08-17 03:00 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 0 | 6DN fdr#2 Load dropped 183A (273-90A) Not checked yet |  | 1 | 3:00 | Night | Friday | 2018 | 8
9275 | 2018-08-17 03:00 | 2018-08-25 12:58 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked and found 5442-R.6D200 T/R 1x R/F 51N Counter 9-19. Patrolled and found Broken Dead end on pole 5D47 @2. Cause : Lightning |  | 1 | 3:00 | Night | Friday | 2018 | 8
9276 | 2018-08-17 03:00 | 2018-08-17 03:00 | MINAS POWER PLANT | Fair | Under investigation | 0 | MGT #10 Trip Off, by Alarm High Vibration, 0.83 I/s cause: under investigation |  | 1 | 3:00 | Night | Friday | 2018 | 8
9277 | 2018-08-17 03:03 | 2018-08-17 03:03 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 23 | 5B VCB fdr#4 T/R 1x not checked yet |  | 1 | 3:03 | Night | Friday | 2018 | 8
9278 | 2018-08-17 03:03 | 2018-08-25 12:23 | 13.8KV 5B FEEDER #4 | Rain and Lightning | Lightning | 23 | Checked and found 5BSB-13.8OCB4 T/R 1x R/F 50 Counter 371-372. Patrolled and found Broken dead end o/p 4B-5B 13 @1. Cause : Lightning |  | 1 | 3:03 | Night | Friday | 2018 | 8
9279 | 2018-08-17 03:04 | 2018-08-17 03:04 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Lightning | 0 | Minas ACB fdr#2 T/R 1x Not checked yet |  | 1 | 3:04 | Night | Friday | 2018 | 8
9280 | 2018-08-17 03:04 | 2018-08-28 09:48 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found, Minas ACB #13 fdr #2 T/R 1x Ctr: 73-74 R/F: 51@2 Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 3:04 | Night | Friday | 2018 | 8
9281 | 2018-08-17 03:09 | 2018-08-17 03:09 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | 5B Fdr#1 Load dropped 83A (120-37A) Not checked yet |  | 1 | 3:09 | Night | Friday | 2018 | 8
9282 | 2018-08-17 03:09 | 2018-08-28 05:30 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recloser 5B-06 T/R 1x ctr: 94-95 R/F: 51N. Patrolled the line but found nothing. Cause: Suspected by Lightning. |  | 1 | 3:09 | Night | Friday | 2018 | 8
9283 | 2018-08-17 03:10 | 2018-08-17 03:10 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 60 | 03:10 4B VCB fdr#1 T/R 1x. 20:10 Checked & found 4B OCB fdr#1 T/R 1x Ctr:334-335 R/F:50N@1@2@3. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 3:10 | Night | Friday | 2018 | 8
9284 | 2018-08-17 04:17 | 2018-08-17 04:17 | MINAS POWER PLANT |  |  | - | 04:17 S/U MGT#6 then on line the unit at 04:46. |  | 1 | 4:17 | Morning | Friday | 2018 | 8
9285 | 2018-08-17 04:45 | 2018-08-17 04:45 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Tree | 0 | 04:45 It was reported no power at Gate#1 Minas, Clinic, Sec Off (Minas fdr#2). Checked & found 4160V Recl. M2-01 T/O Ctr:659-660. 05:56 Patrolled the line & found Fallen tree near Ware House Minas, then Isolated. 06:14 Blocked & Closed 4160V Recl M2-01, the release the block. Cause: Tree. |  | 1 | 4:45 | Morning | Friday | 2018 | 8
9286 | 2018-08-17 07:05 | 2018-08-17 07:05 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | C.Duri 13.8 KV ACB fdr#4 T/R 1x. Not checked yet. |  | 1 | 7:05 | Morning | Friday | 2018 | 8
9287 | 2018-08-17 07:05 | 2018-08-19 07:05 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | Patrolled the line and found C.Duri 13.8 KV ACB fdr#4 T/R 1x ctr: 509-510 R/F: 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 7:05 | Morning | Friday | 2018 | 8
9288 | 2018-08-17 15:22 | 2018-08-17 15:22 | 13.8KV 4D FEEDER #4 | Fair | Planned Maintenance | 6 | 15:22 Manully opened 4D13.8Kv OCB Fdr#4,----->Closed at :16:57. Replaced Dead end insulator broken. Causce Planed maintenance. |  | 1 | 15:22 | Afternoon | Friday | 2018 | 8
9289 | 2018-08-18 09:02 | 2018-08-18 09:02 | 4.16KV EAST RUMBAI FEEDER #1 | Fair | Planned Maintenance | 0 | 09:02. Manual open LBS: 4RD-02, d/s East Rumbai fdr #1 RCC , JATI & IKSORA Camp off. Cutting Tree around Wisma Bukit. Cause: Planned Maintenance. |  | 1 | 9:02 | Morning | Saturday | 2018 | 8
9290 | 2018-08-18 10:30 | 2018-08-18 10:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 7 | It was reported B/O fuse at well Pagar #28 d/s Ketigul fdr#2 15:50 checked and fond @1 B/O fuse for 150 Kva Tx Replaced the B/O fuse above with same size .then energized . Cause. Animal |  | 1 | 10:30 | Morning | Saturday | 2018 | 8
9291 | 2018-08-19 10:23 | 2018-08-19 10:23 | 4.16KV MINAS IND FEEDER | Fair | Planned Maintenance | 0 | 10:23. Manual open Disconnect Switch IJS-00, d/s Minas fdr #2.then closed at 11:55. Replaced Broken flash over Dead End Insulator & LA. Cause: Planned Maintenance. |  | 1 | 10:23 | Morning | Sunday | 2018 | 8
9292 | 2018-08-19 14:20 | 2018-08-19 14:20 | 13.8KV MINAS FEEDER #2 | Fair | Planned Maintenance | 0 | 14:20 Manually Open 4160V Recl. M1-02 Minas Housing (Minas fdr #2). Replaced @1@2@3 Broken Pin Insulator o/p 7E-143. 16:38 Blocked & closed 4160V Recl M1-02, then release the block. Cause: Plan Maintenance. |  | 1 | 14:20 | Afternoon | Sunday | 2018 | 8
9293 | 2018-08-19 14:30 | 2018-08-19 14:30 | 13.8KV MINAS FEEDER #1 | Fair | Planned Maintenance | 209 | 14:30 Manually Open Minas 13.8KV ACB fdr #1. Replaced @1@2@3 Broken Pin Insulator o/p 7E-143. 16:25 Blocked & closed Minas 13.8Kv ACB fdr#1, then release the block. Cause: Plan Maintenance. |  | 1 | 14:30 | Afternoon | Sunday | 2018 | 8
9294 | 2018-08-19 23:30 | 2018-08-19 23:30 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified (Fuse) | 91 | 23:30 It was reported B/O Fuse at well PMT#38 (PMT fdr#2) Not checked yet |  | 1 | 23:30 | Night | Sunday | 2018 | 8
9295 | 2018-08-19 23:30 | 2018-08-20 23:30 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified (Fuse) | 91 | 10:10 Checked and found @2 b/o fuse for 30KVA TX at well Pematang #38. Performed TTR test and Megger the TX, OK. Replaced the b/o fuse above with same size, Then energized the TX. OK. Cause: Unidentified fuse. |  | 1 | 23:30 | Night | Sunday | 2018 | 8
9296 | 2018-08-20 06:19 | 2018-08-20 06:19 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 0 | 06:19 Bangko fdr#4 Load dropped 89A (181-92A). Bangko GFPC T/R 1x. Not checked yet. 20:00 Checked & found Recl. 25Z07 T/R 1x Ctr:203-204 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 6:19 | Morning | Monday | 2018 | 8
9297 | 2018-08-20 06:33 | 2018-08-20 06:33 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | C.Duri fdr#7 Load dropped 150A (173-23A). Not checked yet. |  | 1 | 6:33 | Morning | Monday | 2018 | 8
9298 | 2018-08-20 06:33 | 2018-08-23 10:32 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | Patrolled and found 5441-Recl 03-03-42 T/R 1x R/F: 51 @1 Counter: 168-169. Cause : Unidentified |  | 1 | 6:33 | Morning | Monday | 2018 | 8
9299 | 2018-08-20 14:40 | 2018-08-20 14:40 | CENTRAL DURI POWER PLANT |  |  | - | 14:40 S/U CDGT #1 and online the system at:15:08 for running test.(after MO). 22:02 Off line CGT#1. then S/D the unit for Maintenance. |  | 1 | 14:40 | Afternoon | Monday | 2018 | 8
9300 | 2018-08-20 15:05 | 2018-08-20 15:05 | 13.8KV BATANG FEEDER #3 | Fair | Construction Job | 0 | 15:05 Manually open Batang 13.8 KV OCB fdr #3,----->Closed at:15:34. O/C HLC for reactive well at Pemburu#14. New well at Pemburu #30. Cause: Construction job. |  | 1 | 15:05 | Afternoon | Monday | 2018 | 8
9301 | 2018-08-20 17:45 | 2018-08-20 17:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 17:45 It was reported b/o fuse o/p:08-L3-16. Not checked yet. |  | 1 | 17:45 | Afternoon | Monday | 2018 | 8
9302 | 2018-08-20 17:45 | 2018-08-21 17:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | 16:00 Checked and found @2 b/o fuse foe 112.5KVA TX o/p:08-L3-16. Performed TTR test and Megger the TX. OK. Replaced the b/o fuse above with same size. the energized the TX. OK. Cause: Unidentified fuse. |  | 1 | 17:45 | Afternoon | Monday | 2018 | 8
9303 | 2018-08-21 10:48 | 2018-08-21 10:48 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 97 | Ketigul 13.8KV VCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 10:48 | Morning | Tuesday | 2018 | 8
9304 | 2018-08-21 10:48 | 2018-08-23 08:48 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 97 | Checked and found 13.8KV VCB #2 T/R 1x Ctr: 293-294 R/F: 51N @3. Patrolled the line and found dead animal o/p Pagar #40, B/O Fuse link 2 pcs. Cause: Animal. |  | 1 | 10:48 | Morning | Tuesday | 2018 | 8
9305 | 2018-08-21 11:11 | 2018-08-21 11:11 | 13.8KV 6DN FEEDER #2 | Fair | Unidentified | 73 | 11:11 6DN fdr #3 load dropped 167A (273-106A). 13:03 Checked and found Recloser 6D-200 T/SO ctr:10-13 R/F:51@2. Blocked and Closed the recloser . ok. Then release the block. Not checked yet. |  | 1 | 11:11 | Morning | Tuesday | 2018 | 8
9306 | 2018-08-21 11:11 | 2018-08-28 17:30 | 13.8KV 6DN FEEDER #2 | Fair | Unidentified | 73 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 11:11 | Morning | Tuesday | 2018 | 8
9307 | 2018-08-21 19:54 | 2018-08-21 19:54 | 13.8KV NORTH DURI FEEDER #9 | Fair | Lightning | 0 | N.Duri VCB fdr#9 T/R 1x. Not checked yet. |  | 1 | 19:54 | Night | Tuesday | 2018 | 8
9308 | 2018-08-21 19:54 | 2018-08-22 17:02 | 13.8KV NORTH DURI FEEDER #9 | Fair | Lightning | 0 | Checked and found NDRSB-13.8VCB9 T/R 1x R/F 51N Counter: 59-60 Patrolled and found BROKEN LA on pole 12 G7.2 25 @3. Cause : Lightning |  | 1 | 19:54 | Night | Tuesday | 2018 | 8
9309 | 2018-08-22 08:05 | 2018-08-22 08:05 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Animal | 353 | Checked and found OKB OCB fdr# 2 T/SO R/F : 51 N Counter : 1325-1326 Weather : Cloudy 09:47 : Manually blocked and closed OKB OCB fdr# 2 but failed 11:02 : Patrolled the line and found animal o/p 37-CX-11 LBS, then dismantle the animal 11:46 : Manually blocked and closed OKB OCB fdr# 2 -->>> OK and then released the block Cause : Animal (monkey) |  | 1 | 8:05 | Morning | Wednesday | 2018 | 8
9310 | 2018-08-22 08:05 | 2018-08-22 08:05 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Cloudy | Animal | 11 | 13.8KV CENTRAL KOTABATAK FEEDER #1 T/R 1x Weather : Cloudy 09:46 : 13.8KV CENTRAL KOTABATAK FEEDER #1 T/R 1x again 11:02 : Patrolled the line and found animal o/p 37-CX-11 LBS (two way feeder with OKB fdr#2), then dismantle the animal Cause : Animal (monkey) |  | 1 | 8:05 | Morning | Wednesday | 2018 | 8
9311 | 2018-08-22 11:28 | 2018-08-22 11:28 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Theft | 19 | It was reported missing secondary cable at KULIM # 10 D/S CD fdr# 1 R/ by HO DSC |  | 1 | 11:28 | Morning | Wednesday | 2018 | 8
9312 | 2018-08-22 11:28 | 2018-08-23 10:37 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Theft | 19 | Checked and found MISSING CABLE SECONDERY on location KULIN#10 Cause : Theft |  | 1 | 11:28 | Morning | Wednesday | 2018 | 8
9313 | 2018-08-22 14:35 | 2018-08-22 14:35 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified (Fuse) | 34 | It was reported b/o fuse on pole 08-L7-10 D/S C Duri fdr #1. Not checked yet. |  | 1 | 14:35 | Afternoon | Wednesday | 2018 | 8
9314 | 2018-08-22 14:35 | 2018-08-23 10:39 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified (Fuse) | 34 | Checked and found B/O FUSE @1 on pole 08 L7 10 Cause : unidentified |  | 1 | 14:35 | Afternoon | Wednesday | 2018 | 8
9315 | 2018-08-22 17:37 | 2018-08-22 17:37 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Animal | 0 | Ketigul fdr #2 load dropped 169A (229-60A). Not checked yet. |  | 1 | 17:37 | Afternoon | Wednesday | 2018 | 8
9316 | 2018-08-22 17:37 | 2018-08-25 12:02 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Animal | 0 | Checked and found PKTGL-13.8VCB2 T/R 1x R/F 51N Counter 293-294. Patrolled and found B/O FUSE at Pagar#40 @2. Cause : Animal |  | 1 | 17:37 | Afternoon | Wednesday | 2018 | 8
9317 | 2018-08-23 09:52 | 2018-08-23 09:52 | 13.8KV LIBO FEEDER #2 | Fair | Construction Job | 0 | 09:52 Manually opened Recloser: 23-BW-02 D/S Libo fdr #2. Due to install Guy and jumper at well Hitam #2. Manually blocked and closed Recloser: 23-BW-02 , and then released the block. Cause: Constuction Job. |  | 1 | 9:52 | Morning | Thursday | 2018 | 8
9318 | 2018-08-23 10:49 | 2018-08-23 10:49 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 5 | 10:49 : Manually opened HLC on TOP Bangko #92, #242 . due to replace Pin Insulator 13:20 : Manually closed HLC on TOP Bangko #92, #242 . Cause : Plan Maintenance |  | 1 | 10:49 | Morning | Thursday | 2018 | 8
9319 | 2018-08-24 09:34 | 2018-08-24 09:34 | 13.8KV BANGKO FEEDER #1 | Fair | Construction Job | 0 | 09:34 Manually opened BKO OCB fdr# 1 due to Pilling Guy rig for new well at BKO Field 10:04 Manually blocked and closed BKO OCB fdr# 1 and then released the block Cause : Construction Job |  | 1 | 9:34 | Morning | Friday | 2018 | 8
9320 | 2018-08-24 15:40 | 2018-08-24 15:40 | CENTRAL DURI POWER PLANT |  |  | - | 15:40 S/U CDGT#1 and then online the unit at 15:56. |  | 1 | 15:40 | Afternoon | Friday | 2018 | 8
9321 | 2018-08-24 17:42 | 2018-08-24 17:42 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain and Lightning | Unidentified | 0 | NKBS VCB fdr#3 T/R 1x. NKBS fdr#5 load dropped 122A (156-34A). NKBS fdr#4 load dropped 73A (150-77A) Not checked yet. |  | 1 | 17:42 | Afternoon | Friday | 2018 | 8
9322 | 2018-08-24 17:42 | 2018-08-25 14:45 | 13.8KV NEW KOTABATAK FEEDER #3 | Rain and Lightning | Unidentified | 0 | Checked and found NKBKSB-13.8OCB3 T/R 1x R/F 51N Counter 317 - 318. Patrolled and found nothing. Cause : unidentified |  | 1 | 17:42 | Afternoon | Friday | 2018 | 8
9323 | 2018-08-25 09:00 | 2018-08-25 09:00 | 13.8KV NORTH DURI FEEDER #9 | Fair | Planned Maintenance | 0 | 09:00 Opened Fuse Cut Out on pole 11-G7-19 D/S N Duri fdr #9. Due to repaired ground bushing transformer. (4 wells off during this job). 11:02 Closed Fuse Cut Out and energized the transformer. Cause: Plan Maintenance. |  | 1 | 9:00 | Morning | Saturday | 2018 | 8
9324 | 2018-08-25 16:00 | 2018-08-25 16:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 48 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 16:00 | Afternoon | Saturday | 2018 | 8
9325 | 2018-08-25 16:00 | 2018-08-30 08:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 48 | Checked & found Ketigul VCB fdr#2 T/R 1x Ctr:294-295 R/F:51@1. Patrolled the line & found @1 Broken Dead End Insulato on T/P Pagar#1. Cause : Dead End Insulator. |  | 1 | 16:00 | Afternoon | Saturday | 2018 | 8
9326 | 2018-08-25 16:00 | 2018-08-25 16:00 | 13.8KV KETIGUL FEEDER#1 | Fair | Normal Condition | 0 | Ketigul fdr #1 load dropped 69A (129-60A). Not checked yet. |  | 1 | 16:00 | Afternoon | Saturday | 2018 | 8
9327 | 2018-08-25 16:00 | 2018-05-09 20:00 | 13.8KV KETIGUL FEEDER#1 | Fair | Normal Condition | 0 | Checked VCB fdr#1 Normal Condition. Patrolled the line but found nothing. Cause : Normal Condition |  | 1 | 16:00 | Afternoon | Saturday | 2018 | 8
9328 | 2018-08-25 18:07 | 2018-08-25 18:07 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Transformer leakage | 0 | It was reported B/O fuse on pole 03-05-24 2@ D/S CD fdr#7. Not checked yet. |  | 1 | 18:07 | Afternoon | Saturday | 2018 | 8
9329 | 2018-08-25 18:07 | 2018-08-26 10:47 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Transformer leakage | 0 | Checked and found TRAFO LEAKAGE on pole 03 05 24 and then replaced b/o fuse @1,3 . Cause : Transformer leakage |  | 1 | 18:07 | Afternoon | Saturday | 2018 | 8
9330 | 2018-08-26 09:00 | 2018-08-26 09:00 | CENTRAL DURI POWER PLANT |  |  | - | 09:00 S/U CDGT#4 and then online the unit at 09:22. |  | 1 | 9:00 | Morning | Sunday | 2018 | 8
9331 | 2018-08-26 10:10 | 2018-08-26 10:10 | CENTRAL DURI POWER PLANT |  |  | - | 10:10 Off line CDGT #1 and then S/D the unit at :10:11. |  | 1 | 10:10 | Morning | Sunday | 2018 | 8
9332 | 2018-08-26 11:05 | 2018-08-26 11:05 | MINAS POWER PLANT |  |  | - | 11:05 S/U MGT #1 and then online the unit at 11:34. |  | 1 | 11:05 | Morning | Sunday | 2018 | 8
9333 | 2018-08-26 11:43 | 2018-08-26 11:43 | MINAS POWER PLANT |  |  | - | 11:43 S/U MGT #3 and then online the unit at 12:05. |  | 1 | 11:43 | Morning | Sunday | 2018 | 8
9334 | 2018-08-26 14:30 | 2018-08-26 14:30 | MINAS POWER PLANT |  |  | - | 14:30 S/U MGT #4 and then online the unit at 14:47. |  | 1 | 14:30 | Afternoon | Sunday | 2018 | 8
9335 | 2018-08-26 16:45 | 2018-08-26 16:45 | MINAS POWER PLANT |  |  | - | 16:45 S/U CDGT#4 and then online the unit at 17:00. |  | 1 | 16:45 | Afternoon | Sunday | 2018 | 8
9336 | 2018-08-26 17:55 | 2018-08-26 17:55 | MINAS POWER PLANT |  |  | - | 17:55 Off line MGT #2 and then S/D the unit. |  | 1 | 17:55 | Afternoon | Sunday | 2018 | 8
9337 | 2018-08-26 22:00 | 2018-08-26 22:00 | NORTH DURI POWER PLANT |  |  | - | 22:00 Off line NDC #1 and then S/D the unit . |  | 1 | 22:00 | Night | Sunday | 2018 | 8
9338 | 2018-08-26 22:00 | 2018-08-27 09:00 | NORTH DURI POWER PLANT |  |  | - | 09:00 Reduce load 12 MW from BOB. |  | 1 | 22:00 | Night | Sunday | 2018 | 8
9339 | 2018-08-27 05:33 | 2018-08-27 05:33 | NEW KOTABATAK SUBSTATION | Fair | Under investigation | 248 | 05:33 OKB & NKB No Power 06:55 Checked and found NKB C/S T/O R/F: 86HR Counter 234-235. 07:14 Manually open NKBS # 3 Manually open NKBS # 4 Manually open NKBS # 5 07:16 Closed NKB C/S ------> OK 07:21 Manually closed NKBS # 3 07:24 Manually closed NKBS # 4 07:25 Manually closed NKBS # 5 07:22 Manually open CKBS # 5 07:46 Manually closed CKBS # 5 Cause : Under investigation |  | 1 | 5:33 | Morning | Monday | 2018 | 8
9340 | 2018-08-27 10:15 | 2018-08-27 10:15 | CENTRAL DURI POWER PLANT |  |  | - | S/U CDGT#1 and then online the unit at:1035 |  | 1 | 10:15 | Morning | Monday | 2018 | 8
9341 | 2018-08-27 12:38 | 2018-08-27 12:38 | 13.8KV LIBO FEEDER #2 | Fair | Construction Job | 0 | 12:38 Manually opened Recl 23-BW-02 D/S LIBO Fdr#2 due to plan Shutdown well Hitam for POP well Hitam#02. 16:29 Manually blocked and closed Recl 23-BW-02 and then released the block. Cause : Construction Job |  | 1 | 12:38 | Afternoon | Monday | 2018 | 8
9342 | 2018-08-27 14:23 | 2018-08-27 14:23 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 21 | 14:23 Manually opened Recloser 7D-81 D/s MNS fdr#3 due to c/o transformer at location 7C-79. 16:38 Manually blocked and closed Recloser 7D-81 and then released the block. Cause : Plan Maintenance |  | 1 | 14:23 | Afternoon | Monday | 2018 | 8
9343 | 2018-08-27 19:28 | 2018-08-27 19:28 | NORTH DURI POWER PLANT |  |  | - | 19:28 S/U NDC#1 and then online the unit at 19:55. |  | 1 | 19:28 | Night | Monday | 2018 | 8
9344 | 2018-08-27 22:50 | 2018-08-27 22:50 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Powerline - Hot Line Clamp | 0 | 22:50 It was reported Spark of TX at Training Center. 23:30 Checked and found @! lost connection at HLC o/p SD-03C for 3 X 50KVA TX at Training Center. 23:59 Manually Open D. Comm. fdr #3,----->Closed at 00:03. Open all Fuse for 3 X 50KVA TX to Isolated spark. Cause: Hot Line Clamp. |  | 1 | 22:50 | Night | Monday | 2018 | 8
9345 | 2018-08-28 00:31 | 2018-08-28 00:31 | NORTH DURI POWER PLANT |  |  | - | 00:31 Off line NDC #1 and then S/D the unit (Vibration). |  | 1 | 0:31 | Night | Tuesday | 2018 | 8
9346 | 2018-08-28 01:00 | 2018-08-28 01:00 | NORTH DURI POWER PLANT |  |  | - | 01:00 S/U NDC #1 and then on line the unit at:01:36. |  | 1 | 1:00 | Night | Tuesday | 2018 | 8
9347 | 2018-08-28 02:07 | 2018-08-28 02:07 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain | Unidentified | 0 | DURI-COMY ACB fdr #1 T/R 1x. Not checked yet. |  | 1 | 2:07 | Night | Tuesday | 2018 | 8
9348 | 2018-08-28 02:07 | 2018-08-30 08:07 | 13.8KV DURI COMMUNITY FEEDER #1 | Rain | Unidentified | 0 | Checked & found Duri Community fdr#1 T/R 1x Ctr:126-127 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 2:07 | Night | Tuesday | 2018 | 8
9349 | 2018-08-28 03:33 | 2018-08-28 03:33 | NORTH DURI POWER PLANT |  |  | - | 03:33 North Duri CT #3 Off Line, then Shutted Down for Off Line Wash Cause : Planned Maintenance |  | 1 | 3:33 | Night | Tuesday | 2018 | 8
9350 | 2018-08-28 10:00 | 2018-08-28 10:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse at well KULIM#80 D/S CD#1. R/ HO DSC Cause : Not checked yet |  | 1 | 10:00 | Morning | Tuesday | 2018 | 8
9351 | 2018-08-28 10:00 | 2018-05-09 19:00 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Replaced @1 B/O fuse for 75 KVa Tx with the same size at Kulim#80. Cause : Unidentified (Fuse). |  | 1 | 10:00 | Morning | Tuesday | 2018 | 8
9352 | 2018-08-28 15:00 | 2018-08-28 15:00 | 13.8KV 5B FEEDER #3 | Fair | Planned Maintenance | 29 | 15:00 Manually Open 5B fdr #3,------>Closed at 16:39. 15:00 Manually Open LBS: 4D-160,------>Closed at 16:42. Replaced transformer at well: 4D-41N. Replaced Recloser 4C-65A. Cause: Plan Maintenance. |  | 1 | 15:00 | Afternoon | Tuesday | 2018 | 8
9353 | 2018-08-28 16:18 | 2018-08-28 16:18 | 13.8KV NORTH DURI FEEDER #1 | Fair | Lightning | 0 | N. Duri 13.8KV VCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 16:18 | Afternoon | Tuesday | 2018 | 8
9354 | 2018-08-28 16:18 | 2018-08-28 19:18 | 13.8KV NORTH DURI FEEDER #1 | Fair | Lightning | 0 | Checked & found N.Duri fdr#1 T/R 1x Ctr:296-297 R/F:51N. Patrolled the line & found @1 Broken LA o/p NF06. Cause : Lightning. |  | 1 | 16:18 | Afternoon | Tuesday | 2018 | 8
9355 | 2018-08-28 20:47 | 2018-08-28 20:47 | 13.8KV NELLA FEEDER #2 | Cloudy | Lightning | 41 | Nella fdr#2 T/R 1x. Nella GFPC T/R 1x. Not checked yet. |  | 1 | 20:47 | Night | Tuesday | 2018 | 8
9356 | 2018-08-28 20:47 | 2018-08-28 20:47 | 13.8KV NELLA FEEDER #1 | Fair | Powerline - Conductor | 952 | 20:47 Nella fdr#1 T/R. 20:48 Nella fdr #1 T/LO ctr:..... R/F:....... 22:10 Patrolled the line and found @1 broken Conductor o/p: Bangko # 35. Open LBS: 20-U-01, ----->Closed at 22:45. 22:11 Blocked and closed Nella fdr #1, Ok, then released the block. Open TTAP: 21-V-09 to isolated broken Conductor. The JOB will be Continued tomorrow. | 12345 | 1 | 20:47 | Night | Tuesday | 2018 | 8
9357 | 2018-08-28 20:47 | 2018-08-29 11:23 | 13.8KV NELLA FEEDER #1 | Fair | Powerline - Conductor | 952 | 11:23 Manually Opened LBS 20 U 01 (Nella Fdr#1) Repair & Connected Broken Conductor o/p Well BKO #35 and Closed T-Tap Jumper o/p 21 V 09. 11:45 Manually Closed the LBS above after finished the Jobs Cause: Broken Conductor. Total Prod Loss : 1092 bbls / 78 wells 28 Aug : 147 bbls / 17 wells 29 Aug : 945 bbls / 61 wells | 12345 | 1 | 20:47 | Night | Tuesday | 2018 | 8
9358 | 2018-08-29 04:55 | 2018-08-29 04:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Theft | 0 | 04:55 It was reported Secondary Cable vandalism at well Kulim #87. Not checked yet. |  | 1 | 4:55 | Morning | Wednesday | 2018 | 8
9359 | 2018-08-29 04:55 | 2018-05-09 19:55 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Theft | 0 | Checked & found @1@2@3 B/O fuse at well Kulim#87. Vandalism Secondary Cable. Cause : Theft. |  | 1 | 4:55 | Morning | Wednesday | 2018 | 8
9360 | 2018-08-29 10:30 | 2018-08-29 10:30 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 288 | 10:30 Manually Opened Recloser 23 BW 02 (Libo fdr#2) Replaced 400KVATX with the same size 13:25 Manually Block & Closed the Recloser above after finished the Jobs Cause : Planned maintenance |  | 1 | 10:30 | Morning | Wednesday | 2018 | 8
9361 | 2018-08-29 17:13 | 2018-08-29 17:13 | 13.8KV 4D FEEDER #5 | Fair | Lightning | 132 | 17:13 4D Fdr#5 Load dropped 220A (250-30A). 18:35 Checked & found Recl. 4D-14A T/SO Ctr:51-52. Blocked & closed Recl. 4D-14A, then release the block. Not patrolled yet. |  | 1 | 17:13 | Afternoon | Wednesday | 2018 | 8
9362 | 2018-08-29 17:13 | 2018-04-09 07:13 | 13.8KV 4D FEEDER #5 | Fair | Lightning | 132 | Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 17:13 | Afternoon | Wednesday | 2018 | 8
9363 | 2018-08-30 07:30 | 2018-08-30 07:30 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Animal | 0 | 07:30 It was reported B/O fuse o/p SLI1A08 (D.Comm fdr#2). 10:50 Checked & found @1@2 B/O fuse for 25Kva Tx o/p SLI1A08. Replaced @1@2 B/O fuse with the same size, then Energized Tx. Cause: Animal (Squirrel). |  | 1 | 7:30 | Morning | Thursday | 2018 | 8
9364 | 2018-08-30 14:07 | 2018-08-30 14:07 | 13.8KV 6DN FEEDER #2 | Fair | Lightning | 0 | 6DN fdr#2 Load dropped 202A (261-59A). 6DN fdr#1 Load dropped 47A (160-113A). Not checked yet. |  | 1 | 14:07 | Afternoon | Thursday | 2018 | 8
9365 | 2018-08-30 14:07 | 2018-04-09 07:07 | 13.8KV 6DN FEEDER #2 | Fair | Lightning | 0 | Checked & found Recl. 5D-112 T/R 1x Ctr:30-31. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 14:07 | Afternoon | Thursday | 2018 | 8
9366 | 2018-08-30 18:54 | 2018-08-30 18:54 | NORTH DURI POWER PLANT |  |  | - | 18:54 S/U NDC#3 and then On Line the unit at 19:35. |  | 1 | 18:54 | Afternoon | Thursday | 2018 | 8
9367 | 2018-08-30 19:18 | 2018-08-30 19:18 | 13.8KV PETANI FEEDER #1 | Fair | Others | 1189 | Petani fdr #1 load dropped 236A (243-7A). Petani fdr #2 load dropped 49A (65-16A). 20:25 Manually opened Petani fdr #1. 20:26 Manually opened Petani fdr #2. Request : Operator Petani GS due to maintain level tank. 20:59 Manually blocked and closed Petani fdr #1 --> OK and then released the blocked. 21:14 Manually opened Petani fdr #1 for replaced @2 broken fuse (30K) 600 Kvar Cap bank. 21:37 Manually blocked and closed Petani fdr #1 --> OK and then released the blocked. 22:07 Manually opened Petani fdr #1 , suspect unbalance on Power Transformer. 22:14 Manually opened Rokan fdr #2 Request : Operator Petani GS due to maintain level tank. Production Loss: 1. Petani feeder #1 = 554 Bbls / 33 wells. 2. Petani feeder #2 = 172 Bbls / 20 wells. 3. Rokan feeder #2 = 51 Bbls / 7 wells. ---------------------------------------- + Total = 777 Bbls / 60 wells. (Up to 24:00). | 12345 | 1 | 19:18 | Night | Thursday | 2018 | 8
9368 | 2018-08-30 19:18 | 2018-08-31 00:12 | 13.8KV PETANI FEEDER #1 | Fair | Others | 1189 | 00:12 Manually opened 44 KV OCB #1 (44 KV Line Pematang Main to Petani ) from DSC but failed. 00:30 Manually opened 44 KV OCB #1 (44 KV Line Pematang Main to Petani ) from Pematang Main Subst. Due to replaced @3 broken fuse for Incoming 44 KV Power Tx at Petani Substation. 01:02 Manually blocked and closed 44 KV OCB #1 (44 KV Line Pematang Main to Petani ) --> Ok. and then released the block. 01:06 Manually blocked and closed Petani OCB fdr #1 --> Ok and then released the block. 01:08 Manually blocked and closed Petani OCB fdr #2 --> Ok and then released the block. 01:10 Manually blocked and closed Rokan OCB fdr #2 --> Ok and then released the block. Petani Substation back to Normal. Cause: Others (Broken Fuse for Incoming Power Tx at Petani Substation). Production Loss: 1. Petani feeder #1 = 187 Bbls / 33 wells. 2. Petani feeder #2 = 60 Bbls / 20 wells. 3. Rokan feeder #2 = 35 Bbls / 7 wells. ---------------------------------------- + Total = 282 Bbls / 60 wells. (August 31 , 2018. from 24:00 Up to 01:10). Grand Total = 1059 Bbls (777 Bbls + 282 Bbls) / 60 wells. | 12345 | 1 | 19:18 | Night | Thursday | 2018 | 8
9369 | 2018-08-30 21:37 | 2018-08-30 21:37 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified | 295 | 21:37 Pematang OCB fdr #2 T/O. 22:27 Checked and found Pematang OCB fdr #2 T/O Counter: 495-496 R/F: Not appear. Patrolled the line nothing found. 23:30 Manually blocked and closed Pematang OCB fdr #2 --> OK and then released the blocked. Cause: Unidentified. |  | 1 | 21:37 | Night | Thursday | 2018 | 8
9370 | 2018-08-30 21:37 | 2018-05-09 21:37 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified | 295 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 21:37 | Night | Thursday | 2018 | 8
9371 | 2018-08-31 00:36 | 2018-08-31 00:36 | NORTH DURI POWER PLANT |  |  | - | 00:36 Off Line NDC #2 and then S/D the unit for stand by. |  | 1 | 0:36 | Night | Friday | 2018 | 8
9372 | 2018-08-31 00:46 | 2018-08-31 00:46 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Unidentified | 138 | Bekasap Main OCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 0:46 | Night | Friday | 2018 | 8
9373 | 2018-08-31 00:46 | 2018-05-09 20:46 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Unidentified | 138 | Checked & found Bekasap VCB fdr#2 T/R 1x Ctr:893-894 R/F:51. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 0:46 | Night | Friday | 2018 | 8
9374 | 2018-08-31 01:17 | 2018-08-31 01:17 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 27 | Bekasap Main fdr #6 load dropped 71A (188-117A). Not checked yet. |  | 1 | 1:17 | Night | Friday | 2018 | 8
9375 | 2018-08-31 01:17 | 2018-05-09 19:17 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Lightning | 27 | Checked & found Bekasap VCB fdr#6 T/R 1x Ctr:893-894 R/F:51. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 1:17 | Night | Friday | 2018 | 8
9376 | 2018-08-31 01:57 | 2018-08-31 01:57 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Unidentified | 0 | Duri Community ACB #33 (feeder #5) T/R 1x. Not checked yet. |  | 1 | 1:57 | Night | Friday | 2018 | 8
9377 | 2018-08-31 01:57 | 2018-05-09 19:57 | 13.8KV DURI COMMUNITY FEEDER #5 | Rain and Lightning | Unidentified | 0 | Checked & found Duri Community fdr#5 T/R 1x Ctr:120-121 R/F:51N. Patrolled the line but nothing. Cause : Unidentified. |  | 1 | 1:57 | Night | Friday | 2018 | 8
9378 | 2018-08-31 11:05 | 2018-08-31 11:05 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 0 | 11:05 Manually Opened Recl.19D 14A (8C fdr#1) to Repair Hot Spot on LBS 9C 14 as in line Switching transfer Load 8C fdr#1 to 8D fdr#11 16:25 Manually Closed Recl. 9D 14A, after finished the Jobs Cause: Planned Maintenance |  | 1 | 11:05 | Morning | Friday | 2018 | 8
9379 | 2018-01-09 08:12 | 2018-01-09 08:12 | MINAS POWER PLANT |  |  | - | Off line MGT#3 then s/d the unit for stand by. |  | 1 | 8:12 | Morning | Tuesday | 2018 | 1
9380 | 2018-01-09 08:26 | 2018-01-09 08:26 | MINAS POWER PLANT |  |  | - | Off line MGT#1 then S/D the unit for Stand by. |  | 1 | 8:26 | Morning | Tuesday | 2018 | 1
9381 | 2018-01-09 09:05 | 2018-01-09 09:05 | GAS TURBINE |  |  | - | Off line MGT#4 then S/D the unit for S/B. |  | 1 | 9:05 | Morning | Tuesday | 2018 | 1
9382 | 2018-01-09 09:05 | 2018-01-09 09:05 | GAS TURBINE |  |  | - | Off line MGT#4 then S/D the unit for S/B. |  | 1 | 9:05 | Morning | Tuesday | 2018 | 1
9383 | 2018-01-09 09:40 | 2018-01-09 09:40 | MINAS POWER PLANT |  |  | - | Off line MGT#6then S/D the unit for S/B |  | 1 | 9:40 | Morning | Tuesday | 2018 | 1
9384 | 2018-01-09 11:00 | 2018-01-09 11:00 | 13.8KV 5B FEEDER #1 | Fair | Unidentified | 0 | 11:00 It was reported b/o fuse at well 5B.64 (5B fdr#1) Checked & found @1@2 b/o fuse for 300KVATX 15:19 Replaced the fuse with the same size, then Energized the TX Cause: Unidentified |  | 1 | 11:00 | Morning | Tuesday | 2018 | 1
9385 | 2018-01-09 14:07 | 2018-01-09 14:07 | CENTRAL DURI POWER PLANT |  |  | - | Off line CDGT#4 then S/D the unit for S/B. |  | 1 | 14:07 | Afternoon | Tuesday | 2018 | 1
9386 | 2018-01-09 16:55 | 2018-01-09 16:55 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 68 | Ketigul VCB fdr#1 T/R 1x Not checked yet |  | 1 | 16:55 | Afternoon | Tuesday | 2018 | 1
9387 | 2018-01-09 16:55 | 2018-05-09 16:55 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 68 | Checked & found Ketigul VCB fdr#1 T/R 1x Ctr:202-203 R/F:51@1@2. Patrolled the line Dead Civet o/p 32AK37. Cause : Animal. |  | 1 | 16:55 | Afternoon | Tuesday | 2018 | 1
9388 | 2018-02-09 | 2018-02-09 | CPI POWER SYSTEM |  |  | - | Normal system condition. |  | 1 | 0:00 | Night | Friday | 2018 | 2
9389 | 2018-03-09 10:38 | 2018-03-09 10:38 | MINAS POWER PLANT |  |  | - | 10:38 S/U MGT#6 Then online the unit at 11:08. 12:18 Off line MGT#6 the S/D the unit for S/B. |  | 1 | 10:38 | Morning | Friday | 2018 | 3
9390 | 2018-03-09 10:40 | 2018-03-09 10:40 | 13.8KV KOTABATAK FEEDER #2 | Fair | Construction Job | 0 | 10:40 Manually open OKB fdr#2 Install 300 Kva Tx for reactive well KB#341. 11:50 Blocked & closed OKB#2 ,the release the block. Cause: Construction Job. |  | 1 | 10:40 | Morning | Friday | 2018 | 3
9391 | 2018-03-09 17:05 | 2018-03-09 17:05 | 13.8KV LIBO FEEDER #1 | Fair | Animal | 73 | 17:05 It was reported b/o fuse at well SE.Libo#56 ( Libo fdr#1 ). 22:15 Checked & found @1 b/o fuse for 300 kva Tx. Replace b/o fuse above with the same size and energized the Tx. Cause : Animal (squirrel). |  | 1 | 17:05 | Afternoon | Friday | 2018 | 3
9392 | 2018-04-09 08:31 | 2018-04-09 08:31 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 0 | 08:31 Petani OCB fdr#1 T/R 5x Checked & found Petani OCB fdr#1 T/R 5x, Ctr: 65-70, R/F: 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 8:31 | Morning | Monday | 2018 | 4
9393 | 2018-04-09 10:33 | 2018-04-09 10:33 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 46 | 10:33 Manually opened Recl *d-18A (8C fdr#3). Replaced 225Kva Tx with 250Kva Tx at well 8D-52E. 11:23 Blocked & closed Recl. 8D-18A, then release the block. Cause: Plan Maintenance. |  | 1 | 10:33 | Morning | Monday | 2018 | 4
9394 | 2018-04-09 15:10 | 2018-04-09 15:10 | 13.8KV PETANI FEEDER #1 | Fair | Planned Maintenance | 88 | 15:10 Manually opened Petani OCB fdr#1. Dismantle 300Kvar Cap Bank at Petani GS. 15:27 Blocked & closed Petani OCB fdr#1, then release the block. Cause: Capacitor Bank. |  | 1 | 15:10 | Afternoon | Monday | 2018 | 4
9395 | 2018-04-09 17:10 | 2018-04-09 17:10 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Lightning | 350 | 17:10 C.Duri fdr#7 Load dropped 119A (148-29A). 20:00 Checked and found Recloser 03-03-42 T/SO (in block position) Counter: 169-170. 20:14 Blocked and Closed Recloser 03-03-42 --> Ok 23:14 And Checked & found Recloser 03-02-02 T/O, Counter: 804-805, due to Control Failure Replaced the Control Card. Block & Closed the Recloser 03-02-02 Cause: Not patrolled yet. |  | 1 | 17:10 | Afternoon | Monday | 2018 | 4
9396 | 2018-04-09 17:10 | 2018-07-09 17:10 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Lightning | 350 | Patrolled the line & found, @1 broken Dead-end Insulator on Pole 03-01-13. Cause: Lightning. |  | 1 | 17:10 | Afternoon | Monday | 2018 | 4
9397 | 2018-04-09 18:25 | 2018-04-09 18:25 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 76 | Ketigul VCB fdr#2 T/R 1x. Ketigul fdr#1 Load dropped 30A (126-96A). Ketigul fdr#3 Load dropped 14A (35-21A). Not checked yet. |  | 1 | 18:25 | Afternoon | Monday | 2018 | 4
9398 | 2018-04-09 18:25 | 2018-07-09 18:25 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 76 | Checked & found, Ketigul VCB fdr #2 T/R 1x ctr: 295-296 R/F: 51N. Patrolled the line & found, @3 broken Pin Insulator on Pole 29 AN 04. Cause: Lightning. |  | 1 | 18:25 | Afternoon | Monday | 2018 | 4
9399 | 2018-05-09 00:23 | 2018-05-09 00:23 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 261 | 00:23 Petani VCB fdr#1 T/R 1x 01:13 Petani VCB fdr#1 T/R 1x 01:42 Petani VCB fdr#1 T/R 1x Checked & found Ctr: 71-74, R/F: 51 @3 Patrolled the Line, but found nothing Cause: Unidentified 15:40 Petani VCB fdr#1 T/R 1x again. 17:54 Petani VCB fdr#1 T/R 1x again. Not checked yet. 23:10 Petani VCB fdr#1 T/R 1x again. Not checked yet. | 1234 | 1 | 0:23 | Night | Wednesday | 2018 | 5
9400 | 2018-05-09 10:45 | 2018-05-09 10:45 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 0 | 10:45 It was reported b/o fuse o/p 10-K4-37, d/s N.Duri fdr #9 15:23 Checked and found @1,@2,@3 b/o fuse for TX 112.5 KVA. Replaced b/o fuse above with the same size and energize the TX. Cause:Animal (Monkey). 15:27 Blocked N.Duri 13.8 KV VCB fdr #9, for cleaning TX from animal carcasses. 15:37 Normalize block N Duri 13.8 Kv VCB Fdr#9. |  | 1 | 10:45 | Morning | Wednesday | 2018 | 5
9401 | 2018-05-09 11:52 | 2018-05-09 11:52 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 27 | 11:52 Manually opened CKBS VCB fdr #1,----->Closed at:12:53. Replaced 350 - 550 KVA , R/M 200 HP,VOLT 2200 TX at well KB # 301. Cause:Planned Maintenance. |  | 1 | 11:52 | Morning | Wednesday | 2018 | 5
9402 | 2018-05-09 11:55 | 2018-05-09 11:55 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 0 | 11:55 Manually opened LBS 5C-59 d/s 6D fdr #1,----->Closed at:12:49. Open fuse for LTC well at 6d-19. Causre:Planned Maintenance. |  | 1 | 11:55 | Morning | Wednesday | 2018 | 5
9403 | 2018-06-09 06:43 | 2018-06-09 06:43 | 13.8KV RANGAU FEEDER #2 | Fair | Lightning | 0 | Rangau load dropped 110A (117-7A). Not checked yet. |  | 1 | 6:43 | Morning | Saturday | 2018 | 6
9404 | 2018-06-09 06:43 | 2018-12-09 06:43 | 13.8KV RANGAU FEEDER #2 | Fair | Lightning | 0 | Checked and found Recolser: 23-BD-01 T/R 3X ctr: 342-345. Patrolled the line and found @3 Broken LA o/p: 22-BD-15. Cause: Lightning. |  | 1 | 6:43 | Morning | Saturday | 2018 | 6
9405 | 2018-06-09 08:40 | 2018-06-09 08:40 | CENTRAL DURI POWER PLANT |  |  | - | 08:40 S/U CDGT #5 and then online the unit at:09:05. |  | 1 | 8:40 | Morning | Saturday | 2018 | 6
9406 | 2018-06-09 10:41 | 2018-06-09 10:41 | CENTRAL DURI POWER PLANT |  |  | - | 10:41 Offline CDGT#4 and then S/D the unit for standby. |  | 1 | 10:41 | Morning | Saturday | 2018 | 6
9407 | 2018-06-09 14:14 | 2018-06-09 14:14 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Under investigation | 0 | 14:14 D. Community 13.8KV ACB fdr #1 T/LO. 14:58 Checked and found D. Comm. fdr #1 T/LO ctr:127-129 R/F:51N, 51@1. 15:12 Open Recloser KT-74. 15:15 Closed LBS: BKS-12, OK (MessHall and Sibayak Camp d/f: D. Com. fdr #2). 16:20 Patrolled the line but found nothing. 16:25 Blocked and closed D. Comm. fdr #1, but tripped again ctr:130 R/F: 51N, 51@1. Open LBS: KT-18, ----->Closed at 17:38. Open LBS: 2DF-8, ----->Closed at 17:42. Open LBS: LKT-61, ----->Closed at 17:51 but D. Comm. fdr #1 Tripped. (suspected under ground Cable ground) 17:46 Open LBS: LKT-72, ----->Closed at.......... 17:51 Re Open LBS: LKT-61. 17:51 Blocked and Closed D. Community fdr #1. OK. 19:10 Open Disconnect Switch foe under ground Cable 19:14 Blocked D.Comm Fdr#1, then Closed LBS LKT 61 22:40 Isolate TXs Bowling, Recreation, and Parking Lot Open Line Switch to GOR Closed LBS LKT 61, but D.Comm ACB fdr#1 T/O Opened back LBS LKT 61, then Closed back D.Comm ACB fdr#1 22:59 Opened Fuse Line at Wisma Antara to Mutiara, then Closed LBS LKT 61 23:40 Opened LBS LKT 61, thenClosed back Line Fuse at Wisma Antara to Mutiara Closed LBS LKT 61 00:12 Block & Closed D.Comm ACB fdr#2, then Closed TX 5A Mess Hall Normalized block D.Comm Fdr#1 &#2 Cause: Under Investigate |  | 1 | 14:14 | Afternoon | Saturday | 2018 | 6
9408 | 2018-07-09 10:35 | 2018-07-09 10:35 | 13.8KV 5B FEEDER #1 | Fair | Recloser | 26 | 10:35 5B 13.8 KV OCB fdr #1 load dropped 41A (127-104A). 10:37 It was reported no Power at GS#6 Control Room. Checked and found Recloser 5B-93 T/O (Unplug position). 11:11 Open Recloser 5B-06. 11:27 Closed bypass switch Recloser 5B-93. 11:29 Closed Recloser 5B-06 and open again due to spark on isolation switch. 11:55 Manually Open 5B 13,8 KV OCB fdr #1. Clossed bypass switch Recloser 5B-06. 12:07 Closed 5B13.8 KV OCB fdr#1. Cause:Recloser. |  | 1 | 10:35 | Morning | Monday | 2018 | 7
9409 | 2018-07-09 15:44 | 2018-07-09 15:44 | 13.8KV NEW KOTABATAK FEEDER #4 | Fair | Low mega-ohm reading | 0 | 15:44 It was reported b/o fuse o/p: KB# 338. Checked and found @1, @2 b/o fuse for 550KVA TX. Performed TTR test and Megger the TX and found Low Mega ohm reading TX. Not replaced yet. |  | 1 | 15:44 | Afternoon | Monday | 2018 | 7
9410 | 2018-07-09 16:30 | 2018-07-09 16:30 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Low mega-ohm reading | 0 | 16:30 It was reported b/o fuse o/p: 04-01-19. Checked and found @1, @2 b/o fuse for 112.5KVA TX. Performed TTR test and Megger the TX and found Low Mega ohm reading TX. Not replaced yet. |  | 1 | 16:30 | Afternoon | Monday | 2018 | 7
9411 | 2018-07-09 16:42 | 2018-07-09 16:42 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | N.Duri VCB fdr#5 T/R 1x Not checked yet |  | 1 | 16:42 | Afternoon | Monday | 2018 | 7
9412 | 2018-07-09 16:42 | 14/09/2018 15:33 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | Checked & found N.Duri VCB fdr#5 T/R 1x, Ctr: 129-130, R/F: 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 16:42 | Afternoon | Monday | 2018 | 7
9413 | 2018-07-09 21:29 | 2018-07-09 21:29 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 76 | 5B 13.8Kv OCB#1 T/R 1X. 5B fdr#3 load dropped 67A (96-29A). 5B fdr#6 load dropped 182A (187-5A)(Pump Off). 5B Fdr#2 Load dropped 146A (164-18A) Not checked yet. |  | 1 | 21:29 | Night | Monday | 2018 | 7
9414 | 2018-07-09 21:29 | 14/09/2018 15:49 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 76 | Checked & found 5B OCB fdr#1 T/R 1x, Ctr: 257-259, R/F: 51 Patrolled the line, found @3 Broken Dead end o/p 4B-57 Cause: Lighting. |  | 1 | 21:29 | Night | Monday | 2018 | 7
9415 | 2018-08-09 06:02 | 2018-08-09 06:02 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 39 | Menggala VCB fdr#1 T/R 1x. Menggala GFPC T/R 1x. Not checked yet. |  | 1 | 6:02 | Morning | Thursday | 2018 | 8
9416 | 2018-08-09 09:12 | 2018-08-09 09:12 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified (Fuse) | 0 | 09:12 It was Reported b/o fuse o/p: 09-M1-94. 13:50 Checked and found @1, @2 b/o fuse for 112.5KVA TX. Replaced the b/o fuse above with same size then energized the TX. OK. Cause: Animal (Monkey). |  | 1 | 9:12 | Morning | Thursday | 2018 | 8
9417 | 2018-08-09 09:12 | 2018-09-09 09:20 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified (Fuse) | 0 | 09:20 It was reported unbalance voltage for TX o/p: 09=M1-04. 14:00 Checked and found @3b/o fuse for 112.5KVA TX. TTR test and megger the TX. Good. Replaced the b/o fuse above with same size. then energized the TX. Cause: Unidentified (fuse). |  | 1 | 9:12 | Morning | Thursday | 2018 | 8
9418 | 2018-08-09 10:20 | 2018-08-09 10:20 | 13.8KV 6D FEEDER #5 | Fair | Low mega-ohm reading | 27 | 10:20 It was reported b/o fuse at well #5D-56. Checked and found @1, @2 fuse for 150KVA TX. Performed TTR test and Megger the TX and found Low Mega Ohm reading TX. Not replaced yet. |  | 1 | 10:20 | Morning | Thursday | 2018 | 8
9419 | 2018-08-09 12:31 | 2018-08-09 12:31 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 25 | Petani 13.8KV OCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 12:31 | Afternoon | Thursday | 2018 | 8
9420 | 2018-08-09 12:31 | 14/09/2018 15:34 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 25 | Checked & found Petani OCB fdr#1 T/R 1x, Ctr: 255-256, R/F: 50 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 12:31 | Afternoon | Thursday | 2018 | 8
9421 | 2018-08-09 17:12 | 2018-08-09 17:12 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Others | 134 | 17:12 C. Duri fdr #1 load dropped 24A (92-68A0. It was reported no Power at Puncak GS. 18:30 Patrolled the line but found nothing. Re-Patrolled the line & found LBS 37AQ08 Open. 19:45 Blocked Recl. 39AV36, then release the block at 20:00. 19:49 Closed LBS 37AQ08. Cause: Others (Vandalism). |  | 1 | 17:12 | Afternoon | Thursday | 2018 | 8
9422 | 2018-08-09 23:14 | 2018-08-09 23:14 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 0 | 5B OCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 23:14 | Night | Thursday | 2018 | 8
9423 | 2018-08-09 23:14 | 14/09/2018 14:03 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found 5B OCB fdr#3 T/R 1x, Ctr: 392-393, R/F: 51 Patrolled the Line, found @1 broken Dead end o/p 4C-62 Cause : Lightning |  | 1 | 23:14 | Night | Thursday | 2018 | 8
9424 | 2018-09-09 11:02 | 2018-09-09 11:02 | 13.8KV NEW KOTABATAK FEEDER #4 | Fair | Planned Maintenance | 9 | 11:02 Open LBS: 37-CV-18, ----->Closed at 11:36. Replaced TX at well KB #338. Cause: Plan Maintenance. |  | 1 | 11:02 | Morning | Sunday | 2018 | 9
9425 | 2018-09-09 15:56 | 2018-09-09 15:56 | CENTRAL DURI POWER PLANT | Fair | Under investigation | 640 | 15:56 13.8KV ACB #14 (TX-1) T/O. CGT #1 Generator Breaker T/O R/F: Non. (No Power to C. Duri BUS-1). 16:40 Checked and found 13.8KV ACB #14 (for TX-1) T/O R/F: 51N-BUS. 16:47 Manually Open C. Duri fdr #1, ----->Closed at 17:05. 16:47 Manually Open C. Duri fdr #2, ----->Closed at 17:06 R/F:51G. 16:47 Manually Open C. Duri fdr #3, ----->Closed at 17:06 R/F:51G. 16:59 Manually Open C. Duri fdr #15, ----->Closed at 17:08. 17:00 Closed 13.8KV ACB #14 (for TX-1). 17:16 CGT #1 On Line to the system. Cause: Under investigation. | 123 | 1 | 15:56 | Afternoon | Sunday | 2018 | 9
9426 | 2018-09-09 17:20 | 2018-09-09 17:20 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 0 | 17:20 It was reported Dead Monkey o/p: 06-Q5-19. 17:45 Checked and found @3 b/o fuse for 112.5KVA TX. (Not replaced yet). Cause: Animal (Monkey). |  | 1 | 17:20 | Afternoon | Sunday | 2018 | 9
9427 | 2018-10-09 10:45 | 2018-10-09 10:45 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Over voltage | 0 | 10:45 It was reported Over voltage o/p 08-M5A-04 (C.Duri Fdr#2) Not checked yet. |  | 1 | 10:45 | Morning | Tuesday | 2018 | 10
9428 | 2018-10-09 10:45 | 14/09/2018 15:39 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Over voltage | 0 | Checked & found, TX 41AX16 o/p 08-M5A-04 (C.Duri ACB fdr#2) Ensure the Voltage, its Unbalance Voltage Cause : Over voltage |  | 1 | 10:45 | Morning | Tuesday | 2018 | 10
9429 | 2018-10-09 14:42 | 2018-10-09 14:42 | 13.8KV NEW KOTABATAK FEEDER #3 | Fair | Planned Maintenance | 106 | 14:42 Manually Open Recloser: 36-CT-10, ----->Closed at 15:45. Replaced 150KVA TX at well #377. Plan Maintenance. |  | 1 | 14:42 | Afternoon | Tuesday | 2018 | 10
9430 | 2018-10-09 16:43 | 2018-10-09 16:43 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Planned Maintenance | 42 | 16:43 Manually opened Recl 03-5-27 (C.Duri fdr#7). Replaced 112.5 Kva Tx with the same size o/p 03-5-27. 17:39 Blocked & closed Recl 03-5-27, then release the block. Cause: Plan Maintenance. |  | 1 | 16:43 | Afternoon | Tuesday | 2018 | 10
9431 | 2018-11-09 07:01 | 2018-11-09 07:01 | 13.8KV 8D FEEDER #2 | Cloudy | Unidentified | 0 | 8D 13.8KV OCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 7:01 | Morning | Friday | 2018 | 11
9432 | 2018-11-09 07:01 | 14/09/2018 07:01 | 13.8KV 8D FEEDER #2 | Cloudy | Unidentified | 0 | Checked & found 8D OCB fdr#2 T/R 1x, Ctr: 51 @2@3 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 7:01 | Morning | Friday | 2018 | 11
9433 | 2018-11-09 08:00 | 2018-11-09 08:00 | 13.8KV PETAPAHAN FEEDER #7 | Fair | Normal Condition | 0 | Petapahan 13.8KV VCB fdr #7 T/R 1X. Not che checked yet. |  | 1 | 8:00 | Morning | Friday | 2018 | 11
9434 | 2018-11-09 08:00 | 22/09/2018 08:00 | 13.8KV PETAPAHAN FEEDER #7 | Fair | Normal Condition | 0 | Checked fdr & Recl. not operated. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 8:00 | Morning | Friday | 2018 | 11
9435 | 2018-11-09 09:54 | 2018-11-09 09:54 | 13.8KV MINAS FEEDER #1 | Fair | Animal | 0 | 09:54 It was reported b/o Fuse at well 7D-29. Checked and found @2, @3 b/o fuse for 300KVA TX. Performed TTR test and Megger the TX. good. Replaced the b/o fuse above with same size then energized the TX. OK. Cause: Animal (squirrel). |  | 1 | 9:54 | Morning | Friday | 2018 | 11
9436 | 2018-11-09 10:06 | 2018-11-09 10:06 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 44 | Batang 13.8KV OCB fdr #3 T/R 1X. Not checked yet. |  | 1 | 10:06 | Morning | Friday | 2018 | 11
9437 | 2018-11-09 12:56 | 2018-11-09 12:56 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Unidentified | 75 | 3D 13.8KV OCB fdr #3 T/R 1. 3D fdr #5 Load dropped 144A (147-3A) (Pump Off). 3D fdr #2 Load dropped 181A (240-59A). Not checked yet. |  | 1 | 12:56 | Afternoon | Friday | 2018 | 11
9438 | 2018-11-09 12:56 | 14/09/2018 12:56 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Unidentified | 75 | Checked & found 3D OCB fdr#3 T/R 1x, Ctr: 444-444 (not change), R/F: 50 @2@3 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 12:56 | Afternoon | Friday | 2018 | 11
9439 | 2018-11-09 12:56 | 2018-11-09 12:56 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | 3D fdr#4 Load dropped 199A (236-37A). Not checked yet. |  | 1 | 12:56 | Afternoon | Friday | 2018 | 11
9440 | 2018-11-09 12:56 | 19/09/2018 12:56 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found Recl. 2D-14 T/R 1x Ctr:82-83. Patrolled the line & found @1 Broken Pin Insulator o/p 2D-101. Cause : Lightning. |  | 1 | 12:56 | Afternoon | Friday | 2018 | 11
9441 | 2018-11-09 18:53 | 2018-11-09 18:53 | 13.8KV KOTABATAK FEEDER #2 | Fair | Normal Condition | 0 | OKB 13.8Kv fdr#2 T/R 1x. Not checked yet. |  | 1 | 18:53 | Afternoon | Friday | 2018 | 11
9442 | 2018-11-09 18:53 | 25/09/2018 08:53 | 13.8KV KOTABATAK FEEDER #2 | Fair | Normal Condition | 0 | Checked Feeder Not operated. Patrolled the line but found nothing. Cause: Normal Condition. |  | 1 | 18:53 | Afternoon | Friday | 2018 | 11
9443 | 2018-11-09 22:43 | 2018-11-09 22:43 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 3743 | 22:43 Petani OCB fdr#1 T/r 1x. Petani fdr#2 Load dropped 42A (66-42A). 22:45 It was reported spark at Petani Substation. 22:54 44Kv Line Pematang Main-Petani GCB #1 T/R 1x. Not checked yet. | 123 | 1 | 22:43 | Night | Friday | 2018 | 11
9444 | 2018-11-09 22:43 | 2018-12-09 14:18 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 3743 | 14:18 Test 44/13.8 Tx Petani substation. Replace B/O fuse 125A and Holder 200A. Repair hot spot o/p 34-AY-20. Replace 150KVATX at petani GS. 14:24 Blocked and closed 44Kv OCB#1 Pematang main - Petani, Then Released the block 14:43 Blocked and closed Petani fdr#1, Then Released the block 14:48 Blocked and closed Petani fdr#2. Then Released the block 15:50 Blocked and closed Rokan VCB#2. Then Released the block Cause : Under intervigation. 17:00 Checked and found Petani 13.8KV OCB fdr #1 T/R 1X ctr: 83-84 R/F: 50@3. Patrolled the line and found broken LA o/p: P{etani #25. Cause: Lighting. Production Loss: Petani fdr #1 : 2722 Bbls / 34 Wells. Petani fdr #2 : 702 Bbls / 20 Wells. Rokan fdr #1 : 503 Bbls / 18 Wells. -------------------------------------------+ TOTAL : 3927 Bbls / 72 Wells | 123 | 1 | 22:43 | Night | Friday | 2018 | 11
9445 | 2018-12-09 10:26 | 2018-12-09 10:26 | 13.8KV MINAS FEEDER #3 | Fair | Construction Job | 0 | 10;26 Manually opened Minas 13.8Kv ACB#2 fdr#3. 11:51 Blocked & closed Minas 13.8Kv ACB#2 fdr#3,then Released block. Cause : Maintain level Tank. |  | 1 | 10:26 | Morning | Sunday | 2018 | 12
9446 | 2018-12-09 10:31 | 2018-12-09 10:31 | 13.8KV 8C FEEDER #5 | Fair | Planned Maintenance | 0 | 10:31 Manually Opened 8C OCB fdr#5 Repair Hot Spot at GS2 TX pump 11:40 Manually Block & Closed the OCB after finished the job, then Released the Block Cause : Planned Maintenance |  | 1 | 10:31 | Morning | Sunday | 2018 | 12
9447 | 2018-12-09 10:40 | 2018-12-09 10:40 | 13.8KV KETIGUL FEEDER#2 | Fair | Others | 503 | 10:40 It was reported no Power at Ubi & Sikladi Field ( Ketigul fdr#2 ) Patrolled the line & found LBS 29- AL-07 in Open Status (Connected KTG fdr#2 & Mgl fdr#2). 19:49 Closed LBS 29-AL-07, then Patrolled the line but found nothing. Cause: Others (Vandalism). | 123 | 1 | 10:40 | Morning | Sunday | 2018 | 12
9448 | 2018-12-09 10:54 | 2018-12-09 10:54 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 197 | 10:54 It was reported no power at well pagar#47 D/S Ketigul fdr#2. Not checked yet. |  | 1 | 10:54 | Morning | Sunday | 2018 | 12
9449 | 2018-12-09 10:54 | 19/09/2018 10:54 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 197 | Checked & found @1@2@3 B/O fuse at well Pagar#47. Cause : Transformer Failure. |  | 1 | 10:54 | Morning | Sunday | 2018 | 12
9450 | 2018-12-09 10:54 | 21/09/2018 10:54 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 197 | Replace 150 Kva Tx with the same size at well Pagar#47. Cause: Transformer Failure. |  | 1 | 10:54 | Morning | Sunday | 2018 | 12
9451 | 2018-12-09 14:53 | 2018-12-09 14:53 | 13.8KV 4B FEEDER #1 | Fair | Construction Job | 0 | 14:53 Manually open recloser 3A-28 (4B fdr#1). Cut jumper o/p 3A-30, OBS wells 3A-30. 14:59 Manually block 4B fdr#1 Opened visual opening TX to OBS Well 3A-65 17:55 By Passed Recloser 3A-28, due to Control Problem Normalized block 4B fdr#1 Cause : Construction job. |  | 1 | 14:53 | Afternoon | Sunday | 2018 | 12
9452 | 2018-12-09 17:19 | 2018-12-09 17:19 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 99 | ketigul 13.8Kv fdr#1 T/R 1x. Ketigul fdr#2 load dropped 36A (223-187A). Ketigul fdr#3 load dropped 12A (36-24A) Not checked yet. |  | 1 | 17:19 | Afternoon | Sunday | 2018 | 12
9453 | 2018-12-09 17:19 | 19/09/2018 07:19 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 99 | Checked & found Ketigul VCB fdr#1 T/R 1x Ctr:203-204 R/F:51. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:19 | Afternoon | Sunday | 2018 | 12
9454 | 2018-12-09 18:53 | 2018-12-09 18:53 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 211 | 18:53 OKB 13.8KV OCB fdr #2 T/O. 20:27 Checked and found OKB fdr #2 T/O ctr:1327-1328 R/F: 51N. (The Block appered while OKB fdr #2 Tripped). 20:34 Blocked and closed OKB fdr #2, OK the released the block. Not patrolled yet. | 123 | 1 | 18:53 | Afternoon | Sunday | 2018 | 12
9455 | 2018-12-09 18:53 | 25/09/2018 08:54 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 211 | Patrolled the line but found nothing. Cause: Unidentified. | 123 | 1 | 18:53 | Afternoon | Sunday | 2018 | 12
9456 | 2018-09-13 08:08 | 2018-09-13 08:08 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 62 | 08:08 Sintong fdr#1 Load dropped 17A (95-78A). Sintong fdr#1 Ground fault alarm. 11:40 Checked and found Recloser 26-AE-22 T/O Ctr: 254-255 (in block position). Replaced 150 KvaTX at well Kerang #08 for parallel jobs 12:00 Manually closed Recloser 26-AE-22, then energized the TX. After finished the Jobs Patrolled the Line but found nothing Cause: Unidentified. Prod Loss = 52 Bbls (6 wells) |  | 1 | 8:08 | Morning | Thursday | 2018 | 9
9457 | 2018-09-13 10:40 | 2018-09-13 10:40 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Tree | 652 | 10:40 C.Duri fdr#1 load dropped 28A (97-69A). 14:04 Checked and found Recl 41-AW-62 T/LO Ctr: 281-284. Patrolled the line, found Fall down tree o/p 10-AV-21 at well Kulim#10. 17:25 Manually Blocked and Closed Recl 41 AW 62. After Clearing the fall down trees. Cause:Tree. Prod Loss = 361 Bbls (51 wells) | 123 | 1 | 10:40 | Morning | Thursday | 2018 | 9
9458 | 2018-09-13 12:57 | 2018-09-13 12:57 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri 13.8Kv VCB#28 fdr#16 T/R 1x. Not checked yet. |  | 1 | 12:57 | Afternoon | Thursday | 2018 | 9
9459 | 2018-09-13 12:57 | 2018-09-19 12:57 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked & found C.Duri fdr#16 T/R 1x Ctr:327-328 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 12:57 | Afternoon | Thursday | 2018 | 9
9460 | 2018-09-13 14:37 | 2018-09-13 14:37 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Planned Maintenance | 95 | 14:37 Manually Opened Recl 04-01-02 (C.Duri fdr#9). Replaced 112.5KvaTX o/p 04-01-19. 16:13 Manually Closed Recl 04-01-02, then energized the TX Cause: Planned Maintenance. Prod Loss = 101 Bbls (72 wells) |  | 1 | 14:37 | Afternoon | Thursday | 2018 | 9
9461 | 2018-09-13 16:36 | 2018-09-13 16:36 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 0 | It was reported B/O fuse o/p 05-N3-19 (CD fdr#14) Not checked yet |  | 1 | 16:36 | Afternoon | Thursday | 2018 | 9
9462 | 2018-09-13 16:36 | 2018-09-14 16:36 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified (Fuse) | 0 | Checked & found @1 b/o fuse for 112.5KVATX o/p 05-N3-19 (CDuri Fdr#14) Replaced the Fuse with the same size, then energized the TX Cause : Unidentified (Fuse) |  | 1 | 16:36 | Afternoon | Thursday | 2018 | 9
9463 | 2018-09-13 16:40 | 2018-09-13 16:40 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 2 | 16:40 It was reported b/o fuse at well Benar#04 ( Sintong fdr#2 ). Checked and found @1 b/o fuse of 150Kva Tx. 17:00 Replaced the b/o fuse above With the same size, Then energized the Tx. Cause : Unidentified. |  | 1 | 16:40 | Afternoon | Thursday | 2018 | 9
9464 | 2018-09-14 11:40 | 2018-09-14 11:40 | 13.8KV NORTH DURI FEEDER #7 | Fair | Theft | 0 | 11:40 It was reported No power o/p 10-K4-26 (N.Duri fdr#7). 14:21 Checked and found loss secondary cable and fuses for 112.5KVATX. Cause:Theft. |  | 1 | 11:40 | Morning | Friday | 2018 | 9
9465 | 2018-09-14 16:41 | 2018-09-14 16:41 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 72 | Ketigul VCB Fdr#1 T/R 1x Not checked yet. |  | 1 | 16:41 | Afternoon | Friday | 2018 | 9
9466 | 2018-09-14 16:41 | 2018-09-19 07:41 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 72 | Checked & found Ketigul fdr#1 T/R 1x Ctr:203-204 R/F:51. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 16:41 | Afternoon | Friday | 2018 | 9
9467 | 2018-09-14 16:41 | 2018-09-14 16:41 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 0 | Ketigul Fdr#2 Load Dropped 79A (216 - 137A). Not Checked yet. |  | 1 | 16:41 | Afternoon | Friday | 2018 | 9
9468 | 2018-09-14 16:41 | 2018-09-21 07:41 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 0 | Checked & found Ketigul VCB fdr#2 Normal Operation (not operated). Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 16:41 | Afternoon | Friday | 2018 | 9
9469 | 2018-09-14 16:41 | 2018-09-14 16:41 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 0 | Ketigul Fdr#3 Load dropped 16A (37-29A) Not checked yet |  | 1 | 16:41 | Afternoon | Friday | 2018 | 9
9470 | 2018-09-14 16:41 | 2018-09-21 07:42 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 0 | Checked & found Ketigul VCB fdr#3 Not Operated. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 16:41 | Afternoon | Friday | 2018 | 9
9471 | 2018-09-14 18:15 | 2018-09-14 18:15 | 13.8KV SURAM FEEDER #1 | Fair | Unidentified | 0 | 18:15 Suram 13.8 kV OCB feeder #1 T/R 1x 18:16 Suram 13.8 kV OCB feeder #1 Trip again and reclose at 18:51 18:53 Suram 13.8 kV OCB feeder #1 Trip again and reclose at 18:54 20:05 Suram 13.8 kV OCB feeder #1 indicate trip again (load still reading 78 A) and reclose at 20:46 Not Checked Yet |  | 1 | 18:15 | Afternoon | Friday | 2018 | 9
9472 | 2018-09-14 18:15 | 2018-09-25 08:15 | 13.8KV SURAM FEEDER #1 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 18:15 | Afternoon | Friday | 2018 | 9
9473 | 2018-09-14 22:13 | 2018-09-14 22:13 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Equipment Failure | 0 | 22:13 13.8 kV Petani OCB fdr #1 T/R 1x Petani fdr #2 Load Drop 30 A (62 - 32 A) Not Checked Yet |  | 1 | 22:13 | Night | Friday | 2018 | 9
9474 | 2018-09-14 22:13 | 2018-09-15 10:24 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Equipment Failure | 0 | Checked and found PTNSB-13.8OCB1 T/R 1X R/F 51 @3 Counter : 88-89. Patrolled and found nothing. Cause : Normal Condition |  | 1 | 22:13 | Night | Friday | 2018 | 9
9475 | 2018-09-14 22:43 | 2018-09-14 22:43 | 13.8KV NORTH DURI FEEDER #10 | Rain and Lightning | Unidentified | 83 | 22:43 N.Duri VCB Fdr #10 T/O (in Block Position, Rig Jobs) Contact RIG BN #09, its Clear status 22:47 Manual Closed the VCB after Conform with BN#9 team Not Checked Yet |  | 1 | 22:43 | Night | Friday | 2018 | 9
9476 | 2018-09-14 22:43 | 2018-09-21 07:43 | 13.8KV NORTH DURI FEEDER #10 | Rain and Lightning | Unidentified | 83 | Checked & found N.Duri VCB fdr#10 T/R 1x Ctr:23-24 R/F:NN. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 22:43 | Night | Friday | 2018 | 9
9477 | 2018-09-15 02:10 | 2018-09-15 02:10 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 34 | 02:10 It was reported b/o fuse at well Meno #04 ( Menggala fdr#1 ). Checked and found @1 b/o fuse for 300Kva Tx. 10:00 Blocked Recl.19-AN-04.Replaced fuse With the same size, Then energized the Tx. Cause : Unidentified. |  | 1 | 2:10 | Night | Saturday | 2018 | 9
9478 | 2018-09-15 06:58 | 2018-09-15 06:58 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C.Duri 13.8Kv VCB#28 fdr#16 T/R 1x. Not checked yet. |  | 1 | 6:58 | Morning | Saturday | 2018 | 9
9479 | 2018-09-15 06:58 | 2018-09-15 14:58 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked and found CDRSG-13.8ACB28 T/R 1X @2 R/F 51 Counter: 327-328. Patrolled and found nothing. Cause : Unidentified |  | 1 | 6:58 | Morning | Saturday | 2018 | 9
9480 | 2018-09-15 10:15 | 2018-09-15 10:15 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified (Fuse) | 0 | 10:15 It was reported b/o fuse O/P 05-N3-19 ( Darling fdr #3 ). Checked and found @1 b/o fuse for 112.5Kva Tx. 11:45 Replaced fuse With the same size, Then energized the Tx. Cause : Unidentified. |  | 1 | 10:15 | Morning | Saturday | 2018 | 9
9481 | 2018-09-15 14:56 | 2018-09-15 14:56 | 13.8KV PETANI FEEDER #1 | Fair | Equipment Failure | 104 | Petani 13.8Kv OCB fdr #1 T/R 1X. Cause : Starting motor at Petani GS | 111111 | 1 | 14:56 | Afternoon | Saturday | 2018 | 9
9482 | 2018-09-15 14:56 | 2018-09-16 14:56 | 13.8KV PETANI FEEDER #1 | Fair | Equipment Failure | 104 | Checked and found PTNSB-13.8OCB1 T/R 1X R/F 51 @1 Counter : 89 - 90. Patrolled and found nothing. Cause : Normal Condition | 111111 | 1 | 14:56 | Afternoon | Saturday | 2018 | 9
9483 | 2018-09-16 06:21 | 2018-09-16 06:21 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 80 | 06:21 Petani 13.8KV OCB fdr #1 T/R 1X. 06:40 Petani 13.8KV OCB fdr #1 T/R again. Petani fdr #2 load drooped 36A (66-30A). Not checked yet. |  | 1 | 6:21 | Morning | Sunday | 2018 | 9
9484 | 2018-09-16 06:21 | 2018-09-21 07:21 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 80 | Checked & found Petani VCB fdr#1 T/R 1x Ctr:85-86 R/F:51@3. Patrolled the line & found @3 Broken LA on T/P Petani#25. Cause : Lightning. |  | 1 | 6:21 | Morning | Sunday | 2018 | 9
9485 | 2018-09-16 06:26 | 2018-09-16 06:26 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Duri field VCB fdr #4 T/R 1X. Not checked yet. |  | 1 | 6:26 | Morning | Sunday | 2018 | 9
9486 | 2018-09-16 06:26 | 2018-09-21 07:26 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 0 | Checked & found Duri Field ACB fdr#4 T/R 1x Ctr:535-537 R/F:51@1@2,51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 6:26 | Morning | Sunday | 2018 | 9
9487 | 2018-09-16 10:37 | 2018-09-16 10:37 | 13.8KV NORTH DURI FEEDER #11 | Cloudy | Animal | 626 | 10:37 N.Duri VCB fdr #11 T/LO 4x, Ctr: 172-176, R/F: 51 @123 12:12 Cheked and found at recl: 13-F3-49, broken Bushing and dead monkey. Bypass Recl. 13-F3-49, after dismantle the Monkey. 13:08 Blocked and Closed N.Duri fdr#11 and then released the block. Cause:Animal (Monkey). | 123 | 1 | 10:37 | Morning | Sunday | 2018 | 9
9488 | 2018-09-16 11:00 | 2018-09-16 11:00 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Planned Maintenance | 255 | 11:00 Manually Opened Petapahan VCB fdr#3. Cut off and raised up jumper terminal pole. 12:03 Manually Block & Closed the VCB after finished the Jobs Cause: Planned Maintenance. |  | 1 | 11:00 | Morning | Sunday | 2018 | 9
9489 | 2018-09-16 11:09 | 2018-09-16 11:09 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | 11:09 Rangau fdr#2 load drooped 129A (146-17). Cause: Not checked yet. |  | 1 | 11:09 | Morning | Sunday | 2018 | 9
9490 | 2018-09-16 11:09 | 2018-09-21 11:09 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | Checked & found Recl 23BD01 T/R 1x Ctr:345-346 R/F:51. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 11:09 | Morning | Sunday | 2018 | 9
9491 | 2018-09-16 12:35 | 2018-09-16 12:35 | 13.8KV NELLA FEEDER #1 | Rain | Lightning | 108 | Nella vcb fdr#1 T/R 1x. Nella GFPC T/R 1x Ground fault Alarm at Nella fdr#1 Cause: Not checked yet. |  | 1 | 12:35 | Afternoon | Sunday | 2018 | 9
9492 | 2018-09-16 13:08 | 2018-09-16 13:08 | 13.8KV DURI FIELD FEEDER #4 | Rain | Unidentified | 0 | Checked and found, DFSG-13.8ACB51 T/R Counter : 537 - 538 Relay Flag : 51 Patrolled the line but found nothing Cause : Unidentified. |  | 1 | 13:08 | Afternoon | Sunday | 2018 | 9
9493 | 2018-09-16 13:08 | 2018-09-26 12:15 | 13.8KV DURI FIELD FEEDER #4 | Rain | Unidentified | 0 | Checked and found, DFSG-13.8ACB51 T/R Counter : 537 - 538 Relay Flag : 51 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 13:08 | Afternoon | Sunday | 2018 | 9
9494 | 2018-09-16 13:08 | 2018-09-26 13:08 | 13.8KV DURI FIELD FEEDER #4 | Rain | Unidentified | 0 | Checked and found Duri Field 13.8KV VCB fdr#4 T/R 1x ctr: 537-538 R/F: 51 @1, @2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 13:08 | Afternoon | Sunday | 2018 | 9
9495 | 2018-09-16 14:00 | 2018-09-16 14:00 | 13.8KV PETANI FEEDER #1 | Cloudy | Lightning | 83 | Petani VCB fdr #1 T/R 1x Cause: Not checked yet. |  | 1 | 14:00 | Afternoon | Sunday | 2018 | 9
9496 | 2018-09-16 14:00 | 2018-09-21 08:00 | 13.8KV PETANI FEEDER #1 | Cloudy | Lightning | 83 | Checked & found Petani VCB fdr#1 T/R 1x Ctr:86-87 Ctr:51@3. Patrolled the line & found @3 Broken LA on T/P Petani#25. Cause : Lightning. |  | 1 | 14:00 | Afternoon | Sunday | 2018 | 9
9497 | 2018-09-16 14:04 | 2018-09-16 14:04 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 0 | 14:04 By passed & Opened CKB VCB fdr#1 to Function Test & Trouble Shoot the Breaker above 14:12 Normalized back the VCB after finished the Jobs Cause: Planned Maintenace |  | 1 | 14:04 | Afternoon | Sunday | 2018 | 9
9498 | 2018-09-16 15:48 | 2018-09-16 15:48 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 49 | Ketigul VCB fdr#2 T/R 1x Not checked yet |  | 1 | 15:48 | Afternoon | Sunday | 2018 | 9
9499 | 2018-09-16 15:48 | 2018-09-21 07:48 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 49 | Checked & found Ketigul VCB fdr#2 T/R 1x Ctr:296-297 R/F:51@2. Patrolled the line & found @2 Flashed over Dead End Insulator o/p 29AL10. Cause : Dead End Insulator. |  | 1 | 15:48 | Afternoon | Sunday | 2018 | 9
9500 | 2018-09-17 07:14 | 2018-09-17 07:14 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | N.Duri OCB fdr #11 T/R 1X. Not checked yet. |  | 1 | 7:14 | Morning | Monday | 2018 | 9
9501 | 2018-09-17 07:14 | 2018-09-21 07:14 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | Checked & found N.Duri VCB fdr#11 T/R 5x Ctr:172-178 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 7:14 | Morning | Monday | 2018 | 9
9502 | 2018-09-17 08:59 | 2018-09-17 08:59 | 13.8KV PETANI FEEDER #1 | Cloudy | Lightning | 106 | 08:59 Petani OCB Fdr #1 T/R 1x. Not checked yet. 21:26 Petani 13.8KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 8:59 | Morning | Monday | 2018 | 9
9503 | 2018-09-17 08:59 | 2018-09-21 08:59 | 13.8KV PETANI FEEDER #1 | Cloudy | Lightning | 106 | Checked & found Petani VCB fdr#1 T/R1x Ctr:87-88 R/F:51@3. Patrolled the line & found @3 Broken LA o/p 33AY37. Cause : Lightning. |  | 1 | 8:59 | Morning | Monday | 2018 | 9
9504 | 2018-09-17 10:31 | 2018-09-17 10:31 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Under investigation | 10 | 10:31 Duri Community ACB fdr#1 T/O Checked & found, Ctr: 132-133, R/F: None 10:52 Manually Block & Closed DCom ACB fdr#1, then released the block Cause: Under Investigation |  | 1 | 10:31 | Morning | Monday | 2018 | 9
9505 | 2018-09-17 17:37 | 2018-09-17 17:37 | NEW KOTABATAK SUBSTATION | Fair | Equipment Failure | 354 | 17:37 It was reported no Power at NKBS fdr #3 and NKBS fdr #4. (NKBS RTU and OKB RTU failed). 18:27 Manually Open CKBS fdr #6. 19:00 Manually Open CKBS fdr #5. 19:19 Manually Open CKBS fdr #1. 19:22 Checked and found NKBS 115KV S/C T/O ctr:...........R/F: 86HR (reset OK). Checked the TX and found normal. 19:30 Manually Open NKBS fdr #3. 19:30 Manually Open NKBS fdr #4. 19:30 Manually Open NKBS fdr #5. 19:56 Closed NKBS 115KV S/C, but tripped again ctr:.............R/F: 86HR (Can not be reseted). 19:58 Manually open OKB fdr #2, 21:55 Closed CKB VCB fdr#1 | 0 | 1 | 17:37 | Afternoon | Monday | 2018 | 9
9506 | 2018-09-17 17:37 | 2018-09-18 00:22 | NEW KOTABATAK SUBSTATION | Fair | Equipment Failure | 354 | 00:22 Open CKBS fdr #4 Closed LBS 1-3 (to parallel line CKBS fdr #3 with CKBS fdr #4) 00:36 Close CKBS fdr #3 (transfer load of CKBS fdr #4 to CKBS fdr #3) 01:08 Close LBS 37-CV-13 (transfer NKBS fdr #4 to CKBS fdr #3) 01:46 Close LBS 37-CV-61 (NKBS fdr #4 parallel to NKBS fdr #5) 09:10 Closed CKB VCB fdr#6 (Field Power) 11:00 Continued trouble shoot The Relay, the Problem still not solved yet. 12:29 Open Isolation switch of NKB VRTX, Fdr#1, Fdr#2, Fdr#3 Manually Closed NKB VCB fdr#5, from Local, Supplied from CKB fdr#3 16:52 Closed CKB VCB fdr#4, Parallel CKB fdr#4 & CKB#5 16:53 Opened LBSCKB 3-1, Se[arate CKB fdr#3 from CKB fdr#4 16:54 Opened CKB VCB fdr#3 16:55 Closed CKB VCB fdr#2 17:00 Closed LBS KB 100 Opened LBS KB 101 Result: CKB fdr#4 Carried NKB fdr#4 & NKB fdr#5 CKBS fdr#2 Carried CKB fdr#2 & part of CKB fdr#4 19:04 Closed CKBS fdr #5. Under investigation. Prod. Loss : - 17 Sept = 231 wells / 1959 Bbls - 18 Sept = OKB fdr #2 = 62 wells / 2146 Bbls CKB fdr #1 = 29 wells / 1515 Bbls CKB fdr #5 = 47 wells / 1762 Bbls CKB fdr #6 = 35 wells / 569 Bbls NKB fdr #3 = 16 wells / 226 Bbls NKB fdr #4 = 9 wells / 190 Bbls - Total = 1959 Bbls + 6408 Bbls = 8367 Bbls | 0 | 1 | 17:37 | Afternoon | Monday | 2018 | 9
9507 | 2018-09-17 17:37 | 2018-09-19 17:10 | NEW KOTABATAK SUBSTATION | Fair | Equipment Failure | 354 | 17:10 Perform SP to Normalize NKB Substation after Replaced the TX Relay. 17:12 Opened NKB VCB fdr#5 (De energized NKB Buss) 17:16 Closed isolation Switch VR#1 17:18 Closed Isolation switch C/S#1, & Opened Personal Ground) 17:19 Closed C/S#1 (Power TX Energized) 18:07 Closed NKB VCB fdr#5 (NKB fdr#4 & #5 Parallel) Opened LBS 37.CV.61 (NKB fdr#4 & #5 Separated) 17:38 Block & Closed OKB VCB fdr#2, then released the block Cause: Under investigation | 0 | 1 | 17:37 | Afternoon | Monday | 2018 | 9
9508 | 2018-09-18 06:23 | 2018-09-18 06:23 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 78 | 06:23 Petani 13.8KV OCB fdr #1 T/R 1X. Not checked yet. 13:12 Petani 13.8KV OCB fdr#1 T/R 1x again. Not checked yet. |  | 1 | 6:23 | Morning | Tuesday | 2018 | 9
9509 | 2018-09-18 06:23 | 2018-09-21 08:23 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 78 | Checked & found Petani VCB fdr#1 T/R 1x Ctr:88-89 R/F:51#3. Patrolled the line & found @3 Broken LA on T/P Petani#25. Cause : Lightning. |  | 1 | 6:23 | Morning | Tuesday | 2018 | 9
9510 | 2018-09-18 12:22 | 2018-09-18 12:22 | 13.8KV 5B FEEDER #1 | Fair | Planned Maintenance | 172 | 12:22 Manually Opened 5B VCB fdr#1 to Repair Hot spot at Rcl 5B-06 16:35 Manually Block & Closed the VCB, then released the block after finished the jobs Cause: Planed Maintence |  | 1 | 12:22 | Afternoon | Tuesday | 2018 | 9
9511 | 2018-09-18 13:32 | 2018-09-18 13:32 | 13.8KV 4B FEEDER #2 | Fair | Others | 22 | 13:27 4B VCB fdr#1 T/SO (in block Status) The VCB trip when Opened LBS 5B-128 to separate 4B Fdr#2 from 5B fdr#1 (Any Spark at LBS Interrupter) 13:32 Manually Block & Closed the VCB, then released the block Cause: Interrupter |  | 1 | 13:32 | Afternoon | Tuesday | 2018 | 9
9512 | 2018-09-18 15:50 | 2018-09-18 15:50 | 13.8KV 5B FEEDER #3 | Fair | Planned Maintenance | 23 | 15:50 Manually Opened 5B VCB fdr#3 to Replaced 500KVATX at Well 4D-41N (with the same size) 16:55 Manually Block & Closed the VCB after finished the Jobs Cause: Planned Maintenance |  | 1 | 15:50 | Afternoon | Tuesday | 2018 | 9
9513 | 2018-09-18 17:37 | 2018-09-18 17:37 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 404 | C.Duri ACB fdr#14 T/R 1x, Ctr: 396-397, R/F: 51@1@2@3, 51N Not Checked Yet |  | 1 | 17:37 | Afternoon | Tuesday | 2018 | 9
9514 | 2018-09-18 17:37 | 2018-09-25 07:37 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 404 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:37 | Afternoon | Tuesday | 2018 | 9
9515 | 2018-09-19 10:40 | 2018-09-19 10:40 | 13.8KV 6DN FEEDER #2 | Fair | Planned Maintenance | 25 | 10:40 Manually open Recl 6D-200 (6DN fdr#2). Replaced Broken Dead End Insulator o/p NN. 11:45 Blocked & closed Recl. 6D-200, then release the block. Cause: Plan Maintenance. |  | 1 | 10:40 | Morning | Wednesday | 2018 | 9
9516 | 2018-09-19 13:50 | 2018-09-19 13:50 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 0 | 13:50 Manually opened Recl. 23BW02 (Libo fdr#2). Cut Jumper at well Hitam#08. 16:18 Blocked & closed Recl. 23BW02, then release the block. Plan Maintenance. |  | 1 | 13:50 | Afternoon | Wednesday | 2018 | 9
9517 | 2018-09-19 14:45 | 2018-09-19 14:45 | 13.8KV 6D FEEDER #5 | Fair | Construction Job | 0 | 14:45 Manually Opened Recl. 5D-10 (6D fdr#5). C/O VSD to Switch board at well 5d-45. Replaced 550 Kva Tx with the same sizeat well 5D-25N. 16:30 Blocked & Closed Recl. 5D-10, then release the block. Cause: Construction Job. |  | 1 | 14:45 | Afternoon | Wednesday | 2018 | 9
9518 | 2018-09-19 14:58 | 2018-09-19 14:58 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | It was reported B/O fuse o/p 01-3-07 & 01-3-08 (C.Duri fdr#14). Not checked yet. |  | 1 | 14:58 | Afternoon | Wednesday | 2018 | 9
9519 | 2018-09-19 14:58 | 2018-09-25 08:58 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 14:58 | Afternoon | Wednesday | 2018 | 9
9520 | 2018-09-19 15:12 | 2018-09-19 15:12 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 16 | 15:12-17:00 Block Bangko fdr#4 & GFPC. Open/Closed HLC o/p 24Z24 for Replaced Broken LA on TOP well Bko#178, #271, #269. (3Well S/D during the job). Cause: Plan Maintenance. |  | 1 | 15:12 | Afternoon | Wednesday | 2018 | 9
9521 | 2018-09-19 15:16 | 2018-09-19 15:16 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 105 | 15:12 Petani VCB fdr#1 T/R 1x. (Test 2 Pump). Not checked yet. 21:32 Petani VCB fdr#1 T/R 1x. Petani VCBfdr#2 load dropped 37A (65-28A) Not checked yet. |  | 1 | 15:16 | Afternoon | Wednesday | 2018 | 9
9522 | 2018-09-19 15:16 | 2018-09-21 08:16 | 13.8KV PETANI FEEDER #1 | Fair | Lightning | 105 | Checked & found Petani VCB fdr#1 T/R 1x Ctr:89-90 R/F:51@3. Patrolled the line & found @3 Broken LA o/p 33AY37. Cause : Lightning. |  | 1 | 15:16 | Afternoon | Wednesday | 2018 | 9
9523 | 2018-09-19 16:05 | 2018-09-19 16:05 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 105 | 16:05 Bangko VCB fdr#4 T/O, (In Block status) 16:10 Block & Closed BKO VCB fdr#4 but Fail, from DSC. Checked & found BKI Fdr#4 T/O, Ctr: 50-51, R/F: 51@1 16:59 Block & Closed BKO VCB fdr#4, OK, Keep in Block Patrolled the Line, found Rcl 25.Z07 T/SO, Ctr: 204-205, toward Benar Field 17:12 Block & Closed the Recloser, Ok, then released the block. Cause: Unidentified |  | 1 | 16:05 | Afternoon | Wednesday | 2018 | 9
9524 | 2018-09-20 12:27 | 2018-09-20 12:27 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 67 | Bangko 13.8KV OCB fdr#4 T/R 1x. Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 12:27 | Afternoon | Thursday | 2018 | 9
9525 | 2018-09-20 12:27 | 2018-09-21 16:00 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 67 | Checked and found 13.8KVBKOFDR4 T/R 1X R/F 51N Counter : 51-52. Patrolled and found nothing (normal operation). Cause : Lightning |  | 1 | 12:27 | Afternoon | Thursday | 2018 | 9
9526 | 2018-09-20 18:11 | 2018-09-20 18:11 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Pin Insulator | 0 | Duri Comminity ACB#33 fdr#5 T/R 1x. Not checked yet. |  | 1 | 18:11 | Afternoon | Thursday | 2018 | 9
9527 | 2018-09-20 18:11 | 2018-09-25 08:11 | 13.8KV DURI COMMUNITY FEEDER #5 | Fair | Pin Insulator | 0 | Checked & found Duri Community ACB fdr#5 T/R 1x Ctr:121-122 R/F:51@1. Patrolled the line & found @1 Broken Pin Insulator o/p II-12. Cause : Pin Insulator. |  | 1 | 18:11 | Afternoon | Thursday | 2018 | 9
9528 | 2018-09-21 01:00 | 2018-09-21 01:00 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 58 | Nella VCB fdr #2 T/R 1x. Nella GFPC T/R 1x. Not checked yet. |  | 1 | 1:00 | Night | Friday | 2018 | 9
9529 | 2018-09-21 01:00 | 2018-09-21 01:00 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 0 | Nella fdr #1 load dropped 47A (211-164A). Not checked yet. |  | 1 | 1:00 | Night | Friday | 2018 | 9
9530 | 2018-09-21 01:00 | 2018-02-10 01:00 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 0 | Nella fdr #1 load dropped 47A (211-164A). Checked and found Nella GFPC T/R 1X ctr: 803-804 R/F: 51N. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 1:00 | Night | Friday | 2018 | 9
9531 | 2018-09-21 01:12 | 2018-09-21 01:12 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Unidentified (Fuse) | 44 | 6DN OCB fdr #6 T/R 1x. 6DN fdr #4 load dropped 53A (210-157A) --> WIP GS #4. Not checked yet. |  | 1 | 1:12 | Night | Friday | 2018 | 9
9532 | 2018-09-21 01:12 | 2018-02-10 01:12 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Unidentified (Fuse) | 44 | 6DN OCB fdr #6 T/R 1x. 6DN fdr #4 load dropped 53A (210-157A) --> WIP GS #4. Checked and found 6DN 13.8KV OCB fdr #6 T/R 1x ctr:355 (not changed) R/F: 50@1. Patrolled the line and found broken fuse PT o/p: 6E-64. Cause : Unidentified (Fuse). |  | 1 | 1:12 | Night | Friday | 2018 | 9
9533 | 2018-09-21 01:40 | 2018-09-21 01:40 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Unidentified | 15 | 4B VCB fdr #2 T/R 1x. 4B fdr #1 load dropped 22A (126-104A). Not checked yet. |  | 1 | 1:40 | Night | Friday | 2018 | 9
9534 | 2018-09-21 01:40 | 2018-09-25 01:40 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Unidentified | 15 | Checked and found 4BSB-13.8OCB2 T/R 1x R/F:51 @1 Counter: 280 - 281. Patrolled the line and found nothing. Cause : Unidentified |  | 1 | 1:40 | Night | Friday | 2018 | 9
9535 | 2018-09-21 10:32 | 2018-09-21 10:32 | 13.8KV 3D FEEDER #4 | Cloudy | Tree | 473 | 10:32 3D fdr#4 T/LO 3D fdr#2 load dropped 178A (244-66A). 3D fdr#3 load dropped 99A (135-36A). 3D fdr#5 load dropped 52A (108-56A) Pump Off. 13:30 Checked & found 3D OCB fdr#4 T/LO Ctr;11-22 R/F:51@2, 50@2@3. Patrol the line & found danger palm sawit then isolated. 15:50 Blocked & closed 3D OCB fdr#4, then release the blocked. 18:05 It was reported no power at well 2D-33, 2D-22, 1D-74, 1D-35.. (3D fdr#4). 21:38 Checked and found Recloser: 2D-33 T/O Counter: 59-61. 21:43 Blocked and closed Recloser: 2D-33 --> OK and then released the block. Cause: Tree. 22:34 3D OCB fdr #4 T/O. 3D fdr #2 load dropped 190A (237-47A). 3D fdr #3 load dropped 89A (125-36A). 3D fdr #5 load dropped 52A (108-56A) --> WIP GS #5. 22:44 Blocked and closed 3D OCB fdr #4 but failed (from DSC). Production loss: 618 Bbls / 62 wells up to 24:00. | 12345 | 1 | 10:32 | Morning | Friday | 2018 | 9
9536 | 2018-09-21 10:32 | 2018-09-22 01:05 | 13.8KV 3D FEEDER #4 | Cloudy | Tree | 473 | 01:05 Checked and found 3D OCB fdr #4 T/LO Counter: 622-630 R/F: 50@2 , 51@2 , 51@3. 01:07 Blocked and closed 3D OCB fdr #4 --> OK and then released the block. 01:25 Checked and found Recloser 2D-14 T/LO Counter: 84-89. Patrolled the line found nothing. 02:00 Checked and found Recloser: 2D-33 T/LO Counter:61-65. Patrolled the line found Akasia tree touching the line. Unplug Recloser:2D-33 (will be demolish the tree this morning) 02:20 Blocked and close Recloser:2D-14 --> OK and then released the block. 09:00 Cut & trimming Akasia Tree touching power line. 11:35 Blocked & closed Recl. 2D-33, then release the block. Cause: Tree. | 12345 | 1 | 10:32 | Morning | Friday | 2018 | 9
9537 | 2018-09-21 13:46 | 2018-09-21 13:46 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Others | 167 | 13:46 OKB fdr#2 load dropped 127A (223-96A). 14:00 Checked & found recl, 38-CW-08 T/SO Ctr:93-94. Blocked & closed recl, 38-CW-08 ,but failed. Patrolled the line but found kite strung up o/p 39-CX-07. 16:50 Blocked & Closed recl, 38-CW-08. OK then release the blocked. Cause: Other (kite). |  | 1 | 13:46 | Afternoon | Friday | 2018 | 9
9538 | 2018-09-21 14:40 | 2018-09-21 14:40 | 13.8KV 8D FEEDER #1 | Fair | Construction Job | 0 | 14:40 Manually open recl,8F-05 (8Dfdr#1). Install 300Kva Tx for reactive well 8E-57N. 15:10 Blocked &closed recl, 8F-05, then released the block. Cause: Construction job. |  | 1 | 14:40 | Afternoon | Friday | 2018 | 9
9539 | 2018-09-22 23:59 | 2018-09-22 23:59 | CPI POWER SYSTEM | Fair | Normal Condition | - | Normal Condition. |  | 1 | 23:59 | Night | Saturday | 2018 | 9
9540 | 2018-09-23 16:33 | 2018-09-23 16:33 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 0 | Darling VCB Fdr#3 T/R 1x. Not checked yet |  | 1 | 16:33 | Afternoon | Sunday | 2018 | 9
9541 | 2018-09-23 16:33 | 2018-09-26 06:09 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 0 | Checked and found, DRLG3-13.8VCB3 None Counter : 248 - 248 Relay Flag : 50 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 16:33 | Afternoon | Sunday | 2018 | 9
9542 | 2018-09-23 17:51 | 2018-09-23 17:51 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 221 | 17:51 C.Duri fdr#1 Load dropped 50A (103-53A). 19:10 Checked and found Recloser: 39-AV-36 T/O (In blocked position) Counter: 160-161. Due to RIG activity at well Puncak #05. Patrolled the line nothing found. 20:58 Blocked and close Recloser: 39-AV-36 --> OK (still in block position). Cause: Unidentified. |  | 1 | 17:51 | Afternoon | Sunday | 2018 | 9
9543 | 2018-09-23 20:27 | 2018-09-23 20:27 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Unidentified | 0 | Duri Field VCB #51 (feeder #4) T/R 1x. Not checked yet. |  | 1 | 20:27 | Night | Sunday | 2018 | 9
9544 | 2018-09-23 20:27 | 2018-09-25 09:27 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 20:27 | Night | Sunday | 2018 | 9
9545 | 2018-09-23 20:43 | 2018-09-23 20:43 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Dead End Insulator | 0 | C Duri ACB #41 (feeder #9) T/R 1x Ctr:394-395 R/F: 50@1. Not patrolled yet. |  | 1 | 20:43 | Night | Sunday | 2018 | 9
9546 | 2018-09-23 20:43 | 2018-09-29 20:43 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Dead End Insulator | 0 | Patrolled the line and found Dead End Insulator o/p: 04-07-27. Cause : Dead End Insulator. |  | 1 | 20:43 | Night | Sunday | 2018 | 9
9547 | 2018-09-23 20:45 | 2018-09-23 20:45 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Unidentified | 0 | C Duri feeder #7 load dropped 68A (91-23A). Not checked yet. |  | 1 | 20:45 | Night | Sunday | 2018 | 9
9548 | 2018-09-23 20:45 | 2018-09-29 20:45 | 13.8KV CENTRAL DURI FEEDER #7 | Rain and Lightning | Unidentified | 0 | Checked and found Recloser 03-03-42 T/R 1X ctr: 170-171 R/F: 51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 20:45 | Night | Sunday | 2018 | 9
9549 | 2018-09-23 22:37 | 2018-09-23 22:37 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 0 | S Balam fdr #4 load dropped 60A (186-126A). S Balam GFPC T/R 1x fault alarm on S Balam fdr #4. Not checked yet. |  | 1 | 22:37 | Night | Sunday | 2018 | 9
9550 | 2018-09-23 22:37 | 2018-09-30 22:37 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found Recl. 16AB03 T/R 1x Ctr:459-460 R/F:51@1@2. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 22:37 | Night | Sunday | 2018 | 9
9551 | 2018-09-23 22:47 | 2018-09-23 22:47 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 19 | 22:47 Ketigul fdr #2 load dropped 19A (216-197A). It was reported no power at Sikeladi field. 02:37 Checked and found Recloser: 27-AL-21 T/O Counter: 543-544 (In block position) Due to Rig activity at well Sikeladi #18. 02:40 Blocked and close Recloser: 27-AL-21 --> OK (still in block position). Cause: Not patrolled yet. |  | 1 | 22:47 | Night | Sunday | 2018 | 9
9552 | 2018-09-24 09:00 | 2018-09-24 09:00 | MINAS POWER PLANT |  |  | - | 09:00 S/U Mgt#6, then O/L the unit at 09:36. |  | 1 | 9:00 | Morning | Monday | 2018 | 9
9553 | 2018-09-24 10:05 | 2018-09-24 10:05 | MINAS POWER PLANT |  |  | - | 10:05 Off line MGT#8, then O/L the unit at 10:19. (Transfer Gas to Distillate Test). 14:08 Off line MGT#8, then S/D the unit for Maintenance. |  | 1 | 10:05 | Morning | Monday | 2018 | 9
9554 | 2018-09-24 11:05 | 2018-09-24 11:05 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 0 | 11:05 Manually Open LBS 9D-96 (8C fdr#1). Replaced Tx at well 8E-93. 11:30 Closed LBS 9D-96. Cause: Plan Maintenance. |  | 1 | 11:05 | Morning | Monday | 2018 | 9
9555 | 2018-09-24 13:28 | 2018-09-24 13:28 | MINAS POWER PLANT |  |  | - | 13:28 Off line MGT#7, then O/L the unit at 14:00. |  | 1 | 13:28 | Afternoon | Monday | 2018 | 9
9556 | 2018-09-25 08:43 | 2018-09-25 08:43 | MINAS POWER PLANT | Fair | Under investigation | 0 | MGT#5 Trip by alarm Exciter Trip. |  | 1 | 8:43 | Morning | Tuesday | 2018 | 9
9557 | 2018-09-25 08:43 | 2018-09-25 08:43 | 13.8KV MINAS FEEDER #6 | Fair | Unidentified | 135 | 08:43 Minas ACB fdr#6 T/LO Ctr:174-176 R/F:51@1@2. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 8:43 | Morning | Tuesday | 2018 | 9
9558 | 2018-09-25 09:16 | 2018-09-25 09:16 | MINAS POWER PLANT |  |  | - | 09:16 S/U MGT#3, then on line the unit at 09:43. |  | 1 | 9:16 | Morning | Tuesday | 2018 | 9
9559 | 2018-09-25 10:28 | 2018-09-25 10:28 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 0 | 10:28 Manually opened LBS 9D-96 (8C fdr#1). Replaced 550Kva Tx with 260Kva Tx at well 8E-93. 10:58 Closed LBS 9D-96. Cause: Plan Maintenance. |  | 1 | 10:28 | Morning | Tuesday | 2018 | 9
9560 | 2018-09-25 11:22 | 2018-09-25 11:22 | 13.8KV MINAS FEEDER #2 | Fair | Planned Maintenance | 0 | 11:22 Manually opened Recl. M2-01 (Minas fdr#2). Replaced 400Kva Tx with 150Kva Tx at well 7E-31. 11:55 Blocked & closed Recl: M2-01, then release the block. Cause: Plan Maintenance. |  | 1 | 11:22 | Morning | Tuesday | 2018 | 9
9561 | 2018-09-25 14:00 | 2018-09-25 14:00 | 13.8KV 6DN FEEDER #6 | Fair | Planned Maintenance | 19 | 14:00 Manually Opened Recl. 6E-30 (6DN fdr#6). Replaced Broken Pin Insulator on T/P well 6E-72. 14:25 Blocked & closed Recl 6E-30, then release the block. Cause: Plan Maintenance. |  | 1 | 14:00 | Afternoon | Tuesday | 2018 | 9
9562 | 2018-09-25 21:10 | 2018-09-25 21:10 | 13.8KV DARLING VCB FEEDER #3 | Fair | Broken Fuse Cut Out | 0 | 21:10 It was reported spark on FCO at CGS #5 D/S Darling fdr #3. 21:30 Checked and found spark on FCO for 2.5 Mva Tx #A at CGS #5. 00:16 Transfer Load Tx #A to Tx #B by closed Tie breaker. Cause: Broken Fuse Cut Out. |  | 1 | 21:10 | Night | Tuesday | 2018 | 9
9563 | 2018-09-25 23:59 | 2018-09-25 23:59 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 0 | Pinang OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 23:59 | Night | Tuesday | 2018 | 9
9564 | 2018-09-26 06:36 | 2018-09-26 06:36 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 84 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 6:36 | Morning | Wednesday | 2018 | 9
9565 | 2018-09-26 06:36 | 2018-09-30 20:36 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 84 | Checked & found Ketigul VCB fdr#2 T/R 2x Ctr:297-299 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 6:36 | Morning | Wednesday | 2018 | 9
9566 | 2018-09-26 11:35 | 2018-09-26 11:35 | 13.8KV BATANG FEEDER #2 | Fair | Construction Job | 0 | 11:35 Open HLC o/p 37-AL-01. Tie In New power line at well Pemburu # 32. two well off (Pemburu # 17 and # 21) during the JOB. Cause: Contruction. |  | 1 | 11:35 | Morning | Wednesday | 2018 | 9
9567 | 2018-09-26 13:14 | 2018-09-26 13:14 | 13.8KV RANGAU FEEDER #2 | Rain | Unidentified | 0 | 13:14 Rangau fdr #2 load dropped 146A (157-11A). Rangau fdr #1 load dropped 11A (64=53A). Not checked yet. |  | 1 | 13:14 | Afternoon | Wednesday | 2018 | 9
9568 | 2018-09-26 13:14 | 2018-09-29 13:14 | 13.8KV RANGAU FEEDER #2 | Rain | Unidentified | 0 | Checked & found Recl. 23BD01 T/R 1x Ctr:346-347 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 13:14 | Afternoon | Wednesday | 2018 | 9
9569 | 2018-09-26 13:40 | 2018-09-26 13:40 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Unidentified | 15 | Petani 13.8KV OCB fdr #2 T/R 1X. Petani fdr #1 load dropped 77A (221-144A). Not checked yet. |  | 1 | 13:40 | Afternoon | Wednesday | 2018 | 9
9570 | 2018-09-26 13:40 | 2018-09-29 13:40 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Unidentified | 15 | Checked & found Petani VCB fdr#2 T/R 1x Ctr:257-258 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 13:40 | Afternoon | Wednesday | 2018 | 9
9571 | 2018-09-26 14:32 | 2018-09-26 14:32 | KETIGUL SUBSTATION | Rain | Under investigation | 890 | 14:32 Ketigul 115KV OCB #2 T/O. Ketigul 115KV OCB #3 T/O. (No power to Ketigul Substation). 17:00 Checked and found : Ketigul 115KV OCB #2 T/O, ---->Closed at 17:24 ctr:174. Ketigul 115KV OCB #3 T/O, ---->Closed at 17:32 ctr: 165. Checked TX condition, OK R/F: 51N. Also found R/F: 51N at ketigul fdr #2. 17:15 Open Ketigul fdr #1, ---->Closed at 17:30 ctr:206. Open Ketigul fdr #2, ---->Closed at 17:31 ctr:299. Open Ketigul fdr #3, ---->Closed at 17:32 ctr:203. Cause: Under investigation. | 1234 | 1 | 14:32 | Afternoon | Wednesday | 2018 | 9
9572 | 2018-09-26 18:16 | 2018-09-26 18:16 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Recloser - Control Recloser | 0 | 4D Fdr#5 Load dropped 165A (252-67A) Not checked yet |  | 1 | 18:16 | Afternoon | Wednesday | 2018 | 9
9573 | 2018-09-26 18:16 | 2018-09-27 01:30 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Recloser - Control Recloser | 0 | 01:30 It was reported No power under 4D fdr #2. 06:30 Checked and found Recl.: 4D-204 T/SO ctr: (Blank). Blocked and closed the Recl. but failed (suspected Control problem). 10:40 Continued to check and found Recl.: 4D-14A T/SO ctr:52-53. 10:45 Blocked and closed Recl. : 4D-14A, OK then released the block. Continued to patrolled the line but found nothing. 11:35 Blocked and closed Recl.: 4D-204, OK then energized the block. Cause: Control Recloser. |  | 1 | 18:16 | Afternoon | Wednesday | 2018 | 9
9574 | 2018-09-26 19:24 | 2018-09-26 19:24 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 8 | Libo VCB FDR#1 T/R 1x Not checked yet |  | 1 | 19:24 | Night | Wednesday | 2018 | 9
9575 | 2018-09-26 19:24 | 2018-09-29 19:24 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 8 | Checked & found Libo VCB fdr#1 T/R 1x Ctr:579-580 R/F:50@1@2. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 19:24 | Night | Wednesday | 2018 | 9
9576 | 2018-09-26 19:29 | 2018-09-26 19:29 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 0 | Pungut VCB fdr#2 T/R 1x Not checked yet |  | 1 | 19:29 | Night | Wednesday | 2018 | 9
9577 | 2018-09-26 19:29 | 2018-09-29 19:29 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found Petani VCB fdr#2 T/R 1x Ctr:417-418 R/F:51@2@3. Patrolled the line & found @2 Broken LA on T/P Piala#01. @3 Flash Over Pin Insulator o/p PK-09. Cause : Lightning. |  | 1 | 19:29 | Night | Wednesday | 2018 | 9
9578 | 2018-09-26 19:38 | 2018-02-10 07:42 | MINAS SWITCH YARD | Rain and Lightning | Unidentified | 0 | Checked and found MNSSY-115GCB31 Counter : 195 - 195 Relay Flag : NONE Patrolled the line but found nothing Cause : Unidentified |  | 1 | 19:38 | Night | Wednesday | 2018 | 9
9579 | 2018-09-26 19:38 | 2018-02-10 07:42 | MINAS SWITCH YARD | Rain and Lightning | Unidentified | 0 | Checked and found MNSSY-115GCB31 Counter : 195 - 195 Relay Flag : NONE Patrolled the line but found nothing Cause : Unidentified |  | 1 | 19:38 | Night | Wednesday | 2018 | 9
9580 | 2018-09-26 19:38 | 2018-11-10 17:00 | MINAS SWITCH YARD | Rain and Lightning | Unidentified | 0 | Checked & found; Minas 115KV GCB #31 & GCB #33 are Not real Trip or Reclose, Counter and Relay flag not changes patrolled the line, but found nothing Cause : Unidentified |  | 1 | 19:38 | Night | Wednesday | 2018 | 9
9581 | 2018-09-26 19:53 | 2018-09-26 19:53 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 0 | 8D Fdr#11 Load dropped 68A (134-48A) Not checked yet |  | 1 | 19:53 | Night | Wednesday | 2018 | 9
9582 | 2018-09-26 19:53 | 2018-08-10 07:53 | 13.8KV 8D FEEDER #11 | Rain and Lightning | Lightning | 0 | 8D Fdr#11 Load dropped 68A (134-48A) Checked and found 5442-R.9E02 T/R 1x Counter: 1066 - 1067. Patrolled the line and found nothing. Cause : Lightning |  | 1 | 19:53 | Night | Wednesday | 2018 | 9
9583 | 2018-09-26 20:30 | 2018-09-26 20:30 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 13 | 3D VCB fdr#3 T/R 1x Not checked yet |  | 1 | 20:30 | Night | Wednesday | 2018 | 9
9584 | 2018-09-26 20:30 | 2018-09-29 12:30 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 13 | Checked and found, 3D OCB fdr#3 T/R 1x, Ctr: 444-445, R/F: 50 Patrolled the Line, but found nothing. Cause: Lightning |  | 1 | 20:30 | Night | Wednesday | 2018 | 9
9585 | 2018-09-26 20:30 | 2018-09-26 20:30 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Unidentified | 0 | 3d Fdr#2 Load dropped 78A (245-167A) Not checked yet |  | 1 | 20:30 | Night | Wednesday | 2018 | 9
9586 | 2018-09-26 20:30 | 2018-09-30 07:42 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found 3DSB-13.8OCB2 Counter : 262 - 262 Relay Flag : NONE Patrolled the line found Not Trip..Normal Cause : Unidentified |  | 1 | 20:30 | Night | Wednesday | 2018 | 9
9587 | 2018-09-26 20:30 | 2018-11-10 17:08 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found, all Recloser under 3D OCB fdr#2 are normal conditions Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 20:30 | Night | Wednesday | 2018 | 9
9588 | 2018-09-26 20:30 | 2018-09-29 07:42 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found 3DSB-13.8OCB4 Counter : - Relay Flag : NONE Patrolled the line found Not trip..Normal |  | 1 | 20:30 | Night | Wednesday | 2018 | 9
9589 | 2018-09-26 20:30 | 2018-09-29 07:42 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found 3DSB-13.8OCB4 Counter : - Relay Flag : NONE Patrolled the line found Not trip..Normal |  | 1 | 20:30 | Night | Wednesday | 2018 | 9
9590 | 2018-09-26 20:30 | 2018-11-10 17:08 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found All Recloser under 3D OCB fdr#4 are normal condition, Counter & Relay flag are not changes Cause: Unidentified |  | 1 | 20:30 | Night | Wednesday | 2018 | 9
9591 | 2018-09-26 20:34 | 2018-09-26 20:34 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 44 | 4B VCB fdr#2 T/R 1x Not checked yet |  | 1 | 20:34 | Night | Wednesday | 2018 | 9
9592 | 2018-09-26 20:34 | 2018-07-10 09:24 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 44 | Checked and found 4B VCB fdr#2 T/R 1x Counter: 280-281 R/F: 51N. Patrolled the line found @1 broken dead end insulator on pole 5A-19. Cause: Lightning. |  | 1 | 20:34 | Night | Wednesday | 2018 | 9
9593 | 2018-09-27 02:07 | 2018-09-27 02:07 | 13.8KV PETAPAHAN FEEDER #2 | Rain and Lightning | Unidentified | 0 | Petapahan Fdr#2 Load dropped 82A (82-0A) Not checked yet. |  | 1 | 2:07 | Night | Thursday | 2018 | 9
9594 | 2018-09-27 02:07 | 2018-09-29 02:07 | 13.8KV PETAPAHAN FEEDER #2 | Rain and Lightning | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 2:07 | Night | Thursday | 2018 | 9
9595 | 2018-09-27 02:07 | 2018-09-27 02:07 | 13.8KV PETAPAHAN FEEDER #7 | Rain and Lightning | Unidentified | 0 | Petapahan Fdr#7 Load drpped 48A (61-13A) Not checked yet |  | 1 | 2:07 | Night | Thursday | 2018 | 9
9596 | 2018-09-27 02:07 | 2018-09-29 02:07 | 13.8KV PETAPAHAN FEEDER #7 | Rain and Lightning | Unidentified | 0 | Petapahan Fdr#7 Load drpped 48A (61-13A). Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 2:07 | Night | Thursday | 2018 | 9
9597 | 2018-09-27 07:51 | 2018-09-27 07:51 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 601 | 07:51 C.Duri fdr#1 load dropped 25A (99-74A). It was reported no power at well Puncak GS. 10:15 Checked and found recl, 41 AW 62 T/LO. Patrolled the line and found @2 broken pin insulation O/P 39 AV 27. 13:20 Replaced @2 broken Pin Insulator above. 13:28 Closed Recl.: 41-AW-62. Cause: Pin Insulator. | 1234 | 1 | 7:51 | Morning | Thursday | 2018 | 9
9598 | 2018-09-27 09:03 | 2018-09-27 09:03 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Tree | 158 | 09:03 Ketigul fdr#2 load dropped 175A (218-43A). Not checked yet. 15:44 It was reported no power at Sikladi Field (Ketigul Fdr#2) 18:20 Checked & found Recl. 26-AK-02 T/LO, Ctr: 202-206 Patrolled the Line, but found nothing. 18:40 Block & Closed the Recloser, but Trip again Repatrolled the line, found Fall down Tree at Well Ubi#31 20:57 Block & Closed Recl 26-AK-02, then released the block After Dismantled Fallen Trees Cause: TREE |  | 1 | 9:03 | Morning | Thursday | 2018 | 9
9599 | 2018-09-27 10:35 | 2018-09-27 10:35 | 13.8KV 4D FEEDER #4 | Fair | Planned Maintenance | 0 | 10:35 Open recl,4D-85 d/s (4D fdr#4). Replaced 550Kva Tx at well 5D-14. 11:35 Closed recl,4D-85. Cause : Plan maintenance. |  | 1 | 10:35 | Morning | Thursday | 2018 | 9
9600 | 2018-09-27 14:44 | 2018-09-27 14:44 | 13.8KV KETIGUL FEEDER#3 | Fair | Emergency | 9 | 14:40 Manually open Ketigul 13.8KV VCB fdr #3. Open HLC o/p: 32-AS-04 to isolate Pole fell at well Gulamo # 02. 15:15 Closed Ketigul 13.8KV VCB fdr #3. Emergency. |  | 1 | 14:44 | Afternoon | Thursday | 2018 | 9
9601 | 2018-09-27 17:17 | 2018-09-27 17:17 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Lightning | 0 | Duri Comm. 13.8KV ACB fdr #3 T/R 1X. Not checked yet. |  | 1 | 17:17 | Afternoon | Thursday | 2018 | 9
9602 | 2018-09-27 17:17 | 2018-01-10 15:46 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Lightning | 0 | Checked & found DComm ACB fdr#3 T/R 1x, Ctr: 83-84, R/F: 51 @2 Patrolled the Line, found @2 broken Pin Insulator O/P 6-F3 Cause : Lightning |  | 1 | 17:17 | Afternoon | Thursday | 2018 | 9
9603 | 2018-09-28 06:20 | 2018-09-28 06:20 | MINAS SWITCH YARD | Fair | Unidentified | 0 | 115KV Minas switch yard GCB #21 T/R 1x. 115KV Minas switch yard GCB #23 T/R 1x. 115KV Minas switch yard GCB #43 T/R 1x. 115KV Minas switch yard GCB #51 T/R 1x. Not checked yet. |  | 1 | 6:20 | Morning | Friday | 2018 | 9
9604 | 2018-09-28 06:20 | 2018-10-10 09:20 | MINAS SWITCH YARD | Fair | Unidentified | 0 | Checked & found, No Breaker activity, normal operation (Counter Not change) MNSSY-115 KV GCB#31 MNSSY-115 KV GCB#33 MNSSY-115 KV GCB#43 MNSSY-115 KV GCB#51 MNSSY-115 KV GCB#21 MNSSY-115 KV GCB#23 Cause : Unidentified (Suspected Server Error) |  | 1 | 6:20 | Morning | Friday | 2018 | 9
9605 | 2018-09-28 14:50 | 2018-09-28 14:50 | 13.8KV CENTRAL DURI FEEDER #4 | Cloudy | Unidentified | 0 | 14:50 C.Duri 13.8Kv ACB Fdr#4 R/T 1x. Not Checked yet. |  | 1 | 14:50 | Afternoon | Friday | 2018 | 9
9606 | 2018-09-28 14:50 | 2018-01-10 15:48 | 13.8KV CENTRAL DURI FEEDER #4 | Cloudy | Unidentified | 0 | Checked & found CDuri ACB fdr#4 T/R 1x, Ctr: 510-511, R/F: 51N Patrolled the Line, but found nothing Cause: Unidentified |  | 1 | 14:50 | Afternoon | Friday | 2018 | 9
9607 | 2018-09-28 15:10 | 2018-09-28 15:10 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 84 | 15:10 Manually open Reclocer 36-CT-10 d/s CKBS Fdr#1 replaced 550Kv - 600Kv R/M.140 Hp-300 Hp V.2400 Volt Cause: Plan Maintenance. |  | 1 | 15:10 | Afternoon | Friday | 2018 | 9
9608 | 2018-09-28 18:50 | 2018-09-28 18:50 | 13.8KV DARLING VCB FEEDER #7 | Cloudy | Unidentified | 0 | Darling VCB fdr#7 T/R 1x. Not checked yet. |  | 1 | 18:50 | Afternoon | Friday | 2018 | 9
9609 | 2018-09-28 18:50 | 2018-09-30 18:50 | 13.8KV DARLING VCB FEEDER #7 | Cloudy | Unidentified | 0 | Checked & found Darling VCB fdr#7 T/R 1x Ctr:170-171 R/F:50N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 18:50 | Afternoon | Friday | 2018 | 9
9610 | 2018-09-29 09:29 | 2018-09-29 09:29 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Tree | 84 | 09:29 CD fdr #1 Load Drop 8 A (94 -8 8 A) it was reported no power o/p 09-L7-01 to 09-L1-19 10:37 Checked and found RCL 09-L7-01 T/LO (counter: 246 - 250) Patrolled the line and found fall tree on pole 09-L7-07 14:17 Manually close RCL 09-L7-01 Cause: Tree Prod Loss = 99.9 Bbls / 32 wells. |  | 1 | 9:29 | Morning | Saturday | 2018 | 9
9611 | 2018-09-29 11:23 | 2018-09-29 11:23 | 13.8KV BATANG FEEDER #3 | Fair | Construction Job | 0 | 11:23 Manually Open Batang 13.8KV VCB fdr #3. Tie in new power line at well Pemburu #1. 14:53 Closed Batang 13.8KV VCB fdr #3. Contruction JOB. |  | 1 | 11:23 | Morning | Saturday | 2018 | 9
9612 | 2018-09-30 15:52 | 2018-09-30 15:52 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | C.Duri 13.8Kv ACB#13 fdr#3 T/R 1x. Not checked yet. |  | 1 | 15:52 | Afternoon | Sunday | 2018 | 9
9613 | 2018-09-30 15:52 | 2018-01-10 15:52 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | Checked and found CDRSG-13.8ACB13 T/R 1x R/F: 50 Counter: 208 - 209. Patrolled the line and found nothing. Cause : Unidentified |  | 1 | 15:52 | Afternoon | Sunday | 2018 | 9
9614 | 2018-09-30 15:58 | 2018-09-30 15:58 | 13.8KV NELLA FEEDER #2 | Heavy Rain | Lightning | 52 | Nella 13.8Kv OCB#2 T/R 1x. Nella fdr#1 load dropped 99A (210-111A). Not checked yet. |  | 1 | 15:58 | Afternoon | Sunday | 2018 | 9
9615 | 2018-09-30 16:56 | 2018-09-30 16:56 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | Menggala fdr#1 load dropped 53A (199-146A). Menggala GFPC T/R 1x. Not checked yet. |  | 1 | 16:56 | Afternoon | Sunday | 2018 | 9
9616 | 2018-09-30 18:21 | 2018-09-30 18:21 | 13.8KV 8D FEEDER #4 | Rain and Lightning | Lightning | 0 | 8D 13.8Kv OCB fdr#4 T/R 1x. 8D fdr#1 load dropped 77A (148-71A). 8D fdr#2 load dropped 29A (101-72A). 8D fdr#3 load dropped 36A (99-63A). 8D fdr#5 load dropped 122A (158-71A). Not checked yet. |  | 1 | 18:21 | Afternoon | Sunday | 2018 | 9
9617 | 2018-09-30 18:21 | 2018-07-10 16:05 | 13.8KV 8D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found 8D OCB fdr #4 T/R 1x Counter: 1545-1546 R/F: 50@1. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 18:21 | Afternoon | Sunday | 2018 | 9
9618 | 2018-09-30 18:44 | 2018-09-30 18:44 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 6 | 6D OCB fdr#4 T/R 1x. 6D fdr#5 Load dropped 28A (106-78A). 6D fdr#6 Load dropped 60A (194-134A) Pump off. Not checked yet. |  | 1 | 18:44 | Afternoon | Sunday | 2018 | 9
9619 | 2018-09-30 18:44 | 2018-02-10 18:44 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 6 | Checked and found 6DSB-13.8OCB4 T/R 1x R/F: 51N @2 Counter: 558 - 559. Patrolled the line and found Broken Pin Insulator Ø1 on Pole 5C-124 near loc. 5C-85. Cause : Lightning |  | 1 | 18:44 | Afternoon | Sunday | 2018 | 9
9620 | 2018-09-30 18:46 | 2018-09-30 18:46 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 0 | 4D fdr#4 Load dropped 29A (51-22A). 4D fdr#6 Load dropped 87A (151-64A) Pump off. Not checked yet. |  | 1 | 18:46 | Afternoon | Sunday | 2018 | 9
9621 | 2018-09-30 18:46 | 2018-07-10 09:42 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found 4D OCB fdr #4 T/R 1x Counter: 1617-1618 R/F: None. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 18:46 | Afternoon | Sunday | 2018 | 9
9622 | 2018-09-30 18:47 | 2018-09-30 18:47 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Pin Insulator | 0 | 3D OCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 18:47 | Afternoon | Sunday | 2018 | 9
9623 | 2018-09-30 18:47 | 2018-07-10 09:37 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Pin Insulator | 0 | Checked and found 3D OCB fdr#3 T/R 1x Counter:445-446 R/F: 50@1. Patrolled the line found @1 broken pin insulator on pole 3C-29. Cause: Broken Pin Insulator. |  | 1 | 18:47 | Afternoon | Sunday | 2018 | 9
9624 | 2018-09-30 19:01 | 2018-09-30 19:01 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning Arrester | 30 | 19:01 3D OCB fdr#4 T/R 1x. 19:34 3D OCB fdr#4 T/R 1x again. Not checked yet. 22:40 Patrolled the line & found sparked at Fuse Cut Out Recl 2D-44. 1 Oktober 2018. 00:05 Opened Recl. 2D-14. 03:30 By pass Recl. 24-44. 03:36 Blocked & closed Rec;. 2D14, then release the block. Not checked yet. |  | 1 | 19:01 | Night | Sunday | 2018 | 9
9625 | 2018-09-30 19:01 | 2018-07-10 09:30 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning Arrester | 30 | Checked and found 3D OCB fdr#4 T/R 2x Counter:632-634 R/F: 51N. Patrolled the line @1 broken Lightning Arrester on pole 1E-53. Cause: Broken Lightning Arrester. |  | 1 | 19:01 | Night | Sunday | 2018 | 9
9626 | 2018-09-30 22:25 | 2018-09-30 22:25 | 13.8KV SINTONG FEEDER #1 | Cloudy | Unidentified (Fuse) | 6 | It was reported B/O fuse at well Kerang#20. Not checked yet. |  | 1 | 22:25 | Night | Sunday | 2018 | 9
9627 | 2018-01-10 00:33 | 2018-01-10 00:33 | 13.8KV SINTONG FEEDER #2 | Cloudy | Unidentified (Fuse) | 0 | It was reported Sparked at Fuse Cut Out at well Benar#39 (Sintong fdr#2). Shutt Off well Kerang #20. Not checked yet. |  | 1 | 0:33 | Night | Wednesday | 2018 | 1
9628 | 2018-01-10 11:00 | 2018-01-10 11:00 | 13.8KV ROKAN FEEDER #3 | Fair | Construction Job | 0 | 11:00 Manually open Rokan fdr#3. 13:03 Closed Rokan fdr#3. Cause :Contention job. |  | 1 | 11:00 | Morning | Wednesday | 2018 | 1
9629 | 2018-01-10 11:00 | 2018-01-10 11:00 | 13.8KV ROKAN FEEDER #4 | Fair | Construction Job | 0 | 11:00 Manually open Rokan fdr#4. 13:03 Closed Rokan fdr#4. Cause :Contention job. |  | 1 | 11:00 | Morning | Wednesday | 2018 | 1
9630 | 2018-02-10 06:40 | 2018-02-10 06:40 | 13.8KV KETIGUL FEEDER#3 | Fair | Transformer Failure | 0 | It was reported Transformer OIL Leak at well Gulamo#07 (Ketigul fdr#3) Not checked yet |  | 1 | 6:40 | Morning | Saturday | 2018 | 2
9631 | 2018-02-10 06:40 | 2018-06-10 08:40 | 13.8KV KETIGUL FEEDER#3 | Fair | Transformer Failure | 0 | Checked and found FUSE B/O on location Gulamo #07 @1,2. Test the transformer and the result Transformer Failure. |  | 1 | 6:40 | Morning | Saturday | 2018 | 2
9632 | 2018-02-10 10:22 | 2018-02-10 10:22 | BEKASAP MAIN SUBSTATION | Fair | Planned Maintenance | 325 | 10:22 Manually Open Main Bekasap 13.8KV VCB fdr #6. 10:27 Manually Open Main Bekasap 13.8KV VCB fdr #2. 10:59 Manually Open Main Bekasap 13.8KV VCB fdr #5. Replaced Recloser #A for 5MVA TX-A at Bekasap GS. 11:58 Closed Main Bekasap 13.8KV VCB fdr #5. 12:12 Closed Main Bekasap 13.8KV VCB fdr #2. 12:26 Closed Main Bekasap 13.8KV VCB fdr #6. Cause: Planned Maintenance. | 1234 | 1 | 10:22 | Morning | Saturday | 2018 | 2
9633 | 2018-02-10 14:45 | 2018-02-10 14:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 0 | 14:45 Manually open recl,40-AW-17 ( C.Duri fdr#1). to Replace 150Kva TX at well Kulim#78. 15:45 Closed recl,40-AW-17, After finished the Jobs. Cause: Planned maintenance. |  | 1 | 14:45 | Afternoon | Saturday | 2018 | 2
9634 | 2018-02-10 16:22 | 2018-02-10 16:22 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 0 | Ketigul feeder #2 Load Dropped 177 A (233 - 56 A) Not Checked Yet |  | 1 | 16:22 | Afternoon | Saturday | 2018 | 2
9635 | 2018-02-10 17:15 | 2018-02-10 17:15 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 0 | 4D OCB fdr#5 T/R 8x. (at 17:15, 17:16, 17:19, 17:24, 17:26, 17:27, 17:30, 17:32) Not checked yet. |  | 1 | 17:15 | Afternoon | Saturday | 2018 | 2
9636 | 2018-02-10 17:15 | 2018-09-10 14:24 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, 4D OCB fdr#5 T/R 1x, Ctr: 130-311, R/F: 51 @1@2 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 17:15 | Afternoon | Saturday | 2018 | 2
9637 | 2018-02-10 17:15 | 2018-02-10 17:15 | 13.8KV 4D FEEDER #6 | Rain and Lightning | Lightning | 0 | 4D fdr#6 load dropped 143A (144-1A). Not checked yet. |  | 1 | 17:15 | Afternoon | Saturday | 2018 | 2
9638 | 2018-02-10 17:15 | 2018-07-10 08:59 | 13.8KV 4D FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked and found 4DSB-13.8OCB6 no device operated R/F: None Counter: 191 - 191. Patrolled the line and found nothing. Cause: Lightning |  | 1 | 17:15 | Afternoon | Saturday | 2018 | 2
9639 | 2018-02-10 17:16 | 2018-02-10 17:16 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 77 | 6DN fdr#2 load dropped 167A (281-114A). Not checked yet. |  | 1 | 17:16 | Afternoon | Saturday | 2018 | 2
9640 | 2018-02-10 17:16 | 2018-10-10 04:17 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 77 | Checked & found, Recl. 5D112 T/R 1x, Ctr: 32-33, R/F: None Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 17:16 | Afternoon | Saturday | 2018 | 2
9641 | 2018-02-10 17:17 | 2018-02-10 17:17 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 43 | 3D 13.8Kv OCB fdr#2 T/R 2x. 3D GFPC T/R 2x. 3D fdr#3 load dropped 9A ( 52-39A ). 3D fdr#4 load dropped 22A ( 233-211A ). Not checked yet. |  | 1 | 17:17 | Afternoon | Saturday | 2018 | 2
9642 | 2018-02-10 17:17 | 2018-07-10 16:02 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 43 | Checked and found 3D OCB fdr #2 T/R 2x Counter: 269-271 R/F: 51@2. Patrolled the line nothing found. Cause: Suspected Lightning. |  | 1 | 17:17 | Afternoon | Saturday | 2018 | 2
9643 | 2018-02-10 17:29 | 2018-02-10 17:29 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Pin Insulator | 28 | 4B OCB fdr#2 T/R 1x. 4B fdr#1 load dropped 13A ( 108- 95A ). Not checked yet. |  | 1 | 17:29 | Afternoon | Saturday | 2018 | 2
9644 | 2018-02-10 17:29 | 2018-07-10 16:27 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Pin Insulator | 28 | Checked and found 4B OCB fdr #2 T/R 1x Counter: 282-283 R/F:51@3. Patrolled the line found @3 broken pin insulator on pole 4B-81. Cause: Broken pin insulator. |  | 1 | 17:29 | Afternoon | Saturday | 2018 | 2
9645 | 2018-02-10 17:33 | 2018-06-10 15:33 | 13.8KV 5B FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked and found 5B OCB#6 T/SO, R/F: 50, Counter: 262 - 263 Patrolled the line, but found nothing. Cause : Lightning |  | 1 | 17:33 | Afternoon | Saturday | 2018 | 2
9646 | 2018-02-10 17:33 | 2018-12-10 00:24 | 13.8KV 5B FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 5B OCB fdr#6 T/R 1x, Ctr: 262-263, R/F: 50 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 17:33 | Afternoon | Saturday | 2018 | 2
9647 | 2018-02-10 17:33 | 2018-02-10 17:33 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | 5B fdr#1 load dropped 75A (91-16A). Not checked yet. |  | 1 | 17:33 | Afternoon | Saturday | 2018 | 2
9648 | 2018-02-10 17:33 | 2018-12-10 00:24 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found, Recl. 5B-06 T/R 1x, Ctr:97-98, R/F: none Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 17:33 | Afternoon | Saturday | 2018 | 2
9649 | 2018-02-10 17:33 | 2018-02-10 17:33 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Unidentified | 0 | 5B fdr#2 load dropped 166A (174-8A). Not checked yet. |  | 1 | 17:33 | Afternoon | Saturday | 2018 | 2
9650 | 2018-02-10 17:33 | 2018-12-10 07:48 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found 5B OCB fdr#2, Counter not change & No relay flag Patrolled the Line, but found nothing, no Recloser Trip Or Reclose Cause : Unidentified |  | 1 | 17:33 | Afternoon | Saturday | 2018 | 2
9651 | 2018-02-10 17:33 | 2018-02-10 17:33 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Unidentified | 0 | 5B fdr#3 load dropped 85A (95-10A). Not checked yet. |  | 1 | 17:33 | Afternoon | Saturday | 2018 | 2
9652 | 2018-02-10 17:33 | 2018-04-10 07:42 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Unidentified | 0 | Checked and found 5B OCB Fdr#2 T/R 1x Ctr:386 R/F:NONE Patrolled the line but found nothing Cause : Unidentified |  | 1 | 17:33 | Afternoon | Saturday | 2018 | 2
9653 | 2018-02-10 17:36 | 2018-02-10 17:36 | 13.8KV 3D FEEDER #7 | Rain and Lightning | Lightning | 36 | 3D 13.8Kv OCB fdr#7 T/R 1x. Not checked yet. |  | 1 | 17:36 | Afternoon | Saturday | 2018 | 2
9654 | 2018-02-10 17:36 | 2018-07-10 16:12 | 13.8KV 3D FEEDER #7 | Rain and Lightning | Lightning | 36 | Checked and found 3D OCB fdr #7 T/R 1x Counter: 212-213 R/F: 50@1 , @2. Patrolled the line nothing found. Cause: Suspected lightning. |  | 1 | 17:36 | Afternoon | Saturday | 2018 | 2
9655 | 2018-02-10 17:37 | 2018-02-10 17:37 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Dead End Insulator | 24 | 3D OCB fdr#8 T/R 1x. Not checked yet. |  | 1 | 17:37 | Afternoon | Saturday | 2018 | 2
9656 | 2018-02-10 17:37 | 2018-07-10 16:15 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Dead End Insulator | 24 | Checked and found 3D OCB fdr #8 T/R 1x Counter: 311-312 R/F: 50@1,2,3. Patrolled the line found @2 broken dead end insulator on pole 3D-99. Cause: Broken dead end insulator. |  | 1 | 17:37 | Afternoon | Saturday | 2018 | 2
9657 | 2018-02-10 17:37 | 2018-02-10 17:37 | 13.8KV 3D FEEDER #6 | Rain and Lightning | Unidentified | 0 | 3D fdr#6 load dropped 118A (252-134A). Not checked yet. |  | 1 | 17:37 | Afternoon | Saturday | 2018 | 2
9658 | 2018-02-10 17:37 | 2018-07-10 16:09 | 13.8KV 3D FEEDER #6 | Rain and Lightning | Unidentified | 0 | Checked and found 3D OCB fdr #6 Counter: 263-263 R/F: None Normal. Cause: Unidentified. |  | 1 | 17:37 | Afternoon | Saturday | 2018 | 2
9659 | 2018-02-10 17:52 | 2018-02-10 17:52 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 11 | 4B OCB fdr#5 T/R 1x. (WIP) Not checked yet. |  | 1 | 17:52 | Afternoon | Saturday | 2018 | 2
9660 | 2018-02-10 17:52 | 2018-04-10 07:42 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 11 | Checked and found 4BSB-13.8OCB5 T/R Counter : 147 - 148 Relay Flag : 51 Patrolled the line but found nothing Cause : Lightning |  | 1 | 17:52 | Afternoon | Saturday | 2018 | 2
9661 | 2018-02-10 17:52 | 2018-12-10 07:40 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 11 | Checked & found, 4B OCB fdr#5 T/R 1x, Ctr: 147-148, R/F: 51 @2 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 17:52 | Afternoon | Saturday | 2018 | 2
9662 | 2018-02-10 17:52 | 2018-02-10 17:52 | 13.8KV 4B FEEDER #4 | Rain and Lightning | Lightning | 0 | 4B fdr#4 load dropped 183A (189-6A). 4B fdr#6 load dropped 87A (126-39A). Not checked yet. |  | 1 | 17:52 | Afternoon | Saturday | 2018 | 2
9663 | 2018-02-10 21:31 | 2018-02-10 21:31 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Tree | 0 | Dumai 4.16Kv VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 21:31 | Night | Saturday | 2018 | 2
9664 | 2018-02-10 21:31 | 2018-04-10 21:31 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Tree | 0 | Checked and found Dumai 4.16Kv VCB fdr#1 T/R 1x ctr: 295-296 R/F: 51N. Patrolled the line and found High Pinang tree toutched power ling o/p: W103. Cause: Tree. |  | 1 | 21:31 | Night | Saturday | 2018 | 2
9665 | 2018-02-10 22:01 | 2018-02-10 22:01 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 60 | 22:01 4B 13.8Kv OCB fdr#1 T/R 1x. 4B fdr#4 load dropped 243A (249-6A). (WIP) 4B fdr#5 load dropped 124A (126-2A). (WIP) Not checked yet. |  | 1 | 22:01 | Night | Saturday | 2018 | 2
9666 | 2018-02-10 22:01 | 2018-07-10 16:21 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 60 | Checked and found 4B OCB fdr #1 T/R 2x Counter: 335-337 R/F: 51@1,2. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 22:01 | Night | Saturday | 2018 | 2
9667 | 2018-02-10 22:01 | 2018-02-10 22:01 | 13.8KV 4B FEEDER #6 | Cloudy | Unidentified | 0 | 4B Fdr#6 Load dropped 106A (126-20A) Not checked yet |  | 1 | 22:01 | Night | Saturday | 2018 | 2
9668 | 2018-02-10 22:01 | 2018-07-10 16:31 | 13.8KV 4B FEEDER #6 | Cloudy | Unidentified | 0 | Checked and found Recloser: 4B-148 T/R 1x Counter: 79-80. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 22:01 | Night | Saturday | 2018 | 2
9669 | 2018-02-10 22:16 | 2018-02-10 22:16 | 13.8KV 5B FEEDER #4 | Cloudy | Construction Job | - | 22:16 Man Open 5B OCB Fdr#4 GS 6 to Maintain tank Level 01:19 Closed back the OCB, GS 6 requested Cause: Planned Construction |  | 1 | 22:16 | Night | Saturday | 2018 | 2
9670 | 2018-03-10 07:40 | 2018-03-10 07:40 | 13.8KV BATANG FEEDER #2 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse at well Rantau Bais #7 D/S Batang fdr #2. Not checked yet. |  | 1 | 7:40 | Morning | Saturday | 2018 | 3
9671 | 2018-03-10 08:40 | 2018-03-10 08:40 | MINAS POWER PLANT |  |  | 0 | 08:40 S/U MGT #5 and then On Line the unit at 08:54. |  | 1 | 8:40 | Morning | Saturday | 2018 | 3
9672 | 2018-03-10 13:34 | 2018-03-10 13:34 | 13.8KV NORTH DURI FEEDER #11 | Drizzle | Unidentified | 0 | N.Duri VCB fdr #11 T/R 1X. Not checked yet. |  | 1 | 13:34 | Afternoon | Saturday | 2018 | 3
9673 | 2018-03-10 14:59 | 2018-03-10 14:59 | 13.8KV CENTRAL DURI FEEDER #1 | Rain | Unidentified | 0 | C Duri fdr # 1 load dropped 37A (99-62A). Not checked yet. |  | 1 | 14:59 | Afternoon | Saturday | 2018 | 3
9674 | 2018-04-10 07:52 | 2018-04-10 07:52 | 13.8KV PEMATANG FEEDER #2 | Cloudy | Unidentified | 86 | Pematang OCB fdr #2 T/R 1x. Pematang fdr #1 load dropped 153A (202-49A). Not checked yet. |  | 1 | 7:52 | Morning | Tuesday | 2018 | 4
9675 | 2018-04-10 07:52 | 2018-04-10 07:52 | 13.8KV PEMATANG FEEDER #2 | Cloudy | Unidentified | 86 | Pematang OCB fdr #2 T/R 1x. Pematang fdr #1 load dropped 153A (202-49A). Not checked yet. |  | 1 | 7:52 | Morning | Tuesday | 2018 | 4
9676 | 2018-04-10 08:20 | 2018-04-10 08:20 | CENTRAL DURI POWER PLANT |  |  | 0 | 08:20 S/U CDGT #4 and then On Line the unit at 08:40. |  | 1 | 8:20 | Morning | Tuesday | 2018 | 4
9677 | 2018-04-10 10:43 | 2018-04-10 10:43 | CENTRAL DURI POWER PLANT |  |  | 0 | 10:43 Off Line CDGT #5 and then S/D the unit at 11:00. |  | 1 | 10:43 | Morning | Tuesday | 2018 | 4
9678 | 2018-04-10 15:11 | 2018-04-10 15:11 | 13.8KV RANGAU FEEDER #2 | Heavy Rain | Unidentified | 0 | Rangau fdr #2 load dropped 143A (144-1A). Not checked yet. |  | 1 | 15:11 | Afternoon | Tuesday | 2018 | 4
9679 | 2018-04-10 15:11 | 2018-11-10 14:49 | 13.8KV RANGAU FEEDER #2 | Heavy Rain | Unidentified | 0 | Checked & found, Recl 23.BD.01 Ctr: 347 - 348, R/F : 51 @1@3 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 15:11 | Afternoon | Tuesday | 2018 | 4
9680 | 2018-04-10 16:05 | 2018-04-10 16:05 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 61 | 16:05 Menggala OCB fdr #1 T/R 1x. 16:56 Report to TDO Operation load Menggala fdr #1 still drop 138 A (202 - 64 A) 18:30 Checked and found RCL 19-AN-04 T/LO (counter 617 - 621). Patrolled the lines but found nothing 21:00 Block and Close RCL 19-AN-04, OK then release the block. Not checked yet. |  | 1 | 16:05 | Afternoon | Tuesday | 2018 | 4
9681 | 2018-04-10 16:36 | 2018-04-10 16:36 | 13.8KV CENTRAL DURI FEEDER #1 | Heavy Rain | Others | 133 | 16:36 C Duri fdr #1 load dropped 40A (95-55A). 17:56 Checked and found RCL 39-AV-36 T/O (HLT Blocked) Patrolled the lines and found any kite yarn at KULIN #36 then release it 19:33 Blocked and Close RCL 39-AV-36, OK then release the blocked. Cause : others (kite) |  | 1 | 16:36 | Afternoon | Tuesday | 2018 | 4
9682 | 2018-05-10 09:58 | 2018-05-10 09:58 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 4 | 09:58 Blocked Recloser:16-AA-08 D/S Balam fdr #4. For opening Hot line clamp on TOP So Balam #308. due to replaced @1 broken Fuse Cut Out at well So Balam #308. 11:06 Closed Hot line clamp on TOP So Balam #308 and then released the block Recloser. Cause: Plan Maintenance. |  | 1 | 9:58 | Morning | Thursday | 2018 | 5
9683 | 2018-05-10 12:47 | 2018-05-10 12:47 | 13.8KV 4D FEEDER #5 | Fair | Unidentified | 504 | 12:17 4D fdr #5 Load dropped 141A (228-87A). 15:00 Checked and found Recloser: 4D-14A T/SO Counter: 52-54. Patrolled the line found nothing. 16:15 Blocked and close Recloser: 4D-14A --> Ok and then released the block. Cause: Unidentified. | 12345 | 1 | 12:47 | Afternoon | Thursday | 2018 | 5
9684 | 2018-06-10 04:17 | 2018-06-10 04:17 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | 04:17 Ground Fault Alarm at Menggala fdr #1 Menggala fdr #1 Load Drop 115 A (177 - 62 A) Not Checked Yet |  | 1 | 4:17 | Morning | Sunday | 2018 | 6
9685 | 2018-06-10 11:00 | 2018-06-10 11:00 | MINAS POWER PLANT |  |  | - | 11:00 S/U MGT#8 and then On line the unit at 11:19. |  | 1 | 11:00 | Morning | Sunday | 2018 | 6
9686 | 2018-06-10 15:40 | 2018-06-10 15:40 | MINAS POWER PLANT |  |  | - | 15:40 Off line MGT#9 and then S/D the Unit for S/B. |  | 1 | 15:40 | Afternoon | Sunday | 2018 | 6
9687 | 2018-07-10 02:27 | 2018-07-10 02:27 | 13.8KV SINTONG FEEDER #1 | Fair | Unidentified | 0 | 02:27 SINTONG GFPC T/R 1x SINTONG FDR #1 LOAD DROP 53 A (100 - 47 A). 10:00 Checked and found Recloser #25 AD 26 T/R 1X ctr: 124-125 R/F: 51 @2 And also found Sintong GFPC T/R 2X ctr:: 1094-1096 R/F : 51N. patrolled and found normal but found nothing. Cause : Unidentified. |  | 1 | 2:27 | Night | Tuesday | 2018 | 7
9688 | 2018-07-10 07:00 | 2018-07-10 07:00 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 103 | So.Balam 13.8Kv VCB fdr#1 T/O (blocked position). Not checked yet. |  | 1 | 7:00 | Morning | Tuesday | 2018 | 7
9689 | 2018-07-10 08:25 | 2018-07-10 08:25 | CENTRAL DURI POWER PLANT |  |  | - | 08:25 S/U CDGT #5 and then On line the Unit at 09:02. |  | 1 | 8:25 | Morning | Tuesday | 2018 | 7
9690 | 2018-07-10 09:37 | 2018-07-10 09:37 | CENTRAL DURI POWER PLANT |  |  | 0 | 09:37 Off Line CDGT #4 and then S/D the Unit for Stand By. |  | 1 | 9:37 | Morning | Tuesday | 2018 | 7
9691 | 2018-07-10 11:09 | 2018-07-10 11:09 | 13.8KV 8D FEEDER #11 | Fair | Construction Job | 0 | 11:09 Manualy open 8D OCB fdr #11. Due to replaced 20" pipe towards well 8E-72E. 17:46 Manually blocked and closed 8D OCB fdr #11 and then released the block. Cause: Construction job. |  | 1 | 11:09 | Morning | Tuesday | 2018 | 7
9692 | 2018-07-10 15:05 | 2018-07-10 15:05 | 13.8KV DARLING VCB FEEDER #3 | Fair | Animal | 0 | It was reported b/o fuse on pole 05-M5-24 D/S Darling fdr #3. Not checked yet. |  | 1 | 15:05 | Afternoon | Tuesday | 2018 | 7
9693 | 2018-07-10 15:05 | 2018-09-10 15:41 | 13.8KV DARLING VCB FEEDER #3 | Fair | Animal | 0 | Replaced @1,@2 b/o fuse for 112,5 KVA TX o/p: 05-M5-24. Cause: Animal (Monkey). |  | 1 | 15:05 | Afternoon | Tuesday | 2018 | 7
9694 | 2018-07-10 16:15 | 2018-07-10 16:15 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse on pole 07-T1-16 D/S D Field fdr #2. Not checked yet. |  | 1 | 16:15 | Afternoon | Tuesday | 2018 | 7
9695 | 2018-07-10 16:28 | 2018-07-10 16:28 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 0 | Minas fdr #3 Load dropped 109A (170-61A). Not checked yet. |  | 1 | 16:28 | Afternoon | Tuesday | 2018 | 7
9696 | 2018-07-10 16:28 | 2018-09-10 14:11 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked & found, Rcl. 7D93 T/R 1x, Ctr: 70-71, R/F: None Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 16:28 | Afternoon | Tuesday | 2018 | 7
9697 | 2018-07-10 16:33 | 2018-07-10 16:33 | 8 CHARLIE SUBSTATION | Rain and Lightning | Under investigation | 129 | 16:33 8C 115 KV CIRCUIT SWITCHER #2 T/O. No power at 8C OCB fdr # 4 ,5 ,6 ( GS #2 black out). 16:51 Manually open 8C OCB fdr #3 Closed at: 17:56. 17:04 Manually open Minas ACB fdr #3 Closed at: 18:07. 17:04 Manually open Minas ACB fdr #4 Closed at: 18:18. 17:08 Manually open 8D OCB fdr #3 Closed at: 18:17. 17:20 Checked and found 8C 115 KV C/S #2 T/O R/F: 86 HR Counter:165-166. 17:28 Manually open 8C OCB fdr #4 Closed at: 17:44. 17:28 Manually open 8C OCB fdr #5 Closed at: 17:44. 17:28 Manually open 8C OCB fdr #6 Closed at: 17:37. 17:33 Manually closed 8C 115 KV C/S #2 --> Success. and then revived affected feeders. Cause: Under investigation. |  | 1 | 16:33 | Afternoon | Tuesday | 2018 | 7
9698 | 2018-07-10 16:49 | 2018-07-10 16:49 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 19 | 6D OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 16:49 | Afternoon | Tuesday | 2018 | 7
9699 | 2018-07-10 16:49 | 2018-09-10 14:04 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 19 | Checked & found, 6D OCB fdr#1T/R 1x, Ctr: 332-333, R/F: 51 @1 Patrolled the Line, found @1 Broken Pin insulator O/P 6C-21 Cause : Lightning |  | 1 | 16:49 | Afternoon | Tuesday | 2018 | 7
9700 | 2018-07-10 22:33 | 2018-07-10 22:33 | 13.8KV SINTONG FEEDER #2 | Fair | Powerline - Conductor | 237 | 22:32 SINTONG GFPC T/R 1x 22:33 SINTONG VCB FDR #2 T/LO 23:40 Checked and found Sintong fdr #2 T/LO ctr:474-478 R/F: 51N, 51@2. Also found Sintong GFPC T/R 2X ctr:1096-1098. Patrolled the line and found broken conductor at Main Line phase @2, between Pole 27-AF-13 and 27-AF-14. On Oct. 08, 2018. 01:30 Manually Open Visual Opening Sintong fdr #2. Repaired broken Conductor. 05:38 Blocked and closed Sintong fdr #2. OK then released the block. Cause : Conductor. Prod Loss : 22:33 - 00:00 = 56 wells / 297 Bbls 00:00 - 05:38 = 56 wells / 1152 Bbls | 0 | 1 | 22:33 | Night | Tuesday | 2018 | 7
9701 | 2018-07-10 22:34 | 2018-07-10 22:34 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Bangko feeder #4 Load Drop 50 A (160 - 110 A) Cause : Not Checked Yet |  | 1 | 22:34 | Night | Tuesday | 2018 | 7
9702 | 2018-08-10 07:49 | 2018-08-10 07:49 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 1089 | 07:49 It was reported no power at Benar GS. 09:45 Checked and found recloser: 28-AF-02 T/SO Counter: 1535-1536. Manually blocked and closed Recloser: 28-AF-02 --> Success , and then released the block. Prod Loss = 26 wells / 1089 Bbls (BENAR GS) Cause: Not patrolled yet. | 0 | 1 | 7:49 | Morning | Friday | 2018 | 8
9703 | 2018-08-10 10:00 | 2018-08-10 10:00 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 4 | It was reported b/o fuse at well Meso #08 D/S Menggala fdr #1. Not checked yet. |  | 1 | 10:00 | Morning | Friday | 2018 | 8
9704 | 2018-08-10 10:00 | 2018-09-10 11:12 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 4 | Replaced @1,2 b/o fuse for 300 Kva Tx at Menggala South #08. Cause: Animal (Monkey). |  | 1 | 10:00 | Morning | Friday | 2018 | 8
9705 | 2018-08-10 10:21 | 2018-08-10 10:21 | 13.8KV 8D FEEDER #11 | Fair | Construction Job | 0 | 10:21 Manualy open 8D OCB fdr #11. Due to replaced 20" pipe towards well 8E-72E. Manually blocked and closed 8D OCB fdr #11 and then released the block. Cause: Construction job. |  | 1 | 10:21 | Morning | Friday | 2018 | 8
9706 | 2018-08-10 16:00 | 2018-08-10 16:00 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 65 | 16:00 It was reported no power at Perkebunan and Genting field. 18:30 Checked and patrol the lines, found RCL 29-Z-13A T/SO and no findings at the lines 20:15 Blocked and Close RCL 29-Z-13A, success then release the blocked. Cause : Unidentified. |  | 1 | 16:00 | Afternoon | Friday | 2018 | 8
9707 | 2018-08-10 16:10 | 2018-08-10 16:10 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 31 | Pungut OCB fdr#1 T/R 1x. Pungut fdr#2 load dropped 50A (60-10A). Not checked yet. |  | 1 | 16:10 | Afternoon | Friday | 2018 | 8
9708 | 2018-08-10 16:10 | 2018-11-10 07:54 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning | 31 | Checked & found, Pungut OCB fdr#2 T/R 1x, Ctr: 418-419, R/F: 51 @1@3 Patrolled the Line, found @3 flash over by pass switch O/P 45 BR 07 Cause: Lightning |  | 1 | 16:10 | Afternoon | Friday | 2018 | 8
9709 | 2018-08-10 16:39 | 2018-08-10 16:39 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 94 | 16:39 Nella OCB fdr#1 T/O 1x (In block position due to RIG ACS #01 activity at well Bangko #68). 16:49 Manually block & closed Nella OCB fdr#1 --> Success. Still in block position due to RIG Activity. Cause: Not patrolled yet. |  | 1 | 16:39 | Afternoon | Friday | 2018 | 8
9710 | 2018-08-10 17:40 | 2018-08-10 17:40 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 23 | Pinang OCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 17:40 | Afternoon | Friday | 2018 | 8
9711 | 2018-08-10 17:40 | 2018-09-10 17:40 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 23 | Checked & found, Pinang OCB fdr# 1 T/R, Ctr: 442-443, R/F: 51G Patrolled the Line, found @1@2 broken LA O/Top Well Pinang#15 Cause : Lightning |  | 1 | 17:40 | Afternoon | Friday | 2018 | 8
9712 | 2018-09-10 11:28 | 2018-09-10 11:28 | 13.8KV KETIGUL FEEDER#3 | Fair | Planned Maintenance | 11 | 11:28 Manually open Ketigul OCB fdr#3. Duo to C/O Tx at Gulamo #07. 12:11 Manually block & closed Ketigul OCB fdr#3 and then released the block. Cause: Plain maintenance. |  | 1 | 11:28 | Morning | Monday | 2018 | 9
9713 | 2018-09-10 13:32 | 2018-09-10 13:32 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | 13:32 Sintong fdr#2 load dropped 18A (248-230A). Sintong GFPC T/R 1x. 17:24 It was reported no power at Genting field. 20:21 Checked and found RCL 29-Z-13A T/LO, Ctr: 192 - 197, R/F: 59 Blocked and Closed the Recloser but trip again, then patrol the lines 21:36 Reported patrol finding, @3 broken LA O/P 31-Z-06 Planned to isolate tomorrow due to rain. Cause : Lightning Arrester |  | 1 | 13:32 | Afternoon | Monday | 2018 | 9
9714 | 2018-09-10 13:32 | 14/10/2018 07:41 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | Checked & found Recl.29Z-13A T/R 1x, Ctr: None, R/F: 59 Patrolled the Line, found @3 Broken LA o/p 31 Z 06 Cause : Lightning |  | 1 | 13:32 | Afternoon | Monday | 2018 | 9
9715 | 2018-09-10 14:38 | 2018-09-10 14:38 | 115KV NELLA SW. STA - PINANG LINE | Rain and Lightning | Lightning | 117 | 115KV Nella GCB #27 (Line to Pinang) T/R 1x. Not checked yet. |  | 1 | 14:38 | Afternoon | Monday | 2018 | 9
9716 | 2018-09-10 14:38 | 17/10/2018 08:27 | 115KV NELLA SW. STA - PINANG LINE | Rain and Lightning | Lightning | 117 | Checked and found 115 kV Nella GCB #27 T/R 1x, ctr : 185-186, R/F : None Patrolled and found @1 dead end flash over o/p DP-308 and DP-313 Cause : Lightning |  | 1 | 14:38 | Afternoon | Monday | 2018 | 9
9717 | 2018-09-10 16:19 | 2018-09-10 16:19 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Unidentified | 51 | CKBS fdr#5 load dropped 234A (295-61A). Not checked yet. |  | 1 | 16:19 | Afternoon | Monday | 2018 | 9
9718 | 2018-09-10 16:19 | 2018-12-10 08:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Unidentified | 51 | Checked & found, Recl. 36-CU-25 T/R 1x, Ctr: 54-5, R/F : none Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 16:19 | Afternoon | Monday | 2018 | 9
9719 | 2018-09-10 16:24 | 2018-09-10 16:24 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 9 | 5B OCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 16:24 | Afternoon | Monday | 2018 | 9
9720 | 2018-09-10 16:24 | 2018-12-10 00:07 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 9 | Checked & found, 5B OCB fdr#3 T/R 1x, Ctr: 394-395, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 16:24 | Afternoon | Monday | 2018 | 9
9721 | 2018-09-10 16:35 | 2018-09-10 16:35 | 13.8KV 4B FEEDER #4 | Rain and Lightning | Lightning | 13 | 4B OCB fdr#4 T/R 1x. Not checked yet. |  | 1 | 16:35 | Afternoon | Monday | 2018 | 9
9722 | 2018-09-10 16:35 | 2018-11-10 11:57 | 13.8KV 4B FEEDER #4 | Rain and Lightning | Lightning | 13 | Checked & found, 4B OCB fdr#4 T/R 1x, Ctr: 239-240, R/F: 50N @1 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 16:35 | Afternoon | Monday | 2018 | 9
9723 | 2018-09-10 16:35 | 2018-09-10 16:35 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 0 | 4B OCB fdr#5 T/R 1x. Not checked yet. |  | 1 | 16:35 | Afternoon | Monday | 2018 | 9
9724 | 2018-09-10 16:35 | 2018-11-10 11:59 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found, 4B OCB fdr#5 T/R 1x, Ctr: 147-148, R/F: 50N Patrolled the Line, but Found nothing Cause : Lightning, |  | 1 | 16:35 | Afternoon | Monday | 2018 | 9
9725 | 2018-09-10 16:35 | 2018-09-10 16:35 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Unidentified | 18 | 4B fdr#6 load dropped 96A (126-30A). Not checked yet. |  | 1 | 16:35 | Afternoon | Monday | 2018 | 9
9726 | 2018-09-10 16:35 | 13/10/2018 07:56 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Unidentified | 18 | Checked & found, Some Recloser 4B-148 under 4B fdr#6, Counter Not change. Patrolled the Line, found nothing. Cause: Unidentified |  | 1 | 16:35 | Afternoon | Monday | 2018 | 9
9727 | 2018-09-10 16:57 | 2018-09-10 16:57 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Lightning | 25 | Minas ACB#13 fdr#2 T/R 1x R/F: 51 @2 Counter:74-75. Not Patrolled yet. |  | 1 | 16:57 | Afternoon | Monday | 2018 | 9
9728 | 2018-09-10 16:57 | 2018-12-10 00:01 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Lightning | 25 | Checked & found, Minas ACB fdr#2 T/R 1x, Ctr: 74-75, R/F: 51 @2 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 16:57 | Afternoon | Monday | 2018 | 9
9729 | 2018-09-10 17:01 | 2018-09-10 17:01 | 4.16KV NO RUMBAI FEEDER #2 | Rain and Lightning | Pin Insulator | 0 | N.Rumbai VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 17:01 | Afternoon | Monday | 2018 | 9
9730 | 2018-09-10 17:01 | 13/10/2018 22:17 | 4.16KV NO RUMBAI FEEDER #2 | Rain and Lightning | Pin Insulator | 0 | Checked and found N.Rumbai VCB fdr#2 T/R 1x Counter: 360-361 R/F: 51N. Patrolled the line found @2 broken pin insulator on pole 1RD-09. Cause: Broken Pin Insulator. |  | 1 | 17:01 | Afternoon | Monday | 2018 | 9
9731 | 2018-09-10 17:04 | 2018-09-10 17:04 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 17 | 6D OCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 17:04 | Afternoon | Monday | 2018 | 9
9732 | 2018-09-10 17:04 | 2018-12-10 00:09 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 17 | Checked & found, 6D OCB fdr#5 T/R 1x, Ctr: 788-789, R/F: 50N Patrolled The Line, but found nothing Cause : Lightning |  | 1 | 17:04 | Afternoon | Monday | 2018 | 9
9733 | 2018-09-10 17:42 | 2018-09-10 17:42 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Dead End Insulator | 24 | 6D OCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 17:42 | Afternoon | Monday | 2018 | 9
9734 | 2018-09-10 17:42 | 13/10/2018 22:25 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Dead End Insulator | 24 | Checked and found 6D OCB fdr #1 T/R 1x Counter: 333-334 R/F: 51@1. Patrolled the line found @1 broken dead end insulator on pole 5B-124. Cause: Broken Dead End Insulator. |  | 1 | 17:42 | Afternoon | Monday | 2018 | 9
9735 | 2018-09-10 17:42 | 2018-09-10 17:42 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Unidentified | 0 | 6D fdr #2 Load dropped 79A (204-125A). 6D fdr #3 Load dropped 17A (178-161A). Not checked yet. |  | 1 | 17:42 | Afternoon | Monday | 2018 | 9
9736 | 2018-09-10 17:42 | 13/10/2018 07:49 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found Recloser - 6D-298 & 6D-78 (6D Fdr#2), Counter not change - Recl. 6D-03 (6D Fdr#3) , Counter not change Patrolled the Line, found nothing. Cause: Unidentified |  | 1 | 17:42 | Afternoon | Monday | 2018 | 9
9737 | 2018-10-10 11:04 | 2018-10-10 11:04 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 96 | It was reported B/O fuse o/p 04-01-06 & 04-01-08 (C.Duri fdr#9). Not checked yet. |  | 1 | 11:04 | Morning | Wednesday | 2018 | 10
9738 | 2018-10-10 11:04 | 14/10/2018 11:15 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 96 | Checked & found, B/O fuse for 12.5 KVATX @2 o/p 04 01 06 and @2 o/p 04 01 08 Patrolled the Line, but found nothing Cause: Unidentified (Fuse) |  | 1 | 11:04 | Morning | Wednesday | 2018 | 10
9739 | 2018-10-10 13:42 | 2018-10-10 13:42 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 75 | 13:42 Bangko OCB fdr#4 T/R 1x. Bangko fdr #1 load drooped 134A(134-32 A). 13:47 Bangko OCB fdr#4 T/R 1x and GFPC T/R 1x. Not chekhed yet. |  | 1 | 13:42 | Afternoon | Wednesday | 2018 | 10
9740 | 2018-10-10 13:42 | 14/10/2018 11:15 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 75 | Checked & found, BKO OCB fdr#4 T/R 1x, Ctr: 52-54, R/F: 51N Patrolled the Line, found @2 broken Pin insulator o/p 25-Y-03 Cause: Lightning |  | 1 | 13:42 | Afternoon | Wednesday | 2018 | 10
9741 | 2018-10-10 14:27 | 2018-10-10 14:27 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Unidentified | 191 | 14:27 Menggala fdr#1 load drooped 152A (184-31A) 17:44 Checked & found Recl.19-AN-04 T/O (In Block Status, Rig Job at well Meno #01) Block & Closed the Recloser, then released the block Patrolled the Line, but found nothing Cause: Unidentified |  | 1 | 14:27 | Afternoon | Wednesday | 2018 | 10
9742 | 2018-10-10 14:53 | 2018-10-10 14:53 | 13.8KV SINTONG FEEDER #1 | Fair | Construction Job | 0 | 14:53 Blocked Rec: 27-AF-17 (Sintong fdr#1). Opened HLC o/p 27-AF-37 (5 wells off) to Install one spend Power Line 16:07 Closed the HLC after finished the Job. Cause : Plant maintenance. |  | 1 | 14:53 | Afternoon | Wednesday | 2018 | 10
9743 | 2018-10-10 15:45 | 2018-10-10 15:45 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 11 | 15:45 Libo OCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 15:45 | Afternoon | Wednesday | 2018 | 10
9744 | 2018-10-10 15:45 | 15/10/2018 15:05 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 11 | Checked & found, Libo OCB fdr#1 T/R 1x, Ctr: 580-581, R/F: 50N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 15:45 | Afternoon | Wednesday | 2018 | 10
9745 | 2018-10-10 18:15 | 2018-10-10 18:15 | 13.8KV BANGKO GFPC | Fair | Unidentified | 0 | 18:15 Bangko GFPC T/R 1x. Bangko fdr #1 load drooped 9A(165-156A). Bangko fdr#4 load drooped 42A(160-188A). Not checked yet. |  | 1 | 18:15 | Afternoon | Wednesday | 2018 | 10
9746 | 2018-10-10 18:15 | 15/10/2018 15:22 | 13.8KV BANGKO GFPC | Fair | Unidentified | 0 | Checked & found, BKO GFPC T/R 3x, Ctr: 181-184, R/F: 51N Patrolled the Line, but found nothing Cause: Unidentified |  | 1 | 18:15 | Afternoon | Wednesday | 2018 | 10
9747 | 2018-11-10 14:47 | 2018-11-10 14:47 | 13.8KV NORTH DURI FEEDER #9 | Rain and Lightning | Unidentified | 0 | N.Duri 13.8 kv VCB fdr#9 T/R. Not checked yet. |  | 1 | 14:47 | Afternoon | Saturday | 2018 | 11
9748 | 2018-11-10 14:47 | 18/10/2018 14:47 | 13.8KV NORTH DURI FEEDER #9 | Rain and Lightning | Unidentified | 0 | Checked & found N.Duri VCB fdr#9 T/R 1x Ctr:73-74 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 14:47 | Afternoon | Saturday | 2018 | 11
9749 | 2018-12-10 12:31 | 2018-12-10 12:31 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | 0 | C.Duri fdr#1 load drooped 40A (100-60A). Not checked yet. |  | 1 | 12:31 | Afternoon | Monday | 2018 | 12
9750 | 2018-12-10 12:31 | 18/10/2018 12:31 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | 0 | Checked & found Recl. 41AW62 T/R 1x Ctr:289-290. Patrolled the line & found @2 Broken LA o/p 41AW54. Cause : Lightning. |  | 1 | 12:31 | Afternoon | Monday | 2018 | 12
9751 | 2018-12-10 18:48 | 2018-12-10 18:48 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 50 | Ketigul VCB fdr#2 T/R 1x Not checked yet |  | 1 | 18:48 | Afternoon | Monday | 2018 | 12
9752 | 2018-12-10 18:48 | 18/10/2018 18:48 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 50 | Checked & found Ketigul VCB fdr#2 T/r 1x Ctr:299-300 R/F:51@3. Patrolled the line & found @3Broken Pin Insulator o/p 24AN04. Cause : Lightning. |  | 1 | 18:48 | Afternoon | Monday | 2018 | 12
9753 | 2018-12-10 22:10 | 2018-12-10 22:10 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Transformer Failure | 0 | 22:10 It was reported no power at Pari Office D/S C Duri fdr #2. 24:00 Checked and found Recloser: 40-BA-02 T/LO Counter:1488-1492. Patrolled the line found @1,@3 b/o fuse for 150 Kva Transformer (The Transformer is swollen). Disconnect transformer. 01:00 Blocked and closed Recloser: 40-BA-02 --> Success and then released the block. Cause: Transformer failure. |  | 1 | 22:10 | Night | Monday | 2018 | 12
9754 | 2018-10-13 06:52 | 2018-10-13 06:52 | 13.8KV MINAS FEEDER #6 | Cloudy | Unidentified | 0 | Minas fdr #6 load dropped 89A (160-71A). Not checked yet. |  | 1 | 6:52 | Morning | Saturday | 2018 | 10
9755 | 2018-10-13 10:00 | 2018-10-13 10:00 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified (Fuse) | 0 | 10:00 It was reported B/O Fuse at well Balam # 396 (S. Balam fdr # 4). Not checked yet. |  | 1 | 10:00 | Morning | Saturday | 2018 | 10
9756 | 2018-10-14 11:31 | 2018-10-14 11:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 0 | C.Duri Fdr#1 Load dropped 32A (94-62A) Not checked yet |  | 1 | 11:31 | Morning | Sunday | 2018 | 10
9757 | 2018-10-14 11:31 | 2018-10-18 11:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 0 | Checked & found Recl. 41AW62 T/R 1x Ctr:290-291. Patrolled the line & found @2 Broken LA o/p 41AW54. Cause : Lightning. |  | 1 | 11:31 | Morning | Sunday | 2018 | 10
9758 | 2018-10-14 15:51 | 2018-10-14 15:51 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 72 | Menggala OCB fdr#1 T/R 1x Not checked yet |  | 1 | 15:51 | Afternoon | Sunday | 2018 | 10
9759 | 2018-10-15 17:02 | 2018-10-15 17:02 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 371 | 17:02 Nella OCB fdr#1 T/O InBlock Position Rig ACS01 at well Bangko 68, Confirm Its OK. 17:55 Checked & found, Nella OCB fdr#1 T/O, Ctr: 531-532, R/F: 51 @1@2@3. Closed Nella OCB fdr#1 in Block position, OK. after Confirm to Rig ACS01. Patrolled the Line, but found nothing Cause: Lightning |  | 1 | 17:02 | Afternoon | Monday | 2018 | 10
9760 | 2018-10-15 22:12 | 2018-10-15 22:12 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning | 68 | Sintong VCB fdr #2 T/R 1x. Sintong GFPC T/R 1x , fault alarm on Sintong fdr #2. Not checked yet. |  | 1 | 22:12 | Night | Monday | 2018 | 10
9761 | 2018-10-15 22:12 | 2018-10-17 08:30 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning | 68 | Checked and found 1.8 kV VCB Sintong fdr #2 T/R 1x, ctr : 478-479, R/F : 51N Patrolled and found nothing. Cause : Lightning |  | 1 | 22:12 | Night | Monday | 2018 | 10
9762 | 2018-10-16 01:38 | 2018-10-16 01:38 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 32 | So Bekasap fdr #1 load dropped 104A (110-6A). Not checked yet. |  | 1 | 1:38 | Night | Tuesday | 2018 | 10
9763 | 2018-10-16 01:38 | 2018-10-18 01:38 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 32 | Checked & found Recl. 34BI18 T/R 2x Ctr:175-177. Patrolled the line & found @2 Broken LA o/p 31E08. Cause : Lightning. |  | 1 | 1:38 | Night | Tuesday | 2018 | 10
9764 | 2018-10-16 10:09 | 2018-10-16 10:09 | 13.8KV DARLING VCB FEEDER #3 | Fair | Lightning | 0 | Darling 13.8Kv VCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 10:09 | Morning | Tuesday | 2018 | 10
9765 | 2018-10-16 10:09 | 2018-10-18 10:09 | 13.8KV DARLING VCB FEEDER #3 | Fair | Lightning | 0 | Checked & found Darling VCB fdr@3 T/R 1x. Ctr:248 R/F51N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 10:09 | Morning | Tuesday | 2018 | 10
9766 | 2018-10-16 13:09 | 2018-10-16 13:09 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 121 | It was reported b/o fuse at well Pagar#43 (Ketigul fdr#2). Not checked yet. |  | 1 | 13:09 | Afternoon | Tuesday | 2018 | 10
9767 | 2018-10-16 13:09 | 2018-10-18 13:09 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified (Fuse) | 121 | Checked & found B/O fuse at well Pagar#43 (Ketigul fdr#2). Replaced @1 B/O fuse for 150Kva Tx with the same size. Cause : Unidentified (Fuse). |  | 1 | 13:09 | Afternoon | Tuesday | 2018 | 10
9768 | 2018-10-16 23:50 | 2018-10-16 23:50 | MINAS POWER PLANT |  |  | 0 | 23:50 MGT #11 Trip by alarm Auto transfer to distillate. |  | 1 | 23:50 | Night | Tuesday | 2018 | 10
9769 | 2018-10-17 02:10 | 2018-10-17 02:10 | CENTRAL DURI POWER PLANT |  |  | 0 | 02:10 S/U CDGT #4 and then Online the unit at 02:45. |  | 1 | 2:10 | Night | Wednesday | 2018 | 10
9770 | 2018-10-17 03:00 | 2018-10-17 03:00 | MINAS POWER PLANT |  |  | 0 | 03:00 S/U MGT #4 and then Online the unit at 03:15. |  | 1 | 3:00 | Night | Wednesday | 2018 | 10
9771 | 2018-10-17 06:35 | 2018-10-17 06:35 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 106 | Ketigul VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 6:35 | Morning | Wednesday | 2018 | 10
9772 | 2018-10-17 06:35 | 2018-10-17 06:35 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 106 | Checked and found VCB KTGL fdr #2 T/R 1x, ctr: 301-302, R/F: 51N Patrolled and found broken dead end @3 o/p 30-AN-04 Cause : Lightning |  | 1 | 6:35 | Morning | Wednesday | 2018 | 10
9773 | 2018-10-17 06:35 | 2018-10-17 06:35 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 0 | Ketigul fdr #1 load dropped 57A (127-70A). Not checked yet. |  | 1 | 6:35 | Morning | Wednesday | 2018 | 10
9774 | 2018-10-17 06:35 | 2018-10-26 17:57 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 0 | Checked and found breaker and recloser normal (not operate), ctr: 204, R/F: None Patrolled and found nothing. Cause : Unidentified |  | 1 | 6:35 | Morning | Wednesday | 2018 | 10
9775 | 2018-10-17 12:28 | 2018-10-17 12:28 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri fdr#1 load drooped 40A(100-60). Not checked yet. |  | 1 | 12:28 | Afternoon | Wednesday | 2018 | 10
9776 | 2018-10-17 12:28 | 2018-10-22 18:42 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found Recl 41-AW-62 T/R 1x, Ctr: 291-292, R/F : None Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 12:28 | Afternoon | Wednesday | 2018 | 10
9777 | 2018-10-17 15:17 | 2018-10-17 15:17 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Planned Maintenance | 0 | 15:17 Manually Open 13.8 kV ACB CD feeder #2 for PGT Maintenance job to repair broken jumper/conductor @1 on pole 3-H-2. 16:15 Blocked and Close 13.8 kV ACB CD feeder #2, success then release the block. Cause : Planned Maintenance |  | 1 | 15:17 | Afternoon | Wednesday | 2018 | 10
9778 | 2018-10-17 18:06 | 2018-10-17 18:06 | 13.8KV CENTRAL DURI FEEDER #16 | Heavy Rain | Unidentified | 0 | 13.8 kV VCB CD fdr #16 T/R 1x, R/F : 50P @1, @2, ctr : 328 - 329 Cause : Not Checked Yet |  | 1 | 18:06 | Afternoon | Wednesday | 2018 | 10
9779 | 2018-10-17 18:08 | 2018-10-17 18:08 | 13.8KV PEMATANG FEEDER #2 | Heavy Rain | Unidentified (L/A) | 74 | Pematang fdr#2 T/R 1x. Not checked yet. |  | 1 | 18:08 | Afternoon | Wednesday | 2018 | 10
9780 | 2018-10-17 18:08 | 2018-10-20 18:08 | 13.8KV PEMATANG FEEDER #2 | Heavy Rain | Unidentified (L/A) | 74 | Checked & found Pematang VCB fdr#2 T/R 1x Ctr:497-498 R/F:51@2. Patrolled the line & found @2 Broken Dead End Insulator o/p34BC90. @2 Broken Pin Supported o/p 34BC63. Cause : Unidentified (L/A). |  | 1 | 18:08 | Afternoon | Wednesday | 2018 | 10
9781 | 2018-10-17 18:08 | 2018-10-17 18:08 | 13.8KV PEMATANG FEEDER #1 | Heavy Rain | Unidentified | 0 | Pematang fdr#1 load dropped 127A (201-74A). Not checked yet. |  | 1 | 18:08 | Afternoon | Wednesday | 2018 | 10
9782 | 2018-10-17 18:08 | 2018-10-20 18:08 | 13.8KV PEMATANG FEEDER #1 | Heavy Rain | Unidentified | 0 | Checked & found Recl. 34BC14 T/R 1x Ctr:136-137. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 18:08 | Afternoon | Wednesday | 2018 | 10
9783 | 2018-10-17 18:10 | 2018-10-17 18:10 | 13.8KV DARLING VCB FEEDER #3 | Heavy Rain | Unidentified | 0 | Darling fdr#3 T/R 1x. Not checked yet. |  | 1 | 18:10 | Afternoon | Wednesday | 2018 | 10
9784 | 2018-10-17 18:10 | 2018-10-18 18:10 | 13.8KV DARLING VCB FEEDER #3 | Heavy Rain | Unidentified | 0 | Checked & found Darling VCB fdr#3 T/R 1x Ctr:248 R/F:51@2. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 18:10 | Afternoon | Wednesday | 2018 | 10
9785 | 2018-10-17 18:28 | 10/21/0201 20:48 | 13.8KV BEKASAP FEEDER #6 | Heavy Rain | Unidentified | 0 | Checked & found, Rcl. 38-BD-18 T/R 1x, Ctr: 91-92, R/F: None Patrolled the Line, found @1 broken Deadend insulator o/p 38-BD-07 Cause : Unidentified |  | 1 | 18:28 | Afternoon | Wednesday | 2018 | 10
9786 | 2018-10-17 18:28 | 2018-10-17 18:28 | 13.8KV BEKASAP FEEDER #6 | Heavy Rain | Unidentified | 0 | Bekasap fdr#6 load dropped 54A (188-134A). Not checked yet. |  | 1 | 18:28 | Afternoon | Wednesday | 2018 | 10
9787 | 2018-10-17 18:29 | 2018-10-17 18:29 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Lightning Arrester | 0 | N.Duri fdr#8 T/R 2x. N.Duri GFPC T/R 2x. Not checked yet. |  | 1 | 18:29 | Afternoon | Wednesday | 2018 | 10
9788 | 2018-10-17 18:29 | 2018-10-20 18:29 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Lightning Arrester | 0 | Checked & found N.Duri VCB fdr#8 T/R 2x Ctr:89-91 R/F:51@1@2. Patrolled the line & found @1@2 Broken jumper o/p 10-K5-03. Cause : Lightning Arrester. |  | 1 | 18:29 | Afternoon | Wednesday | 2018 | 10
9789 | 2018-10-17 18:42 | 2018-10-17 18:42 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Construction Job | 0 | Manually open Bekasap fdr#2. Cause: Maintain level tank. |  | 1 | 18:42 | Afternoon | Wednesday | 2018 | 10
9790 | 2018-10-17 18:59 | 2018-10-17 18:59 | NORTH DURI POWER PLANT | Rain and Lightning | Under investigation | 20 | 18:59 NDC#3 Open generator breaker. Freq : 58.86 Hz. load sheading level #3. 4B fdr#1 T/O. then closed at 19:14 4B fdr#4 T/O. then closed at 19:06 5B fdr#4 T/O. then closed at 19:15 5B fdr#5 T/O. then closed at 19:16 3D fdr#6 T/O. then closed at 19:08 4D fdr#4 T/O. then closed at 19:17 4D fdr#5 T/O. then closed at 19:17 8D fdr#1 T/O. then closed at 19:18 8D fdr#3 T/O. then closed at 19:18 suram fdr#1 T/O. then closed at 20:50 Lukut load drooped 14 MW. 19:13 closed Gen Breaker GCB # 35 19:14 closed Gen Breaker GCB# 33 Couse: Under investigation. |  | 1 | 18:59 | Afternoon | Wednesday | 2018 | 10
9791 | 2018-10-17 22:55 | 2018-10-17 22:55 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Lightning | 0 | Minas ACB fdr#4 T/R 1x. Not checked yet. |  | 1 | 22:55 | Night | Wednesday | 2018 | 10
9792 | 2018-10-17 22:55 | 2018-10-22 22:55 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked Feeder & Recl. Not operated. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 22:55 | Night | Wednesday | 2018 | 10
9793 | 2018-10-18 00:01 | 2018-10-18 00:01 | 13.8KV KOTABATAK FEEDER #2 | Drizzle | Lightning | 54 | 00:01 OKB OCB fdr#2 T/R 1x. 16:00 Checked & found OKB VCB fdr#2 T/R 1x Ctr; 1335-1336 R/F:51N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 0:01 | Night | Thursday | 2018 | 10
9794 | 2018-10-18 08:30 | 2018-10-18 08:30 | SINTONG SUBSTATION | Fair | Planned Maintenance | 6554 | 08:30 Perform SP to De Energize 115KV Batang OCB #1 and Sintong GCB #23, to Service 115KV Sintong GCB#25 and Recplaced broken CCPD 14:20 Energized Back 115KV Batang OCB #1 and Sintong GCB #23 After finished Installed Temporary bypass of 115KV Sintong GCB#25 and Recplaced broken CCPD Cause : Planned Maintenance Feeders Impact Manual Open. Bangko GS: 08:30 Open Nella OCB fdr#1 , Closed at: 14:47 08:35 Open Nella OCB fdr#2 , Closed at: 13:35 08:37 Open Bangko OCB fdr#1 , Closed at: 13:59 08:38 Open Bangko OCB fdr#4 , Closed at: 14:01 08:52 Open Bangko OCB fdr#2 , Closed at: 13:45 08:56 Open Bangko OCB fdr#2 , Closed at: 13:46 09:06 Open Sintong OCB fdr#1 , Closed at: 14:12 09:10 Open Sintong OCB fdr#2 , Closed at: 14:08 09:11 Open Pinang OCB fdr#1 , Closed at: 14:13 Balam GS: 08:45 Open Balam OCB fdr#1 , Closed at: 14:07 08:47 Open Balam OCB fdr#4 , Closed at: 14:09 09:04 Open Balam OCB fdr#2 , Closed at: 14:04 09:05 Open Balam OCB fdr#3 , Closed at: 13:05 Prod Loss: BKO GS: 4086 Bbls, 193 wells. STG GS: 1640 Bbls, 80 wells. Pinang : 227 Bbls, 27 wells. BLM GS : 2157 Bbls, 196 wells. Total Prod Loss : 8110 Bbls, 496 wells. | 123 | 1 | 8:30 | Morning | Thursday | 2018 | 10
9795 | 2018-10-18 09:59 | 2018-10-18 09:59 | 13.8KV MINAS FEEDER #1 | Fair | Planned Maintenance | 91 | 09:59 Manually Opened FUSE for 500KVATX at Wells 7D-51, 7D-42, 7D-41B (Minas fdr#1) to Perform House keeping Transformer Pad. 11:30 Manually Closed the Fuse after finished the Jobs Cause: Maintenance |  | 1 | 9:59 | Morning | Thursday | 2018 | 10
9796 | 2018-10-18 10:15 | 2018-10-18 10:15 | 13.8KV 3D FEEDER #2 | Fair | Construction Job | 0 | 10:15 Manually Opened LBS 3E-64 (3D fdr#2) due to PT RWS Lifting Jobs 18:05 Manually Closed the LBS after finished the Jobs Cause: Construction Job |  | 1 | 10:15 | Morning | Thursday | 2018 | 10
9797 | 2018-10-18 18:24 | 2018-10-18 18:24 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 70 | Ketigul VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 18:24 | Afternoon | Thursday | 2018 | 10
9798 | 2018-10-18 20:02 | 2018-10-18 20:02 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 34 | 6DN fdr#2 load dropped 214A (236-22A). 6DN fdr#3 load dropped 135A (207-72A). Not checked yet. |  | 1 | 20:02 | Night | Thursday | 2018 | 10
9799 | 2018-10-18 20:02 | 2018-10-21 14:22 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 34 | Checked & found 6DN OCB fdr#2 T/R 1x, Ctr: 15-16, R/F: none Patrolled the Line, found @2 Broken Dead End o/p 5D-41 Cause : Lightning |  | 1 | 20:02 | Night | Thursday | 2018 | 10
9800 | 2018-10-19 10:56 | 2018-10-19 10:56 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | 10:56 ND feeder #2 T/SO 11:02 Manually close ND fdr #2 Checked and found R/F 51P @1, @2 Counter : 276 - 277 Cause : Not Patrolled Yet |  | 1 | 10:56 | Morning | Friday | 2018 | 10
9801 | 2018-10-19 10:56 | 2018-10-26 18:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | North Duri fdr #2 T/SO, ctr: 276-277, R/F: 51P @1, @2 Patrolled and found nothing. Cause : Unidentified |  | 1 | 10:56 | Morning | Friday | 2018 | 10
9802 | 2018-10-19 14:30 | 2018-10-19 14:30 | MINAS POWER PLANT |  |  | - | 14:30 S/U MGT#11 and then Online at :15:00 to restore power after trip. |  | 1 | 14:30 | Afternoon | Friday | 2018 | 10
9803 | 2018-10-19 15:50 | 2018-10-19 15:50 | CENTRAL DURI POWER PLANT |  |  | - | 15:50 CDGT #4 Offline 16:07 CDGT #4 Shut Down |  | 1 | 15:50 | Afternoon | Friday | 2018 | 10
9804 | 2018-10-19 19:48 | 2018-10-19 19:48 | MINAS POWER PLANT |  |  | - | 19:48 Off line & S/D the unit MGT#4. |  | 1 | 19:48 | Night | Friday | 2018 | 10
9805 | 2018-10-19 20:59 | 2018-10-19 20:59 | 115KV MINAS - 6D LINE | Rain and Lightning | Lightning | 0 | 20:59 115 kV Line MNS-6D GCB #65 T/R 1x, R/F: 87LA, 21GA 115 kV Line MNS-6D GCB #63 T/R 1x 115 kV L6D-MNS GCB #22 T/O, R/F: 87LA, 67LA 22:00 Checked and found GCB #22 at 6D T/O. Closed at 22:31 22:29 Checked and found GCB #63 Open. Closed at 22:32 22:29 Checked and found GCB #65 Open. Closed at 22:32 Cause: Not Checked Yet |  | 1 | 20:59 | Night | Friday | 2018 | 10
9806 | 2018-10-19 20:59 | 2018-10-23 13:40 | 115KV MINAS - 6D LINE | Rain and Lightning | Lightning | 0 | Checked and found - 115 kV GCB #63 MNS SY T/R 2x, ctr: 263 - 265, R/F: 87L @1 - 115 kV GCB #65 MNS SY T/R 2x, ctr: 243 - 245, R/F: 21GB - 115Kv OCB#22 6D T/O, R/F: 87LA 67LA. Patrolled and found nothing. Cause : Lightning |  | 1 | 20:59 | Night | Friday | 2018 | 10
9807 | 2018-10-19 21:59 | 2018-10-19 21:59 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 0 | 3D fdr#4 load dropped 177A (229-52A). Not checked yet. |  | 1 | 21:59 | Night | Friday | 2018 | 10
9808 | 2018-10-20 02:48 | 2018-10-20 02:48 | MINAS POWER PLANT |  |  | - | MGT#3 Trip by alarm Lube Oil Pressure Low. |  | 1 | 2:48 | Night | Saturday | 2018 | 10
9809 | 2018-10-20 21:49 | 2018-10-20 21:49 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found VCB fdr #4 BKO T/R 1x, ctr: 61-62, R/F: 51N Patrolled and found Nothing Cause : Lightning |  | 1 | 21:49 | Night | Saturday | 2018 | 10
9810 | 2018-10-20 21:49 | 2018-10-20 21:49 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Bangko fdr#4 T/R 1x. Bangko GFPC T/R 1X. Not checked yet. |  | 1 | 21:49 | Night | Saturday | 2018 | 10
9811 | 2018-10-20 21:49 | 2018-10-20 21:49 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked and found RCL 25-Z-07 T/R 1x, ctr: 206-207, R/F: 51N Patrolled and found nothing Cause : Lightning |  | 1 | 21:49 | Night | Saturday | 2018 | 10
9812 | 2018-10-20 21:49 | 2018-10-20 21:49 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked and found RCL 25-Z-07 T/R 1x, ctr: 206-207, R/F: 51N Patrolled and found nothing Cause : Lightning |  | 1 | 21:49 | Night | Saturday | 2018 | 10
9813 | 2018-10-21 03:36 | 2018-10-21 03:36 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 0 | OKB OCB fdr #2 T/R 1x Not checked yet |  | 1 | 3:36 | Night | Sunday | 2018 | 10
9814 | 2018-10-21 03:36 | 2018-10-22 07:13 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked and found OKB OCB fdr #2 T/R 1x, ctr: 1336-1337, R/F: 51N Patrolled the line, but found nothing Cause : Lightning |  | 1 | 3:36 | Night | Sunday | 2018 | 10
9815 | 2018-10-21 04:14 | 2018-10-21 04:14 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | 44Kv Line Mns-Rbi ACB#21 T/R 1x Ctr:85-86 R/F:.. Not patrolled yet. |  | 1 | 4:14 | Morning | Sunday | 2018 | 10
9816 | 2018-10-21 04:14 | 2018-10-21 04:14 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Checked and found 13.8 kV ACB #21 Minas T/R, ctr: 85 - 86, R/F: 21P @3 Patrolled and found Broken Suspension o/p MR-66 @3 Cause : Lightning |  | 1 | 4:14 | Morning | Sunday | 2018 | 10
9817 | 2018-10-21 10:15 | 2018-10-21 10:15 | 13.8KV DURI COMMUNITY FEEDER #2 | Drizzle | Unidentified | 0 | DCM feeder #1 T/R 1x cause: not checked yet |  | 1 | 10:15 | Morning | Sunday | 2018 | 10
9818 | 2018-10-21 15:37 | 2018-10-21 15:37 | 13.8KV ROKAN FEEDER #2 | Cloudy | Unidentified (Fuse) | 0 | Reported b/o fuse on pole 29-AV-28 Cause: not checked yet |  | 1 | 15:37 | Afternoon | Sunday | 2018 | 10
9819 | 2018-10-21 15:37 | 2018-10-26 18:06 | 13.8KV ROKAN FEEDER #2 | Cloudy | Unidentified (Fuse) | 0 | Patrolled and found broken fuse of TX @1 o/p 29-AV-28 Cause : Unidentified (Fuse) |  | 1 | 15:37 | Afternoon | Sunday | 2018 | 10
9820 | 2018-10-22 10:17 | 2018-10-22 10:17 | 13.8KV LIBO FEEDER #2 | Fair | Lightning | 0 | 06:55 Libo fdr #2 Load Drop 43 A (62 - 19 A) 10:17 Reported no power at Waduk and Hitam Field 11:19 Checked and found RCL 23-BW-02 T/SO, ctr 347-348, R/F 51P @3 11:21 Blocked and close the recloser, success then release the blocked. Cause : not patrolled yet |  | 1 | 10:17 | Morning | Monday | 2018 | 10
9821 | 2018-10-22 10:17 | 2018-10-27 15:09 | 13.8KV LIBO FEEDER #2 | Fair | Lightning | 0 | Checked and found RCL 23-BW-02 T/SO, ctr: 347-348, R/F: None Patrolled and found nothing Cause : Lightning |  | 1 | 10:17 | Morning | Monday | 2018 | 10
9822 | 2018-10-22 17:00 | 2018-10-22 17:00 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Static Wire | 81 | 17:00 BKS Main fdr #2 T/R 1x BKS Main fdr #1 Drop 10 A (14 - 4 A) ---> BKS GS 18:59 It was reported Broken Conductor near taman seroja Bekasap/Pematang Area. 20:18 Checked & found 5 Span fall down Static o/p 35BC02-35BC08. 20:58 Man. Open Bekasap fdr#2, then open Isolation switch Bekasap fdr#2. Cut jumper o/p BD-74 for isolation. 23:04 Blocked & closed Bekasap fdr#2, then release the block. Continued tomorrow. | 123 | 1 | 17:00 | Afternoon | Monday | 2018 | 10
9823 | 2018-10-22 17:00 | 2018-10-26 18:05 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Static Wire | 81 | Checked and found BKS fdr #2 T/R 1x, ctr: 585 - 586, R/F: 51N Patrolled and found broken static wire o/p 35-BC-02. Cause : Static Wire | 123 | 1 | 17:00 | Afternoon | Monday | 2018 | 10
9824 | 2018-10-22 17:31 | 2018-10-22 17:31 | 13.8KV CENTRAL DURI FEEDER #4 | Cloudy | Animal | 31 | 17:31 CD ACB fdr#4 T/LO, ctr: 511 - 515, R/F: 50P @1 and @2, 51P @2 18:19 Patrolled and found broken LA jumper on pole 09-Q4-02 (@1, @2, @3) Cause : Animal (monkey) |  | 1 | 17:31 | Afternoon | Monday | 2018 | 10
9825 | 2018-10-22 17:43 | 2018-10-22 17:43 | 13.8KV CENTRAL DURI FEEDER #7 | Cloudy | Lightning | 0 | 17:43 CD fdr #7 Load Drop 55 A (120 - 75 A) Cause : Not Checked Yet |  | 1 | 17:43 | Afternoon | Monday | 2018 | 10
9826 | 2018-10-22 17:43 | 2018-10-29 16:51 | 13.8KV CENTRAL DURI FEEDER #7 | Cloudy | Lightning | 0 | Checked and found RCL 03-3-42 T/R 1x, ctr: 171 - 172, R/F: None Patrolled and found nothing. Cause : Lightning |  | 1 | 17:43 | Afternoon | Monday | 2018 | 10
9827 | 2018-10-23 02:41 | 2018-10-23 02:41 | 13.8KV SINTONG FEEDER #1 | Cloudy | Unidentified | 65 | Sintong fdr#1 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 2:41 | Night | Tuesday | 2018 | 10
9828 | 2018-10-23 05:21 | 2018-10-23 05:21 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 21 | 05:21 Pinang OCB fdr#1 T/R 1x. 05:22 Pinang OCB fdr#1 T/R 1x again. 05:24 Pinang OCB fdr#1 T/R 1x again. 05:36 Pinang OCB fdr#1 T/R 1x again. Not checked yet. |  | 1 | 5:21 | Morning | Tuesday | 2018 | 10
9829 | 2018-10-23 06:15 | 2018-10-23 06:15 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Unidentified | 0 | 06:15 Libo fdr#2 45A (64-19) 08:13 checked and found Recloser 23 Bw 02 T/LO. ctr: 348-348, not change, R/f 51p @3 patrolled the line and found nothing. 09:37 blocket and close recloser 23 Bw 02, success. release the blocked and unplugged control cable cause: unidentified |  | 1 | 6:15 | Morning | Tuesday | 2018 | 10
9830 | 2018-10-23 06:43 | 2018-10-23 06:43 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 115 | Nella fdr#1 load dropped 100A (201-101A). Nella GFPC T/R 1x. Not checked yet. |  | 1 | 6:43 | Morning | Tuesday | 2018 | 10
9831 | 2018-10-23 07:22 | 2018-10-23 07:22 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 29 | Nela fdr#2 T/R 1x couse: not checked yet |  | 1 | 7:22 | Morning | Tuesday | 2018 | 10
9832 | 2018-10-23 12:14 | 2018-10-23 12:14 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 40 | 5B fdr#2 T/R 8x not checked yet |  | 1 | 12:14 | Afternoon | Tuesday | 2018 | 10
9833 | 2018-10-23 12:14 | 2018-10-25 16:32 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 40 | Patrolled and found OCB fdr #2 T/R 10x, ctr: 386 - 396, R/F: 51N Patrolled and found broken pin support @3 on pole 5C-30 Cause : Lightning |  | 1 | 12:14 | Afternoon | Tuesday | 2018 | 10
9834 | 2018-10-23 13:50 | 2018-10-23 13:50 | 13.8KV PUNGUT FEEDER #2 | Cloudy | Tree | 21 | Pungut Fdr #2 T/R 1x Couse: Not checked yet |  | 1 | 13:50 | Afternoon | Tuesday | 2018 | 10
9835 | 2018-10-23 13:50 | 2018-10-27 14:32 | 13.8KV PUNGUT FEEDER #2 | Cloudy | Tree | 21 | Checked and found PGT fdr #2 T/R 1x, ctr: 419 - 420, R/F: 51P @1 Patrolled and found high trees at pole DK-70 Cause : Tree |  | 1 | 13:50 | Afternoon | Tuesday | 2018 | 10
9836 | 2018-10-24 08:58 | 2018-10-24 08:58 | 13.8KV MINAS FEEDER #6 | Cloudy | Unidentified | 49 | Minas ACB#18 ( feeder #6 ) T/R 1x R/F: 51N Counter: 176-177. Not patrolled yet. |  | 1 | 8:58 | Morning | Wednesday | 2018 | 10
9837 | 2018-10-24 08:58 | 2018-10-25 16:58 | 13.8KV MINAS FEEDER #6 | Cloudy | Unidentified | 49 | Checked and found MNS ACB #16 T/R 1x, ctr: 176 - 177, R/F 51N Patrolled and found nothing Cause : Unidentified |  | 1 | 8:58 | Morning | Wednesday | 2018 | 10
9838 | 2018-10-24 10:03 | 2018-10-24 10:03 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Construction Job | 0 | 10:03 Manually open Recloser: 05-N7-02 D/S C Duri fdr #14. Due to pilling bridge at 7N-72. 14:46 Manually blocked and closed Recloser: 05-N7-02 , and then released the block. Cause: Construction job. |  | 1 | 10:03 | Morning | Wednesday | 2018 | 10
9839 | 2018-10-24 11:55 | 2018-10-24 11:55 | 13.8KV MINAS FEEDER #2 | Cloudy | Unidentified | 50 | 11:55 Minas ACB #13 ( fdr #2 ) T/O. Checked and found Minas ACB #13 (feeder #2) T/LO R/F: 51@2 Counter: 75-77. 12:15 Manually blocked and closed Minas ACB #13 (feeder #2) --> Success and then released the block. Prod Loss : Area 2 (11 W / 28 Bbls) Area 3 (26 w / 22 Bbls) Cause: Not patrolled yet. |  | 1 | 11:55 | Morning | Wednesday | 2018 | 10
9840 | 2018-10-24 11:55 | 2018-10-25 16:24 | 13.8KV MINAS FEEDER #2 | Cloudy | Unidentified | 50 | Checked and found Minas ACB #13 T/LO 1x, ctr: 75 - 77, R/F: 51P @2 Patrolled and found nothing. Cause : Unidentified |  | 1 | 11:55 | Morning | Wednesday | 2018 | 10
9841 | 2018-10-25 13:24 | 2018-10-25 13:24 | KOTABATAK JUNCTION SW STA | Cloudy | Suspension Insulator | 0 | 13:24 115 KV Duri Ring Bus - KBJ Line Trip. Duri Ring Bus: 115 KV OCB #26 T/O 115 KV OCB #28 T/O. Checked and found 115 KV OCB #26 T/O R/F: 21G Zone 1 , 67N Inst Counter: 916-916. 115 KV OCB #28 T/O Counter: 183-184. KBJ: 115 KV GCB #43. T/O. 115 KV GCB #45 T/O. Checked and found 115 KV GCB #43. T/O R/F: 87L , 21G , 67N Inst Counter: 424-425. 115 KV GCB #45 T/O Counter: 308-309. Patrolled the line found @3 broken suspension insulator on pole DK-56. Reset relay 86L. 17:35 Manually closed 115 KV OCB #26 --> OK. Manually closed 115 KV OCB #28 --> but failed (spring discharge). 17:36 Manually closed 115 KV OCB #45 --> OK. Manually closed 115 KV OCB #43 --> OK. 115 KV Duri Ring Bus - KBJ Line energize. Cause: Broken suspension insulator. |  | 1 | 13:24 | Afternoon | Thursday | 2018 | 10
9842 | 2018-10-26 10:15 | 2018-10-26 10:15 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Planned Maintenance | 12 | 10:15 Manually 0pen LBS 34-CT- 68 D/S CKBS feeder #6. due to dismantle Tx at well KB: 176. 11:10 Manually closed LBS 34-CT-68. Cause: Plan Maintenance. |  | 1 | 10:15 | Morning | Friday | 2018 | 10
9843 | 2018-10-26 14:52 | 2018-10-26 14:52 | 13.8KV CENTRAL DURI FEEDER #9 | Cloudy | Unidentified | 0 | 14:52 C.Duri ACB# 41 (feeder #9) T/O (in block position). 15:06 Manually blocked and closed C.Duri ACB# 41 (feeder #9) --> Success , (still in block position). Cause: Not Patrolled yet. |  | 1 | 14:52 | Afternoon | Friday | 2018 | 10
9844 | 2018-10-26 14:52 | 2018-10-29 16:50 | 13.8KV CENTRAL DURI FEEDER #9 | Cloudy | Unidentified | 0 | Checked and found ACB fdr #9 T/O (block position), ctr: 395 - 396, R/F: 51 Patrolled and found nothing. Cause : Unidentified |  | 1 | 14:52 | Afternoon | Friday | 2018 | 10
9845 | 2018-10-26 14:55 | 2018-10-26 14:55 | 13.8KV CENTRAL DURI FEEDER #15 | Cloudy | Lightning | 0 | C Duri ACB #18 (feeder #15) T/R 1x. Not checked yet. |  | 1 | 14:55 | Afternoon | Friday | 2018 | 10
9846 | 2018-10-26 14:55 | 2018-10-29 16:53 | 13.8KV CENTRAL DURI FEEDER #15 | Cloudy | Lightning | 0 | Checked and found ACB CD fdr #15 T/R 1x, ctr: 383 - 384, R/F: 50P @1 Patrolled and found Broken Fuse PT of RCL 06-Q3-02. Cause : Lightning |  | 1 | 14:55 | Afternoon | Friday | 2018 | 10
9847 | 2018-10-27 04:15 | 2018-10-27 04:15 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 27 | Libo 13.8KV OCB fdr #2 T/R 1 X. Not checked yet. |  | 1 | 4:15 | Morning | Saturday | 2018 | 10
9848 | 2018-10-27 04:15 | 2018-10-27 15:08 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Lightning | 27 | Checked and found LIBO fdr #2 T/R 1x, ctr: 478 - 479, R/F: 51N Patrolled and found nothing Cause : Lightning |  | 1 | 4:15 | Morning | Saturday | 2018 | 10
9849 | 2018-10-27 13:25 | 2018-10-27 13:25 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Lightning Arrester | 164 | 13:25 N.Duri VCB fdr#2 T/R 1x. Checked and found Recloser: 13-G41-08 T/O (in block position). 15:50 Blocked and closed Recloser: 13-G41-08 --> Success (still in block position). Not patrolled yet. |  | 1 | 13:25 | Afternoon | Saturday | 2018 | 10
9850 | 2018-10-27 13:25 | 2018-01-11 08:08 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Lightning Arrester | 164 | Checked & found ND VCB fdr#2 T/R 1x, Ctr: 274-278, R/F: 51 @2 Patrolled the Line, found @2 broken LA jumper o/p LBS NF-07-F2 Cause : Lightning Arrester |  | 1 | 13:25 | Afternoon | Saturday | 2018 | 10
9851 | 2018-10-27 13:46 | 2018-10-27 13:46 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Dead End Insulator | 35 | Bekasap fdr#6 load dropped 47A (192-145A). Bekasap fdr#5 load dropped 116A (223-107A) WIP. Not checked yet. |  | 1 | 13:46 | Afternoon | Saturday | 2018 | 10
9852 | 2018-10-27 13:46 | 2018-01-11 08:45 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Dead End Insulator | 35 | Checked & found Rcl. 38-BE-10 T/R 1x, Ctr: 92-93, R/F: None Patrolled the Line, @1 Flash over Dead end insulator o/p 39-BD-11 Cause : Dead End Insulator |  | 1 | 13:46 | Afternoon | Saturday | 2018 | 10
9853 | 2018-10-27 13:47 | 2018-10-27 13:47 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 78 | 13:47 3D OCB feeder #2 T/O (In block position , Rig activity at well 3D-75). 14:12 Manually blocked and closed 3D OCB feeder #2 --> Success and then released the block. Not patrolled yet. |  | 1 | 13:47 | Afternoon | Saturday | 2018 | 10
9854 | 2018-10-27 13:47 | 2018-01-11 16:22 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 78 | Checked & found 3S OCB fdr#2 T/R 1x, Ctr: 271-272, R/F: 50 @2 Patrolled the Line, found @2 broken LA o/p 3D-82 Cause : Lightning |  | 1 | 13:47 | Afternoon | Saturday | 2018 | 10
9855 | 2018-10-27 13:47 | 2018-10-27 13:47 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 56 | 3D fdr#4 load dropped 100A (226-126A). Not checked yet. |  | 1 | 13:47 | Afternoon | Saturday | 2018 | 10
9856 | 2018-10-27 13:47 | 2018-02-11 13:43 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 56 | Checked & found Recl: 2D-44 Normal, Ctr: Not change, R/F: N/A Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 13:47 | Afternoon | Saturday | 2018 | 10
9857 | 2018-10-27 13:56 | 2018-10-27 13:56 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Tree | 0 | 13:56 4B fdr#1 load dropped 31A (99-68A). 21:36 Checked and found RCL 4B-101 T/LO, ctr: 627 - 631 Block and close the RCL but failed, then patrolled the lines 23:44 Found fallen tree at T/P 2A-54 then removed 00:04 Blocked and close RCL 4B-101, success then release block. last ctr: 632 Cause: Tree |  | 1 | 13:56 | Afternoon | Saturday | 2018 | 10
9858 | 2018-10-27 13:59 | 2018-10-27 13:59 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Dead End Insulator | 0 | Pematang fdr#1 load dropped 182A (209-27A) WIP. Pematang fdr#2 load dropped 15A (89-74A). Not checked yet. |  | 1 | 13:59 | Afternoon | Saturday | 2018 | 10
9859 | 2018-10-27 13:59 | 2018-01-11 08:46 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Dead End Insulator | 0 | Checked & found Rcl 35-BC-14 T/R 1x, Ctr: 137-138, R/F: None Patrolled the L1ne, found @2 Flash Over Dead end o/p 35-BD-20 Cause : Dead End Insulator Date Patrol : 30-OCT-2018 |  | 1 | 13:59 | Afternoon | Saturday | 2018 | 10
9860 | 2018-10-27 14:06 | 2018-10-27 14:06 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 34 | 5B OCB feeder #2 T/R 5x R/F: 51N Counter:396-401. Not patrolled yet. |  | 1 | 14:06 | Afternoon | Saturday | 2018 | 10
9861 | 2018-10-27 14:06 | 2018-01-11 16:22 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 34 | Checked & found 5B OCB fdr#2 T/R 5x, Ctr: 396-401, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 14:06 | Afternoon | Saturday | 2018 | 10
9862 | 2018-10-27 15:08 | 2018-10-27 15:08 | 4.16KV SO RUMBAI FEEDER #4 | Rain and Lightning | Unidentified | 0 | 15:08 So.Rumbai 4160V RCL fdr#4 T/O R/F: 51N Counter: 172-173. Patrolled the line nothing found. 17:49 Blocked and closed So.Rumbai 4160V RCL fdr#4 --> Success and then released the block. Cause: Unidentified. |  | 1 | 15:08 | Afternoon | Saturday | 2018 | 10
9863 | 2018-10-28 07:30 | 2018-10-28 07:30 | 13.8KV BANGKO FEEDER #4 | Cloudy | Unidentified | 0 | Bangko fdr #4 load dropped 97A (180-83A). Bangko fdr #1 load dropped 15A (175-160A). Bangko GFPC T/R 1x. Checked and found Recloser: 25-Z-07 T/R 2x Counter: 207-209 R/F: 51 @1,@2. Bangko GFPC T/R 3x Counter: 186-189 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 7:30 | Morning | Sunday | 2018 | 10
9864 | 2018-10-28 13:59 | 2018-10-28 13:59 | 4.16KV DUMAI (INDUST FEEDER) FEEDER #5 | Fair | Planned Maintenance | 0 | 13:59 Manually open LBS: I-21 D/S Dumai fdr #5. Due to 1. Replaced FCO to Line switch on pole W-01. 2. Replaced Hot line Clamp to Permanent jumpers on pole W-08. 3. Repair hot spot on LBS W-09. 16:51 Manually closed LBS: I-21. Cause: Plan Maintenance. |  | 1 | 13:59 | Afternoon | Sunday | 2018 | 10
9865 | 2018-10-28 15:07 | 2018-10-28 15:07 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Unidentified (Fuse) | 0 | It was reported b/o fuse on pole 05-N3-06 D/S C Duri fdr #10. Not checked yet. |  | 1 | 15:07 | Afternoon | Sunday | 2018 | 10
9866 | 2018-10-28 15:07 | 2018-10-29 16:57 | 13.8KV CENTRAL DURI FEEDER #10 | Fair | Unidentified (Fuse) | 0 | Checked and found broken fuse @1 on pole 05-N3-06 Cause : Unidentified (Fuse) |  | 1 | 15:07 | Afternoon | Sunday | 2018 | 10
9867 | 2018-10-28 17:30 | 2018-10-28 17:30 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 15 | 17:30 Ketigul VCB feeder#1 T/R 1x. 19:07 Checked and found VCB feeder #1 T/R 1x, ctr: 206 - 207, R/F: 51N 22:38 Patrolled and found nothing Cause: Unidentified. |  | 1 | 17:30 | Afternoon | Sunday | 2018 | 10
9868 | 2018-10-28 17:30 | 2018-10-28 17:30 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 0 | Ketigul feeder#2 load dropped 70A (232-162A). Not checked yet. |  | 1 | 17:30 | Afternoon | Sunday | 2018 | 10
9869 | 2018-10-28 17:30 | 2018-01-11 08:50 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 0 | Checked & found KTG VCB fdr#2 T/R 1x, Ctr: 302-303, R/F: 51 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 17:30 | Afternoon | Sunday | 2018 | 10
9870 | 2018-10-28 17:30 | 2018-01-11 08:50 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 0 | Checked & found KTG VCB fdr#2 T/R 1x, Ctr: 302-303, R/F: 51 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 17:30 | Afternoon | Sunday | 2018 | 10
9871 | 2018-10-29 10:45 | 2018-10-29 10:45 | MINAS POWER PLANT |  |  | 0 | 10:45 S/U Mgt#4 and then Online the unit at 11:05. |  | 1 | 10:45 | Morning | Monday | 2018 | 10
9872 | 2018-10-29 13:00 | 2018-10-29 13:00 | MINAS POWER PLANT |  |  | 0 | 13:00 Off line MGT#5 and then S/D the unit for S/B. |  | 1 | 13:00 | Afternoon | Monday | 2018 | 10
9873 | 2018-10-29 13:16 | 2018-10-29 13:16 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 27 | 13:16 5B OCB Feeder#2 T/R Not checked yet. |  | 1 | 13:16 | Afternoon | Monday | 2018 | 10
9874 | 2018-10-29 13:16 | 2018-02-11 13:49 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 27 | Checked & found 5B OCB fdr#2 T/LO, Ctr: 408-415, R/F: 51N Patrolled the Line, found @123 broken Pin Insulator o/p 5C-11 Cause : Lightning |  | 1 | 13:16 | Afternoon | Monday | 2018 | 10
9875 | 2018-10-30 10:10 | 2018-10-30 10:10 | MINAS POWER PLANT |  |  | 0 | 10:10 S/U MGT #5 and then Online the unit at 11:15. |  | 1 | 10:10 | Morning | Tuesday | 2018 | 10
9876 | 2018-10-30 10:28 | / | 13.8KV 8D FEEDER #11 | Fair | Construction Job | 0 | - |  | 1 | 10:28 | Morning | Tuesday | 2018 | 10
9877 | 2018-10-30 13:41 | 2018-10-30 13:41 | 13.8KV LIBO FEEDER #2 | Rain | Pin Insulator | 60 | Libo OCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 13:41 | Afternoon | Tuesday | 2018 | 10
9878 | 2018-10-30 13:41 | 2018-03-11 11:33 | 13.8KV LIBO FEEDER #2 | Rain | Pin Insulator | 60 | Checked & found Libo OCB fdr#2 T/LO, Ctr: 479-480, R/F: 51N Patrolled the Line, found @1 broken Pin insulator o/p 23-BV-24 Cause : Pin Insulator |  | 1 | 13:41 | Afternoon | Tuesday | 2018 | 10
9879 | 2018-10-30 13:45 | 2018-10-30 13:45 | MINAS POWER PLANT |  |  | 0 | 13:45 Offline MGT #4 and then S/D the unit , Status Standby. |  | 1 | 13:45 | Afternoon | Tuesday | 2018 | 10
9880 | 2018-10-30 14:27 | 2018-10-30 14:27 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 41 | Ketigul OCB Feeder#2 T/R 1x. Not checked yet. |  | 1 | 14:27 | Afternoon | Tuesday | 2018 | 10
9881 | 2018-10-30 14:27 | 2018-01-11 08:54 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 41 | Checked & found KTG VCB fdr#2 T/R 1x, Ctr: 302-303, R?F: 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 14:27 | Afternoon | Tuesday | 2018 | 10
9882 | 2018-10-31 09:36 | 2018-10-31 09:36 | 13.8KV MINAS FEEDER #4 | Fair | Construction Job | 0 | 09:36 Manually Open Recl. 7D-121 (Minas fdr#4). Installed Pipe Jumper at well 7D-58. 11:30 Blocked & closed Recl. 7D-121, then release the block. Cause: Construction Job. |  | 1 | 9:36 | Morning | Wednesday | 2018 | 10
9883 | 2018-10-31 12:50 | 2018-10-31 12:50 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 552 | 12:50 5B OCB fdr#2 T/O Checked & found 5B OCB fdr#2 T/LO, Ctr: 408-414, R/F: 51N 15:45 Patrolled the Line, Found @1 broken Jumper o/p 5C-30 @1 Flash over Dead end o/p 5C-30 @1 broken jumper o/p 3C-33 17:48 Blocke & Closed 5B OCB fdr#2, but Triped again After Finished Fixed the Problem. 18:07 Opened LBS 5C-01 Block & Closed 5B OCB fdr#2, OK . Cause: @1 broken jumper ( will be done tomorrow morning). Prod loss: 563 bbls / 26 wells up to 24:00. | 12345 | 1 | 12:50 | Afternoon | Wednesday | 2018 | 10
9884 | 2018-10-31 12:50 | 2018-01-11 09:30 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 552 | 09:30 Manually Open 3D OCB fdr#2. 11:50 Replaced @1@2@3 Broken Suspention Insulator o/p 5C-11. @1 Broken Dead End Insulator o/p 5C-11. Clean Up Fall Down trees. 12:25 Blocked & Closed 5B OCB fdr#2, then release the block. Cause: Lightning. Prod loss : 563 bbls / 26 wells up to 24:00 ( Oct 31,2018). Prod loss : 677 bbls / 26 wells up to 13:25 (Nov 01,2018). ----------------------------------------------------------------- + Grand Total: 1240 bbls / 26 wells. | 12345 | 1 | 12:50 | Afternoon | Wednesday | 2018 | 10
9885 | 2018-01-11 15:18 | 2018-01-11 15:18 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 48 | 3D OCB fdr#2 T/R 1x 3D fdr#3 Load dropped 74A (133-59A) Not checked yet. |  | 1 | 15:18 | Afternoon | Thursday | 2018 | 1
9886 | 2018-01-11 15:18 | 2018-06-11 15:18 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 48 | Checked & found 3D fdr#2 T/R 1x Ctr:272-273 R/F:51@2. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 15:18 | Afternoon | Thursday | 2018 | 1
9887 | 2018-01-11 15:18 | 2018-01-11 15:18 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 5 | 3D feeder #4 Load dropped 188A (216-28A). Not checked yet. |  | 1 | 15:18 | Afternoon | Thursday | 2018 | 1
9888 | 2018-01-11 15:18 | 2018-06-11 15:18 | 13.8KV 3D FEEDER #4 | Rain and Lightning | Lightning | 5 | Checked & found Recl. 2D-44 T/R 1x Ctr:226-227 R/F:51N. Patrolled the line & found @3 Broken Dead End Insulator o/p 2D-11. Cause : Lightning. |  | 1 | 15:18 | Afternoon | Thursday | 2018 | 1
9889 | 2018-01-11 18:22 | 2018-01-11 18:22 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain | Unidentified | 0 | Duri Community fdr#3 T/R 1x. Not checked yet. |  | 1 | 18:22 | Afternoon | Thursday | 2018 | 1
9890 | 2018-01-11 18:22 | 2018-08-11 18:22 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain | Unidentified | 0 | Checked & found Duri Community fdr#3 T/R 1x Ctr:84-85 R/F:51. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 18:22 | Afternoon | Thursday | 2018 | 1
9891 | 2018-02-11 17:05 | 2018-02-11 17:05 | CENTRAL DURI POWER PLANT |  |  | 0 | CGT #4 S/U, then On Line at 17:29 to backed Up CGT #5, Reboot Computer(anticipate Unit Trip) |  | 1 | 17:05 | Afternoon | Sunday | 2018 | 2
9892 | 2018-02-11 19:15 | 2018-02-11 19:15 | CENTRAL DURI POWER PLANT |  |  | 0 | 19:15 Offline CDGT #4 and then S/D the unit for Stand by. |  | 1 | 19:15 | Night | Sunday | 2018 | 2
9893 | 2018-02-11 23:00 | 2018-02-11 23:00 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Animal | 47 | Libo OCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 23:00 | Night | Sunday | 2018 | 2
9894 | 2018-02-11 23:00 | 2018-03-11 11:32 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Animal | 47 | Checked & found Libo OCB fdr#2 T/R 1x, Ctr: 480-481, R/F: 51N Patrolled the Line, found dead Bird on @2 Structure substation Cause : Animal (Bird) |  | 1 | 23:00 | Night | Sunday | 2018 | 2
9895 | 2018-03-11 08:00 | 2018-03-11 08:00 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 53 | 08:00 Rangau fdr#2 Load dropped 142A (150-8A). 11:43 Checked & found Recl. 23-BD-01 T/LO, Ctr: 248-252, R/F: 51N Patrolled the Line, but found nothing. Manually blocked and closed Recloser: 23-BD-01 --> Success and then released the block. Cause : Unidentified. |  | 1 | 8:00 | Morning | Sunday | 2018 | 3
9896 | 2018-03-11 13:32 | 2018-03-11 13:32 | 44KV NORTH DURI - DUMAI LINE | Cloudy | Tree | 0 | N.Duri 44Kv GCB#1 T/R 1x. Not checked yet. |  | 1 | 13:32 | Afternoon | Sunday | 2018 | 3
9897 | 2018-03-11 13:32 | 2018-07-11 11:17 | 44KV NORTH DURI - DUMAI LINE | Cloudy | Tree | 0 | Checked and found 44 kV GCB #1 ND T/R 1x, ctr: 128 - 129, R/F: 51P @1, @2 Patrolled and found a rubber tree closed to line near pole DD-86. Cause : Tree |  | 1 | 13:32 | Afternoon | Sunday | 2018 | 3
9898 | 2018-03-11 17:35 | 2018-03-11 17:35 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | 17:35 N.Duri fdr#1 T/O (in Blocked position). 17:39 Blocked & closed N.Duri fdr#1, then released the block after confirm with WSM Rig BN 18 Not checked yet. |  | 1 | 17:35 | Afternoon | Sunday | 2018 | 3
9899 | 2018-03-11 17:35 | 2018-07-11 11:11 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked and found ND fdr #1 T/R, ctr: 297 - 298, R/F: 51P @1, @2 Patrolled and found nothing Cause : Unidentified |  | 1 | 17:35 | Afternoon | Sunday | 2018 | 3
9900 | 2018-04-11 10:15 | 2018-04-11 10:15 | 13.8KV NORTH DURI FEEDER #6 | Cloudy | Recloser | 143 | 10:15 It was reported No Power o/p 12-F11-08 (ND fdr#6) 13:30 Checked & found, Recl. 12-F11-02 T/O, Ctr: 79-80 Tried to Close the Redcloser, but Fail, control Recloser problem, 15:25 Man. Opened ND fdr#6, to Install Bypass 15:35 Man. Closed ND fdr #6, after finished by pass Recl 12-F11-02 Patrolled the Line but found nothing Cause: Recloser (Control) |  | 1 | 10:15 | Morning | Wednesday | 2018 | 4
9901 | 2018-04-11 13:40 | 2018-05-11 10:30 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 225 | On 04 Nov 2018 at 15:00, Bangko VCB Feeder 1 T/R 1X counter: 62-63, R/F : 51, on phase B, patrolled and found normal operation. |  | 1 | 13:40 | Afternoon | Wednesday | 2018 | 4
9902 | 2018-04-11 13:40 | 2018-05-11 10:30 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 225 | On 04 Nov 2018 at 15:00, Bangko VCB Feeder 1 T/R 1X counter: 62-63, R/F : 51, on phase B, patrolled and found normal operation. |  | 1 | 13:40 | Afternoon | Wednesday | 2018 | 4
9903 | 2018-04-11 13:41 | 2018-04-11 13:41 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 133 | Nella VCB Fdr #1, T/R 1x Not checked yet |  | 1 | 13:41 | Afternoon | Wednesday | 2018 | 4
9904 | 2018-04-11 13:41 | 2018-05-11 10:30 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 133 | Checked & found Nella VCB Fdr #1, T/R 1x, Ctr: 533-534, R/F : 51N Patrolled the Line, but found Nothing. Cause: Lightning |  | 1 | 13:41 | Afternoon | Wednesday | 2018 | 4
9905 | 2018-04-11 14:30 | 2018-04-11 14:30 | 115KV MINAS - 5B LINE | Rain and Lightning | Lightning | 141 | 14:30 115Kv Line Minas-5B GCB#51 T/O, R/F: 87 Z1. then Closed at 14:55 115Kv Line Minas-5B GCB#53 T/O, then Closed at 14:55 115Kv Line 5B-Minas OCB#22 T/O, R/F : 87 Z1 Then Closed at 14:55 115Kv Line 5B-Minas OCB#25 T/O, then Closed at 14:55 Freq : 60:81 HZ Minas fdr# 1 load dropped 90A (197-105A). Prod loss: 39 Bbls / 15 wells. 3D fdr#2 load dropped 36A (211-175A). 3D fdr#3 load dropped 19A (125-106A). 3D fdr#4 load dropped 35A (195-160A). 3D fdr#7 load dropped 52A (117-65A). 3D fdr#8 load dropped 69A (155-86A). 4D fdr#4 load dropped 29A (52-23A). 4D fdr#5 load dropped 42A (254-212A). 4D fdr#6 load dropped 67A (154-87A). 6DN fdr#1 load dropped 130A (167-37A). Prod loss: 36 Bbls / 20 wells. 6DN fdr#2 load dropped 216A (277-61A). Prod loss: 86 Bbls / 33 wells. 6DN fdr#3 load dropped 42A (188-146A). WIP. 6DN fdr#4 load dropped 45A (209-164A). WIP. 6DN fdr#6 load dropped 34A (201-167A). 4B fdr#5 load dropped 39A (174-135A). 4B fdr#6 load dropped 20A (105-85A). 4B fdr#8 load dropped 54A (180-126A). 5B fdr#1 T/R 1x. 5B fdr#2 load dropped 126A (188-62A). 5B fdr#3 load dropped 52A (111-59A). 5B fdr#4 load dropped 26A (91-65A). 5B fdr#5 load dropped 10A (26-16A). 5B fdr#6 load dropped 167A (175-8A). 6D fdr#1 load dropped 167A (242-75A). 6D fdr#2 load dropped 85A (204-119A). 6D fdr#3 load dropped 61A (178-117A). 6D fdr#4 load dropped 72A (218-146A). 6D fdr#6 load dropped 179A (243-64A). 8C fdr#1 load dropped 142A (174-32A). 8C fdr#2 load dropped 38A (92-54A). 8C fdr#3 load dropped 87A (208-121A). 8C fdr#4 load dropped 235A (282-47A). 8C fdr#5 load dropped 127A (193-66A). 8C fdr#6 load dropped 48A (202-154A). 8D fdr#1 load dropped 42A (98-56A). 8D fdr#2 load dropped 13A (89-76A). 8D fdr#3 load dropped 30A (99-69A). 8D fdr#5 load dropped 41A (157-116A). 8D fdr#7 load dropped 11A (198-187A). 8D fdr#8 load dropped 111A (180-69A). 8D fdr#9 load dropped 144A (155-11A). 8D fdr#10 load dropped 33A (134-101A). 8D fdr#11 load dropped 16A (117-101A). Bangko fdr#2 load dropped 82A ( 252-170A). Bangko fdr#3 load dropped 30A ( 225-195A). Bangko fdr#4 load dropped 53A ( 188-135A). Sintong fdr#2 load dropped 12A (185-173A). So.Bekasap fdr#1 load dropped 78A (126-48A). Bekasap fdr#5 load dropped 77A (223-146A). Pematang fdr#1 load dropped 72A (214-142A) Pematang fdr#2 load dropped 15A (97-82A) OKB fdr#2 load dropped 12A (262-250A). NKBS fdr#5 load dropped 77A (150-73A). CKBS fdr#1 load dropped 45A (290-245A). CKBS fdr#2 load dropped 227A (251-24A). CKBS fdr#5 load dropped 55A (291-236A). CKBS fdr#6 load dropped 8A (173-165A). Petapahan fdr#2 load dropped 83A (83-0A). Petapahan fdr#3 load dropped 21A (152-131A). Petapahan fdr#6 load dropped 22A (60-38A). Petapahan fdr#7 load dropped 46A (67-21A). 14:30 Man. Opened Gen. Breaker MGT #6, then Closed at 14:35 14:32 Man. Opened Gen. Breaker MGT #7, then Closed at 14:55 14:34 Man. Opened Gen. Breaker MGT #8, then Closed at 15:04 14:37 Manually Open Minas fdr# 3, then Closed at 15:00 (Req. GS#2) Prod loss: 69 Bbls / 29 wells. 14:37 Manually Open Minas fdr# 4, then Closed at 15:00 (Req. GS#2) Prod loss: 48 Bbls / 15 wells. Cause : Under investigation | 12345 | 1 | 14:30 | Afternoon | Wednesday | 2018 | 4
9906 | 2018-04-11 14:30 | 14/11/2018 15:42 | 115KV MINAS - 5B LINE | Rain and Lightning | Lightning | 141 | Checked and found MNS GCB #51 T/O, ctr: 180-181, R/F 87L MNS GCB #53 T/O, ctr: 163-164, R/F None 5B GCB #22 T/O, ctr: 663-663, R/F: 81 5B GCB #25 T/O, ctr: 225-226, R/F: None Patrolled and found Broken Suspension Insulator Ø1 on Pole M5B-15 near Loc. 6D-55 Cause : Lightning | 12345 | 1 | 14:30 | Afternoon | Wednesday | 2018 | 4
9907 | 2018-04-11 19:18 | 2018-04-11 19:18 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 153 | 19:18 Sintong OCB fdr #2 T/R 1x. counter: 480-481, R/F : 51N Sintong GFPC T/R 1x. 19:46 It was reported no power at Benar GS and Field. 21:00 Patrolled the line, found Recloser: 28-AF-02 T/O Counter: 1536-1537. (In block position due to Rig BN #08 activity at well Benar #05). 21:02 Manually blocked and closed Recloser: 28-AF-02 --> Success (Recloser still in block position). Cause: Lightning |  | 1 | 19:18 | Night | Wednesday | 2018 | 4
9908 | 2018-04-11 19:26 | 2018-04-11 19:26 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 73 | Bangko OCB fdr #4 T/R 1x. Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 19:26 | Night | Wednesday | 2018 | 4
9909 | 2018-04-11 19:26 | 2018-05-11 10:00 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 73 | Checked & found Bangko VCB Fdr#4 T/R 1x, Ctr: 56-57, R/F : 51, @C Patrolled the line, but found nothing Cause: Lightning |  | 1 | 19:26 | Night | Wednesday | 2018 | 4
9910 | 2018-05-11 08:05 | 2018-05-11 08:05 | 13.8KV 6D FEEDER #3 | Cloudy | Lightning | 14 | 6D fdr #3 load dropped 31A (178-147A). Not checked yet. |  | 1 | 8:05 | Morning | Friday | 2018 | 5
9911 | 2018-05-11 08:05 | 13/11/2018 19:05 | 13.8KV 6D FEEDER #3 | Cloudy | Lightning | 14 | Checked & found Recl. 6D-03 T/R 1x Ctr:164-165 R/F:51N. Patrolled the line & found @1@3 Broken Dead End Insulator o/p 6D-06. Cause : Lightning. |  | 1 | 8:05 | Morning | Friday | 2018 | 5
9912 | 2018-05-11 09:20 | 2018-05-11 09:20 | 13.8KV 4D FEEDER #5 | Cloudy | Lightning | 9 | 4D OCB fdr#5 T/R 1x Not checked yet |  | 1 | 9:20 | Morning | Friday | 2018 | 5
9913 | 2018-05-11 09:20 | 2018-06-12 14:19 | 13.8KV 4D FEEDER #5 | Cloudy | Lightning | 9 | Checked and found, 4DSB-13.8OCB5 T/R Counter : 332 - 333 Relay Flag : 50 Patrolled the line & found Phase 1, 2, Broken Bushing Recl on pole 4D51A Cause : Lightning |  | 1 | 9:20 | Morning | Friday | 2018 | 5
9914 | 2018-05-11 13:30 | 2018-05-11 13:30 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Lightning | 76 | S.Balam VCB fdr#4 T/R 1x not checked yet |  | 1 | 13:30 | Afternoon | Friday | 2018 | 5
9915 | 2018-05-11 13:30 | 2018-06-11 13:30 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Lightning | 76 | Checked & found So Balam VCB Fdr 4 T/R 3X Ctr:361-364 R/F:51N. So.Balam GFPC T/R 1X Ctr:458-459 . Patrolled the Line & found @1@2 B/O fuse PT Recloser O/P 17-AA-43. Cause: Lightning. |  | 1 | 13:30 | Afternoon | Friday | 2018 | 5
9916 | 2018-05-11 13:52 | 2018-05-11 13:52 | 13.8KV 8C FEEDER #1 | Rain and Lightning | Unidentified (Fuse) | 0 | 8C fdr#1 Load dropped 112A(164-56A) Not checked yet |  | 1 | 13:52 | Afternoon | Friday | 2018 | 5
9917 | 2018-05-11 13:52 | 13/11/2018 07:28 | 13.8KV 8C FEEDER #1 | Rain and Lightning | Unidentified (Fuse) | 0 | Checked and found RCL 9D-111 not operate, ctr: 1250-1250, R/F: 50N Patrolled and found fuse PT of RCL 9D-111 B/O Cause : Unidentified (Fuse) |  | 1 | 13:52 | Afternoon | Friday | 2018 | 5
9918 | 2018-05-11 13:54 | 2018-05-11 13:54 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 0 | 8D OCB fdr#7 T/R 1x Not checked yet |  | 1 | 13:54 | Afternoon | Friday | 2018 | 5
9919 | 2018-05-11 13:54 | 13/11/2018 07:14 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 0 | Checked and found 8D fdr #7 T/R 1x, ctr: 675 - 676, R/F: 50N Patrolled and found nothing. Cause : Lightning |  | 1 | 13:54 | Afternoon | Friday | 2018 | 5
9920 | 2018-05-11 13:59 | 2018-05-11 13:59 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 29 | 6D OCB feeder #2 T/R 1x Not checked yet. |  | 1 | 13:59 | Afternoon | Friday | 2018 | 5
9921 | 2018-05-11 13:59 | 13/11/2018 19:59 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 29 | Checked & found 6D fdr#2 T/R 1x Ctr:245-246 R/F:51N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 13:59 | Afternoon | Friday | 2018 | 5
9922 | 2018-05-11 14:11 | 2018-05-11 14:11 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 83 | Sintong GFPC T/R 1x Sintong Fdr#2 Load dropped 117A(185-68) Not checked yet. |  | 1 | 14:11 | Afternoon | Friday | 2018 | 5
9923 | 2018-05-11 14:18 | 2018-05-11 14:18 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 48 | Sintong fdr #1 load dropped 55A (97-42A). Not checked yet. |  | 1 | 14:18 | Afternoon | Friday | 2018 | 5
9924 | 2018-05-11 14:18 | 2018-06-11 10:30 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 48 | Checked & found Recloser 25 AD 26 T/R 1x, Ctr: 125-126, R/F : 51 @123 patrolled the line, but found nothing Cause: Lightning |  | 1 | 14:18 | Afternoon | Friday | 2018 | 5
9925 | 2018-05-11 14:21 | 2018-05-11 14:21 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | Bangko fdr #4 load dropped 67A (180-113A). Not checked yet. |  | 1 | 14:21 | Afternoon | Friday | 2018 | 5
9926 | 2018-05-11 15:10 | 2018-09-11 08:15 | 115KV CENTRAL DURI - BALAI MAKAM LINE | Rain and Lightning | Lightning | 255 | Cause : Lightning Date Patrol : 05-NOV-2018 Operated Device : 13.8KVKTGLFDR1 T/R Counter : 164 - 165 Relay Flag : 87 Finding Patrol : NONE Phase : 1, 2, Pole : 0 Date Patrol : 05-NOV-2018 Operated Device : 13.8KVKTGLFDR3 T/O Counter : 197 - 198 Relay Flag : 87 Finding Patrol : NONE Phase : 1, 2, Pole : 0 Patrol by : NA/BKP Nas Input by : NAKHYAR |  | 1 | 15:10 | Afternoon | Friday | 2018 | 5
9927 | 2018-05-11 15:10 | 2018-09-11 08:15 | 115KV CENTRAL DURI - BALAI MAKAM LINE | Rain and Lightning | Lightning | 255 | Cause : Lightning Date Patrol : 05-NOV-2018 Operated Device : 13.8KVKTGLFDR1 T/R Counter : 164 - 165 Relay Flag : 87 Finding Patrol : NONE Phase : 1, 2, Pole : 0 Date Patrol : 05-NOV-2018 Operated Device : 13.8KVKTGLFDR3 T/O Counter : 197 - 198 Relay Flag : 87 Finding Patrol : NONE Phase : 1, 2, Pole : 0 Patrol by : NA/BKP Nas Input by : NAKHYAR |  | 1 | 15:10 | Afternoon | Friday | 2018 | 5
9928 | 2018-05-11 16:04 | 2018-05-11 16:04 | 13.8KV 8D FEEDER #2 | Fair | Others | 0 | 16:04 Manually opened 8D OCB fdr #2. Due to maintain water level tank. |  | 1 | 16:04 | Afternoon | Friday | 2018 | 5
9929 | 2018-05-11 16:04 | 2018-06-11 19:32 | 13.8KV 8D FEEDER #2 | Fair | Others | 0 | 19:32 Manually blocked and closed 8D OCB fdr #2 --> OK. and then released the block. Cause: Others. |  | 1 | 16:04 | Afternoon | Friday | 2018 | 5
9930 | 2018-06-11 07:22 | 2018-06-11 07:22 | 13.8KV DURI COMMUNITY FEEDER #2 | Cloudy | Unidentified | 0 | Duri Community ACB fdr#2 T/R 1x. Not checked yet. |  | 1 | 7:22 | Morning | Monday | 2018 | 6
9931 | 2018-06-11 07:22 | 2018-11-11 04:22 | 13.8KV DURI COMMUNITY FEEDER #2 | Cloudy | Unidentified | 0 | Checked & found Duri Community fdr#2 T/R 1x Ctr:101-102 R/F:51@2. Patrolled the line & found @2 Broken Dead End Insulator o/p 2F16. Cause : Unidentified. |  | 1 | 7:22 | Morning | Monday | 2018 | 6
9932 | 2018-07-11 06:16 | 2018-07-11 06:16 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | N Duri VCB fdr #5 T/R 1x. Not checked yet. |  | 1 | 6:16 | Morning | Wednesday | 2018 | 7
9933 | 2018-07-11 06:16 | 2018-11-11 06:16 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | Checked & found N.Duri fdr#5 T/R 1x Ctr:130-131 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 6:16 | Morning | Wednesday | 2018 | 7
9934 | 2018-07-11 09:33 | 2018-07-11 09:33 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 82 | 44 kV OCB fdr #1 PMT Main (line to Petani) T/R 1x Not Checked Yet |  | 1 | 9:33 | Morning | Wednesday | 2018 | 7
9935 | 2018-07-11 09:33 | 2018-11-11 21:33 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 82 | Checked & found 44Kv Line Pematang-Petani OCB#1 T/R 1x Ctr:4018-4019 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 9:33 | Morning | Wednesday | 2018 | 7
9936 | 2018-07-11 09:33 | 2018-07-11 09:33 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 0 | Pematang fdr#1 Load dropped 154A (208-54A). Pematang fdr#2 Load dropped 22A (88-66A). Not checked yet. |  | 1 | 9:33 | Morning | Wednesday | 2018 | 7
9937 | 2018-07-11 09:33 | 13/11/2018 07:36 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 0 | Checked and found all in normal condition, ctr OCB fdr #1: 138 - 138 Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 9:33 | Morning | Wednesday | 2018 | 7
9938 | 2018-07-11 16:13 | 2018-07-11 16:13 | 13.8KV NORTH DURI FEEDER #2 | Drizzle | Lightning | 0 | North Duri fdr #2 Load Dorp 168 A (196 - 28 A) North Duri fdr #3 Load Drop 16 A (79 - 63 A) Not Checked Yet |  | 1 | 16:13 | Afternoon | Wednesday | 2018 | 7
9939 | 2018-07-11 16:13 | 2018-11-11 06:13 | 13.8KV NORTH DURI FEEDER #2 | Drizzle | Lightning | 0 | Checked & found Recl NC-04 T/R 2x Ctr:54-56 R/F:51@3. Patrolled the line & found @3 Broken LA o/p NN. Cause : Lightning. |  | 1 | 16:13 | Afternoon | Wednesday | 2018 | 7
9940 | 2018-07-11 17:05 | 2018-07-11 17:05 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | Rangau fdr #2 drop 140 A (156 - 16 A) Not Checked Yet |  | 1 | 17:05 | Afternoon | Wednesday | 2018 | 7
9941 | 2018-07-11 17:05 | 2018-11-11 19:05 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | Checked & found Recl 23BD01 T/R 2x Ctr:352-354 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:05 | Afternoon | Wednesday | 2018 | 7
9942 | 2018-08-11 08:53 | 2018-08-11 08:53 | SINTONG SUBSTATION | Fair | Planned Maintenance | 4932 | 09:36 Man Open 115 kV GCB #1 Batang - Sintong Line, closed at 11:49 09:37 Man Open 115 kV OCB #23 Sintong, closed at12:29 09:34 Man Open 115 kV OCB #22 Sintong, closed bypass switch at 12:30 (closing coil burned out) 09:35 Man Open 115 kV OCB #21 Sintong, closed at 12:30 09:33 Man Open 115 kV OCB #24 Bangko, closed at 12:31 09:31 Man Open 115 kV GCB #26 Nella, closed at 12:34 09:29 Man Open 115 kV GCB #27 Nella, closed at 12:35 12:27 Closed 115 kV GCB #25 Sintong 09:00 Open Nella VCB fdr #1, closed at 13:03 09:01 Open Nella VCB fdr #2, closed at 13:00 09:04 Open Bangko VCB fdr #1, closed at 12:43 09:05 Open Bangko VCB fdr #4, closed at 12:45 09:11 Open BKO VCB fdr #2, closed at 12:41 09:18 Open BKO VCB fdr #3, closed at 12:37 09:24 Open STG VCB fdr #1, closed at 12:48 09:26 Open STG VCB fdr #2, closed at 12:47 09:29 Open 115 kV Nella GCB #27 (Pinang fdr #1), closed at 12:35 09:08 Open BLM VCB fdr #1, closed at 12:54 09:08 Open BLM VCB fdr #4, closed at 13:09 09:15 Open BLM VCB fdr #2, closed at 12:53 09:16 Open BLM VCB fdr #3, closed at 12:51 Cause : Planned Maintenance - Re-energize 115 kV GCB #25 Sintong - Re-energize New 115 kV CCPD Sintong - Repair 115 kV Isolation Switch of OCB #22 Sintong - Repair 115 kV Line Switch of OCB #22 Sintong Prod Loss: BKO GS : 4644 Bbls 315 wells. BLM GS : 1933 Bbls 199 Wells. Total Prod Loss : 6577 Bbls 514 wells. | 123 | 1 | 8:53 | Morning | Saturday | 2018 | 8
9943 | 2018-08-11 14:23 | 2018-08-11 14:23 | 4.16KV EAST RUMBAI FEEDER #1 | Fair | Under investigation | 0 | 14:23 4.16 kV East Rumbai fdr #1 T/R 21x (during 14:23 to 17:02) 15:02 Patrolled the lines and found nothing 18:00 Re-check the relay and found over current relay on @3 was failed and then unplug the relay cause : Under Investigation |  | 1 | 14:23 | Afternoon | Saturday | 2018 | 8
9944 | 2018-08-11 15:40 | 2018-08-11 15:40 | 13.8KV 3D FEEDER #8 | Fair | Planned Maintenance | 0 | 15:54 Manual Open 3D OCB fdr #8 for replace broken dead end o/p 3D-99 17:02 Blocked and Close 3D OCB fdr #8, then release the block after finished the job. Cause: Planned Maintenance |  | 1 | 15:40 | Afternoon | Saturday | 2018 | 8
9945 | 2018-09-11 08:49 | 2018-09-11 08:49 | MINAS POWER PLANT |  |  | 0 | 08:49 S/U MGT#10 Then on line the unit at 11:20. (Running Test). 21:50 Off line MGT#10, then S/D the unit for Maintenance. |  | 1 | 8:49 | Morning | Tuesday | 2018 | 9
9946 | 2018-09-11 16:18 | 2018-09-11 16:18 | 13.8KV 6DN FEEDER #6 | Fair | Construction Job | 0 | 16:18 Manually open 6DN fdr#6. Dismantling 16"pipe. 18:30 Blocked closed 6DN fdr#6. Cause : Construction job. |  | 1 | 16:18 | Afternoon | Tuesday | 2018 | 9
9947 | 2018-09-11 17:46 | 2018-09-11 17:46 | NEW PETAPAHAN SUBSTATION | Heavy Rain | Under investigation | 2196 | 17:46 115 kV GCB #3 NEW PTP T/O 115 kV GCB #5 NEW PTP T/O 18:20 Check and found TX-2 NEW PTP OFF, R/F 87T; 50/51N; 51P @1, @2 18:24 Manual Open PTP fdr #2 18:24 Manual Open PTP fdr #3 18:24 Manual Open PTP fdr #4 18:25 Manual Open PTP fdr #6 18:26 Manual Open PTP fdr #7 18:26 Manual Open PTP fdr #8 18:27 Manual Open Tie Breaker Bus-1 and Bus-2 19:32 Manually closed 115 kV GCB #5 NEW PTP. 19:50 Blocked & closed PTP fdr#8. OK. 20:09 Manually Close MOD/line Switch of TX-1 PTP. 20:10 Closed 115KV GCB#2. 20:11 Closed 115KV GCB#3. 20:15 Blocked & closed PTP fdr#2. 20:18 Manually open PTP fdr#2. 20:49 Blocked & closed PTP fdr#2. 21:05 Blocked & closed PTP fdr#3. 21:05 Blocked & closed PTP fdr#4. 23:09 Patrolled the line D/S PTP fdr#6 & found @2@3 Broken Jumper o/p 31DA08. 23:27 Blocked & closed PTP fdr#6, then release the block. Cause: Under Investigation. | 123 | 1 | 17:46 | Afternoon | Tuesday | 2018 | 9
9948 | 2018-09-11 18:13 | 2018-09-11 18:13 | 4.16KV SO RUMBAI FEEDER #4 | Rain and Lightning | Lightning | 0 | 18:13 South Rumbai fdr #4 T/SO 18:18 Reported by FM Helpdest that no power at some housing complex (flamboyant, cemara, etc) and reported any spark at TX at golf court (near SD) 19:23 Check & Found south RBI fdr#4 T/So R/F 51@3, Ctr:173-174. 19:24 Blocked & closed S.RBI fdr#4 then release the block. cause: Not checked yet. |  | 1 | 18:13 | Afternoon | Tuesday | 2018 | 9
9949 | 2018-09-11 18:13 | 13/11/2018 19:13 | 4.16KV SO RUMBAI FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked & found So.Rumbai fdr#4 T/R 1x Ctr:173-174 R/F:51@3. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 18:13 | Afternoon | Tuesday | 2018 | 9
9950 | 2018-10-11 09:35 | 2018-10-11 09:35 | 13.8KV 6DN FEEDER #6 | Fair | Construction Job | 0 | 09:35 Manual Open 6DN fdr #6 Dismantling and repair 16 pipe 18:10 Blocked and Close 6DN fdr #6, ok then release the block cause: construction job |  | 1 | 9:35 | Morning | Thursday | 2018 | 10
9951 | 2018-10-11 10:00 | 2018-10-11 10:00 | 13.8KV 8D FEEDER #10 | Fair | Planned Maintenance | 0 | 10:00 Manual Open RCL 7E-21 Change out TX at 8D-19 225 kVA to 300 kVA, R/M 75 - 125 HP 11:15 Block and close RCL 7E-21, ok then release the block cause: planned maintenance |  | 1 | 10:00 | Morning | Thursday | 2018 | 10
9952 | 2018-10-11 10:01 | 2018-10-11 10:01 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Planned Maintenance | 143 | 10:01 Manual Open PTP fdr #6 Repair broken jumper on pole 31-DA-08 12:13 Blocked and close PTP fdr #6, ok then release the block cause: planned maintenance |  | 1 | 10:01 | Morning | Thursday | 2018 | 10
9953 | 2018-10-11 14:45 | 2018-10-11 14:45 | MINAS POWER PLANT |  |  | - | 14:45 S/U MGT#10 and then online the unit at 15:19. |  | 1 | 14:45 | Afternoon | Thursday | 2018 | 10
9954 | 2018-10-11 17:10 | 2018-10-11 17:10 | CENTRAL DURI POWER PLANT |  |  | - | 17:10 CDGT-5 S/U and put to ON/L at 17:43 |  | 1 | 17:10 | Afternoon | Thursday | 2018 | 10
9955 | 2018-10-11 17:50 | 2018-10-11 17:50 | CENTRAL DURI POWER PLANT |  |  | - | 17:50 CDGT-4 OFF/L and S/D cause: high vibration at 88FC-3 |  | 1 | 17:50 | Afternoon | Thursday | 2018 | 10
9956 | 2018-11-11 01:42 | 14/11/2018 09:13 | 13.8KV 8C FEEDER #2 | Rain and Lightning | Lightning | 133 | Checked and found, 8CSB-13.8VCB2 T/R Counter : 521 - 522 Relay Flag : 50N Patrolled the line, found Phase 2 Broken Pin supp. 9D176 on pole 9D176 Cause : Lightning |  | 1 | 1:42 | Night | Sunday | 2018 | 11
9957 | 2018-11-11 01:42 | 14/11/2018 09:13 | 13.8KV 8C FEEDER #2 | Rain and Lightning | Lightning | 133 | Checked and found, 8CSB-13.8VCB2 T/R Counter : 521 - 522 Relay Flag : 50N Patrolled the line, found Phase 2 Broken Pin supp. 9D176 on pole 9D176 Cause : Lightning |  | 1 | 1:42 | Night | Sunday | 2018 | 11
9958 | 2018-11-11 01:42 | 2018-11-11 01:42 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 42 | 8C OCB feeder#3 T/R1x. Not checked yet. |  | 1 | 1:42 | Night | Sunday | 2018 | 11
9959 | 2018-11-11 01:42 | 13/11/2018 19:42 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 42 | Checked & found 8C OCB fdr#3 T/R 1x Ctr:515-516 R/F:50N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 1:42 | Night | Sunday | 2018 | 11
9960 | 2018-11-11 09:34 | 2018-11-11 09:34 | 13.8KV 6DN FEEDER #6 | Fair | Construction Job | 0 | 09:34 Manual Open VCB 6DN fdr #6 16:50 Block and Close VCB 6DN fdr #6, Ok then release the block. cause: Construction Job |  | 1 | 9:34 | Morning | Sunday | 2018 | 11
9961 | 2018-11-11 17:11 | 2018-11-11 17:11 | 13.8KV KETIGUL FEEDER#3 | Fair | Emergency | 0 | 17:11 Manual Open KTGL fdr #3 (flooded at Gulamo Field) Cause: Emergency |  | 1 | 17:11 | Afternoon | Sunday | 2018 | 11
9962 | 2018-12-11 06:26 | 2018-12-11 06:26 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified (L/A) | - | Rokan VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 6:26 | Morning | Tuesday | 2018 | 12
9963 | 2018-12-11 06:26 | 13/11/2018 08:06 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified (L/A) | - | Checked and found RKN fdr #2 T/R 1x, ctr: 1271 - 1272, R/F: 51P @3 Patrolled and found broken LA @3 Cause : Unidentified (L/A) |  | 1 | 6:26 | Morning | Tuesday | 2018 | 12
9964 | 2018-12-11 10:33 | 2018-12-11 10:33 | MINAS POWER PLANT | Fair |  | 0 | 10:33 Off line MGT#10, then S/D the unit for Vibration balancing. 14:49 S/U MGT#10, then on line the unit at 15:22. 16:02 Off line MGT#10, then S/D the unit for Vibration Balancing. |  | 1 | 10:33 | Morning | Tuesday | 2018 | 12
9965 | 2018-12-11 17:42 | 2018-12-11 17:42 | CENTRAL DURI POWER PLANT |  |  | 0 | 17:42 CDGT #1 OFF/L and S/D Purpose to maintain gas pressure to CDGT (MAWP) 17:45 Close ACB-19 Tie Breaker for Bus-1 an Bus-2 at CD |  | 1 | 17:42 | Afternoon | Tuesday | 2018 | 12
9966 | 2018-11-13 06:53 | 2018-11-13 06:53 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | - | C.Duri fdr#1 Load dropped 38A (99-61A). Not checked yet. |  | 1 | 6:53 | Morning | Tuesday | 2018 | 11
9967 | 2018-11-13 06:53 | 2018-11-15 17:33 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | - | Checked and found RCL 39-AV-36 T/R 1x, ctr: 293 - 294, R/F: None Patrolled the line and found broken pin @2 and @3 o/p 39-AV-36 Cause : Lightning |  | 1 | 6:53 | Morning | Tuesday | 2018 | 11
9968 | 2018-11-13 11:15 | 2018-11-13 11:15 | MINAS POWER PLANT | Fair |  | 0 | 11:15 Started Up MGT #3 and On line to the sytem at 11:30. |  | 1 | 11:15 | Morning | Tuesday | 2018 | 11
9969 | 2018-11-13 15:46 | 2018-11-13 15:46 | 13.8KV RANGAU FEEDER #2 | Fair | Lightning | 26 | 15:46 Rangau fdr #2 load dropped 130A (147-17A). Not checked yet. |  | 1 | 15:46 | Afternoon | Tuesday | 2018 | 11
9970 | 2018-11-13 15:46 | 2018-11-15 17:36 | 13.8KV RANGAU FEEDER #2 | Fair | Lightning | 26 | Checked and found RCL 39-AV-36 T/R 1x, ctr: 354 - 355, R/F: None Patrolled the line but found nothing. Cause : Lightning |  | 1 | 15:46 | Afternoon | Tuesday | 2018 | 11
9971 | 2018-11-13 16:33 | 2018-11-13 16:33 | MINAS POWER PLANT |  |  | 0 | 16:33 S/U MGT#10. then On line the unit at 17:05. (Taking data vibration). 17:30 Off line MGT#10, then S/D the unit for Maintenance. |  | 1 | 16:33 | Afternoon | Tuesday | 2018 | 11
9972 | 2018-11-14 10:31 | 2018-11-14 10:31 | 13.8KV BATANG FEEDER #2 | Fair | Construction Job | 0 | 10:31 Manually opened Batang OCB fdr #2. Due to cut jumper to isolate 11 wells at Rantau Bais field. 12:15 Manually blocked and close Batang OCB fdr #2 and then released the block. Cause: Construction job ( water flooding). |  | 1 | 10:31 | Morning | Wednesday | 2018 | 11
9973 | 2018-11-14 10:58 | 2018-11-14 10:58 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | - | it was reported b/o fuse on pole 05-P1-19 D/S C Duri fdr #15. Not checked yet. |  | 1 | 10:58 | Morning | Wednesday | 2018 | 11
9974 | 2018-11-14 10:58 | 2018-11-15 17:36 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified (Fuse) | - | Checked and found b/o fuse @1 o/p 05-P1-19 Cause : Unidentified (Fuse) |  | 1 | 10:58 | Morning | Wednesday | 2018 | 11
9975 | 2018-11-14 13:27 | 2018-11-14 13:27 | 13.8KV CENTRAL DURI FEEDER #7 | Cloudy | Guy Wire | 0 | 13:27 C Duri fdr #7 load dropped 83A (112-29A) 15:41 Checked and found Recloser 03-03-42 T/O (in block position). 15:48 Blocked closed Recloser 03-03-42 --> but failed. Patrolled the line nothing found. 17:35 Blocked closed Recloser 03-03-42 --> but failed again. 18:00 Manually open LBS: 03- 01-02. 18:22 Manually open C Duri fdr #7 due to close by pass Recl: 03-03-42. 18:27 Manually blocked and closed C Duri fdr #7 --> Success. 18:45 Manually closed LBS: 03-01-02. 18:50 Re-checked and found no power along road 03-02-xx Patrolled the line and found RCL 03-2-02 T/LO 18:54 Manually blocked and closed Recl: 03-02-02 --> but failed. 20:05 Continue patrolled the line d/s 03-2-02 but found nothing 22:17 Blocked and closed RCL 03-2-02 but failed again November 15, 2018. 02:58 Re-patrolled the lines and found broken pin support insulator o/p 03-2-02 @3 (the jumper hanging) 03:14 Blocked and closed RCL 03-2-02, but failed again 03:18 Call HO to open padlock of test station area-3 (SW-1) 04:01 Checked the line and TX inside TS SW-1 and found normal 04:16 Call TL-OPS and decided to continue the patrolled by new crew (morning crew) 05:30 Continue patrolled the line found broken Fuse Cut Out behind of Test Station on pole 03-02-36C. then isolated by open Hot Line Clamp. 1. Replaced 3 pcs broken Fuse Cut Out. 2. Replaced 3 pcs Hot Line Clamp. 3. Replaced guy wire on pole 03-02-36A. 08:45 Blocked and closed Recloser 03-02-02 --> Success and then released the block. Cause: Broken Guy wire. |  | 1 | 13:27 | Afternoon | Wednesday | 2018 | 11
9976 | 2018-11-14 18:33 | 2018-11-14 18:33 | MINAS POWER PLANT | Fair |  | - | 18:33 Started Up MGT #1 and the On line to the system at 18:50 to restore the load. |  | 1 | 18:33 | Afternoon | Wednesday | 2018 | 11
9977 | 2018-11-14 20:36 | 2018-11-14 20:36 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 0 | 20:36 CKBS fdr #5 load dropped 253A (298-45A). Not checked yet. |  | 1 | 20:36 | Night | Wednesday | 2018 | 11
9978 | 2018-11-14 20:36 | 2018-11-15 17:01 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked and found RCL 36-CU-29 T/R 1x, ctr: 5 - 56, R/F: 51 @3 Patrolled the line but found nothing Cause : Lightning |  | 1 | 20:36 | Night | Wednesday | 2018 | 11
9979 | 2018-11-15 07:03 | 2018-11-15 07:03 | 13.8KV BANGKO FEEDER #4 | Fair | Animal | - | It was reported b/o fuse at well Bangko #179 D/S Bangko fdr #1. Not checked yet. |  | 1 | 7:03 | Morning | Thursday | 2018 | 11
9980 | 2018-11-15 07:41 | 2018-11-15 07:41 | 13.8KV DURI COMMUNITY FEEDER #2 | Cloudy | Powerline - Jumper | 0 | 07:41 Dr Comy ACB #30 ( feeder #2) T/O. Checked and found broken jumper Lightning Arrester in front of Heavy Duty office. 08:40 Open LBS: 2E-15-I. 08:25 Manually blocked and closed Dr Comy fdr #2 --> Success. Continue repair broken jumper Lightning Arrester. 10:30 Closed LBS: 2E-15-I. Cause: Jumper LA. |  | 1 | 7:41 | Morning | Thursday | 2018 | 11
9981 | 2018-11-15 08:18 | 2018-11-15 08:18 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | 0 | C Duri fdr #1 load dropped 38A (102-68A). Not checked yet. |  | 1 | 8:18 | Morning | Thursday | 2018 | 11
9982 | 2018-11-15 08:18 | 2018-11-18 09:12 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Lightning | 0 | Checked and found RCL 41-AW-62 T/R 1x, ctr: 294 - 295, R/F: None. Patrolled the line and found high trees @1 near pole 39-AV-23. Cause : Lightning |  | 1 | 8:18 | Morning | Thursday | 2018 | 11
9983 | 2018-11-15 11:02 | 2018-11-15 11:02 | 13.8KV 5B FEEDER #2 | Fair | Planned Maintenance | 109 | 11:02 Manually open LBS 5C-01 D/S 5B fdr#2 (Bus Voltage 14.6Kv). Due to replaced fuse cut out at well 5C-38N. 11:40 Manually closed LBS 5C-01. Cause: Plain Maintenance. |  | 1 | 11:02 | Morning | Thursday | 2018 | 11
9984 | 2018-11-15 13:45 | 2018-11-15 13:45 | 13.8KV MINAS FEEDER #4 | Fair | Construction Job | 0 | 13:45 Manually open recloser 7D-121 D/S Minas fdr#4. Due to install jumper production line by PT SGJ near well 7D-86. 17:36 Manually closed recloser 7D-121. Cause: Construction job. |  | 1 | 13:45 | Afternoon | Thursday | 2018 | 11
9985 | 2018-11-15 14:30 | 2018-11-15 14:30 | MINAS POWER PLANT |  |  | - | 14:30 S/U MGT #10 , and then Online the unit at 15:16. Status running test , loading is limited to 10 MW. |  | 1 | 14:30 | Afternoon | Thursday | 2018 | 11
9986 | 2018-11-15 15:34 | 2018-11-15 15:34 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Planned Maintenance | 0 | 15:34 Manually open Recloser: 01-02-34 D/S C Duri fdr #3. Replaced T Tap at 5 Steam Station Area #1. 16:00 Manually closed Recloser: 01-02-34. Cause: Plan Maintenance. |  | 1 | 15:34 | Afternoon | Thursday | 2018 | 11
9987 | 2018-11-15 18:22 | 2018-11-15 18:22 | MINAS POWER PLANT |  |  | - | 18:22 MGT #10 Trip , high vibration 0.78. |  | 1 | 18:22 | Afternoon | Thursday | 2018 | 11
9988 | 2018-11-16 00:58 | 2018-11-16 00:58 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning | 2 | Ketigul 13.8KV VCB fdr #3 T/R 1X. Ketigul fdr #1 load dropped 9A (112-103A). Ketigul fdr #2 load dropped 28A (248-220A). Not checked yet. |  | 1 | 0:58 | Night | Friday | 2018 | 11
9989 | 2018-11-16 00:58 | 2018-11-18 09:14 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning | 2 | Checked and found KTGL fdr #3 T/R 1x, ctr: 206 - 207, R/F: 51N Patrolled the line but found nothing. Cause : Lightning |  | 1 | 0:58 | Night | Friday | 2018 | 11
9990 | 2018-11-16 07:32 | 2018-11-16 07:32 | 13.8KV BANGKO FEEDER #3 | Fair | Animal | 0 | Bangko OCB fdr #3 T/R 1x Bangko fdr #2 load dropped 163A (250-87A). Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 7:32 | Morning | Friday | 2018 | 11
9991 | 2018-11-16 07:32 | 2018-11-16 07:32 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | Bangko fde #4 load dropped 91A (182-91A). Not checked yet. |  | 1 | 7:32 | Morning | Friday | 2018 | 11
9992 | 2018-11-16 07:42 | 2018-11-16 07:42 | 13.8KV CENTRAL DURI FEEDER #6 | Cloudy | Unidentified | 0 | C Duri ACB #23 (feeder #6) T/R 1x R/F: 51 @2 Counter: 484-485. Not patrolled yet. |  | 1 | 7:42 | Morning | Friday | 2018 | 11
9993 | 2018-11-16 23:02 | 2018-11-16 23:02 | 13.8KV BATANG GFPC | Fair | Unidentified | - | Batang GFPC T/R 1x, no load drop at any feeders. Cause: Not Checked Yet |  | 1 | 23:02 | Night | Friday | 2018 | 11
9994 | 2018-11-16 23:02 | 2018-11-21 12:08 | 13.8KV BATANG GFPC | Fair | Unidentified | - | Checked & found BTG GFPC T/R 1x, Ctr: 308-309, R/F: 51N Patrolled the Line but found nothing Cause : Unidentified |  | 1 | 23:02 | Night | Friday | 2018 | 11
9995 | 2018-11-17 10:59 | 2018-11-17 10:59 | 13.8KV 4B FEEDER #2 | Fair | Planned Maintenance | 172 | 10:59 Manually open recloser 5B-93 D/S 4B fdr#2. Manually open recloser 5B-06 D/S 5B fdr#1. Due to repair LBS 5B-128. 15:49 Manually closed recloser 5B-93. 16:09 Manually closed recloser 5B-06. Cause: plain Maintenance. |  | 1 | 10:59 | Morning | Saturday | 2018 | 11
9996 | 2018-11-17 14:43 | 2018-11-17 14:43 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | - | 14:43 It was reported b/o fuse at well Mutiara#1 D/S Bangko fdr#1. Not checked yet. |  | 1 | 14:43 | Afternoon | Saturday | 2018 | 11
9997 | 2018-11-17 15:53 | 2018-11-17 15:53 | MINAS POWER PLANT |  |  | - | 15:53 S/U MGT #10 , and then Online the unit at 16:08. Status running test , loading is limited to 10 MW. |  | 1 | 15:53 | Afternoon | Saturday | 2018 | 11
9998 | 2018-11-17 18:04 | 2018-11-17 18:04 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 18 | Ketigul VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 18:04 | Afternoon | Saturday | 2018 | 11
9999 | 2018-11-17 18:04 | 2018-11-22 07:31 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 18 | Checked & found Ketigul VCB Fdr#1 T/R 1x, Ctr: 207-208. R/F: 51@2 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 18:04 | Afternoon | Saturday | 2018 | 11
10000 | 2018-11-17 20:58 | 2018-11-17 20:58 | 13.8KV RANGAU FEEDER #2 | Heavy Rain | Unidentified | - | Rangau fdr #2 Load Dropped 146A (162-16A) Not Checked Yet |  | 1 | 20:58 | Night | Saturday | 2018 | 11
10001 | 2018-11-17 20:58 | 2018-11-22 07:58 | 13.8KV RANGAU FEEDER #2 | Heavy Rain | Unidentified | - | Checked & found Recl. 23BD01 T/R 1x Ctr:355-356. Patrolled the line & but found nothing. Cause : Unidentified. |  | 1 | 20:58 | Night | Saturday | 2018 | 11
10002 | 2018-11-17 21:10 | 2018-11-17 21:10 | 13.8KV ROKAN FEEDER #2 | Cloudy and Lightning | Post Pin Insulator | - | Rokan fdr #2 T/R 2x cause : Not Checked Yet |  | 1 | 21:10 | Night | Saturday | 2018 | 11
10003 | 2018-11-17 21:10 | 2018-11-22 12:46 | 13.8KV ROKAN FEEDER #2 | Cloudy and Lightning | Post Pin Insulator | - | Checked & found Rokan VCB fdr#2 T/R 3x, Ctr: 1272-1275, R/F: 51 @1 Patrolled the Line, found @1 Pin Post Insulator Flash Over o/p 31 AV 26 Cause : Post Pin Insulator |  | 1 | 21:10 | Night | Saturday | 2018 | 11
10004 | 2018-11-17 22:08 | 2018-11-17 22:08 | 13.8KV BANGKO FEEDER #1 | Rain | Lightning | - | Ground fault alarm at Bangko fdr #1 Bangko fdr #1 drop 85A (174 - 89 A) Cause: Not Checked Yet |  | 1 | 22:08 | Night | Saturday | 2018 | 11
10005 | 2018-11-17 22:08 | 2018-11-17 22:08 | 13.8KV BANGKO FEEDER #4 | Rain | Lightning | - | Ground fault alarm at Bangko fdr #4 Bangko fdr #4 drop 83A (182 - 99 A) Cause: Not Checked Yet |  | 1 | 22:08 | Night | Saturday | 2018 | 11
10006 | 2018-11-18 13:14 | 2018-11-18 13:14 | 13.8KV RANGAU FEEDER #2 | Fair | Transformer Failure | - | It was reported b/o fuse at well JURONG #13 D/S Rangau fdr #2. Not checked yet. |  | 1 | 13:14 | Afternoon | Sunday | 2018 | 11
10007 | 2018-11-18 13:14 | 2018-11-22 12:48 | 13.8KV RANGAU FEEDER #2 | Fair | Transformer Failure | - | Checked & found @1@2 B/O fuse and Transformer failure at well Rangau #13 (Rangau fdr#2) Patrolled the Line, found Recloser 23-BD-01 T/R 1x, Ctr: 35-356, R/F: 51N Cause : Transformer Failure |  | 1 | 13:14 | Afternoon | Sunday | 2018 | 11
10008 | 2018-11-18 13:29 | 2018-11-18 13:29 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Lightning | 69 | 13:29 Minas ACB #1 (feeder #4) T/LO Counter: 91-93 R/F: 51N. Patrolled the line nothing found. 14:40 Blocked and closed Minas ACB #1 (feeder #4) --> Success. Cause: Suspected Lightning. |  | 1 | 13:29 | Afternoon | Sunday | 2018 | 11
10009 | 2018-11-18 20:39 | 2018-11-18 20:39 | 13.8KV 8C FEEDER #6 | Heavy Rain | Lightning | 0 | 8C fdr #6 T/R 1x Cause: Not Checked Yet |  | 1 | 20:39 | Night | Sunday | 2018 | 11
10010 | 2018-11-18 20:39 | 2018-11-22 09:52 | 13.8KV 8C FEEDER #6 | Heavy Rain | Lightning | 0 | Checked & found 8C VCB fdr#6 T/R 1x, Ctr: 598-599, R/F: 51@1 Patrolled the Line, found @1 Broken fuse PT of Recloser o/p 8C-94 Cause : Lightning |  | 1 | 20:39 | Night | Sunday | 2018 | 11
10011 | 2018-11-18 23:38 | 2018-11-18 23:38 | MINAS POWER PLANT | Fair |  | - | MGT #1 Offline and S/D Reason: Exhaust problem |  | 1 | 23:38 | Night | Sunday | 2018 | 11
10012 | 2018-11-19 03:39 | 2018-11-19 03:39 | 13.8KV DARLING VCB FEEDER #7 | Fair | Animal | 0 | Darling fdr #7 T/R 1x Cause: Not Checked Yet |  | 1 | 3:39 | Night | Monday | 2018 | 11
10013 | 2018-11-19 03:39 | 2018-11-23 17:10 | 13.8KV DARLING VCB FEEDER #7 | Fair | Animal | 0 | Checked & found Darling VCB fdr#7, Ctr: 171-172, R/F: 51 @1 Patrolled the Line, but found nothing. Cause : Animal |  | 1 | 3:39 | Night | Monday | 2018 | 11
10014 | 2018-11-19 06:41 | 2018-11-19 06:41 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | ND fdr #9 T/R 2x cause: Not Checked Yet |  | 1 | 6:41 | Morning | Monday | 2018 | 11
10015 | 2018-11-19 06:41 | 2018-11-22 12:43 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | Checked & found, NDuri VCB fdr#9 T/R 3x, Ctr: 74-77, R/F: 51 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 6:41 | Morning | Monday | 2018 | 11
10016 | 2018-11-19 16:48 | 2018-11-19 16:48 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | - | It was reported b/o fuse on pole 04-03-07 D/S C Duri fdr #9. Not checked yet. |  | 1 | 16:48 | Afternoon | Monday | 2018 | 11
10017 | 2018-11-19 16:48 | 2018-11-23 17:29 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | - | Checked & found CD ACB fdr#9 T/R 3x, Ctr: 74-77, R/F: 51 @1@2 patrolled the Line, but found nothing Cause : Unidentified (Fuse) |  | 1 | 16:48 | Afternoon | Monday | 2018 | 11
10018 | 2018-11-21 02:33 | 2018-11-21 02:33 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Emergency | - | 02:33 Manually Open CKBS feeder #1 52 Well 2913 BOPD, 93823 BWPD, 96736 BFPD. 03:58 Manually Open CKBS feeder #6 35 Well 1267 BOPD, 51190 BWPD, 52457 BFPD. 05:47 Manually Open OKBS feeder #2 62 Well 2100 BOPD, 98487 BWPD, 100588 BFPD. 08:34 Manually Open PTH feeder #4 41 Well 3944 BOPD, 78890 BWPD, 82834 BFPD Closed at 11:40. 08:35 Manually Open PTH feeder #6 10 Well 1417 BOPD, 30321 BWPD, 31738 BFPD 09:12 Manually Open PTH feeder #3 52 Well 5587 BOPD, 48522 BWPD, 54109 BFPD 11:33 S/D wells on PTH Feeder #8 10 Well 955 BOPD, 37966 BWPD, 38921 BFPD Cause: Pigging Stuck at PKM 31600. |  | 1 | 2:33 | Night | Wednesday | 2018 | 11
10019 | 2018-11-21 02:33 | 2018-11-22 09:41 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Emergency | - | 09:41 Manually Blocked & Closed OKBS fdr#2, then release the block. 11:16 Manually Opened CKBS Fdr#5,48 Well à 1814 BOPD, 96028 BWPD, 97842 BFPD. |  | 1 | 2:33 | Night | Wednesday | 2018 | 11
10020 | 2018-11-21 08:34 | 2018-11-21 08:34 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Construction Job | - | 08:34 Manually open Petapahan fdr#4. 11:40 Manually closed Petapahan fdr#4. Cause: Maintenance level tank. |  | 1 | 8:34 | Morning | Wednesday | 2018 | 11
10021 | 2018-11-21 08:35 | 2018-11-21 08:35 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Construction Job | - | 08:35 Manually open Petapahan fdr#6. Manually closed Petapahan fdr#6. Cause: Maintenance level tank. |  | 1 | 8:35 | Morning | Wednesday | 2018 | 11
10022 | 2018-11-21 09:12 | 2018-11-21 09:12 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Construction Job | - | 09:12 Manually open Petapahan fdr#3. Manually closed Petapahan fdr#3. Cause: Maintenance level tank, Pinging stuck. |  | 1 | 9:12 | Morning | Wednesday | 2018 | 11
10023 | 2018-11-21 09:23 | 2018-11-21 09:23 | MINAS POWER PLANT |  |  | - | 09:23 MGT#6 Off line then S/D For S/B. |  | 1 | 9:23 | Morning | Wednesday | 2018 | 11
10024 | 2018-11-21 11:02 | 2018-11-21 11:02 | MINAS POWER PLANT |  |  | - | 11:02 MGT#10 Off line then S/D For S/B. |  | 1 | 11:02 | Morning | Wednesday | 2018 | 11
10025 | 2018-11-21 20:48 | 2018-11-21 20:48 | MINAS POWER PLANT |  |  | - | 20:48 Off Line MGT#3 and then S/D the unit for Stand By. |  | 1 | 20:48 | Night | Wednesday | 2018 | 11
10026 | 2018-11-22 15:55 | 2018-11-22 15:55 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | - | C.Duri ACB fdr#15 T/R 1x Ctr:284-285 R/F:51@2. Not patrolled yet. |  | 1 | 15:55 | Afternoon | Thursday | 2018 | 11
10027 | 2018-11-22 15:55 | 2018-11-23 17:08 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Unidentified | - | Checked & found CD ACB fdr#15 T/R 1x, Ctr: 384-385, R/F: 51 @1. Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 15:55 | Afternoon | Thursday | 2018 | 11
10028 | 2018-11-22 17:07 | 2018-11-22 17:07 | 115KV KOTABATAK JUNCTION - LIBO LINE | Rain and Lightning | Equipment Failure | 859 | 17:07 115 KV Line KBJ - Libo GCB # 53 and GCB # 55 T/O Frequency: 60.66 Hz. 17:09 NDC #3 T/O by Blade patch spread > 110 deg F and Blade patch differential. 17:10 Feeder Load dropped Production Loss Pinang feeder #1 12A (101-89A) : 0 SO.Balam feeder#1 92A (138-46A) : 22 Bbls / 1 well. SO.Balam feeder#3 65A (66-1A) : WIP. SO.Balam feeder#4 117A (185-68A) : 66 Bbls / 2 wells. Nella feeder#1 37A (207-170A) : 38 Bbls / 11 wells. Bangko feeder#1 117A (171-54A) : 65 Bbls / 37 wells. Bangko feeder#2 205A (252-47A) : WIP. Bangko feeder#3 147A (224-77A) : WIP. Bangko feeder#4 132A (193-61A) : 51 Bbls / 28 wells. Menggala feeder#1 138A (190-52A) : 0 Sintong feeder#1 47A (99-52A) : 0 Sintong feeder#2 60A (178-118A) : 0 Batang feeder#3 11A (60-49A) : 0 S.Bekasap feeder#1 94A (123-29A) : 23 Bbls / 32 wells. Bekasap feeder#2 11A (184-173A) : 0 Bekasap feeder#3 23A (94-71A) : 0 Bekasap feeder#5 117A (221-104A) : WIP. Bekasap feeder#6 19A (174-155A) : 0. Pematang feeder#1 111A (201-90A) : 51 Bbls / 16 wells. Pematang feeder#2 44A (100-56A) : 0 Rangau feeder#2 150A (157-7A) : 34 Bbls / 17 wells. Petani feeder#1 20A (187-167A) : 0 Ketigul feeder#1 60A (117-57A) : 7 Bbls / 1 well. Ketigul feeder#2 202A (243-41A) : 70 Bbls / 6 wells 8D feeder#1 9A (122-113A) : 45 Bbls / 15 wells. 8D feeder#2 10A (90-80A) : 0 8D feeder#3 8A (99-91A) : Area 2 : 185 Bbls / 69 wells. 8D feeder#8 116A (186-70A) : 0 8D feeder#10 12A (125-113A) : 0 8D feeder#11 27A (127-100A) : 0 8C feeder#1 59A (173-114A) : 0 8C feeder#2 9A (81-72A) : 0 8C feeder#3 45A (191-146A : 0 8C feeder#4 126A (244-118A) : 0 8C feeder#5 33A (198-165A) : 0 8C feeder#6 33A (192-159A) : 0 Minas feeder#1 38A (228-190A) : 28 Bbls / 2 wells. Minas feeder#3 24A (153-129A) : 0 Minas feeder#4 22A (175-153A) : 0 3D feeder#2 57A (166-109A) : 0. 3D feeder#4 31A (216-185A) : 0 3D feeder#5 197A (200-3A) : 0 3D feeder#7 58A (113-55A) : 0 3D feeder#8 77A (150-73A) : 0 4D feeder#1 52A (191-139A) : 0 4D feeder#6 70A (86-16A) : 0. | 1234 | 1 | 17:07 | Afternoon | Thursday | 2018 | 11
10029 | 2018-11-22 17:07 | 2018-11-22 17:07 | 115KV KOTABATAK JUNCTION - LIBO LINE | Rain and Lightning | Equipment Failure | 859 | 4B feeder#1 18A (96-78A) : 1 Bbl / 1 well. 4B feeder#2 12A (35-23A) : 0 4B feeder#4 119A (183-64A) : 0 4B feeder#5 57A (210-153A) : 0 5B feeder#1 22A (71-49A) : 6 Bbls / 1 well. 5B feeder#2 128A(198-70A) : 0 5B feeder#3 49A (110-16A) : 0 5B feeder#6 50A (120-70A) : 0 5B feeder#4 13A (91-78A) : 4 Bbls / 1 well. 5B feeder#8 27A (187-160A) : 0 6D feeder#1 110A (243-133A) : 2 Bbls / 36 wells. 6D feeder#2 50A (196-146A) : 21 Bbls / 1 well. 6D feeder#4 61A (214-153A) : 0 6D feeder#5 61A (350-289A) : 0 6D feeder#6 64A (247-183A) : 14 Bbls / 1 well. 6DN feeder#4 46A (204-158A) : 0 6DN feeder#6 29A (197-168A) : 0 17:11 MGT # 7 Open generator breaker Closed at : 17:15. 17:12 MGT # 8 Open generator breaker Closed at : 17:17. 17:12 CDGT # 5 Open generator breaker Closed at : 17:22. 17:21 Manually open 4D fdr#3 Closed at 18:18 Production loss : 17 Bbls / 10 wells. 17:22 Manually open 4D fdr#2 Closed at 19:18 Production loss : 91 Bbls / 26 wells. 17:28 Manually open 3D fdr#3 Closed at 18:33 Production loss : 44 Bbls / 16 wells. ------------------------------------ + Total : 152 Bbls / 52 wells. Load shedding level #1. 17:39 4D feeder# 5 Trip Closed at 18:36 Production loss : 0 4D feeder# 4 Trip Closed at 18:37 Production loss : 41 Bbls / 17 wells. BOB Zamrud feeder#2 Trip Closed at 20:00 BOB Beruk fdr#2 Trip Closed at 20:00 Load shedding level #2. 18:10 8D feeder# 1 Trip Closed at 18:38 Production loss : 45 Bbls / 18 wells. 8D feeder# 3 Trip Closed at 18:39 Production loss : 0 20:05 Manually closed 115 KV GCB #53 at KBJ --> Success. Manually closed 115 KV GCB #55 at KBJ --> Success. Back to Normal LIBO Substation. 17:10 Libo feeder #1 closed at 20:05 Production loss: 99 Bbls / 9 wells. 17:10 Libo feeder #1 closed at 20:05 Production loss: 337 Bbls / 8 wells. Production loss SLN : 863 Bbls / 168 wells. Production loss SLS : 544 Bbls / 214 wells. ----------------------- + Grand total :1047 Bbls / 382 wells. Cause: Under Investigation. | 1234 | 1 | 17:07 | Afternoon | Thursday | 2018 | 11
10030 | 2018-11-22 18:00 | 2018-11-22 18:00 | MINAS POWER PLANT |  |  | - | 18:00 S/U MGT #10 and then Online the unit at 18:14. |  | 1 | 18:00 | Afternoon | Thursday | 2018 | 11
10031 | 2018-11-22 18:16 | 2018-11-22 18:16 | CENTRAL DURI POWER PLANT |  |  | - | 18:16 S/U CDGT #4 and then Online the unit at 18:37. |  | 1 | 18:16 | Afternoon | Thursday | 2018 | 11
10032 | 2018-11-22 21:37 | 2018-11-22 21:37 | MINAS POWER PLANT |  |  | - | 21:37 S/U MGT #6 and then Online the unit at 22:00. |  | 1 | 21:37 | Night | Thursday | 2018 | 11
10033 | 2018-11-23 05:37 | 2018-11-23 05:37 | CENTRAL DURI POWER PLANT |  |  | - | 05:37 CGT#5 Open Generator Breaker, then S/D the unit for Maintenance. |  | 1 | 5:37 | Morning | Friday | 2018 | 11
10034 | 2018-11-23 06:40 | 2018-11-23 06:40 | NORTH DURI POWER PLANT | Fair | Planned Maintenance | - | 06:40 S/U NDC#3, then on line the unit at 07:13. 07:15 Closed GCB#33. |  | 1 | 6:40 | Morning | Friday | 2018 | 11
10035 | 2018-11-23 08:30 | 2018-11-23 08:30 | MINAS POWER PLANT | Fair | Planned Maintenance | - | 08:30 Off line MGT#6, then S/D the unit for S/B. |  | 1 | 8:30 | Morning | Friday | 2018 | 11
10036 | 2018-11-23 14:04 | 2018-11-23 14:04 | MINAS POWER PLANT | Fair | Planned Maintenance | - | Off line MGT#7, then S/D the unit for Maintenance. |  | 1 | 14:04 | Afternoon | Friday | 2018 | 11
10037 | 2018-11-23 15:06 | 2018-11-23 15:06 | MINAS POWER PLANT | Fair | Planned Maintenance | - | 15:06 S/U MGT#6, the on line the unit at 15:27. |  | 1 | 15:06 | Afternoon | Friday | 2018 | 11
10038 | 2018-11-23 16:32 | 2018-11-23 16:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 80 | 16:32 C.Duri ACB fdr#1 Load dropped 32A (107-72A). 18:00 Checked & found Recl 38AS09 T/SO (Blocked Position) Ctr292-293. Blocked & Closed Recl. 38AS09. Not patrolled yet. |  | 1 | 16:32 | Afternoon | Friday | 2018 | 11
10039 | 2018-11-23 16:32 | 2018-11-27 07:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 80 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 16:32 | Afternoon | Friday | 2018 | 11
10040 | 2018-11-25 08:25 | 2018-11-25 08:25 | CENTRAL DURI POWER PLANT |  |  | - | 08:25 CDGT#5 S/U, then On line at 08:40 to increase power capability |  | 1 | 8:25 | Morning | Sunday | 2018 | 11
10041 | 2018-11-25 09:20 | 2018-11-25 09:20 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 24 | SOBEK fdr#1 Load dropped 55A (127-37A) Checked & found Recloser 34 BI 18 T/R 1x, Ctr: 177-178 Not patrolled yet |  | 1 | 9:20 | Morning | Sunday | 2018 | 11
10042 | 2018-11-25 09:20 | 2018-11-27 07:20 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Unidentified | 24 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 9:20 | Morning | Sunday | 2018 | 11
10043 | 2018-11-25 18:15 | 2018-11-25 18:15 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Unidentified | 28 | 18:15 Nella VCB fdr#2 T/R 1x not checked yet. |  | 1 | 18:15 | Afternoon | Sunday | 2018 | 11
10044 | 2018-11-25 18:15 | 2018-11-28 18:15 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Unidentified | 28 | Checked and found Nella 13.8KV VCB fdr#2 T/R 1X Ctr: 319-320 R/F: None. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 18:15 | Afternoon | Sunday | 2018 | 11
10045 | 2018-11-25 18:15 | 2018-11-25 18:15 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 59 | 18:15 Nella fdr #1 load dropped 100A (210-110A). 19:25 Checked and found Recloser: 22-V-06 T/O Counter: 82-83. (In block position , Rig HPS #08 activity at BKO #95). Block and closed Recloser: 22-V-06 --> OK (still in block position). Cause: Not Patrolled yet. |  | 1 | 18:15 | Afternoon | Sunday | 2018 | 11
10046 | 2018-11-25 18:15 | 2018-11-28 18:15 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 59 | Checked and found Recloser: 22-V-06 T/O Counter: 82-83. Patrolled the line, found @3 broken LA o/p Bangko #16. Cause : Lightning. |  | 1 | 18:15 | Afternoon | Sunday | 2018 | 11
10047 | 2018-11-25 18:15 | 2018-11-25 18:15 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 32 | Bangko Fdr#1 Load dropped 67A (156-89) not checked yet |  | 1 | 18:15 | Afternoon | Sunday | 2018 | 11
10048 | 2018-11-25 18:15 | 2018-11-28 15:13 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 32 | Checked & found Recl. 23W12 T/R 1x, Ctr: 313-314, R/F: None Patrolled the Line, found @1 broken Dead end insulator o/p Bangko #01 Cause : Lightning |  | 1 | 18:15 | Afternoon | Sunday | 2018 | 11
10049 | 2018-11-26 10:00 | 2018-11-26 10:00 | 13.8KV 3D FEEDER #8 | Fair | Construction Job | - | 10:00 Manually Opened LBS 3D-41 (3D fdr#8). Tie in over flow Tank#1 at GS#5. 16:00 Closed LBS 3D-41. Cause: Plan Maintenance. |  | 1 | 10:00 | Morning | Monday | 2018 | 11
10050 | 2018-11-26 11:45 | 2018-11-26 11:45 | CENTRAL DURI SWITCH YARD | Fair | Under investigation | 0 | 11:45 C Duri 13.8/115KV TX-4 T/O. R/F: 86HR, 86T (No Load shedding) C Duri 13.8 KV ACB #44 T/O C Duri 115 KV GCB #65 T/O C Duri 115 KV GCB #63 Fail to trip, by Breaker Failure, then Causing to Trip 115KV Bus-4 C Duri 115 KV Bus-4 (GCB#10, GCB#21,GCB#41) T/O, CDGT #4 Generator running independent (Islander) 12:35 Man. Closed 13.8KV Tie Brk Bus 3-4 ACB#39, to avoid fail Power supply to CD Fdr#9 12:50 Checked & found 115KV GCB #63 Zero Pressure to Close the Breaker. C Duri 115 KV GCB #65 T/O, R/F:86T,86HR. C Duri 115 KV GCB #10 T/O, then closed at 16:32. C Duri 115 KV GCB #21 T/O, then closed at 16:33. C Duri 115 KV GCB #41 T/O, then closed at 16:34. 14:22 Racked Out 13.8KV ACB#44 15:00 Open Isolation Switch 115KV GCB#63 & #65, to trouble shoot TX#4. 16:00 Closed isolation Switch 115KV GCB#65. 16:30 Closed 115Kv GCB#65 (Tx-4 Energized). 16:56 Man. Closed 13.8KV ACB #44 , to Energized TX-4 16:56 Man. Opened 13.8KV Tie Brk Bus 3-4 ACB#39 Cause : Under investigate |  | 1 | 11:45 | Morning | Monday | 2018 | 11
10051 | 2018-11-26 15:40 | 2018-11-26 15:40 | MINAS POWER PLANT |  |  | - | 15:40 S/U MGT#7, then on line the unit at 16:00. |  | 1 | 15:40 | Afternoon | Monday | 2018 | 11
10052 | 2018-11-26 16:07 | 2018-11-26 16:07 | MINAS POWER PLANT |  |  | - | Off line MGT#10, then S/D the unit for S/B. |  | 1 | 16:07 | Afternoon | Monday | 2018 | 11
10053 | 2018-11-26 18:50 | 2018-11-26 18:50 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 24 | 18:50 Pematang 44KV line to Rangau GCB #2 T/R 1x Rangau Substation no power as a times. Rangau OCB feeder #1 Prod Loss : 4 Bbls / 3 wells. Rangau OCB feeder #2 Prod Loss : 44 Bbls / 17 wells. Pematang feeder #1 Load dropped 141A (202-59A) Prod loss : 0. Pematang feeder #2 Load dropped 6A (99-93A) Prod loss : 0. Petani feeder #1 load dropped 24A (192-168A) Prod loss : 0. ------------------------------------------- + Total Prod loss : 48 Bbls / 20 wells. Not checked yet. |  | 1 | 18:50 | Afternoon | Monday | 2018 | 11
10054 | 2018-11-26 18:50 | 2018-11-28 17:16 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 24 | Checked & found Pematang 44KV OCB#2 T/R 1x, Ctr: 48884-48885, R/F: 50 Patrolled the Line, found Broken Dead end o/p RGU#49 Cause : Lightning |  | 1 | 18:50 | Afternoon | Monday | 2018 | 11
10055 | 2018-11-26 19:27 | 2018-03-11 09:59 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Unidentified | 22 | Checked & found Recloser 45-RB-01 T/R 1x, 512-513 Patrolled the Line, but found noting Cause : Unidentified |  | 1 | 19:27 | Night | Monday | 2018 | 11
10056 | 2018-11-26 19:27 | 2018-11-26 19:27 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Unidentified | 22 | 19:27 Pungut feeder #2 Load dropped 16A (60-44A). 19:31 Pungut feeder #2 Load dropped 44A (60-16A). Pungut GS Prod loss : 0. Libo GS Prod loss : 0. Not checked yet. |  | 1 | 19:27 | Night | Monday | 2018 | 11
10057 | 2018-11-26 19:31 | 2018-11-26 19:31 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Pin Insulator | 68 | 19:27 Pungut fdr #1 Load dropped 37A (72-35A). 19:31 Pungut OCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 19:31 | Night | Monday | 2018 | 11
10058 | 2018-11-26 19:31 | 2018-11-27 00:10 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Pin Insulator | 68 | 00:10 It was reported No power at well Pungut #1 , 37 , 28 , 39. 01:25 Checked and found Pungut OCB feeder #1 T/R 1x R/F : 50 @1,2,3 Counter: 410-411. 02:09 Checked and found Recloser : 45-BP-09 T/LO Counter: 135-140. Blocked and closed Recloser : 45-BP-09 --> Failed. Patrolled the line found nothing. 03:40 Blocked and closed Recloser : 45-BP-09 --> but Failed again. Will be continued this morning. 08:00 Patrolled the line & found @1 Broken Pin Insulator o/p 44BP-02. Replaced @1 Broken Pin Insulator o/p 44BP-02. 09:30 Blocked & closed Recl. 45BP-09, then release the block. Cause: Pin Insulator. |  | 1 | 19:31 | Night | Monday | 2018 | 11
10059 | 2018-11-27 00:30 | 2018-11-27 00:30 | 4.16KV MINAS IND FEEDER | Rain and Lightning | Lightning | - | 00:30 4160 V Minas Industrial feeder T/O Counter: 683-684. 00:48 Blocked and closed Minas Industrial feeder --> Success and then release the block. Cause: Not Patrolled yet. |  | 1 | 0:30 | Night | Tuesday | 2018 | 11
10060 | 2018-11-27 00:30 | 2018-11-30 00:30 | 4.16KV MINAS IND FEEDER | Rain and Lightning | Lightning | - | Checked and found 4160 V Minas Industrial feeder T/O Ctr: 683-684 R/F: None. Patrolled the line, but found nothing. Cause : Lightning. |  | 1 | 0:30 | Night | Tuesday | 2018 | 11
10061 | 2018-11-27 07:38 | 2018-11-27 07:38 | 13.8KV SINTONG FEEDER #1 | Fair | Lightning | 0 | Sintong fdr#1 Load dropped 52A (104-52A). Not checked yet. |  | 1 | 7:38 | Morning | Tuesday | 2018 | 11
10062 | 2018-11-27 07:38 | 2018-11-30 07:38 | 13.8KV SINTONG FEEDER #1 | Fair | Lightning | 0 | Checked and found Recl. :26-AE-22 T/R 1X R/F: 51N. Patrolled the line and found @1 Broken LA TP : Kerang #06. Cause : Lightning. |  | 1 | 7:38 | Morning | Tuesday | 2018 | 11
10063 | 2018-11-27 08:36 | 2018-11-27 08:36 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified | 18 | C.Duri ACB fdr#1 T/R 1x Ctr:234-235 R/F:51N Not patrolled yet. |  | 1 | 8:36 | Morning | Tuesday | 2018 | 11
10064 | 2018-11-27 08:36 | 2018-11-30 08:36 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified | 18 | Checked and found C.Duri 13.8KV ACB fdr#1 T/R 1x Ctr:234-235 R/F:51N. Patrolled the line, but found nothing. Cause : Unidentified. |  | 1 | 8:36 | Morning | Tuesday | 2018 | 11
10065 | 2018-11-28 14:19 | 2018-11-28 14:19 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 154 | 14:19 C. Duri fdr #1 load dropped 46A (102-56A). It was reported no Power at Puncak GS. 14:40 Checked and found Recl. :28-as-09 T/O (In blocked). Blocked and closed the Recl., but failed. 17:15 Manually Open Recl. :39-AV-36, Closed By Pass Recloser 28-AS-09. Not patrolled yet. |  | 1 | 14:19 | Afternoon | Wednesday | 2018 | 11
10066 | 2018-11-28 14:19 | 2018-06-12 17:11 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 154 | Checked and found, 5441-R.39AV36 T/R Counter : 262 - 263 Relay Flag : NONE Patrolled the line & found @1 Broken Fuse on pole Puncak #32 Cause : Lightning |  | 1 | 14:19 | Afternoon | Wednesday | 2018 | 11
10067 | 2018-11-28 16:45 | 2018-11-28 16:45 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified | 14 | Rokan 13.8KV VCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 16:45 | Afternoon | Wednesday | 2018 | 11
10068 | 2018-11-28 16:45 | 2018-04-12 07:41 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified | 14 | Checked and found Rokan fdr #2 T/R 1x, ctr: 1275 - 1276, R/F: 51P @1 Patrolled and found broken pin insulator phase 1 on pole NN - Near Kopar #07 Cause : Unidentified |  | 1 | 16:45 | Afternoon | Wednesday | 2018 | 11
10069 | 2018-11-28 17:38 | 2018-11-28 17:38 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Pin Insulator | 255 | 17:38 Ketigul 13.8KV VCB fdr #2 T/LO. Ketigul fdr #3 load dropped 7A (7-0A). Not checked yet. |  | 1 | 17:38 | Afternoon | Wednesday | 2018 | 11
10070 | 2018-11-28 17:38 | 2018-01-12 14:12 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Pin Insulator | 255 | Checked & found KTG VCB fdr#2 T/LO, Ctr: 303-307, R/F: 51 @1 Patrolled the Line, found @1 Broken Pin Insulator o/p 29-AL-14 Cause : Pin Insulator |  | 1 | 17:38 | Afternoon | Wednesday | 2018 | 11
10071 | 2018-11-29 11:37 | 2018-11-29 11:37 | NORTH DURI POWER PLANT | Rain and Lightning | Under investigation | 369 | 11:37 NDC CT #3 Tripped Off. Frequency system dropped to 59.70Hzs. Followed by Load Shedding Level -3. 8C feeder #1 T/O, and closed at 13:10. 8D feeder #1 T/O, and closed at 12:39 ----->WIP. 8D feeder #10 T/O, and closed at 12:27 ----->WIP. 3D feeder #5 T/O, and closed at 13:04. 4D feeder #5 T/O, and closed at 13:10. 3D feeder #2 T/O, and closed at 13:04. 4D feeder #5 T/O, and closed at 12:08. 3D feeder #3 T/O, and closed at 13:02. 3D feeder #6 T/O, and closed at 12:06. 4D feeder #2 T/O, and closed at 13:06. 4D feeder #3 T/O, and closed at 13:07. 4D feeder #6 T/O, and closed at 12:19. 4B feeder #1 T/O, and closed at 13:47. 4B feeder #4 T/O, and closed at 12:08 ----->WIP. 4B feeder #5 T/O, and closed at 13:45. 4B feeder #6 T/O, and closed at 13:52. 5B feeder #1 T/O, and closed at 13:48. 5B feeder #4 T/O, and closed at 13:49. 5B feeder #5 T/O, and closed at 13:49. Beruk feeder #1 T/O, and closed at 13:09. Beruk feeder #2 T/O, and closed at 13:09. Zamrud feeder #1 T/O, and closed at 13:09. Zamrud feeder #2 T/O, and closed at 13:09. Zamrud feeder #4 T/O, and closed at 13:09. Pusaka feeder #1 T/O, and closed at 13:15. Pusaka feeder #2 T/O, and closed at 13:16. Suram feeder #1 T/O, and closed at 13:12. 12:18 Started Up NDC CT #3 and On Line to the system at 12:57. 13:01 Closed 230KV GCB #33. Cause: Under Investigation. Prod loss GS#1 : 151 bbls, 38 wells. GS#2 : 121 bbls, 24 wells. GS#3 : 55 bbls, 24 wells. GS#4 : 72 bbls, 53 wells. GS#5 : 319 bbls, 78 wells. GS#6 : 308 bbls, 76 wells. Total Prod loss : 1026 bbls, 275 wells. | 1234 | 1 | 11:37 | Morning | Thursday | 2018 | 11
10072 | 2018-11-29 11:55 | 2018-11-29 11:55 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Pin Insulator | 106 | 11:55 Pematang OCB fdr #2 T/O (In blocked due to RIG activity). 12:01 Blocked and closed Pematang fdr #2, OK. Not checked yet. |  | 1 | 11:55 | Morning | Thursday | 2018 | 11
10073 | 2018-11-29 11:55 | 2018-06-12 17:14 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Pin Insulator | 106 | Checked & found PMT OCB fdr#2 T/O, Ctr: 498-499, R/F: 51 @3 Patrolled the line, found @3 Broken Pin insulator o/p 34-BC-52 Cause : Pin Insulator |  | 1 | 11:55 | Morning | Thursday | 2018 | 11
10074 | 2018-11-29 11:55 | 2018-11-29 11:55 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Normal Condition | 0 | Pematang fdr #1 load dropped 143A (199-56A). Not checked yet. |  | 1 | 11:55 | Morning | Thursday | 2018 | 11
10075 | 2018-11-29 11:55 | 2018-06-12 17:14 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Normal Condition | 0 | Checked and found, PMTSB-13.8OCB2 T/O Counter : 498 - 499 Relay Flag : 51 Patrolled the line, found Phase 3 Pin insolator broken on pole 34 BC 52 Cause : Pin Insulator |  | 1 | 11:55 | Morning | Thursday | 2018 | 11
10076 | 2018-11-29 12:24 | 2018-03-11 08:09 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 97 | Checked & found Sintong OCB fdr#2 T/R 1x, Ctr: 482-483, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 12:24 | Afternoon | Thursday | 2018 | 11
10077 | 2018-11-29 12:24 | 2018-11-29 12:24 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 97 | Sintong 13.8KV VCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 12:24 | Afternoon | Thursday | 2018 | 11
10078 | 2018-11-29 12:24 | 2018-11-29 12:24 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 38 | Sintong fdr #1 load dropped 76A (101-25A). Not checked yet. |  | 1 | 12:24 | Afternoon | Thursday | 2018 | 11
10079 | 2018-11-29 12:24 | 2018-11-30 12:24 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 38 | Checked and found Recl. :25-AD-26 T/R 1X Ctr: 126-127 R/F: 51N. Patrolled the line and found Broken fuse Cap. Bank o/p: 24-AC-03. Cause : Lightning. |  | 1 | 12:24 | Afternoon | Thursday | 2018 | 11
10080 | 2018-11-29 13:04 | 2018-11-29 13:04 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 0 | 13:04 Manualy Open Recl. 23-BW-02. Replaced Pin Insulator o/p #23-BW-22, #23-BW-24. o/p #21-BW-08, #21-BW-09. 15:12 Closed Recl. 23-BW-02. Cause: Plan maintenance. |  | 1 | 13:04 | Afternoon | Thursday | 2018 | 11
10081 | 2018-11-29 17:58 | 2018-11-29 17:58 | 44KV PEMATANG MAIN - PETANI LINE | Rain and Lightning | Dead End Insulator | 108 | 44Kv Line Pematang Main-Petani GCB#1 T/R 2x Ctr:4019-4921 R/F:51@1@2@3, 51N. (Freq. 60.16 Hz). Pematang fdr#1 Load dropped 115A (138-23A). Pematang fdr#2 Load dropped 59A (61-2A). Rangau fdr#1 Load dropped 29A (4617A). Rangau fdr#2 Load dropped 82A (83-1A). Petani fdr#1 Load dropped 165A (173-8A). Petani fdr#2 Load dropped 133A (138-5A). Nella fdr#1 Load dropped 30A 9205-175A). Bangko fdr#1 Load dropped 18A (166-148A). Bangko fdr#4 Load dropped 15A (189-174). Sintong fdr#2 Load dropped 30A (183-153A). Not checked yet. Prod. Loss. Rangau GS : 29 bbls, 21wells. Pematang GS : 132 bbls 37wells. Petani GS : 109 bbls 55 wells. Total prod loss : 280 bbls, 113 wells. |  | 1 | 17:58 | Afternoon | Thursday | 2018 | 11
10082 | 2018-11-29 17:58 | 2018-03-12 09:14 | 44KV PEMATANG MAIN - PETANI LINE | Rain and Lightning | Dead End Insulator | 108 | CChecked and found Pematang Main-Petani 44KV GCB#1 T/R 2x Ctr:4019-4921 R/F:51@1@2@3, 51N. Patrolled the line and found @1, @3 broken Dead End Insulator at PTN # 15. Cause : Dead End Insulator. |  | 1 | 17:58 | Afternoon | Thursday | 2018 | 11
10083 | 2018-11-29 19:37 | 2018-11-29 19:37 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Unidentified | 0 | N.Duri VCB fdr#2 T/R 2x. Not checked yet. |  | 1 | 19:37 | Night | Thursday | 2018 | 11
10084 | 2018-11-29 19:37 | 2018-01-12 16:32 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found NDuri VCB fdr#2 T/R 2x, Ctr: 278-279, R/F: 51 Patrolled the Line, but found Nothing Cause : Unidentified |  | 1 | 19:37 | Night | Thursday | 2018 | 11
10085 | 2018-11-29 20:29 | 2018-11-29 20:29 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Powerline - Conductor | 0 | 20:39 Batang OCB fdr #2 T/R 2x. 22:06 Batang VCB fdr#2 T/LO. Batang GFPC T/R. |  | 1 | 20:29 | Night | Thursday | 2018 | 11
10086 | 2018-11-29 20:29 | 2018-11-30 07:51 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Powerline - Conductor | 0 | 00:57 Checked and found Batang 13.8KV VCB fdr#2 T/LO Ctr: 176-182 R/F: 51 @1, @2, @3. Patrolled the line and found broken Conductor o/p: 34-AD-02. Open isolation switch Batang VCB fdr #2. 02:30 Cut Jumper On Main Power Line O/P: 34-AD-02. Closed isolation switch Batang VCB fdr #2. 02:35 Blocked and closed Batang VCB fdr #2, OK then released the block. Cause : Conductor (Broken). |  | 1 | 20:29 | Night | Thursday | 2018 | 11
10087 | 2018-11-29 21:15 | 2018-11-29 21:15 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Unidentified | 18 | Ketigul VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 21:15 | Night | Thursday | 2018 | 11
10088 | 2018-11-29 21:15 | 2018-01-12 15:14 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Unidentified | 18 | Checked & found KTG VCB fdr#1 T/R 1x, Ctr: 208-209, R/F: 51 @3 Patrolled the Line, found @3 Flash Over Dead End Insulator o/p Tilan #27 Cause : Unidentified |  | 1 | 21:15 | Night | Thursday | 2018 | 11
10089 | 2018-11-29 22:06 | 2018-11-29 22:06 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Lightning | 25 | 22:06 Batang VCB fdr#2 T/LO Batang GFPC T/R 23:00 it was reported Broken Conductor o/p 34-AD-02, Near well RBS#22 DEC 30-2018 00:57 Checked & found Batang VCB fdr#2 T/LO, Ctr: 176-182, R/F: 51@1, 51N Opened Isolation switch of BTG VCB fdr#2 to Isolate the broken conductor. 02:30 Cut jumper on Main line pole 34AD02. Closed Isolation Switch Batang VCB fdr#2. 02:35 Blocked & closed Batang VCB fdr#2, then release the block. Cause: Broken Conductor. |  | 1 | 22:06 | Night | Thursday | 2018 | 11
10090 | 2018-11-30 08:15 | 2018-11-30 08:15 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 448 | 08:15 N. Duri fdr#2 load droppet 15A (213-198A). 09:50 It was reported no power on road 13-G4 & 65. 10:55 Checked and found Recloser :13G4.1.08 T/O. Blocked and closed the Recloser. but tripped again. 11:11 Patrolled the line,but found Nothing Open LBS 13-G5.1-37. 11:22 Blocked and closed Recloser 13-G4.1-08-OK then released the block. 17:00 Continued to patrolled the line, but found Nothing. 17:37 Closed LBS 13-G5.1-37. Cause: Unidentified. |  | 1 | 8:15 | Morning | Friday | 2018 | 11
10091 | 2018-11-30 15:33 | 2018-11-30 15:33 | 13.8KV BATANG FEEDER #2 | Fair | Planned Maintenance | 0 | 15:33 Manually open Batang fdr#2. Repaired broken conductor o/p 34-AD-03. 16:15 Block & closed Batang fdr#2. Cause: Pain maintenance. |  | 1 | 15:33 | Afternoon | Friday | 2018 | 11
10092 | 2018-01-12 06:05 | 2018-01-12 06:05 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Animal | 18 | Ketigul VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 6:05 | Morning | Friday | 2018 | 1
10093 | 2018-01-12 06:05 | 2018-03-12 06:05 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Animal | 18 | Checked and found Ketigul 13.8KV VCB fdr#2 T/R 1x crt: 307-308 R/F: 51 @2. Patrolled the line and found dead monkey o/p: 29-AM-34. Cause : Animal. |  | 1 | 6:05 | Morning | Friday | 2018 | 1
10094 | 2018-01-12 15:18 | 2018-01-12 15:18 | 44KV PEMATANG MAIN - RANGAU LINE | Lightning | Dead End Insulator | 25 | Pematang main--Rangau 44KV line OCB#2 T/R. Not checked yet. |  | 1 | 15:18 | Afternoon | Friday | 2018 | 1
10095 | 2018-01-12 15:18 | 2018-04-12 07:31 | 44KV PEMATANG MAIN - RANGAU LINE | Lightning | Dead End Insulator | 25 | Checked and found 44 kV OCB #2 PMT Main T/R 1x, ctr: 48885-50006 (counter problem), R/F: 51 Patrolled the lines and found broken dead end insulator o/p RGU-56 Cause : Dead End Insulator |  | 1 | 15:18 | Afternoon | Friday | 2018 | 1
10096 | 2018-01-12 16:15 | 2018-01-12 16:15 | 13.8KV 4B FEEDER #4 | Rain and Lightning | Lightning | 44 | 4B fdr#4 T/R 1x. Not checked yet. |  | 1 | 16:15 | Afternoon | Friday | 2018 | 1
10097 | 2018-01-12 16:15 | 2018-04-12 19:15 | 13.8KV 4B FEEDER #4 | Rain and Lightning | Lightning | 44 | Checked & found 4B OCB fdr#4 T/R 2x Ctr:241-243 R/F:50N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 16:15 | Afternoon | Friday | 2018 | 1
10098 | 2018-01-12 16:15 | 2018-01-12 16:15 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 0 | 4B fdr#5 T/R 1x. Not checked yet. |  | 1 | 16:15 | Afternoon | Friday | 2018 | 1
10099 | 2018-01-12 16:15 | 2018-04-12 19:15 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found 4B OCB fdr#5 T/R 2x R/F:50N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 16:15 | Afternoon | Friday | 2018 | 1
10100 | 2018-01-12 19:20 | 2018-01-12 19:20 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 87 | Sintong VCB fdr#2 T/R 2x. Sintong GFPC T/R 2x. Bangko fdr#4 Load dropped 74A (186-112A). Not checked yet. |  | 1 | 19:20 | Night | Friday | 2018 | 1
10101 | 2018-01-12 19:20 | 2018-03-12 17:53 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | 87 | Checked & found Sintong OCB fdr#2 T/R 1x, Ctr: 484-485, R/F: 51TN Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 19:20 | Night | Friday | 2018 | 1
10102 | 2018-02-12 01:50 | 2018-02-12 01:50 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | It was reported B/O fuse @2@3 at Well Sintong #30 and @1 at Sintong #47 (Sintong fdr#2) Not checked yet |  | 1 | 1:50 | Night | Monday | 2018 | 2
10103 | 2018-02-12 01:50 | 2018-03-12 17:55 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | Checked and found, STGSB-13.8OCB2 None Counter : 484 - 485 Relay Flag : 51N Patrolled the line & found none Cause : Lightning |  | 1 | 1:50 | Night | Monday | 2018 | 2
10104 | 2018-02-12 10:47 | 2018-02-12 10:47 | 13.8KV 4D FEEDER #5 | Fair | Planned Maintenance | 0 | 10:47 Manual Open RCL 4D-51A Purpose: repair critical hotspot at HLC on pole 4E-20 11:28 Blocked and close RCL 4D-51A, ok then release the blocked. cause: planned maintenance |  | 1 | 10:47 | Morning | Monday | 2018 | 2
10105 | 2018-02-12 16:49 | 2018-02-12 16:49 | 4.16KV MINAS IND FEEDER | Rain and Lightning | Lightning | 39 | 16:49 Minas feeder #2 load drop 24 A (125 - 100 A) Checked and found 4.16kV ACB Minas Industrial T/LO, ctr: 684 - 685, R/F : 50N 17:15 Blocked and close 4.16 kV ACB Minas Industrial, Success then release the block. cause: Not Patrolled Yet |  | 1 | 16:49 | Afternoon | Monday | 2018 | 2
10106 | 2018-02-12 16:49 | 2018-04-12 17:59 | 4.16KV MINAS IND FEEDER | Rain and Lightning | Lightning | 39 | Patrolled the line & found @1@2@3 Broken Dead End Insulator o/p IIS3. Cause : Lightning. |  | 1 | 16:49 | Afternoon | Monday | 2018 | 2
10107 | 2018-02-12 16:55 | 2018-02-12 16:55 | 13.8KV 8C FEEDER #3 | Heavy Rain | Lightning | 46 | 16:55 8C feeder #3 load drop 139 A (194 - 55 A) cause : not checked yet |  | 1 | 16:55 | Afternoon | Monday | 2018 | 2
10108 | 2018-02-12 16:55 | 2018-05-12 09:11 | 13.8KV 8C FEEDER #3 | Heavy Rain | Lightning | 46 | Checked and found, 5442-R.8D18A T/R Counter : 179 - 180 Relay Flag : NONE Patrolled the line & found Phase 1, 2, Broken Broken Dead end on pole 8D-16 Cause : Lightning |  | 1 | 16:55 | Afternoon | Monday | 2018 | 2
10109 | 2018-02-12 16:56 | 2018-02-12 16:56 | 13.8KV MINAS FEEDER #6 | Heavy Rain | Lightning | 12 | Minas fdr#6 Load dropped 110A (164-54A). Not checked yet. |  | 1 | 16:56 | Afternoon | Monday | 2018 | 2
10110 | 2018-02-12 16:56 | 2018-04-12 19:56 | 13.8KV MINAS FEEDER #6 | Heavy Rain | Lightning | 12 | Checked & found Recl. 6E-23A T/R 1x Ctr:537-538. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 16:56 | Afternoon | Monday | 2018 | 2
10111 | 2018-02-12 18:27 | 2018-02-12 18:27 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 46 | Petani 13.8KV OCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 18:27 | Afternoon | Monday | 2018 | 2
10112 | 2018-02-12 18:27 | 2018-06-12 17:15 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Lightning | 46 | Checked and found OCB PTN fdr #2 T/R 1x, ctr: 259-260, R/F: 50P Patrolled the lines and found Broken fuse at Petani #124 Cause : Lightning |  | 1 | 18:27 | Afternoon | Monday | 2018 | 2
10113 | 2018-02-12 18:27 | 2018-02-12 18:27 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Normal Condition | 0 | Petani OCB fdr #1 dropped 117 (175-58A.) Not checked yet. |  | 1 | 18:27 | Afternoon | Monday | 2018 | 2
10114 | 2018-02-12 18:27 | 2018-06-12 17:18 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Normal Condition | 0 | Checked and found recloser 33-AY-47 is in normal condition, ctr: 168 Cause : Normal Condition |  | 1 | 18:27 | Afternoon | Monday | 2018 | 2
10115 | 2018-02-12 18:34 | 2018-02-12 18:34 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Circuit Breaker | 877 | 18:34 Pematang 13.8KV OCV fdr #2 T/O. 19:58 Checked & found Pematang OCB fdr#2 T/LO Ctr:499-503 R/F:51@1@2. Patrolled the line & found @1 Broken Pin Insulator O/P 34BD52. @2 Broken Pin Insulator toward Pematang #36. 23:40 Open Isolation Switch Pematang fdr#2, then closed at 23:40. Replaced @1 Broken Pin Insulator O/P 34BD52. @2 Broken Pin Insulator toward Pematang #36. 23:40 Blocked & closed Pematang fdr#2, but failed. Open Isolation Switch Pematang fdr#2, then closed at 23:40. Function test Pematang OCB fdr#2,but failed (OCB failure). 24:00 Closed LBS 34BC42 (Pematang fdr#2 transfer to Pematang fdr#1). Cause: Breaker failure. | 1234 | 1 | 18:34 | Afternoon | Monday | 2018 | 2
10116 | 2018-02-12 18:34 | 2018-02-12 18:34 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Normal Condition | 0 | Pematang fdr #1 dropped 84 (151-67A.) Not checked yet. |  | 1 | 18:34 | Afternoon | Monday | 2018 | 2
10117 | 2018-02-12 18:34 | 2018-06-12 17:21 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Normal Condition | 0 | Checked and found RCL 35-BC-14 is in Normal Condition, ctr: 168 Cause : Normal Condition |  | 1 | 18:34 | Afternoon | Monday | 2018 | 2
10118 | 2018-02-12 18:34 | 2018-02-12 18:34 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Unidentified | 0 | Rangau fdr #2 dropped 150 (164-14A.) Not checked yet. |  | 1 | 18:34 | Afternoon | Monday | 2018 | 2
10119 | 2018-02-12 18:34 | 2018-04-12 07:36 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found RCL 23-BD-01 T/R 4x, ctr: 456 - 460, R/F: None Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 18:34 | Afternoon | Monday | 2018 | 2
10120 | 2018-03-12 09:20 | 2018-03-12 09:20 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified | 0 | ND fdr #8 T/R 1x cause: not checked yet |  | 1 | 9:20 | Morning | Monday | 2018 | 3
10121 | 2018-03-12 09:20 | 2018-06-12 12:46 | 13.8KV NORTH DURI FEEDER #8 | Fair | Unidentified | 0 | Checked and found, NDRSB-13.8VCB8 T/R Counter : 91 - 92 Relay Flag : 51N Patrolled the line & found Nothing Cause : Unidentified |  | 1 | 9:20 | Morning | Monday | 2018 | 3
10122 | 2018-03-12 09:45 | 2018-03-12 09:45 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Lightning | 0 | 09:45 CD ACB fdr #3 T/O (on block position) 09:54 Checked and found ACB fdr #3 T/O, ctr: 209 - 210, R/F: 50P @3, 51G 10:17 Block and close ACB fdr #3, success. cause: not patrolled yet |  | 1 | 9:45 | Morning | Monday | 2018 | 3
10123 | 2018-03-12 09:45 | 2018-06-12 17:24 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Lightning | 0 | Checked and found CD fdr #3 T/O (on block Position), ctr: 209-210, R/F: 51N Patrolled the lines and found broken fuse phase @3 o/p 03-4-08 Cause : Lightning |  | 1 | 9:45 | Morning | Monday | 2018 | 3
10124 | 2018-03-12 11:21 | 2018-03-12 11:21 | 13.8KV 6D FEEDER #3 | Fair | Planned Maintenance | 16 | 11:21 Manually Opened Recl. 6D-03 (6D fdr#3). Replaced @1 Broken Dead End Insulator o/p 6D-06. (S/D 10 wells for the job). 12:15 Blocked & closed Recl. 6D-03, then release the block. Cause: Plan Maintenance. |  | 1 | 11:21 | Morning | Monday | 2018 | 3
10125 | 2018-04-12 16:15 | 2018-04-12 16:15 | CENTRAL DURI POWER PLANT |  |  | - | CGT #1 Started Up at 16:15 and On line to the system at 16:40 to restore load. (CGT #3 will be S/D for HRSG PSV certification). |  | 1 | 16:15 | Afternoon | Thursday | 2018 | 4
10126 | 2018-04-12 17:05 | 2018-04-12 17:05 | CENTRAL DURI POWER PLANT |  |  | - | CGT #3 Off line and then S/D at 17:05 waiting for HRSG PSV Re Certification. |  | 1 | 17:05 | Afternoon | Thursday | 2018 | 4
10127 | 2018-04-12 23:59 | 2018-04-12 23:59 | CPI POWER SYSTEM |  |  | - | CPI Power system has Normal condition |  | 1 | 23:59 | Night | Thursday | 2018 | 4
10128 | 2018-05-12 01:39 | 2018-05-12 01:39 | 13.8KV BEKASAP FEEDER #6 | Lightning | Others | 35 | Bekasap 13.8KV ACB#6 T/R 1x. Not checked yet. |  | 1 | 1:39 | Night | Saturday | 2018 | 5
10129 | 2018-05-12 01:39 | 2018-07-12 10:23 | 13.8KV BEKASAP FEEDER #6 | Lightning | Others | 35 | Checked and found VCB BKS fdr #6 T/R 1X, ctr: 371-372, R/F: 51P Patrolled the lines and found kite at conductor phase @1 and @3 near Bekasap #160 Cause : Others |  | 1 | 1:39 | Night | Saturday | 2018 | 5
10130 | 2018-05-12 16:35 | 2018-05-12 16:35 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | - | C Duri feeder#1 load dropped 43A (104-61A). |  | 1 | 16:35 | Afternoon | Saturday | 2018 | 5
10131 | 2018-05-12 16:35 | 2018-07-12 10:25 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | - | Checked and found RCl 41-AW-62 T/R 1X, ctr: 371 - 372, R/F: 51P Patrolled the lines but found nothing. Cause : Lightning |  | 1 | 16:35 | Afternoon | Saturday | 2018 | 5
10132 | 2018-05-12 17:18 | 2018-05-12 17:18 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 138 | Bekasap Main feeder #2 load dropped 114A (184-70A). Bekasap GFPC Tx #C T/R 1x. Not checked yet. |  | 1 | 17:18 | Afternoon | Saturday | 2018 | 5
10133 | 2018-05-12 17:18 | 2018-07-12 10:31 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Lightning | 138 | Checked and found RCL 37-BD-12 T/R 1X, ctr: 1026 - 1027, R/F: None Patrolled the lines but found nothing. Cause : Lightning |  | 1 | 17:18 | Afternoon | Saturday | 2018 | 5
10134 | 2018-06-12 01:37 | 2018-06-12 01:37 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Lightning | 0 | 13.8 kV VCB Duri Community fdr #3 T/R 1x Cause: Not Checked Yet |  | 1 | 1:37 | Night | Tuesday | 2018 | 6
10135 | 2018-06-12 01:37 | 2018-07-12 10:33 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found VCB DCM fdr #3 T/R 1X, ctr: 85 - 86, R/F" 51N Patrolled the lines and found broken pin insulator phase @2 o/p SN-03B Cause : Lightning |  | 1 | 1:37 | Night | Tuesday | 2018 | 6
10136 | 2018-06-12 01:42 | 2018-06-12 01:42 | 13.8KV DARLING VCB FEEDER #3 | Rain and Lightning | Lightning | 0 | 13.8 kV VCB Darling fdr #3 T/R 1x Cause: Not Checked Yet |  | 1 | 1:42 | Night | Tuesday | 2018 | 6
10137 | 2018-06-12 01:42 | 2018-07-12 10:35 | 13.8KV DARLING VCB FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found VCB DRL fdr #3 T/R 1X, ctr: 249-250, R/F: 50P Patrolled the lines but found nothing Cause : Lightning |  | 1 | 1:42 | Night | Tuesday | 2018 | 6
10138 | 2018-06-12 13:56 | 2018-06-12 13:56 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Others | 65 | CKBS feeder #5 load dropped 217A (287-70A). Not checked yet. |  | 1 | 13:56 | Afternoon | Tuesday | 2018 | 6
10139 | 2018-06-12 13:56 | 2018-07-12 07:58 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Others | 65 | Checked and found, 5443-R.36CU29 T/R Counter : 56 - 59 Relay Flag : 2 Patrolled the line found Nothing Cause : Others |  | 1 | 13:56 | Afternoon | Tuesday | 2018 | 6
10140 | 2018-06-12 19:14 | 2018-06-12 19:14 | 13.8KV KETIGUL FEEDER#3 | Cloudy | Lightning | 12 | VCB Ketigul fdr #3 T/R 1x Cause: Not Checked Yet |  | 1 | 19:14 | Night | Tuesday | 2018 | 6
10141 | 2018-06-12 19:14 | 2018-08-12 08:25 | 13.8KV KETIGUL FEEDER#3 | Cloudy | Lightning | 12 | Checked And Found VCB KTGL Feeder 3 T/R 1x , Counter: 207 - 208 Relay Flag: 51N Patrolled The Line And Found Flash over Pin @2 On Pole 31 AS 01 Cause : Lightning |  | 1 | 19:14 | Night | Tuesday | 2018 | 6
10142 | 2018-06-12 19:33 | / | CENTRAL DURI POWER PLANT |  |  | - | - |  | 1 | 19:33 | Night | Tuesday | 2018 | 6
10143 | 2018-06-12 21:30 | 2018-06-12 21:30 | CENTRAL DURI POWER PLANT |  |  | - | CDGT-4 Offline and Shut Down for repair evaporator tube leak. |  | 1 | 21:30 | Night | Tuesday | 2018 | 6
10144 | 2018-08-12 09:26 | 2018-08-12 09:26 | 13.8KV NELLA FEEDER #1 | Fair | Planned Maintenance | 33 | 10:05 Opened Hot Line Clamp on pole 22-W-14 D/S Recloser: 22-V-01 (Nella fdr #1). Due to replace 19 Pcs Pin Insulator (5 poles).. 2 wells were OFF during this job. 11:35 Closed Hot Line Clamp on pole 22-W-14. Cause: Plan Maintenance. |  | 1 | 9:26 | Morning | Sunday | 2018 | 8
10145 | 2018-08-12 12:46 | 2018-08-12 12:46 | 115KV KOTABATAK JUNCTION - LIBO LINE | Fair | Powerline - Conductor | 2264 | 12:46 KBJ 115 KV GCB #53 T/O ( 115 KV Line KBJ-LIBO) KBJ 115 KV GCB #55 T/O No Power at LIBO Substation. 13:40 Manually open Libo OCB feeder #1. Manually open Libo OCB feeder #2. 14:15 Checked and found: KBJ 115 KV GCB #53 T/O R/F: ALPS 67NT Counter: 239-241. KBJ 115 KV GCB #55 T/O Counter: 323-325. 14:49 Manually closed KBJ 115 KV GCB #53 --> but failed. Manually closed KBJ 115 KV GCB #55 (Select selector switch SC to DL) --> but failed. Disable ALPS. 15:16 Manually closed KBJ 115 KV GCB #53 --> Success. 15:17 KBJ 115 KV GCB #53 T/O again. R/F: D 60 : 67N Inst , 67N Time , 21G Zone 1 (distance 1.3 Km from KBJ). Continue patrolled the line found broken conductor between pole KW 09 - KW 10. Due to acacia trees fall down power line. 18:30 Open line switch of 115 KV KBJ - LIBO. Close grounding switch of 115 KV KBJ - LIBO. Repair conductor. | 0 | 1 | 12:46 | Afternoon | Sunday | 2018 | 8
10146 | 2018-08-12 12:46 | 2018-09-12 07:28 | 115KV KOTABATAK JUNCTION - LIBO LINE | Fair | Powerline - Conductor | 2264 | 07:28 Open grounding switch of 115 KV KBJ - LIBO. 07:38 Close Line switch of 115 KV KBJ - LIBO. 07:40 Manually closed Libo OCB feeder #2 --> Success. 07:41 Manually closed Libo OCB feeder #1 --> Success. Libo Substation back to normal. Cause: Conductor. | 0 | 1 | 12:46 | Afternoon | Sunday | 2018 | 8
10147 | 2018-08-12 15:50 | 2018-08-12 15:50 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Broken Fuse Cut Out | 0 | C Duri ACB #21 (feeder #4) T/R 1x R/F: 51N Counter: 515-516. Not patrolled yet. |  | 1 | 15:50 | Afternoon | Sunday | 2018 | 8
10148 | 2018-08-12 15:50 | 2018-12-12 18:22 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Broken Fuse Cut Out | 0 | Checked & Found CD ACB Fdr 4 T/R 1x, Ctr: 515-516, R/F: 51 Patrolled The Line, Found b/o Fuse for 150 KVATX o/p 09 R8 09 Cause : Broken Fuse Cut Out |  | 1 | 15:50 | Afternoon | Sunday | 2018 | 8
10149 | 2018-09-12 06:51 | 2018-09-12 06:51 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | VCB CD fdr #16 T/R 2x, ctr: 329 - 331, R/F: 50P @1, @2 Cause: Not Checked Yet |  | 1 | 6:51 | Morning | Wednesday | 2018 | 9
10150 | 2018-09-12 06:51 | 2018-12-12 18:50 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked And Found VCB CDRSG Feeder 16 T/R 2x , Counter: 330 - 331 Relay Flag: 51 Patrolled The Line And Found nothing Cause : Unidentified |  | 1 | 6:51 | Morning | Wednesday | 2018 | 9
10151 | 2018-09-12 13:56 | 2018-09-12 13:56 | 13.8KV BANGKO FEEDER #3 | Fair | Planned Maintenance | 0 | 13:56 Opened LBS: 22-Z-03 D/S Bangko feeder #3. For repairing hot spot on pole 22-Z-11. 14:16 Closed LBS: 22-Z-03 . Cause: Plan Maintenance. |  | 1 | 13:56 | Afternoon | Wednesday | 2018 | 9
10152 | 2018-09-12 15:46 | 2018-09-12 15:46 | 13.8KV SINTONG FEEDER #1 | Cloudy | Unidentified | 65 | Sintong VCB fdr#1 T/R 1x. Sintong fdr#2 load dropped 7A (186-179A). Not checked yet. |  | 1 | 15:46 | Afternoon | Wednesday | 2018 | 9
10153 | 2018-10-12 06:45 | 2018-10-12 06:45 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 20 | 06:45 6D fdr #1 T/R 1X 6D fdr #2 Load Drop 11 A (204 - 193 A) Not Checked Yet |  | 1 | 6:45 | Morning | Friday | 2018 | 10
10154 | 2018-10-12 06:45 | 2018-12-12 18:21 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 20 | Checked And Found VCB 6D Feeder 1 T/R 1x , Counter: 334 - 335 Relay Flag: 50 Patrolled The Line And Found @2 Broken dead end On Pole 5B-56 , 5B-52 Cause : Lightning |  | 1 | 6:45 | Morning | Friday | 2018 | 10
10155 | 2018-10-12 14:29 | 2018-10-12 14:29 | 115KV BANGKO - NELLA LINE | Rain and Lightning | Lightning | 257 | 14:29 Bangko 115 KV OCB#24 (115 KV Line Bangko - Nella) T/R 1x Frequency: 60:33 Hz. Pinang , S Balam , Nella Substation black out , breaker still on close position. So Balam Substation: 1. So Balam VCB feeder #1 Production loss: 86 Bbls / 95 wells. 2. So Balam VCB feeder #3 Production loss: 3 Bbls / 2 wells. 3. So Balam VCB feeder #4 Production loss:139 Bbls /113 wells. Nella Substation. 1. Nella VCB feeder #1 Production loss:126 Bbls / 64 wells. 2. Nella VCB feeder #2 Production loss: 38 Bbls / 19 wells. Pinang Substatio. 1. Pinang VCB feeder #1 Production loss: 22 Bbls / 30 wells. ------------------------------------ + Total :414 Bbls /323 wells. Respectively load dropped at any feeder : 1. Bangko feeder #1 load dropped 150A (172-22A). Bangko feeder #2 load dropped 230A (250-20A). Bangko feeder #3 load dropped 138A (222-84A). Bangko feeder #4 load dropped 137A (196-59A). 2. Menggala feeder #1 load dropped 148A (200-52A). 3. Sintong feeder #1 load dropped 33A (100-67A). Sintong feeder #2 load dropped 81A (186-105A). 4. Batang feeder #3 load dropped 7A (64-57A). 5. Ketigul feeder #1 load dropped 60A (113-53A). Ketigul feeder #2 load dropped 55A (245-190A). Ketigul feeder #3 load dropped 13A (26-13A). 6. Petani feeder #1 load dropped 72A (189-117A). Not checked yet. |  | 1 | 14:29 | Afternoon | Friday | 2018 | 10
10156 | 2018-10-12 14:29 | 2018-11-12 14:29 | 115KV BANGKO - NELLA LINE | Rain and Lightning | Lightning | 257 | Checked & found 115 kV OCB #24 Bangko Nella T/R 1x, Ctr: 192-193, R/F: 51N, 51 @1, Ph Dist Z2 latched, Phase A and B, Neutral/Ground patrolled the Line, but found nothing Cause: Unidentified |  | 1 | 14:29 | Afternoon | Friday | 2018 | 10
10157 | 2018-10-12 14:45 | 2018-10-12 14:45 | 13.8KV 5B FEEDER #3 | Fair | Planned Maintenance | 3 | 14:45 Manually opened 5B OCB feeder#3. Due to replace @3 broken dead end insulator on pole 4C-62. 15:32 Manually closed 5B OCB feeder#3 --> OK , and then release the block. Cause: Plan Maintenance. |  | 1 | 14:45 | Afternoon | Friday | 2018 | 10
10158 | 2018-11-12 02:57 | 2018-11-12 02:57 | 13.8KV NORTH DURI FEEDER #8 | Rain | Unidentified | - | ND feeder #8 T/R 1x Not Checked Yet |  | 1 | 2:57 | Night | Monday | 2018 | 11
10159 | 2018-11-12 02:57 | 13/12/2018 10:53 | 13.8KV NORTH DURI FEEDER #8 | Rain | Unidentified | - | Checked & found ND VCB fdr#8 T/R 1x, Ctr: 92-93, R/F: 51 @1@2 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 2:57 | Night | Monday | 2018 | 11
10160 | 2018-11-12 02:58 | 2018-11-12 02:58 | 13.8KV NORTH DURI FEEDER #2 | Rain | Unidentified | - | 02:58 ND feeder #2 drop 172 A (200 - 28 A) ND feeder #3 deop 50A (85 - 35 A) Not Checked Yet |  | 1 | 2:58 | Night | Monday | 2018 | 11
10161 | 2018-11-12 02:58 | 13/12/2018 11:13 | 13.8KV NORTH DURI FEEDER #2 | Rain | Unidentified | - | Checked & found RCL NC04 T/R 1x, Ctr: 56-57, R/F: 51. Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 2:58 | Night | Monday | 2018 | 11
10162 | 2018-11-12 06:33 | 2018-11-12 06:33 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 81 | VCB Ketigul fdr #2 T/R 1x Not Checked Yet |  | 1 | 6:33 | Morning | Monday | 2018 | 11
10163 | 2018-11-12 06:33 | 2018-11-12 06:33 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Normal Condition | - | Ketigul fdr #1 Load Drop 20A (113 - 93 A) Not Checked Yet |  | 1 | 6:33 | Morning | Monday | 2018 | 11
10164 | 2018-11-12 11:09 | 2018-11-12 11:09 | 13.8KV 5B FEEDER #1 | Fair | Planned Maintenance | 0 | 11:09 Manually open Recloser: 5B-06 D/S 5B feeder #1. Due to replace 39 pcs Pin to Post Pin Insulator and dead end insulator on pole 5B-44. 11:51 Manually blocked and closed Recloser: 5B-06 --> Success , and then released the block. Cause: Plan Maintenance. |  | 1 | 11:09 | Morning | Monday | 2018 | 11
10165 | 2018-11-12 14:22 | 2018-11-12 14:22 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 44 | 14:22 Manually open Recloser: 8D-18A D/S 8C feeder #3. Due to replace dead end insulator on pole 8D-16. Manually blocked and closed Recloser: 8D-18A --> Success , and then released the block. Cause: Plan Maintenance. |  | 1 | 14:22 | Afternoon | Monday | 2018 | 11
10166 | 2018-11-12 15:03 | 2018-11-12 15:03 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 21 | 15:03 Manually open Recloser: 37-BG-48 D/S So Bekasap feeder #1. Due to bypassed Recloser 37-BG-48 (unit failure) 15:08 Manually blocked and closed Recloser 37-BG-48 --> Success , and then released the block. Cause: Plan Maintenance. |  | 1 | 15:03 | Afternoon | Monday | 2018 | 11
10167 | 2018-12-12 10:20 | 2018-12-12 10:20 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Unidentified | 278 | 10:20 CKB 13.8Kv VCB Feeder#1 T/O 11:40 Checked & found CKB VCB feeder#1, Ctr: 239 -240, R/F: Display blank. Patrolled the line, but found nothing. Blocked & Closed CKB VCB feeder#1, then released the block. Cause: Unidentified |  | 1 | 10:20 | Morning | Wednesday | 2018 | 12
10168 | 2018-12-12 10:23 | 2018-12-12 10:23 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 308 | CKBS feeder #5 T/R 1x Not checked yet. |  | 1 | 10:23 | Morning | Wednesday | 2018 | 12
10169 | 2018-12-12 10:23 | 15/12/2018 17:00 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 308 | Checked and found CKB VCB fdr#5 T/R, Ctr: 139-140, R/F: 51 Patrolled the line, found Recloser 36 CU 29 T/R 1x, Ctr: 59-60 R/F: none Also patrolled the line under the recloser, but found nothing. Cause: Unidentified |  | 1 | 10:23 | Morning | Wednesday | 2018 | 12
10170 | 2018-12-13 06:27 | 2018-12-13 06:27 | 13.8KV ROKAN FEEDER #2 | Drizzle | Pin Insulator | 9 | Rangau VCB fdr @ T/R 1x. Rangau fdr #4 load dropped 26A (37-11A) --> WTP. Not checked yet. |  | 1 | 6:27 | Morning | Thursday | 2018 | 12
10171 | 2018-12-13 06:27 | 2018-12-18 07:12 | 13.8KV ROKAN FEEDER #2 | Drizzle | Pin Insulator | 9 | Checked & found Rokan VCB fdr#2 T/R 1x. Ctr: 1277-1278, R/F: 51N Patrolled the Line, found @2,3 broken Pin Insulator o/p 31 AV 03 Cause : Pin Insulator |  | 1 | 6:27 | Morning | Thursday | 2018 | 12
10172 | 2018-12-13 13:10 | 2018-12-13 13:10 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 37 | 13:10 Manually Opened LBS 5B-56 (6D fdr#1) to Replaced broken Deadend Insulator O/P 5B-57 Load dropped 82A (239-157A) 15:39 Manually Closed the LBS after finished the Jobs Cause: Planned Maintenance |  | 1 | 13:10 | Afternoon | Thursday | 2018 | 12
10173 | 2018-12-14 06:33 | 2018-12-14 06:33 | KOTABATAK SUBSTATION | Heavy Rain | Animal | 450 | 06:33 OKB OCB feeder #2 T/R 1x. Checked & found OKB 115KV Circuit Switcher for TX#1 T/O, R/F: 51G, OIL, Temperature and condition Visually Normal. Also No Power to OKB substation OKB VCB fdr#2 T/SO, Ctr: 1338-1340, R/F: 51 Patrolled the Line, fond Dead Monkey o/p 38-CX-03, and Recl. 38-CW-08 fail to T/O. Opened LBS 38-CW-23, to dismantled Dead monkeys 09:25 Manually Closed OKB Circuit switcher, Energized the TX#1 09:30 Manually Closed OKB VCB fdr#2 10:59 Manually Opened Recl.38-CW-08, for trouble shooting 11:49 Manually Closed back Recl. 39-CW-08 Cause: Animal (monkey) | 12345 | 1 | 6:33 | Morning | Friday | 2018 | 12
10174 | 2018-12-14 09:11 | 2018-12-14 09:11 | DARLING SUBSTATION | Fair | Animal | 21 | 09:11 Darling 115 kv GCB#2 T/O. Darling 115 kv GCB#4 T/O. Darling Tx-1 also Trip, no power to Darling Substation. Checked and found GCB#2 ctr: 82 - 83. GCB#4 ctr: 89 - 90. Tx-1 R/f : 51. All so found that monkey at bussing Darling fdr#1. Manually open Darling fdr # 1, #2, #3, #4. Dismantle the monkey at bussing Darling VCB fdr #1. 10:21 Manually closed GCB #2, and GCB #4 to energize Darling Tx-1. 10:25 Closed VCB fdr#2, and VCB fdr#4,( VCB fdr#1 and VCB fdr#2 still open. Cause : animal ( Monkey ). |  | 1 | 9:11 | Morning | Friday | 2018 | 12
10175 | 2018-12-14 09:34 | 2018-12-14 09:34 | MINAS POWER PLANT |  |  | - | 09:34 S/U MGT#10 and then O/L at 09:57. For preparation NDC#3 will be offline wash. |  | 1 | 9:34 | Morning | Friday | 2018 | 12
10176 | 2018-12-14 09:40 | 2018-12-14 09:40 | 13.8KV SINTONG FEEDER #2 | Fair | Construction Job | 0 | 09:40 Sintong fdr #2 Load dropped 36A (190-154A)--->WIp tripped. Bangko fdr #4 Load dropped 80A (195-115A))--->WIp tripped. Manually Open Sintong fdr #2, and closed at 13:29. 13:29 Checked and found VR at Sintong fdr #2, Normal. Cause: Under investigation. | 12345 | 1 | 9:40 | Morning | Friday | 2018 | 12
10177 | 2018-12-14 18:34 | 2018-12-14 18:34 | MINAS POWER PLANT |  |  | - | 18:34 Offline MGT #10 and then S/D the unit for Standby. |  | 1 | 18:34 | Afternoon | Friday | 2018 | 12
10178 | 2018-12-15 11:58 | 2018-12-15 11:58 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Pin Insulator | 0 | Duri Community ACB #25 fdr#1 T/R 1x. not checked yet |  | 1 | 11:58 | Morning | Saturday | 2018 | 12
10179 | 2018-12-15 11:58 | 2018-12-16 17:00 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Pin Insulator | 0 | Checked & found DCom. ACB fdr#1 T/R, Ctr: 133-134, R/F: 51N Patrolled the Line, @2 Broken Pin insulator o/p 4 DD 58 Cause : Pin Insulator |  | 1 | 11:58 | Morning | Saturday | 2018 | 12
10180 | 2018-12-15 19:29 | 2018-12-15 19:29 | 13.8KV 6D FEEDER #6 | Fair | Lightning | 4 | 6D OCB feeder #6 T/R 1x. 6D feeder #4 load dropped 82A (232-150A). Not checked yet. |  | 1 | 19:29 | Night | Saturday | 2018 | 12
10181 | 2018-12-15 19:29 | 2018-12-20 13:37 | 13.8KV 6D FEEDER #6 | Fair | Lightning | 4 | Checked and found 6D OCB fdr 6 T/R 1x, ctr: 608 - 609, R/F: 51P Patrolled the lines and found broken LA @3 on pole LBS 6D-104 Cause : Lightning |  | 1 | 19:29 | Night | Saturday | 2018 | 12
10182 | 2018-12-15 19:29 | 2018-12-15 19:29 | 13.8KV 6D FEEDER #5 | Fair | Lightning | 77 | 6D feeder #5 load dropped 283A (361-78A). Not checked yet. Production loss : 86 Bbls / 37 wells. GS #3. Production loss : 22 Bbls / 19 wells. GS #4. ------------------------------------------ + Total :108 Bbls / 56 wells. |  | 1 | 19:29 | Night | Saturday | 2018 | 12
10183 | 2018-12-15 19:29 | 2018-12-20 13:32 | 13.8KV 6D FEEDER #5 | Fair | Lightning | 77 | Checked and found RCL 6D-50 on Normal Condition, ctr: none, R/F: none Patrolled the line and found broken LA @1, 2, 3 on pole LBS 6D-09 Cause : Lightning |  | 1 | 19:29 | Night | Saturday | 2018 | 12
10184 | 2018-12-16 06:17 | 2018-12-16 06:17 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | C Duri feeder #1 load dropped 47A (100-53A). Not checked yet. |  | 1 | 6:17 | Morning | Sunday | 2018 | 12
10185 | 2018-12-16 06:17 | 2018-12-20 23:01 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified (Fuse) | 0 | Checked & found, Recloser 39 AV 36 T/R 3x, Ctr: 263-267, R/F: 51 Patrolled the Line, found B/O Fuse ling o/p 37-AP-50 Cause : Unidentified (Fuse) |  | 1 | 6:17 | Morning | Sunday | 2018 | 12
10186 | 2018-12-16 16:50 | 2018-12-16 16:50 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified | 9 | Rokan VCB fdr#2 T/R 1x. Not checked yet |  | 1 | 16:50 | Afternoon | Sunday | 2018 | 12
10187 | 2018-12-16 16:50 | 2018-12-20 10:31 | 13.8KV ROKAN FEEDER #2 | Fair | Unidentified | 9 | Checked & found Rokan VCB fdr#2 T/R 1x, Ctr: 1278-1279, R/F: 51 @2 Patrolled the Line, found @2 broken L.A Cause : Unidentified (L/A) |  | 1 | 16:50 | Afternoon | Sunday | 2018 | 12
10188 | 2018-12-16 19:02 | 2018-12-16 19:02 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 0 | Petani Fdr#1 Load dropped 97A (180-83A) Not checked yet |  | 1 | 19:02 | Night | Sunday | 2018 | 12
10189 | 2018-12-16 19:02 | 2018-12-20 10:47 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 0 | Checked & found Petani OCB fdr#1 Ctr: 168-168, R/F: None Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 19:02 | Night | Sunday | 2018 | 12
10190 | 2018-12-17 05:57 | 2018-12-17 05:57 | 13.8KV LIBO FEEDER #2 | Fair | Unidentified | 39 | Libo VCB feeder #2 T/R 1x. Libo feeder #1 load dropped 14A (66-52A). Not checked yet. |  | 1 | 5:57 | Morning | Monday | 2018 | 12
10191 | 2018-12-17 05:57 | 2018-12-17 17:29 | 13.8KV LIBO FEEDER #2 | Fair | Unidentified | 39 | Checked & found Libo OCB fdr#2 T/R 1x, 482-483, 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 5:57 | Morning | Monday | 2018 | 12
10192 | 2018-12-17 06:43 | 2018-12-17 06:43 | 13.8KV NORTH DURI FEEDER #11 | Rain | Unidentified | 0 | N Duri VCB feeder #11 T/R 1x. Not checked yet. |  | 1 | 6:43 | Morning | Monday | 2018 | 12
10193 | 2018-12-17 06:43 | 2018-12-20 09:33 | 13.8KV NORTH DURI FEEDER #11 | Rain | Unidentified | 0 | Checked & found, NDuri VCBV fdr#11 T/R 1x, Ctr: 179-180, R/F: 51 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 6:43 | Morning | Monday | 2018 | 12
10194 | 2018-12-17 07:11 | 2018-12-17 07:11 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Lightning | 0 | C.Duri ACB fdr#16 T/R 1x, Ctr: 331-332, R/F: 51N,51 @1,2 Not checked yet |  | 1 | 7:11 | Morning | Monday | 2018 | 12
10195 | 2018-12-17 07:11 | 2018-12-20 09:15 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Lightning | 0 | Checked & found CD ACB fdr#16 T/R 1x, Ctr: 331-332, R?F: 51 @3 Patrolled the Line, found @3 broken L.A o/p 39-N4-10 Cause : Lightning |  | 1 | 7:11 | Morning | Monday | 2018 | 12
10196 | 2018-12-17 16:49 | 2018-12-17 16:49 | 13.8KV NORTH DURI FEEDER #1 | Rain | Unidentified (L/A) | 0 | N Duri VCB fdr#1 T/R 1x Not checked yet |  | 1 | 16:49 | Afternoon | Monday | 2018 | 12
10197 | 2018-12-17 16:49 | 2018-12-20 09:39 | 13.8KV NORTH DURI FEEDER #1 | Rain | Unidentified (L/A) | 0 | Checked & found, NDuri VCB fdr#1 T/R 1x, Ctr: 298-300, R/F: 51 @3 Patrolled the Line, found @3 broken L.A o/p 12 E5 08, NF 06, 12 E3 21. Cause : Unidentified (L/A) |  | 1 | 16:49 | Afternoon | Monday | 2018 | 12
10198 | 2018-12-17 16:49 | 2018-12-17 16:49 | 13.8KV NORTH DURI FEEDER #2 | Rain | Unidentified | 0 | NDuri fdr#2 Load dropped 28A (198-172A) Not checked yet |  | 1 | 16:49 | Afternoon | Monday | 2018 | 12
10199 | 2018-12-17 16:49 | 2018-12-21 07:58 | 13.8KV NORTH DURI FEEDER #2 | Rain | Unidentified | 0 | Checked and found RCL MBL2 #2 T/R 1x, ctr: 20 - 21, R/F: None Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 16:49 | Afternoon | Monday | 2018 | 12
10200 | 2018-12-17 18:34 | 2018-12-17 18:34 | 44KV NORTH DURI - DUMAI LINE | Cloudy | Lightning | 0 | 18:34 44KV Line N Duri GCB#1 T/O (Line to Dumai) No power at Dumai Substation. 19:50 Checked and found 44KV Line N Duri GCB#1 T/LO. Ctr: 129-132, R/F: 51@1,@2 , 51G , 51N. Patrolled the line, but found nothing. 21:09 Blocked and closed 44 KV GCB #1 --> Success , and then released the block. Cause: Lightning. |  | 1 | 18:34 | Afternoon | Monday | 2018 | 12
10201 | 2018-12-18 06:54 | 2018-12-18 06:54 | 13.8KV 8C FEEDER #6 | Fair | Tree | 25 | 8C VCB feeder #6 T/R 1x. Not checked yet. |  | 1 | 6:54 | Morning | Tuesday | 2018 | 12
10202 | 2018-12-18 06:54 | 2018-12-23 07:54 | 13.8KV 8C FEEDER #6 | Fair | Tree | 25 | Checked and found 8C VCB fdr #6 T/R 1x, ctr: 598 - 599, R/F 51N Patrolled the lines and found high tress between pole 8C-41 and 8C-42 Cause : Tree |  | 1 | 6:54 | Morning | Tuesday | 2018 | 12
10203 | 2018-12-18 11:10 | 2018-12-18 11:10 | 13.8KV PEMATANG FEEDER #2 | Fair | Under investigation | 321 | 11:10 Checked & found Pematang VCB fdr#2 T/O (Carried Pematang Fdr#1 thought LBS 34.BC.42) Ctr: 516-517, R/F: 51N (In block Position, RIG BMS 05) 11:23 Man. Block & Closed PMT VCB fdr#2, released the block after conform with RIG BMS 05 has been Move Out 12:13 Pematang VCB fdr#2 T/R 1x, Ctr: 517-518, R/F: 51N 12:35 Pematang VCB fdr#2 T/R 1x, Ctr: 518-519, R/F: 51N Cause : under investigate |  | 1 | 11:10 | Morning | Tuesday | 2018 | 12
10204 | 2018-12-18 11:10 | 2018-12-18 11:10 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | It was reported B?O fuse o/p 12-F3-17 (NDuri fdr#11) not checked yet |  | 1 | 11:10 | Morning | Tuesday | 2018 | 12
10205 | 2018-12-18 11:10 | 2018-12-21 08:15 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | Checked and found B/O fuse @1 on pole 12-F3-17 Replaced with same type fuse. Cause : Unidentified |  | 1 | 11:10 | Morning | Tuesday | 2018 | 12
10206 | 2018-12-18 11:30 | 2018-12-18 11:30 | 13.8KV 3D FEEDER #3 | Fair | Planned Maintenance | 14 | 11:30 Manually open 3D fdr#3. Changer broken @1,@2@3 pin insulation O/P 3C-59. 12:02 Manually closed 3D fdr#3. After finished the Jobs Cause: Plain Maintenance. |  | 1 | 11:30 | Morning | Tuesday | 2018 | 12
10207 | 2018-12-18 12:48 | 2018-12-18 12:48 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Normal Condition | 25 | So.Bekasap fdr#1 load dropped 81A (111-30A). Not checked yet. |  | 1 | 12:48 | Afternoon | Tuesday | 2018 | 12
10208 | 2018-12-18 12:48 | 2018-12-24 14:48 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Normal Condition | 25 | Checked and found all protection devices on Normal Condition. Cause : Normal Condition |  | 1 | 12:48 | Afternoon | Tuesday | 2018 | 12
10209 | 2018-12-18 13:07 | 2018-12-18 13:07 | 13.8KV RANGAU FEEDER #2 | Fair | Construction Job | 0 | 13:07 Rangau VCB fdr#2 M/O. due to Pematang GS WIP T/O 14:06 Manually Closed back Rangau VCB fdr#2 After PMT WIP success to Start Cause: Planned Construction |  | 1 | 13:07 | Afternoon | Tuesday | 2018 | 12
10210 | 2018-12-18 13:19 | 2018-12-18 13:19 | 13.8KV PEMATANG FEEDER #2 | Fair | Planned Maintenance | 143 | 13:19 Manually Opened Pematang VCB fdr#2 Due to Pematang WIP T/O Opened LBS PMT 34.BC.42 to separate PMT fdr#1 13:45 Manually Closed Pematang VCB fdr#1, to S/U PMT WIP 14:29 Manually Closed Pematang VCB fdr#2 After success S/U Pematang WIP Cause: Planned Construction |  | 1 | 13:19 | Afternoon | Tuesday | 2018 | 12
10211 | 2018-12-19 09:37 | 2018-12-19 09:37 | 4.16KV EAST RUMBAI FEEDER #1 | Cloudy | Unidentified (Fuse) | 0 | East Rumbai feeder #1 T/R 1x Cause: Not Checket Yet |  | 1 | 9:37 | Morning | Wednesday | 2018 | 12
10212 | 2018-12-19 09:37 | 2018-12-23 07:48 | 4.16KV EAST RUMBAI FEEDER #1 | Cloudy | Unidentified (Fuse) | 0 | Checked and found East Rumbai VCB fdr #1 T/R, ctr: 579 - 580, R/F 51N Patrolled the lines then found b/o fuse o/p 4RD-11 (feed to no resident housing) Cause : Unidentified (Fuse) |  | 1 | 9:37 | Morning | Wednesday | 2018 | 12
10213 | 2018-12-20 11:24 | 2018-12-20 11:24 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | 11:24 SINTONG feeder #2 load drop 108 A (168-60 A) WIP T/O BANGKO feeder #4 load drop 73 A (191-118 A) WIP T/O 18:05 RCL of Cap Bank SINTONG SS T/O SINTONG feeder #2 drop again 71 A (168-97 A) WIP T/O BANGKO feeder #4 drop 81 A (191 - 110 A) WIP T/O BANGKO feeder #1 drop 19 A (168 - 149 A) NELLA feeder #1 drop 14 A (214 - 200 A) Weather : lightning Cause: Not Checked Yet. |  | 1 | 11:24 | Morning | Thursday | 2018 | 12
10214 | 2018-12-20 11:24 | 2018-12-25 08:24 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 0 | Checked and found All protection devices are Normal. Patrolled the lines but found nothing/normal. Cause : Unidentified |  | 1 | 11:24 | Morning | Thursday | 2018 | 12
10215 | 2018-12-20 14:15 | 2018-12-20 14:15 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning | 0 | Rokan 13.8KV VCB#2 T/R 1x. Not cheeked yet. |  | 1 | 14:15 | Afternoon | Thursday | 2018 | 12
10216 | 2018-12-20 14:15 | 2018-12-24 14:50 | 13.8KV ROKAN FEEDER #2 | Fair | Lightning | 0 | Checked and found RKN VCB fdr #2 T/R 1x, ctr: 1279 - 1280, R/F: 51P @1 Patrolled the lines and found flash oven pin insulator on pole 31-AV-26 Cause : Lightning |  | 1 | 14:15 | Afternoon | Thursday | 2018 | 12
10217 | 2018-12-20 18:02 | 2018-12-20 18:02 | 13.8KV SINTONG FEEDER #1 | Lightning | Main breaker | 65 | Sintong 13.8KV VCB fdr #1 T/R 2X. Sintong GFPC in blocked position. Not checked yet. |  | 1 | 18:02 | Afternoon | Thursday | 2018 | 12
10218 | 2018-12-20 18:02 | 2018-12-25 17:17 | 13.8KV SINTONG FEEDER #1 | Lightning | Main breaker | 65 | Checked and found STG VCB fdr #1, ctr: 396 - 398, R/F: 51N Patrolled the line but found nothing Cause : Main breaker |  | 1 | 18:02 | Afternoon | Thursday | 2018 | 12
10219 | 2018-12-21 13:23 | 2018-12-21 13:23 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Powerline - Jumper | 160 | 13:23 6D feeder #1 T/LO 6D feeder #2 load dropped 133 A (184 - 51A) 6D feeder #3 load dropped 98 A (176 - 78 A) 13:56 Checked and found 6D OCB fdr #3 T/LO, ctr: 335 - 339, R/F: 51P @1 15:15 Patrolled the lines and found broken jumper of RCL 5C-42 on @1 and @2 Cut Jumper then bypassed the RCL 5C-42 16:32 Blocked and closed 6D OCB feeder #1, success then release the block. Cause: Jumper |  | 1 | 13:23 | Afternoon | Friday | 2018 | 12
10220 | 2018-12-21 14:16 | 2018-12-21 14:16 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Tree | 12 | 14:16 3D feeder #3 T/R 1x 3D feeder #2 dropped 89 A (160 - 71 A) 3D feeder #4 dropped 79 A (216 - 137 A) 3D feeder #5 dropped 56 A (59 - 3 A) Cause: Not Checked Yet |  | 1 | 14:16 | Afternoon | Friday | 2018 | 12
10221 | 2018-12-21 14:16 | 2018-12-25 14:23 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Tree | 12 | Checked and found 3D OCB fdr #3 T/R 1x, ctr: 449 - 450, R/F: 50P @1, 2, 3 Patrolled the lines and found High Tree touch the power line near loc 4C-24B Cause : Tree |  | 1 | 14:16 | Afternoon | Friday | 2018 | 12
10222 | 2018-12-21 14:49 | 2018-12-21 14:49 | 13.8KV PETAPAHAN FEEDER #2 | Fair | Unidentified | 0 | 14:49 New PTP feeder #2 drop 87 A (87-0 A) GS Pumps New PTP feeder #7 drop 51 A (69-18 A) GS Pumps 15:18 Manual open PTP feeder #4 and PTP feeder #3 for maintain tank level 15:30 Block and close PTP feeder #3 and PTP feeder #4 Cause: GS pumps trip |  | 1 | 14:49 | Afternoon | Friday | 2018 | 12
10223 | 2018-12-22 08:06 | 2018-12-22 08:06 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Recloser - Control Recloser | 214 | 08:06 CKBS feeder #5 load drop 238 A (289 - 51 A) 09:06 Reported No Power around area KB #323 09:39 Checked and found RCL 36-CU-29 T/SO, ctr: 60 (not change), R/F: None Block and Close RCL 36-CU-29, success then release the block Cause: Not Patrolled Yet |  | 1 | 8:06 | Morning | Saturday | 2018 | 12
10224 | 2018-12-22 08:06 | 2018-12-24 07:06 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Recloser - Control Recloser | 214 | Checke3d and found RCL 36-CU-29 T/SO, ctr: 60 (not changed), R/F: None Patrolled the lines but found nothing Cause : Control Recloser |  | 1 | 8:06 | Morning | Saturday | 2018 | 12
10225 | 2018-12-22 12:46 | 2018-12-22 12:46 | 13.8KV NORTH DURI FEEDER #6 | Fair | Unidentified | 0 | 12:46 ND feeder #6 T/R 1x Cause: Not Checked Yet |  | 1 | 12:46 | Afternoon | Saturday | 2018 | 12
10226 | 2018-12-22 12:46 | 2018-12-25 16:01 | 13.8KV NORTH DURI FEEDER #6 | Fair | Unidentified | 0 | Checked and found ND VCB fdr #6 T/R 1x, ctr: 306 - 307, R/F: 51N Patrolled the lines but found nothing. Cause : Unidentified |  | 1 | 12:46 | Afternoon | Saturday | 2018 | 12
10227 | 2018-12-22 19:56 | 2018-12-22 19:56 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Unidentified | 197 | 19:56 CKBS Feeder#5 Load dropped 240A (291-51A) 21:20 Checked & found Recloser.36-CU-29 T/O Ctr.60-61 Blocked & Closed Recloser 36-CU-29 the release the block. (Unplug control recloser 36-CU-29) |  | 1 | 19:56 | Night | Saturday | 2018 | 12
10228 | 2018-12-22 19:56 | 2018-12-24 07:46 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Unidentified | 197 | Checked and found RCL 36-CU-29 T/SO, ctr: 60 - 61, R/F: None. Unplugged the cable control of recloser. Patrolled the lines but found nothing. Cause : Unidentified |  | 1 | 19:56 | Night | Saturday | 2018 | 12
10229 | 2018-12-23 07:45 | 2018-12-23 07:45 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Lightning | 44 | Ketigul VCB feeder #2 T/R 1x Cause: Not Checked Yet |  | 1 | 7:45 | Morning | Sunday | 2018 | 12
10230 | 2018-12-23 07:45 | 2018-12-25 16:27 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Lightning | 44 | Checked and found KTGL VCB fdr #2 T/R 1x, ctr: 310 - 311, R/F: 51N Patrolled the lines and found flash over pin @2 on TOP Pager #45 Cause : Lightning |  | 1 | 7:45 | Morning | Sunday | 2018 | 12
10231 | 2018-12-23 08:43 | 2018-12-23 08:43 | CENTRAL DURI POWER PLANT |  |  | 0 | 08:43 CDGT #4 S/U and then online at 09:00 |  | 1 | 8:43 | Morning | Sunday | 2018 | 12
10232 | 2018-12-23 10:58 | 2018-12-23 10:58 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 14 | 10:58 So Balam feeder #1 dropped 20 A (136 - 116 A) 13:01 Reported no power around location BLM #212 14:11 Checked and found RCL 16-Z-88 T/SO, ctr: 60 (not change), alarm: interrupter malfunction are occured, R/F: None 14:14 Blocked and close the RCL, success. release the block after close. Cause: Not Patrolled Yet |  | 1 | 10:58 | Morning | Sunday | 2018 | 12
10233 | 2018-12-23 10:58 | 2018-12-27 09:09 | 13.8KV S. BALAM FEEDER #1 | Fair | Unidentified | 14 | Patrolled the lines d/s of RCL 16-Z-88 but found nothing Cause Unidentified. |  | 1 | 10:58 | Morning | Sunday | 2018 | 12
10234 | 2018-12-23 11:45 | 2018-12-23 11:45 | CENTRAL DURI POWER PLANT |  |  | 0 | 11:45 CDGT #3 offline and then S/D Preparation for HRSG Certification |  | 1 | 11:45 | Morning | Sunday | 2018 | 12
10235 | 2018-12-23 15:59 | 2018-12-23 15:59 | 4.16KV EAST RUMBAI FEEDER #1 | Fair | Lightning | 0 | East RUMBAI VCB feeder #1 T/R 1x Cause: Not Checked Yet |  | 1 | 15:59 | Afternoon | Sunday | 2018 | 12
10236 | 2018-12-23 15:59 | 2018-12-29 09:10 | 4.16KV EAST RUMBAI FEEDER #1 | Fair | Lightning | 0 | Checked & found East Rumbai 4160V VCB fdr#1 T/R 1x, Ctr: 580-581, R/F: 51N Patrolled the Line, Found @2 broken L.A O/p 4RD-11 Cause : Lightning |  | 1 | 15:59 | Afternoon | Sunday | 2018 | 12
10237 | 2018-12-24 00:06 | 2018-12-24 00:06 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 281 | 00:06 It was reported no power at road 08-L5-35 (C.Duri fdr#1). 06:29 Checked & found Recl 08-L5-35 T/O (Block position) Ctr:949-950. 07:00 Patrolled the line but found nothing. 07:12 Blocked & closed Recl. 08-L5-35. Cause; Unidentified. |  | 1 | 0:06 | Night | Monday | 2018 | 12
10238 | 2018-12-24 00:06 | 2018-12-25 16:47 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 281 | Checked and found RCL 08-L5-35 T/O, ctr: 949 - 950, R/F: None Patrolled the lines and found broken jumper of LA o/p 08-L5-27 @1, @3 Cause : Lightning |  | 1 | 0:06 | Night | Monday | 2018 | 12
10239 | 2018-12-24 06:04 | 2018-12-24 06:04 | 13.8KV LIBO FEEDER #1 | Fair | Animal | 11 | 06:04 Libo fdr#1 T/R 1x. 14:22 Checked and found LIBO VCB fdr #1 T/R 1x, ctr: 582 - 583, R/F: 51N Patrolled the lines and found animal (monkey) touch the line on @1 at LIBO GS Cause : Animal |  | 1 | 6:04 | Morning | Monday | 2018 | 12
10240 | 2018-12-24 06:19 | 2018-12-24 06:19 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 240 | 06:19 Ketigul fdr#2 T/R 1x. Ketigul fdr#1 Load dropped 50A(96-46A). 06:50 Ketigul fdr#2 T/R 1x again. Not checked yet. |  | 1 | 6:19 | Morning | Monday | 2018 | 12
10241 | 2018-12-24 06:19 | 2018-12-25 16:25 | 13.8KV KETIGUL FEEDER#2 | Fair | Lightning | 240 | Checked and found KTGL VCB fdr #2 T/R 2x, ctr: 311- 313, R/F 51N Patrolled the lines and found Flash oven pin insulator @2 at terminal pole Pager #45 Cause : Lightning |  | 1 | 6:19 | Morning | Monday | 2018 | 12
10242 | 2018-12-25 07:31 | 2018-12-25 07:31 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified (L/A) | 0 | CKBS VCB feeder #6 T/R 1x Cause: Not Checked Yet |  | 1 | 7:31 | Morning | Tuesday | 2018 | 12
10243 | 2018-12-25 07:31 | 2018-12-27 07:47 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Unidentified (L/A) | 0 | Checked and found CKBS VCB fdr 6 T/R 1x, ctr: 147 - 148, R/F: 50P Patrolled the lines and found broken LA @1, @2, @3 on pole 35-CU-35 Cause : Unidentified (L/A) |  | 1 | 7:31 | Morning | Tuesday | 2018 | 12
10244 | 2018-12-25 08:12 | 2018-12-25 08:12 | 13.8KV 8D FEEDER #5 | Cloudy | Unidentified | 0 | 8D VCB feeder #5 T/R 1x Cause: Not Checked Yet |  | 1 | 8:12 | Morning | Tuesday | 2018 | 12
10245 | 2018-12-25 08:12 | 2018-12-28 17:07 | 13.8KV 8D FEEDER #5 | Cloudy | Unidentified | 0 | Checked and found 8D OCB fdr #5 T/R 1x, ctr: 566 (not change), R/F: 50N Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 8:12 | Morning | Tuesday | 2018 | 12
10246 | 2018-12-25 09:11 | 2018-12-25 09:11 | 13.8KV 4B FEEDER #1 | Fair | Lightning | 144 | 11:25 4B feeder #1 T/R 1x Not Checked Yet 17:18 It was reported no power at Nusa Field. 17:50 It was reported no Power at Security Post at KBJ. 21:55 Checked & found Recl 4B-101 T/LO Ctr:632-636. Patrolled the line but found nothing. 01:00 Blocked & closed Recl. 4B-101, then release the block. Cause: Unidentified. |  | 1 | 9:11 | Morning | Tuesday | 2018 | 12
10247 | 2018-12-25 09:11 | 2018-12-29 16:09 | 13.8KV 4B FEEDER #1 | Fair | Lightning | 144 | Checked & found 4B OCB fdr#1 T/R 1x, Ctr: 339-340, F/R: 50N Patrolled the Line, but Found nothing Cause : Lightning |  | 1 | 9:11 | Morning | Tuesday | 2018 | 12
10248 | 2018-12-25 20:32 | 2018-12-25 20:32 | 13.8KV 3D FEEDER #7 | Rain and Lightning | Lightning | 0 | 3D fdr#7 T/R 1x. Not checked yet. |  | 1 | 20:32 | Night | Tuesday | 2018 | 12
10249 | 2018-12-25 20:32 | 2018-12-27 17:12 | 13.8KV 3D FEEDER #7 | Rain and Lightning | Lightning | 0 | Checked and found 3D OCB fdr #7 T/R 1x, ctr: 213 - 214, R/F: 50N Patrolled the lines but found nothing Cause : Lightning |  | 1 | 20:32 | Night | Tuesday | 2018 | 12
10250 | 2018-12-25 20:34 | 2018-12-25 20:34 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 22 | 3D fdr#2 T/R 1x. Not checked yet. |  | 1 | 20:34 | Night | Tuesday | 2018 | 12
10251 | 2018-12-25 20:34 | 2018-12-27 17:04 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 22 | Checked and found 3D OCB fdr #2 T/R 1x, ctr: 274 - 275, R/F: 51N Patrolled the lines and found broken pin insulator at @1 and @2 on pole 3E-46 Cause : Lightning |  | 1 | 20:34 | Night | Tuesday | 2018 | 12
10252 | 2018-12-26 08:49 | 2018-12-26 08:49 | 44KV NORTH DURI - DUMAI LINE | Cloudy | Unidentified | 0 | ND 44 kV GCB #1 T/R 1x Cause: Not Checked Yet |  | 1 | 8:49 | Morning | Wednesday | 2018 | 12
10253 | 2018-12-26 08:49 | 2018-12-28 15:48 | 44KV NORTH DURI - DUMAI LINE | Cloudy | Unidentified | 0 | Checked and found 44 kV GCB #1 ND T/R 1x, ctr: 132 - 133, R/F: 51N Patrolled the lines but found nothing. Cause : Unidentified |  | 1 | 8:49 | Morning | Wednesday | 2018 | 12
10254 | 2018-12-26 17:48 | 2018-12-26 17:48 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Lightning | 0 | 17:48 CD ACB feeder #2 (ACB 12) T/R 1x Ctr: 390 - 391, R/F: 51G and 51N Cause: Not Patrolled Yet |  | 1 | 17:48 | Afternoon | Wednesday | 2018 | 12
10255 | 2018-12-26 17:48 | 2018-12-28 15:58 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Lightning | 0 | Patrolled the lines and found broken LA @2 on pole SAA-15 Cause : Lightning |  | 1 | 17:48 | Afternoon | Wednesday | 2018 | 12
10256 | 2018-12-27 03:51 | 2018-12-27 03:51 | 13.8KV BATANG GFPC | Fair | Unidentified | 0 | Batang 13.8KV GFPC T/R 1X. No load dropped. Not checked yet. |  | 1 | 3:51 | Night | Thursday | 2018 | 12
10257 | 2018-12-27 03:51 | 2018-12-30 16:22 | 13.8KV BATANG GFPC | Fair | Unidentified | 0 | Checked and found BTG GFPC T/R 2x, ctr: 914-916, R/F: 50N Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 3:51 | Night | Thursday | 2018 | 12
10258 | 2018-12-27 06:25 | 2018-12-27 06:25 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | C. Duri fdr #1 Load dropped 51A (a105-54A). Not checked yet. |  | 1 | 6:25 | Morning | Thursday | 2018 | 12
10259 | 2018-12-27 06:25 | 2018-12-30 16:26 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | Checked and found RCL 41-AW-62 T/R 1x, ctr: 296-297, R/F: none Patrolled the lines and found broken pin insulator @3 on pole 39-AW-15 Cause : Pin Insulator |  | 1 | 6:25 | Morning | Thursday | 2018 | 12
10260 | 2018-12-28 10:25 | 2018-02-01 13:27 | MINAS POWER PLANT |  |  | 0 | Checked & Found Recloser 34-BI-18 T/R 1x, Ctr: 178-180, R/F: None Patrolled the line, but found nothing Cause : Unidentified |  | 1 | 10:25 | Morning | Friday | 2018 | 12
10261 | 2018-12-28 10:25 | 2018-12-28 10:25 | MINAS POWER PLANT |  |  | 0 | 10:25 MGT #9 S/U and then online at 10:50 for running test. |  | 1 | 10:25 | Morning | Friday | 2018 | 12
10262 | 2018-12-28 18:40 | 2018-12-28 18:40 | 13.8KV LIBO FEEDER #2 | Cloudy and Lightning | Unidentified | 40 | 18:40 LIBO VCB feeder #2 T/R 1x Cause: Not Checked Y |  | 1 | 18:40 | Afternoon | Friday | 2018 | 12
10263 | 2018-12-28 18:40 | 2018-12-31 15:21 | 13.8KV LIBO FEEDER #2 | Cloudy and Lightning | Unidentified | 40 | Checked and found LIBO VCB feeder #2 T/R 1x, ctr: 483-484, R/F: 51N Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 18:40 | Afternoon | Friday | 2018 | 12
10264 | 2018-12-28 19:13 | 2018-12-28 19:13 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Unidentified | 0 | Rangau fdr #2 load dropped 147A (161-14A). Not checked yet. |  | 1 | 19:13 | Night | Friday | 2018 | 12
10265 | 2018-12-28 19:13 | 2019-02-01 13:36 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found Recl 23 BD 01 T/R 1x, Ctr: 360-361, R/F: None Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 19:13 | Night | Friday | 2018 | 12
10266 | 2018-12-28 19:31 | 2018-12-28 19:31 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Unidentified | 0 | S. Bekasap fdr #1 load dropped 82A (109-27A). Not checked yet. |  | 1 | 19:31 | Night | Friday | 2018 | 12
10267 | 2018-12-28 19:31 | 2019-02-01 13:38 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked & found Recloser 34-BI-18 T/R 2x, Ctr: 178-180, R/F: None Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 19:31 | Night | Friday | 2018 | 12
10268 | 2018-12-29 08:45 | 2018-12-29 08:45 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Lightning | 0 | 08:45 Reported no power along road 06-P7-xx, 09:33 Checked and found RCL 06-P7-02 T/O (on block position), ctr: 517 - 518 09:34 Manual close the RCL then release the block. Cause: Not Patrolled Yet |  | 1 | 8:45 | Morning | Saturday | 2018 | 12
10269 | 2018-12-29 08:45 | 2018-12-30 16:33 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Lightning | 0 | Checked and found RCL 06-P7-02 T/O (on block position), ctr: 217-218, R/F : None Patrolled the lines but found nothing Cause : Lightning |  | 1 | 8:45 | Morning | Saturday | 2018 | 12
10270 | 2018-12-29 08:57 | 2018-12-29 08:57 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | DARLING feeder #7 T/R 1x Cause: Not Checked Yet |  | 1 | 8:57 | Morning | Saturday | 2018 | 12
10271 | 2018-12-29 08:57 | 2019-02-01 13:39 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Checked & found Darling VCB fdr#7 T/R 1x, Ctr: 172-173, R/F: 51N Patrolled the Line, but Found nothing Cause : Unidentified |  | 1 | 8:57 | Morning | Saturday | 2018 | 12
10272 | 2018-12-29 09:06 | 2018-02-12 08:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Tree | 61 | Checked & found Ketigul VCB fdr#2 T/R 4x, Ctr: 544-548, R/F 51N Patrolled the Line, Found High Trees and touching @1,@2 the conductor o/p 26- AL-03 Cause : Tree |  | 1 | 9:06 | Morning | Saturday | 2018 | 12
10273 | 2018-12-29 09:06 | 2018-12-29 09:06 | 13.8KV KETIGUL FEEDER#2 | Fair | Tree | 61 | 09:06 KETIGUL feeder #2 T/R 1x KETIGUL feeder #1 load dropped 11A (102 - 91 A) Cause: Not Checked Yet |  | 1 | 9:06 | Morning | Saturday | 2018 | 12
10274 | 2018-12-30 02:27 | 2018-12-30 02:27 | NORTH DURI POWER PLANT | Fair | Under investigation | 451 | 02:27 NDC CT #1 Generator Breaker Tripped Off. Frequency System dropped to: 59:63Hzs. Followed by Load Shedding Level #2. 4D fedder #5 T/O , Closed at 02:45. 4D fedder #4 T/O , Closed at 02:44. 3D fedder #6 T/O , Closed at 02:38. 5B fedder #5 T/O , Closed at 02:46. 4B fedder #4 T/O , Closed at 02:40. 8D fedder #3 T/O , Closed at 02:47. 5B fedder #4 T/O , Closed at 02:46. 8D fedder #1 T/O , Closed at 02:47. 4B fedder #1 T/O , Closed at 02:46. Beruk feeder #2 T/O , Closed at 02:44. Zamrud feeder #1 T/O , Closed at 02:44. Zamrud feeder #2 T/O , Closed at 02:44. Minas feeder #4 load dropped 14A (204-190A) ,---->WIP. 3D feeder #5 load dropped 93A (95-2A) ,---->WIP. 4D feeder #2 load dropped 18A (137-109A). 4D feeder #5 load dropped 8A (102-94). 5B feeder #6 load dropped 118A (176-58A ) ,---->WIP. 5B feeder #8 load drooped 72A (185-113A ,---->WIP. 6D feeder #6load dropped 110A (244-134A) ,---->WIP. 8D feeder #8 load dropped 117A (127-10A ) ,---->WIP. 8D feeder #9 load dropped 105A (116-11A ) ,---->WIP. 8C feeder #3 load dropped 13A (195-182A ). 8C feeder #4 load dropped 42A (238-196A ) ,---->WIP. 8C feeder #5 load dropped 27A (181-154A ) ,---->WIP. 02:47 NDC CT #1 On line to the System. Cause: Under Investigation. 04:06 NDC CT #1 Generator Breaker Tripped Off. Frequency System dropped to: 59:63Hzs. Followed by Load Shedding Level #2. 4D fedder #5 T/O , Closed at 04:17. 4D fedder #4 T/O , Closed at 04:17. 5B fedder #5 T/O , Closed at 04:18. 4B fedder #4 T/O , Closed at 04:14. 8D fedder #3 T/O , Closed at 04:20. 5B fedder #4 T/O , Closed at 04:18. 8D fedder #1 T/O , Closed at 04:19. 4B fedder #1 T/O , Closed at 04:14. Beruk feeder #2 T/O , Closed at 04:11. Zamrud feeder #1 T/O , Closed at 04:11. Zamrud feeder #2 T/O , Closed at 04:11. 04:10 NDC CT #1 On line to the System. Cause: Under Investigation. Prod Loss : GS#1: 31 Bbls, 7 wells. GS#2: 100 Bbls, 24 wells. GS#3: - GS#4: 62 Bbls, 22 wells. GS#5: 128 Bbls, 29 wells. GS#6: 130 Bbls, 29 wells. Total Prod. Loss : 451 Bbls, 111 wells. |  | 1 | 2:27 | Night | Sunday | 2018 | 12
10275 | 2018-12-30 06:42 | 2018-12-30 06:42 | 44KV NORTH DURI - DUMAI LINE | Fair | Tree | 0 | 44KV GCB #1 ND (line to Dumai) T/R 1X. Not checked yet. |  | 1 | 6:42 | Morning | Sunday | 2018 | 12
10276 | 2018-12-30 06:42 | 2019-01-01 17:42 | 44KV NORTH DURI - DUMAI LINE | Fair | Tree | 0 | Checked & found 44KV ND GCB #44 T/R 1x, Ctr: 133-134, R/F: 51 @1 Patrolled the Line, found High Trees touching @1 O/P 55-56 Cause : Tree (High Trees) |  | 1 | 6:42 | Morning | Sunday | 2018 | 12
10277 | 2018-12-30 11:27 | 2018-12-30 11:27 | 13.8KV KETIGUL FEEDER#2 | Fair | Tree | 263 | 11:27 KETIGUL feeder #2 Load Dropped 184 A (229 - 45 A) 13:12 Reported that no power at UBI and SIKALADI field 14:25 Checked and found RCL 29-AL-03 on normal condition 14:38 Checked and found RCL 27-AL-21 T/LO, ctr: 544 - 548, R/F: 51P @1, @2 Patrolled the lines and found fallen tree near shagging pole 26-AO-03 and near location UBI #34 17:50 Closed RCL 27-AL-21 by direct trigger (due to control recloser problem), success. Cause: Tree |  | 1 | 11:27 | Morning | Sunday | 2018 | 12
10278 | 2018-12-30 19:30 | 2018-12-30 19:30 | MINAS POWER PLANT |  |  | 0 | Off line MGT#6, then S/D the unit for S/B. |  | 1 | 19:30 | Night | Sunday | 2018 | 12
10279 | 2018-12-30 20:31 | 2018-02-01 13:46 | 13.8KV 3D TX-1 GFPC | Fair | Unidentified | 0 | Checked & found 3 D TX#1 GFPC T/R 1x, 4195-4196 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 20:31 | Night | Sunday | 2018 | 12
10280 | 2018-12-30 20:31 | 2018-12-30 20:31 | 13.8KV 3D TX-1 GFPC | Fair | Unidentified | 0 | 20:31 3D GFPC TX-1 T/R 1x 3D feeder #4 Load Dropped 57 A (214 - 157 A) Cause: Not Checked Yet |  | 1 | 20:31 | Night | Sunday | 2018 | 12
10281 | 2018-12-31 23:59 | 2018-12-31 23:59 | CPI POWER SYSTEM |  |  | - | Normal System Condition. |  | 1 | 23:59 | Night | Monday | 2018 | 12
10282 | 2019-01-01 23:59 | 2019-01-01 23:59 | CPI POWER SYSTEM |  |  | - | Normal System Condition. |  | 1 | 23:59 | Night | Tuesday | 2019 | 1
10283 | 2019-02-01 06:35 | 2019-02-01 06:35 | 13.8KV NORTH DURI FEEDER #2 | Fair | Recloser - Control Recloser | 0 | 06:35 NDuri Fdr#2 Load dropped 30A (203-174A) 09:00 It was reported No Power at road 10-J8... 11:10 Checked & found Recl. 10-J8-17 T/SO, Ctr: 66-67, R/F: 51G @2 Manually Closed Recloser 10-J8-17. Patrolled the Line, but found nothing Cause: Recloser control (Suspected) |  | 1 | 6:35 | Morning | Friday | 2019 | 2
10284 | 2019-03-01 09:00 | 2019-03-01 09:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Construction Job | 0 | 09:00 Man. opened LBS 27-AL-03 (Ketigul fdr#2, Old Mgl fdr#2) 32 Wells Down at Ubi Field, as Requested Balam FON, for repair Leakage 12" Prod. Line near Ubi #10. Cause : Planned contstruction |  | 1 | 9:00 | Morning | Friday | 2019 | 3
10285 | 2019-03-01 09:28 | 2019-03-01 09:28 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 17 | Ketigul VCB fdr#2 T/R 1x Not checked yet |  | 1 | 9:28 | Morning | Friday | 2019 | 3
10286 | 2019-03-01 11:15 | 2019-03-01 11:15 | 13.8KV 5B FEEDER #8 | Fair | Tree | 0 | 11:15 5B Vcb fdr #8 T/R 2x. 13:00 Checked Ctr :9989-9991 R/f : 50/51 N. Found High Tree near pole M5B 35. Caused : Tree. |  | 1 | 11:15 | Morning | Friday | 2019 | 3
10287 | 2019-03-01 11:49 | 2019-03-01 11:49 | 230KV NORTH DURI SWITCH YARD | Fair | Under investigation | 0 | 11:49 ND 230-115KV TX#5 T/O, 115KV Line ND-CDSWY ND 115KV GCB #3 T/O ND 230KV GCB#41 T/O ND 230KV GCB#43 In Open status 13:00 Checked & found TX #5 R/F: 86T, 87T, 86HR Winding temp 85 C, OIL temp 90 C Breaker at TX panel Q2 trip (Over Load Pump) 15:21 Manually Closed GCB #3 to Energized power supply for station service TX#5 Manually Run test TX cooling Fans & Pumps the results, 1 Unit Cooling Fan Off and 1 Unit Oil Pump Over Load Release & reseted 86HR Bucholl & 86T . 17:00 ND TX #5 Decided for Stand by, continuous troubleshoot Cause : Under investigation |  | 1 | 11:49 | Morning | Friday | 2019 | 3
10288 | 2019-03-01 11:50 | 2019-03-01 11:50 | MINAS POWER PLANT |  |  | - | 11:50 S/U Mgt#4 then online the unit at 12:02. Do to Mgt#5 S/D for repaired Inlet House. |  | 1 | 11:50 | Morning | Friday | 2019 | 3
10289 | 2019-03-01 14:24 | 2019-03-01 14:24 | MINAS POWER PLANT |  |  | - | 14: Mgt#5 Offline and S/D to repaire Inlet House. |  | 1 | 14:24 | Afternoon | Friday | 2019 | 3
10290 | 2019-03-01 19:10 | 2019-03-01 19:10 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Recloser - Control Recloser | 0 | 19:10 6D fdr#5 Load dropped 53A (340-287A). Not checked yet. |  | 1 | 19:10 | Night | Friday | 2019 | 3
10291 | 2019-03-01 19:10 | 2019-04-01 11:08 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Recloser - Control Recloser | 0 | 11:08 Checked & found Recl 5D-10, Ctr: 483-484, R/F: None also Found @1@2 b/o PT Fuse, then Replaced PT Fuse Manually Closed the Recloser Patrolled the Line, but found nothing Cause: Control Recloser |  | 1 | 19:10 | Night | Friday | 2019 | 3
10292 | 2019-03-01 21:11 | 2019-03-01 21:11 | 13.8KV 5B FEEDER #8 | Rain and Lightning | Unidentified | 0 | 21:11 5B OCB fdr#8 T/R 1x. 23:10 5B OCB fdr#8 T/R 2x again. Not checked yet. |  | 1 | 21:11 | Night | Friday | 2019 | 3
10293 | 2019-03-01 21:11 | 2019-06-01 21:48 | 13.8KV 5B FEEDER #8 | Rain and Lightning | Unidentified | 0 | Checked & found 5B OCB fdr#8 T/R, CT: 9989-9991, R/F: 51N Patrolled the Line, but found nothing Cause: Unidentified |  | 1 | 21:11 | Night | Friday | 2019 | 3
10294 | 2019-04-01 06:17 | 2019-04-01 06:17 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 0 | Darling VCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 6:17 | Morning | Monday | 2019 | 4
10295 | 2019-04-01 06:17 | 2019-06-01 08:05 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 0 | Checked and found Darling VCB fdr#2. T/R 1x. Ctr: 251-251. R/F: 51G. Patrolled the line, bat not. Cause : Unidentified. |  | 1 | 6:17 | Morning | Monday | 2019 | 4
10296 | 2019-04-01 07:24 | 2019-04-01 07:24 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Tree | 0 | D.Com Acb #30 fdr #2 T/r 1x. Not checked yet. |  | 1 | 7:24 | Morning | Monday | 2019 | 4
10297 | 2019-04-01 07:24 | 2019-06-01 08:25 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Tree | 0 | Checked and found D.commy fdr#2. T/R 1x. Ctr: 104-105. R/F: 51N. Patrolled the line,found High Trees o/p MR 12. Cause :Tree. |  | 1 | 7:24 | Morning | Monday | 2019 | 4
10298 | 2019-05-01 14:58 | 2019-05-01 14:58 | 13.8KV 5B FEEDER #8 | Fair | Planned Maintenance | - | 14:58 Manually Open 5B VCB fdr#8. to replace broken @1 FCO for 2.5 MVA Tx Gs #4. 15:15 Manually Closed 5B VCB fdr#8 after finished the Jobs. Cause: Planned Maintenance |  | 1 | 14:58 | Afternoon | Wednesday | 2019 | 5
10299 | 2019-05-01 15:44 | 2019-05-01 15:44 | 13.8KV PETAPAHAN FEEDER #8 | Fair | Unidentified | 34 | 15:44 Petapahan VCB#8 T/R 1x. Not checked yet. |  | 1 | 15:44 | Afternoon | Wednesday | 2019 | 5
10300 | 2019-05-01 15:44 | 2019-07-01 09:01 | 13.8KV PETAPAHAN FEEDER #8 | Fair | Unidentified | 34 | Checked & found Petapahan VCB fdr#8 T/R 1x, Ctr: 366-367, R/F: 50N Patrolled the Line, but found nothing Cause: Unidentified |  | 1 | 15:44 | Afternoon | Wednesday | 2019 | 5
10301 | 2019-05-01 17:30 | 2019-05-01 17:30 | MINAS POWER PLANT |  |  | - | MGT #9 T/O, by Alarm Hydraulic Press Low System Frequency 59.83 Hz, No Load Shedding. Will Replaced with MGT #6 |  | 1 | 17:30 | Afternoon | Wednesday | 2019 | 5
10302 | 2019-05-01 19:40 | 2019-05-01 19:40 | MINAS POWER PLANT |  |  | - | 19:40 S/U MGT#6, then on line the unit at 19:57. |  | 1 | 19:40 | Night | Wednesday | 2019 | 5
10303 | 2019-06-01 13:50 | 2019-06-01 13:50 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 56 | 5B 138KV OCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 13:50 | Afternoon | Saturday | 2019 | 6
10304 | 2019-06-01 13:50 | 2019-08-01 12:06 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 56 | Checked & found 5B VCB fdr#3 T/R 1x, Ctr: 397-398, R/F: 51N Patrolled the Line, but found Nothing Cause : Lightning |  | 1 | 13:50 | Afternoon | Saturday | 2019 | 6
10305 | 2019-06-01 13:50 | 2019-06-01 13:50 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Normal Condition | 0 | 5B fdr#1 load dropped 44A (61-17A). Not checked yet. |  | 1 | 13:50 | Afternoon | Saturday | 2019 | 6
10306 | 2019-06-01 13:50 | 2019-06-01 13:50 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Unidentified | 0 | 5B fdr#2 load dropped 181A (197-16A). 5B fdr#6 load dropped 174A (179-5A).WIP Not checked yet. |  | 1 | 13:50 | Afternoon | Saturday | 2019 | 6
10307 | 2019-06-01 13:50 | 14/01/2019 07:35 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found 5B OCB fdr #2 T/R 1x, ctr: 99994 - 99995, R/F: 51N Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 13:50 | Afternoon | Saturday | 2019 | 6
10308 | 2019-07-01 23:59 | 2019-07-01 23:59 | CPI POWER SYSTEM |  |  | - | Normal System Condition. |  | 1 | 23:59 | Night | Monday | 2019 | 7
10309 | 2019-08-01 11:09 | 2019-08-01 11:09 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Powerline - Conductor | 16 | C.Duri fdr#1 load dropped 44A (140-96A). Not checked yet. |  | 1 | 11:09 | Morning | Thursday | 2019 | 8
10310 | 2019-08-01 11:09 | 2019-11-01 08:58 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Powerline - Conductor | 16 | Checked and found RCL 41-AW-62 T/R 1x, ctr: 297-298, R/F: 51P @3 Patrolled the lines and found broken conductor phase 3 near pole 41-AW-12 Cause : Conductor |  | 1 | 11:09 | Morning | Thursday | 2019 | 8
10311 | 2019-08-01 14:10 | 2019-08-01 14:10 | MINAS POWER PLANT |  |  | - | 14:10 S/U Mgt#9 then online the unit at 14:33. |  | 1 | 14:10 | Afternoon | Thursday | 2019 | 8
10312 | 2019-08-01 14:50 | 2019-08-01 14:50 | MINAS POWER PLANT |  |  | - | 14:50 MGT #11 Off Line then S/D for Stand by (Generator Ground) |  | 1 | 14:50 | Afternoon | Thursday | 2019 | 8
10313 | 2019-08-01 15:20 | 2019-08-01 15:20 | DURI RING BUS | Fair | Under investigation | 0 | 15:20 Duri Ring Bus 115KV GCB#26 T/R 1x, Ctr: not change Duri Ring Bus 115KV GCB#28 T/O, Ctr: 199-201 Checked & found Relay L90 & D60 R/F: 67N & 87L also found GCB #28 Spring Dischard. and Battery Voltage 144 VDC , due to Air conditioner too Hot Open the Charger panel door, the Voltage drop to 130VDC Open Both Isolation Switch of OCB #28 to Function test, ok 17:32 Manually Closed DRB 115KV OCB #28 Cause: Under Investigate |  | 1 | 15:20 | Afternoon | Thursday | 2019 | 8
10314 | 2019-08-01 18:00 | 2019-08-01 18:00 | 13.8KV ROKAN FEEDER #2 | Fair | Broken Fuse Cut Out | 7 | Rokan VCB Fdr#2 T/R 1x Not checked Yet |  | 1 | 18:00 | Afternoon | Thursday | 2019 | 8
10315 | 2019-08-01 18:00 | 2019-11-01 09:29 | 13.8KV ROKAN FEEDER #2 | Fair | Broken Fuse Cut Out | 7 | Checked and found VCB RKN fdr #2 T/R 1x, ctr: 1280-1281, R/F: 51P @1, @2 Patrolled the lines and found broken fuse link @1 and @2at 29-AV-40 Cause : Broken Fuse Cut Out |  | 1 | 18:00 | Afternoon | Thursday | 2019 | 8
10316 | 2019-08-01 21:29 | 2019-08-01 21:29 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 4 | 4D fdr#5 T/R 1x. 4D fdr#4 Load dropped 50A (200-150A). Not checked yet. |  | 1 | 21:29 | Night | Thursday | 2019 | 8
10317 | 2019-08-01 21:29 | 2019-12-01 14:26 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 4 | Checked and found 4d OCB fdr #5 T/R 1x, ctr: 337-338, R/F: 50N Patrolled the line but nothing found Cause : Lightning |  | 1 | 21:29 | Night | Thursday | 2019 | 8
10318 | 2019-08-01 21:40 | 2019-08-01 21:40 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 73 | 8D fdr#1 T/R 1x. Not checked yet. |  | 1 | 21:40 | Night | Thursday | 2019 | 8
10319 | 2019-08-01 21:40 | 2019-12-01 14:44 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 73 | Checked and found 8D OCB fdr #1 T/R 1x, ctr: 316-317, R/F: 50N Patrolled the line and found broken pin @2 o/p 8E-136 Cause : Lightning |  | 1 | 21:40 | Night | Thursday | 2019 | 8
10320 | 2019-08-01 21:40 | 2019-11-01 17:05 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found 8D OCB fdr#5 T/R 1x, Ctr: 566-566, R/F: 50N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 21:40 | Night | Thursday | 2019 | 8
10321 | 2019-08-01 21:40 | 2019-08-01 21:40 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 0 | 8D fdr#10 T/R 1x. Not checked yet. |  | 1 | 21:40 | Night | Thursday | 2019 | 8
10322 | 2019-08-01 21:40 | 2019-12-01 15:01 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 0 | Checked and found 8D OCB fdr #10 T/R 1x, ctr: 260-261, R/F: 50N Patrolled the lines and found broken LA o/p 7E-100 Cause : Lightning |  | 1 | 21:40 | Night | Thursday | 2019 | 8
10323 | 2019-08-01 21:40 | 2019-12-01 15:01 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 0 | Checked and found 8D OCB fdr #10 T/R 1x, ctr: 260-261, R/F: 50N Patrolled the lines and found broken LA o/p 7E-100 Cause : Lightning |  | 1 | 21:40 | Night | Thursday | 2019 | 8
10324 | 2019-08-01 21:51 | 2019-08-01 16:54 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 42 | Checked & found Minas fdr#1 T/R 1x, Ctr: 80-81, R/F: 51N Patrolled the Line, but found nothing Cause: Lightning (suspected) |  | 1 | 21:51 | Night | Thursday | 2019 | 8
10325 | 2019-08-01 21:51 | 2019-08-01 21:51 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 42 | Minas fdr#1 T/R 1x CXtr:80-81 R/F:51N. Not patrolled yet. |  | 1 | 21:51 | Night | Thursday | 2019 | 8
10326 | 2019-08-01 21:51 | 2019-08-01 21:51 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Lightning | 0 | 21:51 Minas fdr#2 Load dropped 12A (108-96A). 23:35 Checked & found Recl. 4160V Industrial T/LO Ctr:685-686 R/F:51N. Blocked & closed Recl. 4160V Minas industrial, then release the block. Not patrolled yet. |  | 1 | 21:51 | Night | Thursday | 2019 | 8
10327 | 2019-08-01 21:51 | 16/01/2019 17:17 | 13.8KV MINAS FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked & found Recl. 4160V Industrial T/LO Ctr:685-686 R/F:51N Patrolled the lines and found B/O fuse @1 Cause : Lightning |  | 1 | 21:51 | Night | Thursday | 2019 | 8
10328 | 2019-08-01 22:01 | 2019-08-01 22:01 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 20 | 6D fdr#2 Load dropped 160A (189-29A). Not checked yet. |  | 1 | 22:01 | Night | Thursday | 2019 | 8
10329 | 2019-08-01 22:01 | 2019-11-01 16:58 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 20 | Checked & found 6D fdr#2 T/R, 1x, Ctr: 79-80, R/F: Not appear Patrolled the Line, but found nothing Cause: Lightning (Suspected) |  | 1 | 22:01 | Night | Thursday | 2019 | 8
10330 | 2019-09-01 17:06 | 2019-09-01 17:06 | 13.8KV CENTRAL DURI FEEDER #1 | Fair |  | 16 | 17:06 Manually opened Recl: 41 AW 62 ( C.Duri #1 ). Emergency case ( Broken conductor o/p 39 AU 14 and 39 AU 15 ). Isolate the conductor by cutting jumper o/p 39 AV 31. 17:15 Block and close Recl: 41 AW 62. success the realease the block. ( ctr: 298 -299 ). |  | 1 | 17:06 | Afternoon | Sunday | 2019 | 9
10331 | 2019-10-01 05:48 | 2019-10-01 05:48 | 13.8KV NELLA FEEDER #1 | Fair | Lightning | 0 | Nella fdr#1 load dropped 93A (222-129A). Nella GFPC T/R. Not checked yet. |  | 1 | 5:48 | Morning | Tuesday | 2019 | 10
10332 | 2019-10-01 05:48 | 13/01/2019 15:48 | 13.8KV NELLA FEEDER #1 | Fair | Lightning | 0 | Checked and found RCL 22-V-01 T/R 1x, ctr: 104-105, R/F: 51P Patrolled the line and found broken LA @1 on TOP BKO #193 Cause : Lightning |  | 1 | 5:48 | Morning | Tuesday | 2019 | 10
10333 | 2019-10-01 15:02 | 2019-10-01 15:02 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 49 | 15:02 Manually open Recl: 41 AW 62 ( C.Duri Fdr #1). Reconnected broken jumper at Kulin# 12 by Mtce crew. 15:45 Manually Closed Recl 41 AW 62. Ctr: 299 - 300. Cause: Planned Maintenance |  | 1 | 15:02 | Afternoon | Tuesday | 2019 | 10
10334 | 2019-10-01 16:20 | 2019-10-01 16:20 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning | 5 | Ketigul VCB fdr # 3 T/R 1x. Not checked yet. |  | 1 | 16:20 | Afternoon | Tuesday | 2019 | 10
10335 | 2019-10-01 16:20 | 2019-12-01 08:10 | 13.8KV KETIGUL FEEDER#3 | Fair | Lightning | 5 | Checked and found KTGL VCB fdr #3 T/R 1x, ctr: 208 - 209, R/F: 51P Patrolled the lines and found flash over pin insulator o/p 31-AS-01 Cause : Lightning |  | 1 | 16:20 | Afternoon | Tuesday | 2019 | 10
10336 | 2019-10-01 22:33 | 2019-10-01 22:33 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Lightning | 0 | Duri field 13.8KV VCB#51 fdr#4 T/R 1x. Not checked yet. |  | 1 | 22:33 | Night | Tuesday | 2019 | 10
10337 | 2019-10-01 22:33 | 2019-12-01 08:04 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found ACB fdr #4 T/R 1x, ctr: 541 - 542, R/F: 51P @2 Patrolled the lines and found bypass switch broken phase 2 o/p 07-V5-02 Cause : Lightning |  | 1 | 22:33 | Night | Tuesday | 2019 | 10
10338 | 2019-11-01 00:18 | 2019-11-01 00:18 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | - | 4D fdr#4 load dropped 126A (200-74A). Not checked yet. |  | 1 | 0:18 | Night | Friday | 2019 | 11
10339 | 2019-11-01 00:19 | 2019-11-01 00:19 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | - | 4D fdr#5 load dropped 85A (97-12A). Not checked yet. |  | 1 | 0:19 | Night | Friday | 2019 | 11
10340 | 2019-11-01 00:19 | 15/01/2019 20:44 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | - | Checked & found Recl. 4D 14A T/R 1x, Ctr: 62-63, R/F: none Patrolled the line, but found nothing Cause : Lightning |  | 1 | 0:19 | Night | Friday | 2019 | 11
10341 | 2019-11-01 00:31 | 2019-11-01 00:31 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 84 | 00:316D 13.8KV VCB fdr#5 T/R 1x. 00:51 6D 13.8KV VCB fdr#5 T/R 1x again. Not checked yet. |  | 1 | 0:31 | Night | Friday | 2019 | 11
10342 | 2019-11-01 00:31 | 13/01/2019 12:45 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 84 | Checked and found 6D OCB fdr 5 T/R 2x, ctr: 789-791, R/F: 51N Patrolled the lines and found broken deadend and pin insulator @1 o/p 5D-09 Cause : Lightning |  | 1 | 0:31 | Night | Friday | 2019 | 11
10343 | 2019-11-01 00:31 | 2019-11-01 00:31 | 13.8KV 6D FEEDER #6 | Rain and Lightning | Unidentified | - | 6D fdr#6 load dropped 124A (248-124A). Not checked yet. |  | 1 | 0:31 | Night | Friday | 2019 | 11
10344 | 2019-11-01 00:31 | 19/01/2019 20:20 | 13.8KV 6D FEEDER #6 | Rain and Lightning | Unidentified | - | Checked and found all protective devices are normal Patrolled the lines and found nothing, suspect GS pumps was off. Cause : Unidentified |  | 1 | 0:31 | Night | Friday | 2019 | 11
10345 | 2019-11-01 00:36 | 2019-11-01 00:36 | MINAS POWER PLANT |  |  | - | MGT#4 Trip by alarm Exciter failure. |  | 1 | 0:36 | Night | Friday | 2019 | 11
10346 | 2019-11-01 00:39 | 2019-11-01 00:39 | 13.8KV 5B FEEDER #8 | Rain and Lightning | Lightning | 0 | 5B 13.8Kv VCB fdr#8 T/R 1x. Not checked yet. |  | 1 | 0:39 | Night | Friday | 2019 | 11
10347 | 2019-11-01 00:39 | 15/01/2019 20:49 | 13.8KV 5B FEEDER #8 | Rain and Lightning | Lightning | 0 | Checked & found 5B OCB fdr#8 T/R 1x, Ctr: 99994-99995, R/F: 51GN patrolled the Line, but found nothing Cause : Lightning |  | 1 | 0:39 | Night | Friday | 2019 | 11
10348 | 2019-11-01 00:41 | 2019-11-01 00:41 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | - | 8D fdr#1 load dropped 54A (129-75A). Not checked yet. |  | 1 | 0:41 | Night | Friday | 2019 | 11
10349 | 2019-11-01 00:41 | 15/01/2019 18:17 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | - | Checked and found RCL 8F-05 T/R 1x, ctr: 76-77, R/F: none Patrolled the lines but found nothing Cause : Lightning |  | 1 | 0:41 | Night | Friday | 2019 | 11
10350 | 2019-11-01 02:15 | 2019-11-01 02:15 | MINAS POWER PLANT |  |  | - | S/U MGT#5, then on line the unit at 02:28. |  | 1 | 2:15 | Night | Friday | 2019 | 11
10351 | 2019-11-01 07:53 | / | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | - |  | 1 | 7:53 | Morning | Friday | 2019 | 11
10352 | 2019-11-01 09:19 | 2019-11-01 09:19 | 13.8KV DURI FIELD FEEDER #2 | Fair | Recloser | 0 | 09:19 Reported no power along road 07-V3-xx 10:35 Checked and found RCL 07-V3-21 T/SO, ctr 661-662 Patrolled the lines and found broken pin insulator o/p 07-V3-11 @3 and broken dead end @1 o/p 07-V3-12 10:40 Close the RCL n block position but failed. 11:33 Transfer to DF fdr #4 by close LBS o/p 07-V3-02 Cause: Recloser |  | 1 | 9:19 | Morning | Friday | 2019 | 11
10353 | 2019-11-01 18:15 | 2019-11-01 18:15 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified | 0 | 18:15 RANGAU feeder #2 load drop 150 A (164 - 14 A) Cause: Not Checked Yet |  | 1 | 18:15 | Afternoon | Friday | 2019 | 11
10354 | 2019-12-01 07:05 | 2019-12-01 07:05 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 07:05 CD fdr 1 load dropped 46 A (140 - 94 A) Cause: Not Checked Yet |  | 1 | 7:05 | Morning | Sunday | 2019 | 12
10355 | 2019-12-01 16:05 | 2019-12-01 16:05 | 13.8KV KETIGUL FEEDER#3 | Cloudy | Animal | 4 | 16:05 Ketigul fdr #3 T/R 1x Cause: Not Checked Yet |  | 1 | 16:05 | Afternoon | Sunday | 2019 | 12
10356 | 2019-01-13 11:13 | 2019-01-13 11:13 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 43 | 11:13 Sintong VCB feeder #2 T/R 1x Bangko feeder #4 load dropped 77 A (184 - 107 A) Cause: Not Checked Yet |  | 1 | 11:13 | Morning | Sunday | 2019 | 1
10357 | 2019-01-13 11:13 | 2019-01-15 11:13 | 13.8KV SINTONG FEEDER #2 | Fair | Animal | 43 | Checked and found STG OCB feeder #2, ctr: 486-487, R/F: 51N Patrolled the lines and found animal on TOP STG #28 @2 Cause : Animal |  | 1 | 11:13 | Morning | Sunday | 2019 | 1
10358 | 2019-01-14 08:38 | 2019-01-14 08:38 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Lightning | - | 08:38 Duri Community VCB feeder #2 T/R 1x Cause: Not Checked Yet |  | 1 | 8:38 | Morning | Monday | 2019 | 1
10359 | 2019-01-14 14:17 | 2019-01-14 14:17 | MINAS SWITCH GEAR | Rain and Lightning | Lightning | - | 14:17 13.8 kV ACB #21 Minas (to Rumbai) T/R 1x, ctr: 86-87, R/F: 51G Cause: Not Patrolled Yet |  | 1 | 14:17 | Afternoon | Monday | 2019 | 1
10360 | 2019-01-14 14:17 | 2019-01-15 18:11 | MINAS SWITCH GEAR | Rain and Lightning | Lightning | - | Checked and found ACB #21 Minas T/R 1x, ctr: 86-87, R/F: 51G Patrolled the lines and found Broken suspension insulator @1 o/p MR-66 Cause : Lightning |  | 1 | 14:17 | Afternoon | Monday | 2019 | 1
10361 | 2019-01-14 18:10 | 2019-01-14 18:10 | 13.8KV NORTH DURI FEEDER #9 | Cloudy | Unidentified | 0 | 18:10 ND VCB fdr #9 T/R 1x Cause: Not Checked Yet |  | 1 | 18:10 | Afternoon | Monday | 2019 | 1
10362 | 2019-01-15 19:22 | 2019-01-15 19:22 | 13.8KV LIBO FEEDER #2 | Rain | Unidentified | 30 | 19:22 Libo feeder #2 T/R 1s Cause: Not Checked Yet |  | 1 | 19:22 | Night | Tuesday | 2019 | 1
10363 | 2019-01-15 19:22 | 2019-01-17 10:44 | 13.8KV LIBO FEEDER #2 | Rain | Unidentified | 30 | Checked and found VCB Libo feeder #2 T/R 1x, ctr: 484-485, R/F 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 19:22 | Night | Tuesday | 2019 | 1
10364 | 2019-01-16 06:50 | 2019-01-16 06:50 | 13.8KV NELLA FEEDER #1 | Fair | Powerline - Jumper | 99 | Nella VCB fdr#1 T/R 1x Nella fdr#2 Load dropped 50A (71-21) Not checked yet |  | 1 | 6:50 | Morning | Wednesday | 2019 | 1
10365 | 2019-01-16 06:50 | 2019-01-17 16:51 | 13.8KV NELLA FEEDER #1 | Fair | Powerline - Jumper | 99 | Che3cked and found VCB NELLA feeder #1 T/R 1x, ctr: 535-536, R/F: 51P Patrolled the lines and found broken jumper at BKO #288 @1, @2 Cause : Jumper |  | 1 | 6:50 | Morning | Wednesday | 2019 | 1
10366 | 2019-01-16 06:50 | 2019-01-16 06:50 | 13.8KV NELLA FEEDER #2 | Fair | Normal Condition | - | Nella Fdr#2 Load dropped 50A (71-21A) Not checked yet |  | 1 | 6:50 | Morning | Wednesday | 2019 | 1
10367 | 2019-01-16 06:50 | 2019-01-18 11:46 | 13.8KV NELLA FEEDER #2 | Fair | Normal Condition | - | Checked and found all in normal condition Patrolled the lines but found nothing. Cause: Normal Condition |  | 1 | 6:50 | Morning | Wednesday | 2019 | 1
10368 | 2019-01-16 16:19 | 2019-01-16 16:19 | 13.8KV CENTRAL DURI FEEDER #8 | Cloudy | Powerline - Hot Line Clamp | 457 | 16:19 C Duri ACB #32 (feeder #8) T/O R/F: 51N Counter: 453-456. 17:17 Checked and found broken conductor between poles 04-05 28 to 04-05-30. 18:21 Opened Recloser: 04-05-28. 18:23 Blocked and closed C Duri ACB feeder #8 --> OK. and then released the block. Will be replaced tomorrow morning. Jan 17, 2019 12:08 Blocked and closed RCL 04-5-28, ctr 148-152, back to Normal Cause: Broken Conductor |  | 1 | 16:19 | Afternoon | Wednesday | 2019 | 1
10369 | 2019-01-16 18:30 | 2019-01-16 18:30 | 13.8KV BANGKO GFPC | Fair | Lightning | 0 | Bangko GFPC T/R 1x. Bangko feeder #4 load dropped 85A (184-99A). Not checked yet. |  | 1 | 18:30 | Afternoon | Wednesday | 2019 | 1
10370 | 2019-01-16 18:30 | 2019-01-19 17:55 | 13.8KV BANGKO GFPC | Fair | Lightning | 0 | Checked and found BKO GFPC T/R 1x, ctr: 192-193, R/F: None Patrolled the lines and found broken dead end insulator @3 o/p 25-AA-3 Cause : lightning |  | 1 | 18:30 | Afternoon | Wednesday | 2019 | 1
10371 | 2019-01-17 09:15 | 2019-01-17 09:15 | MINAS POWER PLANT |  |  | - | 09:15 S/U MGT #11 and then Online the unit at 09:45. |  | 1 | 9:15 | Morning | Thursday | 2019 | 1
10372 | 2019-01-17 09:53 | 2019-01-17 09:53 | CENTRAL DURI POWER PLANT |  |  | - | 09:53 CDGT #5 Trip by alarm Fire in turbine or accessories trouble. |  | 1 | 9:53 | Morning | Thursday | 2019 | 1
10373 | 2019-01-17 10:13 | 2019-01-17 10:13 | MINAS POWER PLANT |  |  | - | 10:13 Offline MGT #9 and then S/D the unit for standby. |  | 1 | 10:13 | Morning | Thursday | 2019 | 1
10374 | 2019-01-17 11:30 | 2019-01-17 11:30 | CENTRAL DURI POWER PLANT |  |  | - | 11:30 S/U CDGT #5 and then Online the unit at 11:45. |  | 1 | 11:30 | Morning | Thursday | 2019 | 1
10375 | 2019-01-17 21:05 | 2019-01-17 21:05 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 594 | 21:05 Petani VCB fdr #2 T/SO 23:03 Checked and found PTN VCB fdr #2 T/LO, ctr: 260-264, R/F: 50P @3 Checked PTN #99 that reported any blast by Petani GS, but found Normal condition. Jan 18, 2019 00:28 Continue patrolled the lines and found any vandalism act. at PTN #64 and PTN #68 (fuse link are opened and secondary cable has missing) 01:14 Close 13.8 kV VCB fdr #2 on Block Position, success then release the block. Cause: Unidentified | 123 | 1 | 21:05 | Night | Thursday | 2019 | 1
10376 | 2019-01-17 21:05 | 2019-01-18 21:05 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 594 | Jan 18, 2019 00:28 Continue patrolled the lines and found any vandalism act. at PTN #64 and PTN #68 (fuse link are opened and secondary cable has missing) 01:14 Close 13.8 kV VCB fdr #2 on Block Position, success then release the block. Cause: Unidentified | 123 | 1 | 21:05 | Night | Thursday | 2019 | 1
10377 | 2019-01-18 23:59 | 2019-01-18 23:59 | CPI POWER SYSTEM |  |  | - | System normal operation. |  | 1 | 23:59 | Night | Friday | 2019 | 1
10378 | 2019-01-19 10:24 | 2019-01-19 10:24 | 13.8KV BATANG FEEDER #2 | Fair | Planned Maintenance | 21 | 10:24 Manually opened Batang OCB fdr #2. For connecting HLC and T Tap at Rantau bais field. 13:31 Blocked and closed Batang OCB fdr #2 --> Success. and then released the block. Cause: Plan maintenance. |  | 1 | 10:24 | Morning | Saturday | 2019 | 1
10379 | 2019-01-19 14:30 | 2019-01-19 14:30 | CENTRAL DURI POWER PLANT |  |  | - | 14:30 S/U CDGT #3 and then Online the unit at 14:48. |  | 1 | 14:30 | Afternoon | Saturday | 2019 | 1
10380 | 2019-01-19 15:26 | 2019-01-19 15:26 | MINAS SWITCH YARD | Fair | Under investigation | 0 | 15:26 Minas 115 KV GCB #53 T/O. Minas 115 KV GCB #55 T/O. Minas Power Tx #8 tripped. Frequency : 59.96. 16:38 Checked and found : - 115 KV Minas 115 KV GCB #53 T/O Counter: 173-174. - 115 KV Minas 115 KV GCB #55 T/O Counter: 76-77. - R/F: 87T @1 , 86. 17:12 Opened Isolation switch to Power Tx #8 no: 352-73-080. Closed Grounding switch Power Tx #8 no: 352-77-080. Reset relay 87T and 86. Closed 115 KV GCB #53 --> Success. 17:43 Closed 115 KV GCB #55 --> Success. Cause: Under investigation. |  | 1 | 15:26 | Afternoon | Saturday | 2019 | 1
10381 | 2019-01-19 16:30 | 2019-01-19 16:30 | MINAS POWER PLANT |  |  | - | 16:30 S/U MGT #9 and then Online the unit 17:17. |  | 1 | 16:30 | Afternoon | Saturday | 2019 | 1
10382 | 2019-01-19 17:25 | 2019-01-19 17:25 | CENTRAL DURI POWER PLANT |  |  | - | 17:25 Offline CDGT #5 and then S/D the unit. |  | 1 | 17:25 | Afternoon | Saturday | 2019 | 1
10383 | 2019-01-19 18:00 | 2019-01-19 18:00 | 13.8KV BANGKO FEEDER #4 | Fair | Tree | 0 | Bangko fdr #4 load dropped 88A (181-93A). Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 18:00 | Afternoon | Saturday | 2019 | 1
10384 | 2019-01-20 09:48 | 2019-01-20 09:48 | 13.8KV BANGKO FEEDER #1 | Fair | Emergency | - | 09:48 Manually opened Bangko OCB feeder #1. due to 12" Main injector line leakage at Test Station " C ". 12:09 Manually blocked and closed Bangko OCB feeder #1, and then released the block. 10:38 Manually opened Nella OCB feeder #1. due to 12" Main injector line leakage at Test Station " C ". 11:29 Manually blocked and closed Nella OCB feeder #1, and then released the block. Cause: Emergency. |  | 1 | 9:48 | Morning | Sunday | 2019 | 1
10385 | 2019-01-20 13:41 | 2019-01-20 13:41 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Others | 83 | CKBS VCB feeder #5 T/R 1x. Not checked yet. |  | 1 | 13:41 | Afternoon | Sunday | 2019 | 1
10386 | 2019-01-20 13:41 | 2019-01-21 14:04 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Others | 83 | Checked and found CKB VCB fdr #5 T/R 1x, ctr: 166-167, R/F: 51P Patrolled the lines but found nothing Cause : Others |  | 1 | 13:41 | Afternoon | Sunday | 2019 | 1
10387 | 2019-01-20 13:51 | 2019-01-20 13:51 | 13.8KV NELLA FEEDER #2 | Cloudy | Lightning | 31 | Nella OCB feeder #2 T/R 1x. Nella GFPC T/R 1x. Not checked yet. |  | 1 | 13:51 | Afternoon | Sunday | 2019 | 1
10388 | 2019-01-20 13:51 | 2019-01-25 07:51 | 13.8KV NELLA FEEDER #2 | Cloudy | Lightning | 31 | Checked & found Nella VCB fdr#2 T/R 1x Ctr:320-321 R/F:51N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 13:51 | Afternoon | Sunday | 2019 | 1
10389 | 2019-01-20 19:55 | 2019-01-20 19:55 | 4.16KV NO RUMBAI FEEDER #1 | Fair | Unidentified | - | North Rumbai VCB feeder #1 T/R 1x Cause : Not Checked Yet |  | 1 | 19:55 | Night | Sunday | 2019 | 1
10390 | 2019-01-20 19:55 | 2019-01-25 07:55 | 4.16KV NO RUMBAI FEEDER #1 | Fair | Unidentified | - | Checked & found 41.6Kv No.Rumbai VCB fdr#1 T/R 1x Ctr:408-409 R/F:51N. Patrolled the line & found @2 Broken Pin Insulator o/p 2RD-05. Cause : Unidentified. |  | 1 | 19:55 | Night | Sunday | 2019 | 1
10391 | 2019-01-21 12:46 | 2019-01-21 12:46 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Emergency | - | 12:46 Manually opened PTH VCB feeder #6. Due to injection pump problem at Petapahan Substation. 15:48 Manually blocked and closed PTH VCB feeder #6, and then released the block. Cause: Emergency. |  | 1 | 12:46 | Afternoon | Monday | 2019 | 1
10392 | 2019-01-21 14:33 | 2019-01-21 14:33 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 30 | 14:33 Manually opened 8C OCB feeder #1. Due to replace Tx failure at well 9D-25. 14:59 Manually blocked and closed 8C OCB feeder #1, and then released the block. Cause: Plan Maintenance. |  | 1 | 14:33 | Afternoon | Monday | 2019 | 1
10393 | 2019-01-21 20:18 | 2019-01-21 20:18 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Lightning | 10 | 4B 13,8KV VCB fdr #6 T/R 1X. Not checked yet. |  | 1 | 20:18 | Night | Monday | 2019 | 1
10394 | 2019-01-21 20:18 | 2019-01-25 21:14 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Lightning | 10 | Checked & found 4B fdr#6 T/R Ctr:184-185 R/F :51@2. Patrolled the line bat found nothing. Cause : Lightning. |  | 1 | 20:18 | Night | Monday | 2019 | 1
10395 | 2019-01-21 23:25 | 2019-01-21 23:25 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 4 | 5B 13.8KV VCB fdr #3 T/SO. Not checked yet. |  | 1 | 23:25 | Night | Monday | 2019 | 1
10396 | 2019-01-21 23:25 | 2019-01-22 00:17 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 4 | 00:17 Checked and found VCB 5B fdr #3 T/SO Ctr: 398-401 R/F: 51@2@3. 00:19 Blocked and Close VCB 5B fdr #5, success then release the blocked Cause: Not Patrolled Yet |  | 1 | 23:25 | Night | Monday | 2019 | 1
10397 | 2019-01-21 23:25 | 2019-01-25 08:25 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 4 | Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 23:25 | Night | Monday | 2019 | 1
10398 | 2019-01-22 07:39 | 2019-01-22 07:39 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning | 0 | Bangko feeder #4 load dropped 81A (177-96A). Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 7:39 | Morning | Tuesday | 2019 | 1
10399 | 2019-01-22 07:39 | 2019-01-25 08:39 | 13.8KV BANGKO FEEDER #4 | Fair | Lightning | 0 | Checked & found Recl. 25Z-07 T/R 2x Ctr:212-215 R/F:51N. Bangko GFPC T/R 1x Ctr:195-196 R/F:51N. Patrolled the line & found @2@3 Broken Dead End Insulator o/p27Y-08. Cause : Lightning. |  | 1 | 7:39 | Morning | Tuesday | 2019 | 1
10400 | 2019-01-22 14:06 | 2019-01-22 14:06 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Lightning | 0 | C.Duri ACB#28 (feeder #16 ) T/R 1x. Not checked yet. |  | 1 | 14:06 | Afternoon | Tuesday | 2019 | 1
10401 | 2019-01-22 14:06 | 2019-01-24 10:08 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Lightning | 0 | Checked and found C.Duri ACB#28 fdr#16 T/R 1x Ctr: 332-333 R/F: 51N. Patrolled the line & Found @3 broken LA O/P 09 N4 10. Cause : Lightning. |  | 1 | 14:06 | Afternoon | Tuesday | 2019 | 1
10402 | 2019-01-22 14:17 | 2019-01-22 14:17 | 13.8KV 5B FEEDER #3 | Fair | Planned Maintenance | 14 | 14:17 Manually opened LBS: 4C-45 D/S 5B feeder #3. Due to cut palm trees 14:44 Manually closed LBS: 4C-45 D/S 5B feeder #3. Cause: Plan maintenance. |  | 1 | 14:17 | Afternoon | Tuesday | 2019 | 1
10403 | 2019-01-23 09:50 | 2019-01-23 09:50 | 13.8KV 6D FEEDER #5 | Fair | Planned Maintenance | 6 | 09:50 Manually Opened Recl. 6D-200 (6D fdr#5). Relaced @1 Broken Dead End Insulator o/p 5D-41. 11:43 Blocked & closed Recl. 6D-200, then release the block. Cause: Plan maintenance. |  | 1 | 9:50 | Morning | Wednesday | 2019 | 1
10404 | 2019-01-23 12:57 | 2019-01-23 12:57 | 13.8KV BATANG FEEDER #3 | Cloudy | Unidentified | 28 | Batang fdr#3 T/R 1x. Batang GFPC T/R 1x. Not checked yet. |  | 1 | 12:57 | Afternoon | Wednesday | 2019 | 1
10405 | 2019-01-23 12:57 | 26/06/2019 16:32 | 13.8KV BATANG FEEDER #3 | Cloudy | Unidentified | 28 | Checked & found Batang OCB fdr#3 T/R 1x, Ctr: 375-376, R/F: 50N Patrolled the Line, found @2 Broken LA Jumper O/P 39-AL-01 Cause : Unidentified |  | 1 | 12:57 | Afternoon | Wednesday | 2019 | 1
10406 | 2019-01-23 18:21 | 2019-01-23 18:21 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 38 | 18:21 C.Duri ACB #28 (feeder#16) T/LO. Counter:333-337 R/F 51@1@2. Patrolled the line found nothing. 20:01 Opened LBS: 09-P4-02. 20:04 Blocked and closed C.Duri ACB 28 (feeder#16) --> Success. and then released the block. 20:10 Closed LBS: 09-P4-02 --> Success. Cause: unidentified. |  | 1 | 18:21 | Afternoon | Wednesday | 2019 | 1
10407 | 2019-01-23 21:29 | 2019-01-23 21:29 | 13.8KV DURI COMMUNITY FEEDER #3 | Cloudy | Tree | 0 | D Comy ACB #26 (feeder #3) T/R 1x. Not checked yet. |  | 1 | 21:29 | Night | Wednesday | 2019 | 1
10408 | 2019-01-23 21:29 | 2019-01-24 19:21 | 13.8KV DURI COMMUNITY FEEDER #3 | Cloudy | Tree | 0 | Checked & found Dcom ACB #26 fdr#3 T/R 1x, Ctr: 86-87, R/F: 51 @1 Patrolled the Line, found high Tree Leaf touching @1 conductor o/p 6F7 Cause : Tree (Pelepah sawit) |  | 1 | 21:29 | Night | Wednesday | 2019 | 1
10409 | 2019-01-24 01:41 | 2019-01-24 01:41 | 13.8KV PUNGUT FEEDER #1 | Fair | Lightning Arrester | 28 | Pungut OCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 1:41 | Night | Thursday | 2019 | 1
10410 | 2019-01-24 01:41 | 2019-01-27 07:41 | 13.8KV PUNGUT FEEDER #1 | Fair | Lightning Arrester | 28 | Checked & found Pungut VCB fdr#1 T/R 1x Ctr:411-412 R/F:52@1@3. Patrolled the line & found @1@3 Broken LA o/p 45 BQ 29. @1 Broken Dead End Insulator o/p 45 BQ 14. Cause : Lightning Arrester. |  | 1 | 1:41 | Night | Thursday | 2019 | 1
10411 | 2019-01-24 09:40 | 2019-01-24 09:40 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 18 | 09:40 It was reported no power at 09-M3--3 (C.Duri fdr#1). 10:50 Checked & found Recl. 09-M3-01 T/SO Ctr:76-77. Patrolled the line but found nothing. 10:52 Blocked & closed Redcl.09_m3-01, then release the block. Cause: Unidentified. |  | 1 | 9:40 | Morning | Thursday | 2019 | 1
10412 | 2019-01-25 15:15 | 2019-01-25 15:15 | 13.8KV 4B FEEDER #2 | Fair | Planned Maintenance | 0 | 15:15 Opened HLC o/p 4B-47 (4B fdr#2) Replaced @1 Broken Dead End insulator o/p 5A-19 @1,@2 Broken Dead end insulator o/p 4B-57 (S/D Well 4B-93) 17:29 Closed HLC o/p 4B-47 Cause: Planned Maintenance |  | 1 | 15:15 | Afternoon | Friday | 2019 | 1
10413 | 2019-01-26 09:17 | 2019-01-26 09:17 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning | 39 | Sintong VCB fdr#2 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 9:17 | Morning | Saturday | 2019 | 1
10414 | 2019-01-26 09:17 | 2019-01-29 09:17 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning | 39 | Checked & found Sintong VCB fdr#2 T/R 1x Ctr:487-488 R/F:51N. Sintong GFPC T/R 2x Ctr:1104-1106. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 9:17 | Morning | Saturday | 2019 | 1
10415 | 2019-01-26 12:38 | 2019-01-26 12:38 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning | 0 | Menggala fdr#1 Load dropped 53A (199-146A). Menggala GFPC T/R 1x. Not checked yet. |  | 1 | 12:38 | Afternoon | Saturday | 2019 | 1
10416 | 2019-01-26 12:38 | 2019-01-29 09:38 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning | 0 | Checked & found Recl. 19A)01 T/R 1x Ctr:491-492. Patrolled the line & found @3 Broken LA o/p 19AP04. Cause : Lightning. |  | 1 | 12:38 | Afternoon | Saturday | 2019 | 1
10417 | 2019-01-26 16:50 | 2019-01-26 16:50 | 13.8KV PETAPAHAN FEEDER #3 | Fair | Construction Job | 0 | 16:50 Manually Opened PTH Vcb Fdr#3 Petapahan GS WIP Trip Off, to anticipate Tank over level 17:42 Man Closed back the Feeder, as requested GS Operator Cause: Plan construction. |  | 1 | 16:50 | Afternoon | Saturday | 2019 | 1
10418 | 2019-01-27 09:25 | 2019-01-27 09:25 | 13.8KV 8D FEEDER #5 | Fair | Planned Maintenance | 0 | 09:25 Opened LBS 8E-02 (8D fdr#5) Replaced Broken @123 Dead End o/p 7E-156 10:27 Closed back the LBS after finished the job. Cause: Planed Maintenance |  | 1 | 9:25 | Morning | Sunday | 2019 | 1
10419 | 2019-01-27 10:27 | 2019-01-27 10:27 | 13.8KV BATANG FEEDER #2 | Fair | Animal | 0 | It was reported b/o fuse at Well Rantau Bais #33 (Batang fdr#2) Not checked yet |  | 1 | 10:27 | Morning | Sunday | 2019 | 1
10420 | 2019-01-27 19:20 | 2019-01-27 19:20 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 225 | 19:20 OKB OCB feeder #2 T/O. 21:13 Checked and found OKB OCB feeder #2 T/SO. Counter: 1343-1344 R/F: Not appear. 21:21 Blocked and closed OKB OCB feeder #2 --> Success. and then released the block. Cause: Not checked yet. |  | 1 | 19:20 | Night | Sunday | 2019 | 1
10421 | 2019-01-27 19:20 | 2019-01-28 15:44 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 225 | Checked & found KB OCB fdr#2 T/R 1x, Ctr: 1343-1344, R/F: None Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 19:20 | Night | Sunday | 2019 | 1
10422 | 2019-01-27 23:45 | 2019-01-27 23:45 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Lightning | 40 | Ketigul VCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 23:45 | Night | Sunday | 2019 | 1
10423 | 2019-01-27 23:45 | 2019-01-31 17:13 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Lightning | 40 | Checked and found KTGL VCB fdr #2 T/R 1x ctr:315-316 R/F:51N Patrolled the lines and found @3 flashed over FCO on TOP Pager #12 Cause : Lightning |  | 1 | 23:45 | Night | Sunday | 2019 | 1
10424 | 2019-01-28 05:14 | 2019-01-28 05:14 | 13.8KV 4D FEEDER #1 | Fair | Under investigation | 35 | 05:14 4D OCB feeder#3 T/O. 4D OCB feeder#1 T/O. 115 Kv Circuit Switcher #1 T/O. Checked and found : 1. 4D OCB feeder#3 T/SO R/F: 81 Counter:253-254. 2. 4D OCB feeder#1 T/SO R/F: 81 Counter:183-184. 3. 115 Kv Circuit Switcher #1 T/O R/F: 51@A,@C. 06:17 Manually open 4D OCB feeder #2 Counter:267-268. 06:29 Manually closed 115 Kv Circuit Switcher #1 --> Success. 06:32 Manually blocked and closed 4D OCB feeder #2 --> Success. and then released the block. 06:33 Manually blocked and closed 4D OCB feeder #1 --> Success. and then released the block. 06:34 Manually blocked and closed 4D OCB feeder #3 --> Success. and then released the block. Cause: Under investigation. |  | 1 | 5:14 | Morning | Monday | 2019 | 1
10425 | 2019-01-28 14:07 | 2019-01-28 14:07 | 4 DELTA SUBSTATION | Fair | Equipment Failure | 136 | 14:07 4D 115KV Circuit Switcher TX#1 T/O 14:31 Manually Opened 4D Fdr #1,#2,#3 14:50 Checked & found 4D C/S TX#1 T/O, Ctr: 1775-1776, R/F: 51@3, GAS SF.6 Red Flag appear. Perform SP to Transfer all Load 4D fdr#1#2#3 also Closed Tie Bus to energized SST TX#1, (RTU energized) 16:30 Closed Grounding Switch of 115KV TX#1 16:33 Opened Isolation switches VR#1, & Fdr#1,#2,#3 16:38 Closed TIE Bus Breaker, energized SST TX#1, RTU Transfer Load 4d fdr##1,#2,#3 16:46 Closed LBS 3D-09 (4D fdr#3 Transfer to 3D fdr#2) 17:08 Closed LBS#A at GS#5 (4D fdr#1 Transfer to 3d fdr#6) 17:23 Unplug Recl 3D-19 Closed LBS 4D-240 (4D fdr#1 Transfer to 4D fdr#5) Cause: Equipment Failure |  | 1 | 14:07 | Afternoon | Monday | 2019 | 1
10426 | 2019-01-29 08:25 | 2019-01-29 08:25 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified | 0 | Pematang fdr#2 T/R 1x (Pematang Fdr#1 +fdr#2). Not checked yet. |  | 1 | 8:25 | Morning | Tuesday | 2019 | 1
10427 | 2019-01-29 08:25 | 2019-01-31 18:11 | 13.8KV PEMATANG FEEDER #2 | Fair | Unidentified | 0 | Checked and found PMT OCB feeder #2 T/R 2x ctr:519-521 R/F:51P Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 8:25 | Morning | Tuesday | 2019 | 1
10428 | 2019-01-29 08:44 | 2019-01-29 08:44 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | Menggala fdr#1 Load dropped 44A (199-155A). Menggala GFPC T/R 1x. Not checked yet. |  | 1 | 8:44 | Morning | Tuesday | 2019 | 1
10429 | 2019-01-30 04:34 | 2019-01-30 04:34 | 13.8KV 5B FEEDER #4 | Fair | Emergency | 0 | 04:34 Manually opened 5B OCB feeder #4. Due to SB #67 Pump problem at GS #6. 10:27 Manually Closed 5B OCB feeder #4. Cause: Emergency. |  | 1 | 4:34 | Morning | Wednesday | 2019 | 1
10430 | 2019-01-30 10:31 | 2019-01-30 10:31 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 102 | 10:31 Manually Open Recl. 27-AL-21. Closed HLC at well Sikaladi #06 (Reactive well).\ 15:54 Manually Closed Recl. 27-AL-21. Project. |  | 1 | 10:31 | Morning | Wednesday | 2019 | 1
10431 | 2019-01-30 16:33 | 2019-01-30 16:33 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | 16:33 ND 13.8KV VCB fdr #11 T/O (on blocked position). 16:41 Closed ND fdr #11. Cause: Not checked yet. |  | 1 | 16:33 | Afternoon | Wednesday | 2019 | 1
10432 | 2019-01-30 16:33 | 2019-02-02 12:30 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | Checked and found ND VCB fdr #11 T/O (on block post), ctr: 180-181, R/F: 51N Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 16:33 | Afternoon | Wednesday | 2019 | 1
10433 | 2019-01-31 08:46 | 2019-01-31 08:46 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C. Duri fdr #1 load dropped 53A (150-97A). Not checked yet. |  | 1 | 8:46 | Morning | Thursday | 2019 | 1
10434 | 2019-01-31 08:46 | 2019-04-02 16:10 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found RCL 41-AW-62 T/R 1x, ctr: 301-302, R/F: None Patrolled the line but found nothing Cause : Unidentified |  | 1 | 8:46 | Morning | Thursday | 2019 | 1
10435 | 2019-01-31 08:55 | 2019-01-31 08:55 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 0 | MGL feeder #1 load dropped 109 A (185 - 76 A) Not Checked Yet |  | 1 | 8:55 | Morning | Thursday | 2019 | 1
10436 | 2019-01-31 16:57 | 2019-01-31 16:57 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 0 | CD VCB feeder #16 T/R 1x, Counter: 337 - 338, R/F: 51N Not Patrolled Yet. |  | 1 | 16:57 | Afternoon | Thursday | 2019 | 1
10437 | 2019-01-31 16:57 | 2019-04-02 16:11 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 0 | Checked and found ACB #28 T/R 1x, ctr: 337-338, R/F: 51N Checked and found death monkey o/p 09-N2-01 Cause : Animal |  | 1 | 16:57 | Afternoon | Thursday | 2019 | 1
10438 | 2019-01-02 00:57 | 2019-01-02 00:57 | CENTRAL DURI SW GEAR 3-4 | Fair | Under investigation | 628 | 00:57 13.8Kv ACB#34 T/O 13.8 Generator CGT#3 T/O. Checked All protection not found. 01:10 Opened 13.8Kv ACB fdr#7, then closed at 03:10. Opened 13.8Kv ACB fdr#8, then closed at 03:15. 01:32 Opened ACB#37 (for GFW Pump). 02:35 S/D CGT#3. 03:09 Closed ACB#34. 04:15 S/U CGT#3, then on line the unit at 04:33. 06: 48 13.8Kv ACB#34 T/O 13.8 Generator CGT#3 T/O. Manual Open CD ACB feeder #7, then close at 10:04 Manual Open CD ACB feeder #8, then close at 10:05 Checked and found R/F Bus-3 Neutral TOC-5 08:00 Checked and found Relay F-35 at SG 3/4 failed (power supply problem) The relay was initiate ACB #34 to Tripped 09:50 Close 13.8 kV ACB #34 10:07 Close 13.8 kV ACB #37 10:40 Close 13.8 kV ACB #39 (tie breaker) but failed 10:42 S/U CDGT-3 and then O/L at 10:46 Cause: Under Investigation. | 1234 | 1 | 0:57 | Night | Wednesday | 2019 | 1
10439 | 2019-01-02 10:33 | 2019-01-02 10:33 | CENTRAL DURI POWER PLANT |  |  | - | 10:33 S/U CDGT-3 and then O/L the unit at 10:48 |  | 1 | 10:33 | Morning | Wednesday | 2019 | 1
10440 | 2019-02-02 08:52 | 2019-02-02 08:52 | CENTRAL DURI POWER PLANT |  |  | - | 08:52 CGT #1 Off line and then S/D for Gas Scrubber PSV certification. 14:15 CGT #1 S/U and then On line to the system at 14:32. |  | 1 | 8:52 | Morning | Saturday | 2019 | 2
10441 | 2019-02-02 14:15 | 2019-02-02 14:15 | CENTRAL DURI POWER PLANT |  |  | - | CDGT-1 S/U and then online at 14:32 |  | 1 | 14:15 | Afternoon | Saturday | 2019 | 2
10442 | 2019-02-02 15:33 | 2019-02-02 15:33 | MINAS POWER PLANT |  |  | - | MGT-8 S/U and then online at 15:57 |  | 1 | 15:33 | Afternoon | Saturday | 2019 | 2
10443 | 2019-02-02 16:21 | 2019-02-02 16:21 | MINAS POWER PLANT |  |  | - | MGT-10 S/U and then online at 16:37 |  | 1 | 16:21 | Afternoon | Saturday | 2019 | 2
10444 | 2019-02-02 17:51 | 2019-02-02 17:51 | NORTH DURI POWER PLANT |  |  | - | NDC CT-1 offline and shutdown for Off Line Wash Activities |  | 1 | 17:51 | Afternoon | Saturday | 2019 | 2
10445 | 2019-02-02 18:31 | 2019-02-02 18:31 | 13.8KV NORTH DURI FEEDER #11 | Fair | Animal | - | 18:31 ND VCB fdr #11 T/R 1x Not Checked Yet |  | 1 | 18:31 | Afternoon | Saturday | 2019 | 2
10446 | 2019-02-02 18:31 | 2019-06-02 10:53 | 13.8KV NORTH DURI FEEDER #11 | Fair | Animal | - | Checked and found N Duri VCB feeder #11 T/R 2x. R/F:51N Counter:181-183. Patrolled the line found animal (bird) hang on conductor on pole 13-F10-23. Cause: Animal (bird). |  | 1 | 18:31 | Afternoon | Saturday | 2019 | 2
10447 | 2019-02-02 23:52 | 2019-02-02 23:52 | MINAS POWER PLANT |  |  | - | 23:52 MGT#9 Trip Off by Alarm Gas pressure Low (220Psi) Frequency System 59.78, no load shedding 00:57 MGT#9 S/U, then On Line at 01:27 After Gas Press Back to normal Also Rebooted Computer Controller Cause : Under investigate |  | 1 | 23:52 | Night | Saturday | 2019 | 2
10448 | 2019-03-02 10:05 | 2019-03-02 10:05 | 13.8KV BANGKO FEEDER #1 | Fair | Planned Maintenance | 29 | 10:05 Manual Open RCL 24-Y-21 (BKO fdr #1) MTCE team to c/o broken pin and LA o/p 24-X-01 and 24-X-03 11:40 Recloser the RCL 24-Y-21, success Planned Maintenance |  | 1 | 10:05 | Morning | Saturday | 2019 | 3
10449 | 2019-03-02 14:46 | 2019-03-02 14:46 | 13.8KV SINTONG GFPC | Rain and Lightning | Lightning | 0 | 14:46 Sintong GFPC T/R 1x, Alarm at STG fdr #2 Sintong feeder #2 dropped 14 A (189 - 175 A) Not Checked Yet |  | 1 | 14:46 | Afternoon | Saturday | 2019 | 3
10450 | 2019-03-02 18:10 | 2019-03-02 18:10 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 50 | 18:10 KTGL VCB fdr #2 T/R 1x KTGL feeder #1 load dropped 59 A (126 - 67 A) Not Checked Yet |  | 1 | 18:10 | Afternoon | Saturday | 2019 | 3
10451 | 2019-03-02 18:10 | 2019-06-02 10:53 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 50 | Checked and found Ketigul VCB feeder #2 T/R 1x. R/F: 51N Counter: 316-317. Patrolled the line found Animal (monkey) at well Pagar #34. Cause: Animal (monkey). |  | 1 | 18:10 | Afternoon | Saturday | 2019 | 3
10452 | 2019-03-02 19:31 | 2019-03-02 19:31 | NORTH DURI POWER PLANT |  |  | - | 19:31 S/U NDC#1, then on line the unit at 20:31. |  | 1 | 19:31 | Night | Saturday | 2019 | 3
10453 | 2019-03-02 19:34 | 2019-03-02 19:34 | NORTH DURI POWER PLANT |  |  | - | 19:31 NDC CT #1 S/U , then Online at 20:31 After performed Off Line Wash |  | 1 | 19:34 | Night | Saturday | 2019 | 3
10454 | 2019-04-02 01:28 | 2019-04-02 01:28 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | - | Batang OCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 1:28 | Night | Tuesday | 2019 | 4
10455 | 2019-04-02 01:28 | 2019-06-02 10:53 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning | - | Checked and found Batang OCB feeder #3 T/R 1x. R/F: 50@1 Counter: 376-377. Patrolled the line found broken fuse on pole 37-AL-10. Cause: Suspected lightning. |  | 1 | 1:28 | Night | Tuesday | 2019 | 4
10456 | 2019-04-02 02:19 | 2019-04-02 02:19 | NORTH DURI POWER PLANT |  |  | - | 02:19 Off line NDC#2, then S/D the unit for Maintenance. 18:15 S/U NDC#2, then on line the unit at 19:03. |  | 1 | 2:19 | Night | Tuesday | 2019 | 4
10457 | 2019-04-02 09:05 | 2019-04-02 09:05 | MINAS POWER PLANT |  |  | - | 09:05 MGT #1 S/U and then online at 09:35 |  | 1 | 9:05 | Morning | Tuesday | 2019 | 4
10458 | 2019-04-02 09:47 | 2019-04-02 09:47 | 13.8KV NORTH DURI FEEDER #6 | Fair | Planned Maintenance | 31 | 09:47 Manual open RCL 12-F11-02 (ND fdr #6) 11:54 Blocked & closed RCL 12-F11-02,ok, then release the block. Planned Maintenance |  | 1 | 9:47 | Morning | Tuesday | 2019 | 4
10459 | 2019-04-02 10:59 | 2019-04-02 10:59 | 13.8KV 8D FEEDER #10 | Fair | Planned Maintenance | - | 10:59 Manual Open RCL 7E-21 for c/o TX at 8D-19 11:35 Blocked & closed the RCL 7E-21, ok, then release the block. Planned Maintenance |  | 1 | 10:59 | Morning | Tuesday | 2019 | 4
10460 | 2019-05-02 10:13 | 2019-05-02 10:13 | NORTH DURI POWER PLANT |  |  | - | Off line NDC CT#3, then S/D the unit for Maintenance (HGPI Program). |  | 1 | 10:13 | Morning | Thursday | 2019 | 5
10461 | 2019-05-02 23:59 | 2019-05-02 23:59 | CPI POWER SYSTEM |  | Normal Condition | - | Normal System Condition. |  | 1 | 23:59 | Night | Thursday | 2019 | 5
10462 | 2019-06-02 09:42 | 2019-06-02 09:42 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | C Duri ACB #22 (feeder#5) T/R 2x R/F:50@2,3 Counter: 259-261. Not patrolled yet. |  | 1 | 9:42 | Morning | Sunday | 2019 | 6
10463 | 2019-06-02 09:42 | 2019-10-02 08:07 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | Checked and found ACB-22 (CD fdr #5) T/R 2x, ctr: 259-261, R/F 50P @2 @3 Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 9:42 | Morning | Sunday | 2019 | 6
10464 | 2019-06-02 18:45 | 2019-06-02 18:45 | KETIGUL SUBSTATION | Fair | Under investigation | 1069 | 18:45 KETIGUL 115 Kv GCB #2 T/O. KETIGUL 115 Kv GCB #3 T/O. 21:20 Checked and found 115 kV GCB #2 T/O, ctr: 174 - 175, R/F : None 115 kV GCB #3 T/O, ctr: 165 - 166, R/F : None Checked 86HR and 86T found Normal/Not Operate Checked TX condition, found Normal 21:30 Manually opened Ketigul VCB feeder #1, Closed at 22:01, ctr: 209 - 210 21:32 Manually opened Ketigul VCB feeder #3, Closed at 22:02, ctr: 210 - 211 21:35 Manually opened Ketigul VCB feeder #2, Closed at 21:58, ctr: 317 - 318 21:49 Manual Close 115 kV GCB #2, success, ctr: 174 - 175 21:56 Manual Close 115 kV GCB #3, success, ctr: 165 - 166 Cause: Under Investigation | 0 | 1 | 18:45 | Afternoon | Sunday | 2019 | 6
10465 | 2019-07-02 10:48 | 2019-07-02 10:48 | 13.8KV 8D FEEDER #11 | Fair | Planned Maintenance | 69 | 10:48 Manually open 8D OCB feeder #11. Due to Change out Transformer at well 8E-85. 11:13 Manually blocked and closed 8D OCB feeder #11, and then released the block. Cause: Plan maintenance. |  | 1 | 10:48 | Morning | Tuesday | 2019 | 7
10466 | 2019-07-02 11:31 | 2019-07-02 11:31 | 13.8KV 8C FEEDER #2 | Fair | Planned Maintenance | 32 | 11:13 Manually open 8C VCB feeder #2. Due to Change out Transformer at well 8E-81. 11:57 Manually blocked and closed 8C VCB feeder #2, and then released the block. Cause: Plan maintenance. Production loss: 27 Bbls / 9 wells GS#1. Production loss: 11 Bbls / 9 wells GS#2. ----------------------------------------- + Total : 38 Bbls / 18 wells. |  | 1 | 11:31 | Morning | Tuesday | 2019 | 7
10467 | 2019-08-02 06:37 | 2019-08-02 06:37 | 13.8KV PETAPAHAN FEEDER #8 | Fair | Lightning | 32 | 06:37 Petapahan 13.8KV VCB fdr#8 T/R 1x. 10:54 Checked and found PTH VCB feeder #8 T/R 1x. Counter: 367-368 R/F: 51 @2 Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 6:37 | Morning | Friday | 2019 | 8
10468 | 2019-09-02 05:09 | 2019-09-02 05:09 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 23 | 05:09 ACB-51 (DF fdr #4) T/R 2x Counter:542- 544 R/F: 51@1. 08:13 It was reported no power at road 06-R7-07. 09:05 Checked and found Animal (Eagle) hang on Recloser 06-R7-19. Recloser 06-R7-19 T/O Counter:591-592. Cause @1 broken bushing Recloser on pole 06-R7-19. 09:55 Manually open Duri Field VCB #51 (feeder #4). For opening Hot Line clamp on source side of Recloser. and then Bypass the Recloser 06-R7-19. 10:19 Manually blocked and closed Duri Field VCB #51 (feeder #4). and then released the block. Recloser 06-R7-19 status: Bypass. Cause: Animal. |  | 1 | 5:09 | Morning | Monday | 2019 | 9
10469 | 2019-09-02 10:20 | 2019-09-02 10:20 | 4.16KV EAST RUMBAI FEEDER #2 | Fair | Planned Maintenance | 0 | 10:20 Manually open East Rumbai VCB feeder #2. For brush cutting at Kenari complex and Wisma Bukit. 15:25 Manually blocked and closed East Rumbai VCB feeder #2. and then released the block , Counter:534-535. Cause: Plan Maintenance. |  | 1 | 10:20 | Morning | Monday | 2019 | 9
10470 | 2019-09-02 10:24 | 2019-09-02 10:24 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Planned Maintenance | 0 | 10:24 Manually open Dumai 4160V VCB #12 (feeder #1). For replacing cross arm and cut high trees. 15:49 Manually blocked and closed Dumai 4160V VCB #12 (feeder #1). and then released the block , Counter: 298-299. Cause: Plan Maintenance. |  | 1 | 10:24 | Morning | Monday | 2019 | 9
10471 | 2019-09-02 16:01 | 2019-09-02 16:01 | MINAS SWITCH GEAR | Fair | Unidentified | 0 | Minas SWG ACB #21 (44Kv Minas - Rumbai Line) T/R 1x. Counter: 87-88 R/F: 51 @1,@2. Not Patrolled yet. |  | 1 | 16:01 | Afternoon | Monday | 2019 | 9
10472 | 2019-09-02 16:01 | 2019-12-02 17:14 | MINAS SWITCH GEAR | Fair | Unidentified | 0 | Checked and found MNSSG-13.8ACB21 T/R, ctr: 87-88, R/F: 51P Patrolled the line but found nothing Cause : Unidentified |  | 1 | 16:01 | Afternoon | Monday | 2019 | 9
10473 | 2019-09-02 18:21 | 2019-09-02 18:21 | 13.8KV LIBO FEEDER #2 | Cloudy | Unidentified | 31 | Libo OCB feeder #2 T/R 1x. Libo feeder #1 load dropped 27A (67-40A). Not checked yet. |  | 1 | 18:21 | Afternoon | Monday | 2019 | 9
10474 | 2019-09-02 18:21 | 2019-12-02 10:00 | 13.8KV LIBO FEEDER #2 | Cloudy | Unidentified | 31 | Checked and found Libo OCB feeder #2 T/R 1x. Counter: 485-486 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 18:21 | Afternoon | Monday | 2019 | 9
10475 | 2019-10-02 08:05 | 2019-10-02 08:05 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C Duri ACB VCB #28 (feeder#16) T/R 1x. Counter: 338-339 R/F: 51@1,@2. Not patrolled yet. |  | 1 | 8:05 | Morning | Wednesday | 2019 | 10
10476 | 2019-10-02 08:05 | 2019-12-02 16:57 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked and found C Duri ACB #28 (feeder #16) T/R 1x. Counter: 38-339 R/F: 51@1,@2. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 8:05 | Morning | Wednesday | 2019 | 10
10477 | 2019-10-02 15:54 | 2019-10-02 15:54 | 13.8KV CENTRAL DURI FEEDER #6 | Rain | Lightning | 0 | C Duri ACB VCB #23 (feeder#6) T/R 1x. Counter: 486-487 R/F: 50@3. Not patrolled yet. |  | 1 | 15:54 | Afternoon | Wednesday | 2019 | 10
10478 | 2019-10-02 15:54 | 2019-12-02 17:00 | 13.8KV CENTRAL DURI FEEDER #6 | Rain | Lightning | 0 | Checked and found C Duri ACB VCB #23 (feeder#6) T/R 1x. Counter: 486-487 R/F: 50@3. Patrolled the line found @2 Broken fuse on pole 02-01-01A. Cause: Suspected Lightning. |  | 1 | 15:54 | Afternoon | Wednesday | 2019 | 10
10479 | 2019-10-02 16:14 | 2019-10-02 16:14 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 25 | Pematang main 44 Kv OCB #2 (To RANGAU ) T/R 1x. Not checked yet. |  | 1 | 16:14 | Afternoon | Wednesday | 2019 | 10
10480 | 2019-10-02 16:14 | 2019-12-02 17:05 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 25 | Checked and found Pematang main 44 Kv OCB #2 (To RANGAU ) T/R 1x. Counter: 50006 - 51117 R/F: None. Patrolled the line found @1 broken dead end insulator on pole RGU #57. Cause: Lightning. |  | 1 | 16:14 | Afternoon | Wednesday | 2019 | 10
10481 | 2019-10-02 17:38 | 2019-10-02 17:38 | 13.8KV NORTH DURI FEEDER #9 | Cloudy | Unidentified | 0 | N Duri VCB feeder #9 T/R 1x. Not checked yet. |  | 1 | 17:38 | Afternoon | Wednesday | 2019 | 10
10482 | 2019-10-02 17:38 | 2019-12-02 17:11 | 13.8KV NORTH DURI FEEDER #9 | Cloudy | Unidentified | 0 | Checked and found N Duri VCB feeder #9 T/R 1x. Counter: 78-79 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 17:38 | Afternoon | Wednesday | 2019 | 10
10483 | 2019-10-02 18:59 | 2019-10-02 18:59 | 13.8KV NORTH DURI FEEDER #7 | Cloudy | Unidentified | 0 | N Duri VCB feeder #7 T/R 1x. Not checked yet. |  | 1 | 18:59 | Afternoon | Wednesday | 2019 | 10
10484 | 2019-10-02 18:59 | 2019-12-02 17:16 | 13.8KV NORTH DURI FEEDER #7 | Cloudy | Unidentified | 0 | Checked and found N Duri VCB feeder #7 T/R 1x. Counter : 104 - 105 R/F: 50N. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 18:59 | Afternoon | Wednesday | 2019 | 10
10485 | 2019-11-02 15:42 | 2019-11-02 15:42 | 44KV PEMATANG MAIN - RANGAU LINE | Fair | Under investigation | 291 | 15:42 Pematang Main 44Kv OCB #2 (To Rangau) T/O. Rangau OCB feeder #1 T/R. 18:10 Checked and found 44 Kv OCB #2 T/LO. Counter: 51117-84440 ( Error ) R/F: 50@3 and 50N Rangau OCB feeder #1 T/R 1x Counter: 23-24 R/F: Not appear. Power Tx R/F: 87T @1,2,3 and 86T. HSGS --> Close position. 18:16 Manually Open RGU VCB feeder #1, closed at 20.21 Manually Open RGU VCB feeder #2, closed at 20.23 19:58 Release HSGS at Rangau SS, Success 20:15 Manual Close 44 kV GCB feeder #2 at PMT Main, success (TX RGU SS are energized), monitor the TX for a few moment and then continue to energized VCB fdr #1 (20:21) and fdr #2 (20:23) Cause: under investigation |  | 1 | 15:42 | Afternoon | Saturday | 2019 | 11
10486 | 2019-12-02 09:54 | 2019-12-02 09:54 | 13.8KV PETANI FEEDER #2 | Fair | Others | 70 | Petani OCB feeder #2 T/R 1x. Petani feeder #1 load dropped 146A (187-41A). Not checked yet. |  | 1 | 9:54 | Morning | Monday | 2019 | 12
10487 | 2019-12-02 16:30 | 2019-12-02 16:30 | 13.8KV NORTH DURI FEEDER #11 | Fair | Animal | 0 | N Duri VCB feeder #11 T/R 1x. Not checked yet. |  | 1 | 16:30 | Afternoon | Monday | 2019 | 12
10488 | 2019-12-02 16:30 | 14/02/2019 21:30 | 13.8KV NORTH DURI FEEDER #11 | Fair | Animal | 0 | Checked and found N Duri VCB feeder #11 T/R 1x. Counter: 183-184 R/F: 51@1. Patrolled the line found bird dead on Recloser: 13-F10-23. Cause : Animal. |  | 1 | 16:30 | Afternoon | Monday | 2019 | 12
10489 | 2019-02-13 | 2019-02-13 | CPI POWER SYSTEM |  |  | 0 | CPI Power System Normal Condition. |  | 1 | 0:00 | Night | Wednesday | 2019 | 2
10490 | 2019-02-14 00:10 | 2019-02-14 00:10 | 13.8KV KOTABATAK FEEDER #2 | Fair | Lightning | 253 | OKB OCB feeder#2 T/R 1x. Not checked yet. |  | 1 | 0:10 | Night | Thursday | 2019 | 2
10491 | 2019-02-14 00:10 | 2019-02-14 21:24 | 13.8KV KOTABATAK FEEDER #2 | Fair | Lightning | 253 | Checked and found OKB OCB feeder#2 T/R 1x. Counter:1352-1353 R/F: 51N. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 0:10 | Night | Thursday | 2019 | 2
10492 | 2019-02-14 08:01 | 2019-02-14 08:01 | 13.8KV ROKAN FEEDER #2 | Cloudy | Lightning Arrester | 16 | Rokan OCB fdr #2 T/R 1x not checked yet |  | 1 | 8:01 | Morning | Thursday | 2019 | 2
10493 | 2019-02-14 08:01 | 2019-02-16 22:59 | 13.8KV ROKAN FEEDER #2 | Cloudy | Lightning Arrester | 16 | Checked and found Rokan OCB fdr #2 T/R 1x. Counter: 1281-1282 R/F: 51@2. Patrolled the line found @2 broken Lightning Arrester on pole 31-AV-11. Cause: Lightning Arrester. |  | 1 | 8:01 | Morning | Thursday | 2019 | 2
10494 | 2019-02-14 10:53 | 2019-02-14 10:53 | 13.8KV ROKAN FEEDER #4 | Fair | Planned Maintenance | 0 | 10:53 Manually Opened Rokan VCB fdr#4 to PM recloser at RGU WTP 12:00 Closed back the VCB after finished the Jobs Cause: Planned Maintenace |  | 1 | 10:53 | Morning | Thursday | 2019 | 2
10495 | 2019-02-15 01:00 | 2019-02-15 01:00 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 26 | 6D feeder#2 load dropped 141A (198-57A). Not checked yet. Production loss: 35 Bbls / 18 wells. Production loss: 3 Bbls / 1 well. --------------------------------------- + Total : 38 Bbls / 19 wells. |  | 1 | 1:00 | Night | Friday | 2019 | 2
10496 | 2019-02-15 01:00 | 23/02/2019 16:59 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 26 | Checked & found, Rcl 6D 298 T/R 1x, Ctr: 80-81, R/F: none Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 1:00 | Night | Friday | 2019 | 2
10497 | 2019-02-15 01:00 | 2019-02-15 01:00 | 13.8KV 6D FEEDER #3 | Rain and Lightning | Lightning | 12 | 6D feeder#3 load dropped 142A (215-73A). Not checked yet. |  | 1 | 1:00 | Night | Friday | 2019 | 2
10498 | 2019-02-15 01:00 | 23/02/2019 16:52 | 13.8KV 6D FEEDER #3 | Rain and Lightning | Lightning | 12 | Checked & found, Recl 6D03, T/R 1x, Ctr: 167-168, R/F: none Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 1:00 | Night | Friday | 2019 | 2
10499 | 2019-02-15 01:52 | 2019-02-15 01:52 | 13.8KV 8D FEEDER #4 | Rain and Lightning | Lightning | 21 | 8D OCB feeder #4 T/R 1x. Not checked yet. |  | 1 | 1:52 | Night | Friday | 2019 | 2
10500 | 2019-02-15 01:52 | 23/02/2019 17:06 | 13.8KV 8D FEEDER #4 | Rain and Lightning | Lightning | 21 | Checked & found,8D VCB fdr#4 T/R 2x, Ctr: 1546-1548, R/F: 50 @1,2,3 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 1:52 | Night | Friday | 2019 | 2
10501 | 2019-02-15 01:52 | 2019-02-15 01:52 | 13.8KV 8D FEEDER #5 | Rain and Lightning | Lightning | - | 8D OCB feeder #5 T/R 1x. Not checked yet. |  | 1 | 1:52 | Night | Friday | 2019 | 2
10502 | 2019-02-15 07:46 | 2019-02-15 07:46 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 0 | 07:46 Rangau fdr#2 load dropped 120A(140-20A). Not checked yet. |  | 1 | 7:46 | Morning | Friday | 2019 | 2
10503 | 2019-02-15 07:46 | 2019-02-19 13:05 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 0 | Checked & found Recl. 23 BD 01 T/R 2x, C/T: 364-366, R/F: 51N Patrolled the Line @2 B/O Fuse for Tx o/p 22-BD-9 and 22-BD-10 for street light Jurong road Cause : Unidentified |  | 1 | 7:46 | Morning | Friday | 2019 | 2
10504 | 2019-02-15 09:53 | 2019-02-15 09:53 | POWER GENERATION SHORTAGE | Fair | Construction Job | 46 | 09:53 Reduce power Generated due to Gas CoPi Zero flow, HCT team to Install new PCV valve at MDP 10:15 Manually Opened 3D VCB fdr#2, Closed at 21:52 10:18 4B VCB fdr#6, Closed at 17:18 10:20 4D VCB fdr#4 (+6DN fdr#1) Closed at 21:32 10:55 6D VCB fdr#1 Closed at 11:30 10:26 5B VCB fdr#3 Closed at 21:47 10:43 MSU #2 (5B fdr #4 and #5) Closed at 21:30 10:27 3D VCB fdr#3 Closed at 21:41 10:45 8D VCB fdr#3 Closed at 21:36 10:45 4D VCB fdr#5 + 4D fdr#2 Closed at 21:33 10:55 8D VCB fdr#10 Closed at 12:55 21:22 Start Pressure Control Valve (PCV) at MDP. 21:42 Declare Normal Gas. 21:56 Gas from Duri back to normal. 21:30 - 21:52 Energize feeders at Minas. Production Loss 3D VCB fdr#2 + 4D fdr#3 = 427 Bbls / 16 wells. Production Loss 4B VCB fdr#6 = WIP Production Loss 4D VCB fdr#4 + 6DN fdr#1 = 375 Bbls / 23 wells. Production Loss 6D VCB fdr#1 = 56 Bbls / 23 wells. Production Loss 5B VCB fdr#3 = 156 Bbls / 8 wells. Production Loss MSU #2 (5B fdr #4 and #5) = 115 Bbls / 8 wells. Production Loss 3D VCB fdr#3 = 198 Bbls / 15 wells. Production Loss 8D VCB fdr#3 = 0 Production Loss 4D VCB fdr#5 + 4D fdr#2 = 414 Bbls / 25 wells. Production Loss 8D VCB fdr#10 = 97 Bbls / 8 wells. -------------------------------------------------------------- + Grand total Production loss = 1838 Bbls / 126 wells. GS #5 Requested, Due to WIP Trip (DB # 1,2,3,4,5,6,7,8) 23:11 Manually opened 3D VCB fdr#2 + 4D fdr#3 23:11 Manually opened 3D VCB fdr#3 FEB-16-2019 00:56 Manually Opened 4D VCB fdr#5 + 4D fdr#2. Closed at 10:24 00:57 Manually Opened 5B VCB fdr#3 Closed at 10:24 07:35 Manually Opened 3D VCB fdr#4 Closed at 09:05 10:13 Manually Closed 3D VCB fdr#2 + 4D fdr#3 10:13 Manually Closed 3D VCB fdr#3 Cause: Planned Construction |  | 1 | 9:53 | Morning | Friday | 2019 | 2
10505 | 2019-02-15 18:00 | 2019-02-15 18:00 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 66 | Ketigul fdr#2 T/R 1x. Not checked yet. |  | 1 | 18:00 | Afternoon | Friday | 2019 | 2
10506 | 2019-02-15 18:00 | 2019-02-19 12:57 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 66 | Checked & found Ketigul VCB fdr#2 T/R 1x, Ctr: 318-319, R/F: 51 @2. Patrolled the Line, found dead Monkey O/p 29 AL 11 and Dead end flash over phase 2 O/p 29 AL16 Cause : Animal |  | 1 | 18:00 | Afternoon | Friday | 2019 | 2
10507 | 2019-02-16 | 2019-02-16 | CPI POWER SYSTEM |  |  | - | CPI Power System Normal Condition. |  | 1 | 0:00 | Night | Saturday | 2019 | 2
10508 | 2019-02-17 13:35 | 2019-02-17 13:35 | MOBILE SUBSTATION 1 | Fair | Others | 41 | I3:35 It was reported NO Power at GS#4 (5B fdr#8) 12:13 RTU 5B MSU was fail 13:55 Checked & found 115KV CS 5B MSU T/O.. also found MSU 5B TX R/F: 86 HR, Oil Temp. 95 C, Wind temp: 110 C 14:12 Man Opened 4D fdr#4 (+6DN fdr#1), GS #4 Requested due to WIP Trip 15:10 Man CLosed 4D fdr#4 (+6DN fdr#1), GS #4 Requested Normalized 5B TX#2 14:50 Opened Disconnect switch MSU fdr#1 & fdr#2 14:53 Closed Isolation switch 5B fdr#8 & fdr#5 14:58 Blocked & Closed 5B fdr#8, then released the block 15:00 Blocked & Closed 5B fdr#5, then released the block Cause: Under investigation. Production loss 5B fdr #8 : WIP. Production loss 5B fdr #4 : 34 Bbls / 13 wells. Production loss 5B fdr #5 : 25 Bbls / 8wells. ------------------------------------ + Total : 59 Bbls / 21 wells. |  | 1 | 13:35 | Afternoon | Sunday | 2019 | 2
10509 | 2019-02-17 14:31 | 2019-02-17 14:31 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | Sintong GFPC T/R 1x Sintong fdr#2 Load dropped 88A Not checked yet |  | 1 | 14:31 | Afternoon | Sunday | 2019 | 2
10510 | 2019-02-17 14:31 | 2019-02-19 20:15 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | Checked & found Recl 28 AF 17 T/R 1x, Ctr: 457-458, R/F: R/F: 51N Patrolled the Line, found Flas over dead end insulator @1 O/p 28 AG 15 Cause : Lightning |  | 1 | 14:31 | Afternoon | Sunday | 2019 | 2
10511 | 2019-02-17 16:26 | 2019-02-17 16:26 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified (Fuse) | 0 | Rangau fdr#2 Load dropped 141A (155-14A) not checked yet |  | 1 | 16:26 | Afternoon | Sunday | 2019 | 2
10512 | 2019-02-17 16:26 | 2019-02-19 13:07 | 13.8KV RANGAU FEEDER #2 | Cloudy | Unidentified (Fuse) | 0 | Checked & found Rangau Recl. 23-BD-01 T/R 1x, Ctr: 366-367, R/F: 51 Patrolled the Line found B/O @1 Fuse o/p 19-BA-63 at Well Jurong &38 Cause : Unidentified (Fuse) Date Patrol : 18-FEB-2019 |  | 1 | 16:26 | Afternoon | Sunday | 2019 | 2
10513 | 2019-02-17 16:52 | 2019-02-17 16:52 | 13.8KV MENGGALA FEEDER #1 | Heavy Rain | Tree | 71 | Menggala FDPC T/R 1x Menggala fdr#1 Load dropped 160A (207-47A) Not checked yet |  | 1 | 16:52 | Afternoon | Sunday | 2019 | 2
10514 | 2019-02-17 16:52 | 2019-02-19 20:20 | 13.8KV MENGGALA FEEDER #1 | Heavy Rain | Tree | 71 | Checked & found Menggala GFPC TX T/R 1x, Ctr: 085-086, R/F : None Patrolled the Line, found Hight trees at Menggala road Cause : Tree |  | 1 | 16:52 | Afternoon | Sunday | 2019 | 2
10515 | 2019-02-17 17:04 | 2019-02-17 17:04 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Tree | 88 | CKBS VCB feeder #5 T/R 1x. Not checked yet. |  | 1 | 17:04 | Afternoon | Sunday | 2019 | 2
10516 | 2019-02-17 17:04 | 2019-02-20 15:04 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Tree | 88 | Checked and found CKB VCB fdr #5 T/R 3x, ctr: 167-170, R/F: 51P @1 Patrolled the lines and found high palm tree, pole 36-CU-26 pole 36-CU-29 Cause : Tree |  | 1 | 17:04 | Afternoon | Sunday | 2019 | 2
10517 | 2019-02-17 17:19 | 2019-02-17 17:19 | 13.8KV NEW KOTABATAK FEEDER #4 | Rain and Lightning | Pin Insulator | 0 | NKB VCB fdr#4 T/R 1x not checked yet |  | 1 | 17:19 | Afternoon | Sunday | 2019 | 2
10518 | 2019-02-17 17:19 | 2019-02-20 14:59 | 13.8KV NEW KOTABATAK FEEDER #4 | Rain and Lightning | Pin Insulator | 0 | Checked and found NKB OCB fdr #4 T/R 2x, ctr: 284 - 286, R/F: 50N and 51V Patrolled the lines and found broken pin support @2 o/p 37-CV-23 and broken dead end insulator @2 o/p 37-CW-14 Cause : Pin Insulator |  | 1 | 17:19 | Afternoon | Sunday | 2019 | 2
10519 | 2019-02-17 17:19 | 2019-02-17 17:19 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 83 | OKB fdr#2 Load dropped 231A (285-53A) not checked yet |  | 1 | 17:19 | Afternoon | Sunday | 2019 | 2
10520 | 2019-02-17 17:19 | 2019-02-18 15:46 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 83 | Checked & found Recl. 38-CW-01 T/R 1x, Ctr: 118-119, R/F: none Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 17:19 | Afternoon | Sunday | 2019 | 2
10521 | 2019-02-17 17:19 | 2019-02-17 17:19 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 90 | CKBS VCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 17:19 | Afternoon | Sunday | 2019 | 2
10522 | 2019-02-17 17:19 | 2019-02-20 14:59 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Rain and Lightning | Lightning | 90 | Checked and found CKB VCB fdr #1 T/R 1x, ctr: 240-241, R/F: None Patrolled the lines and found flash over dead end @2 o/p 37-CW-19A and broken dead end insulator @2 o/p 36-CV-17 (LBS) Cause : Lightning |  | 1 | 17:19 | Afternoon | Sunday | 2019 | 2
10523 | 2019-02-18 09:35 | 2019-02-18 09:35 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Tree | 133 | CKBS 13.8KV VCB feeder #5 T/R 1x. Not checked yet. |  | 1 | 9:35 | Morning | Monday | 2019 | 2
10524 | 2019-02-18 09:35 | 22/02/2019 11:38 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Tree | 133 | Checked & found CKBS VCB fdr#5 T/R 1x, Ctr: 166-167, R/F: 51N Patrolled the Line, found high tree (sawit) touch the power line o/p 36-CU-27 Cause : Tree |  | 1 | 9:35 | Morning | Monday | 2019 | 2
10525 | 2019-02-19 08:14 | 2019-02-19 08:14 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 592 | 08:14 Kota Batak 13.8KV OCB feeder#2 T/LO, Ctr: 1353-1357, R/F: 51N Patrolled the Line, but Found nothing Manually Block & Closed OKB VCB fdr#2 but T/O again Opened Recl. 38 CW 08, 38 CX 25 and LBS 38 CW 23 Man Block & Closed OKB VCB fdr#2 but T/O again Open both Isolation Switch of OKB VCB fdr#2, and Disabled Relay 51N Manually Block & Closed OKB VCB fdr#2, Success. Found 51N relays Bad Contact, (still Touched contact after occur fault) Fixed & Reset the relay Contact, Closed back both isolation Switch VCB #2 14:38 Manually Block & Closed OKB VCB fdr#2, Success, then released the Block Closed Back LBS 38 CW23 Manually Block & Closed Recl 38 CW 08 & 38 CX 25, then released the Block Cause: Unidentified | 12345 | 1 | 8:14 | Morning | Tuesday | 2019 | 2
10526 | 2019-02-19 10:13 | 2019-02-19 10:13 | 13.8KV ROKAN FEEDER #3 | Fair | Planned Maintenance | 0 | Manually opened Rokan fdr#4. Cause: Planet maintenance. |  | 1 | 10:13 | Morning | Tuesday | 2019 | 2
10527 | 2019-02-19 14:41 | 2019-02-19 14:41 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Tree | 0 | 14:41 C.Duri 13.8KV ACB#23 fdr#6 T/LO, Ctr:487-493. R/F: 50 @3 Patrolled the Line, found Hight Tree touching Power Line O/p 01 03 01 15:29 Manually Block & Closed ACB fdr#6, after finished Cutted the Trees. Cause: Tree |  | 1 | 14:41 | Afternoon | Tuesday | 2019 | 2
10528 | 2019-02-20 00:13 | 2019-02-20 00:13 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | - | Duri Community ACB #26 (feeder #3) T/R 1x. Not checked yet. |  | 1 | 0:13 | Night | Wednesday | 2019 | 2
10529 | 2019-02-20 08:41 | 2019-02-20 08:41 | 13.8KV 5B FEEDER #5 | Fair | Lightning | 21 | 08:41 5B feeder #5 T/R 1x Not Checked Yet |  | 1 | 8:41 | Morning | Wednesday | 2019 | 2
10530 | 2019-02-21 08:46 | 2019-02-21 08:46 | 13.8KV CENTRAL DURI FEEDER #9 | Cloudy | Lightning | - | C.Duri 13.8KV ACB-41 feeder #9 T/R 1x R/F:51 @1&@2 Ctr:396-397. Not checked yet. |  | 1 | 8:46 | Morning | Thursday | 2019 | 2
10531 | 2019-02-21 10:04 | 2019-02-21 10:04 | 13.8KV 8D FEEDER #1 | Fair | Planned Maintenance | - | Manually open recloser 8E-05 D/S 8D feeder#1. Replaced @2 pin Insulator o/p 8E-136. 16Well off during the job. Cause:Plain maintenance. |  | 1 | 10:04 | Morning | Thursday | 2019 | 2
10532 | 2019-02-21 20:26 | 2019-02-21 20:26 | 13.8KV DARLING VCB FEEDER #4 | Fair | Animal | 0 | 20:26 Darling VCB fdr#4 T/R 1x It was reported, no Power at CSS area 6. Checked & found, @3 B/O fuse at 100KVATX and 112.5KVATX also found Dead Civet, below the TX 23:53 Replaced both b/o fuse, then energized the TX. Cause : Animal (CIVET) |  | 1 | 20:26 | Night | Thursday | 2019 | 2
10533 | 2019-02-22 03:51 | 2019-02-22 03:51 | NORTH DURI POWER PLANT |  |  | - | 03:51 S/U NDC#3, then on line the unit at 04:43. |  | 1 | 3:51 | Night | Friday | 2019 | 2
10534 | 2019-02-22 06:33 | 2019-02-22 06:33 | MINAS POWER PLANT |  |  | - | Off line MGT#1, then S/D the unit for S/B. |  | 1 | 6:33 | Morning | Friday | 2019 | 2
10535 | 2019-02-22 08:54 | 2019-02-22 08:54 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 0 | 08:54 Bangko fdr #4 lad dropped 100A (195-95A). Bangko GFPC T/R 1X. Not checked yet. |  | 1 | 8:54 | Morning | Friday | 2019 | 2
10536 | 2019-02-22 13:05 | 2019-02-22 13:05 | 115KV DURI - PUNGUT LINE | Fair | Unidentified | 0 | 13:05 Duri 115KV OCB #29 T/R 1X. Pungut 115KV OCB #21 T/R 1X. Not checked yet. |  | 1 | 13:05 | Afternoon | Friday | 2019 | 2
10537 | 2019-02-22 14:37 | 2019-02-22 14:37 | NORTH DURI POWER PLANT | Fair | Under investigation | 7 | 14:37 NDC CT #3 T/O on load 81.7MW (Running test after HGP). Frequency system dropped to 59.73Hzs. followed Load shedding level-1: 3D feeder #6 T/O, then closed at 14:40. 4D feeder #4 T/O, then closed at 14:41. 4D feeder #5 T/O, then closed at 14:41. Zamrud feeder #2 T/O, Closed at 14:42. Beruk feeder #2 T/O, Closed at 14:42. Cause: Under investigation. (Tubing connector ¾ “ hydraulic supply to CBV loss) |  | 1 | 14:37 | Afternoon | Friday | 2019 | 2
10538 | 2019-02-23 10:43 | 2019-02-23 10:43 | 13.8KV 8D FEEDER #1 | Fair | Planned Maintenance | 39 | 10:43 Manually open 8D feeder #1. Re installed 260KVA TX at well 8E-34 (reactive well). 11:10 Closed 8D feeder #1. Cause: Plan Maintenance. |  | 1 | 10:43 | Morning | Saturday | 2019 | 2
10539 | 2019-02-24 16:19 | 2019-02-24 16:19 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | - | 16:19 C.Duri 13.8Kv ACB-21 feeder#4 T/R 1x Ctr:516 - 617 R/F.51N 51@2. Not Checked yet. |  | 1 | 16:19 | Afternoon | Sunday | 2019 | 2
10540 | 2019-02-25 21:18 | 2019-02-25 21:18 | POWER GENERATION SHORTAGE | Fair | Construction Job | - | Perform Manual Load shedding, due to CoPi Gas Transmission Lines Leaks its causing to Reduce Power system Load and S/D some Generations 21:18 4D FDR#4---->21:18. 21:22 4D FDR#3 (+3D FDR#2) 21:25 5B FDR#4 (+3D FDR#4) 21:28 5B FDR#5 21:29 5B FDR#3 21:31 5B FDR#7 (+3D FDR#3) 21:32 8D FDR#3 21:33 5B FDR#1 21:35 4B FDR#1 Closed at 21:52 21:37 8C FDR#2 21:38 4D FDR#5 21:38 4D FDR#2 (+4D FDR#5) 21:40 8D FDR#1 21:18 6DN FDR#1 (+4D FDR#4) 21:35 3D FDR#4 (+4B FDR#1) 21:44 MINAS FDR#6 21:35 3D FDR#2 21:46 8C FDR#1 21:47 MINAS FDR#3 21:49 4B FDR#6 21:49 6D FDR#2 21:50 8D FDR#10 21:51 6DN FDR#6 21:52 4B FDR#2 Closed at 21:54 21:57 MINAS FDR#2 Closed at 22:59 21:57 8D FDR#5 21:59 MINAS FDR#1 22:01 8D FDR#11 22:02 3D FDR#8 Closed at 22:03 22:04 5B FDR#2 22:06 MINAS FDR#4 22:06 6D FDR#5 22:08 6DN FDR#5. 22:09 8C FDR#3 22:17 8D FDR#2 HO 22:19 C.DURI FDR#4 22:21 DURI FIELD FDR#2 22:22 DURI FIELD FDR#4 22:23 N.DURI FDR#6 22:27 C.DURI FDR#6 SLN 22:34 RANGAU FDR#2 22:36 KETIGUL FDR#3 22:37 PUNGUT FDR#2 22:38 ROKAN FDR#2 22:38 PINANG FDR#1 22:41 LIBO FDR#1 Closed at 22:53 22:44 PETANI FDR#2 22:46 KETIGUL FDR#1 22:48 NELLA FDR#2 22:49 BEKASAP FDR#6 23:01 SINTONG FDR#1 23:08 S.BEKASAP FDR#1 Closed at 00:12 23:09 PEMATANG FDR#2 23:17 Bangko fdr#1 23:19 BEKASAP FDR#2 Closed at 00:12 0:21 Shut Down Generator 21:12 MGT#7 Transfer to Distillate fuel 21:38 MGT#8 Transfer to Distillate fuel 21:52 MGT#9 Off line then S/D the Unit 22:09 MGT#10 Off line then S/D the Unit 22:25 MGT#5 Off line then S/D the Unit 23:20 MGT#6 Off line then S/D the Unit 02:02 MGT#6 S/U then On Line at 02:22 22:30 CGT#4 Off line then S/D the Unit 23:37 NDC#1 Off line then S/D the Unit 00:00 MGT#7 Transfer to Gas fuel 00:15 CGT#1 Off line then S/D the Unit 02:42 CGT#3 Off Line then S/D the Unit 02:31 MGT#7 Transfer to Distillate fuel 08:10 MGT#7 Transfer to Gas fuel 14:16 Closed Minas fdr #1 to rstore power to Fise Shop. 14:14 Open LBS M5-B5 15:12 MGT #6 Tripped Off while transfer to Distillate Fuel. Frequency system dropped to 59:61Hzs. 4B fdr #4 T/O, Closed at 15:33 3D fdr #6 T/O, Closed at 15:42. Bangko fdr #4 load dropped 97A (190-97A). Sintong fdr #6 load dropped 69A (190-121A). 15:27 MGT #6 Started Up and On line to the system at 15:45. |  | 1 | 21:18 | Night | Monday | 2019 | 2
10541 | 2019-02-25 21:18 | 2019-02-27 16:06 | POWER GENERATION SHORTAGE | Fair | Construction Job | - | Manually Closed Pematang Feeder#2 at 10:29 Manually Closed Ketigul Feeder#1 at 10:45 Manually Closed N Duri Feeder#1 at 11:02 Manually Closed D Field Feeder#2 at 11:11 Manually Closed Sintong Feeder#1 at 11:08 Manually Closed 4DFeeder#5 at 11:35 Manually Closed Nella Feeder#2 at 12:01 Manually Closed N Duri Feeder#7 at 12:02 Manually Closed Bekasap Feeder#6 at 12:08 Manually Closed Rokan Feeder#2 at 12:18 Manually Closed Pungut Feeder#2 at 12:22 Manually Closed Petani Feeder#2 at 12:54 Manually Closed Pinang Feeder#1 at 12:57 Manually Closed Ketigul Feeder#3 at 13:44 Manually Closed C.Duri Feeder#4 at 14:35 Manually Closed N.Duri Feeder#6 at 15:02 Manually Closed Bangko Feeder#1 at 15:17 Manually Closed 8D Feeder#11 at 15:32 Manually Closed 6DN Feeder#6 at 15:47 Manually Closed Minas Feeder#4 at 16:05 Manually Closed 3D Feeder#4 at 16:25 Manually Closed 8D Feeder#10 at 16:28 Manually Closed Rangau Feeder#2 at 16:30 Manually Closed Minas Feeder#3 at 16:38 Manually Closed C.Duri Feeder#6 at 17:40 Manually Closed Minas Feeder#1 at 14:03 10:07 S/U CDGT#3 and then O/Line the unit at 10:25 10:35 S/U HRSG Unit#3 and Inject steamat.11:10 17:00 S/U MGT#10 and then O/Line the unit at 17:15 13:53 S/U CDGT#1 and then O/Line the unit at 14:5 14:40 S/U HRSG Unit#1 and Inject steamat.15:00 17:53 S/U MGT#5 and then O/Line the unit at 18:06 |  | 1 | 21:18 | Night | Monday | 2019 | 2
10542 | 2019-02-25 21:18 | 2019-02-28 04:00 | POWER GENERATION SHORTAGE | Fair | Construction Job | - | 04:00 NDC CT #1 Started Up and On line to the system at 05:10. 06:26 Off line and then S/D MGT #7 for S/B. 10:57 Manually closed 8D OCB feeder #2. 11:39 Manually closed 6D OCB feeder #1. 14:21 Manually closed 6D OCB feeder #2. 17:23 Manually closed 4D OCB feeder #4 and 6DN feeder #1. 17:26 Manually closed 3D OCB feeder #2. 17:27 Manually closed 6D OCB feeder #5. |  | 1 | 21:18 | Night | Monday | 2019 | 2
10543 | 2019-02-25 21:18 | 2019-01-03 03:38 | POWER GENERATION SHORTAGE | Fair | Construction Job | - | 03:38 Manual Closed 8D feeder #1. 03:39 Manual Closed 8D feeder #3. 03:40 Manual Closed 8D feeder #5. 03:44 Manual Closed 5B feeder #1. 03:44 Manual Closed 5B feeder #2. 03:48 Manual Closed 5B feeder #3. 03:49 Manual Closed 5B feeder #5. 03:50 Manual Closed 3D feeder #3. 03:50 Manual Closed 4B feeder #6. 03:54 Manual Closed 6DN feeder #5. 14:28 S/U MGT#6 and then online the unit at 14:51. 17:15 S/U MGT#9 and then online the unit at 17:30. 17:43 Manually closed 8C feeder #1. 18:16 S/U NDC#3 and then online the unit at 18:56. 18:59 Manually closed 8C feeder #2. 19:00 Closed 230KV GCB #3. 20:40 Manual Closed feeder to BOB (LUKUT). |  | 1 | 21:18 | Night | Monday | 2019 | 2
10544 | 2019-02-25 21:18 | 2019-02-03 10:22 | POWER GENERATION SHORTAGE | Fair | Construction Job | - | 10:22 Manually closed 8C feeder #3. |  | 1 | 21:18 | Night | Monday | 2019 | 2
10545 | 2019-02-26 15:12 | 2019-02-26 15:12 | MINAS POWER PLANT |  |  | - | 15:12 MGT #6 Tripped Off while Fuel transfer to Dist. Frequency system dropped to 59:61Hzs. 4B fdr #4 T/O, Closed at 15:33. 3D fdr #6 T/O, Closed at 15:42. Bangko fdr #4 load dropped 97A (190-97A). Sintong fdr #6 load dropped 69A (190-121A). 15:27 MGT #6 Started Up and On line to the system at 15:45. 21:55 MGT #6 Off Line & S/D for S/B |  | 1 | 15:12 | Afternoon | Tuesday | 2019 | 2
10546 | 2019-02-26 16:21 | 2019-02-26 16:21 | 13.8KV MINAS FEEDER #5 | Fair | Unidentified | - | 16:21 Minas 13.8KV ACB fdr #5 T/O (on block HLT) ctr:92-93 R/F: 50@1. Patrolled the lione bur found nothing. 17:45 Block and closed Minas fdr #5. Ok, then released the block. Cause: unidentified. |  | 1 | 16:21 | Afternoon | Tuesday | 2019 | 2
10547 | 2019-02-26 17:02 | 2019-02-26 17:02 | CENTRAL DURI POWER PLANT |  |  | - | 17:02 CGT #2 S/U and On line to the system at 17:29. CGT #2 running on Gas Dest. Fuel. |  | 1 | 17:02 | Afternoon | Tuesday | 2019 | 2
10548 | 2019-02-26 23:05 | 2019-02-26 23:05 | 8 CHARLIE SUBSTATION | Rain and Lightning | Transformer Failure | - | 23:05 8C 115KV C/S for TX#2 T/O 01:45 Checked & found 8C TX#2 R/F: 86 HR 01:50 Manually opened 8C fdr#4,#5, #6 Opened Isolation Switch Load side 8C fdr#1,#2,#3 01:55 Opened Isolation Switch VR TX#2 02:02 Closed LBS Tie Bus #1-2 02:05 Manually Block & Closed 8C VCB fdr#6, #5, #4, then released the block Cause: Transformer Failure |  | 1 | 23:05 | Night | Tuesday | 2019 | 2
10549 | 2019-02-26 23:05 | 2019-02-26 23:05 | MINAS SWITCH YARD | Rain and Lightning | Under investigation | - | 23:05 Minas TX #3 T/O Minas ACB #23 T/O Mnsy 115KV OCB #23, and #24 T/O Minas 13.8KV ACB #16 T/O (Tie Bus 1,3) 23:30 Checked & found MNS TX#3 R/F: 86HR 00:04 Manually Opened ACB #17 fdr #5 00:05 Manually Opened ACB #18 fdr #6 00:07 Manually Closed 13.8KV ACB #16 Tie Bus to Energized 44KV Line to Rumbai 01:00 Opened both side Isolation Switch & Line Switch Minas TX#3 Closed Grounding Switch of Minas TX#3 for trouble shooting 01:10 Manually Closed Minas 115KV OCB #23, and #24, to Put on ring system Cause: Under investigation |  | 1 | 23:05 | Night | Tuesday | 2019 | 2
10550 | 2019-02-27 10:07 | 2019-02-27 10:07 | CENTRAL DURI POWER PLANT |  |  | - | 10:07 S/U CDGT #3 and then Online the unit at 10:25. 10:35 S/U HRSG and then inject steam at 11:10. |  | 1 | 10:07 | Morning | Wednesday | 2019 | 2
10551 | 2019-02-27 13:53 | 2019-02-27 13:53 | CENTRAL DURI POWER PLANT |  |  | - | 13:53 S/U CDGT #1 and then Online the unit at 14:15. 14:30 S/U HRSG and then inject steam at 15:00. |  | 1 | 13:53 | Afternoon | Wednesday | 2019 | 2
10552 | 2019-02-27 14:20 | 2019-02-27 14:20 | 13.8KV DURI FIELD FEEDER #2 | Fair | Unidentified | - | 14:20 It was reported no power on pole 07-U1-15 D/S D Field feeder #2. 15:44 Checked and found Recloser: 07-U1-19 T/LO Counter: 63-67. Patrolled the line found nothing. 15:53 Blocked and closed Recloser: 07-U1-19 --> Ok and then released the block. Cause: Unidentified. |  | 1 | 14:20 | Afternoon | Wednesday | 2019 | 2
10553 | 2019-02-27 17:00 | 2019-02-27 17:00 | MINAS POWER PLANT |  |  | - | 17:00 S/U MGT #10 and then Online the unit at 17:15. |  | 1 | 17:00 | Afternoon | Wednesday | 2019 | 2
10554 | 2019-02-27 17:05 | 2019-02-27 17:05 | MINAS POWER PLANT | Fair | Under investigation | - | 17:05 MGT #9 Trip by Alarm Exhaust spread temperature high. Freq: 59:51. Respectively: 1. 4D OCB feeder #5 trip Closed at 18:22. 2. 3D OCB feeder #6 trip Closed at 18:22. Cause: Under investigation. |  | 1 | 17:05 | Afternoon | Wednesday | 2019 | 2
10555 | 2019-02-27 17:53 | 2019-02-27 17:53 | MINAS POWER PLANT |  |  | - | 17:53 S/U MGT #5 Online the unit at 18:06. |  | 1 | 17:53 | Afternoon | Wednesday | 2019 | 2
10556 | 2019-02-28 04:00 | 2019-02-28 04:00 | NORTH DURI POWER PLANT |  |  | - | 04:00 NDC CT #1 Started Up and On line to the system at 05:10. |  | 1 | 4:00 | Morning | Thursday | 2019 | 2
10557 | 2019-02-28 06:26 | 2019-02-28 06:26 | MINAS POWER PLANT |  |  | - | 06:26 Off line and then S/D MGT #7 for S/B. |  | 1 | 6:26 | Morning | Thursday | 2019 | 2
10558 | 2019-02-28 11:25 | 2019-02-28 11:25 | 13.8KV KOTABATAK FEEDER #2 | Fair | Planned Maintenance | 0 | 11:25 Manually open Recloser: 40-CY-16. For replacing 55 Pcs Pin to Pin Post insulator. 16:15 Manually blocked and closed Recloser: 40-CY-16. and then released the block. Cause: Plan maintenance. |  | 1 | 11:25 | Morning | Thursday | 2019 | 2
10559 | 2019-02-28 15:17 | 2019-02-28 15:17 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 0 | 15:17 Open fuse of 112,5 Kva Tx on pole 09-L5-10 D/S CD feeder #1. For replacing @1,2,3 broken Lightning arrester on pole 09-L5-10. 15:50 Closed fuse of 112,5 Kva Tx on pole 09-L5-10. Cause: Plan maintenance. |  | 1 | 15:17 | Afternoon | Thursday | 2019 | 2
10560 | 2019-01-03 07:15 | 2019-01-03 07:15 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Pin Insulator | 0 | Duri field VCB#41 feeder#1 T/R 1x. Not checked yet. |  | 1 | 7:15 | Morning | Thursday | 2019 | 1
10561 | 2019-01-03 14:28 | 2019-01-03 14:28 | MINAS POWER PLANT |  |  | 0 | 14:28 S/U MGT#6 and then online the unit at 14:51. |  | 1 | 14:28 | Afternoon | Thursday | 2019 | 1
10562 | 2019-01-03 17:15 | 2019-01-03 17:15 | MINAS POWER PLANT |  |  | 0 | 17:15 S/U MGT#9 and then online the unit at 17:30. |  | 1 | 17:15 | Afternoon | Thursday | 2019 | 1
10563 | 2019-02-03 01:30 | 2019-02-03 01:30 | 13.8KV 8C FEEDER #1 | Fair | Pin Insulator | 32 | 01:30 8C 13.8KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 1:30 | Night | Sunday | 2019 | 2
10564 | 2019-02-03 01:30 | 2019-05-03 10:30 | 13.8KV 8C FEEDER #1 | Fair | Pin Insulator | 32 | Checked & found 89C VCB fdr#1 T/R 4x, Ctr: 683-687, R/F: 51 @1,2 Patrolled the Line, found @1,2 broken Pin Insulator O/P 9D-37 Cause : Pin Insulator |  | 1 | 1:30 | Night | Sunday | 2019 | 2
10565 | 2019-02-03 08:06 | 2019-02-03 08:06 | 13.8KV NORTH DURI FEEDER #8 | Cloudy | Unidentified | 0 | N.Duri VCB feeder #8 T/R 1x. Not checked yet. |  | 1 | 8:06 | Morning | Sunday | 2019 | 2
10566 | 2019-02-03 09:34 | 2019-02-03 09:34 | 13.8KV PETANI FEEDER #2 | Fair | Construction Job | 0 | 09:34 Manually open Petani OCB fdr#2. Due to repair 30" out going line to wash tank at Petani. 12:20 Block and closed Petani OCB feeder #2. and then released the block. Cause: Construction job. |  | 1 | 9:34 | Morning | Sunday | 2019 | 2
10567 | 2019-02-03 09:51 | 2019-02-03 09:51 | 13.8KV PETANI FEEDER #1 | Fair | Construction Job | 0 | 09:51 Manually open Petani OCB feeder#1. Due to repair 30" out going line to wash tank at Petani. 12:44 Block and closed Petani OCB feeder#1. and then released the block. Cause: Construction job. |  | 1 | 9:51 | Morning | Sunday | 2019 | 2
10568 | 2019-02-03 16:50 | 2019-02-03 16:50 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 0 | Ketigul feeder#2 load dropped 172A (247-75A). Not checked yet. |  | 1 | 16:50 | Afternoon | Sunday | 2019 | 2
10569 | 2019-02-03 16:50 | 2019-07-03 19:28 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 0 | Checked and found Ketigul VCB feeder #2 T/R 1x Counter: 165-166 R/F:51N Patrolled the line found Recloser: 29-AL-03 T/R 1x Counter: Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 16:50 | Afternoon | Sunday | 2019 | 2
10570 | 2019-02-03 21:19 | 2019-02-03 21:19 | 13.8KV PETANI FEEDER #1 | Cloudy | Under investigation | 366 | 21:19 Petani fdr #1 load dropped 155A (184-29A). Petani fdr #2 load dropped 119A (131-12A). 22:00 Manually Open Petani fdr #2. 23:31 Manually Open Rokan fdr #2. 23:35 Checked and found @3 b/o fuse for 10MVA TX at Petani Sub R/F: NA. (The TX Unbalance). 23:42 Manually Open Petani fdr #1. 24:00 Manually Open 44KV Pematang Main OCB #1. On March 03, 2019 01:45 Replaced @3 b/o fuse above and Closed 44KV Pematang Main OCB #1, OK. 01:50 Closed Petani fdr #1. 02:18 Closed Rokan fdr #2. 02:36 Closed Petani fdr #6. Cause: Under investigation. Production Loss: Petani fdr #1 : 27 Bbls / 16 Wellls. Petani fdr #2 : 321 Bbls / 37 Wellls. Rokan fdr #2 : 27 Bbls / 16 Wellls. -------------------------------------------+ Total : 366 Bbls / 60 Wells. |  | 1 | 21:19 | Night | Sunday | 2019 | 2
10571 | 2019-03-03 11:30 | 2019-03-03 11:30 | MINAS POWER PLANT |  |  | 0 | 11:30 Offline MGT #6 and then S/D the unit for S/B. |  | 1 | 11:30 | Morning | Sunday | 2019 | 3
10572 | 2019-03-03 16:00 | 2019-03-03 16:00 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Unidentified | 84 | Checked & found Bekasap VCB fdr #6 T/R 3x, Ctr: 372-375 R/F: 50 @1 Patrolled the Line, but found nothing. Cause: Unidentified |  | 1 | 16:00 | Afternoon | Sunday | 2019 | 3
10573 | 2019-03-03 16:00 | 2019-03-03 16:00 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Unidentified | 84 | Bekasap ACB feeder#6 T/R 1x. Bekasap feeder#5 load dropped 195A (200-5A). Bekasap feeder#3 load dropped 90A (92-2A). Not checked yet. 16:14 Manually opened Bekasap ACB feeder#6. Due to WIP trip. |  | 1 | 16:00 | Afternoon | Sunday | 2019 | 3
10574 | 2019-03-03 17:21 | 2019-03-03 17:21 | 13.8KV 8D FEEDER #2 | Cloudy | Lightning | 377 | 8D OCB feeder#2 T/R 1x. Not checked yet. |  | 1 | 17:21 | Afternoon | Sunday | 2019 | 3
10575 | 2019-03-03 17:21 | 2019-06-03 17:21 | 13.8KV 8D FEEDER #2 | Cloudy | Lightning | 377 | Checked & found 8D vcb fdr#2 T/R 2x, Ctr: 283-285, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 17:21 | Afternoon | Sunday | 2019 | 3
10576 | 2019-04-03 06:10 | 2019-04-03 06:10 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning | 40 | Sintong 13.8KV VCB fdr #2 T/R 1X. Sintong GFPC T/R 1X. Not checked yet. |  | 1 | 6:10 | Morning | Wednesday | 2019 | 4
10577 | 2019-04-03 06:10 | 2019-07-03 21:21 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning | 40 | Checked and found Sintong 13.8KV VCB feeder #2 T/R 1X. Counter: 488-489 R/F: 51N. Patrolled the line found @2 Flash over dead end insulator on pole 27-AF-82. Cause: Dead end Insulator. |  | 1 | 6:10 | Morning | Wednesday | 2019 | 4
10578 | 2019-04-03 13:50 | 2019-04-03 13:50 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 112 | 13:50 4B VCB feeder #1 T/O 14:54 Checked and found 4B VCB feeder #1 T/O. Counter: 342-345, R/F: 51 @2 @3. Patrolled the line found nothing. 15:46 Manually block and closed 4B VCB feeder #1 -->but failed. Re patrolled the line found nothing. 17:15 Manually open Recloser: 4B-101. 18:15 Manually block and closed 4B VCB feeder #1 --> Success. 18:25 Manually block and closed Recloser: 4B-101 --> Success. Re patrolled yet. |  | 1 | 13:50 | Afternoon | Wednesday | 2019 | 4
10579 | 2019-04-03 13:50 | 2019-07-03 19:34 | 13.8KV 4B FEEDER #1 | Fair | Unidentified | 112 | Checked and found 4B OCB feeder #1 T/SO. Counter: 342-345, R/F: 51 @2 @3. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 13:50 | Afternoon | Wednesday | 2019 | 4
10580 | 2019-05-03 12:49 | 2019-05-03 12:49 | 13.8KV 3D FEEDER #4 | Fair | Unidentified | 119 | 12:49 3D OCB feeder#4 T/O. 14:42 Checked and found 3D OCB feeder#4 T/LO. Counter: 634-640 R/F: 50@2,@3. Patrolled the line found Recloser: 2D-14 Open. Counter: Do not change. Patrolled the line down stream Recloser: 2D-14 found nothing. 15:20 Manually block and closed 3D OCB feeder#4 --> Success. 15:34 Manually block and closed Recloser: 2D-14 --> Success. Cause: Unidentified. |  | 1 | 12:49 | Afternoon | Friday | 2019 | 5
10581 | 2019-05-03 12:49 | 2019-05-03 12:49 | 13.8KV 3D FEEDER #2 | Fair | Unidentified | 52 | 3D feeder #2 load dropped 97A (163-66). Not checked yet. |  | 1 | 12:49 | Afternoon | Friday | 2019 | 5
10582 | 2019-05-03 12:49 | 2019-10-03 06:44 | 13.8KV 3D FEEDER #2 | Fair | Unidentified | 52 | Checked and found 3D feeder #2 Breaker and Recloser Normal condition. Cause: Unidentified. |  | 1 | 12:49 | Afternoon | Friday | 2019 | 5
10583 | 2019-05-03 12:49 | 2019-05-03 12:49 | 13.8KV 3D FEEDER #3 | Fair | Unidentified | 37 | 3D feeder #3 load dropped 75A (128-53A). Not checked yet. |  | 1 | 12:49 | Afternoon | Friday | 2019 | 5
10584 | 2019-05-03 12:49 | 2019-10-03 06:48 | 13.8KV 3D FEEDER #3 | Fair | Unidentified | 37 | Checked and found 3D feeder #2 Breaker and Recloser Normal condition. Cause: Unidentified. |  | 1 | 12:49 | Afternoon | Friday | 2019 | 5
10585 | 2019-05-03 18:06 | 2019-05-03 18:06 | MINAS POWER PLANT |  |  | 0 | Minas Gas Turbine #7 Trip by alarm gas scrubber liquid level high. |  | 1 | 18:06 | Afternoon | Friday | 2019 | 5
10586 | 2019-05-03 18:30 | 2019-05-03 18:30 | MINAS POWER PLANT |  |  | 0 | 18:30 S/U MGT #7 and then Online the unit at 18:45. |  | 1 | 18:30 | Afternoon | Friday | 2019 | 5
10587 | 2019-06-03 06:03 | 2019-06-03 06:03 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | N Duri 13.8KV VCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 6:03 | Morning | Monday | 2019 | 6
10588 | 2019-06-03 06:03 | 2019-10-03 04:51 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | Checked & found, N.Duri VCB fdr#1 T/R 2x, Ctr: 301-303, R/F: 51 @1,2 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 6:03 | Morning | Monday | 2019 | 6
10589 | 2019-06-03 10:51 | 2019-06-03 10:51 | MINAS POWER PLANT |  |  | 0 | 10:51 S/U MGT#6, the on lune the unit at 11:12. |  | 1 | 10:51 | Morning | Monday | 2019 | 6
10590 | 2019-06-03 11:15 | 2019-06-03 11:15 | CENTRAL DURI POWER PLANT |  |  | 0 | Off line CGT#4, then S/D the unit for S/B. |  | 1 | 11:15 | Morning | Monday | 2019 | 6
10591 | 2019-06-03 22:00 | 2019-06-03 22:00 | 13.8KV LIBO FEEDER #2 | Fair | Unidentified | 0 | 22:00 It was reported no power at wells Gading #1 , #2 , Ami and Asih. D/S Pungut #2. 23:44 Checked and found Recloser: 44-BX-06 T/SO Counter: 379-380. Patrolled the line found nothing. 23:55 Manually block and closed Recloser: 44-BX-06 --> Success. and then released the block. Cause: Unidentified. |  | 1 | 22:00 | Night | Monday | 2019 | 6
10592 | 2019-07-03 09:19 | 2019-07-03 09:19 | MINAS POWER PLANT |  |  | 0 | Off line MGT#6, then S/D the unit for S/B. |  | 1 | 9:19 | Morning | Wednesday | 2019 | 7
10593 | 2019-07-03 10:15 | 2019-07-03 10:15 | 13.8KV RANGAU FEEDER #2 | Fair | Planned Maintenance | 31 | 10:15 Manually Open Recloser: 23-BD-01 D/S Rangau feeder#2. Replaced burnt out fuse for 25KVa Tx at Ferry Jurong. 11:00 Blocked & closed Recloser: 23-BD-01, then release the block. Cause: Maintenance Plan. |  | 1 | 10:15 | Morning | Wednesday | 2019 | 7
10594 | 2019-07-03 17:28 | 2019-07-03 17:28 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Lightning | 50 | Petapahan fdr#6 T/R 1x. Not checked yet. |  | 1 | 17:28 | Afternoon | Wednesday | 2019 | 7
10595 | 2019-07-03 17:28 | 2019-10-03 16:10 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Lightning | 50 | Checked & found, Petapahan VCB fdr#6 T/R 1x, Ctr: 370-371, R/F: 51 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 17:28 | Afternoon | Wednesday | 2019 | 7
10596 | 2019-08-03 06:18 | 2019-08-03 06:18 | 13.8KV DURI FIELD FEEDER #1 | Heavy Rain | Lightning Arrester | 0 | D Field VCB #41 (feeder #1) T/R 1x. Not checked yet. |  | 1 | 6:18 | Morning | Saturday | 2019 | 8
10597 | 2019-08-03 06:18 | 2019-10-03 16:50 | 13.8KV DURI FIELD FEEDER #1 | Heavy Rain | Lightning Arrester | 0 | Checked & found, Dfield ACB fdr#1 T/R 1x, Ctr: 700-701 Patrolled the Line, found @3 Broken LA at LBS . 01-7-32 Cause : Lightning Arrester |  | 1 | 6:18 | Morning | Saturday | 2019 | 8
10598 | 2019-08-03 07:14 | 2019-08-03 07:14 | 13.8KV LIBO FEEDER #1 | Cloudy | Animal | 9 | Libo VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 7:14 | Morning | Saturday | 2019 | 8
10599 | 2019-08-03 13:47 | 2019-08-03 13:47 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | 13:47 C.Duri ACB fdr#6 T/LO Ctr:497-501 R/F 51@1. Patrolled the line but found nothing. 14:32 Blocked & closed C.Duri ACB fdr#6, then release the block. Cause: Unidentified. |  | 1 | 13:47 | Afternoon | Saturday | 2019 | 8
10600 | 2019-08-03 16:15 | 2019-08-03 16:15 | MINAS POWER PLANT |  |  | 0 | 16:15 S/U MGT#6, then on line the unit at 16:30. |  | 1 | 16:15 | Afternoon | Saturday | 2019 | 8
10601 | 2019-09-03 14:09 | 2019-09-03 14:09 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Planned Maintenance | 0 | 14:09 Manually open LBS 5N-01 (Duri comy fdr#3.) Trimming danger trees at dempo. 16:05 Manually closed LBS 5N-01. Cause: Planned maintenance. |  | 1 | 14:09 | Afternoon | Tuesday | 2019 | 9
10602 | 2019-09-03 14:55 | 2019-09-03 14:55 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Tree | 0 | Duri-comy 13.8KV ACB#25 fdr#1 T/R 1x. Not checked yet. |  | 1 | 14:55 | Afternoon | Tuesday | 2019 | 9
10603 | 2019-09-03 16:11 | 2019-09-03 16:11 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 99 | So.Balam VCB feeder #4 T/R 1x. So Balam GFPC T/R. So.Balam feeder #! load dropped 49A (140-91A). So.Balam feeder #2 load dropped 90A (99-9A).WIP So.Balam feeder #3 load dropped 100A (102-2A).WIP Not checked yet. |  | 1 | 16:11 | Afternoon | Tuesday | 2019 | 9
10604 | 2019-09-03 16:11 | 2019-11-03 17:28 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 99 | Checked & found S.Balam VCB fdr#4 T/R 1x, Ctr: 365-366, R/F: 51N Patrolled the Line, found @3 Broken L/A On terminal Pole Well Balam #205 Cause : Lightning |  | 1 | 16:11 | Afternoon | Tuesday | 2019 | 9
10605 | 2019-09-03 18:01 | 2019-09-03 18:01 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Broken Fuse Holder | 48 | So.Bekasap VCB feeder#1 T/R 1x. Not checked yet. |  | 1 | 18:01 | Afternoon | Tuesday | 2019 | 9
10606 | 2019-09-03 19:00 | 2019-09-03 19:00 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 25 | 19:00 6DN feeder#1 T/R 1x. 19:23 6DN feeder #1 T/R 1x again. Not checked yet. |  | 1 | 19:00 | Night | Tuesday | 2019 | 9
10607 | 2019-09-03 19:00 | 2019-09-03 19:00 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Unidentified | 74 | 6DN fdr#2 Load dropped 132A (162-130A). Not checked yet. |  | 1 | 19:00 | Night | Tuesday | 2019 | 9
10608 | 2019-09-03 19:00 | 18/03/2019 09:07 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Unidentified | 74 | Checked and found RCL 6D-200 T/R 1x, ctr: 17 - 18, R/F: none Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 19:00 | Night | Tuesday | 2019 | 9
10609 | 2019-09-03 19:11 | 2019-09-03 19:11 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 120 | 3D OCB feeder #3 T/O. Not patrolled yet. |  | 1 | 19:11 | Night | Tuesday | 2019 | 9
10610 | 2019-09-03 19:11 | 2019-11-03 23:07 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 120 | Checked and found 3D OCB fdr#3 T/O Ctr:453-454 R/F: 51@1,2,3. Patrolled the line found nothing. Cause: Suspected Lightning. |  | 1 | 19:11 | Night | Tuesday | 2019 | 9
10611 | 2019-09-03 19:14 | 2019-09-03 19:14 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Lightning | 57 | 3D OCB feeder #2 T/R 1x. Not patrolled yet. |  | 1 | 19:14 | Night | Tuesday | 2019 | 9
10612 | 2019-09-03 19:17 | 2019-09-03 19:17 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 307 | 4D OCB fdr#2 T/O. Not checked yet. |  | 1 | 19:17 | Night | Tuesday | 2019 | 9
10613 | 2019-09-03 19:17 | 2019-09-03 19:17 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 90 | 4D OCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 19:17 | Night | Tuesday | 2019 | 9
10614 | 2019-09-03 19:19 | / | 13.8KV 5B FEEDER #8 | Rain and Lightning | Lightning | 0 | - |  | 1 | 19:19 | Night | Tuesday | 2019 | 9
10615 | 2019-09-03 19:23 | 2019-09-03 19:23 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Unidentified | 41 | 6DN OCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 19:23 | Night | Tuesday | 2019 | 9
10616 | 2019-09-03 19:23 | 18/03/2019 09:00 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Unidentified | 41 | Checked and found OCB fdr #1 T/R 3x, ctr: 161 - 164, R/F: 51P @2, @3 Patrolled the lines but found nothing. Cause : Unidentified |  | 1 | 19:23 | Night | Tuesday | 2019 | 9
10617 | 2019-09-03 19:36 | 2019-09-03 19:36 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Powerline - Jumper | 94 | 19:36 4B feeder #1 T/O. Checked and found 4B feeder #1 T/LO, Ctr:354-358, R/f:51@1,@2,@3,51N. 23:00 Patrolled the line found broken jumper towards location 4A-62. |  | 1 | 19:36 | Night | Tuesday | 2019 | 9
10618 | 2019-09-03 19:38 | 2019-09-03 19:38 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 79 | 4B OCB fdr#5 T/O. Ctr:152-169, R/f:51@1,51N. Not Patrolled yet. |  | 1 | 19:38 | Night | Tuesday | 2019 | 9
10619 | 2019-09-03 19:38 | 2019-11-03 23:11 | 13.8KV 4B FEEDER #5 | Rain and Lightning | Lightning | 79 | Checked and found 4B OCB fdr#5 T/LO Ctr:152-169 R/F: 51@1,51N. Patrolled the line found @3 broken dead end insulator on pole 4B-147. Cause: Broken dead end Insulator. |  | 1 | 19:38 | Night | Tuesday | 2019 | 9
10620 | 2019-09-03 19:40 | 2019-09-03 19:40 | 5 BRAVO SUBSTATION | Rain and Lightning | Lightning | 930 | 19:40 115 KV KBJ-5B Line. * 115 KV 5B GCB #22 T/O . Ctr: * 115 KV KBJ GCB #21 T/O . Ctr: 203-204, R/F: 21G @3 * 115 KV KBJ GCB #23 T/O . Ctr: 218-219, R/F: 67L @3 115 KV 4B-5B Line. * 115 KV 4B GCB #22 T/R 1x . Ctr: 314-315 * 115 KV 5B GCB #21 T/R 1x . Ctr: 2945-2946, R/F: 87L * 115 KV 5B GCB #26 T/O . Ctr: Close GS Bbls Wells. 19:40 8D Fdr#1 T/O, Ctr: 319-320, R/F: N.A 23:02. GS-1. 86 19 8D Fdr#3 T/O, Ctr: 232-233, R/F: N.A 23:28 93 23 8D Fdr#10 T/O, Ctr: 263-264, R/F: N.A 21:18 57 27 8D Fdr#11 T/O, Ctr: 923-924, R/F: N.A 23:16 209 31 8C Fdr#1 T/O, Ctr: 687-688, R/F: N.A 21:53 78 23 8C Fdr#4 T/O, Ctr: 622-623, R/F: N.A 21:19 WIP 8C Fdr#5 T/O, Ctr: 533-534, R/F: N.A 21:21 WIP 5B Fdr#1 T/O, Ctr: 263-264, R/F: N.A 21:57 46 11 5B Fdr#2 T/O, Ctr: 417-418, R/F:51@123. 22:08 131 27 5B Fdr#3 T/O, Ctr: 405-406, R/F: N.A 21:56 31 8 5B Fdr#5 T/O, Ctr:305-307, R/F:51@1,51N. 0:23 37 8 19:45 4D Fdr#4 M/O, 23:19 GS-4 93 15 19:47 8C Fdr#2 M/O, 21:51 GS-1 41 9 19:47 8C Fdr#3 M/O, 21:51 GS-1 77 15 19:59 3D Fdr#4 T/R, GS-5 0 0 20:16 6D Fdr#2 M/O, 21:42 GS-4 3 14 20:21 6D Fdr#5 M/O, 22:32 GS-4 47 19 20:49 6DN Fdr#1 M/O 21:30 GS-4 21:14 Mns Fdr#3 M/O 22:13 GS-2 42 33 21:14 Mns Fdr#4 M/O 22:11 GS-2 46 29 21:23 6D Fdr#4 T/O, Ctr: 560-563, R/F:N.A. 23:58 GS-4 WIP 21:31 Checked and found: 115 KV 5B GCB #22 T/O, Ctr: 21:41 115 KV KBJ GCB #21 T/O, Ctr: 203-204 21:43 115 KV KBJ GCB #23 T/O, Ctr: 218-219 21:43 R/F: 21G @3 , 67N @3 , L90: Neutral - Ground @3. --------------------------------------------------------------------------------------------- 19:17 4B fdr #3 Transfer to 4B fdr #4 GS-6 22 4 19:19 4B fdr #2 "Load dropped 19A (45-26A) GS-6 80 10 19:17 4D Fdr#2 T/O 23:59 GS-5 231 24 19:17 4D Fdr#3 T/R GS-5 19:13 3D Fdr#2 T/R GS-4 19:19 5B Fdr#8 T/R GS-4 19:23 6DN Fdr#1 T/R GS-4 8 7 19:36 4B Fdr#1 T/O 1:52 GS-6 122 24 19:38 4B Fdr#5 T/O 1:49 GS-6 WIP 19:11 3D Fdr#3 T/O 0:39 GS-5 145 21 --------------------------------------------------------------------------------- Grand Total 1634 366. Cause: Under investigation. | 1234 | 1 | 19:40 | Night | Tuesday | 2019 | 9
10621 | 2019-09-03 19:40 | 18/03/2019 09:15 | 5 BRAVO SUBSTATION | Rain and Lightning | Lightning | 930 | Checked & found 5B-115KV OCB#21 T/R 1x, Ctr: 2945-2946, R/F: 87G 5B- 115KV OCB#22 T/R 1x, Ctr: 314-315, R/F: None Patrolled the Line found, @3 Broken Dead end o/p K5B 02 Cause : Lightning | 1234 | 1 | 19:40 | Night | Tuesday | 2019 | 9
10622 | 2019-10-03 07:53 | 2019-10-03 07:53 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Lightning | 0 | Duri Community fdr#3 T/R 1x. Not checked yet. |  | 1 | 7:53 | Morning | Thursday | 2019 | 10
10623 | 2019-10-03 07:53 | 15/03/2019 10:52 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Lightning | 0 | Checked and found DCM VCB fdr #3 T/R 1x, ctr: 88 - 89, R/F 51P @2 Patrolled the line and found broken pin insulator @2 o/p 4-DD-58 Cause : Lightning |  | 1 | 7:53 | Morning | Thursday | 2019 | 10
10624 | 2019-10-03 11:22 | 2019-10-03 11:22 | 13.8KV 4B FEEDER #1 | Fair | Planned Maintenance | 93 | 11:22 Manually Opened 4B fdr#1. Repaired Broken Conductor near well 4A-62. 15:03 Blocked & closed 4B fdr#1, then release the block. Cause: Plan Maintenance. |  | 1 | 11:22 | Morning | Thursday | 2019 | 10
10625 | 2019-11-03 11:40 | 2019-11-03 11:40 | 13.8KV 4B FEEDER #1 | Fair | Lightning | 6 | 11:40 It was reported no power D/S 4b feeder#1. 12:05 Checked & found Recl. 3B-18 T/O Ctr:81-82. Blocked & closed Recl. 3B-18, then release the block. Not patrolled yet. |  | 1 | 11:40 | Morning | Sunday | 2019 | 11
10626 | 2019-11-03 11:40 | 18/03/2019 09:21 | 13.8KV 4B FEEDER #1 | Fair | Lightning | 6 | Checked and found RCL 3B-18 T/O, ctr: 81-82, R/F: none Patrolled the line but found nothing. Cause : Lightning |  | 1 | 11:40 | Morning | Sunday | 2019 | 11
10627 | 2019-11-03 20:54 | 2019-11-03 20:54 | 13.8KV ROKAN FEEDER #2 | Cloudy | Tree | 14 | Rokan VCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 20:54 | Night | Sunday | 2019 | 11
10628 | 2019-11-03 20:54 | 16/03/2019 17:04 | 13.8KV ROKAN FEEDER #2 | Cloudy | Tree | 14 | Checked & found, Rokan VCB fdr#2 T/R 1x, Ctr: 1284-1285, RF: 51 @1 Patrolled the Line, High tree (palm) O/P 30 VA 27-28 Cause : Tree |  | 1 | 20:54 | Night | Sunday | 2019 | 11
10629 | 2019-12-03 | 2019-12-03 | CPI POWER SYSTEM |  |  | 0 | CPI Power System Normal Condition. |  | 1 | 0:00 | Night | Tuesday | 2019 | 12
10630 | 2019-03-13 16:54 | 2019-03-13 16:54 | 13.8KV LIBO FEEDER #2 | Heavy Rain | Lightning | 0 | Libo fdr#2 Load dropped 56A (60-4A). Not checked yet. |  | 1 | 16:54 | Afternoon | Wednesday | 2019 | 3
10631 | 2019-03-13 16:54 | 2019-03-14 17:47 | 13.8KV LIBO FEEDER #2 | Heavy Rain | Lightning | 0 | Checked & found Libo OCB fdr#2 T/R 1x, Ctr:86-87, R/F: 50 @2 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 16:54 | Afternoon | Wednesday | 2019 | 3
10632 | 2019-03-14 03:15 | 2019-03-14 03:15 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 32 | Batang fdr#3 T/R 1x. Not checked yet. |  | 1 | 3:15 | Night | Thursday | 2019 | 3
10633 | 2019-03-14 03:15 | 2019-03-15 10:39 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 32 | Checked and found VCB BTG fdr #3 T/R 1x, ctr: 377 - 378, R/F: 51P @1 and @3 Patrolled the line and found flash over dead end @1, @3 o/p 37-AS-09 Cause : Unidentified |  | 1 | 3:15 | Night | Thursday | 2019 | 3
10634 | 2019-03-14 05:11 | 2019-03-14 05:11 | 13.8KV DURI FIELD FEEDER #1 | Rain | Animal | 0 | 05:11 It was reported spark o/p 01-4 19B (Duri field fdr#1). 08:40 Checked and found B/O fuse link Phase @2 and @3 for 2x 1000 kVA (TX-3 and TX-4) and spark at U/G port head. 08:50 Re-energize 2x1000 kVA TX at CGS #1, success Cause: Animal (squirrel) |  | 1 | 5:11 | Morning | Thursday | 2019 | 3
10635 | 2019-03-14 08:55 | 2019-03-14 08:55 | CENTRAL DURI POWER PLANT |  |  | 0 | 08:55 CDGT #4 S/U and then Online at 09:26 |  | 1 | 8:55 | Morning | Thursday | 2019 | 3
10636 | 2019-03-14 10:58 | 2019-03-14 10:58 | CENTRAL DURI POWER PLANT |  |  | 0 | 10:58 CDGT #1 Offline and then S/D at 11:00 Purpose: Offline Wash |  | 1 | 10:58 | Morning | Thursday | 2019 | 3
10637 | 2019-03-14 17:32 | 2019-03-14 17:32 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 0 | ND VCB fdr #9 T/R 1x Cause: Not Checked Yet |  | 1 | 17:32 | Afternoon | Thursday | 2019 | 3
10638 | 2019-03-14 17:32 | 2019-03-18 16:54 | 13.8KV NORTH DURI FEEDER #9 | Fair | Animal | 0 | Checked & found. N Duri VCB fdr#9 T?R 1x, Ctr: 79-80, R/F: 51N Patrolled the Line, found dead animal o/p 11J 502 Cause : Animal |  | 1 | 17:32 | Afternoon | Thursday | 2019 | 3
10639 | 2019-03-15 02:15 | 2019-03-15 02:15 | CENTRAL DURI SWITCH YARD | Fair | Transformer Failure | 0 | 02:15 C.Duri /O for TX#5 TX#5 had been Isolated, under repair, purification 10:00 Checked & found, 115KV OCB#33 T/O, Ctr: 639-640 115KV OCB#35 T/O, Ctr: 427-428 Also Found, TX#5 Bukhol relay & 86T Operate, drained TX Oil fron conservator, then Rested 86T relay 15:21 Manually Closed OCB #33 and OCB #35 Cause: Transformer failure, Bukhol relay |  | 1 | 2:15 | Night | Friday | 2019 | 3
10640 | 2019-03-15 10:36 | 2019-03-18 16:52 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 29 | Checked & found, Bekasap VCB fdr#6 T/R 1x, Ctr: 375-376, R/F: 51 @1. Patrolled the Line, found Broken LA at LBS NN/1-TL-5 also Found High Palm trees Near Pole 37-BE-66 Cause: Unidentified |  | 1 | 10:36 | Morning | Friday | 2019 | 3
10641 | 2019-03-15 10:36 | 2019-03-18 16:52 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 29 | Checked & found, Bekasap VCB fdr#6 T/R 1x, Ctr: 375-376, R/F: 51 @1. Patrolled the Line, found Broken LA at LBS NN/1-TL-5 also Found High Palm trees Near Pole 37-BE-66 Cause: Unidentified |  | 1 | 10:36 | Morning | Friday | 2019 | 3
10642 | 2019-03-15 22:10 | 2019-03-15 22:10 | 13.8KV NELLA FEEDER #2 | Fair | Construction Job | 0 | 22:10 Manually Opened 13.8 KV Nella OCB fdr#2 as requested Blm GS, due to Pump problem. 22:58 Manually Closed back OCB fdr#2 as requested Blm GS. Cause: Planned Construction |  | 1 | 22:10 | Night | Friday | 2019 | 3
10643 | 2019-03-16 09:08 | 2019-03-16 09:18 | 13.8KV DURI FIELD FEEDER #3 | Fair | Planned Maintenance | 57 | 09:18 Manual Open DF VCB fdr #3 for replace LBS 01-9-32 Closed at 14:57 Cause: Planned Maintenance |  | 1 | 9:08 | Morning | Saturday | 2019 | 3
10644 | 2019-03-16 16:35 | 2019-03-16 16:35 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Planned Maintenance | 0 | 16:35 Manual Open RCL 03-4-16 to repair loss connection HLC @3 on pole 3-4-22 Closed at 16:56 Cause: Planned Maintenance |  | 1 | 16:35 | Afternoon | Saturday | 2019 | 3
10645 | 2019-03-17 12:07 | 2019-03-17 12:07 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 39 | Sintong fdr #2 T/R 1x. Sintong GFPC T/R 1x Not Checked Yet |  | 1 | 12:07 | Afternoon | Sunday | 2019 | 3
10646 | 2019-03-17 14:43 | 2019-03-17 14:43 | 13.8KV 5B FEEDER #3 | Fair | Fire | 3 | 14:43 5B feeder #3 load dropped 67 A (80 - 13 A) 15:14 Reported no power d/s of 5B fdr #3 16:20 Checked and found RCL 4C-65A T/SO, ctr: 71-77, and any bush fire under the line down stream of RCL 4C-65A. But the power line reported still OK 16:26 Manual Close the RCL 4C-65A, success. Cause: Fire |  | 1 | 14:43 | Afternoon | Sunday | 2019 | 3
10647 | 2019-03-17 17:22 | 2019-03-17 17:22 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 130 | Menggala feeder #1 dropped 115 A (170-55A) Menggala GFPC T/R 1x. Not Checked Yet. |  | 1 | 17:22 | Afternoon | Sunday | 2019 | 3
10648 | 2019-03-18 06:53 | 2019-03-18 06:53 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 671 | 06:53 BKS fdr #6 load dropped 67 A (202 - 135 A) BKS fdr #5 load dropped 38 A (248 - 210 A) -- WIP Cause : Not Checked Yet 08:44 Checked and found RCL 38-BE-10 T/O (on block position Patrolled the lines but found nothing 10:05 Manual close RCL 38-BE-10, success, the RCL still on BL position for RIG ACS #06 at AMAN #03 Cause: unidentified | 1234 | 1 | 6:53 | Morning | Monday | 2019 | 3
10649 | 2019-03-18 06:53 | 2019-03-20 17:26 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 671 | Checked and found RCL 38-BE-10 T/O (on block position), ctr: 604-605, R/F: None Patrolled the lines but found nothing Cause : Unidentified | 1234 | 1 | 6:53 | Morning | Monday | 2019 | 3
10650 | 2019-03-19 08:11 | 2019-03-19 08:11 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | 08:11 DCM VCB fdr #3 T/R 1x Cause: Not Checked Yet |  | 1 | 8:11 | Morning | Tuesday | 2019 | 3
10651 | 2019-03-19 08:11 | 2019-03-21 05:03 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Animal | 0 | Checked and found DCM ACB fdr #3 T/R 1x, ctr: 89 - 90, R/F 51 @1, 2, 3 Patrolled the line and found broken deadend cause by animal o/p 06-F-01 Cause : Animal |  | 1 | 8:11 | Morning | Tuesday | 2019 | 3
10652 | 2019-03-19 09:16 | 2019-03-19 09:16 | PEMATANG MAIN SUBSTATION | Fair | Planned Maintenance | 4034 | 08:57 Switching to shut down PMT Main SS - Transfer load PTN fdr #1 to MSU fdr #1 - Modification jumper of PTN fdr #1 and 44 kV PMTM-PTN - Repair bypass switch of OCB fdr #1 PMT Main 09:16 Open RGU fdr #1, closed at 15:23, ctr: 26 - 27 09:15 Open RGU fdr #2, closed at 15:31, ctr: 341 - 342 09:22 Open PMT fdr #2, closed at 15:21, ctr: 531 - 532 09:33 Open PMT fdr #1, closed at 14:39, ctr: 177 - 178 09:42 Open PTN fdr #2, closed at ……… , ctr: 268 - 269 09:46 Open PTN fdr #1, closed at 15:27, ctr: 100 - 101 09:38 Open RKN fdr #2, closed at...… , ctr: 1285 - 1286 09:18 Open 44 kV GCB #2 PMT Main, closed at 14:43, ctr: 95550 - 95551 09:35 Open 44 kV GCB #3 PMT Mian, closed at 14:43, ctr: 166 - 167 09:51 Open 44 kV GCB #3 PMT Mian, closed at 14:43, ctr: 296 - 297 Cause: Planned Maintenance | 1234 | 1 | 9:16 | Morning | Tuesday | 2019 | 3
10653 | 2019-03-19 10:25 | 2019-03-19 10:25 | MINAS SWITCH YARD | Fair | Under investigation | 0 | 10:25 115 kV GCB #71 of Minas SY T/O 115 kV GCB #75 of Minas SY T/O 13:55 Checked the problem at Minas SG but found nothing Try to Close 115 kV GCB #75 and GCB #71 but failed 16:40 Troubleshooting continue tomorrow. Cause: Under Investigation |  | 1 | 10:25 | Morning | Tuesday | 2019 | 3
10654 | 2019-03-19 17:22 | 2019-03-19 17:22 | CENTRAL DURI POWER PLANT |  |  | - | 17:22 S/U CGT#1, then on line the unit at 17:56. |  | 1 | 17:22 | Afternoon | Tuesday | 2019 | 3
10655 | 2019-03-19 22:11 | 2019-03-19 22:11 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT#2, then S/D the unit for S/B. |  | 1 | 22:11 | Night | Tuesday | 2019 | 3
10656 | 2019-03-20 10:16 | 2019-03-20 10:16 | 13.8KV CENTRAL KOTABATAK FEEDER #6 | Fair | Planned Maintenance | 69 | 10:16 Manually opened LBS: 34-CT-68 D/S CKBS feeder #6. Due to Installed Tx at well KB #335 (Reactive well). 10:33 Manually closed LBS: 34-CT-68. Cause: Plan Maintenance. |  | 1 | 10:16 | Morning | Wednesday | 2019 | 3
10657 | 2019-03-20 17:24 | 2019-03-20 17:24 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | N Duri VCB Feeder #11 T/R 1x. Not checked yet. |  | 1 | 17:24 | Afternoon | Wednesday | 2019 | 3
10658 | 2019-03-20 17:24 | 2019-03-24 07:57 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | Checked and found ND VCB fdr #11 T/R 1x, ctr: 185 - 186, R/F: 51 @1 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 17:24 | Afternoon | Wednesday | 2019 | 3
10659 | 2019-03-21 00:06 | 2019-03-21 00:06 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | - | Duri Community fdr #3 T/R 1 X. Not checked yet. |  | 1 | 0:06 | Night | Thursday | 2019 | 3
10660 | 2019-03-21 00:06 | 2019-03-24 07:59 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | - | Checked and found ACB DCM fdr #3 T/R 1x, ctr: 90 - 91, R/F: 51N Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 0:06 | Night | Thursday | 2019 | 3
10661 | 2019-03-21 07:10 | 2019-03-21 07:10 | 13.8KV 6DN FEEDER #1 | Fair | Unidentified | 0 | 6DN fdr#1 load dropped 76A (133-57A) Not checked yet. |  | 1 | 7:10 | Morning | Thursday | 2019 | 3
10662 | 2019-03-21 07:10 | 2019-03-24 16:11 | 13.8KV 6DN FEEDER #1 | Fair | Unidentified | 0 | Checked and found RCL 5E-05 T/R 1x, ctr: 276 - 277, R/F: None Patrolled the line but found nothing Cause : Unidentified |  | 1 | 7:10 | Morning | Thursday | 2019 | 3
10663 | 2019-03-21 11:34 | 2019-03-21 11:34 | 13.8KV 6DN FEEDER #6 | Fair | Planned Maintenance | 94 | 11:34 Manually open 6DN OCB feeder #6 (+/- 13 wells). For Installing 115 Kv Lightning Arrester towards 6DN Substation. 14:29 Manually blocked and closed 6DN OCB feeder #6 and released the block. Cause: Plan maintenance. |  | 1 | 11:34 | Morning | Thursday | 2019 | 3
10664 | 2019-03-21 17:47 | 2019-03-21 17:47 | 13.8KV KETIGUL FEEDER#2 | Fair | Under investigation | 619 | Ketigul VCB feeder#2 T/O (In block position ,RIG ACS#05 at loction: Pagar#23). Respectively: Ketigul feeder#1 load dropped 27A (127-100A). Ketigul feeder#3 load dropped 8A (34-26A). 17:56 Manually blocked and close VCB KTGL fdr #2 but failed 19:40 Checked and found VCB KGTL fdr #2 T/O, ctr: 319 - 320, R/F: 51N Patrolled the lines but found nothing 20:47 Blocked and close VCB kTGL fdr #2 (locally), success and then release the block (line for location Pager #23 has cut off, not need to block) Cause: under investigation | 0 | 1 | 17:47 | Afternoon | Thursday | 2019 | 3
10665 | 2019-03-22 06:19 | 2019-03-22 06:19 | 13.8KV 8D FEEDER #4 | Fair | Unidentified | - | 8D fdr #4 dropped 65 A (177 - 112 A) Cause: Not Checked Yet |  | 1 | 6:19 | Morning | Friday | 2019 | 3
10666 | 2019-03-22 06:19 | 2019-03-25 14:24 | 13.8KV 8D FEEDER #4 | Fair | Unidentified | - | Checked and found 8D OCB feeder #4 Normal condition. Cause: Suspected WIP trip. |  | 1 | 6:19 | Morning | Friday | 2019 | 3
10667 | 2019-03-23 06:23 | 2019-03-23 06:23 | 13.8KV BATANG GFPC | Fair | Unidentified | 0 | 06:23 Batang GFPC RCL T/R 1x Triggered by Batang feeder #3 Cause: Not Checked Yet |  | 1 | 6:23 | Morning | Saturday | 2019 | 3
10668 | 2019-03-23 06:23 | 2019-03-28 07:28 | 13.8KV BATANG GFPC | Fair | Unidentified | 0 | Checked & found Batang GFPC TX T/R 1x, CTR: 930-933, R/F: 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 6:23 | Morning | Saturday | 2019 | 3
10669 | 2019-03-23 09:24 | 2019-03-23 09:24 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Fair | Planned Maintenance | 0 | 09:24 Manually opened Recloser: H33-07 D/S 4160V Dumai feeder #4. For tree trimming Manually blocked and closed Recloser: H33-07 --> OK. and then released the block. Cause: Plan Maintenance. |  | 1 | 9:24 | Morning | Saturday | 2019 | 3
10670 | 2019-03-23 17:12 | 2019-03-23 17:12 | 13.8KV BEKASAP FEEDER #6 | Fair | Unidentified | 244 | 17:12 Bekasap feeder #6 load dropped 56A (201-135A). 19:30 Checked and found RCL 38-BE-10 T/O (on block position for RIG ACS #06 at AMN #03), ctr: 605 - 606, R/F: None (form-3 control type) Patrolled the line but found nothing. 20:29 Block and then Closed the RCL 38-BE-10, success. cause: unidentified |  | 1 | 17:12 | Afternoon | Saturday | 2019 | 3
10671 | 2019-03-23 18:38 | 2019-03-23 18:38 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Lightning | 0 | Sintong feeder #1 load dropped 43A (107-64A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 18:38 | Afternoon | Saturday | 2019 | 3
10672 | 2019-03-23 18:38 | 2019-03-28 10:40 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Lightning | 0 | Checked & found RCL 26AE22 T/R 1x, Ctr: 257-258, R/F: 51N also found Rcl.25AD26 T/R 1x, Ctr: 127-128, R/F: 51N Patrolled the Line found @3 flash over pin insulator o/p 25 AG 05 and @1 High trees Cause: Lightning |  | 1 | 18:38 | Afternoon | Saturday | 2019 | 3
10673 | 2019-03-24 18:37 | 2019-03-24 18:37 | 13.8KV BATANG GFPC | Fair | Unidentified | - | Batang GFPC T/R 1x. No load drop at any feeder. Not checked yet. |  | 1 | 18:37 | Afternoon | Sunday | 2019 | 3
10674 | 2019-03-24 18:37 | 2019-03-28 07:29 | 13.8KV BATANG GFPC | Fair | Unidentified | - | Checked & found Batang GFPC TX T/R 1x, Ctr: 933-934, R/F: 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 18:37 | Afternoon | Sunday | 2019 | 3
10675 | 2019-03-25 13:13 | 2019-03-25 13:13 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Dead End Insulator | 0 | 13:13 C Duri ACB #13 (feeder #3) T/O (in block position) due to RIG activity at location: 3R-85B. 13:23 Manually blocked and closed C Duri ACB #13 (feeder #3) --> Success. (still in block position). Cause: Not patrolled yet. |  | 1 | 13:13 | Afternoon | Monday | 2019 | 3
10676 | 2019-03-25 14:52 | 2019-03-25 14:52 | 13.8KV 4D FEEDER #3 | Cloudy | Lightning | 6 | 14:52 4D OCB feeder #3 T/R. 15:47 Checked and found 4D OCB feeder #3 T/R 5x. Counter: 258-263 R/F: 51@2. Cause: Not patrolled yet. |  | 1 | 14:52 | Afternoon | Monday | 2019 | 3
10677 | 2019-03-25 14:52 | 2019-03-31 14:20 | 13.8KV 4D FEEDER #3 | Cloudy | Lightning | 6 | Checked & found 4D OCB fdr#3 T/R 7x, Ctr: 256-263, R/F: 51@2 Patrolled the Line, found @2 Broken pin insulator o/p 4D-66 Cause : Lightning |  | 1 | 14:52 | Afternoon | Monday | 2019 | 3
10678 | 2019-03-26 03:04 | 2019-03-26 03:04 | 13.8KV 4D FEEDER #2 | Fair | Lightning | 1 | 03:04 4D OCB fdr #2 T/R 1x Cause: Not Checked Yet |  | 1 | 3:04 | Night | Tuesday | 2019 | 3
10679 | 2019-03-26 03:04 | 2019-03-31 14:14 | 13.8KV 4D FEEDER #2 | Fair | Lightning | 1 | Checked & found 4D OCB fdr#2 T/R 3x, Ctr: 273-276, R/F: 51@3 Patrolled the Line, Found @3 broken L.A o/p 4D-268 Cause : Lightning |  | 1 | 3:04 | Night | Tuesday | 2019 | 3
10680 | 2019-03-26 03:04 | 2019-03-26 03:04 | 13.8KV 4D FEEDER #3 | Fair | Lightning | 41 | 03:04 4D OCB fdr #3 T/R 1x Cause: Not Checked Yet |  | 1 | 3:04 | Night | Tuesday | 2019 | 3
10681 | 2019-03-26 03:04 | 2019-03-31 14:21 | 13.8KV 4D FEEDER #3 | Fair | Lightning | 41 | Checked & found 4D OCB fdr#4 T/R 1x, Ctr: 258-259, R/F: 51 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 3:04 | Night | Tuesday | 2019 | 3
10682 | 2019-03-26 14:03 | 2019-03-26 14:03 | MINAS POWER PLANT |  |  | - | 14:03 S/U MGT #10 and then Online the unit at 14:52. |  | 1 | 14:03 | Afternoon | Tuesday | 2019 | 3
10683 | 2019-03-26 14:19 | 2019-03-26 14:19 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 13 | Ketigul VCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 14:19 | Afternoon | Tuesday | 2019 | 3
10684 | 2019-03-26 14:19 | 2019-03-28 15:05 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 13 | Checked & found Ketigul VCB fdr#1 T/R 1x, Ctr: 211-212, R/F: 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 14:19 | Afternoon | Tuesday | 2019 | 3
10685 | 2019-03-26 14:52 | 2019-03-26 14:52 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 61 | 14:52 Manually opened 8C VCB feeder #1. Due to replaced @1 broken pin insulator on pole 9D-37. Manually blocked and closed 8C VCB feeder #1. and then released the block. Cause: Plan maintenance. |  | 1 | 14:52 | Afternoon | Tuesday | 2019 | 3
10686 | 2019-03-26 16:25 | 2019-03-26 16:25 | MINAS POWER PLANT |  |  | - | 16:25 Offline MGT #9 and then S/D the unit for standby. |  | 1 | 16:25 | Afternoon | Tuesday | 2019 | 3
10687 | 2019-03-27 02:46 | 2019-03-27 02:46 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Others | 10 | SO BEKASAP 13.8KV OCB fdr #1 T/R 1X. No checked yet. |  | 1 | 2:46 | Night | Wednesday | 2019 | 3
10688 | 2019-03-27 02:46 | 2019-03-29 12:16 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Others | 10 | Checked & found, SOBEK OCB fdr#1 T/R 1x, Ctr: 423-424, R/F: 51 @3 Patrolled, found Some Ribbon twisted & jumper to Conductor o/p 37-BG-41A Cause : Others (Ribbon twisted & jumper to Conductor) |  | 1 | 2:46 | Night | Wednesday | 2019 | 3
10689 | 2019-03-27 02:47 | 2019-03-27 02:47 | 115KV DURI - PUNGUT LINE | Rain and Lightning | Lightning | 20 | 02:47 Duri 115KV OCB #21 T/R 1X. Duri 115KV OCB #29 T/R 1X. Pungut 115KV OCB #21 T/R 1X. KBJ 115KV GCB #51 T/R 1X. KBJ 115KV GCB #53 T/R 1X. (No power to Pungut Substation). 02:53 Duri 115KV OCB #21 T/R 1X. Duri 115KV OCB #29 T/R 1X. Pungut 115KV OCB #21 T/R 1X. KBJ 115KV GCB #51 T/R 1X. KBJ 115KV GCB #53 T/R 1X. (No power to Pungut Substation). No checked yet. |  | 1 | 2:47 | Night | Wednesday | 2019 | 3
10690 | 2019-03-27 02:47 | 2019-03-31 18:30 | 115KV DURI - PUNGUT LINE | Rain and Lightning | Lightning | 20 | Checked & found 115KV DRB OCB # 29 T/R 2x, Ctr: 142-144, R/F: Relay L90: 87L-A, 87L-C, 67N-Inst Patrolled the Line, found @1 flash over Suspension Insulator o/p DP-62 and High Palm Tree touched power line o/p DP-35/36 Cause: Lightning |  | 1 | 2:47 | Night | Wednesday | 2019 | 3
10691 | 2019-03-27 04:31 | 2019-03-27 04:31 | 13.8KV 4D FEEDER #2 | Fair | Lightning | 48 | 04:31 4D OCB dr #2 T/R 1x Cause: Not Checked Yet |  | 1 | 4:31 | Morning | Wednesday | 2019 | 3
10692 | 2019-03-27 04:31 | 2019-03-31 14:21 | 13.8KV 4D FEEDER #2 | Fair | Lightning | 48 | Checked & found 4D OCB fdr#2 T/R 1x, Ctr: 263-264, R/F: 51 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 4:31 | Morning | Wednesday | 2019 | 3
10693 | 2019-03-27 04:42 | 2019-03-27 04:42 | 13.8KV 4D FEEDER #3 | Fair | Lightning | 36 | 04:42 4D fdr # 3 load dropped 167 A (207 - 40 A) 4D fdr #1 load dropped 255 A (260 - 5 A) -- WIP Cause: Not Checked Yet |  | 1 | 4:42 | Morning | Wednesday | 2019 | 3
10694 | 2019-03-27 04:42 | 2019-03-31 14:16 | 13.8KV 4D FEEDER #3 | Fair | Lightning | 36 | Checked & found 4D OCB fdr#3 T/R 1x, Ctr: 273-274, R/F: 51 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 4:42 | Morning | Wednesday | 2019 | 3
10695 | 2019-03-27 09:25 | 2019-03-27 09:25 | 13.8KV MINAS FEEDER #6 | Fair | Planned Maintenance | 12 | 09:25 Manually open LBS 7E-46 (Minas fdr#6). C/O broken dead end insulator on pole M5B ( well off 6E-93 ). 10:30 Manually closed LBS 7E-46. Cause: Plant maintenance. |  | 1 | 9:25 | Morning | Wednesday | 2019 | 3
10696 | 2019-03-27 10:00 | 2019-03-27 10:00 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 81 | 10:00 Manually open Minas fdr#3. Replaced 300KVA TX by 550KVA at well 7D-84. 10:26 Blocked & closed Minas fdr#3 then release the block. Cause: Plan Maintenance. |  | 1 | 10:00 | Morning | Wednesday | 2019 | 3
10697 | 2019-03-27 11:41 | 2019-03-27 11:41 | 13.8KV CENTRAL DURI FEEDER #15 | Cloudy | Dead End Insulator | 0 | C.Duri ACB fdr#15 T/R 1x Ctr:385-386 R/F:51@1@2. Not patrolled yet. |  | 1 | 11:41 | Morning | Wednesday | 2019 | 3
10698 | 2019-03-27 11:41 | 2019-03-29 12:10 | 13.8KV CENTRAL DURI FEEDER #15 | Cloudy | Dead End Insulator | 0 | Checked & found, CD ACB 18 Fdr#15 T/R 1x, Ctr: 385-386, R/F: 51N Patrolled the Line, found @1,2 Broken Deadend insulator o/p 06-Q5-02 Cause : Dead End Insulator |  | 1 | 11:41 | Morning | Wednesday | 2019 | 3
10699 | 2019-03-27 14:27 | 2019-03-27 14:27 | 13.8KV S. BALAM FEEDER #4 | Fair | Powerline - Jumper | 47 | So. Balam VCB fdr#4 T/R1x. So. Balam GFPC T/R 1x. Not checked yet. |  | 1 | 14:27 | Afternoon | Wednesday | 2019 | 3
10700 | 2019-03-27 14:27 | 2019-03-31 17:13 | 13.8KV S. BALAM FEEDER #4 | Fair | Powerline - Jumper | 47 | Checked & found, S.Balam VCB fdr#4 T/R 3x, Ctr: 366-369, R/F: 51N Patroll;ed the Line. @3 lost connection at by pass switch o/p NN-18 Cause : Jumper Bypass switch. |  | 1 | 14:27 | Afternoon | Wednesday | 2019 | 3
10701 | 2019-03-27 15:06 | 2019-03-27 15:06 | 13.8KV BANGKO GFPC | Rain and Lightning | Lightning | 6 | 15:06 Bangko VCB fdr#4 T/R 1x. Bangko GFPC T/R 1x. 15:27 Bangko VCB fdr#4 T/R 1x again. Bangko GFPC T/R 1x again. Not checked yet. |  | 1 | 15:06 | Afternoon | Wednesday | 2019 | 3
10702 | 2019-03-27 15:06 | 2019-03-31 17:25 | 13.8KV BANGKO GFPC | Rain and Lightning | Lightning | 6 | Checked & found Bangko OCB fdr#4 T/R 3x, Ctr: 366-369, R/F: 51N Patrolled the Line found @3 Broken pin support o/p 24Z36 Cause : Lightning |  | 1 | 15:06 | Afternoon | Wednesday | 2019 | 3
10703 | 2019-03-27 15:42 | 2019-03-27 15:42 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 41 | Nella VCB fr#2 T/R 1x. Nella GFPC T/R 1x. Not checked yet. |  | 1 | 15:42 | Afternoon | Wednesday | 2019 | 3
10704 | 2019-03-27 15:42 | 2019-01-04 14:07 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 41 | Checked & found Nella OCB fdr#2 T?R 1x, Ctr: 323-324, R/F: 51N Patrolled the Line, @3 found Broken Dead end insulator o/p 19 W14 Cause : Lightning |  | 1 | 15:42 | Afternoon | Wednesday | 2019 | 3
10705 | 2019-03-27 17:26 | 2019-03-27 17:26 | 13.8KV LIBO FEEDER #2 | Fair | Transformer Failure | 123 | It was reported B?O fuse at Well Hitam #08 (Libo Fdr#2) Not checked yet. |  | 1 | 17:26 | Afternoon | Wednesday | 2019 | 3
10706 | 2019-03-27 17:26 | 2019-03-28 14:30 | 13.8KV LIBO FEEDER #2 | Fair | Transformer Failure | 123 | Checked & found @1,2 B/O fuse for 300 KVATX at Well Hitam #08 (Libo fdr#2) Perform TTR & Megger the TX, the Result Was Low Megger reading Cause : Transformer Failure |  | 1 | 17:26 | Afternoon | Wednesday | 2019 | 3
10707 | 2019-03-27 17:48 | 2019-03-27 17:48 | 13.8KV S. BALAM FEEDER #4 | Fair | Powerline - Jumper | 0 | So. Balam fdr#4 Load dropped 50A (178-128A). So. Balam GFPC T/R 1x. Not checked yet. |  | 1 | 17:48 | Afternoon | Wednesday | 2019 | 3
10708 | 2019-03-27 17:48 | 2019-03-31 17:08 | 13.8KV S. BALAM FEEDER #4 | Fair | Powerline - Jumper | 0 | Checked & found, S.Balam VCB fdr#4 T/R 3x, Ctr: 366-369, R/F: 51N Patroll;ed the Line. @3 lost connection at by pass switch o/p NN-18 Cause : Jumper Bypass switch. |  | 1 | 17:48 | Afternoon | Wednesday | 2019 | 3
10709 | 2019-03-28 03:17 | 2019-03-28 03:17 | 13.8KV S. BALAM FEEDER #4 | Fair | Powerline - Jumper | 43 | S Balam VCB feeder #4 T/R 1x. Not checked yet. |  | 1 | 3:17 | Night | Thursday | 2019 | 3
10710 | 2019-03-28 03:17 | 2019-03-31 17:08 | 13.8KV S. BALAM FEEDER #4 | Fair | Powerline - Jumper | 43 | Checked & found, S.Balam VCB fdr#4 T/R 3x, Ctr: 366-369, R/F: 51N Patroll;ed the Line. @3 lost connection at by pass switch o/p NN-18 Cause : Jumper Bypass switch. |  | 1 | 3:17 | Night | Thursday | 2019 | 3
10711 | 2019-03-28 06:28 | 2019-03-28 06:28 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Powerline - Jumper | 45 | S Balam VCB feeder #4 T/R 1x. Not checked yet. |  | 1 | 6:28 | Morning | Thursday | 2019 | 3
10712 | 2019-03-28 06:28 | 2019-03-31 17:08 | 13.8KV S. BALAM FEEDER #4 | Cloudy | Powerline - Jumper | 45 | Checked & found, S.Balam VCB fdr#4 T/R 3x, Ctr: 366-369, R/F: 51N Patroll;ed the Line. @3 lost connection at by pass switch o/p NN-18 Cause : Jumper Bypass switch. |  | 1 | 6:28 | Morning | Thursday | 2019 | 3
10713 | 2019-03-28 07:26 | 2019-03-28 07:26 | 13.8KV NORTH DURI FEEDER #11 | Fair | Others | 0 | N.Duri VCB fdr#11 T/R 1x . Not checked yet. |  | 1 | 7:26 | Morning | Thursday | 2019 | 3
10714 | 2019-03-28 07:26 | 2019-03-31 18:41 | 13.8KV NORTH DURI FEEDER #11 | Fair | Others | 0 | Checked & found N Duri VCB fdr#11 T/R 1x, Ctr: 186-187, R/F: 51N Patrolled the Line, Found @3 broken Bushing by pass Recloser o/p 13 F10 23 Cause : Others |  | 1 | 7:26 | Morning | Thursday | 2019 | 3
10715 | 2019-03-28 10:15 | 2019-03-28 10:15 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 72 | CKBS fdr#5 T/R 1x. Not checked yet. |  | 1 | 10:15 | Morning | Thursday | 2019 | 3
10716 | 2019-03-28 10:15 | 2019-03-31 06:41 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 72 | Checked & found CKB VCB fdr#5 T/R 1x, Ctr: 170-171, R/F: 51@1 Patrolled the Line, but Found nothing Cause: Unidentified |  | 1 | 10:15 | Morning | Thursday | 2019 | 3
10717 | 2019-03-28 10:20 | 2019-03-28 10:20 | CENTRAL DURI POWER PLANT |  |  | - | 10:20 S/U CGT#3, tehn online the unit at 10:43. 10:35 Closed Tie breaker ACB#39. |  | 1 | 10:20 | Morning | Thursday | 2019 | 3
10718 | 2019-03-28 10:25 | 2019-03-28 10:25 | 13.8KV 4B FEEDER #5 | Fair | Planned Maintenance | 0 | 10:25 Manually Open 4B fdr#5. Dismantle 2x 2500 Kva Tx at GS#6. 10:52 Blocked & closed 4B fdr#5, then release the block. Cause; Plan Maintenance. |  | 1 | 10:25 | Morning | Thursday | 2019 | 3
10719 | 2019-03-28 12:10 | 2019-03-28 12:10 | CENTRAL DURI POWER PLANT |  |  | - | 12:10 Off line CGT#4, then S/D the unit for S/B. 12:12 Closed Tie breaker ACB#39. |  | 1 | 12:10 | Afternoon | Thursday | 2019 | 3
10720 | 2019-03-28 23:31 | 2019-03-28 23:31 | 13.8KV LIBO FEEDER #2 | Fair | Powerline - Conductor | 521 | 23:31 Libo OCB feeder #2 T/O. Not checked yet. Production loss : 28 Bbls / 8 wells. | 12345 | 1 | 23:31 | Night | Thursday | 2019 | 3
10721 | 2019-03-28 23:31 | 2019-03-29 00:51 | 13.8KV LIBO FEEDER #2 | Fair | Powerline - Conductor | 521 | 00:51 Checked and found Libo OCB feeder #2 T/LO. Counter: 487-494 R/F: 51 @1. 00:53 Manually blocked and closed Libo OCB feeder #2 --> but failed. Re patrolled Libo OCB feeder #2. 02:26 Manually Opened Recl. 23BW02. Blocked & closed Libo VCB fdr#2, but fail. 03:15 Manually Opened LBS 33CC06. Blocked & closed Libo VCB fdr#2, but fail. 03:57 Manually Opened LBS 28BY06. Blocked & closed Libo VCB fdr#2, but fail. 07:30 Patrolled the line & found @2 Broken Conductor o/p 23BV13 @1@2@3 Broken Pin Insulator o/p 23BV13. 08:30 Repaired @2 Broken Conductor o/p 23BV13. Replaced @1@2@3 Broken Pin Insulator o/p 23BV13. 10:34 Blocked & closed Libo VCB fdr#2, ok, then release the block. 10:35 Blocked & closed Recl. 23BW02, then release the block. Cause: Broken Conductor. Production loss : 586 Bbls / 7 wells. Total Production loss : 614 Bbls / 8 wells. | 12345 | 1 | 23:31 | Night | Thursday | 2019 | 3
10722 | 2019-03-29 10:16 | 2019-03-29 10:16 | 13.8KV 3D FEEDER #5 | Fair | Planned Maintenance | 0 | 10:16 Manually Open 3D fdr#5. Dismantle & Reconnected 2500Kva Tx (SB#54) at GS#5. 11:10 Blocked & Closed 3D fdr#5, then release the block. Cause: Plan Maintenance. |  | 1 | 10:16 | Morning | Friday | 2019 | 3
10723 | 2019-03-29 10:16 | 2019-03-29 10:16 | 13.8KV 3D FEEDER #7 | Fair | Planned Maintenance | 13 | 10:16 Manually Opened 3D fdr#7. Dismantle 2500Kva Tx (SB#51) at GS#5. 11:10 Blocked & Closed 3D fdr#7, then release the block. Cause: Plan Maintenance. |  | 1 | 10:16 | Morning | Friday | 2019 | 3
10724 | 2019-03-29 19:39 | 2019-03-29 19:39 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Lightning | 0 | N Duri 44KV GCB #1 T/R 1x ( 44KV N Duri - Dumai Line ). Not checked yet. |  | 1 | 19:39 | Night | Friday | 2019 | 3
10725 | 2019-03-29 19:39 | 2019-03-31 17:40 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Lightning | 0 | Checked & found 44KV NDuri GCB #44 T/R 1x, Ctr: 134-135, R/F: 51 @1,2 Patrolled the Line, found @1,2 broken pin insulator o/p DD-64 Cause : Lightning |  | 1 | 19:39 | Night | Friday | 2019 | 3
10726 | 2019-03-31 09:25 | 2019-03-31 09:25 | 13.8KV 8D FEEDER #1 | Fair | Lightning | 0 | 8D fdr#1 T/R 1x. Not checked yet. |  | 1 | 9:25 | Morning | Sunday | 2019 | 3
10727 | 2019-03-31 09:25 | 2019-04-04 07:25 | 13.8KV 8D FEEDER #1 | Fair | Lightning | 0 | Checked & found 8D OCB fdr#1 T/R 1x, Ctr: 320-321, R/F: 51 Patrolled the Line, but found nothing Cause : Lightning Date Patrol : 31-MAR-2019 |  | 1 | 9:25 | Morning | Sunday | 2019 | 3
10728 | 2019-03-31 09:36 | 2019-03-31 09:36 | 13.8KV 4D FEEDER #3 | Fair | Planned Maintenance | 41 | 09:36 Manually Opened 4D fdr#3. Disconnected LBS 3D-09 for parallel 3D fdr#2 & 4D fdr#3. Replaced Broken Pin Insulator D/S 4D fdr#3. 10:17 Blocked & Closed 3D fdr#2, then released the block. 11:06 Blocked & Closed 3D fdr#2, then released the block. Cause: Planned Maintenance. |  | 1 | 9:36 | Morning | Sunday | 2019 | 3
10729 | 2019-03-31 09:38 | 2019-03-31 09:38 | 13.8KV SINTONG FEEDER #1 | Fair | Planned Maintenance | 0 | 09:38 Manually Opened LBS 26-AE-06 ( Sintong fdr#1). Replaced Pin Insulator o/p 25AD12. 10:03 Closed LBS 26-AE-12. Cause: Planned Maintenance. |  | 1 | 9:38 | Morning | Sunday | 2019 | 3
10730 | 2019-03-31 19:49 | 2019-03-31 19:49 | 13.8KV 4B FEEDER #1 | Cloudy | Lightning | 26 | 4B VCB feeder #1 T/R 1x. 4B feeder #3 load dropped 118A (120-2A) --> WIP. Not checked yet. |  | 1 | 19:49 | Night | Sunday | 2019 | 3
10731 | 2019-03-31 19:49 | 2019-03-31 14:17 | 13.8KV 4B FEEDER #1 | Cloudy | Lightning | 26 | Checked & found 4B OCB fdr#1 T/R 1x, Ctr: 360-361, R?F: 51 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 19:49 | Night | Sunday | 2019 | 3
10732 | 2019-03-31 20:39 | 2019-03-31 20:39 | 13.8KV ROKAN FEEDER #2 | Fair | Construction Job | - | 20:39 Manually opened Rokan VCB feeder #2. Due to WIP trip. 23:32 Manually block and closed Rokan VCB feeder #2. and then released the block. Cause: Construction job. |  | 1 | 20:39 | Night | Sunday | 2019 | 3
10733 | 2019-03-31 00:28 | 2019-03-31 00:28 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 34 | Minas ACB #2 (feeder #3) T/R 1x Counter: 51-52 R/F: 51N. Not patrolled yet. |  | 1 | 0:28 | Night | Sunday | 2019 | 3
10734 | 2019-03-31 00:28 | 2019-03-31 14:20 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 34 | Checked & found Minas ACB fdr#2 T/R 1x, Ctr: 80151-80152, R/F: 51 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 0:28 | Night | Sunday | 2019 | 3
10735 | 2019-03-31 14:12 | 2019-03-31 14:12 | 13.8KV S. BALAM FEEDER #4 | Fair | Planned Maintenance | 380 | 14:12 Manually Opened So.Balam fdr#4. Repaired Hot Spot o/p NN-18. 15:36 Blocked & Closed So.Balam fdr#4, then release the block. Cause: Plan Maintenance. |  | 1 | 14:12 | Afternoon | Sunday | 2019 | 3
10736 | 2019-03-31 15:33 | 2019-03-31 15:33 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | N.Duri VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 15:33 | Afternoon | Sunday | 2019 | 3
10737 | 2019-03-31 15:33 | 2019-06-04 14:28 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked & found ND VCB fdr#1 T/R 1x, Ctr: 303-304, R/F: 51 @1,2 Patrolled the Line, found @1,2 Broken L.A O/p 12-E1-06 & 12-ES-21 Cause : Lightning |  | 1 | 15:33 | Afternoon | Sunday | 2019 | 3
10738 | 2019-01-04 10:06 | 2019-01-04 10:06 | 13.8KV 4D FEEDER #2 | Fair | Planned Maintenance | 277 | 10:06 Manually Opened 4D OCB fdr#2 and the isolation switches to Repair Spark LBS 3D-226 (Hard to be Opened also Recl 3D-119 Unplug). 16:20 Manually Closed the Feeder, after isolate the LBS for repairing (5 Wells still OFF 4D-34A, 4D-35, 4D-15, 4D-25NP1, 4d-15NP1) Cause: Planned Maintenance |  | 1 | 10:06 | Morning | Friday | 2019 | 1
10739 | 2019-01-04 15:43 | 2019-01-04 15:43 | 13.8KV NELLA FEEDER #2 | Fair | Construction Job | 478 | 15:43 Manually Opened Nella OCB fdr#2 as requested TL BKO FON, to install Slip, Fixed Pipe Leaks at BKO GS. 22:07 Manually blocked and closed Nella OCB fdr#2 and then released the block. Cause: Construction job. |  | 1 | 15:43 | Afternoon | Friday | 2019 | 1
10740 | 2019-02-04 15:44 | 2019-02-04 15:44 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 1 | Ketigul VCB fdr#1 T/R 1x Ketigul fdr#2 Load dropped 19A(242-223) Not checked yet |  | 1 | 15:44 | Afternoon | Monday | 2019 | 2
10741 | 2019-02-04 15:44 | 2019-06-04 14:22 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 1 | Checked & found Ketigul VCB fdr#1 T/R 1x, Ctr: 212-213, R/F: 51 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 15:44 | Afternoon | Monday | 2019 | 2
10742 | 2019-02-04 19:31 | 2019-02-04 19:31 | 13.8KV NEW KOTABATAK FEEDER #4 | Rain and Lightning | Lightning | 130 | Checked & found NKB VCB fdr#4 T?R 1x, Ctr: 286-287, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 19:31 | Night | Monday | 2019 | 2
10743 | 2019-02-04 19:31 | 2019-02-04 19:31 | 13.8KV NEW KOTABATAK FEEDER #4 | Rain and Lightning | Lightning | 130 | NKBS VCB feeder#4 T/R 1x. NKBS GFPC T/R 1x. Not checked yet. |  | 1 | 19:31 | Night | Monday | 2019 | 2
10744 | 2019-02-04 20:08 | 2019-02-04 20:08 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 8 | 4D OCB feeder#3 T/R 1x. Not checked yet. |  | 1 | 20:08 | Night | Monday | 2019 | 2
10745 | 2019-02-04 20:08 | 2019-04-04 17:45 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 8 | Checked & found 4D OCB fdr#3 T/R 1x, Ctr: 265-266, R/F: 51N Patrolled the Line, found @1 B/O L.A o/p 4C-17 Cause : Lightning |  | 1 | 20:08 | Night | Monday | 2019 | 2
10746 | 2019-02-04 20:34 | 2019-02-04 20:34 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 19 | 8C VCB feeder#6 T/R 1x. Not checked yet. |  | 1 | 20:34 | Night | Monday | 2019 | 2
10747 | 2019-02-04 20:34 | 2019-04-04 17:30 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 19 | Checked & found 8C VCB fdr#6 T/R 2x, Ctr: 619-621, R/F: 50 @2 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 20:34 | Night | Monday | 2019 | 2
10748 | 2019-02-04 20:50 | 2019-02-04 20:50 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Unidentified | 1 | So Bekasap feeder #1 load dropped 121A (128-7A). Not checked yet. |  | 1 | 20:50 | Night | Monday | 2019 | 2
10749 | 2019-02-04 20:50 | 2019-08-04 20:50 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Unidentified | 1 | Checked and fund Recl. 36-BI-04 T/R 1X ctr:473-474. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 20:50 | Night | Monday | 2019 | 2
10750 | 2019-02-04 21:48 | 2019-02-04 21:48 | 13.8KV MENGGALA GFPC | Lightning | Animal | 0 | Menggala feeder #1 load dropped 108A (164-56A). Menggala GFPC T/R 1x. Not checked yet. |  | 1 | 21:48 | Night | Monday | 2019 | 2
10751 | 2019-03-04 09:46 | 2019-03-04 09:46 | 13.8KV NORTH DURI FEEDER #2 | Fair | Planned Maintenance | 0 | 09:46 Manual open RCL 13-J3-08 (ND fdr #2) for PM service of RCL. 11:35 Manual Close RCL 13-J3-08, success. Cause: Planned Maintenance |  | 1 | 9:46 | Morning | Monday | 2019 | 3
10752 | 2019-04-04 09:28 | 2019-04-04 09:28 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Animal | 0 | 09:28 Duri Comm. 13.8KV fdr #2 T/R 2X. 09:40 It was reported TX smoke at Mess Hall. 14:45 Checked and found @1, @2 b/o fuse for 1000KVA TX at Mess Hall. Replaced the b/o fuse above with same size then energized the TX. OK. Not checked yet. |  | 1 | 9:28 | Morning | Thursday | 2019 | 4
10753 | 2019-04-04 09:28 | 2019-08-04 16:45 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Animal | 0 | Checked and found ACB DCM fdr #2 T/R 2x, ctr: 106 - 108, R/F: 51N Patrolled and then found broken LBS @1, @2, @3, for Messhall Cause : Animal (Cat) |  | 1 | 9:28 | Morning | Thursday | 2019 | 4
10754 | 2019-04-04 09:34 | 2019-04-04 09:34 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Lightning | 0 | Checked and found ACB DCM fdr #1 T/R 1x, ctr: 135 - 136, R/F: 51N Patrolled the line and found flash over dead end o/p 5-KT-4 Cause : Lightning |  | 1 | 9:34 | Morning | Thursday | 2019 | 4
10755 | 2019-04-04 09:34 | 2019-04-04 09:34 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Lightning | 0 | Duri Comm. 13.8KV fdr #1 T/R 1X. Not checked yet. |  | 1 | 9:34 | Morning | Thursday | 2019 | 4
10756 | 2019-04-04 10:22 | 2019-04-04 10:22 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Planned Maintenance | - | 10:22 Manually Open 4.16KV DUMAI (WHARF FEEDER) fdr #1. Repaired Buck arm o/p...….. 18:35 Closed 4.16KV DUMAI (WHARF FEEDER) fdr #1. Cause: Plan Maintenance. |  | 1 | 10:22 | Morning | Thursday | 2019 | 4
10757 | 2019-04-04 13:13 | 2019-04-04 13:13 | MINAS POWER PLANT |  |  | - | MGT #7 Emergency S/D due to Lube Oil Bearing Header Temp. Hagh. (Loss of 480V). |  | 1 | 13:13 | Afternoon | Thursday | 2019 | 4
10758 | 2019-04-04 13:56 | 2019-04-04 13:56 | MINAS POWER PLANT |  |  | - | 13:56 MGT #8 S/U and on line to the system at 14:34 to restored the load. |  | 1 | 13:56 | Afternoon | Thursday | 2019 | 4
10759 | 2019-04-04 14:40 | 2019-04-04 14:40 | 13.8KV 4B FEEDER #1 | Fair | Lightning | 0 | 4B 13.8KV VCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 14:40 | Afternoon | Thursday | 2019 | 4
10760 | 2019-04-04 14:40 | 2019-10-04 08:35 | 13.8KV 4B FEEDER #1 | Fair | Lightning | 0 | Checked and found 4B OCB fdr #1 T/R 1x, ctr: 360-361, R/F: 51N Patrolled the line but found nothing Cause : Lightning |  | 1 | 14:40 | Afternoon | Thursday | 2019 | 4
10761 | 2019-04-04 23:38 | 2019-04-04 23:38 | 13.8KV 4B FEEDER #6 | Cloudy | Lightning | 2 | 4B fdr#6 Load dropped 91A(95-3A) 4B fdr#4 Load dropped 115A(123-8A) WIP 4B fdr#5 Load dropped 181A(186-5A) WIP Not checked Yet |  | 1 | 23:38 | Night | Thursday | 2019 | 4
10762 | 2019-04-04 23:38 | 2019-05-04 09:01 | 13.8KV 4B FEEDER #6 | Cloudy | Lightning | 2 | Checked & found Recl.4B-148 T/R 1x, Ctr: 80-81, R?F: 51N Patrolled the Line @0 broken Deadend Insulator O/p 4B-124 Cause : Lightning |  | 1 | 23:38 | Night | Thursday | 2019 | 4
10763 | 2019-05-04 08:21 | 2019-05-04 08:21 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Pin Insulator | 4 | Bangko fdr# ! load dropped 94A (166-72A) Bangko GFPC T/R 1x. Ground fault Alarm at Bangko fdr#1. Bangko fdr# 4 load dropped 80A (172-92A), Pump Off. Bangko fdr# 2 load dropped 62A (251-189A), Pump Off. Not checked yet. |  | 1 | 8:21 | Morning | Saturday | 2019 | 5
10764 | 2019-05-04 18:27 | 2019-05-04 18:27 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 0 | C. Duri 13.8KV ACB fdr #16 T/R 1X ctr:339-340 R/F: 51N, 51 @1 @3. Not checked yet. |  | 1 | 18:27 | Afternoon | Saturday | 2019 | 5
10765 | 2019-05-04 18:27 | 2019-10-04 16:24 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Animal | 0 | Checked and found CD fdr #16 T/R 1x, ctr: 339 - 340, R/F: 51N Patrolled the line and found dead animal on pole 09-N2-01 Cause : Animal |  | 1 | 18:27 | Afternoon | Saturday | 2019 | 5
10766 | 2019-06-04 00:25 | 2019-06-04 00:25 | 13.8KV 8D FEEDER #3 | Fair | Guy Wire | 80 | 00:25 8D OCB fdr#3 T/LO. 8D fdr#1 Load dropped 49A (104-55A). 8D fdr#2 Load dropped 26A (86-60A). 8D fdr#5 Load dropped 24A(63-39A). 02:15 Checked & found 8D OCB fdr#3 T/LO Ctr:247 R/F 51@1@2@3. Patrolled the line & found Broken Guy Wire o/p 9D-01 D/S Recl. 8D-30. Blocked & closed 8D OCB fdr#3, but failed. 03:25 Patrolled the line but found nothing. 03:45 Function test 8D OCB fdr#3 with open isolation switch, but failed. (Suspected OCB/Relay Problem). 03:55 Checked Over Current Relay, not operated stuck at @3 & Repaired. 04:00 Blocked & closed 8D OCB fdr#3, ok, then release the block. 04:20 Blocked & closed Recl. 8D-30, ok, then release the block. 09:50 Manually Open Recl. 8D-30. Repaired Guy Wire o/p 9D-01. 10:54 Blocked & closed Recl. 8D-30, ok, then release the block. Cause: Broken Guy Wire. |  | 1 | 0:25 | Night | Tuesday | 2019 | 6
10767 | 2019-06-04 09:55 | 2019-06-04 09:55 | BANGKO SUBSTATION | Fair | Planned Maintenance | 1 | 09:55 Manually Open Recl. Banko Cap Bank. Function test and Repair Hot Spot. (Shut off 5 wells and 1 WIP under BKO fdr #4 during the JOB). 10:23 Closed Recl. Banko Cap Bank (5 X 600Kvar). Cause: Plan Maintenance. |  | 1 | 9:55 | Morning | Tuesday | 2019 | 6
10768 | 2019-06-04 19:32 | 2019-06-04 19:32 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Powerline - Conductor | 15 | Pungut fdr #1 Load dropped 20A (72-52A). Not checked yet. |  | 1 | 19:32 | Night | Tuesday | 2019 | 6
10769 | 2019-06-04 19:32 | 2019-06-04 19:32 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Powerline - Conductor | 78 | 19:32 Pungut fdr #2 Load dropped 29A (49-20A). 19:45 It was reported no power at Intan Field. 21:00 Checked & found Recl 46BP-12 T/LO Ctr:534-539. Patrolled the line & found @1 Broken Conductor o/p 46BP-08. 22:45 Opened visual opening Recl. 46BP-12. (would be repaired tomorrow morning). Cause: Broken Conductor. |  | 1 | 19:32 | Night | Tuesday | 2019 | 6
10770 | 2019-06-04 19:32 | 2019-07-04 09:32 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Powerline - Conductor | 78 | 09:30 Repair broken conductor on pole 46-BP-17 (6 span was down) 11:52 Blocked and then close the RCL 46-BP-12, success then release the block Cause: broken conductor |  | 1 | 19:32 | Night | Tuesday | 2019 | 6
10771 | 2019-07-04 08:40 | 2019-07-04 08:40 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Unidentified | 0 | Menggala fdr #1 Load Dropped 125 A (185 - 160 A) Menggala GFPC T/R 1x Cause: Not Checked Yet. |  | 1 | 8:40 | Morning | Thursday | 2019 | 7
10772 | 2019-07-04 19:33 | 2019-07-04 19:33 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 72 | Rokan fdr#2 T/R 1x. Not checked yet. |  | 1 | 19:33 | Night | Thursday | 2019 | 7
10773 | 2019-07-04 19:33 | 2019-10-04 16:43 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning | 72 | Checkd and found RKN VCB fdr #2 T/R, ctr: 1288-1289, R/F: 51P @1 Patrolled the line and found broken LA @1, @2 at Kopar #10 Cause : Lightning |  | 1 | 19:33 | Night | Thursday | 2019 | 7
10774 | 2019-07-04 19:50 | 2019-07-04 19:50 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Unidentified | 59 | 19:50 Menggala fdr#1 T/R 1x Menggala GFPC T/R 1x. 20:15 Menggala fdr#1 T/R 1x again. Menggala GFPC T/R 1x again. |  | 1 | 19:50 | Night | Thursday | 2019 | 7
10775 | 2019-07-04 22:52 | 2019-07-04 22:52 | 13.8KV LIBO FEEDER #1 | Cloudy | Unidentified | 5 | LIBO OCB fdr#1 T/R 1x not checked yet |  | 1 | 22:52 | Night | Thursday | 2019 | 7
10776 | 2019-07-04 22:52 | 2019-08-04 16:26 | 13.8KV LIBO FEEDER #1 | Cloudy | Unidentified | 5 | Checked and found VCB LBO fdr #1 T/R 1x, ctr: 585 - 586, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 22:52 | Night | Thursday | 2019 | 7
10777 | 2019-08-04 10:39 | 2019-08-04 10:39 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 455 | 10:39 PTN fdr #1 (MSU fdr #1) dropped 77 A (196 - 119 A) Reported no power at disposal pump (WIP pump) at PTN GS 11:07 Manual Open Rokan fdr #2 (also include PTN fdr #2) Request by Rico Rigelindi (approved by Budi Gunawan) 13:27 Manual Close Rokan fdr #2 14:00 Checked and found RCL for 3700 kVA TX-A T/O and found cover box of Control RCL was Open. Block and then close the RCL, OK then release the block. Counter = 57 - 58 15:44 PTN fdr #1 dropped again 78 A (196 - 118 A) Reported no power at 2 WIP pumps at Petani GS 17:00 Checked and found RCL for TX-A T/LO, ctr: 58 - 59 Closed 4.16 kV Tie breaker TX-A & TX-B Cause: Under Investigation | 123 | 1 | 10:39 | Morning | Sunday | 2019 | 8
10778 | 2019-08-04 15:04 | 2019-08-04 15:04 | 13.8KV NORTH DURI FEEDER #11 | Rain and Lightning | Unidentified | 37 | N.Duri fdr#11 T/R 2x. Not checked yet. |  | 1 | 15:04 | Afternoon | Sunday | 2019 | 8
10779 | 2019-08-04 15:04 | 2019-11-04 18:16 | 13.8KV NORTH DURI FEEDER #11 | Rain and Lightning | Unidentified | 37 | Checked and found ND VCB fdr #11 T/R 1x, Ctr: 187 - 189, R/F 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 15:04 | Afternoon | Sunday | 2019 | 8
10780 | 2019-09-04 07:37 | 2019-09-04 07:37 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | 07:37 CD ACB fdr #16 T/R 1x, ctr: 340 - 341, R/F: 51N, 50P Cause: Not Checked Yet |  | 1 | 7:37 | Morning | Wednesday | 2019 | 9
10781 | 2019-09-04 07:37 | 2019-11-04 18:17 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked and found ACB CD fdr #16 T/R 1x, Ctr: 51N, R/F: 340 - 341 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 7:37 | Morning | Wednesday | 2019 | 9
10782 | 2019-09-04 16:35 | 2019-09-04 16:35 | MINAS POWER PLANT |  |  | 0 | 16:35 S/U MGT#7 and then Online at 16:58. |  | 1 | 16:35 | Afternoon | Wednesday | 2019 | 9
10783 | 2019-09-04 17:45 | 2019-09-04 17:45 | MINAS POWER PLANT |  |  | 0 | 17:45 offline and S/D MGT#8 for replace fuel nozzle. |  | 1 | 17:45 | Afternoon | Wednesday | 2019 | 9
10784 | 2019-10-04 10:07 | 2019-10-04 10:07 | 13.8KV 8C FEEDER #2 | Fair | Planned Maintenance | 21 | 10:07 Manually opened 8C VCB feeder #2. For installing Transformer at well 8E-61 (reactive well). 10:37 Manually blocked and closed 8C VCB feeder #2, and then released the block. Cause: Plan maintenance. |  | 1 | 10:07 | Morning | Friday | 2019 | 10
10785 | 2019-10-04 17:22 | 2019-10-04 17:22 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C Duri ACB #11 (feeder #1) T/R 1x Counter: 238-239 R/F: 51@1. Not patrolled yet. |  | 1 | 17:22 | Afternoon | Friday | 2019 | 10
10786 | 2019-10-04 17:22 | 14/04/2019 13:23 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found ACB CD fdr #1 T/R 1x, ctr: 238 - 239, R/F: 51N, 51P Patrolled the line but found nothing Cause : Unidentified |  | 1 | 17:22 | Afternoon | Friday | 2019 | 10
10787 | 2019-10-04 17:42 | 2019-10-04 17:42 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 0 | C Duri ACB #32 (feeder #8) T/R 1x Counter: 559-560 R/F: 51N. Not patrolled yet. |  | 1 | 17:42 | Afternoon | Friday | 2019 | 10
10788 | 2019-10-04 17:42 | 14/04/2019 13:25 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 0 | Checked and found ACB CD fdr #8 T/R 1x, ctr: 459 - 460, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 17:42 | Afternoon | Friday | 2019 | 10
10789 | 2019-11-04 02:32 | 2019-11-04 02:32 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 133 | 02:32 Darling VCB fdr #3 T/SO GFPC TX-1 Darling T/SO 04:06 Checked and found DRL VCB fdr #3 T/SO, ctr: 251- 252, R/F: 51N GFPC TX-1 T/SO, ctr: 329 - 330, R/F: 50N 04:30 Close RCL GFPC TX-1 (Remote and Locat) but failed Discuss with TL TDO and decide to bypass the GFPC by MTCE team before close the DRL VCB fdr #3 (waiting MTCE crew) 06:25 Bypassed GFPC TX-1 of Darling SS and then isolate the RCL (Under Investigation) 06:33 Blocked and then close DRL VCB fdr #3, OK then release the block. Cause: Not Patrolled Yet. |  | 1 | 2:32 | Night | Monday | 2019 | 11
10790 | 2019-11-04 02:32 | 14/04/2019 13:29 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 133 | Checked and found DRLG VCB fdr #3 T/SO, ctr: 251 - 252, R/F:51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 2:32 | Night | Monday | 2019 | 11
10791 | 2019-11-04 16:26 | 2019-11-04 16:26 | 13.8KV PEMATANG FEEDER #1 | Lightning | Lightning | 0 | Pematang OCB feeder #1 T/R 1x . Not checked yet. |  | 1 | 16:26 | Afternoon | Monday | 2019 | 11
10792 | 2019-11-04 16:26 | 14/04/2019 13:27 | 13.8KV PEMATANG FEEDER #1 | Lightning | Lightning | 0 | Checked and found PMT OCB fdr #1 T/R 1x, ctr: 178 - 179, R/F: 51N Patrolled the line and found Broken pin @3 o/p 35-BC-22 Cause : Lightning |  | 1 | 16:26 | Afternoon | Monday | 2019 | 11
10793 | 2019-11-04 16:26 | 2019-11-04 16:26 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Lightning | 0 | 16:26 Pematang feeder #2 load dropped 58A (98-58A). It was reported no power to Tx 3,75 Mva 18:50 Checked and found Recloser #B T/O Counter: 47-48. Patrolled the line found nothing. 18:55 Blocked and closed Recloser #B --> OK. and then released the block. Cause: Suspected Lightning. |  | 1 | 16:26 | Afternoon | Monday | 2019 | 11
10794 | 2019-11-04 16:26 | 2019-11-04 16:26 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Unidentified | 0 | Rangau feeder #2 load dropped 150A (201-51A). Not checked yet. |  | 1 | 16:26 | Afternoon | Monday | 2019 | 11
10795 | 2019-11-04 16:26 | 14/04/2019 13:35 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found RCL 23-BD-01 T/R 1x, ctr: 370-371, R/F: None Patrolled the line but found nothing Cause : Unidentified |  | 1 | 16:26 | Afternoon | Monday | 2019 | 11
10796 | 2019-11-04 19:17 | 2019-11-04 19:17 | 4.16KV SO RUMBAI FEEDER #1 | Rain and Lightning | Lightning | 0 | 19:17 Reported pumps of WTP Rumbai was OFF Reported no Power at Complex Enau 20:22 Reported no power for WTP Rumbai 20:28 Reported no power at FERT Rumbai 20:49 Checked and found: - South RBI feeder #3 is Close - South RBI feeder #1 T/SO, ctr: 478 (not change), R/F: 50P @1 @3 21:12 Block and close South RBI feeder #1, OK then release the block. Cause: Not Patrolled Yet |  | 1 | 19:17 | Night | Monday | 2019 | 11
10797 | 2019-11-04 19:17 | 14/04/2019 21:04 | 4.16KV SO RUMBAI FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked and found RCL South RBI fdr #1 T/SO, ctr: 478 (not change), R/F 50P Patrolled the line and found broken dead end o/p 5RG-3 Cause : Lightning |  | 1 | 19:17 | Night | Monday | 2019 | 11
10798 | 2019-12-04 09:47 | 2019-12-04 09:47 | 13.8KV 4B FEEDER #3 | Fair | Lightning | 0 | 4B VCB feeder #3 T/R 1x. Not checked yet. |  | 1 | 9:47 | Morning | Wednesday | 2019 | 12
10799 | 2019-12-04 09:47 | 18/04/2019 07:47 | 13.8KV 4B FEEDER #3 | Fair | Lightning | 0 | Checked & found 4B OCB fdr#3 T/R 1x Ctr:174-175 R/F:51@2@3. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 9:47 | Morning | Wednesday | 2019 | 12
10800 | 2019-12-04 09:47 | 2019-12-04 09:47 | 13.8KV 4B FEEDER #1 | Fair | Lightning | 0 | 4B feeder #1 load dropped 66A (73-7A). 4B feeder #2 load dropped 26A (41-15A). Not5 checked yet. |  | 1 | 9:47 | Morning | Wednesday | 2019 | 12
10801 | 2019-12-04 09:47 | 18/04/2019 07:47 | 13.8KV 4B FEEDER #1 | Fair | Lightning | 0 | Checked & found Recl. 4B-101 T/R 2x Ctr:638-640 Patrolled the lint & found @1@2 Broken LA o/p 4B-102. Cause : Lightning. |  | 1 | 9:47 | Morning | Wednesday | 2019 | 12
10802 | 2019-12-04 22:13 | 2019-12-04 22:13 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Unidentified | 67 | Rokan 13.8KV VCB fdr #2 T/R 1X. (also Petani fdr #2). Not checked yet. |  | 1 | 22:13 | Night | Wednesday | 2019 | 12
10803 | 2019-04-13 19:32 | 2019-04-13 19:32 | 13.8KV NORTH DURI FEEDER #1 | Lightning | Unidentified | 0 | 19:32 ND VCB fdr #1 T/R 2x Cause: Not Checked Yet |  | 1 | 19:32 | Night | Saturday | 2019 | 4
10804 | 2019-04-13 19:32 | 2019-04-13 19:32 | 13.8KV NORTH DURI FEEDER #2 | Lightning | Unidentified | 0 | 19:32 ND fdr #2 Load Dropped 31 A (192 - 161 A) Cause: Not Checked Yet |  | 1 | 19:32 | Night | Saturday | 2019 | 4
10805 | 2019-04-14 01:39 | 2019-04-14 01:39 | NORTH DURI POWER PLANT | Fair | Under investigation | 515 | 01:39 NDC CT-3 T/O, caused by fire alarm System load shedding level-2, frequency 59.92 Hz 3D fdr #2 T/O, closed at 03:28 ---> 266 Bbls /27 wells 3D fdr #3 T/O, closed at 03:27 ---> 39 Bbls /15 wells 3D fdr #5 T/O, closed at 01:45 3D fdr #6 T/O, closed at 01:49 4B fdr #1 T/O, closed at 02:31 4B fdr #4 T/O, closed at 01:50 4B fdr #5 T/O, closed at 01:52 4B fdr #6 T/O, closed at 02:57 4D fdr #2 T/O, closed at 03:49 ---> 79 Bbls /24 wells 4D fdr #3 T/O, closed at 02:59 ---> 25 Bbls /11 wells 4D fdr #4 T/O, closed at 02:58 ---> 100 Bbls / 16 wells 4D fdr #5 T/O, closed at 03:05 ---> 32 Bbls /11 wells 4D fdr #6 T/O, closed at 02:00 ---> 5 Bbls /2 wells 5B fdr #1 T/O, closed at 03:29 ---> 103 Bbls /13 wells 5B fdr #3 T/O, closed at 02:43 --->163 Bbls / 19 wells 8C fdr #1 T/O, closed at 02:50 8D fdr #1 T/O, closed at 02:54 8D fdr #3 T/O, closed at 02:52 8D fdr #10 T/O, closed at 02:51 SURAM fdr #2 T/O, closed 03:33 BERUK fdr #1 T/O, closed at 03:14 BERUK fdr #2 T/O, closed at ZAMRUD fdr #1 T/O, closed at ZAMRUD fdr #2 T/O, closed at ZAMRUD fdr #4 T/O, closed at 3D fdr #4 Dropped 14 A (151 - 137 A) 6DN fdr #1 Dropped 11 A (148 - 137 A) 6DN fdr #3 Dropped 60A (125 - 65 A) 6DN fdr #6 Dropped 11 A (199 - 188 A) 8D fdr #7 Dropped 17 A (272 - 255 A) 8D fdr #8 Dropped 124 A (189 - 65 A) 8C fdr #4 Dropped 41 A (300 - 259 A) 02:34 S/U MGT#8 and then online at 02:57 02:35 S/U CDGT#4 and then online at 02:48 05:31 Alarm low frequency (59.90 Hz) Reason: low generation due to low gas supply for MGT 05:43 Manual Open 5B feeder #2 05:47 Manual Open 4B feeder #2, closed again at 05:51 (GS-6 HMI) 05:51 Manual Open 5B feeder #1. 06:17 Manual Open 3D feeder #2. 08:29 Manually opened 4D OCB feeder #4 Closed at :10:24 Request: GS #4. 08:30 Manually closed 5B OCB feeder #2. 09:57 Manually closed 5B OCB feeder #1. 10:29 Manually closed 3D OCB feeder #2. Cause: Under Investigation | 0 | 1 | 1:39 | Night | Sunday | 2019 | 4
10806 | 2019-04-14 01:39 | 2019-04-14 01:39 | NORTH DURI POWER PLANT |  |  | 0 | NDC CT-3 Tripped, Cause: FM 200 (fire alarm) |  | 1 | 1:39 | Night | Sunday | 2019 | 4
10807 | 2019-04-14 02:34 | 2019-04-14 02:34 | MINAS POWER PLANT | Fair |  | 0 | MGT # S/U and then online at 02:57 due to NDC CT-3 Tripped cause by fire alarm. |  | 1 | 2:34 | Night | Sunday | 2019 | 4
10808 | 2019-04-14 02:35 | 2019-04-14 02:35 | CENTRAL DURI POWER PLANT |  |  | 2 | CDGT #4 S/U and then online at 02:48 due to NDC CT-3 problem after tripped by fire alarm. |  | 1 | 2:35 | Night | Sunday | 2019 | 4
10809 | 2019-04-14 14:40 | 2019-04-14 14:40 | MINAS POWER PLANT |  |  | 0 | 14:40 S/U MGT #9 . 14:55 Online to the system. |  | 1 | 14:40 | Afternoon | Sunday | 2019 | 4
10810 | 2019-04-14 17:08 | 2019-04-14 17:08 | SINABUNG MINI SUBSTATION | Fair | Unidentified | 0 | 17:08 It was reported no power at Gading Office , Security. 18:08 Checked and found Recloser Sinabung T/LO Counter: 68-80. 18:12 Manually blocked and closed Recloser Sinabung --> OK. and then released the block. 18:48 Reported no Power again at Gading Office, Security 19:56 Re-patrolled the line and found suspect high trees near Sinabung SS and loss connection at HLC near Gading Office (NN pole) 21:00 Cut the high trees and repair the HLC 21:35 Block and Close RCL 4.16 kV of Sinabung SS, but Tripped again. R/F: Tripped by SGF 21:58 Isolate and checked RCL 4.16 kV of Sinabung SS, NORMAL 22:33 Re-patrolled the line but found nothing 22:45 Blocked (non reclosing) 4.16 kV RCL of Mini IT SS Close 4.16 kV LBS 1-1-48 near Betha office, success. (the load of Mini Sinabung SS has transferred to Mini IT SS Last Counter of RCL 4.16 kV Sinabung SS = 121 Cause: Unidentified. |  | 1 | 17:08 | Afternoon | Sunday | 2019 | 4
10811 | 2019-04-14 18:36 | 2019-04-14 18:36 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 65 | 18:36 Ketigul VCB feeder #2 T/R 1x. 18:40 Ketigul VCB feeder #2 T/R again. Not checked yet. |  | 1 | 18:36 | Afternoon | Sunday | 2019 | 4
10812 | 2019-04-15 01:12 | 2019-04-15 01:12 | MINAS POWER PLANT |  |  | - | 01:12 MGT-6 Tripped by fire alarm (CO2 released). Status Not Standby Cause: Under investigation. |  | 1 | 1:12 | Night | Monday | 2019 | 4
10813 | 2019-04-15 06:13 | 2019-04-15 06:13 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Guy Wire | 321 | 06:13 C. Duri fdr #1 load dropped 67A (111-44A). 08:10 Checked and found Recloser: 39-AV-36 T/LO Counter: 271-275. Patrolled the line found broken guy wire touch to powerline on pole 35-AF-09 11:33 Opened LBS: 37-AQ-08 to isolate. 11:34 Manually block and closed Recloser: 39-AV-36 --> OK. and then released the block. 15:10 Closed LBS: 37-AQ-08. Cause: Broken guy wire. |  | 1 | 6:13 | Morning | Monday | 2019 | 4
10814 | 2019-04-15 18:10 | 2019-04-15 18:10 | 13.8KV NORTH DURI FEEDER #11 | Lightning | Unidentified | 2 | N Duri VCB feeder #11 T/R 1x. N Duri GFPC T/O. Not checked yet. |  | 1 | 18:10 | Afternoon | Monday | 2019 | 4
10815 | 2019-04-15 18:41 | 2019-04-15 18:41 | NORTH DURI POWER PLANT |  |  | - | 17:00 S/U NDC #3 and then Online the unit at 18:41. 18:41 Closed 230 KV GCB #35 by NDC. 18:42 Closed 230 KV GCB #33 by DSC. |  | 1 | 18:41 | Afternoon | Monday | 2019 | 4
10816 | 2019-04-16 07:34 | 2019-04-16 07:34 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Tree | 0 | C Duri ACB #21 (feeder #4) T/R 1x. Not checked yet. |  | 1 | 7:34 | Morning | Tuesday | 2019 | 4
10817 | 2019-04-16 07:34 | 2019-04-18 07:34 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Tree | 0 | Checked & found C.Duri ACB Fdr#4 T/R 1x Ctr:518-519 R/F:51N. Patrolled the line & Found Danger trees near pole 09-Q1-01. Cause : Tree. |  | 1 | 7:34 | Morning | Tuesday | 2019 | 4
10818 | 2019-04-16 07:35 | 2019-04-16 07:35 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 0 | OKB OCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 7:35 | Morning | Tuesday | 2019 | 4
10819 | 2019-04-16 07:35 | 2019-04-19 07:52 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Unidentified | 0 | Checked & found OKB VCB fdr#2 T/R 1x, Ctr: 1364 1365, R/F: 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 7:35 | Morning | Tuesday | 2019 | 4
10820 | 2019-04-16 07:35 | 2019-04-16 07:35 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Cloudy | Lightning | 0 | CKBS VCB feeder #1 T/R 1x. CKBS feeder #2 load dropped 50A (258-208A). Not checked yet. |  | 1 | 7:35 | Morning | Tuesday | 2019 | 4
10821 | 2019-04-16 07:35 | 2019-04-21 09:03 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Cloudy | Lightning | 0 | Checked & found CKB VCB fdr#1 T/R 2x, Ctr: 211-213, R/F: none Patrolled the Line, found @2 broken Deadend O/p 35-CT-18 Cause : Lightning |  | 1 | 7:35 | Morning | Tuesday | 2019 | 4
10822 | 2019-04-16 09:39 | 2019-04-16 09:39 | 4.16KV NO RUMBAI FEEDER #1 | Fair | Planned Maintenance | - | 09:39 Manually open LBS 2RD-07 D/S N Rumbai feeder#1. For replacing broken fuse on pole 2RD-02. 10:34 Manually close LBS 2RD-07 D/S N Rumbai feeder#1. Cause: Plan maintenance. |  | 1 | 9:39 | Morning | Tuesday | 2019 | 4
10823 | 2019-04-16 10:33 | 2019-04-16 10:33 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 59 | 10:33 Manually open LBS : 5C-59 D/S 6D feeder #1. For replacing Transformer at well 6B-25N. 11:24 Manually open 6D OCB feeder #1 11:25 Manually close LBS : 5C-59. 11:25 Manually blocked and closed 6D OCB feeder #1 --> OK. and then released the block. Cause: Plan maintenance. |  | 1 | 10:33 | Morning | Tuesday | 2019 | 4
10824 | 2019-04-16 13:18 | 2019-04-16 13:18 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Animal | 0 | Batang OCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 13:18 | Afternoon | Tuesday | 2019 | 4
10825 | 2019-04-16 13:18 | 2019-04-20 17:29 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Animal | 0 | Checked & found Batang VCB fdr#2 T/R 1x, Ctr: 184-185, R/F: 51 @123 Patrolled the Line, Found @123 Fuse holder Down cause animal (bird) death O/p 35-A-28 Rantau Bais PAD 65 Cause: Animal |  | 1 | 13:18 | Afternoon | Tuesday | 2019 | 4
10826 | 2019-04-16 13:24 | 2019-04-16 13:24 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Tree | 0 | D.Field VCB 51 (feeder#4) T/R 2x. Not checked yet. |  | 1 | 13:24 | Afternoon | Tuesday | 2019 | 4
10827 | 2019-04-16 13:24 | 2019-04-18 13:24 | 13.8KV DURI FIELD FEEDER #4 | Rain and Lightning | Tree | 0 | Checked & found D.Field ACB fdr#4 T/R 1x Ctr:519(Not operated) R/F:None. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 13:24 | Afternoon | Tuesday | 2019 | 4
10828 | 2019-04-16 13:25 | 2019-04-16 13:25 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Dead End Insulator | 28 | Batang OCB fdr#3 T/R 1x. Batang GFPC T/R 1x. Not checked yet. |  | 1 | 13:25 | Afternoon | Tuesday | 2019 | 4
10829 | 2019-04-16 13:25 | 2019-04-20 17:31 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Dead End Insulator | 28 | Checked & found Batang VCB fdr#1 T?R 1x, Ctr: 378-379, R/F: 51 @1 Patrolled the Line, Found @1 Broken Deadend O/p 36-AM-32 Cause: Broken Deadend |  | 1 | 13:25 | Afternoon | Tuesday | 2019 | 4
10830 | 2019-04-16 13:31 | 2019-04-16 13:31 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 28 | C.Duri feeder #1 load dropped 39A (116-77A). Not checked yet. |  | 1 | 13:31 | Afternoon | Tuesday | 2019 | 4
10831 | 2019-04-16 13:31 | 2019-04-20 07:44 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | 28 | Checked & found Recl. 41-AW-62 T/R 1x, Ct4r: NA, R/F: 51 @2 Patrolled the Line, found @2 broken Pin Insulator O/P 40-AW-16 Cause : Lightning |  | 1 | 13:31 | Afternoon | Tuesday | 2019 | 4
10832 | 2019-04-16 13:40 | 2019-04-16 13:40 | MINAS POWER PLANT |  |  | - | 13:40 Offline MGT #11 and then S/D the unit for standby. |  | 1 | 13:40 | Afternoon | Tuesday | 2019 | 4
10833 | 2019-04-16 14:05 | 2019-04-16 14:05 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Powerline - Conductor | 384 | Menggala OCB fdr#1 T/O 1x. Not checked yet. |  | 1 | 14:05 | Afternoon | Tuesday | 2019 | 4
10834 | 2019-04-16 14:05 | 2019-04-20 14:56 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Powerline - Conductor | 384 | Checked & found Menggala VCB fdr#1 T/LO, Ctr: 352-355, R/F: 51N Patrolled the Line, @2 Broken Pin Conductor O/p 20-AN-04 Cause : Conductor |  | 1 | 14:05 | Afternoon | Tuesday | 2019 | 4
10835 | 2019-04-16 14:07 | 2019-04-16 14:07 | 13.8KV MENGGALA FEEDER #2 | Rain and Lightning | Unidentified | 0 | Ketigul fdr#2 load dropped 179A (243-64A). Not checked yet. |  | 1 | 14:07 | Afternoon | Tuesday | 2019 | 4
10836 | 2019-04-16 14:07 | 2019-04-20 17:45 | 13.8KV MENGGALA FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found Ketigul VCB Fdr#2 , its Normal, Counter not changes Patrolled the Line, Found Recl. 29-AL-03 T/R 1x, Ctr: 171-172, R/F: 51N (MENGGALA fDR#2) Cause : Unidentified |  | 1 | 14:07 | Afternoon | Tuesday | 2019 | 4
10837 | 2019-04-16 14:10 | 2019-04-16 14:10 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Pin Insulator | 101 | Bekasap VCB fdr#6 T/R 1x. Not checked yet. |  | 1 | 14:10 | Afternoon | Tuesday | 2019 | 4
10838 | 2019-04-16 14:10 | 2019-04-20 15:23 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Pin Insulator | 101 | Checked & found Bekasap VCB fdr#6 T/R: 376-376, R/F: 51 @1 Patrolled the Line, found @1 Broken Pin Insulator O/p 38-BE-10 Cause : Pin Insulator |  | 1 | 14:10 | Afternoon | Tuesday | 2019 | 4
10839 | 2019-04-16 14:17 | 2019-04-16 14:17 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning Arrester | 67 | Rokan VCB feeder#2 T/R 1x. Not checked yet. |  | 1 | 14:17 | Afternoon | Tuesday | 2019 | 4
10840 | 2019-04-16 14:17 | 2019-04-20 17:33 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Lightning Arrester | 67 | Checked & found Rokan VCB fdr#2 T/R: 1291-1292, R/F: 51 @B Patrolled the Line, found @B Broken L.A O/p 31-AV-30 Cause : Lightning Arrester |  | 1 | 14:17 | Afternoon | Tuesday | 2019 | 4
10841 | 2019-04-16 14:19 | / | MINAS POWER PLANT |  |  | 48 | - |  | 1 | 14:19 | Afternoon | Tuesday | 2019 | 4
10842 | 2019-04-16 14:19 | 2019-04-16 14:19 | 13.8KV BEKASAP FEEDER #2 | Fair | Construction Job | 274 | 14:19 Manually opened Bekasap VCB fdr#2.------>Closed 15:40. 14:19 Manually opened Bekasap VCB fdr#3.------>Closed 15:41. 14:19 Manually opened Bekasap VCB fdr#6.------>Closed 15:42. For maintain water level. Request: Bekasap GS. |  | 1 | 14:19 | Afternoon | Tuesday | 2019 | 4
10843 | 2019-04-16 14:27 | 2019-04-16 14:27 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 29 | 6D OCB fdr#4 T/R 1x. Not checked yet. |  | 1 | 14:27 | Afternoon | Tuesday | 2019 | 4
10844 | 2019-04-16 14:27 | 2019-04-19 20:39 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 29 | Checked & found 6D VCB fdr#4 T/R 1x, Ctr: 563-567, R/F: 51 @2 Patrolled the line, found @2 Broken pin insulator O/P 5C-124 Cause : Lightning |  | 1 | 14:27 | Afternoon | Tuesday | 2019 | 4
10845 | 2019-04-16 14:27 | 2019-04-16 14:27 | 13.8KV 6D FEEDER #6 | Rain and Lightning | Follow Another Outage | 19 | 6D fdr#6 load dropped 187A (195-8A). Not checked yet. |  | 1 | 14:27 | Afternoon | Tuesday | 2019 | 4
10846 | 2019-04-16 14:36 | 2019-04-16 14:36 | 13.8KV 6DN FEEDER #4 | Rain and Lightning | Lightning | 3 | 6DN fdr#4 load dropped 44A (199-155A). Not checked yet. |  | 1 | 14:36 | Afternoon | Tuesday | 2019 | 4
10847 | 2019-04-16 14:36 | 2019-04-24 17:34 | 13.8KV 6DN FEEDER #4 | Rain and Lightning | Lightning | 3 | Checked & found 6DN VCB fdr#4 T/R 2x, Ctr: 563-565, R/F: 51N Patrolled the Line, @1 Broken Pin Insulator O/p 5C-124 Cause : Lightning |  | 1 | 14:36 | Afternoon | Tuesday | 2019 | 4
10848 | 2019-04-16 14:36 | 2019-04-16 14:36 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 0 | 6DN fdr#6 load dropped 133A (183-50A). Not checked yet. |  | 1 | 14:36 | Afternoon | Tuesday | 2019 | 4
10849 | 2019-04-16 14:36 | 2019-04-19 08:59 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 0 | Checked & found Rcl. 6E-30 T/R 1x, Ctr: 44-45, R/F: NONE Patrolled the Line, Found @3 Broken L.A O/P 6E-08 Cause : Lightning |  | 1 | 14:36 | Afternoon | Tuesday | 2019 | 4
10850 | 2019-04-16 14:40 | 2019-04-16 14:40 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 40 | S.Bekasap fdr#1 load dropped 132A (138-6A). Not checked yet. |  | 1 | 14:40 | Afternoon | Tuesday | 2019 | 4
10851 | 2019-04-16 14:40 | 2019-04-18 14:22 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 40 | Checked & found Recl. 36-BI-18 T/R 1x, Ctr: 180-181, R/F: 50N. Patrolled the Line, Found @2 broken L.A O/Top well Sakti #1 Cause : Lightning |  | 1 | 14:40 | Afternoon | Tuesday | 2019 | 4
10852 | 2019-04-16 14:51 | 2019-04-16 14:51 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 0 | CKBS fdr#5 load dropped 199A (238-39A). Not checked yet. |  | 1 | 14:51 | Afternoon | Tuesday | 2019 | 4
10853 | 2019-04-16 14:51 | 2019-04-21 14:51 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found Recl 36CU25 T/R 5x Ctr:320-325. Patrolled the line & found @2 Broken Dead End Insulator o/p 35CS20. Cause : Lightning. |  | 1 | 14:51 | Afternoon | Tuesday | 2019 | 4
10854 | 2019-04-17 02:06 | 2019-04-17 02:06 | 13.8KV ROKAN FEEDER #2 | Drizzle | Lightning Arrester | 67 | 02:06 RKN VCB fdr #2 (+PTN fdr #2) T/R 1x Cause: Not Checked Yet |  | 1 | 2:06 | Night | Wednesday | 2019 | 4
10855 | 2019-04-17 02:06 | 2019-04-20 17:35 | 13.8KV ROKAN FEEDER #2 | Drizzle | Lightning Arrester | 67 | Checked & found Rokan VCB fdr#2 T/R 1x, Ctr: 1292-1294, R/F: 51 @3 Patrolled the Line, Found @3 Broken L.A O/p 31-AV-30 Cause : Lightning Arrester |  | 1 | 2:06 | Night | Wednesday | 2019 | 4
10856 | 2019-04-17 08:45 | 2019-04-17 08:45 | 13.8KV SINTONG FEEDER #2 | Cloudy | Dead End Insulator | 65 | Sintong VCB fdr#2 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 8:45 | Morning | Wednesday | 2019 | 4
10857 | 2019-04-17 08:45 | 2019-04-20 15:23 | 13.8KV SINTONG FEEDER #2 | Cloudy | Dead End Insulator | 65 | Checked & found Sintong VCB fdr#2 T/R 1x, Ctr: 490-491, R/F: 51N Patrolled the Line, found @3 Broken Dead End Insulator O/p 26-AE-19 Cause : Dead End Insulator |  | 1 | 8:45 | Morning | Wednesday | 2019 | 4
10858 | 2019-04-17 11:41 | 2019-04-17 11:41 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Dead End Insulator | 25 | OKB VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 11:41 | Morning | Wednesday | 2019 | 4
10859 | 2019-04-17 11:41 | 2019-04-20 14:26 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Dead End Insulator | 25 | Checked & found OKB VCB fdr#2 T?R 365-366, R/F: 51N @3 Patrolled the Line, found @3 broken Deadend Insulator O/p 38-CX-02 Cause : Deadend Insulator |  | 1 | 11:41 | Morning | Wednesday | 2019 | 4
10860 | 2019-04-18 00:32 | 2019-04-18 00:32 | 13.8KV KETIGUL FEEDER#2 | Fair | Pin Insulator | 61 | 00:32 Ketigul VCB feeder #2 T/R 1x. It was reported no power at Pagar GS. 02:14 Checked and found Recloser: 29-AL-03 T/LO Counter: 166-173. 02:20 Manually blocked and closed Recloser: 29-AL-03 --> OK. and then released the block. 02:42 Checked Ketigul VCB feeder #2 T/R 2x Counter:322-324 R/F: 51N. Cause: Not patrolled yet. |  | 1 | 0:32 | Night | Thursday | 2019 | 4
10861 | 2019-04-18 00:32 | 2019-04-20 15:03 | 13.8KV KETIGUL FEEDER#2 | Fair | Pin Insulator | 61 | Checked & found Ketigul Fdr#2 T/R 1x, Ctr: 236-237, R/F: 51N Patrolled the Line, Found @3 Broken Pin Insulator O/p 30-AJ-232 Cause : Pin Insulator |  | 1 | 0:32 | Night | Thursday | 2019 | 4
10862 | 2019-04-18 10:13 | 2019-04-18 10:13 | 13.8KV 4B FEEDER #6 | Fair | Planned Maintenance | 26 | 10:13 Manually Open REcl.4B-148. Replaced Broken Dead End Insulator o/p 4B-124. 11:10 Blocked & closed Recl 4B-148, then release the block. Cause: Plan Maintenance. |  | 1 | 10:13 | Morning | Thursday | 2019 | 4
10863 | 2019-04-19 07:01 | 2019-04-19 07:01 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 0 | C.Duri fdr#1 Load dropped 38A (113-75A). Not checked yet. |  | 1 | 7:01 | Morning | Friday | 2019 | 4
10864 | 2019-04-19 07:01 | 2019-04-20 10:47 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 0 | Checked & found Recl. 41-AW-62 T/R 1x, Ctr: 305-306, R/F: 51@2 Patrolled the Line, Found @2 broken Pin Insulator O/p 39 AW 28 Cause : Lightning |  | 1 | 7:01 | Morning | Friday | 2019 | 4
10865 | 2019-04-19 14:15 | 2019-04-19 14:15 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | 14:15 It was reported no power at 09-M3-02 (C.Duri fdr#1). 15:00 Checked & found Recl. 09-M3-01 T/O Ctr:77-78. Blocked & closed Recl. 09-M3-01, then release the block. Cause: Unidentified. |  | 1 | 14:15 | Afternoon | Friday | 2019 | 4
10866 | 2019-04-19 15:05 | 2019-04-19 15:05 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Lightning | 21 | Menggala VCB fdr#1 T/R 2x. Menggala GFPC T/R 2x. Not checked yet. |  | 1 | 15:05 | Afternoon | Friday | 2019 | 4
10867 | 2019-04-19 15:05 | 2019-04-20 14:47 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Lightning | 21 | Checked & found Menggala OCB fdr#1 T/R 1x, Ctr: 355-356, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 15:05 | Afternoon | Friday | 2019 | 4
10868 | 2019-04-19 15:26 | 2019-04-19 15:26 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Dead End Insulator | 25 | Sintong fdr#2 Load dropped 100A (187-87A). Not checked yet. |  | 1 | 15:26 | Afternoon | Friday | 2019 | 4
10869 | 2019-04-19 15:26 | 2019-04-20 15:23 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Dead End Insulator | 25 | Checked & found Recl. 28-AF-02, Ct4r: 458-459, R/F: 51N @3 Patrolled the Line, found @3 Broken Dead end O/p 28-AF-21 Cause: Dead End Insulator |  | 1 | 15:26 | Afternoon | Friday | 2019 | 4
10870 | 2019-04-19 17:17 | 2019-04-19 17:17 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Animal | 10 | Libo VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 17:17 | Afternoon | Friday | 2019 | 4
10871 | 2019-04-20 09:35 | 2019-04-20 09:35 | 13.8KV MENGGALA FEEDER #1 | Fair | Planned Maintenance | 95 | 09:35 Manually Opened Menggala VCB fdr#1 to Repair broken Conductor for Katodic protection transforer 11:05 Manually block & Closed Menggala VCB fdr#1, then released the block Cause: Planned Maintenance |  | 1 | 9:35 | Morning | Saturday | 2019 | 4
10872 | 2019-04-20 10:00 | 2019-04-20 10:00 | 13.8KV PUNGUT FEEDER #2 | Fair | Powerline - Jumper | - | 10:00 It Was reported no power at Okasam Field (Pungut fdr#2) Checked & found Recl. 44-BX-06 T/O Ctr: 422-424, R/F: none Patrolled the Line, found @2 broken jumper L.A (4 Wells were Down) 11:51 Blocked & Closed Recloser 44-BX-06, the released the block after isolated the broken jumper Cause: Jumper (L.A) |  | 1 | 10:00 | Morning | Saturday | 2019 | 4
10873 | 2019-04-20 13:02 | 2019-04-20 13:02 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Unidentified | 0 | North Duri VCB fdr#2 T/R 1x Not checked yet. |  | 1 | 13:02 | Afternoon | Saturday | 2019 | 4
10874 | 2019-04-20 13:02 | 2019-04-25 13:21 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found VCB ND fdr #2 T/R 1x, ctr: 279-280, R/F: 50P Patrolled the line but found nothing Cause : Unidentified |  | 1 | 13:02 | Afternoon | Saturday | 2019 | 4
10875 | 2019-04-20 13:08 | 2019-04-20 13:08 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Pin Insulator | 0 | North Duri VCB fdr#2 T/R 1x North Duri GFPC T/R 1x Not checked yet |  | 1 | 13:08 | Afternoon | Saturday | 2019 | 4
10876 | 2019-04-20 13:08 | 2019-04-25 13:25 | 13.8KV NORTH DURI FEEDER #8 | Rain and Lightning | Pin Insulator | 0 | Checked and found ND fdr #8 T/R 1x, ctr: 94-95, R/F: 50P Patrolled the line and found broken pin insulator @3 on pole ND-11-B Cause : Pin Insulator |  | 1 | 13:08 | Afternoon | Saturday | 2019 | 4
10877 | 2019-04-20 13:46 | 2019-04-20 13:46 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 69 | Ketigul VCB fdr#2 T/R 1x Not checked yet |  | 1 | 13:46 | Afternoon | Saturday | 2019 | 4
10878 | 2019-04-20 14:38 | 2019-04-20 14:38 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Unidentified | 59 | 4D VCB fdr#3 T/R 1x Not checked yet |  | 1 | 14:38 | Afternoon | Saturday | 2019 | 4
10879 | 2019-04-20 14:38 | 2019-02-05 02:45 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Unidentified | 59 | Checked and found VCB 4D fdr #3 T/R 1x, counter 268 – 269, R/F: 51 @1,2,3, Patrolled the line but found nothing Cause: Unidentified |  | 1 | 14:38 | Afternoon | Saturday | 2019 | 4
10880 | 2019-04-20 14:38 | 2019-04-20 14:38 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 17 | 4D VCB fdr#5 T/R 1x Not checked yet |  | 1 | 14:38 | Afternoon | Saturday | 2019 | 4
10881 | 2019-04-20 14:38 | 2019-04-25 08:22 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 17 | Checked and found 4D VCB fdr #5 T/R 1x, ctr: 344-345, R/F: 51N Patrolled the line and found broken dead end @1 on pole 4D-09 Cause : Lightning |  | 1 | 14:38 | Afternoon | Saturday | 2019 | 4
10882 | 2019-04-20 14:39 | 2019-04-20 14:39 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 23 | 4D VCB fdr#4 T/R 1x. Not checked yet |  | 1 | 14:39 | Afternoon | Saturday | 2019 | 4
10883 | 2019-04-20 14:39 | 2019-05-05 08:38 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 23 | Checked and found OCB 4D fdr #4 T/R 1x, ctr: 280-281, R/F: 51N Patrolled the line and found broken pin insulator @2 o/p 4D-181 Cause : Lightning |  | 1 | 14:39 | Afternoon | Saturday | 2019 | 4
10884 | 2019-04-20 14:42 | 2019-04-20 14:42 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 0 | 5B VCB fdr#3 T/R 1x. Not checked yet |  | 1 | 14:42 | Afternoon | Saturday | 2019 | 4
10885 | 2019-04-20 14:42 | 2019-04-25 07:01 | 13.8KV 5B FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found 5B VCB fdr #1 T/R 1x, ctr: 408-409, R/F: 50N Patrolled the line and found broken pin @2 on NN pole. Cause : Lightning |  | 1 | 14:42 | Afternoon | Saturday | 2019 | 4
10886 | 2019-04-20 14:42 | 2019-04-20 14:42 | 13.8KV 5B FEEDER #1 | Rain and Lightning | Lightning | 0 | 5B Fdr#1 Load dropped 60a (82-22a) Not checked yet |  | 1 | 14:42 | Afternoon | Saturday | 2019 | 4
10887 | 2019-04-20 14:42 | 2019-04-20 14:42 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Unidentified | 0 | 5B Fdr#2 Load dropped 53A (181-78A) Not checked yet |  | 1 | 14:42 | Afternoon | Saturday | 2019 | 4
10888 | 2019-04-20 14:42 | 2019-02-05 02:45 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found all on normal condition. Cause: Unidentified |  | 1 | 14:42 | Afternoon | Saturday | 2019 | 4
10889 | 2019-04-20 18:11 | 2019-04-20 18:11 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 112 | 18:11 C.Duri ACB #11 (feeder #1) T/LO 4x. Ctr: 239-243, R/F: 50 51 @1, 51N. Patrolled the line found nothing. 19:13 Manually blocked and closed C.Duri ACB #11 (feeder #1) --> Success. and then released the block. Cause: Suspected Animal. |  | 1 | 18:11 | Afternoon | Saturday | 2019 | 4
10890 | 2019-04-21 05:57 | 2019-04-21 05:57 | 13.8KV 8D FEEDER #6 | Cloudy | Lightning | 0 | 8D VCB feeder #6 T/R 1x Not checked yet. |  | 1 | 5:57 | Morning | Sunday | 2019 | 4
10891 | 2019-04-21 05:57 | 2019-07-05 05:57 | 13.8KV 8D FEEDER #6 | Cloudy | Lightning | 0 | Checked and found 8D 13.8KV VCB feeder #6 T/R 1x ctr: 2064-2065 R/F :None. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 5:57 | Morning | Sunday | 2019 | 4
10892 | 2019-04-22 16:30 | 2019-04-22 16:30 | CENTRAL DURI POWER PLANT |  |  | 0 | Off line CGT#1, then S/D the unit for S/B. |  | 1 | 16:30 | Afternoon | Monday | 2019 | 4
10893 | 2019-04-23 10:00 | 2019-04-23 10:00 | 13.8KV 3D FEEDER #4 | Rain | Lightning | 70 | 10:00 3D VCB fdr#4 T/R 1x Checked & found Recl: 2D33 T/Lo, Ctr: 297-300, R/F: None 12:19 Block & Closed the Recloser, then released the block Cause: not patrolled yet |  | 1 | 10:00 | Morning | Tuesday | 2019 | 4
10894 | 2019-04-23 10:00 | 2019-07-05 10:00 | 13.8KV 3D FEEDER #4 | Rain | Lightning | 70 | Checked and found 3D 13.8KV OCB fdr #4 T/LO ctr: 4207-4210 R/F: 51 @1, @2 & @3. Patrolled the line but found nothing. Cause: Lightning. |  | 1 | 10:00 | Morning | Tuesday | 2019 | 4
10895 | 2019-04-23 10:37 | 2019-04-23 10:37 | 115KV SINTONG - BANGKO LINE | Cloudy | Unidentified | 441 | 10:37 115KV Line Sintong-Bangko GCB#22 T/R 1x Frequwency: 60.35 Hz NO Power at Substations of Bangko, Nella, S.Balam, and Pinang. 10:43 MGT#7 Manually Opened Generator breaker, then Closed at 10:48 Cause: Not checked yet | 1234 | 1 | 10:37 | Morning | Tuesday | 2019 | 4
10896 | 2019-04-23 10:43 | 2019-04-23 10:43 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Unidentified | 179 | Menggala Fdr#1 Load dropped 37A (172-135A) Not checked yet |  | 1 | 10:43 | Morning | Tuesday | 2019 | 4
10897 | 2019-04-23 18:44 | 2019-04-23 18:44 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Broken Fuse Cut Out | 33 | OKB VCB fdr#2 T/R 1x Not checked yet |  | 1 | 18:44 | Afternoon | Tuesday | 2019 | 4
10898 | 2019-04-23 18:44 | 2019-04-28 09:06 | 13.8KV KOTABATAK FEEDER #2 | Cloudy | Broken Fuse Cut Out | 33 | Checked and found OCB OKB fdr #2 T/R 1x, ctr: 1366-1367, R/F: 50N Patrolled line and found broken FCO @2 for Cap Bank near KB #76 o/p 37-CX-05 Cause : Broken Fuse Cut Out |  | 1 | 18:44 | Afternoon | Tuesday | 2019 | 4
10899 | 2019-04-24 08:45 | 2019-04-24 08:45 | 13.8KV S. BALAM FEEDER #4 | Fair | Unidentified | 357 | 08:45 South Balam fdr #4 T/R 1x South Balam fdr #1 dropped 26 A (140 - 124 A) Cause: Not Checked Yet |  | 1 | 8:45 | Morning | Wednesday | 2019 | 4
10900 | 2019-04-24 14:47 | 2019-04-24 14:47 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Planned Maintenance | 0 | 14:47 Manual Open RCL 04-5-32 (CD fdr #8) Purpose: MTCE team cut fallen trees that touch to power lines Cause: Planned Maintenance |  | 1 | 14:47 | Afternoon | Wednesday | 2019 | 4
10901 | 2019-04-25 20:15 | 2019-04-25 20:15 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Unidentified | 275 | 20:15 3D OCB fdr#2 T/LO. 3D GFPC T/R 5x. 22:03 Patrolled the line but found nothing. Blocked & closed 3D fdr#2 but failed. Found high trees near pole 3E-23 th 3E-24 and then trimming the trees 23:42 Blocked and closed VCB 3D fdr #2, but failed Continue tomorrow. Friday, April 26th, 2019 11:36 Separate the line by Open LBS 3E-64 and then Block & Close 3D fdr #2, OK Continue line patrol and found palm trees touch the power line. Cut the palm trees about 1 span under the power lines. 16:11 Close LBS 3E-64, 3D VCB fdr #2 T/O (on block position) Re-open the LBS 3E-64 and then close again 3D VCB fdr #2, OK Re-patrolled the line and found broken pin insulator o/p 3E-61 17:45 Replacing the broken pin are finished 17:49 Close LBS 3E-64 but 3D VCB fdr #2 T/O again (on block position) 17:50 Open again the LBS 3E-64 and then closed 3D VCB fdr #2, OK. Continue tomorrow due to heavy rain. Cause: Under Investigation. |  | 1 | 20:15 | Night | Thursday | 2019 | 4
10902 | 2019-04-25 20:15 | 2019-04-27 11:22 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Unidentified | 275 | 11:22 Reported found broken pin insulator o/p 4E-02 and already replaced. 11:24 Blocked 3D VCB fdr #2 + GFPC and then close LBS 3E-64 3D VCB fdr #2 T/O (on block) Open LBS 3E-64 then close 3D VCB fdr #2, OK. 14:09 Isolate U/G cables o/p 4D-17 14:10 Close again LBS 3E-64 but 3D VCB fdr #2 T/O again. Open LBS 3E-64 and then Close 3D VCB fdr #2, OK. 14:12 Close 3D VCB fdr #2, plan to transfer part line to 4D fdr #5 15:06 Blocked 4D fdr #5 then close LBS 4D-88A, 4D VCB fdr #5 T/O (on block). Open LBS 4D-88 and then close 4D VCB fdr #5, OK. 16:03 Disconnect T-Tap on pole 4E-06 16:04 Close again LBS 3E-64, OK Close LBS 4D-88A but 4D fdr #5 T/O again 16:06 Open LBS 4D-88A and then close VCB 4D fdr #5, OK Isolate cap bank on pole 4D-34 16:39 Close again LBS 4D-88A, 4D fdr #5 T/O (on block) Open LBS 4D-88A and then close VCB 4D fdr #5, OK Release block 4D fdr #5 18:51 Blocked VCB 4D fdr #5 and then close LBS 4D-88A VCB 4D fdr #5 T/O again 18:52 Open LBS 4D-88A and then close VCB 4D fdr #5, OK |  | 1 | 20:15 | Night | Thursday | 2019 | 4
10903 | 2019-04-25 20:15 | 2019-04-28 09:00 | 13.8KV 3D FEEDER #2 | Rain and Lightning | Unidentified | 275 | 09:00 Continue re-patrolled pawer line d/s 3D fdr #2 - Replaced pin insulator o/p : … - Open/Isolate LA o/p : … - Disconnect/Open HLC/T-Tap for u/g cable o/p 4E-34 - Disconnect T-Tap o/p 3E-03 17:24 Block VCB 4D fdr #5 Close LBS 4D-88A, OK. and then released the block. Cause: unidentified |  | 1 | 20:15 | Night | Thursday | 2019 | 4
10904 | 2019-04-25 20:31 | 2019-04-25 20:31 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Unidentified | 11 | 4D fdr#3 T/R 1x. 4D fdr#2 Load dropped 5A (92-37A). 4D fdr#1 Load dropped 133A (254-121A). Not checked yet. |  | 1 | 20:31 | Night | Thursday | 2019 | 4
10905 | 2019-04-25 20:31 | 2019-03-05 20:31 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Unidentified | 11 | 4D 13.8KV Feeder #3 T/R 1 X Ctr:268 – 269 R/F: 51 @ 1,@2,@3 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 20:31 | Night | Thursday | 2019 | 4
10906 | 2019-04-25 20:50 | 2019-04-25 20:50 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Unidentified | 27 | 6DN fdr#1 Load dropped 112A (128-16A). Not checked yet. |  | 1 | 20:50 | Night | Thursday | 2019 | 4
10907 | 2019-04-25 20:50 | 2019-03-05 20:50 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Unidentified | 27 | Checked and patrolled, but found nothing. Cause: un identified. |  | 1 | 20:50 | Night | Thursday | 2019 | 4
10908 | 2019-04-25 20:50 | 2019-04-25 20:50 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Unidentified | - | 6DN fdr#2 Load dropped 112A (230-118A). Not checked yet. |  | 1 | 20:50 | Night | Thursday | 2019 | 4
10909 | 2019-04-25 20:50 | 2019-02-05 02:50 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Unidentified | - | Checked and found all in normal condition Cause: Unidentified |  | 1 | 20:50 | Night | Thursday | 2019 | 4
10910 | 2019-04-25 20:52 | 2019-04-25 20:52 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Unidentified | - | 20:52 Minas ACB fdr#3 T/LO Ctr:80152-80154 R/F:51N, 51@1. 23:20 Blocked & closed Minas ACB fdr#3, then release the block. Not patrolled yet. |  | 1 | 20:52 | Night | Thursday | 2019 | 4
10911 | 2019-04-25 20:52 | 2019-03-05 20:52 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Unidentified | - | Checked and found Minas ACB fdr#3 T/LO Ctr:80152-80154 R/F:51N, 51@1. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 20:52 | Night | Thursday | 2019 | 4
10912 | 2019-04-25 21:24 | 2019-04-25 21:24 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Unidentified | 90 | 8C fdr#3 T/R 1x. 8C fdr#1 Load dropped 123A (169-46A). 8C fdr#2 Load dropped 38A (79-41A). Not checked yet. |  | 1 | 21:24 | Night | Thursday | 2019 | 4
10913 | 2019-04-25 21:24 | 2019-02-05 02:44 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Unidentified | 90 | Checked and found 8C fdr #3 T/R 1x, ctr: 520-521, R/F: 51P @1, @2, @3 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 21:24 | Night | Thursday | 2019 | 4
10914 | 2019-04-25 21:24 | 2019-04-25 21:24 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Unidentified | 1 | 8C fdr#4 T/r 1x. Not checked yet. |  | 1 | 21:24 | Night | Thursday | 2019 | 4
10915 | 2019-04-25 21:24 | 2019-02-05 02:45 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Unidentified | 1 | Checked and found 8C fdr #4 T/R 1x, ctr: 623-624, R/F: 50P @1, @2, @3 Patrolled the line but found nothing Cause: Unidentified |  | 1 | 21:24 | Night | Thursday | 2019 | 4
10916 | 2019-04-26 01:11 | 2019-04-26 01:11 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 0 | Ketigul Fdr#2 Load dropped 187A (242-55A Not checked yet |  | 1 | 1:11 | Night | Friday | 2019 | 4
10917 | 2019-04-26 01:11 | 2019-01-05 05:44 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 0 | Checked and found RCL 29-AL-03 T/R 2x, ctr: 172-174, R/F: None Patrolled the line but found nothing Cause : Unidentified |  | 1 | 1:11 | Night | Friday | 2019 | 4
10918 | 2019-04-26 01:37 | 2019-04-26 01:37 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Unidentified | - | Sintong Fdr#2 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 1:37 | Night | Friday | 2019 | 4
10919 | 2019-04-26 09:49 | 2019-04-26 09:49 | 13.8KV BATANG FEEDER #2 | Fair | Unidentified | 0 | 09:49 Batang VCB fdr #2 T/R 1x Cause: Not Checked Yet |  | 1 | 9:49 | Morning | Friday | 2019 | 4
10920 | 2019-04-26 09:49 | 2019-01-05 14:40 | 13.8KV BATANG FEEDER #2 | Fair | Unidentified | 0 | Checked and found BTG fdr #2 T/R 1x, ctr: 185 - 186, R/F: 51 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 9:49 | Morning | Friday | 2019 | 4
10921 | 2019-04-26 12:44 | 2019-04-26 12:44 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 113 | Batang VCB fdr #3 Load Dropped 27 A (41 - 14 A) Batang GFPC T/R 1x Not Checked Yet |  | 1 | 12:44 | Afternoon | Friday | 2019 | 4
10922 | 2019-04-26 12:44 | 2019-01-05 14:43 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 113 | Checked and found RCL 36-AL-13 Normal, ctr: 170, R/F: None Patrolled the line but found nothing Cause : Unidentified |  | 1 | 12:44 | Afternoon | Friday | 2019 | 4
10923 | 2019-04-26 18:26 | 2019-04-26 18:26 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #2 | Rain and Lightning | Lightning | 8 | MSU #1 13.8KV OCB fdr #2 T/R 1X (5B fdr #5). Not checked yet. |  | 1 | 18:26 | Afternoon | Friday | 2019 | 4
10924 | 2019-04-26 18:26 | 2019-07-05 18:26 | 13.8KV MBL SUBSTATION 1 (SOUTH) FEEDER #2 | Rain and Lightning | Lightning | 8 | Checked and found MSU #1 13.8KV OCB fdr #2 T/R 1X ctr:311-312 R/F: 51N(5B fdr #5). Patrolled the line but found nothing/ Cause: Lightning. |  | 1 | 18:26 | Afternoon | Friday | 2019 | 4
10925 | 2019-04-26 18:36 | 2019-04-26 18:36 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 29 | 6DN 13.8KV OCB fdr #1 T/R 1X. Not checked yet. |  | 1 | 18:36 | Afternoon | Friday | 2019 | 4
10926 | 2019-04-26 18:50 | 2019-04-26 18:50 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Tree | 0 | Menggala Fdr#1 Load dropped 118A (162-44A) Not checked yet |  | 1 | 18:50 | Afternoon | Friday | 2019 | 4
10927 | 2019-04-26 18:50 | 2019-04-27 00:50 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Tree | 0 | Checked & found Recloser 19-AO-01 T/Lo, Ctr: 493-497, R/F: 51 @1 Patrolled the Line found, Falldown Tree Touched Conductor at Well Meso #10 Block & Closed Recloser 19-AO-01, then released the block, after Dismantled the Fallen Trees Cause : Tree |  | 1 | 18:50 | Afternoon | Friday | 2019 | 4
10928 | 2019-04-26 20:10 | 2019-04-26 20:10 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Unidentified | 52 | Bangko VCB fdr#4 T/R 1x. Bangko fdr#1 Load dropped 92A (158-66A). Bangko fdr#2 Load dropped 233A (253-20A) Pump Off. Bangko fdr#3 Load dropped 233A (253-20A) Pump Off. Not checked yet. |  | 1 | 20:10 | Night | Friday | 2019 | 4
10929 | 2019-04-27 10:00 | 2019-04-27 10:00 | 4.16KV NO RUMBAI FEEDER #1 | Fair | Planned Maintenance | 0 | 10:00 Switching to transfer past load North RBI fdr #1 to North East RBI fdr #1 Purpose: c/o b/o dead end insulator d/s North RBI fdr #1 10:45 Manual Open VCB fdr #1 North Rumbai, ctr: 410 11:33 Manual Close VCB fdr #1 North Rumbai Cause: Planned Maintenance |  | 1 | 10:00 | Morning | Saturday | 2019 | 4
10930 | 2019-04-27 12:57 | 2019-04-27 12:57 | 13.8KV NORTH DURI - DUMAI FEEDER | Fair | Under investigation | 0 | 12:57 13.8 kV VCB #14 ND (for TX-14 to Dumai) T/O 14:35 Checked and found: - 44 kV GCB #1 ND T/R 1x, ctr: 135 - 136, R/F: 51P @1, @2 - 13.8 kV VCB #14 T/O, ctr: 156 - 157, R/F: 51G W2 - TX-14 were found normal, winding temp = 50 deg C 15:06 Open 44 kV GCB #1 ND 15:07 Close 13.8 kV VCB #14 ND, OK (TX-14 energize) Re-check TX condition, found Normal. 15:09 Blocked and Close 44 kV GCB #1 ND, OK. Line to Dumai energize. Cause: Under Investigation |  | 1 | 12:57 | Afternoon | Saturday | 2019 | 4
10931 | 2019-04-27 17:11 | 2019-04-27 17:11 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Lightning | 124 | CKBS 13.8KV VCB fdr #5 T/R 1X. Not checked yet. |  | 1 | 17:11 | Afternoon | Saturday | 2019 | 4
10932 | 2019-04-27 17:11 | 2019-04-28 16:21 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Cloudy | Lightning | 124 | Checked and found CKB VCB fdr #5 T/R 1x, ctr: 171-172, R/F 51N Patrolled the line but found nothing Cause : Lightning |  | 1 | 17:11 | Afternoon | Saturday | 2019 | 4
10933 | 2019-04-28 08:59 | 2019-04-28 08:59 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Planned Maintenance | 172 | 08:59 Manual Open RCL 06-Q3-02 (CD fdr #15), Closed at 09:30 MTCE team sleeve and dismantle TX on power pole 06-Q3-19 16:51 Manual Open RCL 06-Q3-02 (CD fdr #15), Closed at 17:27 MTCE team re-install TX on pole 06-Q3-19 Cause: Planned Maintenance |  | 1 | 8:59 | Morning | Sunday | 2019 | 4
10934 | 2019-04-29 06:28 | 2019-04-29 06:28 | 13.8KV 8D FEEDER #5 | Fair | Unidentified | 0 | 8D OCB fdr#5 T/R 1x. Not checked yet. |  | 1 | 6:28 | Morning | Monday | 2019 | 4
10935 | 2019-04-29 06:28 | 2019-02-05 02:45 | 13.8KV 8D FEEDER #5 | Fair | Unidentified | 0 | Checked and found 8D fdr #5 T/R 1x, ctr: 566 (not change), R/F: 51P @1,@2,@3 Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 6:28 | Morning | Monday | 2019 | 4
10936 | 2019-04-29 08:47 | 2019-04-29 08:47 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 18 | 08:47 Ketigul VCB fdr #1 T/R 1x Cause: Not Checked Yet |  | 1 | 8:47 | Morning | Monday | 2019 | 4
10937 | 2019-04-29 08:47 | 2019-01-05 15:10 | 13.8KV KETIGUL FEEDER#1 | Fair | Animal | 18 | Checked and found VCB fdr #1 T/R 2x, ctr: 213-215, R/F: 51N Patrolled the line and found dead animal at Tilan #30 Cause : Animal |  | 1 | 8:47 | Morning | Monday | 2019 | 4
10938 | 2019-04-29 11:05 | 2019-04-29 11:05 | CENTRAL DURI SW GEAR 3-4 | Fair | Under investigation | 0 | 11:05 13.8 kV ACB #44 (TX #4-Incoming 13.8 KV) CD T/O Checked and found ACB #44 T/O, ctr: 422 (not changed), R/F: 51N MTCE team working for 115 kV GCB #63 CD at SG 3/4 11:30 Closed 13.8 kV ACB #44 CD, suddenly ACB #46 (Gen Breaker GT-4 CD T/ripped). CD fdr #9 load dropped 27 A (161 - 134 A) due to under voltage to 12.5 kV 11:39 Closed ACB #46 (gen breaker GT-4), OK Cause: Under Investigation |  | 1 | 11:05 | Morning | Monday | 2019 | 4
10939 | 2019-04-29 16:44 | 2019-04-29 16:44 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Fair | Unidentified | 93 | 16:44 Petani 13.8KV MSU #2 OCB fdr #1 T/O (Petani fdr #1). (On blocked due to RIG APS #3512 at well Petani #29). 16:26 Blocked and Closed Petani 13.kKV MSU #2 OCB fdr #1. OK. Not checked yet. |  | 1 | 16:44 | Afternoon | Monday | 2019 | 4
10940 | 2019-04-29 16:44 | 2019-01-05 14:48 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #1 | Fair | Unidentified | 93 | Checked and found VCB MSU fdr #1 T/O (on block), ctr: 323-324, R/F: 51 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 16:44 | Afternoon | Monday | 2019 | 4
10941 | 2019-04-29 23:29 | 2019-04-29 23:29 | 115KV KOTABATAK JUNCTION - 3D LINE | Rain and Lightning | Lightning | 0 | 115Kv line KBJ---->3D GCB#23 T/R 1x. 115Kv line KBJ---->3D GCB#27 T/R 1x. 3D 115KV OCB #21----->?????? Not checked yet. |  | 1 | 23:29 | Night | Monday | 2019 | 4
10942 | 2019-04-29 23:29 | 2019-07-05 08:40 | 115KV KOTABATAK JUNCTION - 3D LINE | Rain and Lightning | Lightning | 0 | Checked and found: 115KVKBJ3D#23 T/R 1x, Ctr: 219-220, R/F 87L 115KVKBJ3D#27 T/R 1x, Ctr: 94-95, R/F: 87L Patrolled the line and found Broken Dead End @3 o/p KN-43 Cause : Lightning |  | 1 | 23:29 | Night | Monday | 2019 | 4
10943 | 2019-04-29 23:30 | 2019-04-29 23:30 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 0 | 23:30 4D 13.8Kv OCB fdr#4 T/O. R/F 51N Ctr: 81-82. 00:44 4D 13.8Kv OCB fdr#4 Closed. Not Checked yet. |  | 1 | 23:30 | Night | Monday | 2019 | 4
10944 | 2019-04-29 23:30 | 2019-02-05 16:21 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 0 | Checked and found 4D fdr #4 T/R 1x, ctr: 81-82, R/F: 51P @1 Patrolled the line but found nothing Cause : Lightning |  | 1 | 23:30 | Night | Monday | 2019 | 4
10945 | 2019-04-29 23:30 | 2019-04-29 23:30 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 6 | 23:30:01 4D 13.8Kv OCB fdr#5 T/O. R/F 51N Ctr: 351-353. 00:45 4D 13.8Kv OCB fdr#5 Closed. Not Checked yet. |  | 1 | 23:30 | Night | Monday | 2019 | 4
10946 | 2019-04-29 23:30 | 2019-02-05 16:40 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 6 | Checked and found VCB 4D fdr #5 T/R 2x, ctr: 351-353, R/F: 51P @1 Patrolled the line and found Broken Pin Insulator and Pin Ø1 on Pole 4D-147 Cause : Lightning |  | 1 | 23:30 | Night | Monday | 2019 | 4
10947 | 2019-04-29 23:30 | 2019-04-29 23:30 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Post Pin Insulator | 12 | 5B 138Kv OCB fdr#2 T/R 1x. 5B fdr#8 load dropped 73A (195-122A). Not checked yet. |  | 1 | 23:30 | Night | Monday | 2019 | 4
10948 | 2019-04-29 23:30 | 2019-03-05 23:30 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Post Pin Insulator | 12 | 5B 13.8KV Feeder #2 T/R 1X Ctr: 419-420 R/F: RF 51N. Patrolled the line and found @1 Flash over Suspension insulator o/p 5C-11. Cause: Flash over Suspension insulator. |  | 1 | 23:30 | Night | Monday | 2019 | 4
10949 | 2019-04-29 23:36 | 2019-04-29 23:36 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 0 | 8D OCB FDR#3 T/R 1X. 8D fdr#1 load dropped 7A (106-99A). 8D fdr#2 load dropped 18A (86-68A). 8D fdr#5 load dropped 54A (119-65A). 8D fdr#11 load dropped 58A (120-62A). 8C fdr#1 load dropped 94A (173-79A). 8C fdr#3 load dropped 47A (217-170A). 8C fdr#4 load dropped 185A (306-121A). Not checked yet. |  | 1 | 23:36 | Night | Monday | 2019 | 4
10950 | 2019-04-29 23:36 | 2019-02-05 16:22 | 13.8KV 8D FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found 8D fdr #3 T/R 1x, ctr: 248-249, R/F: 51P @1 @2 Patrolled the line and found Broken LA Ø2 on Pole Loc. 8D-96 Cause : Lightning |  | 1 | 23:36 | Night | Monday | 2019 | 4
10951 | 2019-04-29 23:37 | 2019-04-29 23:37 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Unidentified | 1 | Minas ACB#2 fdr#3 T/R 1x. Not checked yet. |  | 1 | 23:37 | Night | Monday | 2019 | 4
10952 | 2019-04-29 23:37 | 2019-03-05 23:37 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Unidentified | 1 | Checked and found Minas 13.8KV ACB fdr#3 T/R 1x ctr:...…. R/F:...…. Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 23:37 | Night | Monday | 2019 | 4
10953 | 2019-04-30 00:23 | 2019-04-30 00:23 | 13.8KV MINAS FEEDER #6 | Rain and Lightning | Pin Insulator | 360 | 00:14 Minas OCB#18 fdr#6 T/R 00:23 Minas OCB#18 fdr#6 T/O. 00:30 Checked & found Minas ACB fdr#6 T/Lo Ctr:179-182 R/F:51N. Patrolled the line but found nothing. 04:20 Open LBS 7E-54, Closes at 04:22. Blocked & closed Minas ACB fdr#6, but failed. 04:45 Opened LBS 7E-40A. Blocked & closed Minas ACB fdr#6, ok. 05:30 Patrolled the line but found nothing. 07:40 Open Recl. 7E-67A (will be trouble shoot by Mtce team) 07:42 Closed LBS 7E-40A then blocked and closed Minas fdr #6, but tripped again. Open LBS 7E-40A then blocked and closed Minas fdr #6. OK. 07:46 Blocked 8D fdr #10. Closed LBS 7E-86. OK (part load Minas fdr #6 transfer to 8D fdr #10). 07:56 Closed LBS 7E-40A. OK. Continued patrolled the line under LBS 7D-151: Found broken 1PC pin Insulator o/p M6DN-03 then replaced. Replaced 3 Pcs LA o/p 7E-46. 09:46 Closed LBS 7D-151. (Recl. 7E-67A will be trouble shoot by Mtce team). Cause: Broken Pin Insulator. |  | 1 | 0:23 | Night | Tuesday | 2019 | 4
10954 | 2019-04-30 01:12 | 2019-04-30 01:12 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Tree | 433 | 01:12 Sintong VCB fdr#1 T/O. Sintong fdr#2 load dropped 146A (184-38A). 03:00 Checked & found Sintong VCB fdr#1 T/Lo Ctr:399-403 R/F:51@1@3. Sintong GFPC T/R 2x Ctr:1122-1124. 03:10 Opened LS 26AE06. Blocked & closed Sintong VCB fdr#1, ok, then release the block. 03:21 Patrolled the line & found tree touch power line near pole 25AD09- 25AD10. Conductor fall to ground due to broken Pin Insulator near pole 25AD09- 25AD10. 05:10 Isolated with cut jumper o/p 25AD02. 05:15 Closed LBS 26AE06. (8 wells off for continued the job). | 123 | 1 | 1:12 | Night | Tuesday | 2019 | 4
10955 | 2019-04-30 02:00 | 2019-04-30 02:00 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Unidentified | 382 | 02:00 Ketigul VCB fdr#1 T/R 1x. Ketigul fdr#2 load dropped 61A (244-183A). Ketigul fdr#3 load dropped 31A (38-7A). 04:00 Ketigul fdr#1 still dropped 68A (124-56A). 06:00 Checked & found Ketigul VCB fdr#1 T/X 2x Ctr:213-215 R/F:51N. 06:22 Checked & found Recl 32AK16 T/Lo Ctr:136-140. Blocked & closed Recl 32AK16, ok, release the block. Not patrolled yet. |  | 1 | 2:00 | Night | Tuesday | 2019 | 4
10956 | 2019-04-30 02:00 | 2019-05-05 13:49 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Unidentified | 382 | Checked and found VCB KTGL fdr #1 T/R 2x, ctr: 213-215, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 2:00 | Night | Tuesday | 2019 | 4
10957 | 2019-04-30 09:57 | 2019-04-30 09:57 | 13.8KV 6D FEEDER #1 | Fair | Powerline - Conductor | 466 | 09:57 6D 13.8KV OCB fdr #1 T/R 3X----->WIP & field. 6D fdr #2 droped 141A (192-51A). 6D fdr #3 dropped 71A (160-89A)----->WIP. 11:02 6D VCB fdr #1 T/LO 11:05 Reported/re-confirmed by fire team that any fire at pole 5C-43 11:17 Reported no power at facilities GS-4 (air compressor) 11:31 Checked and found broken conductor and fire near pole 5C-43 11:37 Isolate part line of 6D fdr #1 by Opened LBS 5C-59 11:39 Blocked and Close VCB 6D fdr #1, OK (for GS-4 only) 18:19 Repaired broken conductor has finished (phase @2) 18:29 Open VCB 6D fdr #1 for close LBS 5C-59 due to problem at LBS 18:31 Block and Close VCB 6D fdr #1, OK then release the block. Any broken conductor phase @3 at 4B-46 and has isolated by cutting jumper on TOP 4B-46 (will be repaired tomorrow). Cause: Broken Conductor |  | 1 | 9:57 | Morning | Tuesday | 2019 | 4
10958 | 2019-04-30 16:27 | 2019-04-30 16:27 | 13.8KV DURI FIELD FEEDER #1 | Fair | Animal | 0 | D. Field 13.8KV ACB fdr #1 T/R 1X. Not checked yet. |  | 1 | 16:27 | Afternoon | Tuesday | 2019 | 4
10959 | 2019-04-30 16:27 | 2019-05-05 13:52 | 13.8KV DURI FIELD FEEDER #1 | Fair | Animal | 0 | Checked and found DF fdr #1 T/R 1x, R/F: 51N Patrolled the line and found dead animal o/p 01-5-01, @1, @2, @3 Cause : Animal |  | 1 | 16:27 | Afternoon | Tuesday | 2019 | 4
10960 | 2019-04-30 16:27 | 2019-04-30 16:27 | 13.8KV DURI FIELD FEEDER #3 | Fair | Animal | 0 | D. Field 13.8KV ACB fdr #3 T/R 1X. Not checked yet. |  | 1 | 16:27 | Afternoon | Tuesday | 2019 | 4
10961 | 2019-04-30 16:27 | 2019-05-05 16:27 | 13.8KV DURI FIELD FEEDER #3 | Fair | Animal | 0 | Checked and found DF fdr #3 T/R 1x, ctr: 381-382, R/F: 51P Patrolled the line and found dead animal o/p 01-5-01 Cause : Animal |  | 1 | 16:27 | Afternoon | Tuesday | 2019 | 4
10962 | 2019-04-30 17:57 | 2019-04-30 17:57 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Powerline - Conductor | 0 | 17:57 C. Duri 13.8KV ACB fdr #7 T/LO ctr:523-526 R/F: 51N. Checked and found b/o fuse phase @1 for u/g cable o/p 03-4-24A. Not checked yet. |  | 1 | 17:57 | Afternoon | Tuesday | 2019 | 4
10963 | 2019-04-30 17:57 | 2019-05-05 13:55 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Powerline - Conductor | 0 | Checked and found CD fdr #7 T/LO, ctr: 523-526 (operate on close), R/F: 51N Patrolled the line and found UG cables low megger o/p 03-4-24A Cause : Conductor |  | 1 | 17:57 | Afternoon | Tuesday | 2019 | 4
10964 | 2019-04-30 18:10 | 2019-04-30 18:10 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | 16:10 N.Duri fdr#9 Load dropped 37A (121-84A). 22:00 It was reported no power o/p 11-H1-16. 23:30 Checked & found Recl. 11-H3-05 T/O Ctr: 149-150. Blocked & closed Recl. 11-H3-05. Not patrolled yet. |  | 1 | 18:10 | Afternoon | Tuesday | 2019 | 4
10965 | 2019-04-30 18:10 | 2019-05-05 13:58 | 13.8KV NORTH DURI FEEDER #9 | Fair | Unidentified | 0 | Checked and found RCL 11-H5-03 T/R 1x, ctr: 149-150, R/F: None Patrolled the line but found nothing Cause : Unidentified |  | 1 | 18:10 | Afternoon | Tuesday | 2019 | 4
10966 | 2019-02-05 10:45 | 2019-02-05 10:45 | 13.8KV BATANG FEEDER #2 | Fair | Planned Maintenance | 5 | 10:45 Shutdown Batang feeder #2. Move the Recloser Control to TX. at Rantau Bais GS. 12:00 Manually Blocked & Closed Batang feeder #2. Cause: Planned Maintenance. |  | 1 | 10:45 | Morning | Tuesday | 2019 | 2
10967 | 2019-02-05 11:09 | 2019-02-05 11:09 | 13.8KV 8D FEEDER #11 | Fair | Planned Maintenance | 0 | 11:09 Manual Open RCL 9E-02 d/s 8D feeder #11. Palm Branches Touch the Electric wire. 11:45 Manually Blocked & Closed RCL. 9E-02 d/s 8D feeder #11 Cause: Planned Maintenance. |  | 1 | 11:09 | Morning | Tuesday | 2019 | 2
10968 | 2019-02-05 13:43 | 2019-02-05 13:43 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | C.Duri ACB fdr #3 T/R 1X. R/f: 51N @1& @3 Ctr: 211-212. Not checked yet. |  | 1 | 13:43 | Afternoon | Tuesday | 2019 | 2
10969 | 2019-02-05 13:43 | 2019-05-05 14:09 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | Checked and found CD fdr #3, ctr: 211-212, R/F: 50P Patrolled the line but found nothing Cause : Unidentified |  | 1 | 13:43 | Afternoon | Tuesday | 2019 | 2
10970 | 2019-02-05 17:42 | 2019-02-05 17:42 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | CD ACB fdr #1 T/R 1x R/F: 51G, 51N, Ctr: 243 - 244 Cause: Not Checked Yet |  | 1 | 17:42 | Afternoon | Tuesday | 2019 | 2
10971 | 2019-02-05 17:42 | 2019-05-05 14:06 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found CD fdr #1 T/R 1x, ctr: 243-244, R/F: 51G Patrolled the line but found nothing Cause : Unidentified |  | 1 | 17:42 | Afternoon | Tuesday | 2019 | 2
10972 | 2019-03-05 10:49 | 2019-03-05 10:49 | DARLING SUBSTATION | Fair | Unidentified | 33 | 10:49 Darling 115Kv GCB#4 T/O. Darling 115Kv GCB#2 T/O. Darling 13.8Kv VCB fdr#4 T/R 1x. Darling 13.8Kv VCB fdr#7 T/R 1x. 11:34 CGS#5 tie 4160V to Darling fdr#6, normal at 13:15. 12:03 Checked and found : -86T & 86HR are not operate / Normal. -TXP-1 Darling R/F 51G @2. -Darling VCB fdr#4 : 51N, 51P@B. -Darling VCB fdr#7 : 51N, 51P @A &@B. -TX-1 condition visual oke. --->Lig. temperature 54 degC. --->Winding temperature 56 degC. -VR of TX-1 condition normal. 12:15 Manually open Darling fdr#3 and fdr#4. 12:35 Reset all R/F. 12:43 Closed 115Kv GCB#2 ,ok (on DL mode) ctr:90-91. 12:46 Closed 115Kv GCB#4 ,ok (on SC mode) ctr:183-184. 12:49 Blocked & Closed Darling fdr#3.ok ctr:251 (not change). Blocked & Closed Darling fdr#4.ok ctr:141-143. Cause:Under Invvestigation. |  | 1 | 10:49 | Morning | Tuesday | 2019 | 3
10973 | 2019-03-05 10:49 | 2019-06-05 07:07 | DARLING SUBSTATION | Fair | Unidentified | 33 | Checked and found : 115KVDRLGCB#2 T/O, Ctr : 90 - 91, R/F: 51G 115KVDRLGCB#4 T/O, Ctr: 183 - 184, R/F: 51G Checked TX, VR and others accessories but found nothing (normal) Cause : Under Investigation |  | 1 | 10:49 | Morning | Tuesday | 2019 | 3
10974 | 2019-03-05 10:49 | 2019-03-05 10:49 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified | 0 | Darling VCB fdr #4 T/R 1X. Not checked yet. |  | 1 | 10:49 | Morning | Tuesday | 2019 | 3
10975 | 2019-03-05 10:49 | 2019-03-05 10:49 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified | 0 | Darling VCB fdr #4 T/R 1X. Not checked yet. |  | 1 | 10:49 | Morning | Tuesday | 2019 | 3
10976 | 2019-03-05 10:49 | 2019-03-05 10:49 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Darling VCB fdr #7 T/R 1X. Not checked yet. |  | 1 | 10:49 | Morning | Tuesday | 2019 | 3
10977 | 2019-03-05 10:49 | 2019-08-05 08:43 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Checked & Found Darling VCB fdr#3 T/R 1x, Ctr; 173-174, R/F: none Patrolled the Line, but found nothing Cause: Unidentified |  | 1 | 10:49 | Morning | Tuesday | 2019 | 3
10978 | 2019-03-05 13:27 | 2019-03-05 13:27 | 13.8KV BANGKO FEEDER #3 | Rain and Lightning | Lightning | 0 | Bangko OCB fdr #3 T/R 1. Bangko fdr #1 load dropped 96A (147-51A). Bangko fdr #2 load dropped 224A ( 250-26A). Bangko fdr #4 load dropped 95A ( 169-74A). Not Checked Yet. . |  | 1 | 13:27 | Afternoon | Tuesday | 2019 | 3
10979 | 2019-03-05 13:27 | 2019-04-05 13:53 | 13.8KV BANGKO FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found VCB BKO fdr #3 T/R 1x, ctr: 99949 - 99950, R/F: 51N Patrolled the line but found nothing. Cause : Lightning |  | 1 | 13:27 | Afternoon | Tuesday | 2019 | 3
10980 | 2019-03-05 13:56 | 2019-03-05 13:56 | CENTRAL DURI POWER PLANT |  |  | 0 | 13:56 CDGT#1 S/U ang then online at 14:50. |  | 1 | 13:56 | Afternoon | Tuesday | 2019 | 3
10981 | 2019-03-05 13:56 | 2019-03-05 13:56 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Unidentified | 78 | Bangko OCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 13:56 | Afternoon | Tuesday | 2019 | 3
10982 | 2019-03-05 13:56 | 2019-04-05 13:50 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Unidentified | 78 | Checked and found VCB BKO fdr #1 T/R 1x, ctr: 66-67, R/F: 51N Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 13:56 | Afternoon | Tuesday | 2019 | 3
10983 | 2019-03-05 13:59 | 2019-03-05 13:59 | 13.8KV KETIGUL FEEDER#2 | Rain | Lightning | 0 | Ketigul fdr#2 load dropped 46A(243-197A). Not checked yet. |  | 1 | 13:59 | Afternoon | Tuesday | 2019 | 3
10984 | 2019-03-05 13:59 | 2019-09-05 16:43 | 13.8KV KETIGUL FEEDER#2 | Rain | Lightning | 0 | Checked & found Recl. 29 AL 03 T/R 2x, Ctr: 172-174, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 13:59 | Afternoon | Tuesday | 2019 | 3
10985 | 2019-03-05 15:07 | 2019-03-05 15:07 | CENTRAL DURI POWER PLANT |  |  | 0 | 15:07 CDGT#4 offline and then S/D at 15:08. Repair hydraulic leakage. |  | 1 | 15:07 | Afternoon | Tuesday | 2019 | 3
10986 | 2019-03-05 16:46 | 2019-03-05 16:46 | CENTRAL DURI POWER PLANT |  |  | 0 | CDGT #4 S/U and then Online at 17:06 |  | 1 | 16:46 | Afternoon | Tuesday | 2019 | 3
10987 | 2019-03-05 17:22 | 2019-03-05 17:22 | CENTRAL DURI POWER PLANT |  |  | 0 | CDGT #1 Offline and then S/D at 17:23 |  | 1 | 17:22 | Afternoon | Tuesday | 2019 | 3
10988 | 2019-04-05 09:00 | 2019-04-05 09:00 | PETANI SUBSTATION | Fair | Planned Maintenance | 1187 | 09:08 Shut down line PTN fdr #2 by Open LBS 32-AV-11 10:09 Shut Down line PTN fdr #1 by Open VCB MSU fdr #1 12:34 Manual Close 44 kV GCB #1 PMT Main (TX PTN SS were Energized) 13:31 Manual Close VCB PTN fdr #1 14:29 Manual Close VCB PTN fdr #2 Original Petani SS back to Normal Operation Cause: Planned Maintenance Prod. loss : 1078 Bbls / 57 Wells. | 123 | 1 | 9:00 | Morning | Friday | 2019 | 4
10989 | 2019-04-05 14:33 | 2019-04-05 14:33 | CENTRAL DURI SWITCH YARD | Fair | UnClassified | 0 | 14:33 115 kV OCB #33 T/O, Closed at …… 115 kV GCB #35 T/O, Closed at …… TXP-5 Still Offline (Line Switches are Open) 14:35 Confirm by MTCE SS team that they performing function test for Gen BRK of CDGT-5 Cause: Unclassified |  | 1 | 14:33 | Afternoon | Friday | 2019 | 4
10990 | 2019-04-05 17:30 | 2019-04-05 17:30 | 13.8KV RANGAU FEEDER #2 | Fair | Recloser | 0 | Rangau fdr #2 Load Dropped 138 A (183 - 45 A) Cause: Not Checked Yet |  | 1 | 17:30 | Afternoon | Friday | 2019 | 4
10991 | 2019-04-05 17:30 | 2019-08-05 09:28 | 13.8KV RANGAU FEEDER #2 | Fair | Recloser | 0 | Checked & found Recl 23 BD 01 T/R 1x, Ctr: 374-375, R/F: 51 @2 Patrolled the Line, found @2 Broken L.A O/p 22 BD 17 Cause : Recloser |  | 1 | 17:30 | Afternoon | Friday | 2019 | 4
10992 | 2019-04-05 21:24 | 2019-04-05 21:24 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 35 | 6DN fdr #6 load dropped 108A (175-67A). Not checked yet. |  | 1 | 21:24 | Night | Friday | 2019 | 4
10993 | 2019-04-05 21:24 | 2019-05-05 16:48 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 35 | Checked and found RCL 6E-30 T/R 1x, ctr: 45-46, R/F: 51N Patrolled the line and found broken LA @1 o/p 6E-08 Cause : Lightning |  | 1 | 21:24 | Night | Friday | 2019 | 4
10994 | 2019-04-05 23:34 | 2019-04-05 23:34 | 13.8KV DURI FIELD FEEDER #4 | Fair | Transformer Failure | 0 | Duri Field 13.8KV fdr #4 T/R 1X. Duri Field fdr #2 dropped 47A (140-93A). Not checked yet. |  | 1 | 23:34 | Night | Friday | 2019 | 4
10995 | 2019-04-05 23:34 | 2019-08-05 09:02 | 13.8KV DURI FIELD FEEDER #4 | Fair | Transformer Failure | 0 | Checked & found Duri Field ACB #51 T/R 1x, Ctr: 547-548, R/F: 51N Patrolled the Line, found Broken TX of PT Recloser O/p 06 S7 19 Cause : Transformer Failure |  | 1 | 23:34 | Night | Friday | 2019 | 4
10996 | 2019-05-05 21:12 | 2019-05-05 21:12 | 13.8KV MINAS FEEDER #6 | Fair | Broken Fuse Cut Out | 0 | 21:12 It was reported any spark of TX at Wisma Ukai d/s: Minas fdr #6. 22:25 Checked and found @2 broken FCO for 50KVA TX at Wisma Ukai. 22:35 Open LBS: 7#-46, and Closed at 22:38. Replaced @2 broken FCO (well 6E-93 off during the JOB) Cause: Broken FCO. |  | 1 | 21:12 | Night | Sunday | 2019 | 5
10997 | 2019-06-05 23:59 | / | CPI POWER SYSTEM |  |  | - | - |  | 1 | 23:59 | Night | Wednesday | 2019 | 6
10998 | 2019-07-05 17:24 | 2019-07-05 17:24 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 96 | KETIGUL VCB fdr #2 T/R 1x. KETIGUL VCB fdr #2 T/R again (1x). Not Checked Yet. |  | 1 | 17:24 | Afternoon | Friday | 2019 | 7
10999 | 2019-07-05 17:24 | 2019-12-05 07:24 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 96 | Checked & found Ketigul VCB fdr#2 T/R 2x Ctr:325-327 R/F:51N. Patrolled the line & found Dead Monkey at Well Pagar#30. Cause : Animal. |  | 1 | 17:24 | Afternoon | Friday | 2019 | 7
11000 | 2019-08-05 01:40 | 2019-08-05 01:40 | MINAS POWER PLANT |  | Under investigation | - | MGT #10 Tripped Off by alarm: -88 Exhaust Fan Off. -Hight Vibration. Cause: Under investigation. |  | 1 | 1:40 | Night | Monday | 2019 | 8
11001 | 2019-08-05 02:12 | 2019-08-05 02:12 | MINAS POWER PLANT |  |  | - | 02:12 MGT #11 was S/U and On Line to the system at 02:34 to restore load. |  | 1 | 2:12 | Night | Monday | 2019 | 8
11002 | 2019-08-05 09:12 | 2019-08-05 09:12 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Tree | 0 | D,Community ACB fdr# 3 T/R 1x Not checked yet |  | 1 | 9:12 | Morning | Monday | 2019 | 8
11003 | 2019-08-05 16:48 | 2019-08-05 16:48 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Recloser | 0 | C Duri Fdr #1 Load dropped 59A (144-85A) Not checked yet |  | 1 | 16:48 | Afternoon | Monday | 2019 | 8
11004 | 2019-09-05 15:14 | 2019-09-05 15:14 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 77 | CKBS fdr#5 T/R 1x. Not checked yet. |  | 1 | 15:14 | Afternoon | Thursday | 2019 | 9
11005 | 2019-09-05 15:14 | 2019-11-05 07:14 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 77 | Checked & found CKB VCB fdr#5 T/R 1x Ctr:172-173 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 15:14 | Afternoon | Thursday | 2019 | 9
11006 | 2019-09-05 23:12 | 2019-09-05 23:12 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Powerline - Conductor | 268 | 23:12 S.Bekasap 13.8Kv OCB#1 T/O. Not checked yet. Production loss : 62 Bbls / 21 wells. |  | 1 | 23:12 | Night | Thursday | 2019 | 9
11007 | 2019-09-05 23:12 | 2019-10-05 00:09 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Powerline - Conductor | 268 | 00:09 Checked and found So Bekasap OCB feeder #1 T/LO. Counter:424-428 R/F: 51@3. 00:26 Patrolled the line found @3 broken conductor between poles 37-BG-31 t0 32. Isolated conductor by cut jumper on pole 37-BG-31 towards well So Bek #15. 03:05 Manually blocked and closed So Bekasap OCB feeder #1 --> Success. and then released the block. Cause: Broken conductor. Production loss : 231 Bbls / 21 wells. ( 24:00 up to 03:05 May 10, 2019 ). Production loss : 62 Bbls / 21 wells. ( 23:12 up to 24:00 May 09, 2019 ). ------------------------------------------------ + Grand total Production Loss : 293 Bbls / 21 wells. |  | 1 | 23:12 | Night | Thursday | 2019 | 9
11008 | 2019-10-05 15:00 | 2019-10-05 15:00 | 13.8KV 5B FEEDER #3 | Fair | Planned Maintenance | 10 | 15:00 Manually Open 5B fdr#3. Replaced @2@3 Pin Insulator o/p 4C-62. 15:20 Blocked & closed 5B fdr#3, then release the block. Cause: Plan Maintenance. |  | 1 | 15:00 | Afternoon | Saturday | 2019 | 10
11009 | 2019-11-05 07:30 | 2019-11-05 07:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | C.Duri ACB fdr#1 T/R Ctr:244-245 R/F:51N. Not patrolled yet. |  | 1 | 7:30 | Morning | Tuesday | 2019 | 11
11010 | 2019-11-05 07:30 | 15/05/2019 19:30 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 7:30 | Morning | Tuesday | 2019 | 11
11011 | 2019-11-05 10:45 | 2019-11-05 10:45 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 58 | 10:45 Manually opened So.Bekasap fdr#1. Repaired @1 Broken Jumper o/p 37BG31. 11:40 Blocked & closed So.Bekasap fdr#1, then release the block. Cause: Plan Maintenance. |  | 1 | 10:45 | Morning | Tuesday | 2019 | 11
11012 | 2019-11-05 14:40 | 2019-11-05 14:40 | CENTRAL DURI POWER PLANT |  |  | - | 14:40 S/U CGT#5, then online the unit at 14:56. (Running Test). 17:08 Off line CGT#5, then S/D the unit for Trouble shoot. |  | 1 | 14:40 | Afternoon | Tuesday | 2019 | 11
11013 | 2019-11-05 14:45 | 2019-11-05 14:45 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Tree | 0 | C.Duri ACB fdr#16 T/R 1x Ctr:341-342 R/F:51@1@2. Not patrolled yet. |  | 1 | 14:45 | Afternoon | Tuesday | 2019 | 11
11014 | 2019-11-05 14:45 | 15/05/2019 19:45 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Tree | 0 | Checked & found C.Duri ACB fdr#1 T/R 1x Ctr:244-245 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 14:45 | Afternoon | Tuesday | 2019 | 11
11015 | 2019-12-05 15:16 | 2019-12-05 15:16 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Unidentified | 94 | Bekasap fdr#6 load dropped 50A (181-131A). Not checked yet. |  | 1 | 15:16 | Afternoon | Thursday | 2019 | 12
11016 | 2019-12-05 15:16 | 17/05/2019 16:22 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Unidentified | 94 | Checked and found RCL 1-TL-6 T/R 1x, counter: 67 - 68, R/F: 51 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 15:16 | Afternoon | Thursday | 2019 | 12
11017 | 2019-05-13 06:47 | 2019-05-13 06:47 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Cloudy | Unidentified | 0 | Dumai 4.16KV VCB-22 fdr#4 T/R 1x. Not checked yet. |  | 1 | 6:47 | Morning | Monday | 2019 | 5
11018 | 2019-05-13 06:47 | 2019-05-19 08:31 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Cloudy | Unidentified | 0 | Checked and found VCB fdr #4 T/R 1x, ctr: 283 - 284, R/F 50P Patrolled the line but found nothing Cause : Unidentified |  | 1 | 6:47 | Morning | Monday | 2019 | 5
11019 | 2019-05-13 10:08 | 2019-05-13 10:08 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | 10:08 Minas ACB #21 T/O, (in Block Status, PT PLN Job), Ctr:88-89 R/F: 21L 44KV TX#4 & TX#5 T/O Supply to Rumbai Substations 10:48 Patrolled the Line but found nothing Manually Closed the ACB. kept in Block will be continued to patrolled. |  | 1 | 10:08 | Morning | Monday | 2019 | 5
11020 | 2019-05-13 10:08 | 2019-05-19 22:58 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Patrolled the line, but found nothing (normal operation) Cause: Lightning |  | 1 | 10:08 | Morning | Monday | 2019 | 5
11021 | 2019-05-13 10:27 | 2019-05-13 10:27 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 4 | 6D fdr#2 load dropped 78A (166-88A). 6D fdr#3 load dropped 36A (165-129A). Not checked yet. |  | 1 | 10:27 | Morning | Monday | 2019 | 5
11022 | 2019-05-13 10:27 | 2019-05-13 10:27 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 4 | 6D fdr#2 load dropped 78A (166-88A). 6D fdr#3 load dropped 36A (165-129A). Not checked yet. |  | 1 | 10:27 | Morning | Monday | 2019 | 5
11023 | 2019-05-13 10:27 | 2019-05-16 21:37 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 4 | Checked & found Recl: 6D-87 T/R 2x, R/F: 51N Patrolled the Line, found @1 Broken Deadend O/p 6C-05 Cause : Lightning |  | 1 | 10:27 | Morning | Monday | 2019 | 5
11024 | 2019-05-13 10:27 | 2019-05-16 21:37 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning | 4 | Checked & found Recl: 6D-87 T/R 2x, R/F: 51N Patrolled the Line, found @1 Broken Deadend O/p 6C-05 Cause : Lightning |  | 1 | 10:27 | Morning | Monday | 2019 | 5
11025 | 2019-05-13 10:29 | 2019-05-13 10:29 | 13.8KV 6DN FEEDER #3 | Rain and Lightning | Lightning | 5 | 6DN OCB fdr#3 T/R 1x. --> WIP. 6DN fdr#1 load dropped 30A (125-95A). Not checked yet. |  | 1 | 10:29 | Morning | Monday | 2019 | 5
11026 | 2019-05-13 10:29 | 2019-05-15 19:29 | 13.8KV 6DN FEEDER #3 | Rain and Lightning | Lightning | 5 | Checked & found 6DN fdr#3 T/R 1x Ctr:1135-1136 R/F:51N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 10:29 | Morning | Monday | 2019 | 5
11027 | 2019-05-13 10:29 | 2019-05-13 10:39 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 27 | 6DN fdr#2 load dropped 178A (235-57A). Not checked yet. |  | 1 | 10:29 | Morning | Monday | 2019 | 5
11028 | 2019-05-13 10:29 | 2019-05-17 05:18 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 27 | Checked and found RCL 6D-200 T/R 1x, counter: 19-20, R/F: 51N Patrolled the line and found Flash Over Pin Insulator o/p 5D-112 Cause : Lightning |  | 1 | 10:29 | Morning | Monday | 2019 | 5
11029 | 2019-05-13 10:31 | 2019-05-13 10:31 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 31 | Minas fdr#1 load dropped 134A (172-38A). Not checked yet. |  | 1 | 10:31 | Morning | Monday | 2019 | 5
11030 | 2019-05-13 10:31 | 2019-05-17 10:59 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 31 | Checked and found RCL 7D-20 T/R 1x, counter: 89 - 90, R/F: None Patrolled the line but found nothing Cause : Lightning |  | 1 | 10:31 | Morning | Monday | 2019 | 5
11031 | 2019-05-13 10:38 | 2019-05-13 10:38 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 25 | 6DN OCB fdr#6 T/R 1x. 6DN fdr#4 load dropped 35A (199-165A). Not checked yet. |  | 1 | 10:38 | Morning | Monday | 2019 | 5
11032 | 2019-05-13 10:38 | 2019-05-17 05:21 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 25 | Checked and found OCB 6DN fdr #6 T/R 1x, counter: 356 - 357, R/F: 50P @1 Patrolled the line but found nothing Cause : Lightning |  | 1 | 10:38 | Morning | Monday | 2019 | 5
11033 | 2019-05-13 10:49 | 2019-05-16 21:57 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 21 | Checked & found 4B OCB fdr#1 T/R 1x, Ctr: 372-371, R/F: 51 @3 Patrolled the Line, found @3 Flash Over Pin Insulator O/p 3A-06 Cause : Lightning |  | 1 | 10:49 | Morning | Monday | 2019 | 5
11034 | 2019-05-13 10:55 | 2019-05-13 10:55 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 7 | 4D OCB fdr#3 T/R 2x. Not checked yet. |  | 1 | 10:55 | Morning | Monday | 2019 | 5
11035 | 2019-05-13 10:55 | 2019-05-16 21:49 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 7 | Checked & found 4D OCB fdr#3 T/R 3x, Ctr: 369-372, R/F: 50 @1 Patrolled the line, found @1 Broken L.A O/p 3D-81 Cause : Lightning |  | 1 | 10:55 | Morning | Monday | 2019 | 5
11036 | 2019-05-13 11:27 | 2019-05-13 11:27 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 29 | 4D OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 11:27 | Morning | Monday | 2019 | 5
11037 | 2019-05-13 11:27 | 2019-05-15 19:27 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 29 | Checked & found 4D fdr#2 T/R 1x Ctr:281-282 R/F:50N. patrolled the line but found nothing. Cause : Lightning. |  | 1 | 11:27 | Morning | Monday | 2019 | 5
11038 | 2019-05-13 11:27 | 2019-05-13 11:27 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 7 | 5B OCB fdr#2 T/R 1x. 5B fdr#1 load dropped 42A (80-38A). 5B fdr#3 load dropped 48A (75-27A). 5B fdr#6 load dropped 71A (181-110A). Not checked yet. |  | 1 | 11:27 | Morning | Monday | 2019 | 5
11039 | 2019-05-13 11:27 | 2019-05-19 19:27 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 7 | Checked & found 5B fdr#2 T/R 1x Ctr:420-421 R/F:50N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 11:27 | Morning | Monday | 2019 | 5
11040 | 2019-05-13 15:23 | 2019-05-13 15:23 | CENTRAL DURI POWER PLANT |  |  | - | 15:23 CGT #5 S/U then On Line at 16:05 for testing 17:02 CGT #5 T/O by Exhaust temperature spread |  | 1 | 15:23 | Afternoon | Monday | 2019 | 5
11041 | 2019-05-13 17:25 | 2019-05-13 17:25 | 13.8KV RANGAU FEEDER #2 | Fair | Switchboard Problem | 35 | Rangau Fdr#2 Load dropped 132A (192-60A) Not checked yet |  | 1 | 17:25 | Afternoon | Monday | 2019 | 5
11042 | 2019-05-13 19:45 | 2019-05-13 19:45 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 338 | 19:45 PTN OCB fdr #2 T/O (on block post for Rig APS #3512 at PTN #40) Counter: 309-310, R/F: 51P @1 21:24 Manually blocked and closed PTN OCB fdr #2 --> OK Still on block position Cause: Not Patrolled Yet |  | 1 | 19:45 | Night | Monday | 2019 | 5
11043 | 2019-05-13 19:45 | 2019-05-15 10:43 | 13.8KV PETANI FEEDER #2 | Fair | Unidentified | 338 | Checked and found PTN VCB fdr #2 T/O, Ctr: 309-310, R/F: 50N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 19:45 | Night | Monday | 2019 | 5
11044 | 2019-05-13 20:35 | 2019-05-13 20:35 | 13.8KV 8C FEEDER #3 | Fair | Lightning | 0 | 8C Feeder #3 load dropped 143A (180-37A). Not checked yet. |  | 1 | 20:35 | Night | Monday | 2019 | 5
11045 | 2019-05-13 20:35 | 2019-05-16 21:39 | 13.8KV 8C FEEDER #3 | Fair | Lightning | 0 | Checked & found Recl 8D-18A T/R 2x, Ctr: 181-183, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 20:35 | Night | Monday | 2019 | 5
11046 | 2019-05-13 20:35 | 2019-05-16 21:39 | 13.8KV 8C FEEDER #3 | Fair | Lightning | 0 | Checked & found Recl 8D-18A T/R 2x, Ctr: 181-183, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 20:35 | Night | Monday | 2019 | 5
11047 | 2019-05-14 08:38 | 2019-05-14 08:38 | CENTRAL DURI POWER PLANT |  |  | 0 | 08:38 CDGT#1 S/U then on line at 09:25. ( CDGT#2 will be S/D for certification). |  | 1 | 8:38 | Morning | Tuesday | 2019 | 5
11048 | 2019-05-14 09:40 | 2019-05-14 09:40 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 45 | 09:40 Manually Opened Recl. 41AW62. Replaced Pin Insulator. 10:40 Blocked & closed Recl. 41AW62, then release the block. Cause: Plan Maintenance. |  | 1 | 9:40 | Morning | Tuesday | 2019 | 5
11049 | 2019-05-14 11:39 | 2019-05-14 11:39 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified | 22 | C.Duri fdr#1 T/R 1x Ctr:245-246 R/F:51G, 51N. Not patrolled yet. |  | 1 | 11:39 | Morning | Tuesday | 2019 | 5
11050 | 2019-05-14 11:39 | 2019-05-15 19:39 | 13.8KV CENTRAL DURI FEEDER #1 | Cloudy | Unidentified | 22 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 11:39 | Morning | Tuesday | 2019 | 5
11051 | 2019-05-14 14:02 | 2019-05-14 14:02 | CENTRAL DURI POWER PLANT |  |  | 0 | 14:02 CDGT#5 S/U then on line at 14:23 for running test on load 22.1 MW. 16:43 CDGT#5 Open Generation by Load Rejection test on 10 MW then S/D for S/B. |  | 1 | 14:02 | Afternoon | Tuesday | 2019 | 5
11052 | 2019-05-15 14:58 | 2019-05-15 14:58 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 7 | 8D 13.8KV OCV fdr #1 T/R 1X. Not checked yet. |  | 1 | 14:58 | Afternoon | Wednesday | 2019 | 5
11053 | 2019-05-15 14:58 | 2019-05-17 05:22 | 13.8KV 8D FEEDER #1 | Rain and Lightning | Lightning | 7 | Checked and found OCB 8D fdr #1 T/R 1x, Counter: 322-323, R/F: 50N Patrolled the line but found nothing Cause : Lightning |  | 1 | 14:58 | Afternoon | Wednesday | 2019 | 5
11054 | 2019-05-15 15:03 | 2019-05-15 15:03 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 292 | 15:03 6DN 13.8KV OCB fdr #1 T/R 2X. 15:11 6DN 13.8KV OCB fdr #1 tripped again. Not checked yet. |  | 1 | 15:03 | Afternoon | Wednesday | 2019 | 5
11055 | 2019-05-15 15:03 | 2019-05-16 08:28 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 292 | 08:28 Reported no power at location 5E-55/5E-84/5E-85 17:00 Checked and found RCL 5E-83 T/O, Ctr: 28-28 (not change), R/F: None 17:10 Manual Close RCL 5E-83, OK |  | 1 | 15:03 | Afternoon | Wednesday | 2019 | 5
11056 | 2019-05-15 15:03 | 2019-05-21 16:50 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 292 | Checked and found : 6DNSB-13.8OCB1 T/R, Counter : 166 - 169, Relay Flag : 51 Patrolled the line found: Broken pin and Dead end Cause : Lightning |  | 1 | 15:03 | Afternoon | Wednesday | 2019 | 5
11057 | 2019-05-15 15:05 | 2019-05-15 15:05 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 22 | 6DN VCB fdr #6 T/R 1x Cause: Not Checked Yet |  | 1 | 15:05 | Afternoon | Wednesday | 2019 | 5
11058 | 2019-05-15 15:05 | 2019-05-16 21:51 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Lightning | 22 | Checked & found 6DN OCB fdr#6 T/R 1x, Ctr: 355-356, R/F: 50 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 15:05 | Afternoon | Wednesday | 2019 | 5
11059 | 2019-05-15 15:11 | 2019-05-15 15:11 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 7 | 15:11 Minas fdr #1 dropped 36 A (177 - 141 A) Minas fdr #2 dropped 63 A (114 - 51 A) Minas fdr #3 dropped 56 A (118 - 62 A) Minas fdr #5 dropped 34 A (88 - 54 A) Cause: Not Checked Yet |  | 1 | 15:11 | Afternoon | Wednesday | 2019 | 5
11060 | 2019-05-15 15:11 | 2019-05-22 08:12 | 13.8KV MINAS FEEDER #1 | Rain and Lightning | Lightning | 7 | Checked and found: 5442-R.7D20 None, Counter : 90 - 90, Relay Flag : NONE Patrolled the line found: Nothing Cause : Lightning |  | 1 | 15:11 | Afternoon | Wednesday | 2019 | 5
11061 | 2019-05-15 15:13 | 2019-05-15 15:13 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 23 | 15:13 6DN 13.8KV OCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 15:13 | Afternoon | Wednesday | 2019 | 5
11062 | 2019-05-15 15:13 | 2019-05-21 05:13 | 13.8KV 6DN FEEDER #2 | Rain and Lightning | Lightning | 23 | checked & found 6DN OCB fdr#2 T/R 1x Ctr:326-327 R/F:50G. Patrolled the line & found @2 Broken Dead End Insulator o/p 6D-51. Cause : Lightning. |  | 1 | 15:13 | Afternoon | Wednesday | 2019 | 5
11063 | 2019-05-15 15:28 | 2019-05-15 15:28 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 14 | 6D fdr #1 T/R 1x Cause: Not Checked Yet |  | 1 | 15:28 | Afternoon | Wednesday | 2019 | 5
11064 | 2019-05-15 15:28 | 2019-05-25 09:49 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 14 | Checked and found: 6DSB-13.8OCB1 T/R, Counter : 364 - 365, Relay Flag : 51 Date Patrol : 17-MAY-2019 Operated Device : Patrolled the line found: Broken Dead end Cause : Lightning |  | 1 | 15:28 | Afternoon | Wednesday | 2019 | 5
11065 | 2019-05-15 15:40 | 2019-05-15 15:40 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 89 | Minas 13.8KV ACB fdr #3 T/R 1X. Not checked yet. |  | 1 | 15:40 | Afternoon | Wednesday | 2019 | 5
11066 | 2019-05-15 15:40 | 2019-05-20 08:42 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 89 | Check and found MNSSG-13.8ACB02 T/R, Counter : 135 - 135, Relay Flag : 51N Patrolled the line found: Broken deadend Cause : Lightning |  | 1 | 15:40 | Afternoon | Wednesday | 2019 | 5
11067 | 2019-05-15 15:40 | 2019-05-15 15:40 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Static Wire | 255 | 15:40 Minas 13.8KV ACB fdr #4 T/LO ctr:8095-8097 R/F: 50N. 17:12 Checked and found Recl. 7D-121 T/SO ctr:7-8. Blocked and closed MinaS fdr #4 but tripped again. 17:26 manually open Recl. 7D-150. Blocked and closed MinaS fdr #4 but tripped again. 17:33 Closed LBS 8D-07 to Transfer part load Minas fdr #4 to 8C fdr #3 but failed due to Interrupter problem. 17:51 Continue patrol and found broken static wire at 8-pole near Minas SY (3 span from Minas SY) Cause: Static Wire |  | 1 | 15:40 | Afternoon | Wednesday | 2019 | 5
11068 | 2019-05-15 15:49 | 2019-05-15 15:49 | MINAS POWER PLANT |  |  | 0 | 15:49 MGT#5 Trip by Lightning. (No Load shedding). 20:00 S/U MGT#5, then On line the unit at 20:12. |  | 1 | 15:49 | Afternoon | Wednesday | 2019 | 5
11069 | 2019-05-15 16:57 | 2019-05-15 16:57 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | 44Kv Line Mns-Rbi ACB#21 T/O (Blocked position). Not checked yet. |  | 1 | 16:57 | Afternoon | Wednesday | 2019 | 5
11070 | 2019-05-15 16:57 | 2019-05-16 21:41 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Checked & found 44KV Minas-RBI T/O, Ctr: 88-89, R/F: 21 Patrolled the Line, but Found nothing Cause : Lightning |  | 1 | 16:57 | Afternoon | Wednesday | 2019 | 5
11071 | 2019-05-15 16:57 | 2019-05-16 21:41 | 44KV MINAS - RUMBAI LINE | Rain and Lightning | Lightning | 0 | Checked & found 44KV Minas-RBI T/O, Ctr: 88-89, R/F: 21 Patrolled the Line, but Found nothing Cause : Lightning |  | 1 | 16:57 | Afternoon | Wednesday | 2019 | 5
11072 | 2019-05-15 17:38 | 2019-05-15 17:38 | 13.8KV 8D FEEDER #4 | Rain | Unidentified | 2 | 8D fdr #4 dropped 100 A (107 - 7 A) Cause: Not Checked Yet |  | 1 | 17:38 | Afternoon | Wednesday | 2019 | 5
11073 | 2019-05-15 17:38 | 2019-05-28 20:36 | 13.8KV 8D FEEDER #4 | Rain | Unidentified | 2 | Checked and found all in Normal Condition, no RCL unit operate. Patrol the line but found nothing, suspect motor at GS 1 / 2 was Off. Cause : Unidentified |  | 1 | 17:38 | Afternoon | Wednesday | 2019 | 5
11074 | 2019-05-15 18:24 | 2019-05-15 18:24 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Dead End Insulator | 446 | 18:24 6D 13.8KV OCV fdr #1 T/LO. Ctr: R/F: 20:30 Patrolled the Line & found Broken I Bolt Deadend Insulator O/p 6D-46G 21:30 Opened LBS 5C-121B 21:57 Opened LBS 5C-59 22:00 Closed LBS 6C-21A But Failed the LBS has Broken 22:07 Closed LBS at GS4 its transfer load to 5B Fdr#6 Cause: Broken Deadend . | 123 | 1 | 18:24 | Afternoon | Wednesday | 2019 | 5
11075 | 2019-05-15 18:24 | 2019-05-16 15:38 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Dead End Insulator | 446 | 15:38 Repaired Broken Eye Bolt Clivis Dead End Insulator o/p 6D-464. 15:41 Blocked & closed 6D fdr#1, then release the block. Cause: Dead End Insulator. | 123 | 1 | 18:24 | Afternoon | Wednesday | 2019 | 5
11076 | 2019-05-15 18:28 | 2019-05-15 18:28 | 13.8KV ROKAN FEEDER #2 | Fair | Animal | 16 | Rokan 13.8KV VCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 18:28 | Afternoon | Wednesday | 2019 | 5
11077 | 2019-05-15 18:28 | 2019-05-18 07:40 | 13.8KV ROKAN FEEDER #2 | Fair | Animal | 16 | Checked and found VCB RKN fdr #2 T/R 1x, ctr: 1294 - 1295, R/F : 51P @1 Checked and found dead animal (monkey) at KOPAR #25 (b/o 3 pcs fuse link) on pole 29-AV-73 Cause : Animal |  | 1 | 18:28 | Afternoon | Wednesday | 2019 | 5
11078 | 2019-05-16 06:35 | 2019-05-16 06:35 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Recloser | 341 | C.Duri fdr#16 T/R 1x Ctr:342-343 R/F:51@1@2. Not patrolled yet. |  | 1 | 6:35 | Morning | Thursday | 2019 | 5
11079 | 2019-05-16 06:35 | 2019-05-18 07:50 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Recloser | 341 | Checked and found ACB fdr #16 T/R 1x, ctr: 342 - 343, R/F: 51P @1, @2 Patrolled the line and found bushing @1, @2RCL 09-N4-08 flash/burned Cause : Recloser |  | 1 | 6:35 | Morning | Thursday | 2019 | 5
11080 | 2019-05-16 11:16 | 2019-05-16 11:16 | CENTRAL DURI POWER PLANT |  |  | 0 | 11:16 CDGT-5 S/U and then online at 11:40 Running test until Monday May 20th, 2019 15:03 CDGT-5 Tripped by alarm customer trip (open diverter dumper) 15:23 CDGT-5 S/U again and online at 15:35, after Fixed Diverter control |  | 1 | 11:16 | Morning | Thursday | 2019 | 5
11081 | 2019-05-16 13:39 | 2019-05-16 13:39 | CENTRAL DURI POWER PLANT |  |  | 0 | 13:39 CDGT-2 Offline and then S/D at 13:40 Service breaker station service ACB #25 |  | 1 | 13:39 | Afternoon | Thursday | 2019 | 5
11082 | 2019-05-17 03:17 | 2019-05-17 03:17 | 13.8KV CENTRAL DURI FEEDER #16 | Rain and Lightning | Animal | 93 | 03:17 C.Duri ACB fdr#16 T/LO Ctr:343-347 R/F 51N, 51@1. 04:45 Patrolled the line but found nothing. Blocked & closed C.Duri fdr#16, but failed. 06:00 Opened LBS 09-P4-02. Opened LBS Riser pole D/S C.Duri fdr#16, then closed at 06:39. 06:42 Blocked & closed C.Duri fdr#16 06:44 Closed LBS 09-P4-02, but C.Duri fdr#16 trip again. 07:18 Manual Open RCL 09-M4-01 and RCL 09-P3-08 07:25 Close LBS 09-P4-02, OK. CD fdr #16 still on block postiton 07:32 Blocked and Close RCL 09-P3-08, OK then release the block 07:35 Block and Close RCL 09-M4-01, but CD fdr #16 T/O again (on block) Suspect fault location at RCL 09-M4-01 (animal) 07:38 Closed VCB CD fdr #16, standby on block position 09:10 Animal on RCL 09-M4-01 has been removed 09:11 Blocked and Closed RCL 09-M4-01 (CD fdr #16 on block), OK. then release the block. las counter: RCL 09-M4-01 (194 - 196) RCL 09-P3-08 (145 - 146) CD ACB feeder #16 (349 - 351) Cause: Animal |  | 1 | 3:17 | Night | Friday | 2019 | 5
11083 | 2019-05-17 09:04 | 2019-05-17 09:04 | 13.8KV SINTONG GFPC | Cloudy | Unidentified | 0 | 09:45 Sintong GFPC T/R 1x Sintong fdr #2 dropped 44 A (198 - 154 A) Sintong fdr #1 dropped 34 A (107 - 73 A) Cause: Not Checked Yet |  | 1 | 9:04 | Morning | Friday | 2019 | 5
11084 | 2019-05-17 16:05 | 2019-05-17 16:05 | MINAS POWER PLANT |  |  | 0 | MGT-8 S/U and then online at 16:27 |  | 1 | 16:05 | Afternoon | Friday | 2019 | 5
11085 | 2019-05-17 16:30 | 2019-05-17 16:30 | MINAS POWER PLANT |  |  | 0 | MGT-7 Offline and then S/D to prepared for CI |  | 1 | 16:30 | Afternoon | Friday | 2019 | 5
11086 | 2019-05-17 16:33 | 2019-05-17 16:33 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 58 | 16:53 KTGL VCB fdr #2 T/R 1x KTGL VCB fdr #1 dropped 35 A (128 - 93 A) KTGL VCB fdr #3 dropped 9 A (33 - 24 A) Cause: Not Checked Yet |  | 1 | 16:33 | Afternoon | Friday | 2019 | 5
11087 | 2019-05-17 16:33 | 2019-05-26 07:15 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 58 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 329 - 330, Relay Flag : 51. Patrolled the line found : Dead end Flash Over Cause : Dead End Insulator |  | 1 | 16:33 | Afternoon | Friday | 2019 | 5
11088 | 2019-05-17 19:41 | 2019-05-17 19:41 | 13.8KV 6D FEEDER #1 | Cloudy | Lightning | 393 | 19:41 6D VCB fdr#1 T/O, (in Block position) Ctr: 361-362, R/F: 51N 20:09 Tried Block & Closed the VCB but Fail 21:37 Open LBS 5C-59, Patrolled the Line, found Broken Pin insulator & Deadend O/P...…. 21:39 Closed the VCB, Ok, then Closed Back the VCB to Replaced Pin Insulator Cause: Lightning |  | 1 | 19:41 | Night | Friday | 2019 | 5
11089 | 2019-05-17 19:41 | 2019-05-25 11:28 | 13.8KV 6D FEEDER #1 | Cloudy | Lightning | 393 | Checked and found: 6DSB-13.8OCB1 T/R, Counter : 360 - 364, Relay Flag : 51N. Patrolled the line found : Broken Pin Cause : Lightning |  | 1 | 19:41 | Night | Friday | 2019 | 5
11090 | 2019-05-17 23:29 | 2019-05-17 23:29 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 13 | 5B 13.8KV VCB fdr#2 T/R 1x. 5B fdr#5 load dropped 23A (112-89A). 5B fdr#1 load dropped 60A (80-20A). 5B fdr#3 load dropped 49A (83-34A). 5B fdr#6 load dropped 128A (245-113A). WIP Not checked yet. |  | 1 | 23:29 | Night | Friday | 2019 | 5
11091 | 2019-05-17 23:29 | 2019-05-24 05:51 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 13 | Checked and found OCB 5B fdr #2 T/R 1x, ctr: 421 - 422, R/F : 51N Patrolled the line and found broken insulator @2 on pole 4C-75 Cause : Lightning |  | 1 | 23:29 | Night | Friday | 2019 | 5
11092 | 2019-05-17 23:29 | 2019-05-17 23:29 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 2 | 6D 13.8KV VCB fdr#4 T/R 1x. Not checked yet. |  | 1 | 23:29 | Night | Friday | 2019 | 5
11093 | 2019-05-17 23:29 | 2019-05-22 10:49 | 13.8KV 6D FEEDER #4 | Rain and Lightning | Lightning | 2 | Checked and found: 6DSB-13.8OCB4 T/R, Counter : 567 - 568, Relay Flag : 51N Patrolled the line found: Nothing Cause : Lightning |  | 1 | 23:29 | Night | Friday | 2019 | 5
11094 | 2019-05-17 23:29 | 2019-05-17 23:29 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 8 | 6D 13.8KV VCB fdr#5 T/R 1x. 6D fdr#2 load dropped 127A (175-48A). 6D fdr#6 load dropped 250A (250-0A). WIP Not checked yet. |  | 1 | 23:29 | Night | Friday | 2019 | 5
11095 | 2019-05-17 23:29 | 2019-05-22 10:38 | 13.8KV 6D FEEDER #5 | Rain and Lightning | Lightning | 8 | Checked and found: 5442-R.5D64 T/R, Counter : 97 - 98, Relay Flag : 51N Patrolled the line found: Broken Pin dan deadend Cause : Lightning |  | 1 | 23:29 | Night | Friday | 2019 | 5
11096 | 2019-05-17 23:37 | 2019-05-17 23:37 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 3 | 6DN 13.8KV VCB fdr#1 T/R 1x. 6DN fdr#2 load dropped 113A (267-154A). 6DN fdr#3 load dropped 64A (133-69A). WIP 6DN fdr#4 load dropped 129A (211-82A). WIP Not checked yet. |  | 1 | 23:37 | Night | Friday | 2019 | 5
11097 | 2019-05-17 23:37 | 2019-05-21 20:37 | 13.8KV 6DN FEEDER #1 | Rain and Lightning | Lightning | 3 | Checked & found 6DN fdr#1 T/R 1x Ctr:169-170 R/F:51N. Patrolled the line not found nothing. Cause : Lightning. |  | 1 | 23:37 | Night | Friday | 2019 | 5
11098 | 2019-05-17 23:42 | 2019-05-17 23:42 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 8 | 3D 13.8KV VCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 23:42 | Night | Friday | 2019 | 5
11099 | 2019-05-17 23:42 | 2019-05-22 17:08 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Lightning | 8 | Checked and found: 3DSB-13.8OCB3 T/R, Counter : 485 - 486, Relay Flag : 51 Patrolled the line found: Broken dead end Cause : Lightning |  | 1 | 23:42 | Night | Friday | 2019 | 5
11100 | 2019-05-17 23:43 | 2019-05-17 23:43 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Lightning | 32 | Minas 13.8KV ACB#1 fdr#4 T/R 1x. Not checked yet. |  | 1 | 23:43 | Night | Friday | 2019 | 5
11101 | 2019-05-17 23:43 | 2019-05-23 22:59 | 13.8KV MINAS FEEDER #4 | Rain and Lightning | Lightning | 32 | Checked and found MNS fdr #4 T/LO, ctr: 8095 - 8097, R/F: 50N Patrolled the line but found nothing Cause : Lightning |  | 1 | 23:43 | Night | Friday | 2019 | 5
11102 | 2019-05-18 05:58 | 2019-05-18 05:58 | 115KV CENTRAL DURI - BATANG LINE | Cloudy | Suspension Insulator | 0 | 115Kv Line C.Duri-BTG GCB#31 T/R 1x. 115Kv Line C.Duri-BTG GCB#33 T/R 1x. 115Kv Line BTG-Sintong GCB#1 T/R 1x. 115Kv Line Sintong-BTG GCB#25 T/R 1x. Ground fault at Batang fdr#1 & fdr#2. So.Balm fdr#1 Load dropped 25A (100-75A). So.Balm fdr#2 Load dropped 28A (147-119A). Nella fdr#1 Load dropped 48A (182-134A). Nella fdr#2 Load dropped 41A (202-161A). Bangko fdr#1 Load dropped 15A (154-149A). Bangko fdr#4 Load dropped 18A (168-150A). Sintong fdr#1 Load dropped 10A (107-97A). Sintong fdr#2 Load dropped 16A (198-182A). Batang fdr#3 Load dropped 42A (50-8A). Not checked yet. |  | 1 | 5:58 | Morning | Saturday | 2019 | 5
11103 | 2019-05-18 05:58 | 2019-05-24 07:11 | 115KV CENTRAL DURI - BATANG LINE | Cloudy | Suspension Insulator | 0 | Checked and found: 115 KV BTG GCB T/R, Counter : 95 - 96, Relay Flag : 87 Patrolled the line found: broken suspension insulator Cause : Suspension Insulator |  | 1 | 5:58 | Morning | Saturday | 2019 | 5
11104 | 2019-05-18 07:31 | 2019-05-18 07:31 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 225 | DURI COMM feeder #2 T/R 1x Cause: Not Checked Yet |  | 1 | 7:31 | Morning | Saturday | 2019 | 5
11105 | 2019-05-18 07:31 | 2019-05-22 10:59 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 225 | Checked and found: DCSG-13.8ACB30 T/R, Counter : 108 - 109, Relay Flag : 51. Patrolled the line found: Nothing Cause : Unidentified |  | 1 | 7:31 | Morning | Saturday | 2019 | 5
11106 | 2019-05-18 10:41 | 2019-05-18 10:41 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 83 | 44 kV GCB #1 PMT Main T/R 1x (line to PETANI SS) Cause: Not Checked Yet |  | 1 | 10:41 | Morning | Saturday | 2019 | 5
11107 | 2019-05-18 10:41 | 2019-05-22 11:01 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 83 | Checked and found: PMTMSB-44OCB1 T/R, Counter : 187 - 188, Relay Flag : 51N Patrolled the line found : None Cause : Unidentified |  | 1 | 10:41 | Morning | Saturday | 2019 | 5
11108 | 2019-05-18 14:11 | 2019-05-18 14:11 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 166 | 14:11 Manual Open Minas ACB fdr #3, closed at 15:48 14:12 Manual Open Minas ACB fdr #4, closed at 15:49 14:12 Manual Open Minas ACB fdr #5, closed at 15:49 Repaired Static wire o/p: 8 ( no name). Cause: Planned Maintenance. |  | 1 | 14:11 | Afternoon | Saturday | 2019 | 5
11109 | 2019-05-19 00:13 | 2019-05-19 00:13 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Unidentified | 13 | Rokan VCB fdr#2 T/R 1x Not checked yet |  | 1 | 0:13 | Night | Sunday | 2019 | 5
11110 | 2019-05-19 00:13 | 2019-05-22 10:56 | 13.8KV ROKAN FEEDER #2 | Rain and Lightning | Unidentified | 13 | Checked and found: RKNSB-13.8VCB2 T/R, Counter : 1295 - 1297, Relay Flag : 51 Patrolled the line found: isolation switch broken Cause : Unidentified |  | 1 | 0:13 | Night | Sunday | 2019 | 5
11111 | 2019-05-19 00:44 | 2019-05-19 00:44 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Unidentified | 49 | 00:44 Petani VCB fdr#2 T/O (In Block Status, Rig Job) 00:51 Manually Closed In block status, after confirm to TDO & RIG team Cause : Not checked yet |  | 1 | 0:44 | Night | Sunday | 2019 | 5
11112 | 2019-05-19 00:44 | 2019-05-22 10:12 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Unidentified | 49 | Checked and found: PTNSB-13.8OCB2 T/O, Counter : 310 - 312, Relay Flag : 50N Patrolled the line, but found nothing. Cause : Unidentified. |  | 1 | 0:44 | Night | Sunday | 2019 | 5
11113 | 2019-05-19 00:57 | 2019-05-24 07:13 | 115KV CENTRAL DURI - BATANG LINE | Rain and Lightning | Lightning Arrester | 65 | Checked and found: 115 KV GCB CD T/R, Counter : 42 - 44, Relay Flag : 87 Patrolled the line found: Broken LA Cause : Lightning Arrester |  | 1 | 0:57 | Night | Sunday | 2019 | 5
11114 | 2019-05-19 08:13 | 2019-05-19 08:13 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 39 | 08:13 Manual Open RKN fdr #2, closed at 09:27 to maintain hi level tank due to WIP pump failed to started 08:29 Manual Open PTN fdr #2, closed at 10:56 to maintain level tank still high due to WIP pump failed to started 11:00 Reported no power control for motor of WIP at PETANI GS 11:30 Checked and found no power 220 V for control motor WIP, suspect problem at 50 kVA TX 13:30 Started to troubleshoot the problem Output power 220 V from 50 kVA TX is Normal 15:50 Re-checked and found b/o fuse 2 pcs for 75 kVA at PETANI GS and also found lube oil leak from primary bushing of TX (suspect TX failure) 16:15 Plan to change out the TX tomorrow. Cause: TX failure |  | 1 | 8:13 | Morning | Sunday | 2019 | 5
11115 | 2019-05-19 08:13 | 2019-05-20 10:23 | 13.8KV PETANI FEEDER #1 | Fair | Transformer Failure | 39 | Change out 75 kVA Transformer at PETANI GS Cause: TX Failure |  | 1 | 8:13 | Morning | Sunday | 2019 | 5
11116 | 2019-05-19 08:29 | 2019-05-19 08:29 | 13.8KV PETANI FEEDER #2 | Fair | Others | 326 | 08:29 Manual Open VCB PTN fdr #2 to high level tank at Petani GS. and then Closed at 10:56 R/ Tarmizi/Panggabean |  | 1 | 8:29 | Morning | Sunday | 2019 | 5
11117 | 2019-05-19 09:31 | 2019-05-19 09:31 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 22 | 10:25 CD ACB fdr #1 T/R 1x, ctr: 246 - 247, R/F: 51G, 51N Cause: Not Checked Yet |  | 1 | 9:31 | Morning | Sunday | 2019 | 5
11118 | 2019-05-19 09:31 | 2019-05-24 09:49 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Lightning | 22 | Checked and found: CDRSG-13.8ACB11 T/R, Counter : 246 - 247, Relay Flag : 51G, Patrolled the line found : Bushing recloser Cause : Lightning |  | 1 | 9:31 | Morning | Sunday | 2019 | 5
11119 | 2019-05-19 10:25 | 2019-05-19 10:25 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 71 | 10:25 Manual Open LBS 29-Al-07 Purpose: MTCE team to bypass RCL 29-AL-03 (bushing burned out) Cause: Planned Maintenance |  | 1 | 10:25 | Morning | Sunday | 2019 | 5
11120 | 2019-05-19 15:28 | 2019-05-19 15:28 | 13.8KV 4B FEEDER #3 | Fair | Planned Maintenance | 0 | Manual Open 4B VCB fdr #3 for repair jumper at 2500 kVA TX-5 GS-6 Cause: Planned Maintenance |  | 1 | 15:28 | Afternoon | Sunday | 2019 | 5
11121 | 2019-05-20 05:32 | 2019-05-20 05:32 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 82 | OKB OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 5:32 | Morning | Monday | 2019 | 5
11122 | 2019-05-20 05:32 | 2019-05-22 10:39 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 82 | Checked and found: KBKSB-13.8OCB2 T/R, Counter : 1367 - 1368, Relay Flag : 50N. Patrolled the line found : Broken Deadend. Cause : Lightning |  | 1 | 5:32 | Morning | Monday | 2019 | 5
11123 | 2019-05-20 09:06 | 2019-05-20 09:06 | 13.8KV MINAS FEEDER #4 | Fair | Lightning | 42 | 06:45 Minas ACB fdr#4 T/R 1x Ctr:101-102 R/F:51N. 09:06 MINAS ACB feeder #4 T/R 1x again. Cause: Not Checked Yet |  | 1 | 9:06 | Morning | Monday | 2019 | 5
11124 | 2019-05-20 09:06 | 2019-05-25 11:23 | 13.8KV MINAS FEEDER #4 | Fair | Lightning | 42 | Checked and found: MNSSG-13.8ACB01 T/R, Counter : 8097 - 8098, Relay Flag : 51N. Patrolled : Nothing found Cause : Lightning |  | 1 | 9:06 | Morning | Monday | 2019 | 5
11125 | 2019-05-20 09:53 | 2019-05-20 09:53 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 55 | 09:53 KETIGUL VCB feeder #2 T/R 1x KETIGUL VCB feeder #1 dropped 10A (125 - 115 A) KETIGUL VCB feeder #3 dropped 9 A (33 - 24 A) Cause: Not Checked Yet |  | 1 | 9:53 | Morning | Monday | 2019 | 5
11126 | 2019-05-20 09:53 | 2019-05-24 07:17 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 55 | Checked and found: KBKSB-13.8OCB2 T/R, Counter : 1367 - 1368, Relay Flag : 50N Patrol led the line found: Found Broken Deadend. Cause : Lightning |  | 1 | 9:53 | Morning | Monday | 2019 | 5
11127 | 2019-05-20 11:16 | 2019-05-20 11:16 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Accident | 112 | 11:16 CD fdr #1 dropped 50 A (114 - 64 A) MTCE team plan to working d/s RCL 39-AV-36 (blocked for their job) 12:02 Checked and found RCL 39-AV-36 T/O (on block), ctr: 281 (reported the RCL had operated 3x before blocked, ctr: 277 - 280) 14:23 Patrolled the line and found any dress up activity at area KULIN #54 PT WKS equipment hit PGT pole guy and break the guy wire for terminal pole of KULIN #54. The terminal pole get tilted and the conductor @2 on terminal pole touch to pole/ground. 14:40 Open HLC on TOP KULIN #54 (by MTCE team), to isolate the line 14:44 Blocked and Closed RCL 39-AV-36, OK 16:30 Repair Guy Wire at KULIN #54 completed and well already POP 16:41 Normalize Block RCL 39-AV-36 Cause: Incident (broken guy wire) |  | 1 | 11:16 | Morning | Monday | 2019 | 5
11128 | 2019-05-20 14:03 | 2019-05-20 14:03 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 107 | Nella 13.8KV VCB fdr #1 T/R 2X. Nella 13.8KV GFPC T/R 1X. Nella 13.8KV Recloser Cap Bank T/O. Not checked yet. |  | 1 | 14:03 | Afternoon | Monday | 2019 | 5
11129 | 2019-05-20 14:03 | 2019-05-21 09:30 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 107 | Checked and found: Nella GFPC T/R 2X counter: 971-973 R/F : 51N Nella VCB Feeder 1 T/R 2X counter: 537-539, R/F : 51P @2 and @3 Patrolled and found normal operation. Cause: Lightning |  | 1 | 14:03 | Afternoon | Monday | 2019 | 5
11130 | 2019-05-20 14:09 | 2019-05-20 14:09 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 30 | Nella 13.8KV VCB fdr #2 T/R 1X. Nella 13.8KV GFPC T/R 1X. Not checked yet. |  | 1 | 14:09 | Afternoon | Monday | 2019 | 5
11131 | 2019-05-20 15:58 | 2019-05-20 15:58 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 22 | 15:58 S. Bekasap fdr #1 load dropped 58A (130-72A). Not checked yet. |  | 1 | 15:58 | Afternoon | Monday | 2019 | 5
11132 | 2019-05-20 15:58 | 2019-05-24 10:02 | 13.8KV SO BEKASAP FEEDER #1 | Rain and Lightning | Lightning | 22 | Checked and found: 5440-R.36BI04 T/R, Counter : 473 - 474, Relay Flag : SGF Patrolled the line found : PIN Insulator pecah sedikit di phase 2 Cause : Lightning |  | 1 | 15:58 | Afternoon | Monday | 2019 | 5
11133 | 2019-05-20 16:58 | 2019-05-20 16:58 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Pin Insulator | 18 | 16:58 Pungut 13.8KV OCB fdr #1 T/R 1X. Pungut fdr #2 load dropped 18A (47-29A). 17:25 Pungut 13.8KV OCB fdr #1 T/R again. Not checked yet. |  | 1 | 16:58 | Afternoon | Monday | 2019 | 5
11134 | 2019-05-20 16:58 | 2019-05-24 10:15 | 13.8KV PUNGUT FEEDER #1 | Rain and Lightning | Pin Insulator | 18 | Checked and found: PNTSB-13.8OCB1 T/R, Counter : 412 - 414, Relay Flag : 51 Patrolled the line found : Pin insulator pecah di bagain bawah Cause : Pin Insulator |  | 1 | 16:58 | Afternoon | Monday | 2019 | 5
11135 | 2019-05-20 17:01 | 2019-05-20 17:01 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning Arrester | 10 | Pungut 13.8KV OCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 17:01 | Afternoon | Monday | 2019 | 5
11136 | 2019-05-20 17:01 | 2019-05-24 10:19 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Lightning Arrester | 10 | Checked and found: PNTSB-13.8OCB2 T/R, Counter : 421 - 422, Relay Flag : 51N Patrolled the line found : LA Pecah di phase 3 Cause : Lightning Arrester |  | 1 | 17:01 | Afternoon | Monday | 2019 | 5
11137 | 2019-05-21 09:24 | 2019-05-21 09:24 | 13.8KV 3D FEEDER #2 | Fair | Planned Maintenance | 0 | 09:24 Manual Open LBS: 3E-64 d/s: 3D fdr #2. Manual Open LBS: 4D-88 d/s: 4D fdr #5. Closed Tie Tap o/p: 4E-06. 11:13 Closed LBS: 3E-64 (Load 3D fdr #2 back to normal). Cause: Plan Maintenance. |  | 1 | 9:24 | Morning | Tuesday | 2019 | 5
11138 | 2019-05-21 11:39 | 2019-05-21 11:39 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Planned Maintenance | 7 | 11:39 Open LBS 04-08-27 d/s CD fdr #7 11:50 Open Recl.: 03-00-02 d/s CD fdr #6. (by Mechanical switch due to Control problem). Re Connected Jumper o/p: 03-00-05. 12:53 Closed LBS 04-08-27. Cause: Plan maintenance. |  | 1 | 11:39 | Morning | Tuesday | 2019 | 5
11139 | 2019-05-21 12:57 | 2019-05-21 12:57 | 13.8KV PUNGUT FEEDER #2 | Fair | Unidentified | 49 | 12:57 It was reported no power at wells : Gading #01, Asih #02, N. Asih 302 and Ami #03. 15:00 Checked and found Recl.: 44-BX-06 T/SO ctr:424-425. Patrolled the line, but found nothing. Blocked and closed the Recl. OK then released the block. Cause: Unidentified. |  | 1 | 12:57 | Afternoon | Tuesday | 2019 | 5
11140 | 2019-05-21 17:02 | 2019-05-21 17:02 | 13.8KV 5B FEEDER #3 | Fair | Lightning | 0 | 5B feeder #3 dropped 62 A (74 - 12 A) Cause: Not Checked Yet |  | 1 | 17:02 | Afternoon | Tuesday | 2019 | 5
11141 | 2019-05-21 17:02 | 2019-05-23 07:34 | 13.8KV 5B FEEDER #3 | Fair | Lightning | 0 | Checked and found: 5442-R.4C65A None, Counter : 78 - 78, Relay Flag : NONE Patrolled the line found: Nothing Cause: Lighting |  | 1 | 17:02 | Afternoon | Tuesday | 2019 | 5
11142 | 2019-05-22 10:32 | 2019-05-22 10:32 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Planned Maintenance | - | 10:32 Manually open Recloser 05-P1-23 D/S C.Duri feeder #15. due to replace dead end insulator on pole 05-P1-23A. 14:00 Manually block and closed Recloser 05-P1-23 and then released the block. Cause: Plan maintenance. |  | 1 | 10:32 | Morning | Wednesday | 2019 | 5
11143 | 2019-05-22 13:37 | 2019-05-22 13:37 | CENTRAL DURI POWER PLANT |  |  | 0 | 13:37 S/U CDGT#5 and then on line the unit 14:23. |  | 1 | 13:37 | Afternoon | Wednesday | 2019 | 5
11144 | 2019-05-22 14:20 | 2019-05-22 14:20 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 60 | Ketigul VCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 14:20 | Afternoon | Wednesday | 2019 | 5
11145 | 2019-05-22 14:20 | 2019-05-24 10:08 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Lightning | 60 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 327 - 329, Relay Flag : 51N Patrolled the line found : Dead End Flash Over Cause : Lightning |  | 1 | 14:20 | Afternoon | Wednesday | 2019 | 5
11146 | 2019-05-22 14:20 | 2019-05-22 14:20 | 13.8KV KETIGUL FEEDER#3 | Rain and Lightning | Normal Condition | 7 | Ketigul VCB feeder #3 T/R 1x. Not checked yet. |  | 1 | 14:20 | Afternoon | Wednesday | 2019 | 5
11147 | 2019-05-22 14:20 | 2019-05-28 15:27 | 13.8KV KETIGUL FEEDER#3 | Rain and Lightning | Normal Condition | 7 | Checked and found VCB KTGL fdr #3 is Normal, ctr: 212-212, R/F: None Not need to patrolled the line. Cause : Normal Condition |  | 1 | 14:20 | Afternoon | Wednesday | 2019 | 5
11148 | 2019-05-22 14:20 | 2019-05-22 14:20 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Normal Condition | 6 | Ketigul feeder #1 load dropped 104A (120-16A). Not checked yet. |  | 1 | 14:20 | Afternoon | Wednesday | 2019 | 5
11149 | 2019-05-22 14:20 | 2019-05-26 08:12 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Normal Condition | 6 | Checked and found: 5441-R.32-AK-16 None, Counter : 140 - 140, Relay Flag : NONE Patrolled the line found : Normal Condition, Load Drop 104 Cause : Normal Condition |  | 1 | 14:20 | Afternoon | Wednesday | 2019 | 5
11150 | 2019-05-22 14:55 | 2019-05-22 14:55 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 0 | 6D OCB fdr#1 T/R 1x. 6D fdr#2 load dropped 20A (160-140). Not checked yet. |  | 1 | 14:55 | Afternoon | Wednesday | 2019 | 5
11151 | 2019-05-22 14:55 | 2019-05-25 11:08 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Lightning | 0 | Checked and found: 6DS-B-13.8OCB1 T/R, Counter : 364 - 365, Relay Flag : 51. Patrolled : Broken dead end Cause : Lightning |  | 1 | 14:55 | Afternoon | Wednesday | 2019 | 5
11152 | 2019-05-22 14:55 | 2019-05-22 14:55 | 13.8KV 6DN FEEDER #4 | Rain and Lightning | Unidentified | 0 | 6DN fdr#4 load dropped 127A (213-86A). 6DN fdr#3 load dropped 66A (132-66A). Not checked yet. |  | 1 | 14:55 | Afternoon | Wednesday | 2019 | 5
11153 | 2019-05-22 14:55 | 2019-05-28 20:39 | 13.8KV 6DN FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked and found all in Normal Condition, ctr 6DN OCB fdr #4: 434-434 Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 14:55 | Afternoon | Wednesday | 2019 | 5
11154 | 2019-05-22 14:59 | 2019-05-22 14:59 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | N.Duri VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 14:59 | Afternoon | Wednesday | 2019 | 5
11155 | 2019-05-22 14:59 | 2019-05-26 07:38 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked and found: NDRSB-13.8VCB1 T/R, Counter : 308 - 309, Relay Flag : 51 Patrol led the line found: no finding Cause : Unidentified |  | 1 | 14:59 | Afternoon | Wednesday | 2019 | 5
11156 | 2019-05-22 15:07 | 2019-05-22 15:07 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 43 | 4B OCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 15:07 | Afternoon | Wednesday | 2019 | 5
11157 | 2019-05-22 15:07 | 2019-05-25 10:48 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 43 | Checked and found: 4BSB-13.8OCB1 T/R, Counter : 373 - 374, Relay Flag : 50N. Patrolled the line found : Nothing found Cause : Lightning |  | 1 | 15:07 | Afternoon | Wednesday | 2019 | 5
11158 | 2019-05-22 15:07 | 2019-05-22 15:07 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 23 | 4B OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 15:07 | Afternoon | Wednesday | 2019 | 5
11159 | 2019-05-22 15:07 | 2019-05-25 10:43 | 13.8KV 4B FEEDER #2 | Rain and Lightning | Lightning | 23 | Checked and found: 4BSB-13.8OCB2 T/R, Counter : 288 - 292, Relay Flag : 51. Patrol led the line found: Broken pin Cause : Lightning |  | 1 | 15:07 | Afternoon | Wednesday | 2019 | 5
11160 | 2019-05-22 15:07 | 2019-05-22 15:07 | 13.8KV 4B FEEDER #3 | Rain and Lightning | Unidentified | 0 | 4B fdr#3 load dropped 133A (135-2A). 4B fdr#4 load dropped 121A (127-6A). 4B fdr#5 load dropped 60A (152-92A). Not checked yet. |  | 1 | 15:07 | Afternoon | Wednesday | 2019 | 5
11161 | 2019-05-22 15:07 | 2019-05-28 21:11 | 13.8KV 4B FEEDER #3 | Rain and Lightning | Unidentified | 0 | Checked and found all normal, ctr OCB 4B fdr #3: 175-175, R/F: None Not patrolled the line Cause : Unidentified |  | 1 | 15:07 | Afternoon | Wednesday | 2019 | 5
11162 | 2019-05-22 15:08 | 2019-05-22 15:08 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 0 | 8C fdr#3 load dropped 137A (183-46A). Not checked yet. |  | 1 | 15:08 | Afternoon | Wednesday | 2019 | 5
11163 | 2019-05-22 15:08 | 2019-05-25 10:51 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 0 | Checked and found: 5442-R.8D18A T/R, Counter : 183 - 185, Relay Flag : NONE. Patrolled : Nothing found Cause : Lightning |  | 1 | 15:08 | Afternoon | Wednesday | 2019 | 5
11164 | 2019-05-22 15:12 | 2019-05-22 15:12 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Pin Insulator | 23 | C.Duri fdr#1 load dropped 50A (134-84A). Not checked yet. |  | 1 | 15:12 | Afternoon | Wednesday | 2019 | 5
11165 | 2019-05-22 15:12 | 2019-05-24 08:16 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Pin Insulator | 23 | Checked and found: CDRSG-13.8ACB11 T/R, Counter : 246 - 247, Relay Flag : 51G Patrolled the line found : insulator by pass pecah 3 layer Cause : Pin Insulator |  | 1 | 15:12 | Afternoon | Wednesday | 2019 | 5
11166 | 2019-05-22 15:14 | 2019-05-22 15:14 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Unidentified | 356 | 15:14 N.Duri VCB fdr#2 T/O (In block position Pt. WKS Clean up canal). 15:28 Blocked & closed N.Duri VCB fdr#2. 17:15 It was reported no power o/p: 13-H1.1-39. 00:40 Checked and found Recl.:13-G71-10 T/O (On block PT WKS Clean canal). 00:55 Patrolled the line, but found normal. 01:25 Blocked and closed the Recloser, OK. (Recl.:13-G71-10 still blocked for PT WKS Clean canal) Not checked yet. |  | 1 | 15:14 | Afternoon | Wednesday | 2019 | 5
11167 | 2019-05-22 15:14 | 2019-05-26 07:39 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Unidentified | 356 | Checked and found: NDRSB-13.8VCB2 T/R, Counter : 280 - 281, Relay Flag : 50 Patrolled the line found : nothing Cause : Unidentified |  | 1 | 15:14 | Afternoon | Wednesday | 2019 | 5
11168 | 2019-05-22 16:17 | 2019-05-22 16:17 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Pin Insulator | 0 | Batang VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 16:17 | Afternoon | Wednesday | 2019 | 5
11169 | 2019-05-22 16:17 | 2019-05-24 10:38 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Pin Insulator | 0 | Checked and found: BTGSB-13.8OCB2 T/R, Counter : 187 - 188, Relay Flag : 51 Patrolled the line found : Pin insulator pecah Cause : Pin Insulator |  | 1 | 16:17 | Afternoon | Wednesday | 2019 | 5
11170 | 2019-05-22 16:17 | 2019-05-22 16:17 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning Arrester | 0 | Batang VCB fdr#3 T/R 1x. Not checked yet. |  | 1 | 16:17 | Afternoon | Wednesday | 2019 | 5
11171 | 2019-05-22 16:17 | 2019-05-26 08:19 | 13.8KV BATANG FEEDER #3 | Rain and Lightning | Lightning Arrester | 0 | Checked and found: 5441-MBL1#1-RCL T/R, Counter : 940 - 945, Relay Flag : 50N Patrolled the line found : Jumper LA putuus Cause : Lightning Arrester |  | 1 | 16:17 | Afternoon | Wednesday | 2019 | 5
11172 | 2019-05-22 16:30 | 2019-05-22 16:30 | 13.8KV BANGKO FEEDER #1 | Cloudy | Recloser | 0 | Bangko fdr#1 load dropped 109A (164-55A). Bangko fdr#4 load dropped 80A (168-88A). Not checked yet. |  | 1 | 16:30 | Afternoon | Wednesday | 2019 | 5
11173 | 2019-05-22 16:30 | 2019-05-30 09:24 | 13.8KV BANGKO FEEDER #1 | Cloudy | Recloser | 0 | Checked & found Recl 23 X 08 T/R 2x, Ctr: 209-211, R/F: 51N Patrolled the Line, but found nothing Cause : Recloser |  | 1 | 16:30 | Afternoon | Wednesday | 2019 | 5
11174 | 2019-05-22 16:30 | 2019-05-30 09:24 | 13.8KV BANGKO FEEDER #1 | Cloudy | Recloser | 0 | Checked & found Recl 23 X 08 T/R 2x, Ctr: 209-211, R/F: 51N Patrolled the Line, but found nothing Cause : Recloser |  | 1 | 16:30 | Afternoon | Wednesday | 2019 | 5
11175 | 2019-05-22 16:30 | 2019-05-30 09:30 | 13.8KV BANGKO FEEDER #4 | Cloudy | Recloser | 37 | Checked and found 5440-R.25Z07 T/R, 5440-R.25Z07 T/R, Relay Flag : 51N Date Patrol : 29-MAY-2019 Patrolled the line found : Tree Cause : Recloser |  | 1 | 16:30 | Afternoon | Wednesday | 2019 | 5
11176 | 2019-05-22 16:32 | 2019-05-22 16:32 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Unidentified | 0 | 16:32 Pematang fdr#1 load dropped 147A (207-60A). 16:40 Manually open Pematang OCB feeder #2. Due to maintain water level tank. 17:29 Manually blocked and closed Pematang OCB feeder #2. and then released the block. Not checked yet. |  | 1 | 16:32 | Afternoon | Wednesday | 2019 | 5
11177 | 2019-05-22 16:32 | 2019-05-26 08:04 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked and found:5440-R.35BC14 Unknown, Counter : 138 - 138, Relay Flag : NONE Patrolled the line found: Normal, Tipe Gangguan Load Drop Cause : Unidentified |  | 1 | 16:32 | Afternoon | Wednesday | 2019 | 5
11178 | 2019-05-22 16:32 | 2019-05-22 16:32 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Animal | 0 | Rangau fdr#2 load dropped 64A (200-136A). Not checked yet. |  | 1 | 16:32 | Afternoon | Wednesday | 2019 | 5
11179 | 2019-05-22 16:32 | 2019-05-26 07:48 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Animal | 0 | Checked and found: 5440-R.23BD01 T/R, Counter : 375 - 377, Relay Flag : NONE Patrolled the line found: monyet mati di Lampu 01 Cause : Animal |  | 1 | 16:32 | Afternoon | Wednesday | 2019 | 5
11180 | 2019-05-22 16:33 | 2019-05-22 16:33 | 44KV PEMATANG MAIN - PETANI LINE | Rain and Lightning | Tree | 108 | Pematang Main 44 KV OCB #1 (44 KV Line PMT - PTN) T/R 1x. No power at Petani Substation. - Petani OCB feeder #1. - Petani OCB feeder #2. Not checked yet. |  | 1 | 16:33 | Afternoon | Wednesday | 2019 | 5
11181 | 2019-05-22 16:33 | 2019-05-26 07:26 | 44KV PEMATANG MAIN - PETANI LINE | Rain and Lightning | Tree | 108 | Checked and found: PMTMSB-44OCB1 T/R, Counter : 188 - 189, Relay Flag : 51N. Patrolled the line found : Bambu menentuh line Cause : Tree |  | 1 | 16:33 | Afternoon | Wednesday | 2019 | 5
11182 | 2019-05-23 08:04 | 2019-05-23 08:04 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Tree | 0 | Duri Comy ACB#25 (feeder #1) T/R 1x. Not checked yet. |  | 1 | 8:04 | Morning | Thursday | 2019 | 5
11183 | 2019-05-23 08:04 | 2019-05-26 07:33 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Tree | 0 | Checked and found: DCSG-13.8ACB25 T/R, Counter : 135 - 136, Relay Flag : 51N. Patrol led the line found: : Ranting pohon menyentuh Line Cause : Tree |  | 1 | 8:04 | Morning | Thursday | 2019 | 5
11184 | 2019-05-23 09:26 | 2019-05-23 09:26 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Fair | Planned Maintenance | 0 | 09:26 Manually Open Dumai 4.16 Kv VCB#22 (feeder#4 housing). Due to Tree trimming at TWA Dumai. 11:16 Manually blocked & closed Dumai 4.16 Kv VCB#22 and then release the block. Cause:Plant maintenance. |  | 1 | 9:26 | Morning | Thursday | 2019 | 5
11185 | 2019-05-23 10:41 | 2019-05-23 10:41 | 13.8KV ROKAN FEEDER #2 | Fair | Planned Maintenance | 43 | 10:41 Manually open Rokan VCB fdr#2. Due to replace @1 broken Pin insulator o/p 30-AV-26 , 31-AV-01 , 31-AV-11. 11:57 Manually blocked & closed Rokan VCB fdr#2 and then release the block. Cause: Plant maintenance. |  | 1 | 10:41 | Morning | Thursday | 2019 | 5
11186 | 2019-05-23 14:30 | 2019-05-23 14:30 | 13.8KV 4B FEEDER #2 | Fair | Recloser | 49 | 14:30 It was reported no power D/S Recloser: 5B-93 D/S 4B feeder #2. 15:37 Checked and found Recloser: 5B-93 T/O (Load: 17A). Patrolled the line found nothing. Manually blocked and closed Recloser: 5B-93 but failed. Counter: Did not change , 15:40 Transfer part load 4B feeder #2 to 5B feeder #1 by closed LBS: 5B-128. Cause: Suspected Recloser mal function. |  | 1 | 14:30 | Afternoon | Thursday | 2019 | 5
11187 | 2019-05-23 16:50 | 2019-05-23 16:50 | MINAS POWER PLANT |  |  | - | 16:50 Offline MGT #8 and then S/D the unit for Standby. |  | 1 | 16:50 | Afternoon | Thursday | 2019 | 5
11188 | 2019-05-23 18:39 | 2019-05-23 18:39 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 21 | Duri Field VCB #52 (feeder #3) T/R 1x. Duri Field feeder #2 load dropped 24A (148-124A). Not checked yet. |  | 1 | 18:39 | Afternoon | Thursday | 2019 | 5
11189 | 2019-05-23 18:39 | 2019-05-26 07:31 | 13.8KV DURI FIELD FEEDER #3 | Fair | Unidentified | 21 | Checked and found: DFSG-13.8ACB52 T/R, Counter : 382 - 383, Relay Flag : 50N. Patrolled the line found : No Finding Cause : Unidentified |  | 1 | 18:39 | Afternoon | Thursday | 2019 | 5
11190 | 2019-05-24 10:31 | 2019-05-24 10:31 | 13.8KV 8D FEEDER #10 | Fair | Planned Maintenance | 0 | 10:34 Manually Open 8D OCB fdr#10. Due to C/O at Well 7E-76 (S/B to VSD). Tx=300-400 Kva , Sec.Voltage= 480 V, R/M=160HP. 11:17 Blocked & Closed 8D OCB fdr#10 and then release the block. Cause: Planned Maintenance. |  | 1 | 10:31 | Morning | Friday | 2019 | 5
11191 | 2019-05-24 15:09 | 2019-05-24 15:09 | 13.8KV ROKAN FEEDER #3 | Fair | Planned Maintenance | 0 | 15:09 Manually Open Rokan VCB fdr#3. Due to reposition control Recloser & modification jumpers. 15:52 Manually block & Closed Rokan VCB fdr#3 and release the block. Cause: Planned Maintenance. |  | 1 | 15:09 | Afternoon | Friday | 2019 | 5
11192 | 2019-05-24 22:55 | 2019-05-24 22:55 | CENTRAL DURI POWER PLANT |  |  | 0 | CDGT #5 Tripped by Vibration |  | 1 | 22:55 | Night | Friday | 2019 | 5
11193 | 2019-05-25 00:13 | 2019-05-25 00:13 | MINAS POWER PLANT |  |  | 0 | MGT #8 S/U and then online at 00:41 due to CDGT #2 failed to start. |  | 1 | 0:13 | Night | Saturday | 2019 | 5
11194 | 2019-05-25 08:58 | 2019-05-25 08:58 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Planned Maintenance | 0 | 08:58 Manually Open C.Duri fdr#15 (load 15A after transfer to C,Duri#14). Due to C/O broken dead and Insulator o/p 06-Q5-02. 09:54 Manually blocked & closed C.Duri fdr#15 and then release the block. Cause: Planned Maintenance. |  | 1 | 8:58 | Morning | Saturday | 2019 | 5
11195 | 2019-05-25 11:00 | 2019-05-25 11:00 | CENTRAL DURI POWER PLANT |  |  | 0 | CGT #5 S/U and then online at 11:12. |  | 1 | 11:00 | Morning | Saturday | 2019 | 5
11196 | 2019-05-25 15:38 | 2019-05-25 15:38 | MINAS POWER PLANT |  |  | 0 | 15:38 Offline MGT #8 and then S/D the unit for stanby. |  | 1 | 15:38 | Afternoon | Saturday | 2019 | 5
11197 | 2019-05-26 13:45 | 2019-05-26 13:45 | 13.8KV 4D FEEDER #3 | Fair | Lightning | 20 | 4D OCB feeder #3 T/R 1x. Not checked yet. |  | 1 | 13:45 | Afternoon | Sunday | 2019 | 5
11198 | 2019-05-26 13:45 | 2019-05-28 20:57 | 13.8KV 4D FEEDER #3 | Fair | Lightning | 20 | Checked and found OCB 4D fdr #3 T/R 1x, ctr: 272 - 273, R/F: 51P @1 Patrolled the line and found broken dead end @1 on pole 4D-236 Cause : Lightning |  | 1 | 13:45 | Afternoon | Sunday | 2019 | 5
11199 | 2019-05-26 17:51 | 2019-05-26 17:51 | NORTH DURI SUBSTATION | Fair | Animal | 321 | 17:51 N Duri 115 Kv C/S Tx #12 Trip. No power on : - N Duri VCB feeder #4, Manual Open at 20:40, closed at 20:54 - N Duri VCB feeder #5, Manual Open at 20:40, closed at 20:52 - N Duri VCB feeder #6, Manual Open at 20:40, closed at 20:55 - N Duri VCB feeder #7, Manual Open at 20:40, closed at 20:56 - N Duri VCB feeder #8, Manual Open at 20:40, closed at 20:56 19:53 Checked and found - TX-12 visual condition is Normal, WT: 45 C, LT: 45 C. - C/S TX-12 Tripped, counter: 204 - 205 - 86T & 86HR are not operate - R/F of TX-12 = 51N W2 - Alarm at relay ND feeder #8 = 50N - VCB feeder #5 T/R 1x, counter: 131 - 132, R/F: 51N 20:40 Manual Open All Feeders (feeder #4, #5, #6, #7, #8) 20:48 Manual Close C/S of TX-12 ND, OK, TX-12 Energized. Last Counter: - C/S TX-12 = 205 - VCB feeder #4 = 167 - VCB feeder #5 = 133 - VCB feeder #6 = 310, --- Prod Loss (Area 12 : 308 Bbls/152 Wells) - VCB feeder #7 = 107 - VCB feeder #8 = 96 Cause: Not Patrolled Yet |  | 1 | 17:51 | Afternoon | Sunday | 2019 | 5
11200 | 2019-05-26 17:51 | 2019-05-28 15:21 | NORTH DURI SUBSTATION | Fair | Animal | 321 | Checked and found VCB fdr #5 T/R 1x, ctr: 131 - 132, R/F 51N Patrolled the line d/s ND fdr #5 and found dead animal (monkey) o/p 12-E11-01 Cause : Animal (monkey) |  | 1 | 17:51 | Afternoon | Sunday | 2019 | 5
11201 | 2019-05-26 21:58 | 2019-05-26 21:58 | 13.8KV ROKAN FEEDER #3 | Fair | Tree | - | Rokan VCB fdr#3 T/R 1x. Rokan fdr#2 load dropped 10A (29-19). Not checked yet. |  | 1 | 21:58 | Night | Sunday | 2019 | 5
11202 | 2019-05-26 21:58 | / | 13.8KV ROKAN FEEDER #3 | Fair | Tree | - | Rokan VCB fdr#3 T/R 1x. Rokan fdr#2 load dropped 10A (29-19). Not checked yet. |  | 1 | 21:58 | Night | Sunday | 2019 | 5
11203 | 2019-05-26 21:58 | / | 13.8KV ROKAN FEEDER #3 | Fair | Tree | - | Rokan VCB fdr#3 T/R 1x. Rokan fdr#2 load dropped 10A (29-19). Not checked yet. |  | 1 | 21:58 | Night | Sunday | 2019 | 5
11204 | 2019-05-26 21:58 | / | 13.8KV ROKAN FEEDER #3 | Fair | Tree | - | Rokan VCB fdr#3 T/R 1x. Rokan fdr#2 load dropped 10A (29-19). Not checked yet. |  | 1 | 21:58 | Night | Sunday | 2019 | 5
11205 | 2019-05-27 06:28 | 2019-05-27 06:28 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | - | Duri Comm ACB feeder #1 T/R 1x Cause: Not Checked Yet |  | 1 | 6:28 | Morning | Monday | 2019 | 5
11206 | 2019-05-27 06:28 | 2019-05-31 07:02 | 13.8KV DURI COMMUNITY FEEDER #1 | Fair | Unidentified | - | Checked and found: DCSG-13.8ACB25 T/R, Counter : 137 - 138, Relay Flag : 51N Patrolled the line found : Nothing Cause : Unidentified |  | 1 | 6:28 | Morning | Monday | 2019 | 5
11207 | 2019-05-27 07:23 | 2019-05-27 07:23 | 13.8KV PETANI FEEDER #2 | Fair | Tree | 50 | PETANI OCB feeder #2 T/R 1x. PETANI feeder #1 load dropped 120A (253-133A). Not checked yet. |  | 1 | 7:23 | Morning | Monday | 2019 | 5
11208 | 2019-05-27 07:23 | 2019-02-06 07:23 | 13.8KV PETANI FEEDER #2 | Fair | Tree | 50 | Checked & found Petani VCB fdr#2 T/R 1x Ctr:312-314 R/F:51N. Patrolled the line & found Danger high tree near pole 33AX44. Cause : Tree. |  | 1 | 7:23 | Morning | Monday | 2019 | 5
11209 | 2019-05-27 10:07 | 2019-05-27 10:07 | 13.8KV PETANI FEEDER #2 | Fair | Pin Insulator | 1 | PETANI OCB feeder #2 T/R 1x. PETANI feeder #1 load dropped 182A (253-7A). Not checked yet. |  | 1 | 10:07 | Morning | Monday | 2019 | 5
11210 | 2019-05-27 10:07 | 2019-02-06 10:07 | 13.8KV PETANI FEEDER #2 | Fair | Pin Insulator | 1 | Checked & found Petani VCB fdr#2 Ctr:314-315 R/F:51N. Patrolled the line & found @1@2 Broken Pin Insulator o/p 34AZ40. Cause : Pin Insulator. |  | 1 | 10:07 | Morning | Monday | 2019 | 5
11211 | 2019-05-27 13:50 | 2019-05-27 13:50 | 13.8KV NORTH DURI FEEDER #6 | Fair | Unidentified | 55 | 13:50 It was reported no power o/p 12-F5-08 d/s N.Duri feeder#6. 14:36 Checked and found Recl: 12-F5-02 T/O. Ctr: 79 - 80. 15:23 Manually block and closed Recl: 12-F5-02. Ok and then relased the block. Cause : Unidentified. |  | 1 | 13:50 | Afternoon | Monday | 2019 | 5
11212 | 2019-05-27 15:20 | 2019-05-27 15:20 | MINAS POWER PLANT |  |  | - | 15:20 MGT #7 S/U and then online at 15:36. |  | 1 | 15:20 | Afternoon | Monday | 2019 | 5
11213 | 2019-05-27 16:40 | 2019-05-27 16:40 | CENTRAL DURI POWER PLANT |  |  | - | 16:40 S/U CDGT #2 and then Online the unit at 17:00. |  | 1 | 16:40 | Afternoon | Monday | 2019 | 5
11214 | 2019-05-27 17:26 | 2019-05-27 17:26 | CENTRAL DURI POWER PLANT |  |  | - | 17:26 Offline CGDT #3 and then S/D the unit for standby. |  | 1 | 17:26 | Afternoon | Monday | 2019 | 5
11215 | 2019-05-27 20:40 | 2019-05-27 20:40 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 140 | 20:40 OKB feeder #2 load dropped 109 A (237 - 128 A) Cause: Not Checked Yet |  | 1 | 20:40 | Night | Monday | 2019 | 5
11216 | 2019-05-27 20:40 | 2019-05-31 07:57 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 140 | checked and found: 5443-RCL T/O, Counter : 120 - 121, Relay Flag : NONE Patrolled the line found : notihing Cause : Unidentified |  | 1 | 20:40 | Night | Monday | 2019 | 5
11217 | 2019-05-28 09:51 | 2019-05-28 09:51 | 13.8KV NORTH DURI FEEDER #6 | Fair | Planned Maintenance | 9 | 09:51 Manually open Recloser: 12-F7-02 D/S N Duri feeder #6 due to change out Tx on pole 12-F10-23. 11:10 Manually blocked and closed Recloser: 12-F7-02. and then released the block. Cause: Plan maintenance. |  | 1 | 9:51 | Morning | Tuesday | 2019 | 5
11218 | 2019-05-29 09:33 | 2019-05-29 09:33 | 13.8KV PETANI FEEDER #2 | Fair | Tree | 89 | Petani fdr#2 T/R 1x. Not checked yet. |  | 1 | 9:33 | Morning | Wednesday | 2019 | 5
11219 | 2019-05-29 09:33 | 2019-05-31 07:05 | 13.8KV PETANI FEEDER #2 | Fair | Tree | 89 | Checked and found: PTNSB-13.8OCB2 T/R, Counter : 312 - 314, Relay Flag : 51N Patrolled the line found : Pohon menyentuh line Cause : Tree |  | 1 | 9:33 | Morning | Wednesday | 2019 | 5
11220 | 2019-05-29 16:52 | 2019-05-29 16:52 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Recloser | 430 | 16:52 C. Duri fdr#1 Load dropped 70A (141-71A). 17:34 Checked and found Recloser: 41-AW-62 T/LO Counter: 314-318. Patrolled the line found @1,2,3 broken bushing Recloser: 41-AW-62. 19:54 Manually opened C Duri ACB feeder #1, for closing Bypass of Recloser: 41-AW-62 and opened HLC load side. 20:17 Manually block and closed C Duri ACB feeder #1 but failed. Opened by pass Recloser: 41-AW-62. 20:30 Manually block and closed C Duri ACB feeder #1 --> OK and then released the block. 21:15 Patrolled the line down stream Recloser: 41-AW-62, found @2 broken ball clevis of dead end insulator on pole 39-AU-03. (branch line towards well Kulin 60,87,13,30,88,and Kulin 14). 22:20 Isolated well above by cut jumpers on pole 39-AV-23. 22:53 Manually open C Duri ACB feeder #1. Closed bypass Recloser: 41-AW-62. 22:58 Manually block and closed C Duri ACB feeder #1 --> OK and then released the block. Cause: Broken bushing Recloser. |  | 1 | 16:52 | Afternoon | Wednesday | 2019 | 5
11221 | 2019-05-29 17:15 | 2019-05-29 17:15 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Unidentified | 86 | Bekasap fdr#6 T/R 1x. Not checked yet. |  | 1 | 17:15 | Afternoon | Wednesday | 2019 | 5
11222 | 2019-05-29 17:15 | 2019-02-06 07:15 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Unidentified | 86 | Checked & found Bekasap VCB fdr#6 T/R 1x Ctr:378-379 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 17:15 | Afternoon | Wednesday | 2019 | 5
11223 | 2019-05-29 20:43 | 2019-05-29 20:43 | 13.8KV DURI FIELD FEEDER #4 | Rain | Unidentified | 8 | 20:43 It was reported no power on pole 07-V5-21 D/S Duri Field feeder #4. 23:15 Checked and found Recloser: 07-V5-02 T/O Counter: 166-167. Patrolled the line found nothing. 23:55 Manually blocked and closed Recloser: 07-V5-02 --> Ok, and then released the block. Cause: Unidentified. |  | 1 | 20:43 | Night | Wednesday | 2019 | 5
11224 | 2019-05-30 06:54 | 2019-05-30 06:54 | 13.8KV MINAS FEEDER #6 | Fair | Lightning Arrester | 4 | Minas ACB Fdr#6 T/R 1x, Ctr: 190-191, R/F: 51N . Not patrolled yet. |  | 1 | 6:54 | Morning | Thursday | 2019 | 5
11225 | 2019-05-30 06:54 | 2019-07-06 08:26 | 13.8KV MINAS FEEDER #6 | Fair | Lightning Arrester | 4 | Checked & found Minas ACB Fdr#6 T/R 1x, Ctr: 190-191, R/F: 51N Patrolled the Line, found @2 broken L/AL O/p BS 7E-46 Cause : Lightning Arrester |  | 1 | 6:54 | Morning | Thursday | 2019 | 5
11226 | 2019-05-30 10:00 | 2019-05-30 10:00 | DURI POWER PLANT |  |  | - | 10:00 CDGT#3 S/U then online the unit 10:20. |  | 1 | 10:00 | Morning | Thursday | 2019 | 5
11227 | 2019-05-30 10:40 | 2019-05-30 10:40 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT#2, then S/D the unit for S/B. |  | 1 | 10:40 | Morning | Thursday | 2019 | 5
11228 | 2019-05-30 10:40 | 2019-05-30 10:40 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT#2, then S/D the unit for S/B. |  | 1 | 10:40 | Morning | Thursday | 2019 | 5
11229 | 2019-05-30 10:57 | 2019-05-30 10:57 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 66 | 10:57 Manually opened CDuri ACB fdr#1 & rocked aut. Repaired broken jumper O/P 39-AV-23. 11:42 Blocked & Closed C.Duri fdr#1, then release the block. Cause: Plan maintenance. |  | 1 | 10:57 | Morning | Thursday | 2019 | 5
11230 | 2019-05-31 05:58 | 2019-05-31 05:58 | 13.8KV 8C FEEDER #6 | Fair | Dead End Insulator | 37 | 8C VCB feeder #6 T/R 1x. 8C feeder #5 load dropped 110A (116-6A). 8C feeder #4 load dropped 238A (245-7A). Not checked yet. |  | 1 | 5:58 | Morning | Friday | 2019 | 5
11231 | 2019-05-31 05:58 | 2019-08-06 05:58 | 13.8KV 8C FEEDER #6 | Fair | Dead End Insulator | 37 | Checked & found 8C OCB fdr#6 T/R 2x Ctr:621-623 R/F:51@3. Patrolled the line & found @3 Broken Dead End Insulator o/p 8C-101. Cause : Dead End Insulator. |  | 1 | 5:58 | Morning | Friday | 2019 | 5
11232 | 2019-05-31 15:35 | 2019-05-31 15:35 | DARLING SUBSTATION | Rain and Lightning | Unidentified | 33 | 15:35 Darling 115 Kv GCB#2 T/O. Darling 115 Kv GCB#4 T/O. 16:30 Checked & found Darling 115 Kv GCB#2 T/O Ctr:184-185 R/F:NN. Darling 115 Kv GCB#4 T/O Ctr:91-92 R/F:NN. Darling Tx-1 Normal condition. Darling 13,8Kv fdr#3 T/R Ctr: 251 R/F:51N, 51@1@3. Darling 13,8Kv fdr#4 T/R Ctr: 143-144 R/F:51@1@3. 16:40 Opened Darling fdr#3, then Closed at 17:35. Opened Darling fdr#4, then Closed at 17:20. 17:00 Closed Darling 115 Kv GCB#2. 17:04 Closed Darling 115 Kv GCB#4. Patrolled D/S Darling fdr#3 but found nothing. Cause: Unidentified. |  | 1 | 15:35 | Afternoon | Friday | 2019 | 5
11233 | 2019-01-06 10:16 | 2019-01-06 10:16 | 13.8KV PUNGUT FEEDER #1 | Fair | Planned Maintenance | 77 | 10:16 Manually opened Pungut VCB fdr#1 & Opened bath isolation switches. Planed shutdown C/O Pin insulator o/p 45 Bp 22. 12:33 Closed bath isolation switches Pungut VCB fdr#1. 12:35 Manually closed Pungut VCB fdr#1. After Finished replace pin insulation at : O/P 44 BN 13 -----> @1,2,3. 45 BQ 16------> @1. 44 BN 20 -----> @3. 45 BP 22 -----> @3. |  | 1 | 10:16 | Morning | Sunday | 2019 | 1
11234 | 2019-01-06 15:48 | 2019-01-06 15:48 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 43 | 15:48 Rangau fdr#2 Load dropped 149A (204-55A). 18:10 Checked & found Recl. 23BD01 T/R 5x Ctr:382-387. Not patrolled yet. |  | 1 | 15:48 | Afternoon | Sunday | 2019 | 1
11235 | 2019-01-06 15:48 | 2019-07-06 15:48 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 43 | Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 15:48 | Afternoon | Sunday | 2019 | 1
11236 | 2019-02-06 16:16 | 2019-02-06 16:16 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Lightning | - | C.Duri ACB fdr#5 T/R 1x Ctr:260-261 R/F:50, 51@1@3. Not patrolled yet. |  | 1 | 16:16 | Afternoon | Wednesday | 2019 | 2
11237 | 2019-02-06 16:16 | 2019-07-06 06:16 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Lightning | - | Checked & found C Duri ACB fdr#5 T/R 1x, Cttr: 260-241, R/F: 51 @1 Patrolled the Line, found @1 Flash Over L.A O/P 03-8A-08 Cause: Lightning. |  | 1 | 16:16 | Afternoon | Wednesday | 2019 | 2
11238 | 2019-02-06 16:29 | 2019-02-06 16:29 | 115KV N. DURI SUBST - CD. SW. YARD LINE | Rain and Lightning | Lightning | - | 16:29 115 Kv line C.Duri-N.Duri GCB#53 T/R 1x 115 Kv line C.Duri-N.Duri GCB#53 T/R 1x 115 Kv line N.Duri-N.Duri GCB#53 T/O. 17:30 Checked & found N.Duri GCB#3 T/O Ctr:241-242 R/F:87L, 21@3-N. 18:10 Opened 115 Kv line C.Duri GCB#53, then closed at 18:20. Opened 115 Kv line C.Duri GCB#55, then closed at 18:20. 18:17 Closed 115Kv N.Duri GCB#3. Cause: Lightning. |  | 1 | 16:29 | Afternoon | Wednesday | 2019 | 2
11239 | 2019-02-06 16:42 | 2019-02-06 16:42 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Powerline - Conductor | 249 | 16:42 C.Duri ACB fdr#1 T/LO CTR::255 (Not Operated) R/F:51N. 17:10Manually opened C.Duri ACB fdr#1, due to Breaker T/R 4x. 17:15 It was reported Broken Conductor o/p 40AW17. 20:17 Patrolled the line & found @3 broken conductor. Isolate broken conductor by Open T-Tap at o/p 40-AV-16. Well down impact at Kulin #16,Kulin#17,Kulin#21,Kulin#32,Kulin#62,Kulin#72,Kulin#78,Kulin#79. 20:28 Manually block & Closed C.Duri ACB fdr#1 and then release the block. Cause: Conductor. |  | 1 | 16:42 | Afternoon | Wednesday | 2019 | 2
11240 | 2019-02-06 17:30 | 2019-02-06 17:30 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 39 | OKB fdr#2 T/R 1x. Not checked yet. |  | 1 | 17:30 | Afternoon | Wednesday | 2019 | 2
11241 | 2019-02-06 17:30 | 2019-04-06 08:30 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 39 | Checked & found OKB PCB fdr#1 T/R 1x Ctr:1369-1370 R/F:51N. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 17:30 | Afternoon | Wednesday | 2019 | 2
11242 | 2019-03-06 01:24 | 2019-03-06 01:24 | 13.8KV ROKAN FEEDER #2 | Heavy Rain | Lightning | 29 | Rokan VCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 1:24 | Night | Wednesday | 2019 | 3
11243 | 2019-03-06 01:24 | 2019-07-06 06:24 | 13.8KV ROKAN FEEDER #2 | Heavy Rain | Lightning | 29 | Checked & found Rokan fdr#2 T/R 1x Ctr: 1298-1299 R/F:51@3. Patrolled the line & found @3 Broken Pin Insulator o/p 12AV12. Cause : Lightning. |  | 1 | 1:24 | Night | Wednesday | 2019 | 3
11244 | 2019-03-06 04:51 | 2019-03-06 04:51 | 13.8KV BANGKO FEEDER #4 | Rain | Lightning | 35 | Bangko feeder #4 load dropped 71A (176-105A) Bangko feeder #3 load dropped 204A (235-31A) --> WIP Bangko feeder #2 load dropped 190A (245-55A) --> WIP Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 4:51 | Morning | Wednesday | 2019 | 3
11245 | 2019-03-06 08:25 | 2019-03-06 08:25 | CENTRAL DURI POWER PLANT |  |  | - | 08:25 Off Line CGT#4, then S/D the unit for S/B. 08:28 Closed Tie Breaker ACB#39. |  | 1 | 8:25 | Morning | Wednesday | 2019 | 3
11246 | 2019-03-06 09:56 | 2019-03-06 09:56 | 13.8KV RANGAU FEEDER #2 | Cloudy | Recloser | 14 | Rangau Fdr#2 Load dropped 150A (198-48A). Not checked yet. |  | 1 | 9:56 | Morning | Wednesday | 2019 | 3
11247 | 2019-03-06 09:56 | 2019-07-06 08:41 | 13.8KV RANGAU FEEDER #2 | Cloudy | Recloser | 14 | Checked & found RecL. 23-BD-01 T/R 1x, Ctr: 382-383, R/F: 51 Patrolled the Line, but found nothing Cause : Recloser |  | 1 | 9:56 | Morning | Wednesday | 2019 | 3
11248 | 2019-03-06 11:40 | 2019-03-06 11:40 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 191 | 11:40 Manually Opened C.Duri ACB fdr#1. Re-connected T-Tap o/p 40-AW-16. (After repaired broken conductor o/p 40-AW-17). 13:24 Blocked & closed C.Duri ACB fdr#1, then release the block. Cause: Plan Maintenance. |  | 1 | 11:40 | Morning | Wednesday | 2019 | 3
11249 | 2019-03-06 13:38 | 2019-03-06 13:38 | 13.8KV 6DN FEEDER #2 | Fair | Equipment Failure | 221 | 13:38 Manually Opened 6DN fdr#2. Requested GS#3 by shipping Pump Off at GS#3. |  | 1 | 13:38 | Afternoon | Wednesday | 2019 | 3
11250 | 2019-03-06 13:38 | 2019-04-06 05:26 | 13.8KV 6DN FEEDER #2 | Fair | Equipment Failure | 221 | Manually blocked and closed 6DN OCB feeder #2. and then released the block. Cause: Construction job. |  | 1 | 13:38 | Afternoon | Wednesday | 2019 | 3
11251 | 2019-03-06 22:30 | 2019-03-06 22:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 101 | KETIGUL VCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 22:30 | Night | Wednesday | 2019 | 3
11252 | 2019-03-06 22:30 | 2019-09-06 06:30 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 101 | Checked & found Ketigul VCB fdr#2 T/R 1x Ctr:330-331 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 22:30 | Night | Wednesday | 2019 | 3
11253 | 2019-04-06 03:19 | 2019-04-06 03:19 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | C.Duri ACB#11 (feeder#1) T/R 1x. r/f:51N ctr:257-258. Not checked yet. |  | 1 | 3:19 | Night | Saturday | 2019 | 4
11254 | 2019-04-06 03:19 | 2019-10-06 14:56 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | Checked and found CD ACB fdr #1T/R 1x, Ctr: 257-258, R/F:51N Patrolled the line, found @1 broken Pin Insulator O/p 40 AX 02 Cause : Pin Insulator |  | 1 | 3:19 | Night | Saturday | 2019 | 4
11255 | 2019-04-06 10:55 | 2019-04-06 10:55 | CENTRAL DURI POWER PLANT |  |  | - | 10:55 CGT#4 S/U, then On line the unit at 11:13. 11:07 Opened Tie breaker ACB#39. |  | 1 | 10:55 | Morning | Saturday | 2019 | 4
11256 | 2019-04-06 12:17 | 2019-04-06 12:17 | MINAS POWER PLANT |  |  | - | MGT#7 Off Line , then S/D the unit for S/B. |  | 1 | 12:17 | Afternoon | Saturday | 2019 | 4
11257 | 2019-04-06 15:54 | 2019-04-06 15:54 | 13.8KV BATANG FEEDER #1 | Rain | Normal Condition | 0 | 15:54 Batang VCB fdr#1 T/R 2x Batang Fdr #3 Load dropped 42A (50-8A). Not checked yet. |  | 1 | 15:54 | Afternoon | Saturday | 2019 | 4
11258 | 2019-04-06 15:54 | 2019-04-06 15:54 | 13.8KV BATANG FEEDER #1 | Rain | Normal Condition | 0 | 15:54 Batang VCB fdr#1 T/R 2x Batang Fdr #3 Load dropped 42A (50-8A). Not checked yet. |  | 1 | 15:54 | Afternoon | Saturday | 2019 | 4
11259 | 2019-04-06 15:54 | 13/06/2019 10:52 | 13.8KV BATANG FEEDER #1 | Rain | Normal Condition | 0 | Checked and found: BTGSB-13.8OCB1 None, Counter : 159 - 159, Relay Flag : NONE Patrolled the line found : No Finding Cause : Normal Condition |  | 1 | 15:54 | Afternoon | Saturday | 2019 | 4
11260 | 2019-05-06 08:11 | 2019-05-06 08:11 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 0 | 08:11 C Duri ACB fdr#8 T/R 2x, Ctr: 460-461, R/F: 51 @1 not checked yet |  | 1 | 8:11 | Morning | Monday | 2019 | 5
11261 | 2019-05-06 08:11 | 2019-10-06 14:59 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 0 | Checked and found: CD ACB Fdr #8 T/R 2x, Ctr: 460-462, R/F: 51N Patrolled the line, but found Nothing Cause : Unidentified |  | 1 | 8:11 | Morning | Monday | 2019 | 5
11262 | 2019-05-06 21:16 | 2019-05-06 21:16 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | - | 8C fdr#3 load dropped 167A (184-17A). Not checked yet. |  | 1 | 21:16 | Night | Monday | 2019 | 5
11263 | 2019-05-06 21:16 | 2019-07-06 21:11 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | - | Checked & found Recl. 8D-18A T/R 1x, Ctr: 185-186, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 21:16 | Night | Monday | 2019 | 5
11264 | 2019-05-06 23:35 | 2019-05-06 23:35 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Unidentified | - | Pungut OCB fdr#2 T/R 1x. Pungut fdr#1 load dropped 25A (72-47A). Not checked yet. |  | 1 | 23:35 | Night | Monday | 2019 | 5
11265 | 2019-05-06 23:35 | 2019-10-06 15:10 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Unidentified | - | Checked & found Pungut OCB fdr#2 T/R 1x, Ctr: 422-423, R/F: 51N Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 23:35 | Night | Monday | 2019 | 5
11266 | 2019-06-06 08:34 | 2019-06-06 08:34 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 0 | 08:34 D.Field ACB fdr#1 T/R 1x Not checked yet |  | 1 | 8:34 | Morning | Thursday | 2019 | 6
11267 | 2019-06-06 08:34 | 2019-09-06 06:34 | 13.8KV DURI FIELD FEEDER #1 | Cloudy | Unidentified | 0 | Checked & found D.Field ACB fdr#1 T/R 1x Ctr:702-703 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 8:34 | Morning | Thursday | 2019 | 6
11268 | 2019-06-06 13:41 | 2019-06-06 13:41 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Lightning | 0 | 13:41 S.Balam VCB fdr#1 T/R 1x S.Balam Fdr#4 Load dropped 134A(175-41A) |  | 1 | 13:41 | Afternoon | Thursday | 2019 | 6
11269 | 2019-06-06 13:41 | 2019-06-06 13:41 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 0 | 13:41 Nella Fdr#1 Load dropped 49A (192-143A) Not checked yet |  | 1 | 13:41 | Afternoon | Thursday | 2019 | 6
11270 | 2019-06-06 13:41 | 2019-06-06 13:41 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Lightning | 0 | 13:41 Bangko Fdr#1 Load dropped 22A(151-129A) Not checked yet |  | 1 | 13:41 | Afternoon | Thursday | 2019 | 6
11271 | 2019-06-06 13:41 | 2019-06-06 13:41 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Lightning | 0 | 13:41 Bangko Fdr#4 LOad dropped 77A(174-97A) Not checked yet |  | 1 | 13:41 | Afternoon | Thursday | 2019 | 6
11272 | 2019-06-06 15:05 | 2019-06-06 15:05 | 44KV PEMATANG MAIN - RANGAU LINE | Rain and Lightning | Lightning | 155 | 15:05 Pematang Main Substation 44KV OCB #2 T/LO Supplied to Rangau Substation, the RGU OCB #1, #2 still Close 15:10 Manually Opened Rangau OCB fdr#1 , #2 Checked & found PMT Main 44KV OCB#2, Ctr: 28880-28884, R/F: 51 @2 Patrolled the Line, but found nothing 17:05 Manually Block & Closed Rangau OCB fdr#1, then Released the block 17:07 Manually Block & Closed Rangau OCB fdr#2, then Released the block Cause: Lightning |  | 1 | 15:05 | Afternoon | Thursday | 2019 | 6
11273 | 2019-06-06 16:15 | 2019-06-06 16:15 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning |  | 0 | Sintong fdr#2 load drooped 109 A(196 - 87A ). Sintong GFPC T/R. Not checked yet. |  | 1 | 16:15 | Afternoon | Thursday | 2019 | 6
11274 | 2019-06-06 16:23 | 2019-06-06 16:23 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Unidentified | 51 | 16:23 Petani OCB fdr#2 T/R. Not cheched yet. |  | 1 | 16:23 | Afternoon | Thursday | 2019 | 6
11275 | 2019-06-06 16:23 | 2019-09-06 06:23 | 13.8KV PETANI FEEDER #2 | Rain and Lightning | Unidentified | 51 | Checked & found Petani VCB fdr#2 T/R 1x Ctr:315 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 16:23 | Afternoon | Thursday | 2019 | 6
11276 | 2019-06-06 17:23 | 2019-06-06 17:23 | 13.8KV PETAPAHAN FEEDER #6 | Rain and Lightning | Lightning | 315 | 17:23 Petapahan VCB fr#6 T/R 1x. Petapahan fdr#2 Load dropped 85A (85-0A), Pump Off. Petapahan fdr#7 Load dropped 33A (66-33A), Pump Off. Petapahan fdr#8 Load dropped 29A (83-54A). 17:29 Manually open Petapahan VCB feeder #3 Closed at 17:50. 17:30 Manually open Petapahan VCB feeder #4 Closed at 17:51. 17:30 Manually open Petapahan VCB feeder #6 Closed at 17:54. Due to maintain level tank. Request by Operator Petapahan GS. Not checked yet. |  | 1 | 17:23 | Afternoon | Thursday | 2019 | 6
11277 | 2019-06-06 17:23 | 2019-09-06 19:23 | 13.8KV PETAPAHAN FEEDER #6 | Rain and Lightning | Lightning | 315 | Checked & found Petapahan fdr#6 T/R 1x Ctr:372-374 R/F:51N, 51@2. Patrolled the line & found @2 Broken Pin Insulator o/p 31CZ10. Cause : Lightning. |  | 1 | 17:23 | Afternoon | Thursday | 2019 | 6
11278 | 2019-06-06 17:34 | 2019-06-06 17:34 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 0 | CKBS fdr#5 Load dropped 193A (239-46A). Not checked yet. |  | 1 | 17:34 | Afternoon | Thursday | 2019 | 6
11279 | 2019-06-06 17:34 | 2019-09-06 19:34 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked & found CKBS Recl. 36CU19 T/R 1x Ctr:325-326. Patrolled the line but found nothing. Cause : Lightning. |  | 1 | 17:34 | Afternoon | Thursday | 2019 | 6
11280 | 2019-07-06 01:46 | 2019-07-06 01:46 | 13.8KV LIBO FEEDER #1 | Cloudy | Unidentified | 70 | Libo fdr#1 T/R 1x. Libo fdr#2 load dropped 37A (67-30A). Not checked yet. |  | 1 | 1:46 | Night | Saturday | 2019 | 7
11281 | 2019-07-06 01:46 | 2019-10-06 07:11 | 13.8KV LIBO FEEDER #1 | Cloudy | Unidentified | 70 | Checked and found: LBOSB-13.8OCB1 T/R, Counter : 587 - 588, Relay Flag : 51N Patrolled the line found : 0 Cause : Unidentified |  | 1 | 1:46 | Night | Saturday | 2019 | 7
11282 | 2019-07-06 21:16 | 2019-07-06 21:16 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 53 | Ketigul fdr#2 T/R 1x. Ketigul fdr#1 Loaded dropped 83A (125-43A). Ketigul fdr#3 Loaded dropped 13A (33-20A). Not checked yet. |  | 1 | 21:16 | Night | Saturday | 2019 | 7
11283 | 2019-07-06 21:16 | 2019-10-06 10:34 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 53 | Checked and found KTGL VCB fdr #2 T/R 1x, Counter : 330 - 331, R/F : 51N Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 21:16 | Night | Saturday | 2019 | 7
11284 | 2019-08-06 11:34 | 2019-08-06 11:34 | 13.8KV SINTONG FEEDER #1 | Cloudy | Lightning | 44 | Sintong VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 11:34 | Morning | Tuesday | 2019 | 8
11285 | 2019-09-06 07:08 | 2019-09-06 07:08 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | 28 | Sintong VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 7:08 | Morning | Friday | 2019 | 9
11286 | 2019-09-06 20:25 | 2019-09-06 20:25 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 39 | 20:25 Nella fdr#2 T/R 1x. Nella GFPC T/R 1x. 20:37 Nella fdr#2 T/R 1x again. Not checked yet. |  | 1 | 20:25 | Night | Friday | 2019 | 9
11287 | 2019-09-06 20:25 | 2019-09-06 20:25 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Pin Insulator | 43 | Rangau fdr#2 Load dropped 155 (202-47A). Not checked yet. |  | 1 | 20:25 | Night | Friday | 2019 | 9
11288 | 2019-09-06 20:25 | 2019-12-06 14:02 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Pin Insulator | 43 | Checked and found: 5440-R.23BD01 T/R, Counter : 383 - 385, Relay Flag : NONE Patrolled the line found : Pin Insulator Pecah Bagian Bawah Cause : Pin Insulator |  | 1 | 20:25 | Night | Friday | 2019 | 9
11289 | 2019-09-06 20:25 | 2019-09-06 20:25 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Unidentified | 81 | Nella feeder #1 load dropped 100A (194-94A). Not checked yet. |  | 1 | 20:25 | Night | Friday | 2019 | 9
11290 | 2019-10-06 11:28 | 2019-10-06 11:28 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | ND VCB fdr #1 T/R 1x Cause: Not Checked Yet |  | 1 | 11:28 | Morning | Sunday | 2019 | 10
11291 | 2019-10-06 11:28 | 14/06/2019 16:12 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found ND fdr #1 T/R 1x, ctr: 309 - 310, R/F: 51N Patrolled the lines but found nothing Cause : Unidentified |  | 1 | 11:28 | Morning | Sunday | 2019 | 10
11292 | 2019-10-06 11:28 | 2019-10-06 11:28 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 27 | CD ACB fdr #16 T/R 1x, Ctr: 351 - 352, R/F: 51N Cause: Not Patrolled Yet |  | 1 | 11:28 | Morning | Sunday | 2019 | 10
11293 | 2019-10-06 11:28 | 14/06/2019 16:14 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 27 | Checked and found CD ACB fdr #16 T/R 1x, ctr: 351 - 352, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 11:28 | Morning | Sunday | 2019 | 10
11294 | 2019-11-06 10:40 | 2019-11-06 10:40 | MINAS POWER PLANT |  |  | - | 10:40 MGT-7 S/U and then online at 10:57 to back up MW/MVAR (CDGT-5 plan to shut down) |  | 1 | 10:40 | Morning | Wednesday | 2019 | 11
11295 | 2019-11-06 11:30 | 2019-11-06 11:30 | CENTRAL DURI POWER PLANT |  |  | - | 11:30 CDGT-5 Offline and then S/D at 11:35 to shut down TXP-5 and repair oil leak at TXP-5. |  | 1 | 11:30 | Morning | Wednesday | 2019 | 11
11296 | 2019-11-06 14:57 | 2019-11-06 14:57 | 13.8KV PINANG FEEDER #1 | Cloudy | Lightning Arrester | 7 | PINANG VCB fdr #1 T/R 1x Cause: Not Checked Yet |  | 1 | 14:57 | Afternoon | Wednesday | 2019 | 11
11297 | 2019-11-06 14:57 | 14/06/2019 08:56 | 13.8KV PINANG FEEDER #1 | Cloudy | Lightning Arrester | 7 | Checked and found : PNGSB-13.8OCB1 T/R, Counter : 449 - 450, Relay Flag : 51N Patrolled the line found : Broken LA Cause : Lightning Arrester |  | 1 | 14:57 | Afternoon | Wednesday | 2019 | 11
11298 | 2019-11-06 15:40 | 2019-11-06 15:40 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Unidentified | - | 15:40 BKO fdr #1 dropped 78 A (154 - 76 A) BKO fdr #4 dropped 31 A (173 - 142 A) Cause: Not Checked Yet |  | 1 | 15:40 | Afternoon | Wednesday | 2019 | 11
11299 | 2019-11-06 15:40 | 14/06/2019 08:51 | 13.8KV BANGKO FEEDER #1 | Rain and Lightning | Unidentified | - | Checked and found: 5440-R.23W12 T/R, Counter : 315 - 316, Relay Flag : 51N Patrolled the line found : None Cause : Unidentified |  | 1 | 15:40 | Afternoon | Wednesday | 2019 | 11
11300 | 2019-11-06 19:59 | 2019-11-06 19:59 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Tree | 10 | 4D OCB fdr#4 T/R 1x. Not checked yet. |  | 1 | 19:59 | Night | Wednesday | 2019 | 11
11301 | 2019-11-06 19:59 | 13/06/2019 15:53 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Tree | 10 | Checked and found: 4DSB-13.8OCB4 T/R, Counter : 282 - 283, Relay Flag : 51N Patrolled the line found : Pohon Tinggi Cause : Tree |  | 1 | 19:59 | Night | Wednesday | 2019 | 11
11302 | 2019-11-06 19:59 | 2019-11-06 19:59 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 30 | 5B fdr#2 load dropped 154A (162-8A). 5B fdr#1 load dropped 8A (105-97A). 5B fdr#3 load dropped 31A (98-67A). Not checked yet. |  | 1 | 19:59 | Night | Wednesday | 2019 | 11
11303 | 2019-11-06 19:59 | 16/06/2019 23:37 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 30 | Checked and found 5B OCB fdr #2 T/R 1x, Ctr: 422 - 423, R/F: 51P Patrolled the line and found broken dead end insulator @2 o/p 5C-19 Cause : Lightning |  | 1 | 19:59 | Night | Wednesday | 2019 | 11
11304 | 2019-11-06 19:59 | 2019-11-06 19:59 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 11 | 8D fdr#10 load dropped 75A (144-69A). Not checked yet. |  | 1 | 19:59 | Night | Wednesday | 2019 | 11
11305 | 2019-11-06 19:59 | 15/06/2019 12:01 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning | 11 | Checked and found RCL 6E-23A, ctr: 540 - 541, R/F: None Patrolled the line but found nothing Cause : Lightning |  | 1 | 19:59 | Night | Wednesday | 2019 | 11
11306 | 2019-11-06 20:04 | 2019-11-06 20:04 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Dead End Insulator | 20 | 6D VCB fdr#1 T/R 1x. 6D fdr#2 load dropped 19A (170-151A). 6D fdr#3 load dropped 73A (189-116A). |  | 1 | 20:04 | Night | Wednesday | 2019 | 11
11307 | 2019-11-06 20:04 | 13/06/2019 14:25 | 13.8KV 6D FEEDER #1 | Rain and Lightning | Dead End Insulator | 20 | Checked and found : 6DSB-13.8OCB1 T/R, Counter : 365 - 366, Relay Flag : 51 Patrolled the line found : Broken Dead end Cause : Dead End Insulator |  | 1 | 20:04 | Night | Wednesday | 2019 | 11
11308 | 2019-11-06 20:04 | 2019-11-06 20:04 | 13.8KV 6DN FEEDER #3 | Rain and Lightning | Unidentified | 0 | 6DN fdr#3 load dropped 65A (130-65A). 6DN fdr#4 load dropped 121A (204-83A). Not checked yet. |  | 1 | 20:04 | Night | Wednesday | 2019 | 11
11309 | 2019-11-06 20:04 | 17/06/2019 00:03 | 13.8KV 6DN FEEDER #3 | Rain and Lightning | Unidentified | 0 | Checked and found all protection device are Normal. Ctr OCB fdr #3: 1136 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 20:04 | Night | Wednesday | 2019 | 11
11310 | 2019-11-06 20:12 | 2019-11-06 20:12 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 1 | 8C fdr#3 load dropped 127A (184-57A). Not checked yet. |  | 1 | 20:12 | Night | Wednesday | 2019 | 11
11311 | 2019-11-06 20:12 | 15/06/2019 12:36 | 13.8KV 8C FEEDER #3 | Rain and Lightning | Lightning | 1 | Checked and found RCl 8D-18A T/R 1x, ctr: 186 - 187, R/F: None Patrolled the line but found nothing Cause : Lightning |  | 1 | 20:12 | Night | Wednesday | 2019 | 11
11312 | 2019-11-06 20:15 | 2019-11-06 20:15 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Broken Fuse Cut Out | 32 | 4B VCB fdr#1 T/R 1x. 4B fdr#2 load dropped 13A (22-9A). 4B fdr#3 load dropped 63A (65-2A). 4B fdr#4 load dropped 55A (123-68A). Not checked yet. |  | 1 | 20:15 | Night | Wednesday | 2019 | 11
11313 | 2019-11-06 20:15 | 13/06/2019 15:06 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Broken Fuse Cut Out | 32 | Checked and found: 4BSB-13.8OCB1 T/R, Counter : 374 - 375, Relay Flag : 51 Patrolled the line found : • Broken Fuse Holder Cause : Broken Fuse Cut Out |  | 1 | 20:15 | Night | Wednesday | 2019 | 11
11314 | 2019-11-06 20:17 | 2019-11-06 20:17 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 45 | 4D VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 20:17 | Night | Wednesday | 2019 | 11
11315 | 2019-11-06 20:17 | 14/06/2019 22:06 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Lightning | 45 | Checked and found OCB 4D fdr #2 T/R 1x, ctr: 284 - 285, R/F: 51N Patrolled the line but found nothing Cause : Lightning |  | 1 | 20:17 | Night | Wednesday | 2019 | 11
11316 | 2019-11-06 20:17 | 2019-11-06 20:17 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 10 | 4D VCB fdr#5 T/R 1x. 4D fdr#1 load dropped 65A (253-188A). 4D fdr#4 load dropped 32A (47-15A). 4D fdr#6 load dropped 98A (142-65A). Not checked yet. |  | 1 | 20:17 | Night | Wednesday | 2019 | 11
11317 | 2019-11-06 20:17 | 16/06/2019 11:52 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 10 | Checked and found 4D OCB fdr #5 T/R 1x, Ctr: 353 - 354, R/F: 51P Patrolled the line and found Broken Dead end @2 o/p 4D-13 Cause : Lightning |  | 1 | 20:17 | Night | Wednesday | 2019 | 11
11318 | 2019-11-06 20:20 | 2019-11-06 20:20 | 13.8KV 5B FEEDER #5 | Rain and Lightning | Lightning | 21 | 5B fdr#5 load dropped 42A (89-45A). Not checked yet. |  | 1 | 20:20 | Night | Wednesday | 2019 | 11
11319 | 2019-11-06 20:20 | 15/06/2019 12:14 | 13.8KV 5B FEEDER #5 | Rain and Lightning | Lightning | 21 | Checked and found RCL 4B-06 in Normal, ctr: 260 - 260, R/F: None Patrolled the line but found nothing Cause : Lightning |  | 1 | 20:20 | Night | Wednesday | 2019 | 11
11320 | 2019-06-13 06:56 | 2019-06-13 06:56 | 13.8KV DURI FIELD FEEDER #1 | Fair | Pin Insulator | 0 | DF VCB fdr #1 T/R 1x Cause: Not Checked Yet |  | 1 | 6:56 | Morning | Thursday | 2019 | 6
11321 | 2019-06-13 06:56 | 2019-06-20 07:56 | 13.8KV DURI FIELD FEEDER #1 | Fair | Pin Insulator | 0 | Checked & found Duri Field fdr#1 T/R 1x Ctr:704-705 R/F:51N. Patrolled the line & found @3 Broken Pin Insulator o/p 01-07-22. Cause : Pin Insulator. |  | 1 | 6:56 | Morning | Thursday | 2019 | 6
11322 | 2019-06-14 04:01 | 2019-06-14 04:01 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Pin Insulator | 0 | CD fdr #7 dropped 23 A (184 - 95 A) Cause: Not Checked Yet |  | 1 | 4:01 | Morning | Friday | 2019 | 6
11323 | 2019-06-14 04:01 | 2019-06-18 19:24 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Pin Insulator | 0 | Checked and found RCL 03-1-39 T/R 1x, Ctr: 1381-1382, R/F: 51P @3 Patrolled the line and found Broken Pin Insulator @3 o/p 03-1-13 Cause : Pin Insulator |  | 1 | 4:01 | Morning | Friday | 2019 | 6
11324 | 2019-06-14 10:30 | 2019-06-14 10:30 | 13.8KV 3D FEEDER #4 | Fair | Planned Maintenance | 9 | 10:30 Manually opened LBS: 2D-88 D/S 3D OCB feeder #4. Due to house keeping at pad transformer. 11:37 Manually closed LBS: 2D-88. Cause: Plan maintenance. |  | 1 | 10:30 | Morning | Friday | 2019 | 6
11325 | 2019-06-14 15:18 | 2019-06-14 15:18 | 13.8KV 8D FEEDER #5 | Cloudy | Lightning | 0 | 8D feeder #5 load dropped 55A (166-111A). Not checked yet. |  | 1 | 15:18 | Afternoon | Friday | 2019 | 6
11326 | 2019-06-14 15:18 | 2019-06-18 16:19 | 13.8KV 8D FEEDER #5 | Cloudy | Lightning | 0 | Checked and found all protection device on normal condition Patrolled the line but found nothing Cause : Lightning |  | 1 | 15:18 | Afternoon | Friday | 2019 | 6
11327 | 2019-06-14 17:30 | 2019-06-14 17:30 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Recloser - Control Recloser | 256 | 17:30 Ground fault alarm from Sinting fdr #1. Sintong fdr #1 load dropped 27A (109-82A). 22:08 it was reported No power at Kerang Field. 00:13 Checked and found Recloser 26-AE-22 T/LO ctr:258-261. Patrolled the line and found @1 broken LA at Kerang #06. Blocked and closed the Recl. but failed due to control Recl. problem. Will be continued tomorrow. |  | 1 | 17:30 | Afternoon | Friday | 2019 | 6
11328 | 2019-06-14 17:30 | 2019-06-15 10:15 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Recloser - Control Recloser | 256 | 10:15 Manually block and closed Recloser: 26-AE-22 but failed again. 10:23 Manually opened Sintong OCB feeder #1. For closing Bypass of Recloser: 26-AE-22. 10:28 Manually blocked and closed Sintong OCB feeder #1 --> OK. and then released the block. Recloser: 26-AE-22 status Bypass. Cause: Control Recloser. |  | 1 | 17:30 | Afternoon | Friday | 2019 | 6
11329 | 2019-06-14 21:59 | 2019-06-14 21:59 | 13.8KV CENTRAL DURI FEEDER #14 | Heavy Rain | Tree | 334 | 21:59 CD fdr #14 load dropped 85A (153 - 68A) 02:43 reported any fallen trees near pole 05-N3-01 06:15 Checked and found RCL 06-P8-02 T/LO, ctr: 282 - 286 Patrolled the lines and found fallen tree near pole 05-P1-01 and some branches still hanging on conductor at @2. waiting MTCE team to remove the trees branches. Cause: Tree. |  | 1 | 21:59 | Night | Friday | 2019 | 6
11330 | 2019-06-14 21:59 | 2019-06-15 09:12 | 13.8KV CENTRAL DURI FEEDER #14 | Heavy Rain | Tree | 334 | 09:12 Already cleared tree branches. 09:33 Manually blocked and closed Recloser: 06-P8-02. and then released the block. Cause: Tree. |  | 1 | 21:59 | Night | Friday | 2019 | 6
11331 | 2019-06-14 23:11 | 2019-06-14 23:11 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Tree | 0 | 44KV N Duri- Dumai Line ACB #1 T/R 1X. Not checked yet. |  | 1 | 23:11 | Night | Friday | 2019 | 6
11332 | 2019-06-14 23:11 | 2019-06-16 10:05 | 44KV NORTH DURI - DUMAI LINE | Rain and Lightning | Tree | 0 | Checked and found 44 kV GCB #1 ND T/R 1x, Ctr: 137 - 138, R/F: 51P @2 Patrolled the line and found fallen tree and burned the conductor @2 o/p DD-287 Cause : Tree |  | 1 | 23:11 | Night | Friday | 2019 | 6
11333 | 2019-06-15 02:59 | 2019-11-06 12:15 | 13.8KV BANGKO FEEDER #3 | Heavy Rain | Transformer Failure | 3538 | Energized 5Mva Tx-B at Bangko EOR after replaced Transformer. Cause: Transformer Failure. | 0 | 1 | 2:59 | Night | Saturday | 2019 | 6
11334 | 2019-06-15 02:59 | 2019-06-15 02:59 | 13.8KV BANGKO FEEDER #3 | Heavy Rain | Transformer Failure | 3538 | 02:59 Bangko fdr #3 load dropped 195 A (243 - 48 A) (Some pumps was off) 04:13 Manual Open Nella fdr #2 to maintain level tank (high) (pumps d/s TX-101B failed to started) 04:28 Recheck actual voltage at Bangko EOR and found output voltage from Tx #101B = 4800V. 07:25 Manual Open Nella feeder #1 to maintain level tank (high). 09:15 Perform TTR and Megger Tx #101B found Low Megger. 09:20 Closed 4.160KV Tie breaker at BKO EOR. 10:44 Manually blocked and closed Nella OCB feeder #2 , and then released the block. 15:27 Manually blocked and closed Nella OCB feeder #1 , and then released the block. Cause: Transformer Low Meg. 17:30 BKO fdr #3 load dropped 179A (219-40A). (All Pumps at BKO EOR tripped). 17:33 Manually Open Nella fdr #1 to maintenance Level Tank. 18:00 Checked and found @1 b/o fuse for 3.75MVA (TX 101-A) 19:10 Blocked BKO fdr #3. Replaced the b/o fuse above with same size, then closed the fuse. OK. Released locked BKO fdr #3. 20:38 Closed Nella fdr #1. Cause: Unidentified fuse. Production loss: Nella fdr #1 : 964 bbls / 76 wells (at 07:25- 15:27) Nella fdr #1 : 948 bbls / 76 wells (at 17:33- 20:38) Nella fdr #2 : 493 bbls / 19 wells (at 04:13- 10:44). ------------------------------------------------------------+ Grand Total : 2405 Bbls / 91 wells. | 0 | 1 | 2:59 | Night | Saturday | 2019 | 6
11335 | 2019-06-15 02:59 | 2019-06-18 07:50 | 13.8KV BANGKO FEEDER #3 | Heavy Rain | Transformer Failure | 3538 | 07:50 Manually open Nella OCB feeder #2. due to maintain tank level (Request : Bangko GS). 18:11 Manually closed Nella OCB feeder #2 , and then released the block. | 0 | 1 | 2:59 | Night | Saturday | 2019 | 6
11336 | 2019-06-15 09:58 | 2019-06-15 09:58 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Planned Maintenance | 57 | 09:58 Open Hot Line Clamp on pole: 02-08 04 D/S C.Duri Fdr#3 Replace @3 broken Fuse Cut Out. 10:27 Close HLC on pole:02-08-04 . Cause: Planned Maintenance. |  | 1 | 9:58 | Morning | Saturday | 2019 | 6
11337 | 2019-06-15 12:22 | 2019-06-15 12:22 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 22 | Ketigul VCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 12:22 | Afternoon | Saturday | 2019 | 6
11338 | 2019-06-15 12:22 | 2019-06-18 19:49 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 22 | Checked and found VCB KTGL fdr #1 T/R 1x, ctr: 215 - 216, R/F: 51P @1, @2 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 12:22 | Afternoon | Saturday | 2019 | 6
11339 | 2019-06-15 12:22 | 2019-06-15 12:22 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Tree | 0 | Ketigul feeder #2 load dropped 90A (247-157A). Ketigul feeder #3 load dropped 9A (34-25A). Not checked yet. |  | 1 | 12:22 | Afternoon | Saturday | 2019 | 6
11340 | 2019-06-15 12:22 | 2019-06-19 08:44 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Tree | 0 | Checked and found: RECLOSER 29 AK 24 T/R, Counter : 238 - 239, Relay Flag : 50N Patrolled the line found : Pohon tinggi Cause : Tree |  | 1 | 12:22 | Afternoon | Saturday | 2019 | 6
11341 | 2019-06-15 14:05 | 2019-06-15 14:05 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Unidentified | 5 | C.Duri ACB #28 (feeder#16) T/R 1x R/F: 51@1,2 Counter:352-353. Not patrolled yet. |  | 1 | 14:05 | Afternoon | Saturday | 2019 | 6
11342 | 2019-06-15 14:05 | 2019-06-18 19:30 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Unidentified | 5 | Checked and found ACB CD fdr #16 T/R 1x, Ctr: 352 - 353, R/F: 51P @1, @2, 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 14:05 | Afternoon | Saturday | 2019 | 6
11343 | 2019-06-15 16:02 | 2019-06-15 16:02 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 5 | 16:02 It was reported no power no power on pole 09-M3-02 D/S C Duri #1 17:12 Checked and found Recloser: 09-M3-01 T/O Counter: 78-79. 17:25 Manually blocked and closed Recloser: 09-M3-01 --> OK. and then released the block. Cause: Not patrolled yet. |  | 1 | 16:02 | Afternoon | Saturday | 2019 | 6
11344 | 2019-06-16 07:04 | 2019-06-16 07:04 | 13.8KV NELLA FEEDER #2 | Fair | Others | - | 07:04 Manually open Nella VCB feeder #2. Due to maintain tank level ( Request By Operator Bangko GS). 17:25 Manually blocked and closed Nella VCB feeder #2. Cause: Others (problem at the G pump at Bangko EOR). |  | 1 | 7:04 | Morning | Sunday | 2019 | 6
11345 | 2019-06-16 09:52 | 2019-06-16 09:52 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 728 | 09:52 Manually opened C. Duri ACB #11 (feeder#1). For replacing Recloser: 41-AW-62. Manually block and closed Recloser: 41-AW-62 and then released the block. Cause: Plan Maintenance. |  | 1 | 9:52 | Morning | Sunday | 2019 | 6
11346 | 2019-06-16 10:03 | 2019-06-16 10:03 | 13.8KV MINAS FEEDER #3 | Fair | Planned Maintenance | 62 | 10:03 Manually opened Minas ACB #2 (feeder #3). For replacing @1,@ broken dead end on pole 7D-73. 10:51 Manually block and closed Minas ACB #2 (feeder #3). Cause: Plan maintenance. |  | 1 | 10:03 | Morning | Sunday | 2019 | 6
11347 | 2019-06-16 17:44 | 2019-06-16 17:44 | 13.8KV DURI FIELD FEEDER #1 | Fair | Pin Insulator | - | Duri Field ACB #41 (feeder #1) T/R 1x. Not checked yet. |  | 1 | 17:44 | Afternoon | Sunday | 2019 | 6
11348 | 2019-06-17 08:14 | 2019-06-17 08:14 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | C Duri ACB #13 (feeder#3) T/R 1x R/F: 51N Counter: 212-213. Not patrolled yet. |  | 1 | 8:14 | Morning | Monday | 2019 | 6
11349 | 2019-06-17 08:14 | 2019-06-18 19:35 | 13.8KV CENTRAL DURI FEEDER #3 | Fair | Unidentified | 0 | Checked and found ACB CD fdr #3 T/R 1x, Ctr: 212 - 213, R/F: 51G Patrolled the line but found nothing Cause : Unidentified |  | 1 | 8:14 | Morning | Monday | 2019 | 6
11350 | 2019-06-17 15:33 | 2019-06-17 15:33 | MINAS POWER PLANT |  |  | - | 15:33 S/U MGT #3 and then Online the Unit at 15:54. |  | 1 | 15:33 | Afternoon | Monday | 2019 | 6
11351 | 2019-06-17 15:59 | 2019-06-17 15:59 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C Duri ACB#28 (feeder #16) T/R 1x R/F: 51 @1, @2 Counter: 353-354. Not patrolled yet. |  | 1 | 15:59 | Afternoon | Monday | 2019 | 6
11352 | 2019-06-17 15:59 | 2019-06-18 19:32 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked and found ACB CD fdr #16 T/R 1x, Ctr: 353 - 354, R/F: 51P @1, @2, 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 15:59 | Afternoon | Monday | 2019 | 6
11353 | 2019-06-17 17:25 | 2019-06-17 17:25 | MINAS POWER PLANT |  |  | - | 17:25 S/U MGT #8 and then Online the unit at 17:46. |  | 1 | 17:25 | Afternoon | Monday | 2019 | 6
11354 | 2019-06-17 17:25 | 2019-06-17 17:25 | CENTRAL DURI POWER PLANT |  |  | - | 17:25 S/U CDGT #5 and then Online the unit at 17:44. |  | 1 | 17:25 | Afternoon | Monday | 2019 | 6
11355 | 2019-06-17 21:40 | 2019-06-17 21:40 | MINAS POWER PLANT |  |  | - | MGT-10 S?U and then online the unit at 21:54 Purpose to NDC plan shut down for offline wash |  | 1 | 21:40 | Night | Monday | 2019 | 6
11356 | 2019-06-17 23:13 | 2019-06-17 23:13 | NORTH DURI POWER PLANT |  |  | - | NDC CT-3 Offline and then S/D the unit for Offline Wash Program. |  | 1 | 23:13 | Night | Monday | 2019 | 6
11357 | 2019-06-18 11:32 | 2019-06-18 11:32 | 13.8KV LIBO FEEDER #1 | Fair | Construction Job | - | 11:32 Manually open LBS: 34-CT-1B D/S Libo feeder #1. due to Closed Hot line clamp on pole 33-CT-11 , for reactive well SE Libo #46. 12:10 Manually closed LBS: 34-CT-1B. Cause: Construction job. |  | 1 | 11:32 | Morning | Tuesday | 2019 | 6
11358 | 2019-06-18 22:38 | 2019-06-18 22:38 | NORTH DURI POWER PLANT |  |  | - | 22:38 NDC CT-3 S/U and then online the unit at 00:16 June 19th, 2019 00:17 Closed ND 230 kV GCB #33 00:56 NDC CT-3 Offline and then S/D due to Gas Valcve Control Problem) |  | 1 | 22:38 | Night | Tuesday | 2019 | 6
11359 | 2019-06-19 01:27 | 2019-06-19 01:27 | NORTH DURI POWER PLANT |  |  | - | 01:27 NDC CT-3 S/U and then Online the unit at 02:55 (after offline wash program) 01:57 Closed 230 kV GCB #33 at ND |  | 1 | 1:27 | Night | Wednesday | 2019 | 6
11360 | 2019-06-19 12:38 | 2019-06-19 12:38 | CENTRAL DURI POWER PLANT |  |  | - | 12:38 CDGT#4 Open Generator breaker by alarm exiter trouble, and over excitation detect. 13:05 Closed Generator breaker ACB#46. |  | 1 | 12:38 | Afternoon | Wednesday | 2019 | 6
11361 | 2019-06-19 12:53 | 2019-06-19 12:53 | 13.8KV MINAS FEEDER #6 | Fair | Animal | 130 | 12:53 Minas ACB#18 (feeder#6) T/LO R/F: 51N Counter: 191-193. 13:20 Checked and found @2 broken jumper on pole 7E-36. 14:15 Manually blocked and closed Minas ACB#18 (feeder#6) , and then released the block. Cause: Animal (monkey). Production loss GS#1 = 8 Bbls / 3 wells. Production loss GS#3 = 139 Bbls / 26 wells. --------------------------------------------------- + Grand total = 147 Bbls / 29 wells. |  | 1 | 12:53 | Afternoon | Wednesday | 2019 | 6
11362 | 2019-06-20 06:47 | 2019-06-20 06:47 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | C. Duri fdr#1 Load dropped 54A (141-87A). Not checked yet. |  | 1 | 6:47 | Morning | Thursday | 2019 | 6
11363 | 2019-06-20 06:47 | 2019-06-23 17:47 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | Checked & found Recl. Sbb-07 T/R 1x Ctr:548-549 R/F;51@1. Patrolled the line & found @1 Broken Pin Insulator o/p 08-L5-36. Cause : Pin Insulator. |  | 1 | 6:47 | Morning | Thursday | 2019 | 6
11364 | 2019-06-20 06:53 | 2019-06-20 06:53 | NORTH DURI POWER PLANT |  |  | - | 06:53 NDC CT#1 S/U and On Line to system at 07:35 after perform Compressor Off Line wash |  | 1 | 6:53 | Morning | Thursday | 2019 | 6
11365 | 2019-06-20 07:13 | 2019-06-20 07:13 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | C.Duri ACB fdr#7 T/R 1x Ctr:528-529 R/F:51N. Not patrolled yet. |  | 1 | 7:13 | Morning | Thursday | 2019 | 6
11366 | 2019-06-20 07:13 | 2019-06-24 15:29 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Unidentified | 0 | Checked and found: CDRSG-13.8ACB33 T/R, Counter : 528 - 529, Relay Flag : 51N Patrolled the line found : No Finding Cause : Unidentified |  | 1 | 7:13 | Morning | Thursday | 2019 | 6
11367 | 2019-06-20 11:57 | 2019-06-20 11:57 | NORTH DURI POWER PLANT |  |  | - | 11:57 NDC CT#2 Off Line then S/D for Compressor Off line wash |  | 1 | 11:57 | Morning | Thursday | 2019 | 6
11368 | 2019-06-20 23:16 | 2019-06-20 23:16 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Unidentified | 64 | Sintong VCB feeder#1 T/R 1x. Sintong GFPC T/R 1x. Not Checked yet. |  | 1 | 23:16 | Night | Thursday | 2019 | 6
11369 | 2019-06-20 23:16 | 2019-06-24 08:11 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Unidentified | 64 | Checked and found: STGSB-13.8OCB1 T/R Ctr:406-407 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 23:16 | Night | Thursday | 2019 | 6
11370 | 2019-06-20 23:35 | 2019-06-20 23:35 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 52 | Ketigul VCB feeder #2 T/R 1x. Ketigul feeder #3 load dropped 8A (33-25A). Not checked yet. |  | 1 | 23:35 | Night | Thursday | 2019 | 6
11371 | 2019-06-20 23:35 | 2019-06-23 15:35 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 52 | Checked & found Ketigul fdr#2 T/R 1x Ctr:332-333 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 23:35 | Night | Thursday | 2019 | 6
11372 | 2019-06-21 00:29 | 2019-06-21 00:29 | 44KV PEMATANG MAIN - PETANI LINE | Rain and Lightning | Unidentified (Fuse) | 1471 | 00:29 Pematang Main 44 KV OCB #1 T/O (44 KV Line Pematang to Petani). No power at Petani Substation. 01:57 Checked and found 44 Kv Pematang Main OCB #1 T/O R/F:50N CTR:189-192. 02:18 Patrolled the line found @2 Broken Bus Fuse. Replace @2 broken Bus fuse. 02:20 Manually open Petani OCB fdr#1 Closed at: 06:02. Manually open Petani OCB fdr#2 Closed at: 06:03. 02:14 Manually open Rokan OCB fdr#2 Closed at: 06:16. To maintain Tank Level. 05:10 Manually Closed 44 KV Pematang Main OCB#1. Petani fdr#1 ctr:141-142. Petani fdr#2 ctr:316-317. Cause: Broken Bus Fuse. Production loss Petani feeder #1 = 501 Bbls / 19 wells. Production loss Petani feeder #2 = 891 Bbls / 35 wells. Production loss Rokani feeder #2 = 145 Bbls / 8 wells. ----------------------------------------------------------------- + Grand total = 1537 Bbls / 62 wells. | 12345 | 1 | 0:29 | Night | Friday | 2019 | 6
11373 | 2019-06-21 00:29 | 2019-06-21 00:29 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Follow Another Outage | 0 | Pematang feeder #1 load dropped 180A (210-30A). Pematang feeder #2 load dropped 74A (103-29A). Not checked yet. |  | 1 | 0:29 | Night | Friday | 2019 | 6
11374 | 2019-06-21 00:29 | 2019-06-26 08:05 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Follow Another Outage | 0 | Checked and found all on Normal Condition, RCL 35-BC-14 ctr : 138, R/F: None Patrolled the line and found nothing. Cause : Follow Another Outage |  | 1 | 0:29 | Night | Friday | 2019 | 6
11375 | 2019-06-21 00:29 | 2019-06-21 00:29 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Unidentified | 0 | Rangau feeder #2 load dropped 145A (180-35A). Rangau feeder #1 load dropped 33A (69-36A). Not checked yet. |  | 1 | 0:29 | Night | Friday | 2019 | 6
11376 | 2019-06-21 00:29 | 2019-06-23 15:29 | 13.8KV RANGAU FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked & found Recl. 23BD01 T/R 2x Ctr:388-390 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 0:29 | Night | Friday | 2019 | 6
11377 | 2019-06-21 00:38 | 2019-06-21 00:38 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Unidentified | 0 | C Duri ACB #21 (feeder #4) T/R 1x. Not patrolled yet. |  | 1 | 0:38 | Night | Friday | 2019 | 6
11378 | 2019-06-21 00:38 | 2019-06-23 16:38 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked & found C.Duri ACB fdr#4 T/R 1x Ctr"519-520 R/F:51@2. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 0:38 | Night | Friday | 2019 | 6
11379 | 2019-06-21 00:51 | 2019-06-21 00:51 | 13.8KV DARLING VCB FEEDER #7 | Rain and Lightning | Unidentified | 0 | Darling VCB feeder #7 T/R 1x. Not checked yet. |  | 1 | 0:51 | Night | Friday | 2019 | 6
11380 | 2019-06-21 00:51 | 2019-06-23 15:51 | 13.8KV DARLING VCB FEEDER #7 | Rain and Lightning | Unidentified | 0 | Checked & found Darling fdr#7 T/R 1x Ctr:174-175 R/F:51@1@2. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 0:51 | Night | Friday | 2019 | 6
11381 | 2019-06-21 01:01 | 2019-06-21 01:01 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Powerline - Jumper | 0 | C Duri ACB #22 (feeder #5) T/R 1x. Not patrolled yet. |  | 1 | 1:01 | Night | Friday | 2019 | 6
11382 | 2019-06-21 01:01 | 2019-06-23 17:01 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Powerline - Jumper | 0 | Checked & found C.Duri ACB fdr#5 T/R 1x Ctr:261-262 R/F:51@1. Patrolled the line & found @1 Broken Jumper o/p 03-7-03. Cause : Broken Jumper. |  | 1 | 1:01 | Night | Friday | 2019 | 6
11383 | 2019-06-21 01:12 | 2019-06-21 01:12 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Unidentified | 72 | Bekasap Main VCB feeder #6 T/R 1x. Not checked yet. |  | 1 | 1:12 | Night | Friday | 2019 | 6
11384 | 2019-06-21 01:12 | 2019-06-23 16:12 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Unidentified | 72 | Checked & found Bekasap fdr#6 T/R 1x Ctr:379-380 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 1:12 | Night | Friday | 2019 | 6
11385 | 2019-06-21 01:17 | 2019-06-21 01:17 | 13.8KV DURI FIELD FEEDER #1 | Rain and Lightning | Unidentified | 0 | Duri Field VCB #41 (feeder #1) T/R 1x. Not checked yet. |  | 1 | 1:17 | Night | Friday | 2019 | 6
11386 | 2019-06-21 01:17 | 2019-06-23 16:17 | 13.8KV DURI FIELD FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked & found Duri Field fdr#1 T/R 1x Ctr:705-706 R/F:51@1@2. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 1:17 | Night | Friday | 2019 | 6
11387 | 2019-06-21 01:34 | 2019-06-21 01:34 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 172 | Libo OCB feeder #1 T/R 1x. Libo feeder #2 load dropped 42A (69-27A). Not checked yet. |  | 1 | 1:34 | Night | Friday | 2019 | 6
11388 | 2019-06-21 01:34 | 2019-06-22 09:34 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Lightning | 172 | Checked & found Libo VCB fdr#1 T/R 1x, Ctr:588-591, R/F: 51N Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 1:34 | Night | Friday | 2019 | 6
11389 | 2019-06-21 03:56 | 2019-06-21 03:56 | 13.8KV MINAS FEEDER #3 | Rain and Lightning | Lightning | 83 | 03:56 Minas ACB#2 (fdr#3) T/LO R/F:51 @1,@2 ctr:158-160. 05:23 Patrolled the line, but not found. 05:26 Manually Block & Closed Minas ACB#2 (fdr#3). Cause: Suspected Lightning. |  | 1 | 3:56 | Night | Friday | 2019 | 6
11390 | 2019-06-21 04:59 | 2019-06-21 04:59 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Pin Insulator | 23 | 4B VCB feeder #1 T/R 1x. 4B feeder #2 load dropped 14A (22-8A). 4B feeder #3 load dropped 63A (65-2A). Not checked yet. |  | 1 | 4:59 | Morning | Friday | 2019 | 6
11391 | 2019-06-21 04:59 | 2019-06-27 07:04 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Pin Insulator | 23 | Checked and found 4B fdr #1 T/R 4x, Counter: 375 - 379, R/F: 51P @1 Patrolled the line and found broken pin insulator @1 on pole 4A-100 Cause : Pin Insulator |  | 1 | 4:59 | Morning | Friday | 2019 | 6
11392 | 2019-06-21 04:59 | 2019-06-21 04:59 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Lightning | 39 | 4B ocb feeder #6 T/R 1x. Not checked yet. |  | 1 | 4:59 | Morning | Friday | 2019 | 6
11393 | 2019-06-21 04:59 | 2019-06-26 08:17 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Lightning | 39 | Checked and found 4B OCB fdr #6 T/R 2x, Counter: 189 - 191, R/F 51P @1, @3 Patrolled the line and found Broken Dead end Insulator @1 & @3 o/p 4B-83 Cause : Lightning |  | 1 | 4:59 | Morning | Friday | 2019 | 6
11394 | 2019-06-21 05:00 | 2019-06-21 05:00 | 4 BRAVO SUBSTATION | Rain and Lightning | Under investigation | 0 | 05:00 4B 115 KV C/S#2 T/O r/f:51. 05:30 Manually Open 4B VCB fdr#1 Closed at: 07:24. 06:09 Manually Open 5B VCB fdr#1 Closed at: 07:24. 06:28 Manually Open MSU#1 fdr#2 Closed at: 07:25.(5B Fdr#4, #5) Due to maintain level. 06:37 Manually Open 4B VCB fdr#4 Closed at: 06:58. ctr:249. Manually Open 4B VCB fdr#5 Closed at: 06:58 ctr:172. Manually Open 4B VCB fdr#6 Closed at: 06:58. ctr:189-191. 06:52 Manually Closed 4B 115 KV C/S #2. Cause: Under Investigation. |  | 1 | 5:00 | Morning | Friday | 2019 | 6
11395 | 2019-06-21 06:06 | 2019-06-21 06:06 | 13.8KV SINTONG FEEDER #2 | Rain | Unidentified | 92 | Sintong VCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 6:06 | Morning | Friday | 2019 | 6
11396 | 2019-06-21 06:06 | 2019-06-25 08:53 | 13.8KV SINTONG FEEDER #2 | Rain | Unidentified | 92 | Checked and found: STGSB-13.8OCB2 T/R, Counter : 493 - 494, Relay Flag : 51N Patrolled the line found : None Cause : Unidentified. |  | 1 | 6:06 | Morning | Friday | 2019 | 6
11397 | 2019-06-21 09:00 | 2019-06-21 09:00 | 13.8KV NORTH DURI FEEDER #11 | Cloudy | Unidentified | 809 | 09:00 It was reported no Power Under Recl. 13.F10.23R (ND fdr#11) 12:40 Checked & found Recl. 13 F10 23R T/O (In Block position), Ctr: 106-107, R/F: 51 @1@2@3 Patrolled the Line, but found nothing 12:45 Block & Closed the Recloser, Ok, then released the Block Cause: Unidentified | 123456 | 1 | 9:00 | Morning | Friday | 2019 | 6
11398 | 2019-06-21 09:15 | 2019-06-21 09:15 | 13.8KV CENTRAL DURI FEEDER #7 | Cloudy | Lightning Arrester | 3 | 09:15 It was reported no power Under recl. 03-05-27 (CD fdr#7) 11:10 Checked & found Recl. 03-05-27 T/LO, Ctr: 1389-1394, R/F: None Patrolled the Line, found @3 broken LA o/p 03-05-27 11:44 Block & Closed the Recloser, then released the Block Cause: Lightning Arrester |  | 1 | 9:15 | Morning | Friday | 2019 | 6
11399 | 2019-06-21 12:00 | 2019-06-21 12:00 | NORTH DURI POWER PLANT |  |  | - | 12:00 NDC CT#2 S/U then On Line at 12:37 after perform Compressor Off line Wash |  | 1 | 12:00 | Afternoon | Friday | 2019 | 6
11400 | 2019-06-21 14:40 | 2019-06-21 14:40 | 13.8KV NORTH DURI FEEDER #2 | Cloudy | Recloser - Control Recloser | 905 | 14:40 It was reported no Power Under recl.13.G7.1-10 (ND fdr#2) 15:47 Checked & found Recl. 13.G7.1-10 T/O. Ctr: 25-26 Patrolled the Line, but found nothing 16:29 Block & Closed the Recloser, but T/O again Re patrolled the line again & continue troubleshot. 19:58 Manually blocked Recloser: SC-04. 20:08 Manually closed Recloser: 13-G71-10 and then unplug Recloser. due to recloser control problem. Released block Recloser: SC-04. Cause: Control Recloser. |  | 1 | 14:40 | Afternoon | Friday | 2019 | 6
11401 | 2019-06-21 15:20 | 2019-06-21 15:20 | MINAS POWER PLANT |  |  | - | 15:20 MGT #10 Off Line & S/D for S/B |  | 1 | 15:20 | Afternoon | Friday | 2019 | 6
11402 | 2019-06-21 15:32 | 2019-06-21 15:32 | MINAS POWER PLANT |  |  | - | 15:32 MGT #8 Off Line & S/D for S/B |  | 1 | 15:32 | Afternoon | Friday | 2019 | 6
11403 | 2019-06-21 16:05 | 2019-06-21 16:05 | MINAS POWER PLANT |  |  | - | 16:05 MGT #3 Off line & S/D for S/B |  | 1 | 16:05 | Afternoon | Friday | 2019 | 6
11404 | 2019-06-21 16:05 | 2019-06-21 16:05 | MINAS POWER PLANT |  |  | - | 16:05 MGT #3 Off line & S/D for S/B |  | 1 | 16:05 | Afternoon | Friday | 2019 | 6
11405 | 2019-06-22 09:48 | 2019-06-22 09:48 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 871 | 09:48 Manually Opened Recl. 41.AW 62 (C.Duri fdr#1) to Replace Recl 41 AW 62 Replace Bypass Recloser 41 AW 62 Cut some High Trees 16:44 Manually Block & Closed the Recl. 41 AW 62 after comfirm that the jobs have finished Cause: Planed Maintenance |  | 1 | 9:48 | Morning | Saturday | 2019 | 6
11406 | 2019-06-23 06:00 | 2019-06-23 06:00 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | D Field ACB #41 (feeder #1) T/R 1x. Not checked yet. |  | 1 | 6:00 | Morning | Sunday | 2019 | 6
11407 | 2019-06-23 06:00 | 2019-06-26 17:18 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Checked and found DF VCB fdr #1 T/R 1x, Counter: 706-707, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 6:00 | Morning | Sunday | 2019 | 6
11408 | 2019-06-23 16:42 | 2019-06-23 16:42 | 13.8KV BANGKO FEEDER #4 | Fair | Planned Maintenance | 91 | 16:42 Manually Opened Bangko VCB fdr#4. Repaired Jumper & Replaced FCO on T/P well Bangko#22. 17:42 Blocked & closed Bangko VCB fdr#4, then release the block. Cause: Plan Maintenance. |  | 1 | 16:42 | Afternoon | Sunday | 2019 | 6
11409 | 2019-06-24 06:59 | 2019-06-24 06:59 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 50 | 06:59 Ketigul VCB fdr#3 T/LO. Ketigul fdr#2 Load dropped 219A (261-42A). Ketigul fdr#1 Load dropped 100A (107-7A). 09:58 Checked & found Krtigul fdr#3 T/LO Ctr:212-216 R/F:51N, 51@2@3. Patrolled the line but found nothing. 10:25 Blocked & Closed Ketigul VCB fdr#3. then release the block. Cause: Unidentified. |  | 1 | 6:59 | Morning | Monday | 2019 | 6
11410 | 2019-06-24 16:35 | 2019-06-24 16:35 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 92 | 16:35 44Kv Line Pematang Main-Petani GCB#1 T/R 1x. 17:05 Checked & found 44Kv Line Pematang Main-Petani GCB#1 T/R 1x. Counter:192-193 R/F:51N, 51@1. 17:33 Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 16:35 | Afternoon | Monday | 2019 | 6
11411 | 2019-06-25 07:45 | 2019-06-25 07:45 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 184 | 07:45 Menggala fdr#1 Load dropped 145A (188-43A). Menggala GFPC T/O (Blocked Position). 10:00 Checked & found Recl. 19AN04 T/O (blocked position) Ctr:633-637. Patrolled the line but found nothing. 10:15 Blocked & Closed Recl. 19AN04, then release the block. 11:15 Closed Menggala GFPC. Cause: Unidentified. |  | 1 | 7:45 | Morning | Tuesday | 2019 | 6
11412 | 2019-06-26 00:04 | 2019-06-26 00:04 | 13.8KV BEKASAP FEEDER #3 | Heavy Rain | Normal Condition | 0 | Bekasap feeder #3 load dropped 23A (73-50A). Not checked yet. |  | 1 | 0:04 | Night | Wednesday | 2019 | 6
11413 | 2019-06-26 00:04 | 2019-06-28 05:17 | 13.8KV BEKASAP FEEDER #3 | Heavy Rain | Normal Condition | 0 | Checked and found BKS Main fdr #3 in Normal Condition. No need to patrolled the line, suspect one of BKS EOR pump was off. Cause : Normal Condition |  | 1 | 0:04 | Night | Wednesday | 2019 | 6
11414 | 2019-06-26 00:32 | 2019-06-26 00:32 | 13.8KV PEMATANG FEEDER #2 | Heavy Rain | Dead End Insulator | 71 | Pematang OCB feeder #2 T/R 1x. Pematang feeder #1 load dropped 180A (198-18A). Not checked yet. |  | 1 | 0:32 | Night | Wednesday | 2019 | 6
11415 | 2019-06-26 00:32 | 2019-06-29 13:58 | 13.8KV PEMATANG FEEDER #2 | Heavy Rain | Dead End Insulator | 71 | Checked and found PMT OCB fdr #2 T/R 1x, counter: 534-535, R/F: 51N Patrolled the line and found dead end flash over layer 1 on @3 Cause : Dead End Insulator |  | 1 | 0:32 | Night | Wednesday | 2019 | 6
11416 | 2019-06-26 00:32 | 2019-06-26 00:32 | 13.8KV RANGAU FEEDER #2 | Heavy Rain | Normal Condition | 28 | Rangau feeder #2 load dropped 24A (185-161A) Not checked yet. |  | 1 | 0:32 | Night | Wednesday | 2019 | 6
11417 | 2019-06-26 00:32 | 2019-06-29 13:58 | 13.8KV RANGAU FEEDER #2 | Heavy Rain | Normal Condition | 28 | Checked and found RCL 23-BD-01 in Normal Condition, ctr: 390-390 No patrolled finding, suspect some wells manual off. Cause : Normal Condition |  | 1 | 0:32 | Night | Wednesday | 2019 | 6
11418 | 2019-06-26 15:58 | 2019-06-26 15:58 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | 15:58 It was reported NO power From TX#3 CGS#4 (CD fdr#9) 16:33 Checked & found the fuse for TX#3 Visually were normal 17:30 Reported again, that no Power TX#3 CGS#4 18:15 Rechecked & found @2 B/O fuse of TX#3 CGS#4 Cause: Will trouble shoot The TX |  | 1 | 15:58 | Afternoon | Wednesday | 2019 | 6
11419 | 2019-06-26 15:58 | 2019-06-26 15:58 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Unidentified (Fuse) | 0 | Checked and found b/o fuse at TX-3 CGS-4 @2 Cause : Unidentified (Fuse) |  | 1 | 15:58 | Afternoon | Wednesday | 2019 | 6
11420 | 2019-06-26 16:03 | 2019-06-26 16:03 | 13.8KV BATANG GFPC | Fair | Unidentified | 0 | 16:03 Batang GFPC T/R 1x No feeders load dropped inducation Cause: Not Checked Yet |  | 1 | 16:03 | Afternoon | Wednesday | 2019 | 6
11421 | 2019-06-26 16:03 | 2019-01-07 16:40 | 13.8KV BATANG GFPC | Fair | Unidentified | 0 | Checked and found GFPC BTG operate 4x, ctr: 952 - 955, R/F: 51N No feeder trigger indication, no patrol finding. Cause : Unidentified |  | 1 | 16:03 | Afternoon | Wednesday | 2019 | 6
11422 | 2019-06-26 17:51 | 2019-06-26 17:51 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | 17:51 CD ACB fdr #16 T/R 1x, Counter: 354 - 355, R/F: 50N Cause: Not Patrolled Yet |  | 1 | 17:51 | Afternoon | Wednesday | 2019 | 6
11423 | 2019-06-26 17:51 | 2019-01-07 16:36 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked and found CD fdr #16 T/R 1x, ctr: 354 - 355, R/F: 51P Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 17:51 | Afternoon | Wednesday | 2019 | 6
11424 | 2019-06-27 10:14 | 2019-06-27 10:14 | 13.8KV BANGKO FEEDER #3 | Fair | Under investigation | 0 | 10:10 Decrease load at BKO EOR, d/s BKO fdr #2 and fdr #3 10:11 Open and rack out 4.16 kV Tie Breaker at BKO EOR 10:14 Manual Open LBS 22-Z-07 10:18 Close fuse holder for 5000 kVA TX 101B BKO EOR 10:19 Close LBS 22-Z-07 - Fuse for TX-101B b/o and then Open LBS 22-Z-07. - Checked and found CT secondary of TX 101B were b/o 10:30 Rack in and Close 4.16 kV Tie breaker at BKO EOR 10:31 Close again LBS 22-Z-07 and normalize the pumps. waiting MTCE to check the TX Cause: Under Investigation. |  | 1 | 10:14 | Morning | Thursday | 2019 | 6
11425 | 2019-06-27 18:04 | 2019-06-27 18:04 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Darling VCB fdr #7 T/R 1x Cause: Not Checked Yet |  | 1 | 18:04 | Afternoon | Thursday | 2019 | 6
11426 | 2019-06-27 18:04 | 2019-03-07 16:43 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | 0 | Checked and found Darling VCB fdr #7 T/R 2x Counter: 175-177 R/F: 50@1. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 18:04 | Afternoon | Thursday | 2019 | 6
11427 | 2019-06-28 07:39 | 2019-06-28 07:39 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | 07:39 CD ACB fdr #5 T/R 1x, Counter: 262-263, R/F: 51N, 51G Cause: Not Patrolled Yet |  | 1 | 7:39 | Morning | Friday | 2019 | 6
11428 | 2019-06-28 07:39 | 2019-01-07 16:38 | 13.8KV CENTRAL DURI FEEDER #5 | Fair | Unidentified | 0 | Checked and found CD fdr #5 T/R 1x, ctr: 262 - 263, R/F: 51N Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 7:39 | Morning | Friday | 2019 | 6
11429 | 2019-06-28 09:52 | 2019-06-28 09:52 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Planned Maintenance | 1 | 09:52 Manually open recl 05-P3-02 D/S C.Duri fdr#14. Replaced 112.5KVA TX o/p: 05-P3-06. 01:51 Closed Recl. 05-P3-02. Plan Maintenance. |  | 1 | 9:52 | Morning | Friday | 2019 | 6
11430 | 2019-06-28 11:23 | 2019-06-28 11:23 | 13.8KV BATANG FEEDER #2 | Fair |  | 68 | 11:23 Manual Open 13.8 kV VCB fdr #2 Batang SS Purpose: HCT Team worked d/s power line to remove pig launcher at Batang PSO. 17:01 Manual Close VCB Batang fdr #2, OK Cause: Construction Job. |  | 1 | 11:23 | Morning | Friday | 2019 | 6
11431 | 2019-06-28 17:22 | 2019-06-28 17:22 | 44KV NORTH DURI - DUMAI LINE | Fair | Unidentified | 0 | 17:22:35 44 kV GCB #1 ND Tripped (reclose at 17:22:46) 17:22:36 13.8 kV VCB #14 ND T/LO (for TX-14 ND) 18:12 Checked and found: - 44 kV GCB #1 T/R 1x, R/F: 51N, Ctr: 138 - 140 - 13.8 kV VCB T/LO (TX-14 ND-DMI), R/F: 51N W2, ctr:157-158 TX-14 ND condition Normal, LT: 45 deg C 18:20 Manually Opened 44 kV GCB #1. Closed 13.8KV ND VCB #14. OK. 19:15 Patrolled the line 44 kV to Dumai, but found nothing 19:29 Manually Block & Closed 44 kV GCB #1, then released the block Cause: Unidentified. |  | 1 | 17:22 | Afternoon | Friday | 2019 | 6
11432 | 2019-06-28 21:48 | 2019-06-28 21:48 | 13.8KV PEMATANG FEEDER #2 | Fair | Construction Job | 0 | 21:48 Manuall Opened Pematang VCB fdr#2 as GS Operator Requested to Maintain Tank level 22:28 Manually block & Closed the VCB, then released the block Cause: Planning construction |  | 1 | 21:48 | Night | Friday | 2019 | 6
11433 | 2019-06-29 12:52 | 2019-06-29 12:52 | 13.8KV SURAM FEEDER #2 | Fair | Unidentified | 0 | 10:19 Suram fdr #2 load dropped 18A (46-28A) Reported by PHE (Ramlan) on 12:52 that any dipped at Suram PHE area. Cause: Not Checked Yet |  | 1 | 12:52 | Afternoon | Saturday | 2019 | 6
11434 | 2019-06-29 12:52 | 2019-01-07 08:24 | 13.8KV SURAM FEEDER #2 | Fair | Unidentified | 0 | Checked and found all protection devices are normal. Nothing patrol found. Cause : Unidentified |  | 1 | 12:52 | Afternoon | Saturday | 2019 | 6
11435 | 2019-06-30 10:25 | 2019-06-30 10:25 | 13.8KV 6D FEEDER #4 | Fair | Planned Maintenance | 0 | 10:25 Manually Open 6D fdr #4. Replaced broken Dead End and Pin Insulator o/p: 6D-504. 12:21 Closed 6D fdr #4. Cause: Planned Maintenance. |  | 1 | 10:25 | Morning | Sunday | 2019 | 6
11436 | 2019-06-30 10:35 | 2019-06-30 10:35 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 80 | 10:35 Manually Open 6D fdr #1. Replaced @1 broken Dead End and @2 Pin Insulator o/p: 5D-115. Replaced @3 broken Pin Insulator o/p: 5D-114. 12:42 Closed 6D fdr #1. Plan Maintenance. |  | 1 | 10:35 | Morning | Sunday | 2019 | 6
11437 | 2019-06-30 10:37 | 2019-06-30 10:37 | 13.8KV 6D FEEDER #5 | Fair | Planned Maintenance | 40 | 10:37 Manually Open 6D fdr #5. Replaced broken Dead End and Pin Insulator o/p: 6D-504. 12:21 Closed 6D fdr #5. Plan Maintenance. |  | 1 | 10:37 | Morning | Sunday | 2019 | 6
11438 | 2019-06-30 16:39 | 2019-06-30 16:39 | DARLING SUBSTATION | Fair | Animal | 41 | 16:39 Darling 115KV GCB #2 T/O. Darling 115KV GCB #4 T/O. (No power to Darling Substation). 17:20 Checked and found: Darling 115KV GCB #2 T/O, ctr:185-185 R/F: none. Darling 115KV GCB #4 T/O, ctr:92-93 R/F: none. Darling TX-1, R/F:51G-W2 W/T:56F O/T:50F. GFPC TX-1 On By Pass (Block). Also found Darling fdr #7 T/R 2X ctr:175-177 RF:51 @1. (No Indication tripped at DSC). And also found Dead Monkey on load side of VR-1. 17:59 Manually Open Darling fdr #4. Manually Open Darling fdr #3 (on local). 18:09 Closed Darling 115KV GCB #2. 18:11 Closed Darling 115KV GCB #4. 18:20 Blocked and Closed Darling fdr #3 then released the block. 18:21 Blocked and Closed Darling fdr #4 then released the block. Cause: Animal (monkey). |  | 1 | 16:39 | Afternoon | Sunday | 2019 | 6
11439 | 2019-01-07 10:23 | 2019-01-07 10:23 | BEKASAP MAIN SUBSTATION | Fair | Planned Maintenance | 623 | 10:23 Manually Open 13.8KV VCB Bekasap fdr #2. 10:26 Manually Open 13.8KV VCB Bekasap fdr #1. 10:30 Manually Open 44KV OCB #1. 12:10 Closed 13.8KV OCB MSU fdr #1 (transfer load BKS fdr #1). 12:10 Closed 13.8KV OCB MSU fdr #2 (transfer load BKS fdr #2). (transfer load BKS fdr #1 & #2 to MSU fdr #1 & #2). Plan Maintenance. | 123 | 1 | 10:23 | Morning | Monday | 2019 | 1
11440 | 2019-01-07 17:55 | 2019-01-07 17:55 | CENTRAL DURI POWER PLANT |  |  | - | 17:55 CDGT #2 S/U and then Online at 18:14 as preparation before S/D CDGT #4 for c/o automazing compressor. |  | 1 | 17:55 | Afternoon | Monday | 2019 | 1
11441 | 2019-01-07 20:52 | 2019-01-07 20:52 | CENTRAL DURI POWER PLANT |  |  | - | Off Line CGT#4, then S/D the unit for S/B. (Waiting for replaced Atomizing Air Compressor) |  | 1 | 20:52 | Night | Monday | 2019 | 1
11442 | 2019-01-07 23:22 | 2019-01-07 23:22 | 13.8KV NELLA FEEDER #2 | Fair | Emergency | - | 23:22 Manually Open Nella VCB fdr#2 Bangko GS Requested, due to Pipe Leak at Bukit timah KM 51350 On July 02, 2019 07:53 Closed Nella VCB fdr#2. Cause: Emergency. |  | 1 | 23:22 | Night | Monday | 2019 | 1
11443 | 2019-01-07 23:59 | 2019-01-07 23:59 | 13.8KV S. BALAM FEEDER #4 | Fair | Emergency | 189 | 24:00 Manually Opened S.Balam VCB fdr#4 Balam GS requested, due to any Well Bubling (Blow out) On July 02, 2019 10:15 Closed S.Balam VCB fdr#4. Cause: Emergency. |  | 1 | 23:59 | Night | Monday | 2019 | 1
11444 | 2019-02-07 09:54 | 2019-02-07 09:54 | 13.8KV SO BEKASAP FEEDER #1 | Fair | Planned Maintenance | 255 | 09:54 Manuall Open S. Bekasap fdr #1. 12:56 Closed LBS: LBS: 37-BF -05 but failed due to @2 Blade not fully closed and spark. 13:30 Open Recl:1 TL-06 (d/s Beksap fdr #3). 13:32 Closed LBS: 37-BF -05. 13:48 Closed Recl:1 TL-06. (load S. Bekasap fdr #1 transfer to Bekasap fdr #3) Cause: Plan Maintenance. |  | 1 | 9:54 | Morning | Thursday | 2019 | 2
11445 | 2019-03-07 01:24 | 2019-03-07 01:24 | 13.8KV 8D FEEDER #5 | Fair | Lightning | 0 | 01:24 8D VCB fdr#5 T/R 1x Not checked yet |  | 1 | 1:24 | Night | Thursday | 2019 | 3
11446 | 2019-03-07 01:24 | 2019-09-07 08:11 | 13.8KV 8D FEEDER #5 | Fair | Lightning | 0 | Checked and found 8D VCB feeder #5 T/R 1x R/F: 51N Counter: 565-566. Patrolled the line nothing found. Cause: Lighting |  | 1 | 1:24 | Night | Thursday | 2019 | 3
11447 | 2019-03-07 10:33 | 2019-03-07 10:33 | 13.8KV 6D FEEDER #6 | Fair | Lightning | 0 | 6D OCB feeder #6 T/R 1x. Not checked yet. |  | 1 | 10:33 | Morning | Thursday | 2019 | 3
11448 | 2019-03-07 10:33 | 2019-09-07 08:23 | 13.8KV 6D FEEDER #6 | Fair | Lightning | 0 | Checked and found 6D OCB feeder #6 T/R 1x Counter: 609-610 R/F: 51N. Patrolled the line nothing found. Cause: Lighting |  | 1 | 10:33 | Morning | Thursday | 2019 | 3
11449 | 2019-03-07 10:33 | 2019-03-07 10:33 | 13.8KV 6D FEEDER #5 | Fair | Lightning | 11 | 6D OCB feeder #5 T/R 1x. Not checked yet. |  | 1 | 10:33 | Morning | Thursday | 2019 | 3
11450 | 2019-03-07 10:33 | 2019-09-07 08:05 | 13.8KV 6D FEEDER #5 | Fair | Lightning | 11 | Checked and found 6D OCB feeder #5 T/R 1x R/F: 51N Counter: 798-799. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 10:33 | Morning | Thursday | 2019 | 3
11451 | 2019-03-07 10:34 | 2019-03-07 10:34 | 13.8KV 6D FEEDER #4 | Fair | Unidentified | 20 | 6D feeder #4 load dropped 166A (188-22A). Not checked yet. |  | 1 | 10:34 | Morning | Thursday | 2019 | 3
11452 | 2019-03-07 10:34 | 2019-09-07 08:16 | 13.8KV 6D FEEDER #4 | Fair | Unidentified | 20 | Checked and found 6D feeder #4 load dropped 166A (188-22A). Counter: 569-569 R/F: NONE. Cause: Unidentified. |  | 1 | 10:34 | Morning | Thursday | 2019 | 3
11453 | 2019-03-07 15:00 | 2019-03-07 15:00 | MINAS POWER PLANT |  |  | - | 15:00 S/U MGT #10 and then Online the Unit at 15:26. |  | 1 | 15:00 | Afternoon | Thursday | 2019 | 3
11454 | 2019-03-07 15:50 | 2019-03-07 15:50 | MINAS POWER PLANT |  |  | - | MGT#10 Off Line , then S/D the unit for S/B. |  | 1 | 15:50 | Afternoon | Thursday | 2019 | 3
11455 | 2019-04-07 07:12 | 2019-04-07 07:12 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 0 | C Duri ACB #32 (feeder #8) T/R 1x Counter: 462-463 R/F: 51@1. Not patrolled yet. |  | 1 | 7:12 | Morning | Sunday | 2019 | 4
11456 | 2019-04-07 07:12 | 2019-06-07 15:41 | 13.8KV CENTRAL DURI FEEDER #8 | Fair | Unidentified | 0 | Checked and found ACB CD fdr #8 T/R 1x, counter: 462 - 463, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 7:12 | Morning | Sunday | 2019 | 4
11457 | 2019-04-07 08:10 | 2019-04-07 08:10 | CENTRAL DURI POWER PLANT |  |  | - | 08:10 S/U CDGT #4 , and then Online the unit at 08:27. |  | 1 | 8:10 | Morning | Sunday | 2019 | 4
11458 | 2019-04-07 09:28 | 2019-04-07 09:28 | CENTRAL DURI POWER PLANT |  |  | - | 09:28 Off line CDGT #1 , and then S/D the unit at 09:30. Status Standby. |  | 1 | 9:28 | Morning | Sunday | 2019 | 4
11459 | 2019-04-07 09:28 | 2019-04-07 09:28 | CENTRAL DURI POWER PLANT |  |  | - | 09:28 Off line CDGT #1 , and then S/D the unit at 09:30. Status Standby. |  | 1 | 9:28 | Morning | Sunday | 2019 | 4
11460 | 2019-04-07 14:00 | 2019-04-07 14:00 | 230KV NORTH DURI SWITCH YARD | Fair | Tree | 0 | N Duri 230 Kv GCB #23 T/R 1x. N Duri 230 Kv GCB #25 T/R 1x. Not checked yet. |  | 1 | 14:00 | Afternoon | Sunday | 2019 | 4
11461 | 2019-04-07 14:00 | 2019-10-07 08:00 | 230KV NORTH DURI SWITCH YARD | Fair | Tree | 0 | Checked & found 230Kv GCB#23 T/R 1x Ctr:246-247 R/F:50N. 230Kv GCB#25 Not operated Ctr:205. Patrolled the line & found Danger trees near pole TW-06. Cause : Tree |  | 1 | 14:00 | Afternoon | Sunday | 2019 | 4
11462 | 2019-04-07 14:25 | 2019-04-07 14:25 | 13.8KV LIBO FEEDER #1 | Fair | Construction Job | 0 | 14:25 Manual Open LBS 34-CC-01. Open and Closed HLC o/p 34-CC-6A for Reactive well Se. Libo #44. 14:48 Manual Closed LBS 34-CC-01. Cause: Construction JOB. |  | 1 | 14:25 | Afternoon | Sunday | 2019 | 4
11463 | 2019-05-07 16:41 | 2019-05-07 16:41 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 5 | Ketigul VCB fdr#3 T/R 1x. Ketigul feeder#2 load dropped 12A (256-244A). Not checked yet. |  | 1 | 16:41 | Afternoon | Tuesday | 2019 | 5
11464 | 2019-05-07 16:41 | 2019-10-07 08:41 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 5 | Checked & found Ketigul VCB fdr#3 T/R 1x Ctr:216-217 R/F:51N. Patrolled the line not found nothing. Cause : Unidentified. |  | 1 | 16:41 | Afternoon | Tuesday | 2019 | 5
11465 | 2019-05-07 17:04 | 2019-05-07 17:04 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | Sintong feeder#2 load dropped 142A (200-53A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 17:04 | Afternoon | Tuesday | 2019 | 5
11466 | 2019-05-07 17:04 | 2019-10-07 07:04 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | Checked & found Recl. 28AF02 T/R 1x Ctr:1539-1540 R/F:51N. Patrolled the line & found @1 Broken Dead End Insulator o/p 29Z09. @1 Broken Dead End Insulator o/p 24Y04. @2 Broken Dead End Insulator o/p 29AE08. @2 Broken Dead End Insulator o/p 29AB01. Danger Tree Near pole 29AC07. Cause : Lightning. |  | 1 | 17:04 | Afternoon | Tuesday | 2019 | 5
11467 | 2019-05-07 17:30 | 2019-05-07 17:30 | 13.8KV BANGKO FEEDER #1 | Cloudy | Lightning | 0 | Bangko fdr#1 load dropped 154A (166-12A). Bangko fdr#2 load dropped 232A (254-22A), Pump Off. Bangko fdr#3 load dropped 172A (202-29A), Pump Off. Not checked yet. |  | 1 | 17:30 | Afternoon | Tuesday | 2019 | 5
11468 | 2019-05-07 17:30 | 2019-07-07 08:10 | 13.8KV BANGKO FEEDER #1 | Cloudy | Lightning | 0 | Checked and found RCL 23-X-08 T/R 2x, counter: 411-413, R/F: 51N Patrolled the line and found broken LA @1 at BKO-89 Cause : Lightning |  | 1 | 17:30 | Afternoon | Tuesday | 2019 | 5
11469 | 2019-05-07 18:05 | 2019-05-07 18:05 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Unidentified | 0 | 18:05 So.Balam feeder#4 load dropped 44A (179-135A). So.Balam feeder#1 load dropped 13A (146-133A). So.Balam feeder#3 load dropped 103A (103-0A), Pump Off. So.Balam feeder#2 load dropped 67A (100-33A), Pump Off. 23:31 Reported no power at well BLM #375, #175, etc Saturday, July 6th, 2019 01:30 Checked and found RCL 16-AB-03 T/O (on block for Rig HPS #09) 01:40 Closed RCL 16-AB-03, OK Cause: Not Patrolled yet. |  | 1 | 18:05 | Afternoon | Tuesday | 2019 | 5
11470 | 2019-05-07 18:05 | 2019-06-07 08:29 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Unidentified | 0 | Patrolled the line but found nothing Cause: Unidentified |  | 1 | 18:05 | Afternoon | Tuesday | 2019 | 5
11471 | 2019-05-07 19:02 | 2019-05-07 19:02 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Dead End Insulator | 68 | 19:02 KETIGUL fdr #2 T/R 1x Cause: Not Checked Yet |  | 1 | 19:02 | Night | Tuesday | 2019 | 5
11472 | 2019-05-07 19:02 | 2019-11-07 13:45 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Dead End Insulator | 68 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 333 - 336, Relay Flag : 51 Patrolled the line found : Broken Deadend Cause : Dead End Insulator |  | 1 | 19:02 | Night | Tuesday | 2019 | 5
11473 | 2019-05-07 19:02 | 2019-11-07 07:32 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Unidentified | 0 | Checked ALL Recl. normal operation (Not Operated). Patrolled the line but found nothing. Cause : Unidentified |  | 1 | 19:02 | Night | Tuesday | 2019 | 5
11474 | 2019-05-07 19:02 | 2019-05-07 19:02 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Unidentified | 100 | 19:02 Menggala fdr #1 dropped 52 A (171 - 119 A) Cause: Not Checked Yet |  | 1 | 19:02 | Night | Tuesday | 2019 | 5
11475 | 2019-05-07 19:02 | 2019-11-07 19:02 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Unidentified | 100 | Checked All Recl. Normal Operation (Not Operated). Patrolled the line but found nothing. Cause: Unidentified. |  | 1 | 19:02 | Night | Tuesday | 2019 | 5
11476 | 2019-06-07 07:56 | 2019-06-07 07:56 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | Sintong feeder #2 load dropped 113A (197-84A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 7:56 | Morning | Friday | 2019 | 6
11477 | 2019-06-07 07:56 | 2019-10-07 07:56 | 13.8KV SINTONG FEEDER #2 | Cloudy | Lightning | 0 | Checked & found Recl. 28AF02 T/R 1x Ctr:1539-1540 R/F:51N. Patrolled the line & found @1 Broken Dead End Insulator o/p 29Z09. @1 Broken Dead End Insulator o/p 24Y04. @2 Broken Dead End Insulator o/p 29AE08. @2 Broken Dead End Insulator o/p 29AB01. Danger Tree Near pole 29AC07. Cause : Lightning. |  | 1 | 7:56 | Morning | Friday | 2019 | 6
11478 | 2019-06-07 09:30 | 2019-06-07 09:30 | 13.8KV 4B FEEDER #5 | Fair | Planned Maintenance | 0 | 09:30 Manually open LBS: 4B-147A D/S 4B feeder #5. Due to replace broken HLC on pole 4B-148. shut off wells 4B-53,63,72. 11:03 Manually closed LBS: 4B-147A. Cause: Plan maintenance. |  | 1 | 9:30 | Morning | Friday | 2019 | 6
11479 | 2019-06-07 10:50 | 2019-06-07 10:50 | 13.8KV BANGKO FEEDER #1 | Fair | Construction Job | 731 | 10:50 Manually Open Bangko OCB Feeder #1. 11:19 Manually Open LBS 22-Z-07 due test CT,PT secondary cable at Bangko EOR. 13:47 Manually closed LBS 22-Z-07. 14:00 Manually closed Bangko OCB Feeder #1. Cause: Contruction Job. |  | 1 | 10:50 | Morning | Friday | 2019 | 6
11480 | 2019-06-07 13:18 | 2019-06-07 13:18 | 13.8KV 6D FEEDER #5 | Fair | Others | 0 | 13:18 Manually Open 6D OCB Feeder#5 due to: WIP DB#43 PM.Service. WIP SB#43 Temperature High. Request Operator GS #4. 14:37 Manually Closed 6D OCB Feeder#5. Cause: Maintain water Tank level. |  | 1 | 13:18 | Afternoon | Friday | 2019 | 6
11481 | 2019-06-07 13:34 | 2019-06-07 13:34 | 13.8KV 4D FEEDER #1 | Fair | Unidentified | 0 | 4D OCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 13:34 | Afternoon | Friday | 2019 | 6
11482 | 2019-06-07 13:34 | 2019-11-07 09:02 | 13.8KV 4D FEEDER #1 | Fair | Unidentified | 0 | Checked and found: 4DSB-13.8OCB1 T/R, counter : 185 - 176. Relay Flag : NONE Patrolled the line found : WIP pump shut down at GS#4 Cause : Unidentified |  | 1 | 13:34 | Afternoon | Friday | 2019 | 6
11483 | 2019-06-07 13:34 | 2019-06-07 13:34 | 13.8KV 4D FEEDER #3 | Fair | Pin Insulator | 12 | 4D OCB feeder #3 T/R 1x. Not checked yet. |  | 1 | 13:34 | Afternoon | Friday | 2019 | 6
11484 | 2019-06-07 13:34 | 2019-11-07 08:03 | 13.8KV 4D FEEDER #3 | Fair | Pin Insulator | 12 | Checked and found: 4DSB-13.8OCB3 T/R, Counter : 274 - 275, Relay Flag : 51N Patrolled the line found : Broken Pin Insulator Cause : Pin Insulator |  | 1 | 13:34 | Afternoon | Friday | 2019 | 6
11485 | 2019-06-07 13:40 | 2019-06-07 13:40 | 4.16KV DUMAI (HOUSING FEEDER) FEEDER #4 | Fair | Planned Maintenance | 0 | 13:40 Manually Open Recloser H33-07 D/S Dumai feeder#4. due to Cut danger trees. 14:57 Manually closed Recloser H33-07. Cause:Plan Maintenance. |  | 1 | 13:40 | Afternoon | Friday | 2019 | 6
11486 | 2019-06-07 14:20 | 2019-06-07 14:20 | 13.8KV NELLA FEEDER #1 | Fair | Dead End Insulator | 0 | Nella feeder#1 load dropped 57A (186-129A). Nella GFPC T/R 1X. Not checked yet. |  | 1 | 14:20 | Afternoon | Friday | 2019 | 6
11487 | 2019-06-07 14:20 | 2019-10-07 14:20 | 13.8KV NELLA FEEDER #1 | Fair | Dead End Insulator | 0 | Checked & found Nella GFPC T/R 4x Ctr:877-981 R/F:51N. Patrolled the line & found @3 Broken Dead End Insulator o/p 20T31. Cause : Dead End Insulator. |  | 1 | 14:20 | Afternoon | Friday | 2019 | 6
11488 | 2019-06-07 17:29 | 2019-06-07 17:29 | 13.8KV PETANI FEEDER #2 | Cloudy | Broken Fuse Cut Out | 56 | Petani OCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 17:29 | Afternoon | Friday | 2019 | 6
11489 | 2019-06-07 17:29 | 2019-11-07 13:30 | 13.8KV PETANI FEEDER #2 | Cloudy | Broken Fuse Cut Out | 56 | Checked and found: PTNSB-13.8OCB2 T/R, Counter : 317 - 318, Relay Flag : 51N Patrolled the line found : Fuse putus Petani 1 Cause : Broken Fuse Cut Out |  | 1 | 17:29 | Afternoon | Friday | 2019 | 6
11490 | 2019-06-07 19:31 | 2019-06-07 19:31 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 60 | Ketigul 13.8KV VCB fdr #$2 T/R 1X. Not checked yet. |  | 1 | 19:31 | Night | Friday | 2019 | 6
11491 | 2019-06-07 19:31 | 2019-10-07 08:31 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Unidentified | 60 | Checked & found Ketigul VCb fdr#2 T/R 3x Ctr:333-336 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 19:31 | Night | Friday | 2019 | 6
11492 | 2019-06-07 19:31 | 2019-06-07 19:31 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Unidentified | 0 | Ketigul fdr #1 Load dropped 102A (123-21A). Ketigul fdr #3 Load dropped 19A (19-0A). Not checked yet. |  | 1 | 19:31 | Night | Friday | 2019 | 6
11493 | 2019-06-07 19:31 | 2019-10-07 08:31 | 13.8KV KETIGUL FEEDER#1 | Rain and Lightning | Unidentified | 0 | Checked & found Recl. 32AK16 T/R 1x Ctr:141 not operated. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 19:31 | Night | Friday | 2019 | 6
11494 | 2019-07-07 12:54 | 2019-07-07 12:54 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Pin Insulator | 50 | 4D OCB feeder #2 T/R 1x. Nor checked yet. |  | 1 | 12:54 | Afternoon | Sunday | 2019 | 7
11495 | 2019-07-07 12:54 | 2019-11-07 08:32 | 13.8KV 4D FEEDER #2 | Rain and Lightning | Pin Insulator | 50 | Checked and found: 4DSB-13.8OCB2 T/R. Counter : 286 - 287, Relay Flag : 51N Patrolled the line found : Broken Pin Insulator Cause : Pin Insulator |  | 1 | 12:54 | Afternoon | Sunday | 2019 | 7
11496 | 2019-07-07 12:54 | 2019-07-07 12:54 | 13.8KV 4D FEEDER #6 | Rain and Lightning | Unidentified | - | 4D OCB feeder #6 T/R 1x. Nor checked yet. |  | 1 | 12:54 | Afternoon | Sunday | 2019 | 7
11497 | 2019-07-07 12:54 | 2019-11-07 09:15 | 13.8KV 4D FEEDER #6 | Rain and Lightning | Unidentified | - | Checked and found: 4DSB-13.8OCB6 None, Counter : 193 - 193, Relay Flag : NONE Patrolled the line found: WIP pimp shut down at GS#5 Cause : Unidentified |  | 1 | 12:54 | Afternoon | Sunday | 2019 | 7
11498 | 2019-07-07 12:54 | 2019-07-07 12:54 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Unidentified | 0 | 4D feeder #4 load dropped 27A (47-20A). Nor checked yet. |  | 1 | 12:54 | Afternoon | Sunday | 2019 | 7
11499 | 2019-07-07 12:54 | 2019-11-07 09:22 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked and found: 5442-R.4D85 T/R, Counter : 1617 - 1618, Relay Flag : NONE Patrolled the line found : no found Cause : Unidentified |  | 1 | 12:54 | Afternoon | Sunday | 2019 | 7
11500 | 2019-07-07 12:54 | 2019-07-07 12:54 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 13 | 4D feeder #5 load dropped 76A (98-22A). Nor checked yet. |  | 1 | 12:54 | Afternoon | Sunday | 2019 | 7
11501 | 2019-07-07 12:54 | 2019-11-07 08:25 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | 13 | Checked and found: 5442-R.4D14A Unknown, Counter : 276 - 276, Relay Flag : NONE Patrolled the line found : Nothing Found Cause : Lightning |  | 1 | 12:54 | Afternoon | Sunday | 2019 | 7
11502 | 2019-07-07 17:17 | 2019-07-07 17:17 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | C Duri feeder #1 load dropped 53A (138-85A). Nor checked yet. |  | 1 | 17:17 | Afternoon | Sunday | 2019 | 7
11503 | 2019-07-07 17:17 | 2019-10-07 08:17 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | Checked & found Recl. 41AW62 T/R 2x Ctr:321-323. Patrolled the line @1@3 Broken Pin Insulator o/p 40AX02. Cause : Pin Insulator. |  | 1 | 17:17 | Afternoon | Sunday | 2019 | 7
11504 | 2019-07-07 17:41 | 2019-07-07 17:41 | 13.8KV NELLA FEEDER #1 | Cloudy | Broken Fuse Cut Out | 80 | Nella feeder #1 load dropped 129A (182-53A). Nella GFPC T/R 1x. Nella Recloser for Cap Bank T/O. Not checked yet. |  | 1 | 17:41 | Afternoon | Sunday | 2019 | 7
11505 | 2019-07-07 17:41 | 2019-10-07 17:41 | 13.8KV NELLA FEEDER #1 | Cloudy | Broken Fuse Cut Out | 80 | Checked & found Recl. 22V01 T/R 1x Ctr:135-136 R/F:51N. Patrolled the line & found @1@2 Broken FCO for Capacitor Bank near Bangko#170. Cause : Broken Fuse Holder. |  | 1 | 17:41 | Afternoon | Sunday | 2019 | 7
11506 | 2019-07-07 17:41 | 2019-07-07 17:41 | 13.8KV NELLA FEEDER #2 | Cloudy | Pin Insulator | 0 | Nella feeder #2 load dropped 31A (69-38A). Not checked yet. |  | 1 | 17:41 | Afternoon | Sunday | 2019 | 7
11507 | 2019-07-07 17:41 | 2019-10-07 17:41 | 13.8KV NELLA FEEDER #2 | Cloudy | Pin Insulator | 0 | Checked & found Nella VCB fdr#2 T/R 1x Ctr:333-334 R/F:51N. Patrolled the line & found @1 Broken Pin Insulator o/p 20V09. Cause : Pin Insulator. |  | 1 | 17:41 | Afternoon | Sunday | 2019 | 7
11508 | 2019-08-07 09:43 | 2019-08-07 09:43 | 13.8KV RANGAU FEEDER #2 | Fair | Lightning | 7 | Rangau feeder #2 Load dropped 113A (158-45A). Not checked yet. |  | 1 | 9:43 | Morning | Wednesday | 2019 | 8
11509 | 2019-08-07 09:43 | 2019-12-07 11:19 | 13.8KV RANGAU FEEDER #2 | Fair | Lightning | 7 | Checked and found: 5440-R.23BD01 T/R, Counter : 390 - 394, Relay Flag : 51 Patrolled the line found : Pin insolator flase Cause : Lightning |  | 1 | 9:43 | Morning | Wednesday | 2019 | 8
11510 | 2019-08-07 11:10 | 2019-08-07 11:10 | 13.8KV PINANG FEEDER #1 | Fair | Planned Maintenance | 12 | 11:10 Open HLC on pole 10-D-24. Replaced @1,2,3 broken Lightning Arrester on terminal pole Pinang #15 , and Pinang 30. 13:34 Closed HLC on pole 10-D-24. Cause: Planned Maintenance. |  | 1 | 11:10 | Morning | Wednesday | 2019 | 8
11511 | 2019-08-07 18:48 | 2019-08-07 18:48 | 13.8KV KETIGUL FEEDER#2 | Rain | Pin Insulator | 663 | 18:48 Ketigul 13.8 Kv VCB feeder #2 T/LO. Ketigul feeder #1 load dropped 23A (123-100A). 21:30 checked and found, Ketigul fdr #2 T/LO ctr:336-340 R?F: 51N, 51@1,@2. 21:56 Open LBS: 29-AL-07. Open LBS: 31-AN-32. Open LBS: 27-AL-03. 21:58 Blocked and closed Ketigul fdr #2, OK. 22:02 Closed LBS: 29-AL-07, OK. Patrolled the line to Tilan field, but nothing found. 22:31 Closed LBS: 31-AN-32, OK. Patrooled then line to Ubi and Sikaladi field and found @1, @2 broken Pin Insulator at UBI #25. 22:34 Open Ketigul fdr #2. 22:36 Closed LBS: 27-AL-03. 22:38 Blocked and closed Ketigul fdr #2, but tripped again. 22:39 Open LBS: 27-AL-03. 22:40 Blocked and closed Ketigul fdr #2, OK. Isolated broken Pin Insulator at Ubi #25. 00:09 Closed LBS: 27-AL-03. Cause: Pin Insulator. Prod Loss: 960 Bbls / 59Wells. | 123 | 1 | 18:48 | Afternoon | Wednesday | 2019 | 8
11512 | 2019-08-07 19:35 | 2019-08-07 19:35 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Unidentified | 35 | Menggala GFPC T/R 1X. Menggala fdr #1 load dropped 153A (193-40A). Not checked yet. |  | 1 | 19:35 | Night | Wednesday | 2019 | 8
11513 | 2019-08-07 19:35 | 2019-10-07 17:35 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Unidentified | 35 | Checked & found Recl. 19AN04 T/R 1x Ctr:637-638 R/F:51N. Menggala GFPC T/R 2x Ctr:98-100. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 19:35 | Night | Wednesday | 2019 | 8
11514 | 2019-08-07 20:30 | 2019-08-07 20:30 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Pin Insulator | 8 | Ground fault alarm from S. Balam fdr #2 & #4. S. Balam fdr #4 load dropped 62A (186-124A). S. Balam fdr #2 load dropped 36A (101-65A)---WIP. S. Balam fdr #3 load dropped 103A (103-0A)---WIP. S. Balam fdr #1 load dropped 37A (148-111A). Not checked yet. |  | 1 | 20:30 | Night | Wednesday | 2019 | 8
11515 | 2019-08-07 20:30 | 2019-10-07 17:30 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Pin Insulator | 8 | Checked & found Recl. 19AA07 T/R 1x Ctr:486-487 R/F:51N. Patrolled the line & found @1 Broken Pin Insulator Cause : Pin Insulator. |  | 1 | 20:30 | Night | Wednesday | 2019 | 8
11516 | 2019-09-07 01:49 | 2019-09-07 01:49 | 13.8KV DARLING VCB FEEDER #8 | Fair | Others | 271 | 01:49 It was reported spark on pole 05-N3-23D D/S Darling feeder #3. 03:10 Checked and found burnt out blade of LBS: 05-N3-23D. 12:02 Patrolled the line found Recloser: 05-N3-02 T/O. (in block position) Counter: 124-125. 12:05 Manually block and closed Recloser: 05-N3-02 --> OK. (still in block position due to PT WKS clean up canal). Cause: Others (sparks blade of Load Break Switch). |  | 1 | 1:49 | Night | Saturday | 2019 | 9
11517 | 2019-09-07 07:15 | 2019-09-07 07:15 | 13.8KV MINAS FEEDER #3 | Drizzle | Unidentified | 23 | Minas ACB #2 (feeder #3) T/R 1x. Not patrolled yet. |  | 1 | 7:15 | Morning | Saturday | 2019 | 9
11518 | 2019-09-07 07:15 | 2019-10-07 14:05 | 13.8KV MINAS FEEDER #3 | Drizzle | Unidentified | 23 | Checked and found: MNSSG-13.8ACB02 None, Counter : 80160 - 80160, Relay Flag : NONE Patrolled the line found : not patroll due to breaker T/R Cause : Unidentified |  | 1 | 7:15 | Morning | Saturday | 2019 | 9
11519 | 2019-09-07 07:15 | 2019-09-07 07:15 | 13.8KV MINAS FEEDER #6 | Drizzle | Animal | 121 | 07:15 Minas ACB #18 (feeder #6) T/O. Checked and found Minas ACB #18 (feeder #6) T/LO. Counter:193-195 R/F: 51 @1,@2. 10:00 Patrolled the line found broken Recloser 6E-67A due to animal (monkey). 10:12 Opened LBS: 7E- 40A. 10:13 Opened LBS: 7E- 86 (two way feeders 8D feeder #10 and Minas feeder #6). 13:22 Replaced Recloser 6E-67A. 13:23 Manually closed LBS: 7E- 40A. 13:24 Manually blocked and closed Minas ACB feeder #6 --> Ok. and then released the block. 15:25 Manually blocked & closed Recloser 7E-67A and then release the block. Cause: Animal. |  | 1 | 7:15 | Morning | Saturday | 2019 | 9
11520 | 2019-09-07 07:15 | 2019-09-07 07:15 | 13.8KV MINAS FEEDER #4 | Drizzle | Unidentified | 0 | Minas feeder #4 Load dropped 150A (185-35A). Not checked yet. |  | 1 | 7:15 | Morning | Saturday | 2019 | 9
11521 | 2019-09-07 07:15 | 2019-11-07 09:25 | 13.8KV MINAS FEEDER #4 | Drizzle | Unidentified | 0 | Checked and found: 5442-R.7D121 None, Counter : 19 - 19, Relay Flag : NONE Patrolled the line found : nothing Recloser working Cause : Unidentified |  | 1 | 7:15 | Morning | Saturday | 2019 | 9
11522 | 2019-09-07 07:15 | 2019-09-07 07:15 | 13.8KV MINAS FEEDER #5 | Drizzle | Unidentified | 0 | Minas feeder #5 load dropped 58A (77-19A). Not checked yet. |  | 1 | 7:15 | Morning | Saturday | 2019 | 9
11523 | 2019-09-07 07:15 | 2019-10-07 14:11 | 13.8KV MINAS FEEDER #5 | Drizzle | Unidentified | 0 | Checked and found: 5442-R.7E21 None, Counter : 132 - 132, Relay Flag : NONE Patrolled the line found: Nothing breaker working Cause : Unidentified. |  | 1 | 7:15 | Morning | Saturday | 2019 | 9
11524 | 2019-09-07 07:15 | 2019-09-07 07:15 | 13.8KV 8D FEEDER #10 | Drizzle | Animal | 28 | 8D VCB feeder #10 T/R 1x. Not checked yet. |  | 1 | 7:15 | Morning | Saturday | 2019 | 9
11525 | 2019-09-07 07:15 | 2019-10-07 14:09 | 13.8KV 8D FEEDER #10 | Drizzle | Animal | 28 | Checked and found: 8DSB-13.8OCB10 T/R, Counter : 266 - 267, Relay Flag : 51N Patrolled the line found : Monyet at Recl# 7E-67A Cause : Animal. |  | 1 | 7:15 | Morning | Saturday | 2019 | 9
11526 | 2019-09-07 11:51 | 2019-09-07 11:51 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 96 | 11:51 Manually open LBS: 27-AL-03 D/S Ketigul feeder #2. - Due to squeezed jumpers on pole 26-AL-05. - Replaced @1,2,3 pin insulator on pole 26-AL-03. - Replaced @1,2,3 pin insulator on pole 26-AL-04. - Replaced @2 pin insulator on pole 26-AL-02. 12:51 Manually closed LBS: 27-AL-03. Cause: Planned Maintenance. |  | 1 | 11:51 | Morning | Saturday | 2019 | 9
11527 | 2019-09-07 17:32 | 2019-09-07 17:32 | 13.8KV NORTH DURI FEEDER #8 | Fair | Tree | 0 | N.Duri 13.8Kv VCB feeder #8 T/R 1x. Not checked yet. |  | 1 | 17:32 | Afternoon | Saturday | 2019 | 9
11528 | 2019-09-07 17:32 | 2019-12-07 11:22 | 13.8KV NORTH DURI FEEDER #8 | Fair | Tree | 0 | Checked and found: NDRSB-13.8VCB8 T/R, Counter : 96 - 96, Relay Flag : 51 Patrolled the line found : High tree Cause : Tree |  | 1 | 17:32 | Afternoon | Saturday | 2019 | 9
11529 | 2019-10-07 09:45 | 2019-10-07 09:45 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 162 | 09:45 Manually Opened Rec. 41AW62 (C.Duri fdr#1). Replaced @1@3 Pin Insulator o/p 44AX02. 10:46 Blocked & closed Recl. 41AW62, then release the block. Cause: Plan Maintenance. |  | 1 | 9:45 | Morning | Monday | 2019 | 10
11530 | 2019-10-07 11:20 | 2019-10-07 11:20 | 13.8KV LIBO FEEDER #2 | Fair | Planned Maintenance | 75 | 11:20 Manually Opened Libo VCB fdr#2. Reconnected Jumper toward Loc. SEL#53. 12:35 Blocked & closed Libo VCB fdr#2, then release the block. Cause: Plan Maintenance. |  | 1 | 11:20 | Morning | Monday | 2019 | 10
11531 | 2019-10-07 15:10 | 2019-10-07 15:10 | 13.8KV NORTH DURI FEEDER #8 | Fair | Planned Maintenance | 0 | 15:10 Manually Opened Recl. 10-K6-02 (N.Duri fdr#8). Replaced @1@2@3 Fuse Cut Out at AWT10SE. 15:50 Blocked & closed Recl. 10-K6-02, then release the block. Cause: Plan Maintenance. |  | 1 | 15:10 | Afternoon | Monday | 2019 | 10
11532 | 2019-11-07 08:37 | 2019-11-07 08:37 | 13.8KV BANGKO FEEDER #3 | Fair | Planned Maintenance | 952 | 08:37 Bangko fdr#3 Load dropped 198A(222-24A), Pump Off. 09:12 Manually opened Bangko VCB fdr#1 (Req. BKO GS0, then Close at 12:42. (Maintain Tank Level) 09:30 It was reported B/O fuse for 5Mva Tx-A BKO EOR. 10:03 Opened LBS 22 Z 07 for BKO EOR. Replaced @1 B/O fuse for 5Mva Tx-A BKO EOR. Trouble shoot Tx-B at BKO EOR, after replaced transformer 11:00 Manually open Nella VCB fdr#2 (Req. BKO GS), then Closed at 12:44. (maintain Tank level) 12:15 Closed LBS 22 Z 07 for BKO EOR. Cause: Planned Maintenance Prod.loss. Nella fdr#2 : 124 bbls / 17 Wells. Bangko fdr#1: 878 bbls / 65 Wells. Total : 1002 bbls / 82 Wells. | 1234 | 1 | 8:37 | Morning | Thursday | 2019 | 11
11533 | 2019-11-07 16:46 | 2019-11-07 16:46 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Duri Field fdr#1 T/R 1x. Not checked yet. |  | 1 | 16:46 | Afternoon | Thursday | 2019 | 11
11534 | 2019-11-07 16:46 | 16/07/2019 15:20 | 13.8KV DURI FIELD FEEDER #1 | Fair | Unidentified | 0 | Checked and found: DFSG-13.8ACB41 T/R, Counter : 707 - 708, Relay Flag : 51N. Patrolled the line found : No finding Cause : Unidentified |  | 1 | 16:46 | Afternoon | Thursday | 2019 | 11
11535 | 2019-11-07 18:30 | 2019-11-07 18:30 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 20 | Ketigul VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 18:30 | Afternoon | Thursday | 2019 | 11
11536 | 2019-11-07 18:30 | 16/07/2019 15:32 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 20 | Checked and found: PKTGL-13.8VCB1 T/R, Counter : 216 - 217, Relay Flag : 51N. Patrolled the line found : No Finding Cause : Unidentified |  | 1 | 18:30 | Afternoon | Thursday | 2019 | 11
11537 | 2019-12-07 13:48 | 2019-12-07 13:48 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Planned Maintenance | 97 | 13:48 Manually opened LBS 34CT48 (CKBS fdr#5). Repaired Cross Arm o/p 35CT24. 14:57 Closed LBS 34CT48. Cause: Plan Maintenance. |  | 1 | 13:48 | Afternoon | Saturday | 2019 | 12
11538 | 2019-12-07 14:14 | 2019-12-07 14:14 | MINAS POWER PLANT |  |  | - | 14:14 S/U MGT#9, then on line the unit at 14:40. |  | 1 | 14:14 | Afternoon | Saturday | 2019 | 12
11539 | 2019-12-07 14:48 | 2019-12-07 14:48 | MINAS POWER PLANT |  |  | - | Off line MGT#10, then S/D the unit for Maintenance. |  | 1 | 14:48 | Afternoon | Saturday | 2019 | 12
11540 | 2019-12-07 15:40 | 2019-12-07 15:40 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified | 0 | Darling VCB fdr#4 T/R 1x. Not checked yet. |  | 1 | 15:40 | Afternoon | Saturday | 2019 | 12
11541 | 2019-12-07 15:40 | 16/07/2019 15:27 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified | 0 | Checked and found: DRLG4-13.8VCB4 T/R, Counter : 145 - 146, Relay Flag : 51. Patrolled the line found : No Finding Cause : Unidentified |  | 1 | 15:40 | Afternoon | Saturday | 2019 | 12
11542 | 2019-07-13 14:05 | 2019-07-13 14:05 | 13.8KV S. BALAM FEEDER #4 | Fair | Lightning | 89 | So.Balam fdr#4 T/R 1x. So Balam GFPC T/R 1x. Not checked yet./ |  | 1 | 14:05 | Afternoon | Saturday | 2019 | 7
11543 | 2019-07-13 14:05 | 2019-07-15 15:02 | 13.8KV S. BALAM FEEDER #4 | Fair | Lightning | 89 | Checked and found: SBLM-13.8VCB4 T/R, Counter : 370 - 371, Relay Flag : 51N Patrolled the line found : Pin Insulator flash over Cause : Lightning |  | 1 | 14:05 | Afternoon | Saturday | 2019 | 7
11544 | 2019-07-13 22:17 | 2019-07-13 22:17 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning Arrester | 45 | It was reported no Power at Field Perkebunan & Genting Not checked yet |  | 1 | 22:17 | Night | Saturday | 2019 | 7
11545 | 2019-07-13 22:17 | 2019-07-14 10:50 | 13.8KV SINTONG FEEDER #2 | Fair | Lightning Arrester | 45 | 10:50 Checked & found Recl. 29Z13A T/SO Ctr:203-206. Patrolled the line & found @1 Broken LA on T/P Genting#04. 11:25 Blocked & Closed Recl. 29Z13A, then release the block. Cause: Lightning Arrester. |  | 1 | 22:17 | Night | Saturday | 2019 | 7
11546 | 2019-07-15 00:12 | 2019-07-15 00:12 | 13.8KV 6DN FEEDER #1 | Fair | Tree | 321 | 00:12 6DN fdr#1 load dropped 37A (125-88A). 11:10 It was reported no power at well 5E-64,5E-65,5E-83 & 5E-84. 11:50 Check & Found recl.5E-83 T/LO Ctr: 29-32. Patrolled the line & found Fall down trees at Ped Tx 5E-84. Cleaning the trees at Ped Tx 5E-84. 12:15 Blocked & Closed recl.5E-83 then replaced the block. Cause: Trees. |  | 1 | 0:12 | Night | Monday | 2019 | 7
11547 | 2019-07-15 00:17 | 2019-07-15 00:17 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 49 | OKB 13.8 Kv OCB Feeder #2 T/R 1x. CKB 13.8 Kv VCB Feeder #2 load dropped 112A (262-150A). Not Checked yet. |  | 1 | 0:17 | Night | Monday | 2019 | 7
11548 | 2019-07-15 00:17 | 2019-07-15 16:45 | 13.8KV KOTABATAK FEEDER #2 | Rain and Lightning | Lightning | 49 | Checked and found: 5443-R.38CW01 T/R, Counter : 121 - 122, Relay Flag : 51N. Patrolled the line found : B/O FusLink 550KVA Cause : Lightning |  | 1 | 0:17 | Night | Monday | 2019 | 7
11549 | 2019-07-15 00:39 | 2019-07-15 00:39 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Dead End Insulator | 0 | Batang 13.8 Kv OCB Feeder #2 T/R 1x. Not Checked yet. |  | 1 | 0:39 | Night | Monday | 2019 | 7
11550 | 2019-07-15 00:39 | 2019-07-16 15:36 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Dead End Insulator | 0 | Checked and found: BTGSB-13.8OCB2 T/R, Counter : 189 - 190, Relay Flag : 51. Patrolled the line found : Dead end pecah Counter : 357 - 358, Relay Flag : NONE Patrolled the line found : Pin insulator pecah Cause : Dead End Insulator |  | 1 | 0:39 | Night | Monday | 2019 | 7
11551 | 2019-07-15 07:26 | 2019-07-15 07:26 | 13.8KV 6DN FEEDER #2 | Fair | Broken Fuse Holder | 42 | 6DN fdr#2 T/R 1x. Not checked yet. |  | 1 | 7:26 | Morning | Monday | 2019 | 7
11552 | 2019-07-15 07:26 | 2019-07-18 07:38 | 13.8KV 6DN FEEDER #2 | Fair | Broken Fuse Holder | 42 | Checked and found: FUSE T/R, Counter : 328 - 329, Relay Flag : 50N Patrolled the line found : Broken Fuse Holder Cause : Broken Fuse Holder |  | 1 | 7:26 | Morning | Monday | 2019 | 7
11553 | 2019-07-15 09:40 | 2019-07-15 09:40 | 13.8KV DURI FIELD FEEDER #4 | Fair | Planned Maintenance | 60 | 09:40 Manually open LBS 07-V3-02 ( D Field fdr#4). Replaced broken pin insulation o/p 07-V3-11. Replaced broken Dead end insulation o/p 07-V3-12. 10:37 Closed LBS 07-V3-02. Cause : Planned maintenance. |  | 1 | 9:40 | Morning | Monday | 2019 | 7
11554 | 2019-07-15 14:15 | 2019-07-15 14:15 | 13.8KV BANGKO FEEDER #3 | Fair | Planned Maintenance | 96 | 14:15 Open LBS 22-Z-07 (Bangko fdr#3). Set voltage Tx-B Bangko EOR. 14:40 Manually open Nella fdr#2 15:55 Manually Block & Closed Nella Fdr#2, then released the block After finished Adjusting the voltage Tx-B Bangko EOR 14:20 Closed LBS 22-Z-07. Cause : Planned maintenance |  | 1 | 14:15 | Afternoon | Monday | 2019 | 7
11555 | 2019-07-15 14:40 | 2019-07-15 14:40 | CENTRAL DURI POWER PLANT |  |  | - | 14;40 CDGT#1 then on line the at 15:14. |  | 1 | 14:40 | Afternoon | Monday | 2019 | 7
11556 | 2019-07-15 16:25 | 2019-07-15 16:25 | CENTRAL DURI POWER PLANT |  |  | - | 16:25 Off line CDGT#5 then S/D the unit for maintenance. |  | 1 | 16:25 | Afternoon | Monday | 2019 | 7
11557 | 2019-07-16 10:04 | 2019-07-16 10:04 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | Perform Switching to Shut down Menggala Substation for replacing power TX 10:04 Transfer part load Sintong Fdr#1 to Bangko Fdr#4 by Open Recl. 25AD26 and Closed LBS 25AC33 10:41 Transfer Load Menggala Fdr#1 to Sintong Fdr#1 by Closed LBS 25AF39 10:43 Opened Menggala VCB Fdr#1 10:46 Open Menggala C/S to Shut down Menggala TX substation. Cause: Planned Maintenace. Production loss : 147 Bbls. : 11 wells ( Meno 6,7,19,22,31,35,37,38,39,40,47 ). |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11558 | 2019-07-16 10:04 | 2019-07-17 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | Production loss : 268 Bbls. : 11 wells ( Meno 6,7,19,22,31,35,37,38,39,40,47 ). : Total per today = 415 Bbls |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11559 | 2019-07-16 10:04 | 2019-07-18 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | Production loss : 268 Bbls. : 11 wells ( Meno 6,7,19,22,31,35,37,38,39,40,47 ). : Total per today = 683 Bbls |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11560 | 2019-07-16 10:04 | 2019-07-19 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | Production loss : 268 Bbls. : 11 wells ( Meno 6,7,19,22,31,35,37,38,39,40,47 ). : Total per today = 951 Bbls |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11561 | 2019-07-16 10:04 | 2019-07-20 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | Production loss : 268 Bbls. : 11 wells ( Meno 6,7,19,22,31,35,37,38,39,40,47 ). : Total per today = 1219 Bbls |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11562 | 2019-07-16 10:04 | 2019-07-21 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | Production loss : 268 Bbls. : 11 wells ( Meno 6,7,19,22,31,35,37,38,39,40,47 ). : Total per today = 1487 Bbls |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11563 | 2019-07-16 10:04 | 2019-07-22 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | Production loss : 268 Bbls. : 11 wells ( Meno 6,7,19,22,31,35,37,38,39,40,47 ). : Total per today = 1755 Bbls |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11564 | 2019-07-16 10:04 | 2019-07-23 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | Production loss : 268 Bbls. : 11 wells ( Meno 6,7,19,22,31,35,37,38,39,40,47 ). : Total per today = 2023 Bbls |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11565 | 2019-07-16 10:04 | 2019-07-24 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | Production loss : 268 Bbls. : 11 wells ( Meno 6,7,19,22,31,35,37,38,39,40,47 ). : Total per today = 2291 Bbls |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11566 | 2019-07-16 10:04 | 2019-07-25 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | Production loss : 268 Bbls. : 11 wells ( Meno 6,7,19,22,31,35,37,38,39,40,47 ). : Total per today = 2559 Bbls |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11567 | 2019-07-16 10:04 | 2019-07-26 21:00 | MENGGALA SUBSTATION | Fair | Planned Maintenance | 2781 | 21:00 Energized 11 well at Meno. Production loss : 222 Bbls / 11 wells. Grand total: 2781 Bbls / 11 wells. |  | 1 | 10:04 | Morning | Tuesday | 2019 | 7
11568 | 2019-07-16 12:00 | 2019-07-16 12:00 | 13.8KV CENTRAL KOTABATAK FEEDER #2 | Fair | Lightning | - | 12:00 It was reported no power at GS1 (CKB Fdr#2) 14:00 Checked & found Recl. 101A T/O Block & Closed the Recloser then released the block Cause: Not patrolled yet |  | 1 | 12:00 | Afternoon | Tuesday | 2019 | 7
11569 | 2019-07-16 12:00 | 2019-07-19 08:09 | 13.8KV CENTRAL KOTABATAK FEEDER #2 | Fair | Lightning | - | Checked and found: 5443-RCL 101A T/O, Counter : 3 - 4, Relay Flag : 51N Patrolled the line found: Not Found Cause : Lightning |  | 1 | 12:00 | Afternoon | Tuesday | 2019 | 7
11570 | 2019-07-16 13:50 | 2019-07-16 13:50 | MINAS POWER PLANT |  |  | - | 13:50 S/U MGT#10 then online the unit at 14:45. |  | 1 | 13:50 | Afternoon | Tuesday | 2019 | 7
11571 | 2019-07-16 15:00 | 2019-07-16 15:00 | MINAS POWER PLANT |  |  | - | 15:00 Off line MGT#9 then S/D the unit for S/B. |  | 1 | 15:00 | Afternoon | Tuesday | 2019 | 7
11572 | 2019-07-17 06:07 | 2019-07-17 06:07 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 0 | Darling VCB Fdr#1 T/R 1x not checked yet |  | 1 | 6:07 | Morning | Wednesday | 2019 | 7
11573 | 2019-07-17 06:07 | 2019-07-19 17:41 | 13.8KV DARLING VCB FEEDER #3 | Fair | Unidentified | 0 | Checked and found VCB fdr #3 DRL T/R 1x, ctr: 262-263, R/F: 51P @2 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 6:07 | Morning | Wednesday | 2019 | 7
11574 | 2019-07-17 09:04 | 2019-07-17 09:04 | 13.8KV DURI FIELD FEEDER #1 | Fair | Planned Maintenance | 10 | 09:04 Manual Open LBS 01-7-32 for Maintenance jobs Planned Maintenance |  | 1 | 9:04 | Morning | Wednesday | 2019 | 7
11575 | 2019-07-17 10:15 | 2019-07-17 10:15 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 65 | 10:15 Ketigul VCB Fdr#2 T/R 1x 19:22 Ketigul VCB Fdr#2 T/R 1x Not Patrolled Yet |  | 1 | 10:15 | Morning | Wednesday | 2019 | 7
11576 | 2019-07-17 10:15 | 2019-07-19 17:47 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 65 | Checked and found VCB KTGL fdr #2 T/R 2x, ctr: 342-344, R/F: 51P @1 Patrolled the line just found bird nest at conductor @1 o/p 29-AN-39 Cause : Unidentified |  | 1 | 10:15 | Morning | Wednesday | 2019 | 7
11577 | 2019-07-17 10:15 | 2019-07-17 10:15 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | - | 10:15 KETIGUL FEEDER #1 dropped 68 A (117 - 49 A) KETIGUL FEEDER #3 dropped 11 A (28 - 17 A) Not Checked Yet |  | 1 | 10:15 | Morning | Wednesday | 2019 | 7
11578 | 2019-07-17 10:15 | 2019-07-19 17:49 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | - | Checked and found all RCL are in Normal Condition. No line patrolled finding Cause : Unidentified |  | 1 | 10:15 | Morning | Wednesday | 2019 | 7
11579 | 2019-07-17 14:35 | 2019-07-17 14:35 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 2 | 14:35 DF feeder #4 T/O (block position for PT WKS clean up canal at area-7 15:01 Manual Close DF feeder #4 after make clearance with PT WKS, OK Not Patrolled Yet |  | 1 | 14:35 | Afternoon | Wednesday | 2019 | 7
11580 | 2019-07-17 14:35 | 2019-07-21 15:51 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 2 | Checked and found: DFSG-13.8ACB51 T/O, Counter : 548 - 549, Relay Flag : 50 Patrolled the line found : Nothing Found Cause : Unidentified |  | 1 | 14:35 | Afternoon | Wednesday | 2019 | 7
11581 | 2019-07-17 17:54 | 2019-07-17 17:54 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | 17:54 CD fdr #6 T/R 1x, counter: 501 - 502, R/F 51N, 51G Not Patrolled Yet |  | 1 | 17:54 | Afternoon | Wednesday | 2019 | 7
11582 | 2019-07-17 17:54 | 2019-07-19 17:51 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Unidentified | 0 | Checked and found CD ACB fdr #6 T/R 1x, ctr: 501-502, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 17:54 | Afternoon | Wednesday | 2019 | 7
11583 | 2019-07-18 23:59 | 2019-07-18 23:59 | CPI POWER SYSTEM |  | Normal Condition | - | Normal System Condition |  | 1 | 23:59 | Night | Thursday | 2019 | 7
11584 | 2019-07-19 16:16 | 2019-07-19 16:16 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 0 | 16:16 Batang VCB fdr #3 T/R 1x Not Checked Yet |  | 1 | 16:16 | Afternoon | Friday | 2019 | 7
11585 | 2019-07-19 16:16 | 2019-07-21 15:53 | 13.8KV BATANG FEEDER #3 | Fair | Unidentified | 0 | Checked and found: BTGSB-13.8OCB3 T/R, Counter : 380 - 381, Relay Flag : 51 Patrolled the line found : Nothing Found Cause : Unidentified |  | 1 | 16:16 | Afternoon | Friday | 2019 | 7
11586 | 2019-07-20 10:02 | 2019-07-20 10:02 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | - | 10:02 CD ACB fdr #16 T/R 1x, ctr: 355 - 356, R/F: 51N Not Patrolled Yet |  | 1 | 10:02 | Morning | Saturday | 2019 | 7
11587 | 2019-07-20 10:02 | 2019-07-23 15:43 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | - | Checked and found : CDRSG-13.8ACB28 T/R, Counter : 355 - 356, Relay Flag : 51 Patrolled the line found : None Cause : Unidentified |  | 1 | 10:02 | Morning | Saturday | 2019 | 7
11588 | 2019-07-21 07:30 | 2019-07-21 07:30 | 13.8KV 4B FEEDER #1 | Fair | Normal Condition | 12 | 07:30 4B VCB fdr #1 T/R 1x Not Checked Yet |  | 1 | 7:30 | Morning | Sunday | 2019 | 7
11589 | 2019-07-21 07:30 | 2019-07-24 12:55 | 13.8KV 4B FEEDER #1 | Fair | Normal Condition | 12 | Checked and found: 4BSB-13.8OCB1 T/R, Counter : 379 - 380, Relay Flag : 50N Patrolled the line found : Nothing found Cause : Normal Condition |  | 1 | 7:30 | Morning | Sunday | 2019 | 7
11590 | 2019-07-21 08:55 | 2019-07-21 08:55 | 13.8KV DARLING VCB FEEDER #3 | Fair | Animal | 0 | 08:55 Reported TS-5NE is off (no power) near pole 05-N1-08A (no load dropped at related feeder - DRL fdr #3) waiting to checked by HO electrician team. 14:51 Reported no power from 750 kVA TX for TS-5NE, no b/o fuse indication 16:57 Checked and found b/o fuse link 2 pcs @2, @3 for 750 kVA TX of TS-5NE 17:14 Replace the b/o fuse (2 pcs) and re-energize the TX, OK Cause: Animal (mouse) |  | 1 | 8:55 | Morning | Sunday | 2019 | 7
11591 | 2019-07-21 17:39 | 2019-07-21 17:39 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 21 | 17:39 Ketigul VCB fdr #1 T/R 1x. Not checked yet. |  | 1 | 17:39 | Afternoon | Sunday | 2019 | 7
11592 | 2019-07-21 17:39 | 2019-07-23 08:48 | 13.8KV KETIGUL FEEDER#1 | Fair | Unidentified | 21 | Checked and found: PKTGL-13.8VCB1 T/R, Counter : 217 - 218, Relay Flag : 51N Patrolled the line found : No Finding Cause : Unidentified |  | 1 | 17:39 | Afternoon | Sunday | 2019 | 7
11593 | 2019-07-22 04:26 | 2019-07-22 04:26 | 13.8KV 8D FEEDER #2 | Fair | Normal Condition | 16 | 8D OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 4:26 | Morning | Monday | 2019 | 7
11594 | 2019-07-22 04:26 | 2019-07-24 12:59 | 13.8KV 8D FEEDER #2 | Fair | Normal Condition | 16 | Checked and found: 8DSB-13.8OCB2 T/R, Counter : 287 - 288, Relay Flag : 51N Patrolled the line found : Nothing found Cause : Normal Condition |  | 1 | 4:26 | Morning | Monday | 2019 | 7
11595 | 2019-07-22 17:17 | 2019-07-22 17:17 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | - | 17:17 Ground fault alarm at Sintong fdr #1 and fdr #2 Sintong GFPC T/R 1x Sintong fdr #2 load dropped 102 A (182 - 80 A) Cause: Not checked Yet |  | 1 | 17:17 | Afternoon | Monday | 2019 | 7
11596 | 2019-07-22 17:17 | 2019-07-25 08:43 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Lightning | - | Checked and found:5440-R.28AF02 T/R, Counter : 1543 - 1546, Relay Flag : NONE Patrolled the line found : Broken Pin Support 10% Cause : Lightning |  | 1 | 17:17 | Afternoon | Monday | 2019 | 7
11597 | 2019-07-22 17:50 | 2019-07-22 17:50 | CENTRAL DURI POWER PLANT |  |  | - | 17:50 S/U CGT#2, then on line the unit at 18:40. |  | 1 | 17:50 | Afternoon | Monday | 2019 | 7
11598 | 2019-07-22 17:53 | 2019-07-22 17:53 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 90 | Nella 13.8KV VCB fdr #1 T/R 1X. Nella fdr #2 load dropped 23A (73-50A). Ground fault alarm from Nella fdr #1. Not checked yet. |  | 1 | 17:53 | Afternoon | Monday | 2019 | 7
11599 | 2019-07-22 17:53 | 2019-07-24 09:10 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 90 | Checked and found: NLASB-13.8VCB1 T/R, Counter : 541 - 542, Relay Flag : 51N Patrolled the line found : Broken pin insulator 50% Cause : Lightning |  | 1 | 17:53 | Afternoon | Monday | 2019 | 7
11600 | 2019-07-22 20:00 | 2019-07-22 20:00 | CENTRAL DURI POWER PLANT |  |  | - | Off Line CGT#3, the S/D the unit for S/B. |  | 1 | 20:00 | Night | Monday | 2019 | 7
11601 | 2019-07-22 20:17 | 2019-07-22 20:17 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Dead End Insulator | 0 | N.Duri VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 20:17 | Night | Monday | 2019 | 7
11602 | 2019-07-22 20:17 | 2019-07-26 15:37 | 13.8KV NORTH DURI FEEDER #1 | Rain and Lightning | Dead End Insulator | 0 | Checked and found: NDRSB-13.8VCB1 T/R, Counter : 310 - 311, Relay Flag : 51 Patrolled the line found : Dead end flash over Cause : Dead End Insulator |  | 1 | 20:17 | Night | Monday | 2019 | 7
11603 | 2019-07-22 20:47 | 2019-07-22 20:47 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Tree | 63 | 20:47 3D VCB fdr#3 T/LO 3D fdr#2 Load dropped 128A(160-32A) 3D fdr#4 Load dropped 130A(168-38A) Checked & found Ctr: 486-490, R/F: 50/51 @1@2 23:45 Patrolled the Line, found High Palm Tree touch power line Near LBS 4C-138 24:39 Block & Closed 3D VCB fdr#3, the released the block, after Cut the Trees Cause: High Tree |  | 1 | 20:47 | Night | Monday | 2019 | 7
11604 | 2019-07-22 20:47 | 2019-07-23 08:22 | 13.8KV 3D FEEDER #3 | Rain and Lightning | Tree | 63 | Checked and found : 3DSB-13.8OCB3 T/LO, Counter : 486 - 490, Relay Flag : 51N Patrolled the line found : Found Palm tress touch power line. Cause : Tree |  | 1 | 20:47 | Night | Monday | 2019 | 7
11605 | 2019-07-22 21:14 | 2019-07-22 21:14 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | C.Duri ACB fdr#1 T/R 1x Not checked yet |  | 1 | 21:14 | Night | Monday | 2019 | 7
11606 | 2019-07-22 21:14 | 2019-07-26 15:41 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked and found: CDRSG-13.8ACB11 None, Counter : 260 - 260, Relay Flag : NONE Patrolled the line found : No Finding Cause : Unidentified |  | 1 | 21:14 | Night | Monday | 2019 | 7
11607 | 2019-07-22 21:14 | 2019-07-22 21:14 | 115KV N. DURI SUBST - CD. SW. YARD LINE | Rain and Lightning | Unidentified | 0 | 21:14 115Kv Line C.Duri - N.Duri GCB#53 T/R. 115Kv Line C.Duri - N.Duri GCB#55 T/R. 115Kv Line N.Duri - C.Duri GCB#3 T/O (230/115Kv Tx-5). 21:32 Mannualy Opened 115Kv N.Duri GCB#53, then Closed at 21:35. Mannualy Opened 115Kv N.Duri GCB#55, then Closed at 21:35. 21:33 Closed 115Kv N.Duri GCB#3 (230/115Kv Tx-5). Not checked yet. |  | 1 | 21:14 | Night | Monday | 2019 | 7
11608 | 2019-07-22 21:14 | 2019-07-27 15:08 | 115KV N. DURI SUBST - CD. SW. YARD LINE | Rain and Lightning | Unidentified | 0 | Checked and found: - 115 kV GCB #53 CD T/R 1x (Man Open 1x), ctr: 178 - 180, R/F: 87L - 115 kV GCB #55 CD T/R 1x, (Man Open 1x), ctr: 115 - 118, R/F: 21 - 115 kV GCB #3 ND T/O, ctr: 242 - 243, R/F: None Patrolled the line and found flash over dead end @3 o/p DD-15 Cause : Unidentified |  | 1 | 21:14 | Night | Monday | 2019 | 7
11609 | 2019-07-22 21:15 | 2019-07-22 21:15 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | - | 20:50 It was reported no Power at Pematang GS TX#A, BWM Pump Trip Off. 21:15 Manually opened Pematang VCB fdr#2 to Maintain Tank Level 21:32 Checked & found the Recloser for TX#A T/O Block & Closed Recloser TX#A, the Released the block 22:08 Manually Opened Rangau VCB fdr#2, to Maintain Pematang GS Tank Level 22:51 Closed Rangau VCB fdr#2 22:52 Closed Pematang VCB fdr#2 Cause: Lightning |  | 1 | 21:15 | Night | Monday | 2019 | 7
11610 | 2019-07-22 21:53 | 2019-07-22 21:53 | 115KV DURI - KOTABATAK JUNCTION LINE | Rain and Lightning | Unidentified | 26 | 115Kv Line DRB - Pungut GCB#21 T/R. 115Kv Line DRB - Pungut GCB#29 T/R. 115Kv Line Pungut - DRB GCB#21 T/R. 115Kv Line KBJ - Pungut GCB#51 T/R. 115Kv Line KBJ - Pungut GCB#53 T/R. (Pungut Substation no power). Not checked yet. |  | 1 | 21:53 | Night | Monday | 2019 | 7
11611 | 2019-07-22 21:53 | 2019-07-27 15:11 | 115KV DURI - KOTABATAK JUNCTION LINE | Rain and Lightning | Unidentified | 26 | Checked and found: GCB #51 T/R, Counter : 252 - 253, Relay Flag : NONE. Patrolled the line found: Nothing Found Cause : Unidentified |  | 1 | 21:53 | Night | Monday | 2019 | 7
11612 | 2019-07-23 07:23 | 2019-07-23 07:23 | 13.8KV CENTRAL DURI FEEDER #16 | Drizzle | Dead End Insulator | 0 | CD ACB fdr #16 T/R 1x, ctr: 3546 - 357, R/F 50P @1 @2 Not Patrolled Yet |  | 1 | 7:23 | Morning | Tuesday | 2019 | 7
11613 | 2019-07-23 07:23 | 2019-07-26 16:29 | 13.8KV CENTRAL DURI FEEDER #16 | Drizzle | Dead End Insulator | 0 | Checked and found CD ACB fdr #16 T/R 1x, ctr: 356-357, R/F: 50P @1 and also RCL 09-P3-02 T/R 1x, ctr: 146-147, R/F: 50P @1 Patrolled the line and found broken dead end @1 o/p 03-H-3 Cause : Dead End Insulator |  | 1 | 7:23 | Morning | Tuesday | 2019 | 7
11614 | 2019-07-23 11:10 | 2019-07-23 11:10 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Emergency | 0 | 11:10 Manual Open VCB PTP fdr #6 To maintain level tank due to WIP pumps problem at PTP GS Cause: Emergency |  | 1 | 11:10 | Morning | Tuesday | 2019 | 7
11615 | 2019-07-23 19:48 | 2019-07-23 19:48 | 13.8KV 6DN FEEDER #2 | Lightning | Lightning | 40 | 6DN fdr#2 T/R 1x. 6DN fdr#1 Load dropped 72A (143-71A). 6DN fdr#3 Load dropped 215 A (288-73A), Pump Off. Not checked yet. |  | 1 | 19:48 | Night | Tuesday | 2019 | 7
11616 | 2019-07-23 19:48 | 2019-07-26 08:54 | 13.8KV 6DN FEEDER #2 | Lightning | Lightning | 40 | Checked and found: 6DNSB-13.8OCB2 T/R, Counter : 329 - 330, Relay Flag : 50 Patrolled the line found : Nothing Found Cause : Lightning |  | 1 | 19:48 | Night | Tuesday | 2019 | 7
11617 | 2019-07-24 01:34 | 2019-07-24 01:34 | 13.8KV PETAPAHAN FEEDER #6 | Cloudy | Emergency | - | 01:34 Manually Opened Petapahan VCB fdr#6 Maintain Tank Level due to Petapahan GS WIP,s OFF Cause: Emergency... |  | 1 | 1:34 | Night | Wednesday | 2019 | 7
11618 | 2019-07-24 15:23 | 2019-07-24 15:23 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Duri Community feeder #3 T/R 1X. Not Checked yet. |  | 1 | 15:23 | Afternoon | Wednesday | 2019 | 7
11619 | 2019-07-24 15:23 | 2019-07-27 15:17 | 13.8KV DURI COMMUNITY FEEDER #3 | Fair | Unidentified | 0 | Checked and found ACB DCM fdr #3 T/R 1x, ctr: 93 - 94, R/F 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 15:23 | Afternoon | Wednesday | 2019 | 7
11620 | 2019-07-24 15:24 | 2019-07-24 15:24 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 38 | Pematang 13.8 Kv OCB Feeder #1 T/R 1X. Pematang Feeder #2 load Dropped 68 A (107-39 A). Not Checked yet. |  | 1 | 15:24 | Afternoon | Wednesday | 2019 | 7
11621 | 2019-07-24 15:24 | 2019-07-24 15:24 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 38 | Checked and found PMT fdr #1 T/R 1x, ctr: 179 - 180, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 15:24 | Afternoon | Wednesday | 2019 | 7
11622 | 2019-07-25 08:48 | 2019-07-25 08:48 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 29 | C Duri feeder #1 load dropped 48A (138-90A). Not checked yet. |  | 1 | 8:48 | Morning | Thursday | 2019 | 7
11623 | 2019-07-25 08:48 | 2019-07-30 13:49 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 29 | Checked and found: 5441-R.41-AW-62 T/R, Counter : 324 - 325, Relay Flag : 50N Patrolled the line found : Nothing Found Cause : Unidentified |  | 1 | 8:48 | Morning | Thursday | 2019 | 7
11624 | 2019-07-25 10:29 | 2019-07-25 10:29 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified (Fuse) | 18 | Libo feeder #1 load dropped 25A (69-44A). Not checked yet. |  | 1 | 10:29 | Morning | Thursday | 2019 | 7
11625 | 2019-07-25 10:29 | 2019-07-30 15:29 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified (Fuse) | 18 | Checked and found: LBO1-W.SELBO09 ON/L, Counter : 0 - 0, Relay Flag : NONE Patrolled the line found : Overload TX Cause : Unidentified (Fuse) |  | 1 | 10:29 | Morning | Thursday | 2019 | 7
11626 | 2019-07-25 11:37 | 2019-07-25 11:37 | 13.8KV 5B FEEDER #2 | Fair | Planned Maintenance | 183 | 11:37 Manually opened 5B OCB feeder #2. Due to replace Recloser on pole 5C-07. 13:34 Manually closed 5B OCB feeder #2. Cause: Plan Maintenance. |  | 1 | 11:37 | Morning | Thursday | 2019 | 7
11627 | 2019-07-25 13:33 | 2019-07-25 13:33 | 13.8KV NELLA FEEDER #2 | Fair | Unidentified | 41 | 13:33 Nella VCB fdr#2 T/O (in block position). Due to PT KRS loading and unloading at Bangko northern 24". 14:06 Manually blocked and closed Nella VCB fdr#2 --> OK (still in block position). 14:40 Checked and found Nella VCB fdr#2 T/O. Counter: 337-338 R/F: 51@1. Not patrolled yet. |  | 1 | 13:33 | Afternoon | Thursday | 2019 | 7
11628 | 2019-07-25 13:33 | 2019-07-28 08:33 | 13.8KV NELLA FEEDER #2 | Fair | Unidentified | 41 | Checked and found : NLASB-13.8VCB2 T/SO, Counter : 337 - 338, Relay Flag : 51N. Patrolled the line found : None Cause : Unidentified |  | 1 | 13:33 | Afternoon | Thursday | 2019 | 7
11629 | 2019-07-25 13:48 | 2019-07-25 13:48 | MINAS SWITCH GEAR | Fair | Unidentified | 0 | Minas ACB#21 (Minas- Rumbai 44KV Line) T/R 1x. Counter: 90-91 R/F: 51G. Not patrolled yet. |  | 1 | 13:48 | Afternoon | Thursday | 2019 | 7
11630 | 2019-07-25 13:48 | 2019-07-26 14:15 | MINAS SWITCH GEAR | Fair | Unidentified | 0 | Checked and found: MNSSG-13.8ACB21 T/R, Counter : 90 - 91, Relay Flag : 51G Patrolled the line found : Nothing Found Cause : Unidentified |  | 1 | 13:48 | Afternoon | Thursday | 2019 | 7
11631 | 2019-07-26 15:37 | 2019-07-26 15:37 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Dead End Insulator | 0 | C Duri ACB #23 (feeder #6) T/R 1x. Checked and found C Duri ACB #23 (feeder #6) T/R 1x. R/F: 51N Counter: 502-503. Not patrolled yet. |  | 1 | 15:37 | Afternoon | Friday | 2019 | 7
11632 | 2019-07-26 15:37 | 2019-07-30 13:51 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Dead End Insulator | 0 | Checked and found: CDRSG-13.8ACB23 T/R, Counter : 503 - 504, Relay Flag : 51N. Patrolled the line found : Deadend Flash Cause : Dead End Insulator |  | 1 | 15:37 | Afternoon | Friday | 2019 | 7
11633 | 2019-07-27 13:14 | 2019-07-27 13:14 | 13.8KV KETIGUL FEEDER#2 | Fair | Transformer Failure | 0 | 13:14 Ketigul feeder #2 load dropped 12A (267-255A). 14:26 Checked and found Recloser: 29-AK-24 T/LO Counter: 240-244. Patrolled the line nothing found. 15:10 Block and closed Recloser: 29-AK-24 but pumping. Back on patrol. 17:05 Block and closed Recloser: 29-AK-24, OK 17:28 Back load dropped 22 A (267 - 245 A) Checked and found RCL 29-AK-24 T/SO 18:10 Re-patrolled the line but found nothing Block and close RCL 29-AK-24, but failed 19:39 Close RCL 29-AK-24 by direct DC trigger (approved by TL/MGR OPS PGT) Reported b/o fuse at 1250 kVA TX at Pager GS, @1 Replaced the b/o fuse and then close the fuse holder, suddenly the others fuses are b/o (suspect TX failure) Suggest Pager GS to close the Tie Breaker (waiting for FUM team) Continue to check the 1250 kVA TX tomorrow. Cause: Transformer Failure |  | 1 | 13:14 | Afternoon | Saturday | 2019 | 7
11634 | 2019-07-28 02:25 | 2019-07-28 02:25 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | N Duri fdr #1 Load Dropped 66 A (196 - 130 A) Not Checked Yet |  | 1 | 2:25 | Night | Sunday | 2019 | 7
11635 | 2019-07-28 02:25 | 2019-07-30 13:53 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found: NDRSB-13.8VCB1 T/R, Counter : 311 - 312, Relay Flag : 50 Patrolled the line found : Nothing Found Cause : Unidentified |  | 1 | 2:25 | Night | Sunday | 2019 | 7
11636 | 2019-07-28 08:45 | 2019-07-28 08:45 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Unidentified | 0 | C Duri ACB #28 (feeder #16) T/R 1x. Counter: 357-358 R/F: 51@1,@2. Not oatrolled yet. |  | 1 | 8:45 | Morning | Sunday | 2019 | 7
11637 | 2019-07-28 08:45 | 2019-07-30 13:58 | 13.8KV CENTRAL DURI FEEDER #16 | Cloudy | Unidentified | 0 | Checked and found: CDRSG-13.8ACB28 T/R, Counter : 357 - 358, Relay Flag : 51N. Patrolled the line found : Nothing Found Cause : Unidentified |  | 1 | 8:45 | Morning | Sunday | 2019 | 7
11638 | 2019-07-28 15:57 | 2019-07-28 15:57 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Dead End Insulator | 0 | C Duri ACB #23 (feeder #6) T/R 1x. Counter: 503-504 R/F: 50@1. Not oatrolled yet. |  | 1 | 15:57 | Afternoon | Sunday | 2019 | 7
11639 | 2019-07-28 15:57 | 2019-07-30 14:00 | 13.8KV CENTRAL DURI FEEDER #6 | Fair | Dead End Insulator | 0 | Checked and found: CDRSG-13.8ACB23 T/R, Counter : 357 - 358, Relay Flag : 51N. Patrolled the line found : Deadend Flash Cause : Dead End Insulator |  | 1 | 15:57 | Afternoon | Sunday | 2019 | 7
11640 | 2019-07-29 01:45 | 2019-07-29 01:45 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 7 | Ketigul 13.8KV VCB fdr #3 T/R 1X. Not checked yet. |  | 1 | 1:45 | Night | Monday | 2019 | 7
11641 | 2019-07-29 01:45 | 2019-07-31 15:01 | 13.8KV KETIGUL FEEDER#3 | Fair | Unidentified | 7 | Checked and found: PKTGL-13.8VCB3 T/R, Counter : 217 - 218, Relay Flag : 51N. Patrolled the line and found : No Finding Cause : Unidentified |  | 1 | 1:45 | Night | Monday | 2019 | 7
11642 | 2019-07-29 10:48 | 2019-07-29 10:48 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 24 | 10:48 Manually opened 6D OCB feeder #1. for replacing to LBS. 5C-59. 11:58 Manually closed 6D OCB feeder #1. Cause: Planned maintenance. |  | 1 | 10:48 | Morning | Monday | 2019 | 7
11643 | 2019-07-29 14:30 | 2019-07-29 14:30 | 13.8KV 6D FEEDER #1 | Fair | Planned Maintenance | 59 | 14:30 Manually open LBS: 5C-59 D/S 6D feeder #1. for replacing Recloser on pole 5C-42. 16:42 Manually closed LBS: 5C-59. Cause: Plan maintenance. |  | 1 | 14:30 | Afternoon | Monday | 2019 | 7
11644 | 2019-07-30 06:14 | 2019-07-30 06:14 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | ND feeder #2 T/R 1x Not Checked Yet |  | 1 | 6:14 | Morning | Tuesday | 2019 | 7
11645 | 2019-07-30 06:14 | 2019-07-31 17:00 | 13.8KV NORTH DURI FEEDER #2 | Fair | Unidentified | 0 | Checked and found: NDRSB-13.8VCB2 T/R, Counter : 281 - 282, Relay Flag : 51 Patrolled the line found : none Cause : Unidentified |  | 1 | 6:14 | Morning | Tuesday | 2019 | 7
11646 | 2019-07-30 06:59 | 2019-07-30 06:59 | 13.8KV MENGGALA FEEDER #1 | Fair | Tree | 0 | 06:59 Menggala fdr #1 load dropped 114 A (174 - 60 A). Menggala GFPC T/R 1x. 16:10 Checked and found Recloser: 19-AN-04 T/R 1x Counter: 638-639. Patrolled the line nothing found. Cause: |  | 1 | 6:59 | Morning | Tuesday | 2019 | 7
11647 | 2019-07-30 06:59 | 2019-02-08 11:05 | 13.8KV MENGGALA FEEDER #1 | Fair | Tree | 0 | Checked and found: MGLSB-13.8OCB1 T/R, Counter : 100 - 101, Relay Flag : 51N. Patrolled the line found: Pohon Sawit Menyentuh Line Ujung nya terbakar Cause : Tree |  | 1 | 6:59 | Morning | Tuesday | 2019 | 7
11648 | 2019-07-30 10:05 | 2019-07-30 10:05 | 13.8KV KETIGUL FEEDER#2 | Fair | Planned Maintenance | 4 | 10:05 Open Hot line clamp on pole 29-AF-12 D/S Ketigul feeder #2. For replacing @1 broken dead end insulator on pole 29-AN-31. (well Pagar #32 shut off during this job) 11:27 Close Hot line clamp on pole 29-AF-12. and then energized well Pagar #32. Cause: Plan maintenance. |  | 1 | 10:05 | Morning | Tuesday | 2019 | 7
11649 | 2019-07-30 10:09 | 2019-07-30 10:09 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Lightning Arrester | 100 | CKBS VCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 10:09 | Morning | Tuesday | 2019 | 7
11650 | 2019-07-30 10:09 | 2019-07-31 14:15 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Lightning Arrester | 100 | Checked and found: CKBSSB-13.8VCB1 T/R, Counter : 242 - 243, Relay Flag : NONE. Patrolled the line found : LA BROKEN AT KB-287 Cause : Lightning Arrester |  | 1 | 10:09 | Morning | Tuesday | 2019 | 7
11651 | 2019-07-30 15:30 | 2019-07-30 15:30 | MINAS POWER PLANT |  |  | - | 15:30 MGT-6 S/U and then online at 15:58 for running test. |  | 1 | 15:30 | Afternoon | Tuesday | 2019 | 7
11652 | 2019-07-30 16:05 | 2019-07-30 16:05 | MINAS POWER PLANT |  |  | - | MGT-7 Offline and then S/D the unit for stand by |  | 1 | 16:05 | Afternoon | Tuesday | 2019 | 7
11653 | 2019-07-30 18:33 | 2019-07-30 18:33 | MINAS POWER PLANT |  |  | - | MGT-6 tripped by alarm Generator Door Close (CO2) |  | 1 | 18:33 | Afternoon | Tuesday | 2019 | 7
11654 | 2019-07-30 19:10 | 2019-07-30 19:10 | 13.8KV 5B FEEDER #2 | Fair | Pin Insulator | 93 | 17:10 5B fdr #2 load dropped 121A (145-24A). (No alarm appeared). 20:12 Reported no power d/s of 5B fdr #2 (19 wells found off) 22:00 Checked and found RCL 5C-07 T/SO, ctr: 182 (not change) Blocked and close RCL 5C-07, OK and then release the block Cause: Not Patrolled Yet |  | 1 | 19:10 | Night | Tuesday | 2019 | 7
11655 | 2019-07-30 19:10 | 2019-02-08 10:35 | 13.8KV 5B FEEDER #2 | Fair | Pin Insulator | 93 | Checked and found: 5442-R.5C07 T/SO, Counter : 182 - 182, Relay Flag : NONE. Patrolled the line found : Broken Pin Cause : Pin Insulator |  | 1 | 19:10 | Night | Tuesday | 2019 | 7
11656 | 2019-07-30 19:16 | 2019-07-30 19:16 | MINAS POWER PLANT |  |  | - | S/U MGT-6 and then Online at 19:30 for Running Test |  | 1 | 19:16 | Night | Tuesday | 2019 | 7
11657 | 2019-07-31 11:13 | 2019-07-31 11:13 | 13.8KV 3D FEEDER #3 | Fair | Tree | 11 | 3D fdr#3 T/R 2x. Not checked yet. |  | 1 | 11:13 | Morning | Wednesday | 2019 | 7
11658 | 2019-07-31 11:13 | 2019-02-08 10:57 | 13.8KV 3D FEEDER #3 | Fair | Tree | 11 | Checked and found: 3DSB-13.8OCB3 T/R, Counter : 491 - 494, Relay Flag : 51. Patrolled the line found : Pemotongan kayu oleh warga menyentuh powerline Cause : Tree |  | 1 | 11:13 | Morning | Wednesday | 2019 | 7
11659 | 2019-07-31 11:13 | 2019-07-31 11:13 | 13.8KV 3D FEEDER #2 | Fair | Normal Condition | 2 | 3D fdr#2 load dropped 104A (160-56A). Not checked yet. |  | 1 | 11:13 | Morning | Wednesday | 2019 | 7
11660 | 2019-07-31 11:13 | 2019-02-08 10:14 | 13.8KV 3D FEEDER #2 | Fair | Normal Condition | 2 | Checked and found: RCL 2F-11C None, Counter : 644 - 644, Relay Flag : NONE Patrolled the line found : Nothing Found Cause : Normal Condition |  | 1 | 11:13 | Morning | Wednesday | 2019 | 7
11661 | 2019-07-31 11:13 | 2019-07-31 11:13 | 13.8KV 3D FEEDER #4 | Fair | Normal Condition | 0 | 3D fdr#4 load dropped 83A (164-81A). Not checked yet. |  | 1 | 11:13 | Morning | Wednesday | 2019 | 7
11662 | 2019-07-31 11:13 | 2019-02-08 10:21 | 13.8KV 3D FEEDER #4 | Fair | Normal Condition | 0 | Checked and found: 5442-R.2D38 None, Counter : 87 - 87, Relay Flag : NONE Patrolled the line found : Nothing Found Cause : Normal Condition |  | 1 | 11:13 | Morning | Wednesday | 2019 | 7
11663 | 2019-07-31 12:02 | 2019-07-31 12:02 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 29 | Pematang fdr#1 T/R 1x. Pematang fdr#2 load dropped 17A (105-88A). Not checked yet. |  | 1 | 12:02 | Afternoon | Wednesday | 2019 | 7
11664 | 2019-07-31 12:02 | 2019-03-08 07:50 | 13.8KV PEMATANG FEEDER #1 | Fair | Unidentified | 29 | Checked and found: PMTSB-13.8OCB1 T/R, Counter : 180 - 181, Relay Flag : 51N. Patrolled the line found : No Finding Cause : Unidentified |  | 1 | 12:02 | Afternoon | Wednesday | 2019 | 7
11665 | 2019-07-31 20:35 | 2019-07-31 20:35 | MINAS POWER PLANT |  |  | - | 20:35 Offline MGT #11 and then S/D the unit. Due to 480 V lost. |  | 1 | 20:35 | Night | Wednesday | 2019 | 7
11666 | 2019-07-31 21:00 | 2019-07-31 21:00 | MINAS POWER PLANT |  |  | - | 21:00 S/U MGT #9 and then Online the unit at 21:27. |  | 1 | 21:00 | Night | Wednesday | 2019 | 7
11667 | 2019-01-08 13:50 | 2019-01-08 13:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 312 | 13:50 Manually open Recloser 41- AW - 62 (C.Duri fdr#1). Replace recloser 39-AV-36. Pole sleeve 40-Ax-09 & 39-AV-32. 17:28 Closed the Recloser after finished the jobs Cause : Planned maintenance. |  | 1 | 13:50 | Afternoon | Tuesday | 2019 | 1
11668 | 2019-01-08 14:37 | 2019-01-08 14:37 | MINAS POWER PLANT |  |  | - | 14:37 MGT #8 S/U ,then online at 14:53. After repair gas control Valve. |  | 1 | 14:37 | Afternoon | Tuesday | 2019 | 1
11669 | 2019-01-08 15:03 | 2019-01-08 15:03 | MINAS POWER PLANT |  |  | - | 15:03 MGT#6 S/D for S/B. |  | 1 | 15:03 | Afternoon | Tuesday | 2019 | 1
11670 | 2019-02-08 17:01 | 2019-02-08 17:01 | 13.8KV 6DN FEEDER #1 | Fair | Lightning | 62 | 6DN fdr#1 load dropped 111A (149-38A). Not checked yet. |  | 1 | 17:01 | Afternoon | Friday | 2019 | 2
11671 | 2019-02-08 17:01 | 2019-03-08 17:11 | 13.8KV 6DN FEEDER #1 | Fair | Lightning | 62 | Checked & found Recl 5E 83 T/R 1x, Ctr: 32-33, R/F: 51 Patrolled the Line, but found nothing Cause : Lightning |  | 1 | 17:01 | Afternoon | Friday | 2019 | 2
11672 | 2019-03-08 05:21 | 2019-03-08 05:21 | 13.8KV 5B FEEDER #2 | Fair | Lightning | 0 | 5B feeder #2 load dropped 132A (164-32A). Not checked yet. |  | 1 | 5:21 | Morning | Friday | 2019 | 3
11673 | 2019-03-08 05:21 | 2019-03-08 13:15 | 13.8KV 5B FEEDER #2 | Fair | Lightning | 0 | Checked and found Recloser: 5C-07 T/R 1x Counter: 190-191. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 5:21 | Morning | Friday | 2019 | 3
11674 | 2019-03-08 05:21 | 2019-06-08 08:47 | 13.8KV 5B FEEDER #2 | Fair | Lightning | 0 | Checked and found: 5442-R.5C07 T/R, Counter : 190 - 191, Relay Flag : 51. Patrolled the line found : NOT FOUND Cause : Lightning |  | 1 | 5:21 | Morning | Friday | 2019 | 3
11675 | 2019-03-08 18:18 | 2019-03-08 18:18 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Fair | Unidentified | 186 | CKBS fdr#5 T/R 1x. Not checked yet. |  | 1 | 18:18 | Afternoon | Friday | 2019 | 3
11676 | 2019-04-08 08:43 | 2019-04-08 08:43 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | - | Rangau fdr #2 load dropped 117A. Not checked yet. |  | 1 | 8:43 | Morning | Monday | 2019 | 4
11677 | 2019-04-08 08:43 | 2019-06-08 16:50 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | - | Checked and found: 5440-R.23BD01 T/R, Counter : 396 - 398, Relay Flag : 51G Patrolled the line found : No Finding Cause : Unidentified |  | 1 | 8:43 | Morning | Monday | 2019 | 4
11678 | 2019-04-08 10:16 | 2019-04-08 10:16 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Lightning Arrester | 127 | CKBS fdr#1 T/R 1x. Not checked yet. |  | 1 | 10:16 | Morning | Monday | 2019 | 4
11679 | 2019-04-08 10:16 | 2019-05-08 16:14 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Lightning Arrester | 127 | Checked and found: CKBSSB-13.8VCB1 T/R, Counter : 243 - 244, Relay Flag : 50N. Patrolled the line found : Lightning Arrester Cause : Lightning Arrester |  | 1 | 10:16 | Morning | Monday | 2019 | 4
11680 | 2019-05-08 09:29 | 2019-05-08 09:29 | 13.8KV LIBO FEEDER #1 | Fair | Construction Job | 25 | 09:29 Opened LBS: 34-CC-1B D/S Libo feeder #1. Due to replacement well South east Libo #02 from gas well to oil well. 5 Wells were OFF during this job (South east Libo #44 ,29 , 46 ,09 ,50) 10:26 Closed LBS: 34-CC-1B. Cause: Construction job. |  | 1 | 9:29 | Morning | Wednesday | 2019 | 5
11681 | 2019-06-08 00:05 | 2019-06-08 00:05 | 13.8KV 8C FEEDER #5 | Fair | Unidentified | 0 | 8C VCB feeder #5 T/R 1x. --> WIP GS #2. 8C feeder #6 load dropped 50A (190-140A). --> WIP GS #2. Not checked yet. |  | 1 | 0:05 | Night | Saturday | 2019 | 6
11682 | 2019-06-08 00:05 | 2019-07-08 09:23 | 13.8KV 8C FEEDER #5 | Fair | Unidentified | 0 | Checked and found 8C fdr #5 T/R 1x, ctr: 234 - 235, R/F: 50N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 0:05 | Night | Saturday | 2019 | 6
11683 | 2019-06-08 06:30 | 2019-06-08 06:30 | 13.8KV DURI FIELD FEEDER #3 | Fair | Lightning Arrester | 21 | 06:30 D.Field fdr#3 laod drooped 10A(46-36A). It was reported no power at D.Field road #7 area #1 by HO DSC.( Jasman ). Not checked yet. |  | 1 | 6:30 | Morning | Saturday | 2019 | 6
11684 | 2019-06-08 06:30 | 2019-09-08 08:27 | 13.8KV DURI FIELD FEEDER #3 | Fair | Lightning Arrester | 21 | Checked and found RCK 01-7-01 T/R 1x, ctr: 1315-1316, R/F: None Patrolled the line and found broken LA (jumper) o/p 01-7-08 Cause : Lightning Arrester |  | 1 | 6:30 | Morning | Saturday | 2019 | 6
11685 | 2019-06-08 06:35 | 2019-06-08 06:35 | 13.8KV 6D FEEDER #2 | Foggy and Smoke | Unidentified | 22 | 6D OCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 6:35 | Morning | Saturday | 2019 | 6
11686 | 2019-06-08 06:35 | 2019-07-08 09:33 | 13.8KV 6D FEEDER #2 | Foggy and Smoke | Unidentified | 22 | Checked and found 6D fdr #2 T/R 1x, ctr: 249 - 250, R/F: 50N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 6:35 | Morning | Saturday | 2019 | 6
11687 | 2019-06-08 13:45 | 2019-06-08 13:45 | 13.8KV CENTRAL KOTABATAK FEEDER #1 | Fair | Planned Maintenance | 119 | 13:45 Blocked CKB fdr#1. O/C fuse o/p CU-03 to replace broken LA and Pin. Well infect down 5 wells.(287,288,77,324,290). caused : Plant maintenance. |  | 1 | 13:45 | Afternoon | Saturday | 2019 | 6
11688 | 2019-06-08 18:51 | 2019-06-08 18:51 | 13.8KV KETIGUL FEEDER#3 | Foggy and Smoke | Unidentified | 144 | 18:51 Ketigul VCB feeder #3 T/O. 20:37 Checked and found Ketigul VCB feeder #3 T/LO. Counter: 218-222 R/F: 51N. Patrolled the line nothing found. 23:04 Manually blocked and closed Ketigul VCB feeder #3 --> OK. and then released the block. Cause: Unidentified. |  | 1 | 18:51 | Afternoon | Saturday | 2019 | 6
11689 | 2019-06-08 18:51 | 2019-06-08 18:51 | 13.8KV KETIGUL FEEDER#1 | Foggy and Smoke | Normal Condition | - | Ketigul feeder #1 load dropped 105A (116-11A). Not checked yet. |  | 1 | 18:51 | Afternoon | Saturday | 2019 | 6
11690 | 2019-06-08 18:51 | 2019-11-08 10:32 | 13.8KV KETIGUL FEEDER#1 | Foggy and Smoke | Normal Condition | - | Checked and found all in Normal Condition Suspect follow another outage, no need to patrolled Cause : Normal Condition |  | 1 | 18:51 | Afternoon | Saturday | 2019 | 6
11691 | 2019-06-08 18:51 | 2019-06-08 18:51 | 13.8KV KETIGUL FEEDER#2 | Foggy and Smoke | Normal Condition | 44 | Ketigul feeder #2 load dropped 77A (83-5A). Not checked yet. |  | 1 | 18:51 | Afternoon | Saturday | 2019 | 6
11692 | 2019-06-08 18:51 | 2019-11-08 10:34 | 13.8KV KETIGUL FEEDER#2 | Foggy and Smoke | Normal Condition | 44 | Checked and found all in Normal Condition Suspect follow another outage, o need to patrolled Cause : Normal Condition |  | 1 | 18:51 | Afternoon | Saturday | 2019 | 6
11693 | 2019-07-08 23:59 | 2019-07-08 23:59 | CPI POWER SYSTEM |  |  | - | 23:59:59 CPI Power System Normal Operation. |  | 1 | 23:59 | Night | Monday | 2019 | 7
11694 | 2019-08-08 04:34 | 2019-08-08 04:34 | 13.8KV ROKAN FEEDER #2 | Fair | Dead End Insulator | 17 | Rokan VCB Fdr#2 T/R 1x Not checked yet |  | 1 | 4:34 | Morning | Thursday | 2019 | 8
11695 | 2019-08-08 04:34 | 2019-09-08 08:30 | 13.8KV ROKAN FEEDER #2 | Fair | Dead End Insulator | 17 | Checked and found: RKNSB-13.8VCB2 T/R, Counter : 1301 - 1302, Relay Flag : 51. Patrolled the line found : Dead End Pecah Cause : Dead End Insulator |  | 1 | 4:34 | Morning | Thursday | 2019 | 8
11696 | 2019-08-08 09:42 | 2019-08-08 09:42 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 65 | KTGL feeder #2 T/R 1x Not Checked Yet |  | 1 | 9:42 | Morning | Thursday | 2019 | 8
11697 | 2019-08-08 09:42 | 2019-11-08 10:38 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 65 | Checked and found KTGL VCB fdr #2 T/R 1x, ctr: 344 - 345, R/F: 51N Patrolled the line and found dead animal (monkey) at Pager #05 Cause : Animal (monkey) |  | 1 | 9:42 | Morning | Thursday | 2019 | 8
11698 | 2019-09-08 10:58 | 2019-09-08 10:58 | 13.8KV LIBO FEEDER #1 | Fair | Construction Job | 5 | 10:58 Manual Open LBS 34-CC-1D ( LBO fdr #1) Tie-in power line for reactive well N-LBO #02 (gas to Oil) 3 wells will off during this job (SE-LBO #09, #29, #6) Cause: Construction Job (project) |  | 1 | 10:58 | Morning | Sunday | 2019 | 9
11699 | 2019-09-08 14:43 | 2019-09-08 14:43 | NORTH RUMBAI SUBSTATION | Fair | Under investigation | - | 14:34 appeared Alarm Low Voltage at 4.6KV at N. Rumbai. Load dropped to Zero at N. Rumbai fdr #1, #2. (PT BKP working at N. Rumbai Substation). 15:41 Checked and found N. Rumbai 44KV OCB #1 T/O ctr: 72-73 R/F: 87T. Checked TX Condition, Normal. Manually Open N. Rumbai fdr #1, ---->Blocked and Closed at 15:53 ctr: 410-411. Manually Open N. Rumbai fdr #2, ---->Blocked and Closed at 15:54 ctr: 361-362. 15:45 Blocked 13.8KV Minas- Rumbai ACB #21, and normalized at 16:10. Cause: Under investigation. |  | 1 | 14:43 | Afternoon | Sunday | 2019 | 9
11700 | 2019-09-08 14:50 | 2019-09-08 14:50 | 13.8KV NELLA FEEDER #2 | Fair | Planned Maintenance | 35 | 14:50 Manually Open Recl. 20-V-12 D/S Nella fdr #2. Replaced @2, @3 broken Pin Insulator o/p: 20-V-09. 15:26 Closed Recl. 20-V-12 . Cause: Plan Maintenance. |  | 1 | 14:50 | Afternoon | Sunday | 2019 | 9
11701 | 2019-10-08 18:45 | 2019-10-08 18:45 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Guy Wire | 184 | 18:45 PTP New feeder #4 dropped 36A (172 - 136 A) 20:45 SPS team reported no power at TOPAS Field 21:30 PTP FO and TDO team conform will check the problem tomorrow. TOPAS field leave in down condition. August, 11th, 2019 09:18 Checked and found RCL 08-CW-01 T/SO, counter display was broken. 09:21 Blocked and closed the RCL 08-CW-01, OK 12:00 Re-patrol the line and found broken guy wire at TOPAS #02 12:34 Manual open RCL 28-CW-01 (PTP fdr #4) for MTCE team to dismantle/remove broken guy wire from TOP TOPAS #02 Cause: Broken Guy Wire |  | 1 | 18:45 | Afternoon | Tuesday | 2019 | 10
11702 | 2019-10-08 18:45 | 2019-11-08 12:34 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Guy Wire | 184 | 12:34 Manual open RCL 28-CW-01 (PTP fdr #4) for MTCE team to dismantle/remove broken guy wire from TOP TOPAS #02 Cause: Broken Guy Wire. |  | 1 | 18:45 | Afternoon | Tuesday | 2019 | 10
11703 | 2019-11-08 05:25 | 2019-11-08 05:25 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 131 | Bangko Fdr#4 Load dropped 70A(176-106A) Bangko GFPC T/R 1x Not checked yet |  | 1 | 5:25 | Morning | Friday | 2019 | 11
11704 | 2019-11-08 05:25 | 13/08/2019 09:20 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 131 | Checked and found: GFPC T/R, Counter : 221 - 222, Relay Flag : 51N Patrolled the line found : None Operated Device : 5440-R.25Z07 T/R Counter : 223 - 224 Relay Flag : 51N Finding Patrol : Dead end insulator Broken 5% layer 2 Cause : Unidentified |  | 1 | 5:25 | Morning | Friday | 2019 | 11
11705 | 2019-11-08 07:31 | 2019-11-08 07:31 | 13.8KV MENGGALA FEEDER #1 | Cloudy | Unidentified | 261 | 07:31 MGL GFPC T/R 1x MGL fdr #1 load dropped 134 A (160 - 26 A) 10:09 Checked and found RCL 19-AN-04 T/LO, ctr: 639 - 648 Patrolled the line but found nothing 11:08 Blocked and Close RCL 19-AN-04, OK then release the block. Cause: Unidentified |  | 1 | 7:31 | Morning | Friday | 2019 | 11
11706 | 2019-11-08 08:59 | 2019-11-08 08:59 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | - | SINTONG feeder #2 load dropped 90A (192 - 102 A) Cause: Not Checked Yet |  | 1 | 8:59 | Morning | Friday | 2019 | 11
11707 | 2019-11-08 08:59 | 13/08/2019 09:15 | 13.8KV SINTONG FEEDER #2 | Fair | Unidentified | - | Checked and found: GFPC T/R, Counter : 1152 - 1155, Relay Flag : 51N Patrolled the line found : None Operated Device : 5440-R.28AF17 T/R Counter : 460 - 461 Relay Flag : 51N Finding Patrol : Dead end insulator flash over layer 1 Cause : Unidentified |  | 1 | 8:59 | Morning | Friday | 2019 | 11
11708 | 2019-11-08 12:34 | 2019-11-08 12:34 | 13.8KV NEW KOTABATAK FEEDER #4 | Fair | Planned Maintenance | 169 | 12:34 Manually Opened Recl 28 CW 01 (Petapahan Fdr#4) to Remove Broken Gay Wire O/Top Well Topaz #02 13:05 Closed back after finished the Jobs. Cause: Planned Maintenance |  | 1 | 12:34 | Afternoon | Friday | 2019 | 11
11709 | 2019-12-08 10:00 | 2019-12-08 10:00 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 370 | 10:00 Manual Open RCL 8D-18A (8C feeder #3) MTCE team cutting jumper to support toll road activities. Cutting 2 spend Conductor (o/p:8C-66 to 8C-68). 14:40 Close RCL 8D-18A. 16:46 Closed LBS: 8C-57 to supply power to wells: 8C-58N and 8C-48E d/s: 8C fdr #6. Cause: Planned Maintenance. |  | 1 | 10:00 | Morning | Sunday | 2019 | 12
11710 | 2019-12-08 15:56 | 2019-12-08 15:56 | 13.8KV PETAPAHAN FEEDER #4 | Fair | Planned Maintenance | 6 | 15:56 Manually Open Recl.: 28-CW-01 d/s: Petapahan fdr #4. Reoaired Guy wire at TOP of Topas # 02. 16:16 Closed Recl.: 28-CW-01. Cause: Plan Maintenance. |  | 1 | 15:56 | Afternoon | Sunday | 2019 | 12
11711 | 2019-08-13 07:10 | 2019-08-13 07:10 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 30 | Pinang VCB fdr #1 T/R 1x Cause: Not Checked Yet |  | 1 | 7:10 | Morning | Tuesday | 2019 | 8
11712 | 2019-08-13 07:10 | 2019-08-16 14:42 | 13.8KV PINANG FEEDER #1 | Fair | Unidentified | 30 | Checked and found PINANG VCB fdr#1 T/R 1x, ctr: 450 - 451, R/F: 51N Patrolled the line and found broken pin insulator 10% on @2 o/p 11-D-79 Cause : Unidentified |  | 1 | 7:10 | Morning | Tuesday | 2019 | 8
11713 | 2019-08-13 09:35 | 2019-08-13 09:35 | 44KV PEMATANG MAIN - PETANI LINE | Cloudy | Tree | 80 | 44KV Pematang main - Petani Line OCB #1 T/R 1X. Not checked yet. |  | 1 | 9:35 | Morning | Tuesday | 2019 | 8
11714 | 2019-08-13 09:35 | 2019-08-16 10:29 | 44KV PEMATANG MAIN - PETANI LINE | Cloudy | Tree | 80 | Checked and found PMT Main fdr #1 (line to PTN) T/R 1x, R/F: 50N Patrolled the line and found bamboo tree touch to power line @1 at PTN #23 Cause : Tree |  | 1 | 9:35 | Morning | Tuesday | 2019 | 8
11715 | 2019-08-13 14:44 | 2019-08-13 14:44 | 13.8KV 5B FEEDER #2 | Fair | Planned Maintenance | 92 | 14:44 Manual Open RCL 5C-07 (5B fdr #2), closed at 16:10 MTCE team to replace pin insulator to pin post insulator Cause: Planned Maintenance |  | 1 | 14:44 | Afternoon | Tuesday | 2019 | 8
11716 | 2019-08-14 02:20 | 2019-08-14 02:20 | 13.8KV ROKAN FEEDER #2 | Fair | Powerline - Conductor | 277 | 02:20 Rokan VCB Fdr#2 T/LO 03:50 Checked & found Ctr: 1302-1306, R/F: 50 @1@2@3 Patrolled the Line, But found nothing 04:38 Block & Closed Rokan VCB fdr#2, but T/O again Rack VCB to TEST Position and then function test, but the VCB T/O. Transfer RKN fdr #2 to RKN fdr #4 by closed LBS RT-01, but RKN fdr #4 T/O Open the LBS RT-01 and then close RKN fdr #4, OK 08:27 Continued Patrolled the Line and then found static wire Touches the Conductor o/p 28-AV-58. 08:35 Manually block and close RKN fdr #2, OK and then release the block. Cause: Conductor. |  | 1 | 2:20 | Night | Wednesday | 2019 | 8
11717 | 2019-08-14 09:30 | 2019-08-14 09:30 | 13.8KV 8D FEEDER #3 | Fair | Planned Maintenance | 39 | 09:30 Manual Open RCL 8D-30 (8D fdr #3), closed at 11:30, ctr: 24 Replace Pin Insulator to Pin Post o/p 9D-122 Cause: Planned Maintenance |  | 1 | 9:30 | Morning | Wednesday | 2019 | 8
11718 | 2019-08-14 15:35 | 2019-08-14 15:35 | 4.16KV SO RUMBAI FEEDER #3 | Fair | Planned Maintenance | 0 | 15:35 Manual Open S-RBI feeder #1, closed at 15:44, ctr: 134 Replace b/o fuse for 50 kVA TX o/p 3RF-06 Cause: Planned Maintenance |  | 1 | 15:35 | Afternoon | Wednesday | 2019 | 8
11719 | 2019-08-14 16:19 | 2019-08-14 16:19 | 13.8KV BATANG FEEDER #3 | Rain | Lightning | 27 | Batang 13.8 KV feeder #3 T/R 1X. Not checked yet. |  | 1 | 16:19 | Afternoon | Wednesday | 2019 | 8
11720 | 2019-08-14 16:19 | 2019-08-19 08:52 | 13.8KV BATANG FEEDER #3 | Rain | Lightning | 27 | Checked and found BTG fdr #3 T/R 1x, ctr: 381 - 382, R/F: 51P @1 @2 @3 Patrolled the line and found broken LA @1 @2 @3 o/p 40-AJ-11 Cause : Lightning |  | 1 | 16:19 | Afternoon | Wednesday | 2019 | 8
11721 | 2019-08-15 08:52 | 2019-08-15 08:52 | 13.8KV MENGGALA FEEDER #1 | Rain | Tree | 25 | 08:52 Menggala OCB fdr #1 T/R 1x Menggala GFPC T/R 1x Not checked yet. |  | 1 | 8:52 | Morning | Thursday | 2019 | 8
11722 | 2019-08-15 08:52 | 2019-08-17 09:54 | 13.8KV MENGGALA FEEDER #1 | Rain | Tree | 25 | Checked and found MGL fdr #1 T/R 3x, ctr: 570 - 573, R/F: 51N Patrolled the line and found high trees touch the power line on @1 o/p 20-AN-04 Cause : Tree |  | 1 | 8:52 | Morning | Thursday | 2019 | 8
11723 | 2019-08-15 08:52 | 2019-08-15 08:52 | 13.8KV MENGGALA FEEDER #2 | Rain | Animal | 459 | 08:52 Menggala 13,8 KV OCB fdr #2 T/LO, Ctr: R/F: 51P @1, @2 11:20 Patrolled the line and found 2 Monkeys hanging in @2 at Ubi #25. 11:45 Manually Open LBS 27-AL-03. 12:00 Manually Blocked & closed Menggala fdr #2 and release the block.----> Ok. 12:42 Manually Closed LBS 27-AL-03. Cause: Animal (monkey) |  | 1 | 8:52 | Morning | Thursday | 2019 | 8
11724 | 2019-08-15 17:10 | 2019-08-15 17:10 | 4.16KV SO RUMBAI FEEDER #3 | Fair | Planned Maintenance | - | 17:10 Manual Open LBS 3-RF-07 (So-RBI fdr #3), closed at 18:00 MTCE team to change out 50 kVA TX o/p 2-RF-16 Cause: Planned Maintenance |  | 1 | 17:10 | Afternoon | Thursday | 2019 | 8
11725 | 2019-08-15 19:49 | 2019-08-15 19:49 | 4 BRAVO SUBSTATION | Fair | Under investigation | 42 | 19:49 C/S 4B Subst TX-2 Tripped, TX-2 were OFF, freq rise to 60:13 4B feeder #4, feeder #5 and feeder #6 were down/No Power 21:03 Checked and found: - C/S X-2 is Open, R/F: 51G, ctr: 146 - 147 - Visually TX : Normal Condition - TX W/T: 60 deg; TX L/T: 60 deg - 86HR : Normal / Not Operate - 87T : Normal / Not Operate - No fault indication at TX, VR, CB and BUS 21:27 Manual Open 4B fdr #4, closed at 21:35, counter: 249 -250 Manual Open 4B fdr #4, closed at 21:35, counter: 172 - 173 Manual Open 4B fdr #4, closed at 21:35, counter: 191 - 192 21:30 Close C/S for TX-2, OK, TX re-energize Re-checked TX, VR and others accessories, found normal Cause: Under Investigation |  | 1 | 19:49 | Night | Thursday | 2019 | 8
11726 | 2019-08-15 20:14 | 2019-08-15 20:14 | 13.8KV 5B FEEDER #1 | Fair | Emergency | - | 20:14 Manual Open 5B VCB fdr #1 Maintain Level Tank at GS-6 due to 1 WIP failed to start Cause: Emergency |  | 1 | 20:14 | Night | Thursday | 2019 | 8
11727 | 2019-08-15 20:21 | 2019-08-15 20:21 | 13.8KV 4B FEEDER #1 | Fair | Emergency | - | 20:21 Manual Open 4B VCB fdr #1 Maintain Level Tank at GS-6 due to 1 WIP failed to start Cause: Emergency |  | 1 | 20:21 | Night | Thursday | 2019 | 8
11728 | 2019-08-16 23:59 | / | CPI POWER SYSTEM |  | Normal Condition | - | - |  | 1 | 23:59 | Night | Friday | 2019 | 8
11729 | 2019-08-17 12:57 | 2019-08-17 12:57 | 13.8KV PEMATANG FEEDER #1 | Fair | Lightning | 29 | Pematang OCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 12:57 | Afternoon | Saturday | 2019 | 8
11730 | 2019-08-17 12:57 | 2019-08-21 17:18 | 13.8KV PEMATANG FEEDER #1 | Fair | Lightning | 29 | Checked and found Pematang VCB fdr#1 T/R Ctr:182-183 R/F:51N. Patrolled the line found @1 Broken Pin Insulator o/p 34BC101. Cause : Lightning. |  | 1 | 12:57 | Afternoon | Saturday | 2019 | 8
11731 | 2019-08-17 12:57 | 2019-08-17 12:57 | 13.8KV PEMATANG FEEDER #2 | Foggy and Smoke | Normal Condition | 0 | Pematang feeder #2 load dropped 40A (107-67A). Not checked yet. |  | 1 | 12:57 | Afternoon | Saturday | 2019 | 8
11732 | 2019-08-17 14:00 | 2019-08-17 14:00 | 4.16KV MINAS HSG FEEDER | Fair | Planned Maintenance | - | 14:00 Manualy open 4160 V Minas housing. Replace @1 B/O fuse at complex Elang # 107. 14:25 Manualy close 4160 V Minas housing. Cause: Planned Maintenance. |  | 1 | 14:00 | Afternoon | Saturday | 2019 | 8
11733 | 2019-08-17 17:15 | 2019-08-21 10:05 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Theft | 0 | Checked and found Recl.41-AW-62 T/R 1x Ctr:327-328. Recl. Recl. 39AV36 T/R 1x Ctr:281-282. Patrolled the line & found Pencurian trafo di Kulin 21 dan 70. Sawit menyentuh line near pole 38AS23. Cause : Theft. |  | 1 | 17:15 | Afternoon | Saturday | 2019 | 8
11734 | 2019-08-17 17:27 | 2019-08-17 17:27 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 37 | OKB OCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 17:27 | Afternoon | Saturday | 2019 | 8
11735 | 2019-08-17 17:27 | 2019-08-18 13:55 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 37 | Checked and found OKB OCB fdr #2 T/R 1x, ctr: 1371 - 1372, R/F: 51P Patrolled the line but found nothing Cause : Unidentified |  | 1 | 17:27 | Afternoon | Saturday | 2019 | 8
11736 | 2019-08-18 16:24 | 2019-08-18 16:24 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 29 | Pematang OCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 16:24 | Afternoon | Sunday | 2019 | 8
11737 | 2019-08-18 16:24 | 2019-08-22 10:51 | 13.8KV PEMATANG FEEDER #1 | Rain and Lightning | Lightning | 29 | Checked and found Pematang VCB fdr#1 T/R Ctr:182-183 R/F:51N. Patrolled the line found @1 Flashed over Pin Insulator o/p 34BC101. Cause : Lightning |  | 1 | 16:24 | Afternoon | Sunday | 2019 | 8
11738 | 2019-08-18 16:24 | 2019-08-18 16:24 | 13.8KV PETANI FEEDER #1 | Drizzle | Normal Condition | 0 | Petani feeder #1 load dropped 80A (222-142A). Not checked yet. |  | 1 | 16:24 | Afternoon | Sunday | 2019 | 8
11739 | 2019-08-18 16:24 | 2019-08-22 10:57 | 13.8KV PETANI FEEDER #1 | Drizzle | Normal Condition | 0 | Checked Feeder & Recloser normal operation (Not Operated). Patrolled the line but not founding Cause : Normal Condition. |  | 1 | 16:24 | Afternoon | Sunday | 2019 | 8
11740 | 2019-08-18 16:24 | 2019-08-18 16:24 | 13.8KV RANGAU FEEDER #2 | Drizzle | Normal Condition | 86 | Rangau feeder #2 load dropped 28A (180-152A). Not checked yet. |  | 1 | 16:24 | Afternoon | Sunday | 2019 | 8
11741 | 2019-08-18 16:24 | 2019-08-19 15:27 | 13.8KV RANGAU FEEDER #2 | Drizzle | Normal Condition | 86 | Checked and found all protection device in normal condition Not need to patrolled the line. Cause : Normal Condition |  | 1 | 16:24 | Afternoon | Sunday | 2019 | 8
11742 | 2019-08-19 13:35 | 2019-08-19 13:35 | MINAS POWER PLANT |  |  | - | 13:35 S/U MGT #7 and then Online the unit at 13:52. |  | 1 | 13:35 | Afternoon | Monday | 2019 | 8
11743 | 2019-08-19 14:17 | 2019-08-19 14:17 | MINAS POWER PLANT |  |  | - | 14:17 S/U MGT #6 and then Online the unit at 14:35. |  | 1 | 14:17 | Afternoon | Monday | 2019 | 8
11744 | 2019-08-19 19:18 | 2019-08-19 19:18 | MINAS POWER PLANT |  |  | - | 19:18 MGT #11 S/U and then Online at 19:37 |  | 1 | 19:18 | Night | Monday | 2019 | 8
11745 | 2019-08-19 20:00 | 2019-08-19 20:00 | NORTH DURI POWER PLANT |  |  | - | 20:00 NDC CT-3 Offline for fixing lube oil vapor Extractor system. |  | 1 | 20:00 | Night | Monday | 2019 | 8
11746 | 2019-08-20 06:11 | 2019-08-20 06:11 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 19 | Ketigul VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 6:11 | Morning | Tuesday | 2019 | 8
11747 | 2019-08-20 06:11 | 2019-08-26 07:11 | 13.8KV KETIGUL FEEDER#2 | Fair | Dead End Insulator | 19 | Checked & found Ketigul VCB fdr#2 T/R 1x Ctr:345-346 R/F:51N. Patrolled the line & found @1@2 Broken Dead End Insulator o/p 31AN24B. Cause : Dead End Insulator. |  | 1 | 6:11 | Morning | Tuesday | 2019 | 8
11748 | 2019-08-20 15:50 | 2019-08-20 15:50 | NORTH DURI POWER PLANT |  |  | - | 15:50 NDC CT #3 S/U and On Line to the system at 17:50. |  | 1 | 15:50 | Afternoon | Tuesday | 2019 | 8
11749 | 2019-08-20 18:05 | 2019-08-20 18:05 | 13.8KV DURI FIELD FEEDER #4 | Fair | Pin Insulator | 0 | Duri Field ACB #51 (feeder #4) T/R 1x. Not checked yet. |  | 1 | 18:05 | Afternoon | Tuesday | 2019 | 8
11750 | 2019-08-20 18:05 | 2019-08-26 08:05 | 13.8KV DURI FIELD FEEDER #4 | Fair | Pin Insulator | 0 | Checked & Found Duri Field fdr#4 T/R 1x Ctr:549-550 R/F:51N. Patrolled the line & found @3 Broken Pin Insulator o/p 07-V1-09. @3 Broken LA Jumper o/p 07-U2-01. @1@2@3 Danger Trees Near pole 07-V5-26. Cause : Pin Insulator. |  | 1 | 18:05 | Afternoon | Tuesday | 2019 | 8
11751 | 2019-08-20 20:12 | 2019-08-20 20:12 | MINAS POWER PLANT |  |  | - | 20:12 MGT #10 Off line and then S/D for S/B. |  | 1 | 20:12 | Night | Tuesday | 2019 | 8
11752 | 2019-08-20 20:19 | 2019-08-20 20:19 | MINAS POWER PLANT |  |  | - | 20:19 MGT #6 Off line and then S/D for S/B. |  | 1 | 20:19 | Night | Tuesday | 2019 | 8
11753 | 2019-08-20 20:33 | 2019-08-20 20:33 | MINAS POWER PLANT |  |  | - | 20:33 MGT #7 Off line and then S/D for S/B. |  | 1 | 20:33 | Night | Tuesday | 2019 | 8
11754 | 2019-08-21 14:11 | 2019-08-21 14:11 | 13.8KV 4D FEEDER #2 | Fair | Lightning | 22 | 4D OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 14:11 | Afternoon | Wednesday | 2019 | 8
11755 | 2019-08-21 14:11 | 2019-08-24 14:11 | 13.8KV 4D FEEDER #2 | Fair | Lightning | 22 | Checked & found 4D OCB fdr#2 T/R 1x Ctr:287-288 R/F;51N. Patrolled the line but found nothing. Cause : Lightning |  | 1 | 14:11 | Afternoon | Wednesday | 2019 | 8
11756 | 2019-08-21 16:51 | 2019-08-21 16:51 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 16 | Ketigul VCB fdr#2 T/R 1x. Ketigul fdr#1 Load dropped 88A (109-21A). Ketigul fdr#3 Load dropped 26A (47-21A). Not checked yet. |  | 1 | 16:51 | Afternoon | Wednesday | 2019 | 8
11757 | 2019-08-21 16:51 | 2019-08-26 08:51 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 16 | Checked & found Ketigul VCB fdr#2 T/R 1x Ctr:345-346 R/F:51N. Patrolled the line & found @1@2 Broken Dead End Insulator o/p 31AN24B. Cause : Dead End Insulator. |  | 1 | 16:51 | Afternoon | Wednesday | 2019 | 8
11758 | 2019-08-22 08:06 | 2019-08-22 08:06 | 13.8KV MINAS FEEDER #6 | Drizzle | Unidentified | 32 | 08:06 Minas ACB fdr#6 T/R 1x Ctr:195-196 R/F:51N. 09:00 Minas fdr#6 still dropped 113A. 09:25 Checked & found Recl. 7E-67A T/SO Ctr:81-82. Blocked & closed Recl. 7E-67A, the release the block. Cause: Unidentified. |  | 1 | 8:06 | Morning | Thursday | 2019 | 8
11759 | 2019-08-22 10:21 | 2019-08-22 10:21 | 13.8KV CENTRAL DURI FEEDER #7 | Fair | Planned Maintenance | 11 | 10:21 Manually opened Recl. 03-1-39 (C.Duri fdr#7). Replaced @1@2@3 broken Pin Insulator o/p 03-1-11. 11:01 Blocked & closed Recl 03-1-39, then release the block. Cause: Plan maintenance. |  | 1 | 10:21 | Morning | Thursday | 2019 | 8
11760 | 2019-08-22 15:38 | 2019-08-22 15:38 | 13.8KV SINTONG FEEDER #2 | Fair | Planned Maintenance | 15 | 15:38 Manually open Recl. 29AK24 (Sintong fdr#2). Replaced B/O 100Kva Tx with the same size at Pagar GS. 16:54 Blocked & closed Recl. 29AK24, then release the block. Cause: Plan Maintenance. |  | 1 | 15:38 | Afternoon | Thursday | 2019 | 8
11761 | 2019-08-22 18:26 | 2019-08-22 18:26 | CENTRAL DURI POWER PLANT |  |  | - | CGT#2 Trip due to 480Volt Bus Trip Off. |  | 1 | 18:26 | Afternoon | Thursday | 2019 | 8
11762 | 2019-08-23 03:28 | 2019-08-23 03:28 | 13.8KV 5B FEEDER #8 | Fair | Unidentified | 0 | 5B OCB feeder #8 T/R 1x. Not checked yet. |  | 1 | 3:28 | Night | Friday | 2019 | 8
11763 | 2019-08-23 03:28 | 2019-08-24 15:28 | 13.8KV 5B FEEDER #8 | Fair | Unidentified | 0 | Checked & found 5B OCB fdr#8 T/R 1x Ctr:31-32 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 3:28 | Night | Friday | 2019 | 8
11764 | 2019-08-24 10:01 | 2019-08-24 10:01 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Planned Maintenance | 253 | 10:01 Manually opened Recl 41AW62 (C.Duri fdr#1). Replaced 112.5 KVa with the same size at well Kulin #21. Replaced 112.5 KVa with the same size at well Kulin #70. Replaced Pin Insulator o/p 39AU19, 39AW13, 39AW15. Open HLC TOP Kulin#12 (LTC well). 12:25 Blocked & closed Recl. 41AW62, then release the block. Cause: Plan Maintenance. |  | 1 | 10:01 | Morning | Saturday | 2019 | 8
11765 | 2019-08-24 22:40 | 2019-08-24 22:40 | 13.8KV BEKASAP FEEDER #3 | Fair | Pin Insulator | 0 | Bekasap Main 13.8 KV ACB fdr #3 T/R 1X. Not checked yet. |  | 1 | 22:40 | Night | Saturday | 2019 | 8
11766 | 2019-08-24 22:40 | 2019-08-27 15:39 | 13.8KV BEKASAP FEEDER #3 | Fair | Pin Insulator | 0 | Checked and found: BKSMSB-13.8VCB3 T/R, Counter : 99591 - 99592, Relay Flag : 51N. Patrolled the line found : Pin sompel dan flash over Phase : 1, 2, 3, Pole : Bekasap #35 Date Patrol : 26-AUG-2019 Operated Device : BKSMSB-13.8VCB3 T/R Counter : 99591 - 99592 Relay Flag : 51N Finding Patrol : FCO terbakar Phase : 3 Pole : 37-BG-6 Date Patrol : 26-AUG-2019 Operated Device : BKSMSB-13.8VCB3 T/R Counter : 99591 - 99592 Relay Flag : 51N Finding Patrol : Jumper LA putus Phase : 2 Pole : 37-BG-6 Cause : Pin Insulator |  | 1 | 22:40 | Night | Saturday | 2019 | 8
11767 | 2019-08-25 16:15 | 2019-08-25 16:15 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Animal | 146 | 16:15 CD Fdr#1 T/LO Ctr: 260-264, R/F: 51 @1 2 3, 51G 17:00 Checked & found, B/O Recl. 41 AW 62, Broken at Bushing @1@2 Primary & Secondary 17:30 Man. Block & Closed CD ACB fdr#1 after Isolate & Bypassed Rcl 41 AW 62 Cause: Animal (Monkey). Prod loss : 78 Bbls / 18 wells ( Balam GS ). |  | 1 | 16:15 | Afternoon | Sunday | 2019 | 8
11768 | 2019-08-26 09:15 | 2019-08-26 09:15 | CENTRAL DURI POWER PLANT |  |  | - | 09:15 S/U CGT#2, then on line the unit at 09:35. |  | 1 | 9:15 | Morning | Monday | 2019 | 8
11769 | 2019-08-26 10:55 | 2019-08-26 10:55 | CENTRAL DURI POWER PLANT |  |  | - | 10:55 CGT#4 T/O Generator breaker by over Excitation , then on line the unit at 11:00. |  | 1 | 10:55 | Morning | Monday | 2019 | 8
11770 | 2019-08-26 11:12 | 2019-08-26 11:12 | CENTRAL DURI POWER PLANT |  |  | - | Off line CGT#5, then S/D the unit for S/B. |  | 1 | 11:12 | Morning | Monday | 2019 | 8
11771 | 2019-08-26 15:25 | 2019-08-26 15:25 | MINAS POWER PLANT |  |  | - | 15:25 MGT #7 S/U, then On Line at15:40 for Replacing MGT #8 be S/D |  | 1 | 15:25 | Afternoon | Monday | 2019 | 8
11772 | 2019-08-26 15:45 | 2019-08-26 15:45 | MINAS POWER PLANT |  |  | - | 15:45 MGT #8 S/D for Stand by, due to Computer C problem |  | 1 | 15:45 | Afternoon | Monday | 2019 | 8
11773 | 2019-08-26 16:35 | 2019-08-26 16:35 | CENTRAL DURI POWER PLANT |  |  | - | 16:35 CGT #5 S/U then On Line at 17:00 to Backed up System Voltage |  | 1 | 16:35 | Afternoon | Monday | 2019 | 8
11774 | 2019-08-26 20:13 | 2019-08-26 20:13 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning Arrester | 835 | 20:13 6D OCB feeder #2 T/O. 21:10 Checked and found 6D OCB feeder #2 T/SO R/F: 51N Counter: 249-250. Blocked and closed 6D OCB feeder #2 but tripped again. 23:59 Patrolled the line , SSWA due to heavy rain and slippery road conditions. Continue tomorrow morning. Production loss : 112 Bbls / 16 wells up to 23:59:59 ( Estimate 4 hours ). Cause : Not Patrolled yet |  | 1 | 20:13 | Night | Monday | 2019 | 8
11775 | 2019-08-26 20:13 | 2019-08-27 09:23 | 13.8KV 6D FEEDER #2 | Rain and Lightning | Lightning Arrester | 835 | 09:23 Open recloser 6D-298 D/S 6D fdr#2. Open recloser 6D-78A D/S 6D fdr#2. 09:30 6D fdr#2 try to Closed but Trip again. Solution: Transfer part of load 6D fdr#2 to Fdr#1 & #3 09:40 By closed LBS 6D-68 D/S 6D fdr#3 09:46 By closed LBS 6C-21A D/S 6D fdr#1 Inform FOS & GS area 4 Patrolled 6D fdr#2 till Recloser 6D-298 & Recloser 6D-78A. 15:00 found broken LA @1 o/p 6D-245, and @123 Broken Pin Insulator o/p 6D-77, then Isolated the LA and Replaced broken Pin 15:40 Manually Block & Closed 6D OCB fdr#2, success 16:32 Manually Block & Closed Recloser 6D-298, then Open LBS 6D-68, Separate from 6D fdr#3 16:47 Manually Block & Closed Recloser 6D-78A, then Open LBS 6C-21A, Separate from 6D fdr#1 Load 6D Fdr#2 Back to normal, inform to FOS & GS area 4 Cause: Broken LA Production loss : 112 Bbls / 16 wells up to 23:59:59 ( Estimate 4 hours ). Production loss : 478 Bbls / 16 wells up to 16:47:00 ( Estimate 16 hours ). ------------------------------------------------------------------------------------- + Total : 590 Bbls / 16 wells. ( GS #3 ). Total : 208 Bbls / 11 wells. ( GS #4 ). ----------------------------------------------------------- + Grand total : 798 Bbls / 27 wells. |  | 1 | 20:13 | Night | Monday | 2019 | 8
11776 | 2019-08-27 00:22 | 2019-08-27 00:22 | 13.8KV 5B FEEDER #2 | Rain | Tree | 9 | 5B OCB feeder #2 T/R 1x. 5B feeder #6 load dropped 53A (113-60A) --> WIP. Not checked yet. |  | 1 | 0:22 | Night | Tuesday | 2019 | 8
11777 | 2019-08-27 00:22 | 2019-08-29 16:19 | 13.8KV 5B FEEDER #2 | Rain | Tree | 9 | Checked and found: 5BSB-13.8OCB2 T/R, Counter : 424 - 425, Relay Flag : 50. Patrolled the line found : Pohon tinggi Operated Device : 5BSB-13.8OCB2 T/R Counter : 424 - 425 Relay Flag : 50 Finding Patrol : Broken deadend Phase : 1, 3, Pole : 4C-74 Cause : Tree |  | 1 | 0:22 | Night | Tuesday | 2019 | 8
11778 | 2019-08-27 00:22 | 2019-08-27 00:22 | 13.8KV 5B FEEDER #1 | Rain | Normal Condition | 0 | 5B feeder #1 load dropped 72A (164-92A). Not checked yet. |  | 1 | 0:22 | Night | Tuesday | 2019 | 8
11779 | 2019-08-27 00:22 | 2019-08-29 15:47 | 13.8KV 5B FEEDER #1 | Rain | Normal Condition | 0 | Checked and found all protection devices are normal RCL 5B-06 is Normal, ctr: 104-104, no finding patrol Cause : Normal Condition |  | 1 | 0:22 | Night | Tuesday | 2019 | 8
11780 | 2019-08-27 00:22 | 2019-08-27 00:22 | 13.8KV 5B FEEDER #3 | Rain | Normal Condition | 0 | 5B feeder #3 load dropped 34A (74-40A). Not checked yet. |  | 1 | 0:22 | Night | Tuesday | 2019 | 8
11781 | 2019-08-27 00:22 | 2019-08-29 15:49 | 13.8KV 5B FEEDER #3 | Rain | Normal Condition | 0 | Checked and found: RCL 4C-65A Not Operate, Counter: 78 - 78, R/F: NONE Patrolled : Nothing Found Cause : Normal Condition |  | 1 | 0:22 | Night | Tuesday | 2019 | 8
11782 | 2019-08-27 00:24 | 2019-08-27 00:24 | 13.8KV 8C FEEDER #2 | Rain | Tree | 4 | 8C OCB feeder #2 T/R 1x. 8C feeder #6 load dropped 53A (202-149A) --> WIP. Not checked yet. |  | 1 | 0:24 | Night | Tuesday | 2019 | 8
11783 | 2019-08-27 00:24 | 2019-08-29 16:19 | 13.8KV 8C FEEDER #2 | Rain | Tree | 4 | Checked and found 8C VCB fdr #2 T/R 1x, ctr: 424 - 425, R/F: 50P Patrolled the line and found high trees at pole 5C-38 @2 and broken dead end o/p 4C-74 on @1 and @3 Cause : Tree |  | 1 | 0:24 | Night | Tuesday | 2019 | 8
11784 | 2019-08-27 00:24 | 2019-08-27 00:24 | 13.8KV 8C FEEDER #1 | Rain | Unidentified | 155 | 00:24 8C feeder #1 load dropped 77A (164-92A). 10:25 Checked & found Recl 9D-25 T/LO Ctr:111-117. Patrolled the line but found nothing. Cause: Un identified. |  | 1 | 0:24 | Night | Tuesday | 2019 | 8
11785 | 2019-08-27 00:24 | 2019-08-27 00:24 | 13.8KV 8C FEEDER #3 | Rain | Normal Condition | 31 | 8C feeder #3 load dropped 31A (205-174A). Not checked yet. |  | 1 | 0:24 | Night | Tuesday | 2019 | 8
11786 | 2019-08-27 00:24 | 2019-08-28 14:13 | 13.8KV 8C FEEDER #3 | Rain | Normal Condition | 31 | Checked & found Recl. 8D-18A T/R 1x Ctr:187-188. Patrolled the line but found nothing. Cause : Normal Condition. |  | 1 | 0:24 | Night | Tuesday | 2019 | 8
11787 | 2019-08-27 08:07 | 2019-08-27 08:07 | 13.8KV 6D FEEDER #1 | Fair | Unidentified | 346 | 6D OCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 8:07 | Morning | Tuesday | 2019 | 8
11788 | 2019-08-27 08:07 | 2019-02-09 20:07 | 13.8KV 6D FEEDER #1 | Fair | Unidentified | 346 | Checked & found 6D fdr#1 T/R 1x Ctr:368-369 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 8:07 | Morning | Tuesday | 2019 | 8
11789 | 2019-08-27 18:00 | 2019-08-27 18:00 | 13.8KV 6DN FEEDER #5 | Fair | Emergency | 0 | 18:00 Manually Opened 6D OCB fdr#5 Due to Maintain Level Tank at GS #3 A request from GS. Cause: emergency. |  | 1 | 18:00 | Afternoon | Tuesday | 2019 | 8
11790 | 2019-08-27 23:07 | 2019-08-27 23:07 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Unidentified | 10 | Pungut OCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 23:07 | Night | Tuesday | 2019 | 8
11791 | 2019-08-27 23:07 | 2019-08-31 07:45 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Unidentified | 10 | Checked and found OCB PGT fdr #2 T/R 1x, ctr: 423 - 424, R/F: 51p Patrolled the line but found nothing Cause : Unidentified |  | 1 | 23:07 | Night | Tuesday | 2019 | 8
11792 | 2019-08-28 01:04 | 2019-08-28 01:04 | 13.8KV 8C FEEDER #6 | Drizzle | Unidentified | 5 | 8C VCB feeder #6 T/R 1x. 8C feeder #5 load dropped 59A (233-174A) --> WIP. 8C feeder #4 load dropped 106A (184-78A) --> WIP. Not checked yet. |  | 1 | 1:04 | Night | Wednesday | 2019 | 8
11793 | 2019-08-28 01:04 | 2019-02-09 20:04 | 13.8KV 8C FEEDER #6 | Drizzle | Unidentified | 5 | Checked & found 8C fdr#6 T/R 1x Ctr:622-623 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 1:04 | Night | Wednesday | 2019 | 8
11794 | 2019-08-28 08:45 | 2019-08-28 08:45 | 13.8KV LIBO FEEDER #1 | Fair | Construction Job | 27 | 08:45 Manual Open LBS 33-CC-06, closed at 11:30 Support project to install conductor for SE Libo #43, Gas Well to Oil Well (impacted to SE Libo #05 and SE Libo #18 (well off) during the job) Cause: Construction Job (project) |  | 1 | 8:45 | Morning | Wednesday | 2019 | 8
11795 | 2019-08-28 19:12 | 2019-08-28 19:12 | 13.8KV PETANI FEEDER #2 | Fair | Emergency | - | 19:12 Manually Opened Patani VCB fdr#2. Emergency Maintain Tank level at Petani GS. 20:05 Blocked & closed Petani VCB fdr#2, then releasethe block. Cause: Emergency. |  | 1 | 19:12 | Night | Wednesday | 2019 | 8
11796 | 2019-08-28 19:12 | 2019-08-28 19:12 | 13.8KV ROKAN FEEDER #2 | Fair | Emergency | - | 19:13 Manually Opened Rokan VCB fdr#2. Emergency Maintain Tank level at Petani GS. 20:00 Blocked & closed Rokan VCB fdr#2, then releasethe block. Cause: Emergency. |  | 1 | 19:12 | Night | Wednesday | 2019 | 8
11797 | 2019-08-29 23:59 | 2019-08-29 23:59 | CPI POWER SYSTEM |  | Normal Condition | - | Normal System Condition. |  | 1 | 23:59 | Night | Thursday | 2019 | 8
11798 | 2019-08-30 23:59 | 2019-08-30 23:59 | CPI POWER SYSTEM |  | Normal Condition | - | Normal System Condition. |  | 1 | 23:59 | Night | Friday | 2019 | 8
11799 | 2019-08-31 07:31 | 2019-08-31 07:31 | 13.8KV MINAS FEEDER #6 | Fair | Under investigation | 87 | 07:31 Minas fdr #6 T/LO (2x), ctr: 196 - 198, R/F: 51N, 51P @1, @2 08:30 Checked and found conductor spin (3 phase), 1 span long, behind of EQR office. 09:01 Spin conductor has been repaired. 09:05 Block and close MNS fdr #6, OK, then release the block. 09:21 Continue patrolled the line and found RCL 7E-67A T/SO, ctr: 82 - 83 09:22 Block and Closed RCL 7E-67A, OK, then release the block. Cause: Under Investigation |  | 1 | 7:31 | Morning | Saturday | 2019 | 8
11800 | 2019-08-31 07:31 | 2019-08-31 07:31 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | - | Minas fdr #1 Load Dropped 131A (169 - 38A) Cause: Not Checked Yet |  | 1 | 7:31 | Morning | Saturday | 2019 | 8
11801 | 2019-08-31 07:31 | 2019-03-09 08:43 | 13.8KV MINAS FEEDER #1 | Fair | Unidentified | - | Checked and found: MNSSG-13.8ACB14 Unknown, Counter : 83 - 83, Relay Flag : NONE. Patrolled the line found : Nothing Cause : Unidentified. |  | 1 | 7:31 | Morning | Saturday | 2019 | 8
11802 | 2019-08-31 07:31 | 2019-08-31 07:31 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | - | Minas fdr #2 Load Dropped 61A (137 - 39A) Cause: Not Checked Yet |  | 1 | 7:31 | Morning | Saturday | 2019 | 8
11803 | 2019-08-31 07:31 | 2019-03-09 08:46 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | - | Checked and found: MNSSG-13.8ACB13 Unknown, Counter : 80 - 80, Relay Flag : NONE. Patrolled the line found: Nothing Cause : Unidentified. |  | 1 | 7:31 | Morning | Saturday | 2019 | 8
11804 | 2019-08-31 07:31 | 2019-08-31 07:31 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | - | Minas fdr #3 Load Dropped 98A (137 - 39A) Cause: Not Checked Yet |  | 1 | 7:31 | Morning | Saturday | 2019 | 8
11805 | 2019-08-31 07:31 | 2019-03-09 08:48 | 13.8KV MINAS FEEDER #3 | Fair | Unidentified | - | Checked and found: MNSSG-13.8ACB02 Unknown, Counter : 103 - 103, Relay Flag : NONE. Patrolled the line found : Nothing Cause : Unidentified |  | 1 | 7:31 | Morning | Saturday | 2019 | 8
11806 | 2019-08-31 07:31 | 2019-08-31 07:31 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | - | Minas fdr #4 Load Dropped 127A (163 - 36A) Cause: Not Checked Yet |  | 1 | 7:31 | Morning | Saturday | 2019 | 8
11807 | 2019-08-31 07:31 | 2019-03-09 08:50 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | - | Checked and found: MNSSG-13.8ACB01 Unknown, Counter : 103 - 103, Relay Flag : NONE. Patrolled the line found : Nothing Cause : Unidentified |  | 1 | 7:31 | Morning | Saturday | 2019 | 8
11808 | 2019-08-31 10:00 | 2019-08-31 10:00 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Planned Maintenance | 5 | 10:00 Manual Open RCL 09-N4-08 (CD fdr #16), Closed at 11:32, ctr:229 MTCE team to repair underground cable o/p09-N4-05 Cause: Planned Maintenance |  | 1 | 10:00 | Morning | Saturday | 2019 | 8
11809 | 2019-01-09 18:19 | 2019-01-09 18:19 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 17 | Ketigul fdr #2 T/R 1x Cause: Not Checked Yet |  | 1 | 18:19 | Afternoon | Wednesday | 2019 | 1
11810 | 2019-01-09 18:19 | 2019-03-09 11:02 | 13.8KV KETIGUL FEEDER#2 | Fair | Animal | 17 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 348 - 349, Relay Flag : 51N Patrolled the line found : monkey Cause : Animal. |  | 1 | 18:19 | Afternoon | Wednesday | 2019 | 1
11811 | 2019-01-09 18:29 | 2019-01-09 18:29 | 13.8KV NORTH DURI FEEDER #6 | Fair | Unidentified | 0 | N. Duri 13.8KV VCD fdr c#6 T/R 1 X. Not checked yet. |  | 1 | 18:29 | Afternoon | Wednesday | 2019 | 1
11812 | 2019-01-09 18:29 | 2019-03-09 10:55 | 13.8KV NORTH DURI FEEDER #6 | Fair | Unidentified | 0 | Checked and found : NDRSB-13.8VCB6 T/R, Counter : 310 - 312, Relay Flag : 51N. Patrolled the line found : No Findings Cause : Unidentified |  | 1 | 18:29 | Afternoon | Wednesday | 2019 | 1
11813 | 2019-02-09 14:27 | 2019-02-09 14:27 | 13.8KV 5B FEEDER #3 | Fair | Planned Maintenance | 6 | 14:27 Manual Open LBS 4C-45A (5B fdr #3), closed at 15:00 Change out TX at 4C-49 (300 kVA) Cause: Planned Maintenance |  | 1 | 14:27 | Afternoon | Saturday | 2019 | 2
11814 | 2019-02-09 16:19 | 2019-02-09 16:19 | MINAS POWER PLANT |  |  | - | MGT-8 S/U and then online at 16:39 |  | 1 | 16:19 | Afternoon | Saturday | 2019 | 2
11815 | 2019-02-09 16:35 | 2019-02-09 16:35 | 13.8KV 6DN FEEDER #3 | Fair | Others | 0 | 16:35 6DN fdr #3 dropped 55A (126 -71 A) Bus-2 voltage rise to 14.45 kV 6DN fdr #1 dropped 117 A (155 - 38 A) 6DN fdr #2 dropped 83 A (231 - 148 A) 6DN fdr #6 dropped 6 A (141 - 135 A) Cause: Others, WIP Pump at GS-3 tripped. |  | 1 | 16:35 | Afternoon | Saturday | 2019 | 2
11816 | 2019-02-09 16:42 | 2019-02-09 16:42 | MINAS POWER PLANT |  |  | - | MGT-7 Offline and then S/D at 16:42 |  | 1 | 16:42 | Afternoon | Saturday | 2019 | 2
11817 | 2019-02-09 16:55 | 2019-02-09 16:55 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning | 0 | MGL fdr #1 dropped 98 A (142 - 44 A) Cause: Not Checked Yet |  | 1 | 16:55 | Afternoon | Saturday | 2019 | 2
11818 | 2019-02-09 16:55 | 2019-05-09 08:25 | 13.8KV MENGGALA FEEDER #1 | Fair | Lightning | 0 | checked and found: 5440-R.19AN04 T/R, Counter : 648 - 649, Relay Flag : 51N Patrolled the line found : Broken LA Cause : Lightning |  | 1 | 16:55 | Afternoon | Saturday | 2019 | 2
11819 | 2019-03-09 11:35 | 2019-03-09 11:35 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 0 | Rangau fdr #2 load dropped 115 A (162 - 47 A) Cause: Not Checked Yet |  | 1 | 11:35 | Morning | Saturday | 2019 | 3
11820 | 2019-03-09 11:35 | 2019-07-09 18:06 | 13.8KV RANGAU FEEDER #2 | Fair | Unidentified | 0 | Checked and found RCL 23-BD-01 T/R 3x, ctr: 398 - 401, R/F: None Patrolled the line but found nothing Cause : Unidentified |  | 1 | 11:35 | Morning | Saturday | 2019 | 3
11821 | 2019-03-09 17:49 | 2019-03-09 17:49 | 13.8KV DARLING VCB FEEDER #7 | Fair | Animal | 0 | Darling VCB fdr #7 (ex CD fdr #13) T/R 1x Cause: Not Checked Yet |  | 1 | 17:49 | Afternoon | Saturday | 2019 | 3
11822 | 2019-03-09 17:49 | 2019-07-09 18:07 | 13.8KV DARLING VCB FEEDER #7 | Fair | Animal | 0 | Checked and found DRL fdr #7 T/R 1x, ctr: 177 - 178, R/F: 51P @3 Patrolled the line and found dead animal (monkey) at CSS-6 Trane - A Cause : Animal |  | 1 | 17:49 | Afternoon | Saturday | 2019 | 3
11823 | 2019-03-09 20:58 | 2019-03-09 20:58 | 13.8KV NEW KOTABATAK FEEDER #3 | Cloudy | Tree | 0 | NKBS VCB Fdr#3 T/R 1x (toward KB GS WIP) NKBS GFPC T/R 1x Not checked yet |  | 1 | 20:58 | Night | Saturday | 2019 | 3
11824 | 2019-03-09 20:58 | 2019-04-09 15:23 | 13.8KV NEW KOTABATAK FEEDER #3 | Cloudy | Tree | 0 | Checked and found: NKBKSB-13.8OCB3 T/R, Counter : 322 - 323, Relay Flag : 50N Patrolled the line found : High Trees Cause : Tree |  | 1 | 20:58 | Night | Saturday | 2019 | 3
11825 | 2019-03-09 22:12 | 2019-03-09 22:12 | 4.16KV SO RUMBAI FEEDER #4 | Rain and Lightning | Lightning | - | 22:12 Rumbai Recl fdr#4 T/O Checked & found, Ctr: 174-175, R/F: 51N 23:15 Manually Block & Closed Rumbai Recl Fdr#4 Cause: Not Patrolled yet |  | 1 | 22:12 | Night | Saturday | 2019 | 3
11826 | 2019-03-09 22:12 | 2019-07-09 07:34 | 4.16KV SO RUMBAI FEEDER #4 | Rain and Lightning | Lightning | - | Checked and found RCL fdr #4 So_RBI, ctr: 174 - 175, R/F: 51N Patrolled the line but found nothing Cause : Lightning |  | 1 | 22:12 | Night | Saturday | 2019 | 3
11827 | 2019-04-09 10:31 | 2019-04-09 10:31 | 13.8KV 6DN FEEDER #2 | Fair | Unidentified | 0 | 6DN feeder #2 load dropped 18A (249-231A). Not checked yet. | 123 | 1 | 10:31 | Morning | Tuesday | 2019 | 4
11828 | 2019-04-09 10:31 | 2019-06-09 07:29 | 13.8KV 6DN FEEDER #2 | Fair | Unidentified | 0 | Checked and found all in normal condition Patrolled the line but found nothing Cause : Unidentified | 123 | 1 | 10:31 | Morning | Tuesday | 2019 | 4
11829 | 2019-04-09 18:15 | 2019-04-09 18:15 | 13.8KV MENGGALA FEEDER #1 | Drizzle | Powerline - Jumper | 79 | 18:15 Menggala feeder #1 load dropped 40A (128-88A). Menggala GFPC T/R 1x. 20:38 Reported no power at MESO field (load MGL fdr #1 : 99 A) 21:38 Reported again voltage anbalance at 1 phase (load MGL fdr #1 : 106 A) 22:38 Checked and found b/o jumper @1 at source side of PHE metering on pole 19-AO-04 (call mtce team to repair the b/o jumper) 23:53 Manual Open RCL 19-AO-01 to repair the b/o jumper |  | 1 | 18:15 | Afternoon | Tuesday | 2019 | 4
11830 | 2019-04-09 18:15 | 2019-05-09 01:10 | 13.8KV MENGGALA FEEDER #1 | Drizzle | Powerline - Jumper | 79 | 01:10 Repair b/o jumper completed Block and Close RCL 19-AO-01, OK then release the block Cause: Jumper |  | 1 | 18:15 | Afternoon | Tuesday | 2019 | 4
11831 | 2019-04-09 18:42 | 2019-04-09 18:42 | 13.8KV BEKASAP FEEDER #3 | Fair | Normal Condition | 0 | Bekasap Main feeder #3 load dropped 50A (241-191A). Not checked yet. |  | 1 | 18:42 | Afternoon | Tuesday | 2019 | 4
11832 | 2019-04-09 18:42 | 2019-10-09 07:42 | 13.8KV BEKASAP FEEDER #3 | Fair | Normal Condition | 0 | Checked and found Bekasap Main feeder #3 load dropped 50A (241-191A). Checked Recloser: 1. Recloser: 37-BI-01 Normal condition Counter: 1318-1318. 2. Recloser: 36-BI-04 Normal condition Counter: 474-474. 3. Recloser: 34-BI-10 Normal condition Counter: 186-186. 4. Recloser: 37-BE-27 Normal condition Counter: 198-198. 5. Recloser: 37-BD-01 Normal condition Counter: 698-698. 6. Recloser: 37-BD-39 Normal condition Counter: 128-128. Patrolled the line nothing found. Cause: Unidentified. |  | 1 | 18:42 | Afternoon | Tuesday | 2019 | 4
11833 | 2019-05-09 10:00 | 2019-05-09 10:00 | MINAS POWER PLANT |  |  | - | 10:00 S/U MGT #7 and then Online the unit at 10:20. |  | 1 | 10:00 | Morning | Thursday | 2019 | 5
11834 | 2019-05-09 10:21 | 2019-05-09 10:21 | MINAS POWER PLANT |  |  | - | 10:21 Offline MGT #8 and then S/D the unit for Standby. |  | 1 | 10:21 | Morning | Thursday | 2019 | 5
11835 | 2019-05-09 11:44 | 2019-05-09 11:44 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | - | C.Duri VCB #18 (feeder #15) T/R 1x. R/F:51 @1,@2. 51N. Ctr:388-389. Not checked yet. |  | 1 | 11:44 | Morning | Thursday | 2019 | 5
11836 | 2019-05-09 11:44 | 2019-10-09 07:34 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | - | Cheked and found C.Duri VCB #18 (feeder #15) T/R 1x. R/F:51 @1,@2. 51N Ctr:388-389 Patrolled the line found Animal (monkey) at pole 06-Q%-21. Cause: Animal (monkey). |  | 1 | 11:44 | Morning | Thursday | 2019 | 5
11837 | 2019-05-09 15:54 | 2019-05-09 15:54 | MINAS POWER PLANT |  |  | - | 15:54 S/U MGT #10 and then Online the unit at 16:27. |  | 1 | 15:54 | Afternoon | Thursday | 2019 | 5
11838 | 2019-05-09 16:40 | 2019-05-09 16:40 | MINAS POWER PLANT |  |  | - | 16:40 Offline MGT #9 and then S/D the unit for Standby. |  | 1 | 16:40 | Afternoon | Thursday | 2019 | 5
11839 | 2019-05-09 22:37 | 2019-05-09 22:37 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | - | Darling fdr #7 T/R 1x Cause: Not Checked Yet |  | 1 | 22:37 | Night | Thursday | 2019 | 5
11840 | 2019-05-09 22:37 | 2019-09-09 09:24 | 13.8KV DARLING VCB FEEDER #7 | Fair | Unidentified | - | Checked and found: DRLG7-13.8VCB7 T/R, Counter : 178 - 179, Relay Flag : 51 Patrolled the line found : No Findings Cause : Unidentified |  | 1 | 22:37 | Night | Thursday | 2019 | 5
11841 | 2019-06-09 14:20 | 2019-06-09 14:20 | 13.8KV 8C FEEDER #6 | Fair | Planned Maintenance | 97 | 14:20 Manually open Recloser: 8C-94 D/S 8C feeder #6. Due to Dismantle powerline on pole 8C-18. for toll road construction. 16:18 Manually block and closed Recloser: 8C-94. Cause: Plan maintenance. |  | 1 | 14:20 | Afternoon | Sunday | 2019 | 6
11842 | 2019-07-09 06:17 | 2019-07-09 06:17 | 13.8KV SINTONG FEEDER #2 | Cloudy | Unidentified | 25 | Sintong OCB feeder #2 T/R 1x. Sintong feeder #1 load dropped 13A (125-112A). Not checked yet. |  | 1 | 6:17 | Morning | Tuesday | 2019 | 7
11843 | 2019-07-09 06:17 | 2019-09-09 11:29 | 13.8KV SINTONG FEEDER #2 | Cloudy | Unidentified | 25 | Checked and found: STGSB-13.8OCB2 T/R, Counter : 494 - 495, Relay Flag : 51N Patrolled the line : UNIDENTIFIED Cause : Unidentified |  | 1 | 6:17 | Morning | Tuesday | 2019 | 7
11844 | 2019-07-09 06:48 | 2019-07-09 06:48 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified | 0 | Darling VCB feeder #4 T/R 1x. Not checked yet. |  | 1 | 6:48 | Morning | Tuesday | 2019 | 7
11845 | 2019-07-09 06:48 | 2019-10-09 13:37 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified | 0 | Checked and found : DRLG4-13.8VCB4 T/R, Counter : 146 - 147, Relay Flag : 51 Patrolled the line found : No Findings Cause : Unidentified |  | 1 | 6:48 | Morning | Tuesday | 2019 | 7
11846 | 2019-07-09 09:58 | 2019-07-09 09:58 | 13.8KV CENTRAL DURI FEEDER #2 | Fair | Planned Maintenance | 0 | 09:58 Manually opened Recloser: 40-BA-02 D/S CD feeder #2. Due to change out transformer on Cathodic protection at KM 125. 11:11 Manually block and closed Recloser: 40-BA-02. Cause: Plan maintenance. |  | 1 | 9:58 | Morning | Tuesday | 2019 | 7
11847 | 2019-07-09 13:57 | 2019-07-09 13:57 | 4.16KV SO RUMBAI FEEDER #4 | Fair | Planned Maintenance | 0 | 13:57 Manually opened South Rumbai feeder #4. Opened Line switch on pole 3RG-08. Due to the work of cutting trees at near SD IT to Rumbai Station. 13:59 Manually block and closed South Rumbai feeder #4. 16:17 Manually opened South Rumbai feeder #4. Closed Line switch on pole 3RG-08. 16:18 Manually block and closed South Rumbai feeder #4 Counter: 178. Cause: Plan maintenance. |  | 1 | 13:57 | Afternoon | Tuesday | 2019 | 7
11848 | 2019-08-09 00:01 | 2019-08-09 00:01 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Normal Condition | - | 8D fdr #7 dropped 121 A (273 - 152 A) Cause: Not Checked Yet |  | 1 | 0:01 | Night | Friday | 2019 | 8
11849 | 2019-08-09 00:01 | 2019-11-09 12:02 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Normal Condition | - | Checked and found: 8DSB-13.8OCB07 Unknown, Counter : 676 - 676, Relay Flag : NONE Patrolled the found : Kondisi Normal Cause : Normal Condition |  | 1 | 0:01 | Night | Friday | 2019 | 8
11850 | 2019-08-09 07:32 | 2019-08-09 07:32 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Duri-Comy fdr#2 T/R 1x. Not checked yet. |  | 1 | 7:32 | Morning | Friday | 2019 | 8
11851 | 2019-08-09 07:32 | 2019-10-09 13:46 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Unidentified | 0 | Checked and found: DCSG-13.8ACB30 T/R, Counter : 109 - 110, Relay Flag : 51N Patrolled the line found : No Findings Cause : Unidentified |  | 1 | 7:32 | Morning | Friday | 2019 | 8
11852 | 2019-08-09 08:17 | 2019-08-09 08:17 | 13.8KV 8D FEEDER #11 | Fair | Dead End Insulator | 38 | 8D fdr#11 T/R 1x. Not checked yet. |  | 1 | 8:17 | Morning | Friday | 2019 | 8
11853 | 2019-08-09 08:17 | 2019-11-09 08:34 | 13.8KV 8D FEEDER #11 | Fair | Dead End Insulator | 38 | Checked and found : 8DSB-13.8OCB11 T/R, Counter : 99924 - 99925, Relay Flag : 51N Patrolled the line found : Flash Over Dead End Cause : Dead End Insulator |  | 1 | 8:17 | Morning | Friday | 2019 | 8
11854 | 2019-08-09 09:17 | 2019-08-09 09:17 | 13.8KV DURI COMMUNITY FEEDER #2 | Fair | Planned Maintenance | 0 | 09:17 Manually opened LBS: 41-BE-08 D/S Duri Comm feeder #2. Due to the work of Schedule Service Recloser at MOSC Mini Substation. 10:33 Manually closed LBS: 41-BE-08. Cause: Plan maintenance. |  | 1 | 9:17 | Morning | Friday | 2019 | 8
11855 | 2019-08-09 10:42 | 2019-08-09 10:42 | 13.8KV 3D FEEDER #5 | Fair | Planned Maintenance | 0 | 10:42 Manually opened 3D OCB feeder #5. Manually opened LBS: 3D-144. Due to the work of connecting jumpers on pole 3D-14C. 11:30 Manually closed 3D OCB feeder #5. Cause: Plan maintenance. |  | 1 | 10:42 | Morning | Friday | 2019 | 8
11856 | 2019-08-09 17:50 | 2019-08-09 17:50 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | N Duri VCB feeder #11 T/R 1x. Not checked yet. |  | 1 | 17:50 | Afternoon | Friday | 2019 | 8
11857 | 2019-08-09 17:50 | 2019-10-09 14:16 | 13.8KV NORTH DURI FEEDER #11 | Fair | Unidentified | 0 | Checked and found: NDRSB-13.8VCB11 T/R, Counter : 190 - 191, Relay Flag : 51N. Patrolled the line found : No Findings Cause : Unidentified |  | 1 | 17:50 | Afternoon | Friday | 2019 | 8
11858 | 2019-09-09 00:44 | 2019-09-09 00:44 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | CD fdr #16 T/R 1x, counter: 358 - 359, R/F: 51N, 51P @1 @2 Cause: Not Patrolled Yet |  | 1 | 0:44 | Night | Monday | 2019 | 9
11859 | 2019-09-09 00:44 | 2019-10-09 13:51 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Checked and found: CDRSG-13.8ACB28 T/R, Counter : 358 - 359, Relay Flag : 51 Patrolled the line found : No Findings Cause : Unidentified |  | 1 | 0:44 | Night | Monday | 2019 | 9
11860 | 2019-09-09 05:31 | 2019-09-09 05:31 | 13.8KV MENGGALA FEEDER #1 | Fair | Unidentified | 211 | 05:31 MENGGALA fdr #1 load dropped 74 A (118 - 44 A) 05:38 Reported no power at MENGGALA North (MENO) field. 07:21 Checked and found Recloser: 19-AN-04 T/SO Counter: 649-651. Patrolled the line nothing found. 09:18 Manually blocked and closed Recloser: 19-AN-04 --> Ok. and then released the block. Cause: Unidentified. |  | 1 | 5:31 | Morning | Monday | 2019 | 9
11861 | 2019-09-09 07:51 | 2019-09-09 07:51 | 13.8KV ROKAN FEEDER #2 | Cloudy | Tree | 17 | Rokan VCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 7:51 | Morning | Monday | 2019 | 9
11862 | 2019-09-09 07:51 | 13/09/2019 09:42 | 13.8KV ROKAN FEEDER #2 | Cloudy | Tree | 17 | Checked and found: RKNSB-13.8VCB2 T/R, Counter : 1309 - 1310, Relay Flag : 51N. Patrolled the line found : Pohon sukun menyentuh line Cause : Tree |  | 1 | 7:51 | Morning | Monday | 2019 | 9
11863 | 2019-10-09 13:03 | 2019-10-09 13:03 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Dead End Insulator | 0 | Sintong feeder #1 load dropped 89A (123-34A) Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 13:03 | Afternoon | Wednesday | 2019 | 10
11864 | 2019-10-09 13:03 | 13/09/2019 11:16 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Dead End Insulator | 0 | Checked And Found STG GFPC Fdr #1 T/R 2x, Ctr 1160 - 1162, R/F 51N Patrolled The Line And Found Flash Over Dead End Insulator @ 1, 3 O/P 25 Ad 46 And 25 Ad 21 Cause: Dead End Insulator |  | 1 | 13:03 | Afternoon | Wednesday | 2019 | 10
11865 | 2019-10-09 13:03 | 2019-10-09 13:03 | 13.8KV SINTONG FEEDER #2 | Foggy and Smoke | Unidentified | 0 | Sintong feeder #2 load dropped 77A (197-120A). Not checked yet. |  | 1 | 13:03 | Afternoon | Wednesday | 2019 | 10
11866 | 2019-10-09 13:03 | 13/09/2019 11:22 | 13.8KV SINTONG FEEDER #2 | Foggy and Smoke | Unidentified | 0 | Checked and found: none None, Counter : - , Relay Flag : NONE Patrolled the line found : none Cause : Unidentified |  | 1 | 13:03 | Afternoon | Wednesday | 2019 | 10
11867 | 2019-10-09 16:08 | 2019-10-09 16:08 | 13.8KV 6D FEEDER #5 | Fair | Emergency | 0 | 16:08 Manually Opened 6D fdr#5. ( Emergency ). Requested GS#4 by maintain level Tank (PumWIP B.42 Cannot star). |  | 1 | 16:08 | Afternoon | Wednesday | 2019 | 10
11868 | 2019-10-09 17:11 | 2019-10-09 17:11 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 0 | C.Duri 13.8KV ACB#18 fdr #15 T/R 1X. ctr:389-390 r/f:51N @1. Not checked yet. |  | 1 | 17:11 | Afternoon | Wednesday | 2019 | 10
11869 | 2019-10-09 17:11 | 13/09/2019 09:46 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Animal | 0 | Checked and found: CDRSG-13.8ACB18 T/R, Counter : 389 - 390, Relay Flag : 51N. Patrolled the line found : ada monyet mati didekat pole Cause : Animal |  | 1 | 17:11 | Afternoon | Wednesday | 2019 | 10
11870 | 2019-11-09 06:09 | 2019-11-09 06:09 | 13.8KV KETIGUL FEEDER#2 | Foggy and Smoke | Animal | 18 | Ketigul fdr #2 T/R 1x Cause: Not Checked Yet |  | 1 | 6:09 | Morning | Saturday | 2019 | 11
11871 | 2019-11-09 06:09 | 13/09/2019 09:49 | 13.8KV KETIGUL FEEDER#2 | Foggy and Smoke | Animal | 18 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 349 - 350, Relay Flag : 51N. Patrolled the line found : Ada burung mati dekat bushing 1 dan 2 Cause : Animal |  | 1 | 6:09 | Morning | Saturday | 2019 | 11
11872 | 2019-11-09 16:09 | 2019-11-09 16:09 | MINAS POWER PLANT |  |  | - | 16:09 MGT #09 S/U then On Line at 16:23 to Backup Power due to NDC#1 Down for Off Line Wash |  | 1 | 16:09 | Afternoon | Saturday | 2019 | 11
11873 | 2019-11-09 16:40 | 2019-11-09 16:40 | MINAS POWER PLANT |  |  | - | 16:40 MGT #8 S/U then On Line at 16:50 to restore Power, due to NDC #1 Down for Off Line wash |  | 1 | 16:40 | Afternoon | Saturday | 2019 | 11
11874 | 2019-11-09 17:38 | 2019-11-09 17:38 | MINAS POWER PLANT |  |  | - | 17:38 MGT #09 S/U then On Line at 18:00 to Backup Power due to NDC#1 Down for Off Line Wash |  | 1 | 17:38 | Afternoon | Saturday | 2019 | 11
11875 | 2019-11-09 18:22 | 2019-11-09 18:22 | CENTRAL DURI POWER PLANT |  |  | - | 18:22 CGT#4 Open Gen. breaker, then closed at 18:28. By Exciter Trouble alarm. |  | 1 | 18:22 | Afternoon | Saturday | 2019 | 11
11876 | 2019-11-09 18:39 | 2019-11-09 18:39 | NORTH DURI POWER PLANT |  |  | - | Off Line NDC#1, then S/D the unit for maintenance. |  | 1 | 18:39 | Afternoon | Saturday | 2019 | 11
11877 | 2019-11-09 20:24 | 2019-11-09 20:24 | MINAS POWER PLANT | Fair | Emergency | 0 | 20:24 It was reported decrease gas from Libo. Pressure 16" Gas line : 240 Psig. 20:45 Manually shut down WIP D/S 8C feeder #4 at GS #2 S/U at 23:24. 21:06 Manually shut down WIP D/S 4B feeder #4 at GS #6 S/U at 00:42(Sept 12,2019) 21:16 Manually shut down WIP D/S 6D feeder #3 at GS #3. S/U at 10:01 (Sept 12,2019). 21:12 Manually shut down WIP D/S BKO feeder #3 at BKO EOR S/U at 00:28(Sept 12,2019). 21:15 Manually shut down WIP D/S 4D feeder #6 at GS #5 S/U at 00:10 (Sept 12,2019). 21:42 Manually shut down WIP D/S CKBS feeder #2 at GS #Kota Batak S/U at 00:55 (Sept 12,2019). 22:35 Call BOB for preparing to S/U Turbine ( Mutagien ). Pressure Up to 228 Psig Freq 59:83. 23:00 Call HCT Minas , Crew HCT OTW to New MDP. 23:42 Call MGT due to Freq 59:79 Hz. Anticipate due to load shedding level 1---->59:70 Hz. |  | 1 | 20:24 | Night | Saturday | 2019 | 11
11878 | 2019-11-09 20:24 | 2019-12-09 00:12 | MINAS POWER PLANT | Fair | Emergency | 0 | Manually shut down feeder load shedding level 2: 00:12 Manually open 4D feeder#5+2 00:14 Manually open 4D feeder#4 00:18 Manually open 5B feeder#7. 00:21 Manually open 8D feeder#3. 00:24 Manually open 5B feeder#4. 00:39 Load BOB separated from CPI system. 00:46 Manually blocked and closed 5B feeder #4 Prod Loss: 12 Bbls / 11 wells. 00:48 Manually blocked and closed 8D feeder#3 Prod Loss: 33 Bbls / 17 wells. 00:51 Manually blocked and closed 5B feeder #7 Prod Loss: 56 Bbls / 5 wells. 00:54 Manually blocked and closed 4D feeder #4 Prod Loss: 21 Bbls / 9 wells. 00:59 Manually blocked and closed 4D feeder #5+2 Prod Loss: 0 ----------------------------------- + Grand total : 122 Bbls /42 wells. Cause: Emergency, Insufficient Copi gas supply. |  | 1 | 20:24 | Night | Saturday | 2019 | 11
11879 | 2019-12-09 22:23 | 2019-12-09 22:23 | NORTH DURI POWER PLANT |  |  | - | 22:23 S/U NDC #1 and then Online the unit at 23:11. |  | 1 | 22:23 | Night | Monday | 2019 | 12
11880 | 2019-12-09 23:20 | 2019-12-09 23:20 | NORTH DURI POWER PLANT |  |  | - | 23:20 Offline NDC #1 and S/D the unit due to vibration. |  | 1 | 23:20 | Night | Monday | 2019 | 12
11881 | 2019-12-09 23:40 | 2019-12-09 23:40 | NORTH DURI POWER PLANT |  |  | - | 23:40 S/U NDC #1 and then Online the unit at 00:06. |  | 1 | 23:40 | Night | Monday | 2019 | 12
11882 | 2019-09-13 08:25 | 2019-09-13 08:25 | MINAS POWER PLANT |  |  | - | Off Line MGT#6, then S/D the unit for S/B. |  | 1 | 8:25 | Morning | Friday | 2019 | 9
11883 | 2019-09-13 08:30 | 2019-09-13 08:30 | MINAS POWER PLANT |  |  | - | Off Line MGT#8, then S/D the unit for S/B. |  | 1 | 8:30 | Morning | Friday | 2019 | 9
11884 | 2019-09-13 08:40 | 2019-09-13 08:40 | MINAS POWER PLANT |  |  | - | Off Line MGT#9, then S/D the unit for S/B. |  | 1 | 8:40 | Morning | Friday | 2019 | 9
11885 | 2019-09-13 20:55 | 2019-09-13 20:55 | 13.8KV DURI COMMUNITY FEEDER #1 | Foggy and Smoke | Tree | 0 | D Community ACB #25 (feeder #1) T/R 1x. Not checked yet. |  | 1 | 20:55 | Night | Friday | 2019 | 9
11886 | 2019-09-13 20:55 | 2019-09-18 07:16 | 13.8KV DURI COMMUNITY FEEDER #1 | Foggy and Smoke | Tree | 0 | Checked And Found DC ACB Fdr #1 T/R 2x, Ctr 138 - 140, R/F 51 Patrolled The Line And Found Danger Tree @ 3 O/P Kt-19 Cause: Tree |  | 1 | 20:55 | Night | Friday | 2019 | 9
11887 | 2019-09-14 06:02 | 2019-09-14 06:02 | 13.8KV DURI COMMUNITY FEEDER #1 | Foggy and Smoke | Tree | 0 | Duri-Comy fdr#1 T/R 1x. Not checked yet. |  | 1 | 6:02 | Morning | Saturday | 2019 | 9
11888 | 2019-09-14 06:02 | 2019-09-18 09:11 | 13.8KV DURI COMMUNITY FEEDER #1 | Foggy and Smoke | Tree | 0 | Checked And Found DC ACB Fdr #1 T/R 2x, Ctr 138 - 140, R/F 51N Patrolled The Line And Found Pohon Menyentuh Line @ 3 O/P Kt 19 Cause: Tree |  | 1 | 6:02 | Morning | Saturday | 2019 | 9
11889 | 2019-09-14 09:16 | 2019-09-14 09:16 | 13.8KV PEMATANG FEEDER #2 | Fair | Dead End Insulator | 60 | Pematang VCB Fdr#2 T/R 1x Not checked yet |  | 1 | 9:16 | Morning | Saturday | 2019 | 9
11890 | 2019-09-14 09:16 | 2019-09-18 11:01 | 13.8KV PEMATANG FEEDER #2 | Fair | Dead End Insulator | 60 | Checked And Found PMT OCB Fdr #2 T/R 1x, Ctr 537 - 538, R/F 51N Patrolled The Line And Found Dead End Flash Over @ 1, 2, O/P 34-Bc-121 Cause: Dead End Insulator |  | 1 | 9:16 | Morning | Saturday | 2019 | 9
11891 | 2019-09-14 17:49 | 2019-09-14 17:49 | 13.8KV NORTH DURI FEEDER #1 | Cloudy | Unidentified | 0 | North Duri VCB fdr#1 T/R 1x not checked yet |  | 1 | 17:49 | Afternoon | Saturday | 2019 | 9
11892 | 2019-09-14 17:49 | 2019-09-18 11:17 | 13.8KV NORTH DURI FEEDER #1 | Cloudy | Unidentified | 0 | Checked And Found NDR VCB Fdr #1 T/R 1x, Ctr 312 - 313, R/F 51N Patrolled The Line But Found Nothing Cause: Unidentified |  | 1 | 17:49 | Afternoon | Saturday | 2019 | 9
11893 | 2019-09-15 15:48 | 2019-09-15 15:48 | 13.8KV KETIGUL FEEDER#1 | Fair | Tree | 17 | Ketigul VCB fdr#1 T/R 1x. Ketigul fdr#2 load dropped 17A (75-57A). Not checked yet. |  | 1 | 15:48 | Afternoon | Sunday | 2019 | 9
11894 | 2019-09-15 15:48 | 2019-09-18 09:06 | 13.8KV KETIGUL FEEDER#1 | Fair | Tree | 17 | Checked And Found PKTGL VCB Fdr #1 T/R 1x, Ctr 312 - 313, R/F 51N Patrolled The Line And Found Pohon Akasia Menyentuh Line @ 1, 2 O/P 12-G.3-11 Cause: Tree |  | 1 | 15:48 | Afternoon | Sunday | 2019 | 9
11895 | 2019-09-17 07:00 | 2019-09-17 07:00 | 13.8KV NORTH DURI FEEDER #7 | Foggy and Smoke | Animal | 78 | 07:00 NDuri VCB Fdr#7 T/LO, Ctr: 107-111, R/F: 51 @123 09:10 Patrolled the L1ne, found Dead squirrel on Bypass Recl 10-L1-17 09:25 Block & Closed NDuri VCB fdr#7, then released the Block Cause: Animal (Squirrel) |  | 1 | 7:00 | Morning | Tuesday | 2019 | 9
11896 | 2019-09-17 07:00 | 2019-09-20 10:49 | 13.8KV NORTH DURI FEEDER #7 | Foggy and Smoke | Animal | 78 | Checked And Found NDR VCB Fdr #7 T/R 4x, Ctr 107 - 111, R/F 50N Patrolled The Line And Found Tupai Mati Di Bypass Recloser @2 O/P 10 L1 17 Cause: Animal |  | 1 | 7:00 | Morning | Tuesday | 2019 | 9
11897 | 2019-09-17 09:06 | 2019-09-17 09:06 | 44KV PEMATANG MAIN - PETANI LINE | Foggy and Smoke | Unidentified | 125 | 44KV Line Pematang main - Petani GCB#1 T/R 1x Not checked yet Production loss Petani feeder #1 = 43 Bbls / 17 wells. Production loss Petani feeder #2 = 74 Bbls / 33 wells. -------------------------------------------------------------- + Grand total = 117 Bbls / 50 wells. |  | 1 | 9:06 | Morning | Tuesday | 2019 | 9
11898 | 2019-09-17 09:06 | 2019-09-19 15:47 | 44KV PEMATANG MAIN - PETANI LINE | Foggy and Smoke | Unidentified | 125 | Checked And Found PMT OCB Fdr #1 T/R 1x, Ctr 194 - 195, R/F 51N Patrolled The Line But Found Nothing O/P Cause: Unidentified |  | 1 | 9:06 | Morning | Tuesday | 2019 | 9
11899 | 2019-09-18 10:26 | 2019-09-18 10:26 | NORTH DURI POWER PLANT | Foggy and Smoke |  | - | 10:26 NDC CT #1 Auto Unload by alarm "Rotor Cooler Temp. High". Load Dropped from 90.47MW to 58.16 MW. Freq. System dropped to 59:88 Hzs. (No Load shedding). 15:47 NDC CT #1 Back to normal after Replaced VSD Rotor Cooling Motor. |  | 1 | 10:26 | Morning | Wednesday | 2019 | 9
11900 | 2019-09-18 13:44 | 2019-09-18 13:44 | 13.8KV SINTONG FEEDER #2 | Foggy and Smoke | Unidentified | 79 | 13:44 Sintong 13.8KV GCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 13:44 | Afternoon | Wednesday | 2019 | 9
11901 | 2019-09-18 16:55 | 2019-09-18 16:55 | 13.8KV KETIGUL FEEDER#2 | Foggy and Smoke | Unidentified | 18 | 16:55 Ketigul 13.8KV GCB fdr #2 T/R 1X. Ketigul fdr #1 load dropped 10A (108-98A). Not checked yet. |  | 1 | 16:55 | Afternoon | Wednesday | 2019 | 9
11902 | 2019-09-18 16:55 | 2019-09-20 10:45 | 13.8KV KETIGUL FEEDER#2 | Foggy and Smoke | Unidentified | 18 | Checked And Found PKTGL VCB Fdr #2 T/R 1x, Ctr 350 - 351, R/F 51N Patrolled The Line But Found Nothing Cause: Unidentified |  | 1 | 16:55 | Afternoon | Wednesday | 2019 | 9
11903 | 2019-09-19 10:56 | 2019-09-19 10:56 | 13.8KV KETIGUL FEEDER#1 | Fair | Planned Maintenance | 5 | 10:56 Manual Open LBS 32-AJ-01, closed at 11:39 MTCE team to dismantle conductor ex installation RCL 33-AK-09 (patrol after outage finding) Cause: Planned Maintenance |  | 1 | 10:56 | Morning | Thursday | 2019 | 9
11904 | 2019-09-19 14:22 | 2019-09-19 14:22 | 13.8KV NELLA FEEDER #1 | Foggy and Smoke | Animal | 48 | Nella fdr #1 load dropped 119 A (207 - 88 A) Nella GFPC T/R 1x Cause: Not Checked Yet |  | 1 | 14:22 | Afternoon | Thursday | 2019 | 9
11905 | 2019-09-19 16:23 | 2019-09-19 16:23 | 13.8KV SINTONG FEEDER #2 | Foggy and Smoke | Tree | 78 | 16:23 Sintong GFPC T/R 1x Sintong fdr #2 T/R 1x Cause: Not Checked Yet |  | 1 | 16:23 | Afternoon | Thursday | 2019 | 9
11906 | 2019-09-19 17:47 | 2019-09-19 17:47 | 13.8KV SINTONG FEEDER #1 | Foggy and Smoke | Unidentified | 32 | 17:47 SINTONG fdr #1 T/R 1x SINTONG GFPC T/R 1x Cause: Not Checked Yet |  | 1 | 17:47 | Afternoon | Thursday | 2019 | 9
11907 | 2019-09-20 13:46 | 2019-09-20 13:46 | 230KV N. Duri - KBJ Line - 1 | Foggy and Smoke | Unidentified | 0 | 13:46 230 kV Line-1 DRI - KBJ T/R1x 230 kV GCB #23 ND T/R 1x 230 kV GCB #25 ND T/R 1x 230 kV GCB #91 KBJ T/R 1x 230 kV GCB #92 KBJ T/R 1x Cause: Not Checked Yet |  | 1 | 13:46 | Afternoon | Friday | 2019 | 9
11908 | 2019-09-20 13:46 | 2019-09-23 15:04 | 230KV N. Duri - KBJ Line - 1 | Foggy and Smoke | Unidentified | 0 | Checked And Found - ND-KBJ1 GCB #92 T/R 1x, Ctr 378 - 379, R/F 87 - ND-KBJ1 GCB #23 T/R 1x, Ctr 249 - 250, R/F 87 - ND-KBJ1 GCB #25 T/R 1x, Ctr 205 - 205, R/F NONE - ND-KBJ1 GCB #91 T/R 1x, Ctr 294 - 294, R/F NONE Patrolled The Line And Found Nothing Found Cause: Unidentified |  | 1 | 13:46 | Afternoon | Friday | 2019 | 9
11909 | 2019-09-20 14:20 | 2019-09-20 14:20 | 13.8KV MINAS FEEDER #4 | Foggy and Smoke | Planned Maintenance | 47 | 14:20 Manual Open RCL 7D-150 (MNS fdr #4), closed at 14:36 to dismantle 300 kVA TX (LTC well) at 8D #11 Cause: Planned Maintenance |  | 1 | 14:20 | Afternoon | Friday | 2019 | 9
11910 | 2019-09-20 17:29 | 2019-09-20 17:29 | 13.8KV BANGKO FEEDER #4 | Fair | Unidentified | 11 | Bangko fdr #4 load dropped 79 A (175 - 96 A) --> WIP Benar GS Bangko GFPC T/R 1x Cause: Not Checked Yet |  | 1 | 17:29 | Afternoon | Friday | 2019 | 9
11911 | 2019-09-21 06:21 | 2019-09-21 06:21 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | C.Duri ACB#21 fdr#4 T/R 1x Ctr:520-521 R/F:51N, 51@2. Not Patrolled yet. |  | 1 | 6:21 | Morning | Saturday | 2019 | 9
11912 | 2019-09-21 06:21 | 2019-09-26 16:38 | 13.8KV CENTRAL DURI FEEDER #4 | Fair | Unidentified | 0 | Checked and found ACB CD fdr #4 T/R 1x, ctr: 520-521, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 6:21 | Morning | Saturday | 2019 | 9
11913 | 2019-09-21 07:01 | 2019-09-21 07:01 | 44KV NORTH DURI - DUMAI LINE | Foggy and Smoke | Tree | 0 | NDURI 44KV Line to Dumai GCB#01 T/R 1x Not checked yet |  | 1 | 7:01 | Morning | Saturday | 2019 | 9
11914 | 2019-09-21 07:01 | 2019-09-22 15:07 | 44KV NORTH DURI - DUMAI LINE | Foggy and Smoke | Tree | 0 | Checked and found 44 kV GCB #1 ND T/R 1x, ctr: 141-142, R/F: 51P @1 @3 Patrolled the line and found high trees near pole DD 177-178, DD 262-263 Cause : Tree |  | 1 | 7:01 | Morning | Saturday | 2019 | 9
11915 | 2019-09-22 11:20 | 2019-09-22 11:20 | 13.8KV PINANG FEEDER #1 | Foggy and Smoke | Emergency | - | 11:20 Manual Open VCB PINANG fdr #1 Requested by PINANG GS due to broken production line hit by outsider truck. Cause: Emergency |  | 1 | 11:20 | Morning | Sunday | 2019 | 9
11916 | 2019-09-23 15:43 | 2019-09-23 15:43 | 13.8KV 4B FEEDER #2 | Heavy Rain | Lightning | 34 | 15:43 4B VCB fdr #6 T/SO 17:12 Checked and found VCB fdr #6 T/LO, ctr: 193-194, R/F: 50P @2 17:18 Blocked and close 4B VCB fdr #6, then release the block Cause: Not Patrolled Yet 19:36 It was reported no power D/S fdr. 4B fdr#6. 20:50 Checked & found Recl. 4B-148 T/So Ctr:83-84. 20:56 Blocked & closed Recl. 4B-148, then release the block. Cause: Not Patrolled yet. |  | 1 | 15:43 | Afternoon | Monday | 2019 | 9
11917 | 2019-09-23 15:43 | 2019-09-30 20:54 | 13.8KV 4B FEEDER #2 | Heavy Rain | Lightning | 34 | Checked and found : 4BSB-13.8OCB2 T/LO, Counter : 193 - 194, Relay Flag : 50. Patrolled the line found : None Cause : Lightning |  | 1 | 15:43 | Afternoon | Monday | 2019 | 9
11918 | 2019-09-23 17:56 | 2019-09-23 17:56 | 13.8KV DARLING VCB FEEDER #4 | Heavy Rain | Unidentified | 0 | Darling fdr #4 T/R 1x Cause: Not Checked Yet |  | 1 | 17:56 | Afternoon | Monday | 2019 | 9
11919 | 2019-09-23 17:56 | 2019-09-26 16:32 | 13.8KV DARLING VCB FEEDER #4 | Heavy Rain | Unidentified | 0 | Checked and found DRL fdr #4 T/R 1x, ctr: 147 - 148, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 17:56 | Afternoon | Monday | 2019 | 9
11920 | 2019-09-23 18:01 | 2019-09-23 18:01 | 13.8KV NORTH DURI FEEDER #1 | Heavy Rain | Animal | 0 | North Duri fdr #1 T/R 1x Cause: Not Checked Yet |  | 1 | 18:01 | Afternoon | Monday | 2019 | 9
11921 | 2019-09-23 18:01 | 2019-09-27 14:42 | 13.8KV NORTH DURI FEEDER #1 | Heavy Rain | Animal | 0 | Checked and found : NDRSB-13.8VCB1 T/R, Counter : 313 - 314, Relay Flag : 51 Patrolled the line found : Burung mati di dekat pole Cause : Animal |  | 1 | 18:01 | Afternoon | Monday | 2019 | 9
11922 | 2019-09-23 18:07 | 2019-09-23 18:07 | 13.8KV CENTRAL DURI FEEDER #4 | Heavy Rain | Unidentified | 0 | CD fdr #4 T/R 1x, ctr: 521-522, R/F: 51P @2 Cause: Not Patrolled Yet |  | 1 | 18:07 | Afternoon | Monday | 2019 | 9
11923 | 2019-09-23 18:07 | 2019-09-26 16:21 | 13.8KV CENTRAL DURI FEEDER #4 | Heavy Rain | Unidentified | 0 | Checked and found ACB 21 (CD fdr #4) T/R 1x, ctr: 521-522, R/F: 51P @2 Patrolled the line but found nothing Cause : Unidentified |  | 1 | 18:07 | Afternoon | Monday | 2019 | 9
11924 | 2019-09-23 18:08 | 2019-09-23 18:08 | 13.8KV NORTH DURI FEEDER #9 | Heavy Rain | Unidentified | 0 | ND fdr #9 T/R 1x Cause: Not Checked Yet |  | 1 | 18:08 | Afternoon | Monday | 2019 | 9
11925 | 2019-09-23 18:08 | 2019-09-27 14:44 | 13.8KV NORTH DURI FEEDER #9 | Heavy Rain | Unidentified | 0 | Checked and found: NDRSB-13.8VCB9 T/R, Counter : 80 - 81, Relay Flag : 51 Patrolled the line found : No Findings Cause : Unidentified |  | 1 | 18:08 | Afternoon | Monday | 2019 | 9
11926 | 2019-09-23 18:17 | 2019-09-23 18:17 | 13.8KV CENTRAL DURI FEEDER #5 | Heavy Rain | Tree | 250 | 18:17 C.Duri ACB fdr #5 load dropped 66A (111-45 A) 18:18 Reported no power at CGS #3 and any spark at trafo near CGS #3 19:05 Checked & found Recl. 03-4-16 T/Lo Ctr: 230-233. Patrolled the line & found Fall Down trees near pole 03-4-16, then cleaning. 20:45 Blocked & Closed Recl. 03-4-16, then release the block. Cause: Tree. |  | 1 | 18:17 | Afternoon | Monday | 2019 | 9
11927 | 2019-09-23 18:35 | 2019-09-23 18:35 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 1112 | 18:35 It was reported no power at well Petani#31, #45, #101, #120. 23:30 Checked & found Recloser: 33-AY-47 T/LO Counter:170-175. Patrolled the line but found nothing. |  | 1 | 18:35 | Afternoon | Monday | 2019 | 9
11928 | 2019-09-23 18:35 | 2019-09-24 03:50 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 1112 | 03:50 Blocked & closed Recloser: 33-AY-47 --> OK. and then release the block. 05:49 It was reported no power D/S Recloser: 33-AY-47. 08:09 Checked and found Recloser: 33-AY-47 T/O. Counter : 170-175 did not change. Patrolled the line found nothing. 08:21 Manually blocked and closed Recloser: 33-AY-47 --> OK. and then released the block. Cause : Unidentified. |  | 1 | 18:35 | Afternoon | Monday | 2019 | 9
11929 | 2019-09-23 18:35 | 2019-09-25 07:11 | 13.8KV PETANI FEEDER #1 | Fair | Unidentified | 1112 | Checked And Found PTN 13.8KV Fdr #1 T/R 5x, Ctr 170 - 175, Patrolled The Line But Found Nothing Cause: Unidentified |  | 1 | 18:35 | Afternoon | Monday | 2019 | 9
11930 | 2019-09-23 22:26 | 2019-09-23 22:26 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | - | 22:26 CD fdr #4 load dropped 40 A (155 - 115) Cause: Not Checked Yet |  | 1 | 22:26 | Night | Monday | 2019 | 9
11931 | 2019-09-23 22:26 | 2019-09-24 09:40 | 13.8KV CENTRAL DURI FEEDER #14 | Fair | Unidentified | - | 09:40 Checked and found - RCL 06-Q2-02 T/LO, ctr: 70-74, R/F 51P @1, @2 - RCL 06-R3-23 T/SO, ctr: 99-102, R/F: None Patrolled the line but found nothing 11:06 Blocked and Close RCL 06-Q2-02, OK then release the block 11:17 Blocked and Close RCL 06-R3-23, OK then release the block Cause: Unidentified |  | 1 | 22:26 | Night | Monday | 2019 | 9
11932 | 2019-09-24 05:28 | 2019-09-24 05:28 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Animal | 0 | 05:28 Dumai 4,16Kv ACB#12 fdr#1 T/O. 07:21 Checked and found VCB 12 (fdr #1) T/O, ctr: 300 - 302, R/F 51P @1, 2, 3 Patrolled the line and found high trees near pole I-02 to I-03 Then Execute/Cutting the trees 09:25 Block and close Dumai VCB fdr #1, OK then release the block. Cause: Trees |  | 1 | 5:28 | Morning | Tuesday | 2019 | 9
11933 | 2019-09-24 05:28 | 2019-09-25 06:51 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Animal | 0 | Checked And Found DMI WHARF FEEDER Fdr #1 T/R 2x, Ctr 300 - 302, R/F 50 Patrolled The Line And Found Monkey Dead On Pole W23, High Trees On Pole W 102 To W 103 @1 O/P W23 And W102 And W 103 Cause: Animal |  | 1 | 5:28 | Morning | Tuesday | 2019 | 9
11934 | 2019-09-24 09:35 | 2019-09-24 09:35 | MINAS POWER PLANT |  |  | - | 09:35 MGT-8 Start Up and then Online at 09:56 due to plan CDGT #2 S/D for repair turning vane |  | 1 | 9:35 | Morning | Tuesday | 2019 | 9
11935 | 2019-09-24 10:07 | 2019-09-24 10:07 | CENTRAL DURI POWER PLANT |  |  | - | 10:07 CDGT #2 Offline and then S/D at 10:10 for repair turning vane leak |  | 1 | 10:07 | Morning | Tuesday | 2019 | 9
11936 | 2019-09-24 10:08 | 2019-09-24 10:08 | 13.8KV PEMATANG FEEDER #1 | Fair | Others | 26 | 10:08 Pematang fdr #1 T/R 1x Pematang fdr #2 dropped 105 A (108 - 3 A) Cause: Not Patrolled Yet |  | 1 | 10:08 | Morning | Tuesday | 2019 | 9
11937 | 2019-09-24 10:08 | 2019-09-26 16:38 | 13.8KV PEMATANG FEEDER #1 | Fair | Others | 26 | Checked and found PMT OCB fdr #1 T/R 1x, ctr: 183-184, R/F 51P @1 Patrolled the line and found b/o bushing recloser 34-BC-14 (@1 layer 1) Cause : Others (bushing) |  | 1 | 10:08 | Morning | Tuesday | 2019 | 9
11938 | 2019-09-24 17:30 | 2019-09-24 17:30 | 13.8KV MINAS FEEDER #4 | Fair | Animal | 47 | 17:30 Minas fdr #4 (ACB-1) T/R 1x Cause: Not Checked Yet |  | 1 | 17:30 | Afternoon | Tuesday | 2019 | 9
11939 | 2019-09-24 17:30 | 2019-09-28 21:09 | 13.8KV MINAS FEEDER #4 | Fair | Animal | 47 | Checked and found Minas feeder #4 T/R 1x, ctr: 103-104, R/F: 51N Patrolled the line and found animal (bird) shorting the insulator @2 o/p 7D-121 Cause : Animal |  | 1 | 17:30 | Afternoon | Tuesday | 2019 | 9
11940 | 2019-09-24 23:59 | 2019-09-24 23:59 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 14 | 8D VCB fdr#7 T/R 1x Not checked yet |  | 1 | 23:59 | Night | Tuesday | 2019 | 9
11941 | 2019-09-24 23:59 | 2019-09-28 21:03 | 13.8KV 8D FEEDER #7 | Rain and Lightning | Lightning | 14 | Checked and found 8D feeder #7 T/R 1x, ctr: 676-677, R/F: 50P @2 Patrolled the line and found broken deadend and pin insulator @2 o/p 8D-90 and pole 7E-72 Cause : Lightning |  | 1 | 23:59 | Night | Tuesday | 2019 | 9
11942 | 2019-09-25 02:29 | 2019-09-25 02:29 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Others | 7 | Libo VCB fdr#1 T/R 1x. Not checked yet |  | 1 | 2:29 | Night | Wednesday | 2019 | 9
11943 | 2019-09-25 02:29 | 2019-09-26 08:10 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Others | 7 | Checked And Found LBO OCB Fdr #1 T/R 1x, Ctr 591 - 592, R/F 51 Patrolled The Line But Found Nothing Cause: Others |  | 1 | 2:29 | Night | Wednesday | 2019 | 9
11944 | 2019-09-25 02:39 | 2019-09-25 02:39 | ROKAN SUBSTATION | Fair | Under investigation | 392 | 02:39 Petani,Rokan,Ketigul RTU fail. 11:39 Checked & found Rokan 115KV C/S Trip R/F:51G. No power at Rokan Substation. 13:18 Back to normal Rokan DC system Voltage. 13:29 Manually open Rokan OCB fdr#2. Manually open Rokan OCB fdr#3. Manually open Rokan OCB fdr#4. 13:31 Manually closed Rokan 115KV C/S but failed. 14:00 Manually blocked and closed Rokan OCB fdr#2 --> OK and then released the block 14:02 Manually blocked and closed Rokan OCB fdr#3 --> OK and then released the block. 14:02 Manually blocked and closed Rokan OCB fdr#4 --> OK and then released the block. 13:59 Manually closed Rokan 115KV C/S OK. Rokan substation back to normal. Cause : Under investigation. |  | 1 | 2:39 | Night | Wednesday | 2019 | 9
11945 | 2019-09-25 11:39 | 2019-09-25 11:39 | 13.8KV 4D FEEDER #2 | Heavy Rain | Lightning | 62 | 4D OCB fdr#2 T/R 4x. Not checked yet. |  | 1 | 11:39 | Morning | Wednesday | 2019 | 9
11946 | 2019-09-25 11:39 | 2019-09-28 21:14 | 13.8KV 4D FEEDER #2 | Heavy Rain | Lightning | 62 | Checked and found 4D fdr #2 T/LO, ctr: N/A, R/F: 50N Patrolled the line and found broken pin insulator @2 o/p 36DN-12 Cause : Lightning |  | 1 | 11:39 | Morning | Wednesday | 2019 | 9
11947 | 2019-09-25 12:00 | 2019-09-25 12:00 | 13.8KV MINAS FEEDER #1 | Heavy Rain | Others | 176 | Minas fdr#1 load dropped 132A (185-53A). 14:14 It was reported no power at well 7D#13,13N,23,23E,32,33,42,43,42N,19. 15:53 Patrolled the line found recloser 7D#20 T/so display blur. Blocked & closed reclosed 7D#20 Ok and then relosed the block. Cause: Not patrolled yet. |  | 1 | 12:00 | Afternoon | Wednesday | 2019 | 9
11948 | 2019-09-25 12:00 | 2019-09-28 21:11 | 13.8KV MINAS FEEDER #1 | Heavy Rain | Others | 176 | Checked and found RCL 7D-20 T/SO, ctr: N/A, R/F: None Patrolled the line but found nothing Cause : Others |  | 1 | 12:00 | Afternoon | Wednesday | 2019 | 9
11949 | 2019-09-25 19:12 | 2019-09-25 19:12 | 13.8KV 4D FEEDER #2 | Heavy Rain | Pin Insulator | 138 | 19:12 4D fdr #2 T/LO (load 13 A), R/F: 81, ctr: --- (heavy rain) Suspended to close (conformed by TL OPS South) Cause: Not Patrolled Yet |  | 1 | 19:12 | Night | Wednesday | 2019 | 9
11950 | 2019-09-25 19:12 | 2019-01-10 07:30 | 13.8KV 4D FEEDER #2 | Heavy Rain | Pin Insulator | 138 | Checked and found 4D OCB feeder #2 T/SO R/F: 51@2 Counter: 290-290. Patrolled the line found @2 broken pin insulator on pole 36-DN-12. Cause: Pin Insulator. |  | 1 | 19:12 | Night | Wednesday | 2019 | 9
11951 | 2019-09-25 19:14 | 2019-09-25 19:14 | 13.8KV 4D FEEDER #4 | Heavy Rain | Dead End Insulator | 4 | 19:14 4D fdr #4 T/R 1x Cause: Not Checked Yet |  | 1 | 19:14 | Night | Wednesday | 2019 | 9
11952 | 2019-09-25 19:14 | 2019-01-10 07:35 | 13.8KV 4D FEEDER #4 | Heavy Rain | Dead End Insulator | 4 | Checked and found 4B OCB feeder #4 T/R 1x . R/F: 51 @1,@3 Counter: 298-299. Patrolled the line found @1 broken dead end insulator on pole 3E-61. Cause: Dead end insulator. |  | 1 | 19:14 | Night | Wednesday | 2019 | 9
11953 | 2019-09-26 08:04 | 2019-09-26 08:04 | 13.8KV PETANI FEEDER #2 | Fair | Others | 56 | Petani OCB feeder#2 T/R 1x. Petani feeder#1 load dropped 200A (243-43A). Not checked yet. |  | 1 | 8:04 | Morning | Thursday | 2019 | 9
11954 | 2019-09-26 08:04 | 2019-09-30 14:05 | 13.8KV PETANI FEEDER #2 | Fair | Others | 56 | Checked and found: PTNSB-13.8OCB2 T/R, Counter : 319 - 320, Relay Flag : 51N. Patrolled the line found : Isolator FCO pecah 45% di layer 5, di phase 1 dan di bagian tengah ada bekas terbakar Operated Device : PTNSB-13.8OCB2 T/R Counter : 319 - 320 Relay Flag : 51N Finding Patrol : Dead End flash over di layer 1 Phase : 1 Pole : 34 AY 9 Patrol by : Menalito Input by : VAVT Cause : Others |  | 1 | 8:04 | Morning | Thursday | 2019 | 9
11955 | 2019-09-27 14:20 | 2019-09-27 14:20 | CENTRAL DURI POWER PLANT |  |  | - | 14:20 S/U CDGT #2 and then Online the unit at 15:02. |  | 1 | 14:20 | Afternoon | Friday | 2019 | 9
11956 | 2019-09-27 15:03 | 2019-09-27 15:03 | 13.8KV NEW KOTABATAK FEEDER #4 | Fair | Lightning | 14 | 15:03 NKBS VCB feeder #4 T/R 1x. NKBS feeder #3 load dropped 21A (116-95A). 15:16 It was reported no power at AREA #2 KB GS. 16:55 Checked and found Recloser at Area #2 T/SO Counter: 1013-1014. Manually blocked and closed Recloser at Area #2 --> Ok and then released the block. Cause: Not patrolled yet. |  | 1 | 15:03 | Afternoon | Friday | 2019 | 9
11957 | 2019-09-27 15:03 | 2019-09-28 09:54 | 13.8KV NEW KOTABATAK FEEDER #4 | Fair | Lightning | 14 | Checked and found NKB fdr #4 T/R 1x, ctr: 287 - 288, R/F: 51N Patrolled the line but found nothing Cause : Lightning |  | 1 | 15:03 | Afternoon | Friday | 2019 | 9
11958 | 2019-09-27 15:10 | 2019-09-27 15:10 | MINAS POWER PLANT |  |  | - | 15:10 Offline MGT #8 and then S/D the unit for standby. |  | 1 | 15:10 | Afternoon | Friday | 2019 | 9
11959 | 2019-09-27 16:20 | 2019-09-27 16:20 | CENTRAL DURI POWER PLANT |  |  | - | 16:20 Offline CDGT #5 and then S/D the unit at 16:22. due to LTC stuck. |  | 1 | 16:20 | Afternoon | Friday | 2019 | 9
11960 | 2019-09-28 07:07 | 2019-09-28 07:07 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 15 | Ketigul VCB feeder #2 T/R 1x. Ketigul feeder #1 load dropped 22A (114-92A). Ketigul feeder #3 load dropped 11A (47-36A). Not checked yet. |  | 1 | 7:07 | Morning | Saturday | 2019 | 9
11961 | 2019-09-28 07:07 | 2019-03-10 10:15 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 15 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 351 - 352, Relay Flag : 51 Patrolled the line found : Dead End insulator flash over di layer1 pada phase 2 Cause : Dead End Insulator |  | 1 | 7:07 | Morning | Saturday | 2019 | 9
11962 | 2019-09-28 09:20 | 2019-09-28 09:20 | 44KV PEMATANG MAIN - RANGAU LINE | Fair | Emergency | 280 | 09:20 Manually open OCB #2 (44KV Pematang - Rangau). Due to repair F/O (fiber Optic) on pole RGU #50. 14:43 Manually blocked & Closed OCB #2. Cause: Emergency. |  | 1 | 9:20 | Morning | Saturday | 2019 | 9
11963 | 2019-09-28 09:39 | 2019-09-28 09:39 | 13.8KV SURAM FEEDER #1 | Fair | Animal | 0 | Suram OCB feeder#1 T/R 1x. Not Checked yet. |  | 1 | 9:39 | Morning | Saturday | 2019 | 9
11964 | 2019-09-28 09:39 | 2019-09-30 07:46 | 13.8KV SURAM FEEDER #1 | Fair | Animal | 0 | Checked and found: SRMSB-13.8OCB1 T/R, Counter : 122 - 123, Relay Flag : 51N. Patrolled the line found Animal (Monkey) Cause : Animal. |  | 1 | 9:39 | Morning | Saturday | 2019 | 9
11965 | 2019-09-28 10:00 | 2019-09-28 10:00 | 13.8KV DURI FIELD FEEDER #1 | Fair | Planned Maintenance | 0 | 10:00 Manually Open Recloser 01-06-30 D/S D.Field feeder#1. Due to repair Cros arm corrosion on pole 01-06-07. 12:40 Manually blocked and Closed Recloser 01-06-30 Counter:89-90. Cause: Plan Maintenance. |  | 1 | 10:00 | Morning | Saturday | 2019 | 9
11966 | 2019-09-28 13:17 | 2019-09-28 13:17 | MINAS POWER PLANT |  |  | - | 13:17 S/U MGT #9 and then Online the unit at 13:35. |  | 1 | 13:17 | Afternoon | Saturday | 2019 | 9
11967 | 2019-09-28 13:54 | 2019-09-28 13:54 | MINAS POWER PLANT |  |  | - | 13:54 Offline MGT #10 and then S/D the unit for standby. |  | 1 | 13:54 | Afternoon | Saturday | 2019 | 9
11968 | 2019-09-28 15:09 | 2019-09-28 15:09 | 13.8KV NORTH DURI FEEDER #11 | Rain and Lightning | Others | 0 | N.Duri VCB feeder #11 T/R 1x. Not checked yet. |  | 1 | 15:09 | Afternoon | Saturday | 2019 | 9
11969 | 2019-09-28 15:09 | 2019-03-10 10:00 | 13.8KV NORTH DURI FEEDER #11 | Rain and Lightning | Others | 0 | Checked and found : NDRSB-13.8VCB11 T/R, Counter : 191 - 192, Relay Flag : 50 Patrolled the line found : Insulator By Pass Recloser Pecah Cause : Others |  | 1 | 15:09 | Afternoon | Saturday | 2019 | 9
11970 | 2019-09-28 15:11 | 2019-09-28 15:11 | 13.8KV NORTH DURI FEEDER #9 | Rain and Lightning | Unidentified | 0 | N.Duri VCB feeder #9 T/R 1x. Not checked yet. |  | 1 | 15:11 | Afternoon | Saturday | 2019 | 9
11971 | 2019-09-28 15:11 | 2019-03-10 09:55 | 13.8KV NORTH DURI FEEDER #9 | Rain and Lightning | Unidentified | 0 | Checked and found : NDRSB-13.8VCB9 T/R, Counter : 81 - 82, Relay Flag : 50 Patrolled the line found : Not Found Cause : Unidentified |  | 1 | 15:11 | Afternoon | Saturday | 2019 | 9
11972 | 2019-09-28 15:12 | 2019-09-28 15:12 | 13.8KV NORTH DURI FEEDER #7 | Rain and Lightning | Unidentified | 0 | N.Duri VCB feeder #7 T/R 1x. Not checked yet. |  | 1 | 15:12 | Afternoon | Saturday | 2019 | 9
11973 | 2019-09-28 15:12 | 2019-03-10 10:38 | 13.8KV NORTH DURI FEEDER #7 | Rain and Lightning | Unidentified | 0 | Checked and found: NDRSB-13.8VCB7 T/R, Counter : 111 - 112, Relay Flag : 50N. Patrolled the line found : Not found Cause : Unidentified |  | 1 | 15:12 | Afternoon | Saturday | 2019 | 9
11974 | 2019-09-28 15:14 | 2019-09-28 15:14 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Unidentified | 0 | C.Duri VCB feeder #4 T/R 1x. R/F: 50 @1,@2 Counter: 522-523. Not patrolled yet. |  | 1 | 15:14 | Afternoon | Saturday | 2019 | 9
11975 | 2019-09-28 15:14 | 2019-03-10 10:27 | 13.8KV CENTRAL DURI FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked and found: CDRSG-13.8ACB21 T/R, Counter : 522 - 523, Relay Flag : 50 Patrolled the line found : Not Found Cause : Unidentified |  | 1 | 15:14 | Afternoon | Saturday | 2019 | 9
11976 | 2019-09-28 15:39 | 2019-09-28 15:39 | 13.8KV BATANG FEEDER #1 | Rain and Lightning | Unidentified | 0 | Batang OCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 15:39 | Afternoon | Saturday | 2019 | 9
11977 | 2019-09-28 15:39 | 2019-04-10 13:56 | 13.8KV BATANG FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked and found: RCL GFPC BTG T/R, Counter : 970 - 971, Relay Flag : 50N. Patrolled the line found : Not Found Cause : Unidentified |  | 1 | 15:39 | Afternoon | Saturday | 2019 | 9
11978 | 2019-09-28 15:51 | 2019-09-28 15:51 | 13.8KV MENGGALA GFPC | Rain and Lightning | Tree | - | Menggala GFPC T/R 1x. No load dropped at any feeders. Not checked yet. |  | 1 | 15:51 | Afternoon | Saturday | 2019 | 9
11979 | 2019-09-28 15:51 | 2019-02-10 09:27 | 13.8KV MENGGALA GFPC | Rain and Lightning | Tree | - | Checked and found: 13.8KVMGL_GFPC T/R, Counter : 111 - 112, Relay Flag : 51N Patrolled the line found : High Tree (sawit) Operated Device : 13.8KVMGL_GFPC T/R Counter : 111 - 112 Relay Flag : 51N Finding Patrol : Flash Over 10% Phase : 1 Pole : Near Well MENO#04 Patrol by : PT.BKP Input by : HZML Cause : Tree |  | 1 | 15:51 | Afternoon | Saturday | 2019 | 9
11980 | 2019-09-28 15:52 | 2019-09-28 15:52 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Unidentified | - | Batang OCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 15:52 | Afternoon | Saturday | 2019 | 9
11981 | 2019-09-28 15:52 | 2019-01-10 14:19 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Unidentified | - | Checked and found: BTGSB-13.8OCB2 T/R, Counter : 191 - 194, Relay Flag : 51. Patrolled the line found : No Findings Cause : Unidentified |  | 1 | 15:52 | Afternoon | Saturday | 2019 | 9
11982 | 2019-09-28 16:08 | 2019-09-28 16:08 | 115KV CENTRAL DURI - BATANG LINE | Rain and Lightning | Suspension Insulator | - | 16:08 C.Duri 115 Kv OCB #31 T/R 1x. C.Duri 115 Kv OCB #33 T/R 1x. Batang 115 Kv OCB #1 T/R 1x. Sintong 115 Kv OCB #25 T/R 1x. * No Power at Batang Substation. 1. Batang OCB feeder #1 ( Batang field , PHE ). 2. Batang OCB feeder #2 ( Rantau Bais field ). 3. Batang OCB feeder #3 ( Pemburu, Candi, Balam GS ). - Respectively load dropped at: - So.Balam feeder #1 Load dropped 18A (146-128A). - So.Balam feeder #2 Load dropped 11A (130-119A). EOR. - So.Balam feeder #4 Load dropped 25A (190-165A). - Nella feeder #1 Load dropped 38A (214-176A). - Nella feeder #2 Load dropped 18A (76-58A). - Bangko feeder #1 Load dropped 18A (158-140A). - Bangko feeder #4 Load dropped 12A (172-160A). - Menggala feeder #1 Load dropped 10A (138-128A). No checked yet. |  | 1 | 16:08 | Afternoon | Saturday | 2019 | 9
11983 | 2019-09-28 16:08 | 2019-04-10 14:07 | 115KV CENTRAL DURI - BATANG LINE | Rain and Lightning | Suspension Insulator | - | Checked and found: GCB#31 T/R, Counter : 44 - 45, Relay Flag : 87 Patrolled the line found : Suspention Insulator pecah 92% di layer 1 Phase : 1 Pole : BTG-89 Date Patrol : 02-OCT-2019 Operated Device : OCB#33 T/R Counter : 649 - 650 Relay Flag : NONE Finding Patrol : Jumper dari line ke LA putus Phase : 1 Pole : BTG-16 Cause : Suspension Insulator |  | 1 | 16:08 | Afternoon | Saturday | 2019 | 9
11984 | 2019-09-28 16:16 | 2019-09-28 16:16 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 35 | Sintong OCB feeder #1 T/R 1x. Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 16:16 | Afternoon | Saturday | 2019 | 9
11985 | 2019-09-28 16:16 | 2019-02-10 09:31 | 13.8KV SINTONG FEEDER #1 | Rain and Lightning | Lightning | 35 | Checked and found: STGSB-13.8OCB1 T/R, Counter : 408 - 409, Relay Flag : 51N. Patrolled the line found : Dead end flash over Operated Device : STGSB-13.8OCB1 T/R Counter : 408 - 409 Relay Flag : 51N Finding Patrol : Pin Broken 50% Phase : 3 Pole : 24 AI 6 Date Patrol : 01-OCT-2019 Operated Device : STGSB-13.8OCB1 T/R Counter : 408 - 409 Relay Flag : 51N Finding Patrol : Dead end flash over 10% Phase : 3 Pole : 25 AF 08 Cause : Lightning |  | 1 | 16:16 | Afternoon | Saturday | 2019 | 9
11986 | 2019-09-28 16:16 | 2019-09-28 16:16 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Unidentified | 0 | Sintong feeder #2 load dropped 143A (199-56A). Not checked yet. |  | 1 | 16:16 | Afternoon | Saturday | 2019 | 9
11987 | 2019-09-28 16:16 | 2019-02-10 09:36 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found: NONE, Counter : - , Relay Flag : NONE Patrolled the line found : NONE Cause : Unidentified |  | 1 | 16:16 | Afternoon | Saturday | 2019 | 9
11988 | 2019-09-28 16:48 | 2019-09-28 16:48 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Unidentified | 0 | So.Balam feeder #1 Load dropped 121A (146-25A). So.Balam feeder #2 Load dropped 24A (130-106A) EOR PUMP. So.Balam feeder #3 Load dropped 70A (70-0A) EOR PUMP. So.Balam feeder #4 Load dropped 72A (190-118A). SO.Balam GFPC T/R 1x Fault alarm on So Balam feeder#1 & feeder#2. Weather : Rain & lightning. |  | 1 | 16:48 | Afternoon | Saturday | 2019 | 9
11989 | 2019-09-28 16:48 | 2019-02-10 09:34 | 13.8KV S. BALAM FEEDER #1 | Rain and Lightning | Unidentified | 0 | Checked and found: NONE, Counter : None, Relay Flag : NONE Patrolled the line found : NONE Cause : Unidentified |  | 1 | 16:48 | Afternoon | Saturday | 2019 | 9
11990 | 2019-09-29 15:11 | 2019-09-29 15:11 | 13.8KV NELLA FEEDER #2 | Cloudy | Unidentified | 29 | Nella VCB feeder #2 T/R 1x. Nella GFPC T/O. After discussed with operation TDO Bangko. at 16:14 Closed GFPC from DSC --> OK Not checked yet. |  | 1 | 15:11 | Afternoon | Sunday | 2019 | 9
11991 | 2019-09-29 15:11 | 2019-02-10 09:48 | 13.8KV NELLA FEEDER #2 | Cloudy | Unidentified | 29 | Checked and found: NLASB-13.8VCB2 T/R, Counter : 344 - 345, Relay Flag : 51N Patrolled the line found : NONE Cause : Unidentified |  | 1 | 15:11 | Afternoon | Sunday | 2019 | 9
11992 | 2019-09-29 15:13 | 2019-09-29 15:13 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 16 | Ketigul VCB feeder #1 T/R 1x. Ketigul feeder #2 load dropped 24A (75-51A). Ketigul feeder #3 load dropped 15A (47-32A). Not checked yet. |  | 1 | 15:13 | Afternoon | Sunday | 2019 | 9
11993 | 2019-09-29 15:13 | 2019-03-10 10:12 | 13.8KV KETIGUL FEEDER#1 | Cloudy | Unidentified | 16 | Checked and found: PKTGL-13.8VCB1 T/R, Counter : 219 - 220, Relay Flag : 51 Patrolled the line found : Not Found Cause : Unidentified |  | 1 | 15:13 | Afternoon | Sunday | 2019 | 9
11994 | 2019-09-29 15:30 | 2019-09-29 15:30 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Pin Insulator | 11 | Pungut OCB feeder #2 T/R 1x. Pungut feeder #1 load dropped 24A (73-49A). Not checked yet. |  | 1 | 15:30 | Afternoon | Sunday | 2019 | 9
11995 | 2019-09-29 15:30 | 2019-03-10 11:23 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Pin Insulator | 11 | Checked and found: PNTSB-13.8OCB2 T/R, Counter : 424 - 426, Relay Flag : 51N Patrolled the line found : Pin Insulator pecah 42% Phase : 1 Pole : 49-BT-16 Date Patrol : 02-OCT-2019 Operated Device : PNTSB-13.8OCB2 T/R Counter : 424 - 426 Relay Flag : 51N Finding Patrol : Pin Insulator pecah 78% Phase : 3 Pole : 49-BT-17 Cause : Pin Insulator |  | 1 | 15:30 | Afternoon | Sunday | 2019 | 9
11996 | 2019-09-29 16:18 | 2019-09-29 16:18 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | - | 8C VCB feeder #4 T/R 1x. Not checked yet. |  | 1 | 16:18 | Afternoon | Sunday | 2019 | 9
11997 | 2019-09-29 16:18 | 2019-06-10 09:02 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Lightning | - | Checked and found: 8CSB-13.8VCB4 T/R, Counter : 624 - 626, Relay Flag : 51 Patrolled the line found : NOT FUOND Cause : Lightning |  | 1 | 16:18 | Afternoon | Sunday | 2019 | 9
11998 | 2019-09-29 16:22 | 2019-09-29 16:22 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Unidentified | 460 | 16:22 PTN feeder #1 dropped 54 A (246 - 192 A) 16:51 PTN feeder #1 dropped again 28 A (192 - 184 A) Cause: Not Checked Yet |  | 1 | 16:22 | Afternoon | Sunday | 2019 | 9
11999 | 2019-09-29 16:22 | 2019-09-30 20:53 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Unidentified | 460 | 20:53 Checked and found RCL 33-AY-47 T/LO, ctr: 200-207 Patrolled the line but found nothing 21:38 Blocked and close RCL 33-AY-47, OK then release the block. Cause: Unidentified. |  | 1 | 16:22 | Afternoon | Sunday | 2019 | 9
12000 | 2019-09-29 16:23 | 2019-09-29 16:23 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 38 | 8C VCB feeder #6 T/R 1x. Not checked yet. |  | 1 | 16:23 | Afternoon | Sunday | 2019 | 9
12001 | 2019-09-29 16:23 | 2019-04-10 14:11 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 38 | Checked and found: 8CSB-13.8VCB6 T/R, Counter : 624 - 625, Relay Flag : 50N Patrolled the line found : nothing found Cause : Lightning |  | 1 | 16:23 | Afternoon | Sunday | 2019 | 9
12002 | 2019-09-29 16:43 | 2019-09-29 16:43 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Recloser | 61 | Pematang feeder #2 load dropped 43A (107-64A) Not checked yet. |  | 1 | 16:43 | Afternoon | Sunday | 2019 | 9
12003 | 2019-09-29 16:43 | 2019-04-10 14:29 | 13.8KV PEMATANG FEEDER #2 | Rain and Lightning | Recloser | 61 | Checked and found: PMTSB-13.8OCB2 T/LO, Counter : 538 - 542, Relay Flag : 51 Patrolled the line found: Recloser broken Cause : Recloser |  | 1 | 16:43 | Afternoon | Sunday | 2019 | 9
12004 | 2019-09-29 16:53 | 2019-09-29 16:53 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 13 | 4B VCB feeder #1 T/R 1x. 4B feeder #2 load dropped 15A (32-17A). 4B feeder #3 load dropped 63A (65-2A) --> WIP. Not checked yet. |  | 1 | 16:53 | Afternoon | Sunday | 2019 | 9
12005 | 2019-09-29 16:53 | 2019-04-10 15:06 | 13.8KV 4B FEEDER #1 | Rain and Lightning | Lightning | 13 | Checked and found: 4BSB-13.8OCB1 T/R, Counter : 382 - 383, Relay Flag : 51 Patrolled the line found : Nothing found Cause : Lightning |  | 1 | 16:53 | Afternoon | Sunday | 2019 | 9
12006 | 2019-09-29 21:07 | 2019-09-29 21:07 | 13.8KV PEMATANG FEEDER #2 | Drizzle | Recloser | 1082 | 21:07 Pematang OCB feeder #2 T/LO counter: 538-542, R/F: 51P @3 Patrolled the line but found nothing 23:43 Block and Close (after confirmed to TL OPS) OCB fdr #1 but Tripped again rechecked and found broken pin insulator o/p 34-BC-20 waiting MTCE team to repair the problem Cause: Pins Insulator |  | 1 | 21:07 | Night | Sunday | 2019 | 9
12007 | 2019-09-29 21:07 | 2019-09-30 01:11 | 13.8KV PEMATANG FEEDER #2 | Drizzle | Recloser | 1082 | 01:11 Open Isolation Switch PMT fdr #2 Replace broken pin on @3 o/p 34-BC-20 02:11 Blocked and Close OCB PMT fdr #2, tripped again 02:35 Open visual opening RCL 34-BC-08 to isolate the Recloser 02:36 Blocked and closed OCB PMT fdr #2, OK Will be continue tomorrow. 10:04 Manually opened Pematang OCB feeder #2. For replacing burnt out Recloser: 34-BC-08. 11:35 Manually blocked and closed Pematang OCB feeder #2. and then released the block. Cause: Equipment Failure (Recloser). |  | 1 | 21:07 | Night | Sunday | 2019 | 9
12008 | 2019-09-30 06:58 | 2019-09-30 06:58 | 13.8KV BEKASAP FEEDER #6 | Fair | Pin Insulator | 129 | 06:58 Bekasap feeder #6 load dropped 62A (83-21A). 17:28 It was reported no power at Aman field. (R/ Bek GS:Operator). 18:55 Checked and found Recloser 38-BE-10 T/O (on blocked). 19:12 Blocked and closed Recloser 38-BE-10,OK the released the block. Not Patrolled yet. |  | 1 | 6:58 | Morning | Monday | 2019 | 9
12009 | 2019-09-30 06:58 | 2019-03-10 10:05 | 13.8KV BEKASAP FEEDER #6 | Fair | Pin Insulator | 129 | Checked and found : 5440-R.38BE10 T/R, Counter : 608 - 609, Relay Flag : NONE Patrolled the line found : Pin Insulator pecah di bagian bawah di phase 3 BKS# 160 Phase : 3 Pole : 39 BE 17A Date Patrol : 01-OCT-2019 Operated Device : 5440-R.38BE10 T/R Counter : 608 - 609 Relay Flag : NONE Finding Patrol : LA Pecah di phase 3 Cebakan#01 Phase : 3 Pole : 39-BF-15 Cause : Pin Insulator |  | 1 | 6:58 | Morning | Monday | 2019 | 9
12010 | 2019-09-30 14:21 | 2019-09-30 14:21 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Powerline - Conductor | 231 | 14:21 Batang 13.8KV OCB fdr #2 T/LO. Batang 13.8KV GFPC T/LO. 16:15 Checked and found Batang 13.8KV OCB fdr #2 T/LO ctr:191-194 R/F: 51@1, @2. Patrolled the line and found broken conductor between poles :38-AI13 to 38-AI-15. 20:22 Isolated line to R. Bais by cutting jumper o/p:38-AH-09. (Power to R. Bais field will be still off). 20:28 Blocked and closed Batang GFPC, OK the released the block. 20:30 Blocked and closed Batang VCB fdr #2, OK the released the block. Cause: Conductor. (Will be continued tomorrow). |  | 1 | 14:21 | Afternoon | Monday | 2019 | 9
12011 | 2019-09-30 14:21 | 2019-01-10 12:14 | 13.8KV BATANG FEEDER #2 | Rain and Lightning | Powerline - Conductor | 231 | 12:14 Manually opened Batang OCB feeder #2. Due to squeeze jumpers on pole 38-AH-09. 13:21 Manually blocked and closed Batang OCB feeder #2. Cause: Conductor. |  | 1 | 14:21 | Afternoon | Monday | 2019 | 9
12012 | 2019-01-10 10:26 | 2019-01-10 10:26 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 93 | Pematang Main Substation 44 KV OCB #1 (To Petani) T/R 1x. No power at Petani Substation. - Petani OCB feeder #1 ( Production loss: 42 Bbls / 17 wells). - Petani OCB feeder #2 ( Production loss: 74 Bbls / 30 wells). Total Production loss: 116 Bbls / 47 wells. Not checked yet. |  | 1 | 10:26 | Morning | Thursday | 2019 | 1
12013 | 2019-01-10 10:26 | 2019-05-10 07:49 | 44KV PEMATANG MAIN - PETANI LINE | Fair | Unidentified | 93 | Checked and found: PMTMSB-44OCB1 T/R, Counter : 195 - 196, Relay Flag : 50N Patrolled the line found : No Findings Cause : Unidentified |  | 1 | 10:26 | Morning | Thursday | 2019 | 1
12014 | 2019-01-10 13:10 | 2019-01-10 13:10 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified | - | Darling VCB feeder #4 T/R 1x. Not checked yet. |  | 1 | 13:10 | Afternoon | Thursday | 2019 | 1
12015 | 2019-01-10 13:10 | 2019-01-10 15:27 | 13.8KV DARLING VCB FEEDER #4 | Fair | Unidentified | - | Checked and found: DRLG4-13.8VCB4 T/R, Counter : 148 - 149, Relay Flag : 51 Patrolled the line found : No Findings Cause : Unidentified |  | 1 | 13:10 | Afternoon | Thursday | 2019 | 1
12016 | 2019-01-10 14:22 | 2019-01-10 14:22 | 13.8KV 8C FEEDER #6 | Cloudy | Lightning | 27 | 8C VCB feeder #6 T/R 1x. 8C feeder #4 load dropped 67A (250-183A). Not checked yet. |  | 1 | 14:22 | Afternoon | Thursday | 2019 | 1
12017 | 2019-01-10 14:22 | 2019-04-10 14:49 | 13.8KV 8C FEEDER #6 | Cloudy | Lightning | 27 | Checked and found: 8CSB-13.8VCB6 T/R, Counter : 625 - 627, Relay Flag : 51 Patrolled the line found : Nothing Found Cause : Lightning |  | 1 | 14:22 | Afternoon | Thursday | 2019 | 1
12018 | 2019-01-10 16:19 | 2019-01-10 16:19 | 13.8KV CENTRAL DURI FEEDER #15 | Cloudy | Powerline - Conductor | 118 | 16:19 C Duri ACB #18 (feeder #15) T/LO. Counter: 390-394 R/F: 51@1,@2 and 50@2. 17:18 Patrolled the line found burnt out Recloser: 06-RI-02. 17:26 Patrolled the line found @1,@2 broken conductor on poles 06-Q3-03. Isolated Recloser: 06-R1-02 by open jumpers. Cut jumpers on pole 06-Q3-01. 18:09 Manually Open LBS: 06-Q3-21. 19:18 Blocked and closed C. Duri fdr #15, OK then released the block. 19:43 Blocked and closed C. Duri fdr #14, OK then released the block. (C. Duri fdr #14 and CD fdr #15 back to normal except under LBS: 06-Q3-21 cue to broken Conductor). Cause: Broken Conductor and Jumper. (Will be continued tomorrow). |  | 1 | 16:19 | Afternoon | Thursday | 2019 | 1
12019 | 2019-01-10 16:19 | 2019-02-10 16:55 | 13.8KV CENTRAL DURI FEEDER #15 | Cloudy | Powerline - Conductor | 118 | 16:55 Manually Opened C.Duri ACB fdr#15. Repaired & Re-connected Broken Conductor o/p 06-Q3-02. 17:30 Blocked & closed C.Duri ACB fdr#15, then release the block. 17:32 Blocked & closed Recl. 06-Q3-02, then release the block. Cause: Conductor. Production loss FOD#3: 199 Bbls / 184 wells. (Oct 01 at 16:19 up to 19:43) Production loss FOD#2: 424 Bbls / 32 wells. Production loss FOD#3: 9 Bbls / 55 wells. (Oct 02 at 16:55 up to 17:30) Production loss FOD#2: 14 Bbls / 34 wells. --------------------------------------------------- + Grand total : 646 Bbls / 405 wells. |  | 1 | 16:19 | Afternoon | Thursday | 2019 | 1
12020 | 2019-01-10 17:57 | 2019-01-10 17:57 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 14 | Ketigul 13.8KV VCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 17:57 | Afternoon | Thursday | 2019 | 1
12021 | 2019-01-10 17:57 | 2019-05-10 11:17 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Dead End Insulator | 14 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 352 - 354, Relay Flag : 51 Patrolled the line found : Dead End Flash Over Phase : 1 Pole : 29-AM-30 Date Patrol : 04-OCT-2019 Operated Device : PKTGL-13.8VCB2 T/R Counter : 352 - 354 Relay Flag : 51 Finding Patrol : Pin Insulator Sompel / Pecah sedikit Phase : 1 Pole : 29-AM-4 Cause : Dead End Insulator |  | 1 | 17:57 | Afternoon | Thursday | 2019 | 1
12022 | 2019-01-10 20:57 | 2019-01-10 20:57 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning Arrester | 31 | 8D fdr #10 T/R 1x 8D fdr #11 load dropped 8 A (134 - 126 A) Cause: Not Checked Yet |  | 1 | 20:57 | Night | Thursday | 2019 | 1
12023 | 2019-01-10 20:57 | 2019-04-10 14:06 | 13.8KV 8D FEEDER #10 | Rain and Lightning | Lightning Arrester | 31 | Checked and found: 8DSB-13.8OCB10 T/R, Counter : 270 - 271, Relay Flag : 50 Patrolled the line found : nothing found Cause : Lightning Arrester |  | 1 | 20:57 | Night | Thursday | 2019 | 1
12024 | 2019-01-10 21:00 | 2019-01-10 21:00 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Pin Insulator | 12 | 8C fdr #4 T/R 1x Cause: Not Checked Yet |  | 1 | 21:00 | Night | Thursday | 2019 | 1
12025 | 2019-01-10 21:00 | 2019-04-10 14:16 | 13.8KV 8C FEEDER #4 | Rain and Lightning | Pin Insulator | 12 | Checked and found: 8CSB-13.8VCB4 T/R, Counter : 624 - 626, Relay Flag : 51. Patrolled the line found : Broken pin and deadend Cause : Pin Insulator |  | 1 | 21:00 | Night | Thursday | 2019 | 1
12026 | 2019-02-10 06:58 | 2019-02-10 06:58 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | C.Duri ACB fdr#1 Load dropped 30A (170-140A). Not checked yet. |  | 1 | 6:58 | Morning | Sunday | 2019 | 2
12027 | 2019-02-10 06:58 | 2019-05-10 11:32 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Pin Insulator | 0 | Checked and found: 5441-R.39AV36 T/R, Counter : 283 - 284, Relay Flag : NONE Patrolled the line found : Pin Insulator Pecah Sedikit Phase : 3 Pole : 38-AS-14 Date Patrol : 04-OCT-2019 Operated Device : 5441-R.39AV36 T/R Counter : 283 - 284 Relay Flag : NONE Finding Patrol : Jumper LA putus Phase : 2 Pole : 38-AS-23 Cause : Pin Insulator |  | 1 | 6:58 | Morning | Sunday | 2019 | 2
12028 | 2019-02-10 09:25 | 2019-02-10 09:25 | MINAS POWER PLANT |  |  | - | 09:25 S/U MGT#5, and then Online the unit at 10:38. (For Running test). |  | 1 | 9:25 | Morning | Sunday | 2019 | 2
12029 | 2019-02-10 10:31 | 2019-02-10 10:31 | 13.8KV 8D FEEDER #11 | Fair | Planned Maintenance | 105 | 10:31 Manually Opened 8D fdr#11. Repaired Bypass switch Recl. 9E-02. 11:54 Blocked & closed 8D fdr#11, then release the block. Cause: Plan Maintenance. |  | 1 | 10:31 | Morning | Sunday | 2019 | 2
12030 | 2019-03-10 10:35 | 2019-03-10 10:35 | 13.8KV 5B FEEDER #7 | Fair | Planned Maintenance | 0 | 10:35 Manually open LBS 4C-138 D/S 5B fdr#7. Replaced pin insulation 17 Pcs. 16:04 Manually closed LBS 4C-138 D/S 5B fdr#7. Cause : Plain Maintenance. |  | 1 | 10:35 | Morning | Sunday | 2019 | 3
12031 | 2019-03-10 14:36 | 2019-03-10 14:36 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning Arrester | 0 | C.Duri feeder#1 load dropped 76A (145-69A). Not checked yet. |  | 1 | 14:36 | Afternoon | Sunday | 2019 | 3
12032 | 2019-03-10 14:36 | 2019-05-10 11:35 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning Arrester | 0 | Checked and found : 5441-R.39AV36 T/R, Counter : 283 - 284, Relay Flag : NONE Patrolled the line found : Jumper LA putus Phase : 2 Pole : 38-AS-23 Date Patrol : 04-OCT-2019 Operated Device : 5441-R.39AV36 T/R Counter : 283 - 284 Relay Flag : NONE Finding Patrol : Pin Insulator Pecah Sedikit Phase : 3 Pole : 38-AS-14 Cause : Lightning Arrester |  | 1 | 14:36 | Afternoon | Sunday | 2019 | 3
12033 | 2019-03-10 14:51 | 2019-03-10 14:51 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Dead End Insulator | 18 | Ketigul VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 14:51 | Afternoon | Sunday | 2019 | 3
12034 | 2019-03-10 14:51 | 2019-05-10 11:20 | 13.8KV KETIGUL FEEDER#2 | Rain and Lightning | Dead End Insulator | 18 | Checked and found: PKTGL-13.8VCB2 T/R, Counter : 352 - 354, Relay Flag : 51 Patrolled the line found : Dead End Flash Over Operated Device : PKTGL-13.8VCB2 T/R Counter : 352 - 354 Relay Flag : 51 Finding Patrol : Pin Insulator Sompel / Pecah Sedikit Phase : 1 Pole : 29-AM-4 Cause : Dead End Insulator |  | 1 | 14:51 | Afternoon | Sunday | 2019 | 3
12035 | 2019-04-10 10:10 | 2019-04-10 10:10 | 13.8KV DURI FIELD FEEDER #4 | Fair | Animal | 0 | 10:10 It was reported no power o/p 07-T3-19 D/S (Duri field fdr#4 ). 10:48 Checked & found recloser 07-T3-02 T/O Ctr:558-559 ( in Block). Patrolled the line found dead monkey o/p 07-T3-03. Blocked & closed the recloser, then reset the block. Cause: Animal (monkey). |  | 1 | 10:10 | Morning | Wednesday | 2019 | 4
12036 | 2019-04-10 19:56 | 2019-04-10 19:56 | CENTRAL DURI POWER PLANT |  |  | - | 19:56 Offline CDGT #3 and then S/D the unit ( Not standby ). |  | 1 | 19:56 | Night | Wednesday | 2019 | 4
12037 | 2019-04-10 20:20 | 2019-04-10 20:20 | MINAS POWER PLANT |  |  | - | 20:20 Offline MGT #3 and then S/D the unit for standby. |  | 1 | 20:20 | Night | Wednesday | 2019 | 4
12038 | 2019-05-10 06:23 | 2019-05-10 06:23 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 22 | Libo OCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 6:23 | Morning | Friday | 2019 | 5
12039 | 2019-05-10 06:23 | 2019-07-10 16:23 | 13.8KV LIBO FEEDER #1 | Fair | Unidentified | 22 | Checked & found Libo VCB fdr#1 T/R 1x Ctr:592- 593 R/F:51N. Patrolled the line but found nothing. Cause : Others. |  | 1 | 6:23 | Morning | Friday | 2019 | 5
12040 | 2019-05-10 11:42 | 2019-05-10 11:42 | 13.8KV 6D FEEDER #5 | Fair | Emergency | - | 11:42 Manually open 6D fdr#5. Main ten level tank. 17:05 Blocked & closed 6D fdr#5, then release the block. Cause: Emergency. |  | 1 | 11:42 | Morning | Friday | 2019 | 5
12041 | 2019-07-10 07:43 | 2019-07-10 07:43 | 13.8KV BEKASAP FEEDER #2 | Fair | Emergency | 0 | 07:43 Manually Opened MSU VCB fdr#2 (Supply Bekasap feeder #2) Requested GS for Maintain tank level. 09:95 Blocked & closed Bekasap MSU VCB fdr#2 and then release the block. 19:48 Manually Opened MSU VCB fdr#2 (Supply Bekasap feeder #2). due to BMW EOR failure. Request : Bekasap GS. Cause: Emergency. |  | 1 | 7:43 | Morning | Wednesday | 2019 | 7
12042 | 2019-07-10 08:50 | 2019-07-10 08:50 | 13.8KV KETIGUL FEEDER#2 | Fair | Emergency | 0 | October 07,2019. 08:50 Manually opened Ketigul VCB feeder #2. Requested GS for Tie In Production Line. October 08,2019. 21:17 Manually blocked and closed Ketigul VCB feeder #2. After the tie in job is complete. Cause: Emergency (Tie in and crossing pipe). |  | 1 | 8:50 | Morning | Wednesday | 2019 | 7
12043 | 2019-07-10 09:48 | 2019-07-10 09:48 | 13.8KV BEKASAP FEEDER #6 | Fair | Emergency | 0 | 09:48 Manually Opened Bekasap VCB fdr#6. Requested GS for Maintain tank level. 09:95 Blocked & closed Bekasap VCB fdr#6, Then release the block. Cause: Emergency. |  | 1 | 9:48 | Morning | Wednesday | 2019 | 7
12044 | 2019-07-10 10:25 | 2019-07-10 10:25 | 13.8KV BEKASAP FEEDER #2 | Fair | Dead End Insulator | 66 | 10:25 It was reported no power at well BKS#17, #45, #54, #87. 12:10 Checked & found Recl. 37-BD-12 T/O Counter: 1027-1028. Blocked & closed Recl. 37-BD-12, and then release the block. Not patrolled yet. |  | 1 | 10:25 | Morning | Wednesday | 2019 | 7
12045 | 2019-07-10 10:25 | 2019-09-10 10:41 | 13.8KV BEKASAP FEEDER #2 | Fair | Dead End Insulator | 66 | Checked and found: 5440-R.37BD12 T/O, Counter : 1027 - 1028, Relay Flag : NONE Patrolled the line found : Dead end flash over Cause : Dead End Insulator |  | 1 | 10:25 | Morning | Wednesday | 2019 | 7
12046 | 2019-07-10 15:05 | 2019-07-10 15:05 | 13.8KV KETIGUL FEEDER#1 | Fair | Lightning Arrester | 20 | Ketigul VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 15:05 | Afternoon | Wednesday | 2019 | 7
12047 | 2019-07-10 15:05 | 2019-10-10 09:23 | 13.8KV KETIGUL FEEDER#1 | Fair | Lightning Arrester | 20 | Checked and found: T/R PKTGL-13.8VCB1, Counter : 220 - 221, Relay Flag : 51N Patrolled the line found : LA Putus Cause : Lightning Arrester |  | 1 | 15:05 | Afternoon | Wednesday | 2019 | 7
12048 | 2019-07-10 17:35 | 2019-07-10 17:35 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Others | 0 | Dumai 4160V VCB Fdr#1 T/R 1x Checked & found Counter : 302-303, R/F: 51N @1 2 3 Not patrolled yet. |  | 1 | 17:35 | Afternoon | Wednesday | 2019 | 7
12049 | 2019-07-10 17:35 | 2019-08-10 11:51 | 4.16KV DUMAI (WHARF FEEDER) FEEDER #1 | Fair | Others | 0 | Checked and found: DMISB-4.16ACB12 T/R, Counter : 302 - 303, Relay Flag : 50 Patrolled the line found : Breaker FM rusak 3 pcs Cause : Others |  | 1 | 17:35 | Afternoon | Wednesday | 2019 | 7
12050 | 2019-08-10 16:38 | 2019-08-10 16:38 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 2 | 16:38 Duri Field VCB fdr#4 T/R 1x (In Block Status PT WKS) 17:20 Patrolled the Line, but found nothing, and Confirm to Pt WKS it was Clear Block & Closed the Breaker, the released the Block Cause: Not patrolled yet. |  | 1 | 16:38 | Afternoon | Saturday | 2019 | 8
12051 | 2019-08-10 16:38 | 2019-10-10 16:51 | 13.8KV DURI FIELD FEEDER #4 | Fair | Unidentified | 2 | Checked and found: DFSG-13.8ACB51 T/R, Counter : 559 - 560, Relay Flag : 51N Patrolled the line found : none Cause : Unidentified |  | 1 | 16:38 | Afternoon | Saturday | 2019 | 8
12052 | 2019-09-10 02:15 | 2019-09-10 02:15 | 13.8KV PUNGUT FEEDER #2 | Fair | Tree | 1 | Pungut OCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 2:15 | Night | Tuesday | 2019 | 9
12053 | 2019-09-10 02:15 | 2019-11-10 13:39 | 13.8KV PUNGUT FEEDER #2 | Fair | Tree | 1 | Checked and found: PNTSB-13.8OCB2 T/R, Counter : 426 - 427, Relay Flag : 51N. Patrolled the line found : Dahan pohon sawit menyentuh line Cause : Tree |  | 1 | 2:15 | Night | Tuesday | 2019 | 9
12054 | 2019-09-10 02:20 | 2019-09-10 02:20 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 0 | CKBS feeder #5 load dropped 164A (207-43A). Not checked yet. |  | 1 | 2:20 | Night | Tuesday | 2019 | 9
12055 | 2019-09-10 02:20 | 2019-10-10 07:03 | 13.8KV CENTRAL KOTABATAK FEEDER #5 | Rain and Lightning | Lightning | 0 | Checked and found: Device : 5443-RCL T/R, Counter : 326 - 327, Relay Flag : NONE Patrolled the line found : LA Broken Cause : Lightning |  | 1 | 2:20 | Night | Tuesday | 2019 | 9
12056 | 2019-09-10 02:28 | 2019-09-10 02:28 | 13.8KV BEKASAP FEEDER #3 | Fair | Pin Insulator | 184 | 02:28 Bekasap Main feeder #3 load dropped 19A (267-248A). 03:54 Bekasap Main feeder #3 load dropped 60A (267-207A). Not checked yet. |  | 1 | 2:28 | Night | Tuesday | 2019 | 9
12057 | 2019-09-10 02:28 | 2019-09-10 02:43 | 13.8KV BEKASAP FEEDER #3 | Fair | Pin Insulator | 184 | Checked and found RCL 37-BI-01, ctr: 1318-1319, R/F: None Patrolled the line and found: - flash over dead end @3 o/p 37-BI-03 - broken LA @2 on Terminal pole PMT BOW #14 Cause : Lightning Arrester |  | 1 | 2:28 | Night | Tuesday | 2019 | 9
12058 | 2019-09-10 04:51 | 2019-09-10 04:51 | 13.8KV DURI FIELD FEEDER #4 | Fair | Pin Insulator | 0 | Duri Field ACB #51 (feeder #4) T/R 1x. Not checked yet. |  | 1 | 4:51 | Morning | Tuesday | 2019 | 9
12059 | 2019-09-10 04:51 | 2019-11-10 04:51 | 13.8KV DURI FIELD FEEDER #4 | Fair | Pin Insulator | 0 | Checked and found DF fdr #4 T/R 1x, ctr: 560-561, R/F: 51N, 51P @1 Patrolled the line and found broken pin insulator @1 o/p 07-V1-09 Cause : Pin Insulator |  | 1 | 4:51 | Morning | Tuesday | 2019 | 9
12060 | 2019-09-10 05:15 | 2019-09-10 05:15 | 13.8KV DURI FIELD FEEDER #4 | Rain | Pin Insulator | 336 | 05:15 Duri Field ACB #51 (feeder #4) T/O. 06:12 Checked and found Duri Field ACB #51 (feeder #4) T/LO. Counter: 561-565 R/F : 51P @1 and 51N Patrolled the line 08:30 Reported patrol finding, broken pin insulator @1 o/p 07-V1-09 Planned to c/o by maintenance team 09:40 Rack out VCB DF fdr #4 for mtce team replace the broken insulator 10:31 Rack-In the VCB DF fdr #4 Block and close VCB fdr #4 DFSG, but failed (tripped again) R/F: 51N and 51P @1, counter: 565-566 Re-patrolled the power line and found broken pin insulator @1 on terminal pole of TX for Kayangan Office. 11:12 Rack-Out again VCB fdr #4 DFSG to c/o the broken pin insulators 12:11 Change out the broken pin insulators has completed 12:13 Rack-In the VCB fdr #4 DFSG 12:15 Block and Close VCB fdr #4 (locally due to RTU failed), success and then release the block. Last Counter : 567 Cause: Broken Pin Insulator |  | 1 | 5:15 | Morning | Tuesday | 2019 | 9
12061 | 2019-09-10 06:42 | 2019-09-10 06:42 | 13.8KV MENGGALA FEEDER #1 | Rain and Lightning | Lightning | 221 | Menggala feeder #1 Load dropped 95A (143-48A). Not checked yet. |  | 1 | 6:42 | Morning | Tuesday | 2019 | 9
12062 | 2019-09-10 10:15 | 2019-09-10 10:15 | 13.8KV NELLA FEEDER #1 | Heavy Rain | Lightning | 103 | Nella feeder #1 T/R 1x Nella GFPC T/R 1x Not Checked Yet |  | 1 | 10:15 | Morning | Tuesday | 2019 | 9
12063 | 2019-09-10 16:08 | 2019-09-10 16:08 | MINAS POWER PLANT |  |  | - | MGT #10 S/U and then Online at 16:26 Prepare to S/D MGT #11 for troubleshoot computer problem. |  | 1 | 16:08 | Afternoon | Tuesday | 2019 | 9
12064 | 2019-09-10 16:37 | 2019-09-10 16:37 | MINAS POWER PLANT |  |  | - | 16:37 MGT #11 Offline and then S/D for troubleshoot computer analysis problem. |  | 1 | 16:37 | Afternoon | Tuesday | 2019 | 9
12065 | 2019-09-10 19:16 | 2019-09-10 19:16 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | N.Duri VCB fdr#1 T/R 1x. Not checked yet. |  | 1 | 19:16 | Night | Tuesday | 2019 | 9
12066 | 2019-09-10 19:16 | 2019-09-10 19:16 | 13.8KV NORTH DURI FEEDER #1 | Fair | Unidentified | 0 | Checked and found ND fdr #1 T/R 1x, ctr: 314-315, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 19:16 | Night | Tuesday | 2019 | 9
12067 | 2019-09-10 19:16 | 2019-09-10 19:16 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | N.Duri VCB fdr#5 T/R 1x. Not checked yet. |  | 1 | 19:16 | Night | Tuesday | 2019 | 9
12068 | 2019-09-10 19:16 | 2019-11-10 16:44 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | Checked and found ND fdr #5 T/R 1x, ctr: 133-134, R/F: 51N Patrolled the line but found nothing Cause : Unidentified |  | 1 | 19:16 | Night | Tuesday | 2019 | 9
12069 | 2019-09-10 23:24 | 2019-09-10 23:24 | CENTRAL DURI SWITCH YARD | Fair | Under investigation | 0 | 23:24 115KV C.Duri OCB#33 T/O. 115Kv C.Duri GCB#35 T/O. 00:46 Checked & found 115KV C.Duri OCB#33 T/O Ctr:650-651 R/F: Buchh M.Tank Operated. 115Kv C.Duri GCB#35 T/O Ctr:115-116. C.Duri Tx-5 normal operation. 03:15 Closed 115KV C.Duri OCB#33. Closed 115KV C.Duri OCB#35. Cause: Under investigation. |  | 1 | 23:24 | Night | Tuesday | 2019 | 9
12070 | 2019-10-10 16:32 | 2019-10-10 16:32 | 13.8KV 6DN FEEDER #4 | Fair | Main breaker | - | 16:32 6DN fdr #4 load dropped 158 A (158 - 0) 16:43 Reported no power at TX-2 at GS-3 16:44 Inform to TDO crew (Nasrul Akhyar) 18:00 Checked and found breaker (VCB) for TX-2 at GS-3 tripped suspect any problem at internal TX-2 waiting to checked by maintenance team Cause: Under Investigation |  | 1 | 16:32 | Afternoon | Thursday | 2019 | 10
12071 | 2019-10-10 16:32 | 13/10/2019 16:05 | 13.8KV 6DN FEEDER #4 | Fair | Main breaker | - | Patrolled and found Moin Breaker of TX-2 GS #3 T/SO, The breaker failed to reclose due to solenoid problem Cause : Main breaker |  | 1 | 16:32 | Afternoon | Thursday | 2019 | 10
12072 | 2019-10-10 18:15 | 2019-10-10 18:15 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Lightning | 0 | CD fdr #9 T/R 1x, counter: 399 - 400, R/F: 51N Cause: Not Patrolled Yet |  | 1 | 18:15 | Afternoon | Thursday | 2019 | 10
12073 | 2019-10-10 18:15 | 13/10/2019 08:05 | 13.8KV CENTRAL DURI FEEDER #9 | Fair | Lightning | 0 | Checked and found CD fdr #9 T/R 1x, ctr: 400-401, R/F: 51N Patrolled the line and found dead end insulator flash over @2 o/p 04-7-27 Cause : Lightning |  | 1 | 18:15 | Afternoon | Thursday | 2019 | 10
12074 | 2019-10-10 22:35 | 2019-10-10 22:35 | 13.8KV 6DN FEEDER #5 |  | Emergency | - | 22:35 Manual open 6DN fdr #5 (req by Andi Yoga), closed at 11:05 To maintain tank level due to TX-2 Breaker problem d/s 6DN fdr #4 (for WIP) Cause: Breaker Problem |  | 1 | 22:35 | Night | Thursday | 2019 | 10
12075 | 2019-10-10 23:58 | 2019-10-10 23:58 | 13.8KV 6DN FEEDER #4 |  | Emergency | - | 23:58 Manual open 6DN fdr #4 (req by Andi Yoga), closed at 09:35 To maintain tank level due to TX-2 Breaker problem d/s 6DN fdr #4 (for WIP) Cause: Breaker Problem |  | 1 | 23:58 | Night | Thursday | 2019 | 10
12076 | 2019-11-10 14:49 | 2019-11-10 14:49 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | - | Minas ACB-1 (Minas fdr #4) T/R 1x, ctr: 104-105, R/F: 51G Cause: Not Patrolled Yet |  | 1 | 14:49 | Afternoon | Sunday | 2019 | 11
12077 | 2019-11-10 14:49 | 15/10/2019 08:34 | 13.8KV MINAS FEEDER #4 | Fair | Unidentified | - | Checked and found: MNSSG-13.8ACB01 T/R, Counter : 104 - 105, Relay Flag : 51 Patrolled the line found : Not Found Cause : Unidentified |  | 1 | 14:49 | Afternoon | Sunday | 2019 | 11
12078 | 2019-11-10 15:40 | 2019-11-10 15:40 | CENTRAL DURI POWER PLANT |  |  | - | 15:40 CDGT-3 S/U and then online at 15:55 for Running test at 7MW |  | 1 | 15:40 | Afternoon | Sunday | 2019 | 11
12079 | 2019-11-10 19:58 | 2019-11-10 19:58 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 188 | 19:58 8C VCB fdr#6 T/R 1x. 8C fdr#4 Load dropped 200A (238-38A) (Pump Off). 8C fdr#5 Load dropped 25A (145-120A) (Pump Off). Not checked yet. 23:16 It was reported no power at well 8C-58N, 8C58N, 7D-9E, 8C-19N D/S 8C Fdr#6. 00:36 Checked & found Recl. 9D-94 T/O Ctr:65-66. 00:38 Blocked & closed Recl. 9D-94, then release the block. Not Patrolled yet. |  | 1 | 19:58 | Night | Sunday | 2019 | 11
12080 | 2019-11-10 19:58 | 15/10/2019 16:45 | 13.8KV 8C FEEDER #6 | Rain and Lightning | Lightning | 188 | Checked and found: 8C fdr #6 T/R 1x, ctr: 627-629, R/F: 51P @2 @3, 50N Patrolled the line but found nothing RCL 8C-94 T/SO, ctr: 65-66, R/F: None Patrolled the line and found Broken Pin Insulator @2 o/p 8C-06 and broken dead end @1 @2 o/p 8C-03 Cause : Lightning |  | 1 | 19:58 | Night | Sunday | 2019 | 11
12081 | 2019-11-10 20:39 | 2019-11-10 20:39 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 28 | 5B OCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 20:39 | Night | Sunday | 2019 | 11
12082 | 2019-11-10 20:39 | 15/10/2019 17:09 | 13.8KV 5B FEEDER #2 | Rain and Lightning | Lightning | 28 | Checked and found 5B fdr #2, Ctr: 425 - 426, R/F: 50P @3 Patrolled the line and found Broken Suspension Insulator @3 o/p 5C-06 Cause : Lightning |  | 1 | 20:39 | Night | Sunday | 2019 | 11
12083 | 2019-11-10 20:44 | 2019-11-10 20:44 | 115KV KOTABATAK JUNCTION - 5B LINE | Rain and Lightning | Lightning | 2 | 115Kv Line KBJ-5B GCB#21 T/O, then Closed at 21:21. 115Kv Line KBJ-5B GCB#23 T/O, then Closed at 21:22. 115Kv Line 5B-KBJ GCB#22 T/O, then Closed at 21:21. 4D fdr#4 T/O, then closed at 21:08. 4D fdr#5 T/O, then closed at 21:09. Not checked yet. |  | 1 | 20:44 | Night | Sunday | 2019 | 11
12084 | 2019-11-10 20:44 | 16/10/2019 13:42 | 115KV KOTABATAK JUNCTION - 5B LINE | Rain and Lightning | Lightning | 2 | Checked and found: - 115 KV line 5B-KBJ GCB #22 Counter : 663 (do not change) R/F: NONE - 115 KV line KBJ-5B GCB #21 T/R 1x Counter: 204-205 R/F: 50N. - 115 KV line KBJ-5B GCB #23 T/R 1x Counter: 220-221 R/F: 21BG. Patrolled the line found nothing. Cause: Suspect Lightning. 1. Checked and found 4D OCB feeder #4 T/R 1x. Counter: 299-300 R/F : 81. Not patrolled the line. 2. Checked and found 4D OCB feeder #5 T/R 1x. Counter: 275-276 R/F : 81. Not patrolled the line. |  | 1 | 20:44 | Night | Sunday | 2019 | 11
12085 | 2019-11-10 20:49 | 2019-11-10 20:49 | 115KV PUNGUT - KOTABATAK JUNCTION LINE | Rain and Lightning | Lightning | - | 115Kv Line Pungut-KBJ GCB#22 T/O, then closed at 21:05. 115Kv Line KBJ-Pungut GCB#51 T/R. 115Kv Line KBJ-Pungut GCB#53 T/R. Not checked yet. |  | 1 | 20:49 | Night | Sunday | 2019 | 11
12086 | 2019-11-10 20:49 | 16/10/2019 13:47 | 115KV PUNGUT - KOTABATAK JUNCTION LINE | Rain and Lightning | Lightning | - | Checked and found: - 115 KV line KBJ-Pungut GCB # 51 T/R 2x Counter: 253-255 R/F: none. - 115 KV line KBJ-Pungut GCB # 53 T/R 2x Counter: 246-248 R/F: 51@1. - 115 KV line Pungut-KBJ GCB # 22 T/0. and then closed at 21:05 (Oct 11,2019) Counter: 144-145 R/F: None. Patrolled the line found nothing. Cause: Suspect Lightning. |  | 1 | 20:49 | Night | Sunday | 2019 | 11
12087 | 2019-11-10 20:52 | 2019-11-10 20:52 | 115KV DURI - PUNGUT LINE | Rain and Lightning | Unidentified | 0 | 115Kv Line Duri-Pungut GCB#21 T/O, then closed at 21:11 115Kv Line Duri-Pungut GCB#29 T/O, then closed at 21:11 115Kv Line Pungut-Duri GCB#21 Not Operated. Not checked yet. |  | 1 | 20:52 | Night | Sunday | 2019 | 11
12088 | 2019-11-10 20:52 | 2019-12-10 15:04 | 115KV DURI - PUNGUT LINE | Rain and Lightning | Unidentified | 0 | Checked & found 115KV Line Duri-Pungut, Ctr: 145-146, R/F: 21 Patrolled the Lne, but found nothing Cause : Unidentified |  | 1 | 20:52 | Night | Sunday | 2019 | 11
12089 | 2019-11-10 20:53 | 2019-11-10 20:53 | 13.8KV MBL SUBSTATION 2 (NORTH) FEEDER #2 | Cloudy | Emergency | - | 20:53 Manually opened MSU#2 fdr#2 (BKS fdr#2). Maintain tank level by Pump Off. 22:17 Blocked & closed MSU#2 fdr#2 (BKS fdr#2), then release the block. Cause: Emergency. |  | 1 | 20:53 | Night | Sunday | 2019 | 11
12090 | 2019-11-10 21:01 | 2019-11-10 21:01 | 13.8KV PEMATANG FEEDER #2 | Cloudy | Emergency | - | 21:01 Manually Opened Pematang VCB fdr#2. Maintain tank level by pump off. 21:55 Blocked & closed Pematang fdr#2, then release the block. Cause: Emergency. |  | 1 | 21:01 | Night | Sunday | 2019 | 11
12091 | 2019-11-10 21:34 | 2019-11-10 21:34 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Unidentified | 11 | 21:34 Libo VCB fdr#1 T/R 1x. 21:54 Libo VCB fdr#1 T/R 1x again. Not checked yet. |  | 1 | 21:34 | Night | Sunday | 2019 | 11
12092 | 2019-11-10 21:34 | 13/10/2019 15:59 | 13.8KV LIBO FEEDER #1 | Rain and Lightning | Unidentified | 11 | Checked and found LBO fdr #1 T/R 2x, ctr: 593-595, R/F: 51N Patrolled the line and found nothing Cause : Unidentified |  | 1 | 21:34 | Night | Sunday | 2019 | 11
12093 | 2019-11-10 22:36 | 2019-11-10 22:36 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Pin Insulator | 41 | Libo VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 22:36 | Night | Sunday | 2019 | 11
12094 | 2019-11-10 22:36 | 13/10/2019 16:12 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Pin Insulator | 41 | Checked and found LBO VCB fdr #2 T/R 1x, ctr: 512 - 513, R/F: 51N Patrolled the line and found broken pin support @1 o/p KW-161 Cause : Pin Insulator |  | 1 | 22:36 | Night | Sunday | 2019 | 11
12095 | 2019-11-10 22:52 | 2019-11-10 22:52 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Dead End Insulator | - | 22:52 Pungut VCB fdr#2 T/R 1x. 22:55 Pungut VCB fdr#2 T/R 1x again. 23:39 Pungut VCB fdr#2 T/R 1x again. Not checked yet. |  | 1 | 22:52 | Night | Sunday | 2019 | 11
12096 | 2019-11-10 22:52 | 2019-12-10 20:52 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Dead End Insulator | - | Checked & found Pungut fdr#2 T/R 3x Ctr:427-430 R/F:51@1. Patrolled the line & found @1 Flashed over Dead End Insulator o/p 45BP07. Cause : Dead End Insulator |  | 1 | 22:52 | Night | Sunday | 2019 | 11
12097 | 2019-12-10 00:13 | 2019-12-10 00:13 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain and Lightning | Unidentified | 0 | 00:13 Duri Community fdr#2 T/R 1x. 20:00 Checked & found Duri Community fdr#2 T/R 1x Ctr:110-111 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 0:13 | Night | Tuesday | 2019 | 12
12098 | 2019-12-10 00:13 | 2019-12-10 13:21 | 13.8KV DURI COMMUNITY FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found: DCSG-13.8ACB30 T/R, Counter : 110 - 111, Relay Flag : 51 Patrolled the line found: Not Found Cause : Unidentified |  | 1 | 0:13 | Night | Tuesday | 2019 | 12
12099 | 2019-12-10 00:13 | 2019-12-10 00:13 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Dead End Insulator | 0 | 00:13 Duri Community fdr#3 T/R 1x. 00:25 Duri Community fdr#3 T/R 1x again 20:01 Checked & found Duri Community fdr#3 T/R 2x Ctr:96-98 R/F:51@1. Patrolled the line & found @1 Broken Dead End Insulator o/p 4DD56. Cause : Dead End Insulator. |  | 1 | 0:13 | Night | Tuesday | 2019 | 12
12100 | 2019-12-10 00:13 | 2019-12-10 13:29 | 13.8KV DURI COMMUNITY FEEDER #3 | Rain and Lightning | Dead End Insulator | 0 | Checked and found: DCSG-13.8ACB26 T/R, Counter : 96 - 98, Relay Flag : 51 Patrolled the line found: Broken Dead end Cause : Dead End Insulator |  | 1 | 0:13 | Night | Tuesday | 2019 | 12
12101 | 2019-12-10 00:27 | 2019-12-10 00:27 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Dead End Insulator | 0 | 00:37 C.Duri ACB fdr#5 T/R 1x Ctr:263-264 R/F:51@2. 20:02 Patrolled the line & found @1 Broken Dead End Insulator o/p TL-2. Cause : Dead End Insulator. |  | 1 | 0:27 | Night | Tuesday | 2019 | 12
12102 | 2019-12-10 00:27 | 2019-12-10 15:16 | 13.8KV CENTRAL DURI FEEDER #5 | Rain and Lightning | Dead End Insulator | 0 | Checked and found: CDRSG-13.8ACB22 T/R, Counter : 263 - 264, Relay Flag : 50 Patrolled the line found : Broken Dead End Cause : Dead End Insulator |  | 1 | 0:27 | Night | Tuesday | 2019 | 12
12103 | 2019-12-10 00:30 | 2019-12-10 00:30 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Pin Insulator | 0 | 00:30 C.Duri ACB fdr#9 T/R 1x Ctr:516 R/F:51N. 20:03 Patrolled the line & found @3 Broken Pin Insulator o/p 04-07-25. Cause : Pin Insulator. |  | 1 | 0:30 | Night | Tuesday | 2019 | 12
12104 | 2019-12-10 00:30 | 2019-12-10 15:12 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Pin Insulator | 0 | Checked and found: CDRSG-13.8ACB41 T/R, Counter : 400 - 401, Relay Flag : 51 Patrolled the line found : Pin Insulator Broken Cause : Pin Insulator |  | 1 | 0:30 | Night | Tuesday | 2019 | 12
12105 | 2019-12-10 02:27 | 2019-12-10 02:27 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Lightning | 190 | 02:27 Nella VCB fdr#2 T/SO . Nella GFPC T/R 4x. 04:20 Checked & found Nella VCB fdr#2 T/SO Ctr:245-247 R/F 51@1@3. Nella GFPC T/R 4x Ctr:990-994. 05:40 Patrolled the line but found nothing. Bloacked & closed Nella VCB fdr#2, then release the block. Cause: Unidentified fuse. |  | 1 | 2:27 | Night | Tuesday | 2019 | 12
12106 | 2019-12-10 03:15 | 2019-12-10 03:15 | 13.8KV S. BALAM FEEDER #4 | Rain and Lightning | Lightning | 111 | So.Balam VCB fdr#4 T/R 1x. So.Balam GFPC T/R 1x. So.Balam fdr#1 Load dropped 105A (150-45A). Not checked yet. |  | 1 | 3:15 | Night | Tuesday | 2019 | 12
12107 | 2019-12-10 09:51 | 2019-12-10 09:51 | MINAS POWER PLANT |  |  | - | 09:51 MGT#11 S/U and then online at 10:10. |  | 1 | 9:51 | Morning | Tuesday | 2019 | 12
12108 | 2019-12-10 10:20 | 2019-12-10 10:20 | MINAS POWER PLANT |  |  | - | 10:08 MGT#9 Offline and then S/D for MCU ( Computer checking ). |  | 1 | 10:20 | Morning | Tuesday | 2019 | 12
12109 | 2019-12-10 16:13 | 2019-12-10 16:13 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Emergency | - | 16:13 Manually open Petapahan fdr#6 . WIP pump-8 High vibration. 18:41 Blocked & closed Petapahan fdr#6, then release the block. Cause: Emergency. |  | 1 | 16:13 | Afternoon | Tuesday | 2019 | 12
12110 | 2019-10-13 11:59 | 2019-10-13 11:59 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Pin Insulator | 26 | Pungut feeder#2 T/R 1x. Not checked yet. |  | 1 | 11:59 | Morning | Sunday | 2019 | 10
12111 | 2019-10-13 11:59 | 2019-10-15 14:16 | 13.8KV PUNGUT FEEDER #2 | Rain and Lightning | Pin Insulator | 26 | Checked and found: PNTSB-13.8OCB2 T/R, Counter : 430 - 431, Relay Flag : 50 Patrolled the line found : Pin support pecah Cause : Pin Insulator |  | 1 | 11:59 | Morning | Sunday | 2019 | 10
12112 | 2019-10-13 13:15 | 2019-10-13 13:15 | 13.8KV DURI FIELD FEEDER #2 | Rain and Lightning | Recloser | 43 | 13:15 Duri field feeder#2 load dropped 81A (124-43A). Checked and found RCL 07-U3-21 T/SO Counter: 000 - 001, R/F: 51P @1, @2 15:30 Block and close RCL 07-U3-21, OK then release the block Cause: Not patrolled yet. |  | 1 | 13:15 | Afternoon | Sunday | 2019 | 10
12113 | 2019-10-13 13:15 | 2019-10-15 08:20 | 13.8KV DURI FIELD FEEDER #2 | Rain and Lightning | Recloser | 43 | Checked and found: RCL 07-U3-21 T/SO, Counter : 000 - 001, Relay Flag : NONE Patrolled the line found : Recloser 07-U3-21 malfunction Cause : Recloser |  | 1 | 13:15 | Afternoon | Sunday | 2019 | 10
12114 | 2019-10-13 13:41 | 2019-10-13 13:41 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 32 | 4DOCB feeder#4 T/R 1x. The feeder also handled 3D fdr #2 that transferred on sept 19th Not checked yet. |  | 1 | 13:41 | Afternoon | Sunday | 2019 | 10
12115 | 2019-10-13 13:41 | 2019-10-19 21:30 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Lightning | 32 | Checked and found 4D fdr #4 T/R 2x, ctr: 299 - 301, R/F: 50P Patrolled the line but found nothing Cause : Lightning |  | 1 | 13:41 | Afternoon | Sunday | 2019 | 10
12116 | 2019-10-13 14:47 | 2019-10-13 14:47 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Pin Insulator | 14 | Sintong feeder#2 load dropped 84A (196-112A). Sintong GFPC T/R 1x. Not checked yet. |  | 1 | 14:47 | Afternoon | Sunday | 2019 | 10
12117 | 2019-10-13 14:47 | 2019-10-18 09:44 | 13.8KV SINTONG FEEDER #2 | Rain and Lightning | Pin Insulator | 14 | Checked and found: 1. Recloser: 29-Y-16 T/R 1x Counter: 105-106. Patrolled the line nothing found. 2. Recloser:29-Z-13A T/R 1x Counter: 209-210. Patrolled the line found @3 broken pin insulator on pole 32-Z-13. Cause: Broken Pin Insulator. |  | 1 | 14:47 | Afternoon | Sunday | 2019 | 10
12118 | 2019-10-13 15:12 | 2019-10-13 15:12 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Pin Insulator | 12 | Bangko feeder#4 load dropped 78A (167-89A). Bangko GFPC T/R 1x. Not checked yet. |  | 1 | 15:12 | Afternoon | Sunday | 2019 | 10
12119 | 2019-10-13 15:12 | 2019-10-18 17:38 | 13.8KV BANGKO FEEDER #4 | Rain and Lightning | Pin Insulator | 12 | Checked and found : 1. Bangko GFPC T/R 1x Counter: 222-223 R/F: 51N. 2. Recloser: 25-Z-07 T/R 2x. Counter: 225-227 R/F: 51 on @A and @B. Patrolled the line found @1 broken Pin Insulator on pole 27-Z-05 and @2 broken Pin Insulator on pole 27-Z-02. Towards well Benar 19 and 40. Cause: Broken Pin Insulator. |  | 1 | 15:12 | Afternoon | Sunday | 2019 | 10
12120 | 2019-10-13 15:20 | 2019-10-13 15:20 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Pin Insulator | 25 | Nella VCB fdr#2 T/R 1x. Nella GFPC T/R 1x. Not checked yet. |  | 1 | 15:20 | Afternoon | Sunday | 2019 | 10
12121 | 2019-10-13 15:20 | 2019-10-18 17:50 | 13.8KV NELLA FEEDER #2 | Rain and Lightning | Pin Insulator | 25 | Checked and found: 1. Nella GFPC T/R 2x Counter: 994-996 R/F: 51N. 2. Nella VCB feeder #2 T/R 1x Counter: 347-348 R/F: 51N. Patrolled the line found @2 broken pin insulator on pole 20-V-55, towards well Bangko #244. Cause: Pin Insulator. |  | 1 | 15:20 | Afternoon | Sunday | 2019 | 10
12122 | 2019-10-13 16:06 | 2019-10-13 16:06 | 13.8KV MINAS FEEDER #1 | Heavy Rain | Unidentified | 28 | Minas (ACB #14) fdr #1 T/R 1x, ctr: 83-84, R/F: 51P @2 but load reading still zero in DSC & XHQ Checked and found Minas fdr #1 load analog reading 154 A and also RTU Normal. Not Patrolled Yet |  | 1 | 16:06 | Afternoon | Sunday | 2019 | 10
12123 | 2019-10-13 16:06 | 2019-10-15 17:35 | 13.8KV MINAS FEEDER #1 | Heavy Rain | Unidentified | 28 | Checked and found MNS feeder #1 T/R 1x. Counter: 83-84 R/F: 51N Patrolled the line but found nothing Cause : Unidentified. |  | 1 | 16:06 | Afternoon | Sunday | 2019 | 10
12124 | 2019-10-13 16:17 | 2019-10-13 16:17 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 8 | 4D fdr#3 T/R 1x. Not checked yet. |  | 1 | 16:17 | Afternoon | Sunday | 2019 | 10
12125 | 2019-10-13 16:17 | 2019-10-19 21:45 | 13.8KV 4D FEEDER #3 | Rain and Lightning | Lightning | 8 | checked and found 4D fdr #3 T/R 1x, ctr: 275 - 276, R/F: 51N Patrolled the line and found broken dead end @1 o/p 4D-230 Cause : Lightning |  | 1 | 16:17 | Afternoon | Sunday | 2019 | 10
12126 | 2019-10-13 17:39 | 2019-10-13 17:39 | 4.16KV NO RUMBAI FEEDER #2 | Rain and Lightning | Lightning | 0 | N.Rumbai fdr#2 T/R 1x. Not checked yet. |  | 1 | 17:39 | Afternoon | Sunday | 2019 | 10
12127 | 2019-10-13 17:39 | 2019-10-19 21:27 | 4.16KV NO RUMBAI FEEDER #2 | Rain and Lightning | Lightning | 0 | Checked and found North RBI VCB fdr #2 T/R 1x, ctr: 362-363, R/F: 51N Patrolled the line but found nothing Cause : Lightning |  | 1 | 17:39 | Afternoon | Sunday | 2019 | 10
12128 | 2019-10-14 07:10 | 2019-10-14 07:10 | 13.8KV MINAS FEEDER #6 | Fair | Unidentified | 34 | 07:10 Minas fdr #6 T/R 1x, ctr: 198-199, R/F: 51N Not Checked Yet |  | 1 | 7:10 | Morning | Monday | 2019 | 10
12129 | 2019-10-14 07:10 | 2019-10-15 08:41 | 13.8KV MINAS FEEDER #6 | Fair | Unidentified | 34 | Checked and found: MNSSG-13.8ACB18 T/R, Counter : 198 - 199, Relay Flag : 51N Patrolled the line found : Not Found Date Patrol : 14-OCT-2019 Operated Device : 5442-R.7E67A T/O Counter : 83 - 84 Relay Flag : NONE Finding Patrol : Not Found Phase : 0 Pole : 0 Cause : Unidentified |  | 1 | 7:10 | Morning | Monday | 2019 | 10
12130 | 2019-10-14 10:31 | 2019-10-14 10:31 | 13.8KV DARLING VCB FEEDER #4 | Fair | Planned Maintenance | 0 | 10:31 Manual Open LBS CD12-SA5 to S/D 1500 kVA TX-2 at CSS #6 for MTCE team repair leakage at TX-2 Cause: Planned Maitenance |  | 1 | 10:31 | Morning | Monday | 2019 | 10
12131 | 2019-10-14 10:49 | 2019-10-14 10:49 | 13.8KV 8D FEEDER #11 | Fair | Planned Maintenance | 31 | 10:49 Manual Open RCL 9E-02 (8D fdr #11), closed at 11:13 Purpose: mtce team c/o tx at 9E-31 (area 1/2) Last counter RCL: 147 - 148 Cause: Planned Maintenance |  | 1 | 10:49 | Morning | Monday | 2019 | 10
12132 | 2019-10-15 02:20 | 2019-10-15 02:20 | CENTRAL DURI POWER PLANT |  |  | - | 02:20 CGT#3 Trip by Alarm Lube Oil Pressure Low. 03:05 Closed Tie Breaker ACB#39. |  | 1 | 2:20 | Night | Tuesday | 2019 | 10
12133 | 2019-10-15 03:06 | 2019-10-15 03:06 | CENTRAL DURI POWER PLANT |  |  | - | 03:06 CGT#4 T/O Generator Breaker, then Closed at 03:13. |  | 1 | 3:06 | Night | Tuesday | 2019 | 10
12134 | 2019-10-15 10:47 | 2019-10-15 10:47 | 13.8KV NORTH DURI FEEDER #1 | Fair | Planned Maintenance | 77 | 10:47 Manual Open ND fdr #1, closed at 11:42 PGT Maintenance to repair broken cut out for visual opening switch of RCL 10-J4-26. Cause: Emergency | 0 | 1 | 10:47 | Morning | Tuesday | 2019 | 10
12135 | 2019-10-15 15:16 | 2019-10-15 15:16 | 13.8KV 8C FEEDER #1 | Fair | Planned Maintenance | 49 | 15:16 Manual Open VCB 8C fdr #1, closed at 15:42 PGT Maintenance to repair broken jumper o/p 9D-45 @1 Cause: Planned Maintenance |  | 1 | 15:16 | Afternoon | Tuesday | 2019 | 10
12136 | 2019-10-15 16:07 | 2019-10-15 16:07 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Lightning | 9 | Pinang fdr#1 T/R 1x. Not checked yet. |  | 1 | 16:07 | Afternoon | Tuesday | 2019 | 10
12137 | 2019-10-15 18:51 | 2019-10-15 18:51 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | - | C.Duri ACB fdr#1 Load dropped 50A (142-92A). Not checked yet. |  | 1 | 18:51 | Afternoon | Tuesday | 2019 | 10
12138 | 2019-10-15 18:51 | 2019-10-19 15:06 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Lightning | - | Checked and found RCL 39-AV-36 T/R 7x, ctr: 285-291, R/F: None Patrolled the line and found: - flash over pin insulator @3 on terminal pole KULIN #42 - flash over pin insulator @2 on pole 38-AS-28 Cause : Lightning |  | 1 | 18:51 | Afternoon | Tuesday | 2019 | 10
12139 | 2019-10-16 09:29 | 2019-10-16 09:29 | 13.8KV PEMATANG FEEDER #2 | Fair | Emergency | - | 09:29 Manually opened Pematang OCB fdr#2. Due to maintain the water level in the tank. 10:06 Manually blocked & closed Pematang OCB fdr#2 and then release the block. 10:28 Manually opened Pematang OCB fdr#2. Due to maintain the water level in the tank. 10:48 Manually blocked & closed Pematang OCB fdr#2 and then release the block. 13:58 Manually opened Pematang OCB fdr#2. Due to maintain the water level in the tank. 14:20 Manually blocked & closed Pematang OCB fdr#2 and then release the block. Cause: Emergency. |  | 1 | 9:29 | Morning | Wednesday | 2019 | 10
12140 | 2019-10-17 03:25 | 2019-10-17 03:25 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Pin Insulator | 1459 | 03:25 Nella fdr #1 T/SO 04:26 Checked and found - Nella VCB fdr #1 T/SO, ctr: 559 - 560, R/F: None - Nella Cap Bank RCL T/O - Nella GFPC T/O 05:00 Close GFPC RCL but failed (waiting MTCE team to bypass the GFPC). 06:00 Patrolled the line and found @1 broken pin insulator on pole 22-U-01. Replaced @1 broken pin insulator on pole 22-U-01. 08:31 By Pass NELLA GFPC and on blick position. Manually blocked and closed Nella VCB feeder #1 --> OK. and then released the block. Cause: Broken Pin Insulator. | 123 | 1 | 3:25 | Night | Thursday | 2019 | 10
12141 | 2019-10-17 03:53 | 2019-10-17 03:53 | 115KV KETIGUL - MENGGALA | Rain and Lightning | Unidentified | 596 | 03:53 115 kV Line Ketigul Menggala T/R 1x (freq = 60.33 Hz) - 115 kV GCB #1 Ketigul T/R 1x, ctr: 198 - 199 - 115 kV GCB #3 Ketigul T/SO, ctr: 166 - 167 R/F: 87L @1,2,3, 21PZ1. Closed at 06:07, OK. - 115 kV GCB #29 Menggala T/R 1x. Respectively load dropped at any feeders. 1. So Balam Subst - So BLM fdr #1 load dropped 113 A (149 - 36 A) - So BLM fdr #2 T/R 1x - So BLM fdr #3 T/R 1x - So BLM fdr #4 load dropped 131 A (192 - 61 A) 2. Nella Subst - Nella fdr #2 load dropped 13 A (70 - 57 A) 3. Bangko Subst - Bangko fdr #1 load dropped 125 A (161 - 36 A) - Bangko fdr #2 load dropped 241 A (259 - 18 A) - Bangko fdr #3 load dropped 207 A (219 - 12 A) - Bangko fdr #4 load dropped 88 A (169 -81 A) 4. Sintong Subst - Sintong fdr #1 load dropped 52 A (15 - 63 A) - Sintong fdr #2 load dropped 80 A (198 - 118) 5. Menggala Subst - Menggala fdr #1 load dropped 77 A (158 - 79 A) - Menggala fdr #2 load dropped 149 (168 - 19 A) - Menggala GFPC T/R 1x) 6. Batang Subst - Batang fdr #3 load dropped 12 A (55-43 A) 7. Ketigul Subst - Ketigul fdr #1 17 A (116 - 99 A) - Ketigul fdr #2 55 A (70 - 15 A) - Ketigul fdr #3 31 A (37 - 6 A) 8. Pematang Subst - Pematang fdr #1 38 A (208 - 170 A) - Pematang fdr #2 8 A (110 - 102 A) 9. Rokan Subst - Rokan fdr #3 26 A (45 - 19 A) 10. Petani Subst - Petani fdr #1 44 A (234 - 190 A) Cause: Not Checked Yet. Production loss: So. Balam Sub. : 161 Bbls / 23 Wells. Menggala Sub. : 194 Bbls / 10 Wells. Ketigul Sub. : 241 Bbls / 8 Wells. -------------------------------------------+ TOTAL : 596 Bbls / 41 Wells. | 123 | 1 | 3:53 | Night | Thursday | 2019 | 10
12142 | 2019-10-17 03:53 | 2019-10-27 07:37 | 115KV KETIGUL - MENGGALA | Rain and Lightning | Unidentified | 596 | Checked & found Ketigul GCB #1 T/R 1x, 198-199, R/F: 21 Ketigul GCB #3 Ctr;167 Not Operated. Menggala GCB#29 Not operated. Patrolled the Line, but found nothing Cause : Unidentified | 123 | 1 | 3:53 | Night | Thursday | 2019 | 10
12143 | 2019-10-17 03:53 | 2019-10-17 03:53 | 13.8KV S. BALAM FEEDER #3 | Rain and Lightning | Unidentified | 0 | So Balam VCB fdr #3 T/R 1x. Not checked yet. |  | 1 | 3:53 | Night | Thursday | 2019 | 10
12144 | 2019-10-17 03:53 | 2019-10-19 15:06 | 13.8KV S. BALAM FEEDER #3 | Rain and Lightning | Unidentified | 0 | Checked and found South BALAM fdr #3 not operate, ctr: 172-172, R/F: None Not patrolled the line due to the breaker not operated. Cause : Unidentified |  | 1 | 3:53 | Night | Thursday | 2019 | 10
12145 | 2019-10-17 03:53 | 2019-10-17 03:53 | 13.8KV S. BALAM FEEDER #2 | Rain and Lightning | Unidentified | 0 | So Balam VCB fdr #2 T/R 1x. Not checked yet. |  | 1 | 3:53 | Night | Thursday | 2019 | 10
12146 | 2019-10-17 03:53 | 2019-10-19 15:06 | 13.8KV S. BALAM FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found South BALAM fdr #2 not operated, ctr: 118-118, R/F: None Not patrolled the line due to the breaker not operated/normal. Cause : Unidentified |  | 1 | 3:53 | Night | Thursday | 2019 | 10
12147 | 2019-10-17 09:26 | 2019-10-17 09:26 | 13.8KV 4D FEEDER #4 | Fair | Planned Maintenance | 64 | 09:26 Manually open LBS 4D-88A D/S 4D feeder #4. Due to replaced broken dead end insulator on pole 3E-61. 11:39 Manually Closed LBS 4D-88A. Cause: Plan Maintenance. |  | 1 | 9:26 | Morning | Thursday | 2019 | 10
12148 | 2019-10-17 11:22 | 2019-10-17 11:22 | CENTRAL DURI POWER PLANT |  |  | - | 11:22 CGT #1 Off line and then S/D and then 11:23 for S/B. |  | 1 | 11:22 | Morning | Thursday | 2019 | 10
12149 | 2019-10-17 15:59 | 2019-10-17 15:59 | 115KV KOTABATAK JUNCTION - LIBO LINE | Rain and Lightning | Unidentified | 7 | KBJ 115 KV GCB #53 T/R 1x. KBJ 115 KV GCB #55 T/R 1x. (115KV KBJ - LIBO Line). No power to Libo Substation. Not checked yet. |  | 1 | 15:59 | Afternoon | Thursday | 2019 | 10
12150 | 2019-10-17 15:59 | 2019-10-27 15:59 | 115KV KOTABATAK JUNCTION - LIBO LINE | Rain and Lightning | Unidentified | 7 | Checked & found 115Kv Line KBJ - Libo GCB#53 T/R 1x Ctr:248-249 R/F: 67N. 115Kv Line KBJ - Libo GCB#55 T/R 1x Ctr:326-327. Patrolled the line & found @1 Broken Dead End Insulator o/p KW-11. Cause : Dead End Insulator. |  | 1 | 15:59 | Afternoon | Thursday | 2019 | 10
12151 | 2019-10-17 16:34 | 2019-10-17 16:34 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Animal | 85 | Libo OCB feeder #2 T/R 1x. Not checked yet. |  | 1 | 16:34 | Afternoon | Thursday | 2019 | 10
12152 | 2019-10-17 16:34 | 2019-10-20 08:46 | 13.8KV LIBO FEEDER #2 | Rain and Lightning | Animal | 85 | Checked and found VCB LIBO fdr #2 T/R 1x, ctr: 513-514, R/F: 51N Patrolled the line and found dead animal (bird) at SE LIBO #53 Cause : Animal |  | 1 | 16:34 | Afternoon | Thursday | 2019 | 10
12153 | 2019-10-18 06:08 | 2019-10-18 06:08 | 13.8KV CENTRAL DURI FEEDER #15 | Fair | Powerline - Conductor | 68 | 06:08 CD fdr #15 T/O (on block position for BMS #10 at 6Q-10A) Counter: 415 - 416, R/F: 50P call TDO crew (Fetrineldi) 06:13 Reported by HO DSC, there are broken conductor at pole 06-Q5-09 call rig BMS #10, status clear/ok. call TL Ops (Soski) to inform the case. 06:56 Checked and found b/o conductor on pole 06-Q5-08 // 06-Q5-10. 07:02 Open LBS 06-Q5-02 to isolate broken conductor. 07:26 Manually blocked and closed C Duri ACB #18 (feeder #15) --> OK (still in blocked position due to RIG BMS #10 activity at well # 6Q-10A). Continued reconnect conductor. C Duri feeder #15 still dropped 8A (53-45A). 14:49 Closed LBS 06-Q5-02 , Load C Duri Feeder #15 back to normal. Cause: Conductor. |  | 1 | 6:08 | Morning | Friday | 2019 | 10
12154 | 2019-10-18 07:07 | 2019-10-18 07:07 | 13.8KV NORTH DURI FEEDER #8 | Fair | Dead End Insulator | 0 | N Duri VCB feeder #8 T/R 1x. Not checked yet. |  | 1 | 7:07 | Morning | Friday | 2019 | 10
12155 | 2019-10-18 07:07 | 2019-10-25 07:07 | 13.8KV NORTH DURI FEEDER #8 | Fair | Dead End Insulator | 0 | Checked & found N.Duri VCB fdr#8 T/R 1x Ctr:97-98 R/F:51N. Patrolled the line & foune @1@2 Broken Dead End Insulator o/p NE-08. Cause : Dead End Insulator. |  | 1 | 7:07 | Morning | Friday | 2019 | 10
12156 | 2019-10-18 10:15 | 2019-10-18 10:15 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 0 | 10:15 Manually open Recloser: 8D-18A D/S 8C feeder #3. Due to Change out Tx. at well 8D-43. 10:58 Manually blocked & Closed Recloser 8D 18A --> OK. and then released the block. Cause: Planned Maintenance. |  | 1 | 10:15 | Morning | Friday | 2019 | 10
12157 | 2019-10-18 10:38 | 2019-10-18 10:38 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 21 | 10:38 OKB fdr #2 Load dropped 83A (257-174A). 14:00 Checked and found Recloser: 38-CX-25 T/R 3x. Counter: 337-340. Patrolled the line found nothing. Cause: Unidentified. |  | 1 | 10:38 | Morning | Friday | 2019 | 10
12158 | 2019-10-18 10:38 | 2019-10-21 13:31 | 13.8KV KOTABATAK FEEDER #2 | Fair | Unidentified | 21 | Checked and found : 5443-R.38CX25 T/R, Counter : 337 - 340, Relay Flag : 51N Patrolled the line found : Nothing found Cause : Unidentified. |  | 1 | 10:38 | Morning | Friday | 2019 | 10
12159 | 2019-10-18 14:57 | 2019-10-18 14:57 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | C Duri ACB #28 (feeder #16) T/R 1x. Counter: 359-360 R/F: 51@1,@2. Not patrolled yet. |  | 1 | 14:57 | Afternoon | Friday | 2019 | 10
12160 | 2019-10-18 14:57 | 2019-10-25 08:57 | 13.8KV CENTRAL DURI FEEDER #16 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 14:57 | Afternoon | Friday | 2019 | 10
12161 | 2019-10-18 16:37 | 2019-10-18 16:37 | 13.8KV NELLA FEEDER #1 | Fair | Emergency | - | 16:37 Manually open Nella VCB feeder #1, closed at 18:41 16:38 Manually open Bangko OCB feeder #1, closed at 19:01 due to abnormal condition. - Control valve incoming Surge tank problem. Cause: Emergency |  | 1 | 16:37 | Afternoon | Friday | 2019 | 10
12162 | 2019-10-19 02:03 | 2019-10-19 02:03 | 13.8KV NELLA FEEDER #1 | Rain and Lightning | Lightning | 204 | 02:03 Nella fdr #1 T/R 1x Nella fdr #2 dropped 51 A (70 - 19 A) Bus voltage reach to 14.5 kV and then down to 13.2 kV 03:20 Checked and found: Nella VCB fdr #1 T/R 2x, ctr: 560 - 562, R/F 51P @1,2,3 RCL for Cap Bank T/O 03:27 Manual Close RCL for Cap bank, OK. bus voltage = 13.7 kV Cause: Not Patrolled Yet |  | 1 | 2:03 | Night | Saturday | 2019 | 10
12163 | 2019-10-19 02:03 | 2019-10-19 02:03 | 13.8KV S. BALAM FEEDER #4 | Heavy Rain | Follow Another Outage | 0 | 02:03 So Balam fdr #4 dropped 26 A (192 - 166 A) So Balam fdr #1 dropped 9 A (152 - 143 A ) Cause: Follow Another Outage. |  | 1 | 2:03 | Night | Saturday | 2019 | 10
12164 | 2019-10-19 07:25 | 2019-10-19 07:25 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 15 | C Duri ACB #11 (feeder #1) T/R 1x. Counter: 264 (do not change) R/F: 51@1 , 51N. Not patrolled yet. |  | 1 | 7:25 | Morning | Saturday | 2019 | 10
12165 | 2019-10-19 07:25 | 2019-10-22 08:27 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 15 | Checked and found: - C Duri ACB #11 (feeder #1) T/R 1x. - Counter: 264 (do not change) R/F: 51@1 , 51N. Patrolled the line found nothing. Cause : Unidentified. |  | 1 | 7:25 | Morning | Saturday | 2019 | 10
12166 | 2019-10-19 07:55 | 2019-10-19 07:55 | CENTRAL DURI POWER PLANT |  |  | - | CDGT #1 S/U and then Online the unit at 08:36. |  | 1 | 7:55 | Morning | Saturday | 2019 | 10
12167 | 2019-10-19 09:36 | 2019-10-19 09:36 | CENTRAL DURI POWER PLANT |  |  | - | CDGT #2 Off line and then S/D the unit at 09:25 for S/B. |  | 1 | 9:36 | Morning | Saturday | 2019 | 10
12168 | 2019-10-19 10:30 | 2019-10-19 10:30 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | N Duri VCB feeder #5 T/R 1x. Not checked yet. |  | 1 | 10:30 | Morning | Saturday | 2019 | 10
12169 | 2019-10-19 10:30 | 2019-10-25 10:30 | 13.8KV NORTH DURI FEEDER #5 | Fair | Unidentified | 0 | Checked & found N.Duri VCB fdr#5 T/R 1x Ctr:134-135 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 10:30 | Morning | Saturday | 2019 | 10
12170 | 2019-10-19 14:26 | 2019-10-19 14:26 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Unidentified | 0 | Petapahan VCB feeder #6 T/R 1x. Counter: 378-379 R/F: 51@2. Not patrolled yet. |  | 1 | 14:26 | Afternoon | Saturday | 2019 | 10
12171 | 2019-10-19 14:26 | 2019-10-21 13:33 | 13.8KV PETAPAHAN FEEDER #6 | Fair | Unidentified | 0 | Checked and found: - Petapahan VCB feeder #6 T/R 1x Counter : 378 - 379 Relay Flag : 51N. Patrolled the line found nothing. Cause : Unidentified. |  | 1 | 14:26 | Afternoon | Saturday | 2019 | 10
12172 | 2019-10-19 14:56 | 2019-10-19 14:56 | 13.8KV MENGGALA FEEDER #1 | Fair | Animal | 252 | 14:56 Menggala OCB feeder #1 T/O. BOPD: 1961 Barrels / 31 wells. (Balam GS) Menggala GFPC T/R 1x. 15:53 Checked and found Menggala OCB feeder #1 T/LO . Counter: 573-577 R/F: 51N. Menggala GFPC T/R 2x R/F: 51N. Patrolled the line found: - @2 broken lightning Arrester and @1 broken dead end insulator- on terminal pole well Meno #12 (LTC well). - Jumper of Lightning Arrester touching to buck arm. - Opened HLC on terminal pole Meno #12. to isolated -@2 broken lightning Arrester and @1 broken dead end insulator. 19:03 Blocked and closed Menggala fdr #1, OK then released the block. Caused: Animal (monkey). |  | 1 | 14:56 | Afternoon | Saturday | 2019 | 10
12173 | 2019-10-19 14:56 | 2019-10-19 14:56 | 13.8KV MENGGALA FEEDER #2 | Fair | Lightning | 0 | Menggal feeder #2 load dropped 114A (156-42A). Not checked yet. |  | 1 | 14:56 | Afternoon | Saturday | 2019 | 10
12174 | 2019-10-19 14:56 | 2019-10-27 09:56 | 13.8KV MENGGALA FEEDER #2 | Fair | Lightning | 0 | Checked & found Menggala VCB fdr#2 T/R 1x Ctr:115-116 R/F:51N Patrolled the line & found @2 Broken Dead End Insulator o/p 26AL59. Cause : Lightning. |  | 1 | 14:56 | Afternoon | Saturday | 2019 | 10
12175 | 2019-10-19 16:14 | 2019-10-19 16:14 | 13.8KV BANGKO FEEDER #4 | Drizzle | Lightning | 6 | Bangko OCB feeder #4 T/R 1x. Not checked yet. |  | 1 | 16:14 | Afternoon | Saturday | 2019 | 10
12176 | 2019-10-19 16:14 | 2019-10-23 00:56 | 13.8KV BANGKO FEEDER #4 | Drizzle | Lightning | 6 | Checked and found: - Bangko VCB feeder #4 T/R 1x Counter: 73-74 R/F: 51@1. - Bangko GFPC T/R 1x. Patrolled the line found nothing. Cause: Suspected lightning. |  | 1 | 16:14 | Afternoon | Saturday | 2019 | 10
12177 | 2019-10-19 16:14 | 2019-10-19 16:14 | 13.8KV BANGKO FEEDER #1 | Drizzle | Lightning | 0 | Bangko feeder #1 load dropped 64A (154-94A). Bangko feeder #2 load dropped 118A (260-142A) --> WIP. Bangko feeder #3 load dropped 202A (223-21A) --> WIP. Cause: Not checked yet. |  | 1 | 16:14 | Afternoon | Saturday | 2019 | 10
12178 | 2019-10-19 16:14 | 2019-10-23 01:01 | 13.8KV BANGKO FEEDER #1 | Drizzle | Lightning | 0 | Checked and found: - Bangko GFPC T/R 1x R/F: 51N. - Recloser: 23-W-12 T/R 1x Counter: 316-317 R/F:51 on @1,@3. Patrolled the line found nothing. Cause: Suspected lightning. |  | 1 | 16:14 | Afternoon | Saturday | 2019 | 10
12179 | 2019-10-20 07:06 | 2019-10-20 07:06 | 44KV NORTH DURI - DUMAI LINE | Fair | Animal | 0 | 07:06 N.Duri GCB #1 (44 KV Line Duri - Dumai ) T/R 1X. N.Duri 13.8 KV VCB #14 T/LO. 07:19 Checked and found Animal (dead Monkey) 07:35 Manually Closed N.Duri 13.8 KV VCB #14. Cause : Monkey ( Animal ). |  | 1 | 7:06 | Morning | Sunday | 2019 | 10
12180 | 2019-10-20 08:02 | 2019-10-20 08:02 | 13.8KV S. BALAM FEEDER #1 | Fair | Lightning | 81 | S.Balam VCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 8:02 | Morning | Sunday | 2019 | 10
12181 | 2019-10-20 08:02 | 2019-10-25 08:02 | 13.8KV S. BALAM FEEDER #1 | Fair | Lightning | 81 | Checked & found So.Balam VCB fdr#1 T/R 1x Ctr:407-408 R/F:51N. Patrolled the line & found @2 Broken LA o/p 17Z15. Cause : Lightning |  | 1 | 8:02 | Morning | Sunday | 2019 | 10
12182 | 2019-10-20 21:38 | 2019-10-20 21:38 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Tree | 9 | Pinang VCB feeder #1 T/R 1x Not Checked Yet. |  | 1 | 21:38 | Night | Sunday | 2019 | 10
12183 | 2019-10-20 21:38 | 2019-10-27 07:47 | 13.8KV PINANG FEEDER #1 | Rain and Lightning | Tree | 9 | Checked & found Pinang OCB fdr#1 T/R 1x, Ctr: 453-454, R/F: 51N Patrolled the Line, found Akasia Tree touch @2 O/p 10C-27, and Sawit @1 Near Pinang #22 Cause : Tree |  | 1 | 21:38 | Night | Sunday | 2019 | 10
12184 | 2019-10-21 04:57 | 2019-10-21 04:57 | 13.8KV NELLA FEEDER #2 | Fair | Emergency | 0 | 04:57 Manual Open Nella VCB fdr #2 Due to Maintain level tank at BKO EOR. 06:55 Manually blocked and closed Nella VCB feeder #2. and then released the block. 10:34 Manual Open Nella VCB feeder #2. Due to Maintain level tank at BKO EOR. 14:26 Manually blocked and closed Nella VCB feeder #2. and then released the block. Cause: Emergency. |  | 1 | 4:57 | Morning | Monday | 2019 | 10
12185 | 2019-10-21 06:23 | 2019-10-21 06:23 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 18 | Ketigul 13.8KV VCB fdr #2 T/R 1X. Not checked yet. |  | 1 | 6:23 | Morning | Monday | 2019 | 10
12186 | 2019-10-21 06:23 | 2019-10-25 06:23 | 13.8KV KETIGUL FEEDER#2 | Fair | Unidentified | 18 | Checked & found Ketigul VCB fdr#2 T/R 1x Ctr:355-356 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 6:23 | Morning | Monday | 2019 | 10
12187 | 2019-10-21 11:00 | 2019-10-21 11:00 | 13.8KV 8C FEEDER #3 | Fair | Planned Maintenance | 292 | 11:00 Manually open Recloser: 8D-18A D/S 8C feeder #3. Due to cut jumper on pole 8D-43, 8D-46 and 8D-46A. (to isolated power line for supporting Toll Road project). 14:59 Manually blocked and closed Recloser: 8D-18A and then released the block. 7 wells ON: 8D-33A, 52E, 54, 53, 43, 45, 43A 20:00 Manual Close LBS 7D-177 (Transfer part load 8C fdr #3 to Minas feeder #3) 5 wells ON: 8C-49A, 8C-29E, 8C-29, 8D-41N, 8D-40 20:35 Manual Close LBS 8D-158 (transfer part load 8C feeder #3 to 8C feeder #4) 18 wells ON: 8D-52N, 53A, 52, 61, 51, 41E, 41 8C-78, 79, 68, 69, 59, 76, 77, 58N, 48E, 49, 69F 21:46 Reported still no power at 11 location around wells 8D-52, 8D-53A, etc. 22:19 Open LBS 8D-158 (8C fdr #4) 22:32 Close LBS 8D-247 (transfer part load 8C feeder #3 to 8C fdr #5) 18 wells above transferred from 8C fdr #3 to 8C fdr #5) (8D-52N, 53A, 52, 61, 51, 41E, 41 8C-78, 79, 68, 69, 59, 76, 77, 58N- 48E, 49, 69F) Cause: Planned maintenance. |  | 1 | 11:00 | Morning | Monday | 2019 | 10
12188 | 2019-10-21 13:03 | 2019-10-21 13:03 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Unidentified | 0 | 4D feeder #4 load dropped 90A (216-126A). Not checked yet. |  | 1 | 13:03 | Afternoon | Monday | 2019 | 10
12189 | 2019-10-21 13:03 | 2019-10-27 09:03 | 13.8KV 4D FEEDER #4 | Rain and Lightning | Unidentified | 0 | Checked & found Recl. 4D-51D T/R 1x Ctr:102-103. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 13:03 | Afternoon | Monday | 2019 | 10
12190 | 2019-10-21 13:05 | 2019-10-21 13:05 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | - | 4D feeder #5 load dropped 26A (74-48A). Not checked yet. |  | 1 | 13:05 | Afternoon | Monday | 2019 | 10
12191 | 2019-10-21 13:05 | 2019-10-25 10:40 | 13.8KV 4D FEEDER #5 | Rain and Lightning | Lightning | - | Checked and found : 5442-R.4D14A T/R, Counter : 277 - 278, Relay Flag : NONE Patrolled the line found : Nothing Cause : Lightning |  | 1 | 13:05 | Afternoon | Monday | 2019 | 10
12192 | 2019-10-21 13:25 | 2019-10-21 13:25 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 52 | 3D OCB feeder #8 T/R 1x. Not checked yet. |  | 1 | 13:25 | Afternoon | Monday | 2019 | 10
12193 | 2019-10-21 13:25 | 2019-10-25 10:45 | 13.8KV 3D FEEDER #8 | Rain and Lightning | Lightning | 52 | Checked and found : 3DSB-13.8OCB8 T/R, Counter : 333 - 334, Relay Flag : 51. Patrolled the line found : Broken Dead end Cause : Lightning |  | 1 | 13:25 | Afternoon | Monday | 2019 | 10
12194 | 2019-10-21 14:15 | 2019-10-21 14:15 | 13.8KV NEW KOTABATAK FEEDER #4 | Rain and Lightning | Lightning | 12 | NKBS VCB feeder #4 T/R 1x. NKBS GFPC T/R 1x. Not checked yet. |  | 1 | 14:15 | Afternoon | Monday | 2019 | 10
12195 | 2019-10-21 14:15 | 2019-10-22 07:42 | 13.8KV NEW KOTABATAK FEEDER #4 | Rain and Lightning | Lightning | 12 | Checked and found: - NKBS VCB feeder #4 T/R 1x Counter : 288 - 289, R/F:51N. Patrolled the line found nothing. Cause : Suspected lightning. |  | 1 | 14:15 | Afternoon | Monday | 2019 | 10
12196 | 2019-10-22 05:34 | 2019-10-22 05:34 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 0 | Minas feeder #2 (ACB #13) T/R 1x Not Checked Yet |  | 1 | 5:34 | Morning | Tuesday | 2019 | 10
12197 | 2019-10-22 05:34 | 2019-10-27 09:34 | 13.8KV MINAS FEEDER #2 | Fair | Unidentified | 0 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 5:34 | Morning | Tuesday | 2019 | 10
12198 | 2019-10-22 16:22 | 2019-10-22 16:22 | 13.8KV CENTRAL DURI FEEDER #6 | Rain and Lightning | Lightning Arrester | 0 | C.Duri 13.8KV ACB fdr#6 T/R 1x. Ctr: 508-509 R/F 51G , 51N , 51 @2. Not checked yet. |  | 1 | 16:22 | Afternoon | Tuesday | 2019 | 10
12199 | 2019-10-22 16:22 | 2019-10-27 14:25 | 13.8KV CENTRAL DURI FEEDER #6 | Rain and Lightning | Lightning Arrester | 0 | Checked & found CDuri ACB fdr#6 T/R 1x, Ctr: 508-509, R/F: 51G,51N,51@2 Patrolled the Line, found @2 Broken LA O/P 01 03 07A Cause : Lightning Arrester |  | 1 | 16:22 | Afternoon | Tuesday | 2019 | 10
12200 | 2019-10-22 17:57 | 2019-10-22 17:57 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 16 | Ketigul 13.8KV VCB fdr#2 T/R 1x. Ketigul fdr#1 l;oad dropped 32A (112-80A). Ketigul fdr#3 l;oad dropped 7A (37-30A). Not checked yet. |  | 1 | 17:57 | Afternoon | Tuesday | 2019 | 10
12201 | 2019-10-22 17:57 | 2019-10-27 07:57 | 13.8KV KETIGUL FEEDER#2 | Cloudy | Unidentified | 16 | Checked & Found Ketigul VCB fdr#2 T/R 1x Ctr:355-356 R/F:51N. Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 17:57 | Afternoon | Tuesday | 2019 | 10
12202 | 2019-10-23 14:05 | 2019-10-23 14:05 | 13.8KV NELLA FEEDER #2 | Fair | Emergency | - | 14:05 Manually opened Nella fdr#2. Maintain tank level by air compressor trouble. 14:40 Blocked & closed Nella fdr#2 the reboot the block. Cause: Emergency. |  | 1 | 14:05 | Afternoon | Wednesday | 2019 | 10
12203 | 2019-10-23 15:31 | 2019-10-23 15:31 | 13.8KV 6D FEEDER #2 | Fair | Tree | 64 | 15:31 6D feeder#2 load dropped 106A (171-65A). 16:30 Checked & found Recloser: 6D-298 T/SO Counter: 84-86. Blocked & closed Recloser: 6D-298 and then released the block. Cause: Tree. |  | 1 | 15:31 | Afternoon | Wednesday | 2019 | 10
12204 | 2019-10-23 19:28 | 2019-10-23 19:28 | 13.8KV 6DN FEEDER #1 | Cloudy and Lightning | Tree | 10 | 6DN OCB feeder #1 T/R 1x. Not checked yet. |  | 1 | 19:28 | Night | Wednesday | 2019 | 10
12205 | 2019-10-23 19:28 | 2019-10-27 16:28 | 13.8KV 6DN FEEDER #1 | Cloudy and Lightning | Tree | 10 | Checked & found 6DN fdr#1 T/R 1x Ctr:179-180 R/F:51@2@. Patrolled the line & found Danger Trees Near pole 5E-03 , 5E-04. Cause : Tree. |  | 1 | 19:28 | Night | Wednesday | 2019 | 10
12206 | 2019-10-23 19:28 | 2019-10-23 19:28 | 13.8KV 6D FEEDER #2 | Cloudy and Lightning | Unidentified | 1 | 6DN feeder #2 load dropped 198A (240-42A). 6DN feeder #3 load dropped 63A (197-134A) --> WIP. Not checked yet. |  | 1 | 19:28 | Night | Wednesday | 2019 | 10
12207 | 2019-10-23 19:28 | 2019-10-27 14:28 | 13.8KV 6D FEEDER #2 | Cloudy and Lightning | Unidentified | 1 | Checked & found Recl 6D 298 T/R, Ctr: 83-86, R/F: None Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 19:28 | Night | Wednesday | 2019 | 10
12208 | 2019-10-23 19:42 | 2019-10-23 19:42 | 13.8KV 6DN FEEDER #6 | Rain and Lightning | Pin Insulator | 379 | 19:42 6DN fdr#6 Load dropped 142A (189-47A). 24 Oct 2019. 10:45 Checked & found Recl 6E-64 T/LO ctr:224-237. Patrolled the line & found @2 Broken Pin Insulator o/p 6E-84 then Replaced. 13:35 Blocked & closed Recl. 6E-64, then release the block. Cause: Pin Insulator. |  | 1 | 19:42 | Night | Wednesday | 2019 | 10
12209 | 2019-10-24 00:10 | 2019-10-24 00:10 | 13.8KV 5B FEEDER #2 | Fair | Unidentified | 345 | 5B feeder #2 load dropped 151A (258-107A). Not checked yet. |  | 1 | 0:10 | Night | Thursday | 2019 | 10
12210 | 2019-10-24 00:10 | 2019-10-27 08:35 | 13.8KV 5B FEEDER #2 | Fair | Unidentified | 345 | Checked & found Recl 5C07 T/R, Ctr: 191-192, R/F: None Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 0:10 | Night | Thursday | 2019 | 10
12211 | 2019-10-24 05:50 | 2019-10-24 05:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 25 | 05:50 It was reported no power on pole 08-L5-35. D/S C.Duri feeder #1. 06:47 Checked & found Recloser 08-L5-35 T/SO, (in block position due to PT WKS clean up canal)). 06:50 Manually Blocked & Closed Recloser 08-L5-35 ( Block position).ctr:952-953. Cause: Not patrolled yet. |  | 1 | 5:50 | Morning | Thursday | 2019 | 10
12212 | 2019-10-24 05:50 | 2019-10-27 08:50 | 13.8KV CENTRAL DURI FEEDER #1 | Fair | Unidentified | 25 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 5:50 | Morning | Thursday | 2019 | 10
12213 | 2019-10-24 08:11 | 2019-10-24 08:11 | 13.8KV DURI FIELD FEEDER #4 | Fair | Pin Insulator | 39 | 08:11 Duri Field ACB #51 (feeder#4) T/LO . 09:10 Checked and found: - Duri Field ACB #51 (feeder#4) T/LO Counter:566-570 R/F:51N. Patrolled the line & found: @1 Flash over Pin Insulator o/p 07-V1-18. @2 Flash over Pin Support Insulator o/p 07-V1-23. @1 B/O fuse for 112.5KVA Tx o/p 07-V3-05. 09:45 Blocked & closed Duri Field ACB fdr#4, then release the block. Cause: Pin Insulator. Production loss FOD #1: 70 Bbls / 162 wells. Production loss FOD #2: 12 Bbls / 23 wells. ---------------------------------------------------- + Grand total : 82 Bbls / 185 wells. |  | 1 | 8:11 | Morning | Thursday | 2019 | 10
12214 | 2019-10-25 06:20 | 2019-10-25 06:20 | 44KV PEMATANG MAIN - RANGAU LINE | Cloudy | Dead End Insulator | 19 | Pematang main 44 Kv OCB #2 (To RANGAU ) T/R 1x. Supplied to Rangau Substation, the RGU OCB #1, #2 still Close - Production loss Rangau feeder #1 : 2 bbls / 2wells. - Production loss Rangau feeder #2 :20 bbls / 20 wells. ----------------------------------------------------------- + Grand total : 22 Bbls / 22 wells. Not checked yet. |  | 1 | 6:20 | Morning | Friday | 2019 | 10
12215 | 2019-10-25 06:20 | 2019-10-27 14:17 | 44KV PEMATANG MAIN - RANGAU LINE | Cloudy | Dead End Insulator | 19 | Checked & found Pematang 44KV OCB #2 T/R 1x, Ctr: 39995 - 40006, R/F: 50N Patrolled the Line, Found broken Pin Insulator at RGU 56, and Flash Deadend at RGU 29 Cause : Dead End Insulator |  | 1 | 6:20 | Morning | Friday | 2019 | 10
12216 | 2019-10-25 13:42 | 2019-10-25 13:42 | MINAS POWER PLANT |  |  | - | 13:42 MGT#9 S/U, then On Line at 14:03 to Backed up power due to NDC CT#3 will be S/D |  | 1 | 13:42 | Afternoon | Friday | 2019 | 10
12217 | 2019-10-25 14:22 | 2019-10-25 14:22 | 13.8KV 3D FEEDER #6 | Rain and Lightning | Unidentified | 137 | 14:22 3D Substation RTU Failed. It was reported GS#5 No Power D/S 3D fdr#6. 16:30 Checked & found 3D OCB fdr#6 T/SO Ctr:297-299 R/F:51N. 17:10 Blocked & Closed 3D OCB fdr#6, then release the block. Not Patrolled yet. |  | 1 | 14:22 | Afternoon | Friday | 2019 | 10
12218 | 2019-10-25 14:22 | 2019-10-27 08:47 | 13.8KV 3D FEEDER #6 | Rain and Lightning | Unidentified | 137 | Checked & found 3D OCB fdr#6 T/SO, Ctr: 298-299, R/F: 51 @2,3 Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 14:22 | Afternoon | Friday | 2019 | 10
12219 | 2019-10-25 15:09 | 2019-10-25 15:09 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Animal | 709 | 15:09 C.Duri ACB fdr#1 T/LO Ctr264-268 R/F:51@1@3, 51G. Patrolled the line & found @1 Broken FCO at well Kulim#14. @3 Broken FCO at well Kulim#69. 19:10 Blocked & Closed C.Duri fdr#1, then release the block. Cause: Lightning. |  | 1 | 15:09 | Afternoon | Friday | 2019 | 10
12220 | 2019-10-25 15:09 | 2019-10-26 15:43 | 13.8KV CENTRAL DURI FEEDER #1 | Rain and Lightning | Animal | 709 | Checked and found: CDRSG-13.8ACB11 T/LO, Counter : 264 - 268, Relay Flag : 51. Patrolled the lune found : Relay flag 51 Phase # 1 dan # 3 dan 51 G (monyet di trafo di kulim # 69) Cause : Animal |  | 1 | 15:09 | Afternoon | Friday | 2019 | 10
12221 | 2019-10-25 15:10 | 2019-10-25 15:10 | NORTH DURI POWER PLANT | Rain and Lightning | Under investigation | 968 | 15:10 N Duri CT #3 Generator Breaker Trip, Closed at 15:17 Load shedding Level 2, with Frequency 59.47Hz 4D VCB fdr#4 T/O, Closed at 15:29 Prod Loss: 66 Bbls / 16 wells. 4B VCB fdr#4 T/O, Closed at 15:18 Prod Loss: 8 Bbls / 6 wells. 4B VCB fdr#1 T/O, Closed at 15:19 Prod Loss: 5 Bbls / 25 wells. 5B VCB fdr#7 T/O, Closed at 15:25 Prod Loss: 14 Bbls / 6 wells. 5B VCB fdr#4 T/O, Closed at 15:26 Prod Loss: 16 Bbls / 11 wells. 5B VCB fdr#5 T/O, Closed at 15:27 Prod Loss: 11 Bbls / 7 wells. BOB Jambrud ACB fdr#1 Closed at 15:30 BOB Jambrud ACB fdr#2 Closed at 15:30 15:39 NDC CT #3 Generator Breaker Trip, Closed at 16:01 Cause: Under Investigate. |  | 1 | 15:10 | Afternoon | Friday | 2019 | 10
12222 | 2019-10-25 15:31 | 2019-10-25 15:31 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Lightning Arrester | 494 | 15:31 Petani VCB fdr#1 T/R 1x. Petani fdr#2 Load dropped 49A (60-11A). 18:00 Petani Fdr#1 Load dropped 147A(240-93A) It was reported no Power Under Petani fdr#1. 20:14 Checked and found: - Recloser: 33-AY-47 T/SO Counter: 207-208. 20:25 Manually blocked and closed Recloser: 33-AY-47 --> OK and then released the block. Cause: Not patrolled yet. |  | 1 | 15:31 | Afternoon | Friday | 2019 | 10
12223 | 2019-10-25 15:31 | 2019-10-27 07:08 | 13.8KV PETANI FEEDER #1 | Rain and Lightning | Lightning Arrester | 494 | Checked and found: PTNSB-13.8OCB1 T/R, Counter : 142 - 144, Relay Flag : 51 Patrolled the line found : lightning arrester pecah di phase 2 di terminal Pole Cause : Lightning Arrester |  | 1 | 15:31 | Afternoon | Friday | 2019 | 10
12224 | 2019-10-25 15:36 | 2019-10-25 15:36 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Lightning Arrester | 0 | N.Duri VCB fdr#2 T/R 1x. Not checked yet. |  | 1 | 15:36 | Afternoon | Friday | 2019 | 10
12225 | 2019-10-25 15:36 | 2019-10-29 07:03 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Lightning Arrester | 0 | Checked and found: NDRSB-13.8VCB2 T/R, Counter : 282 - 284, Relay Flag : 50 Patrolled the line found : Temuan di Pole LBS NF 07 jumper LA putus di LBS. Cause : Lightning Arrester |  | 1 | 15:36 | Afternoon | Friday | 2019 | 10
12226 | 2019-10-25 15:37 | 2019-10-25 15:37 | 13.8KV NORTH DURI FEEDER #11 | Rain and Lightning | Tree | 104 | N.Duri VCB fdr#11 T/R 1x. Not checked yet. |  | 1 | 15:37 | Afternoon | Friday | 2019 | 10
12227 | 2019-10-25 15:37 | 2019-10-27 07:24 | 13.8KV NORTH DURI FEEDER #11 | Rain and Lightning | Tree | 104 | Checked and found: NDRSB-13.8VCB11 T/R, Counter : 192 - 193, Relay Flag : 51 Patrolled the line found : Temuan Pohon dekat dengan powerline di phase 1,2,3: Cause : Tree |  | 1 | 15:37 | Afternoon | Friday | 2019 | 10
12228 | 2019-10-25 15:40 | 2019-10-25 15:40 | 13.8KV NORTH DURI FEEDER #5 | Rain and Lightning | Suspension Insulator | 0 | N.Duri VCB fdr#5 T/R 1x, Not checked yet. |  | 1 | 15:40 | Afternoon | Friday | 2019 | 10
12229 | 2019-10-25 15:40 | 2019-10-27 07:01 | 13.8KV NORTH DURI FEEDER #5 | Rain and Lightning | Suspension Insulator | 0 | Checked and found: NDRSB-13.8VCB5 T/R, Counter : 135 - 136, Relay Flag : 51 Patrolled the line found : suspension insulator broken phase 2 layer 1 broken 50% Cause : Suspension Insulator |  | 1 | 15:40 | Afternoon | Friday | 2019 | 10
12230 | 2019-10-25 15:40 | 2019-10-25 15:40 | 13.8KV CENTRAL DURI FEEDER #8 | Rain and Lightning | Unidentified | 904 | C.Duri fdr#8 T/R 1x Ctr:465-469 R/F:51@1@2. Not Patrolled yet. |  | 1 | 15:40 | Afternoon | Friday | 2019 | 10
12231 | 2019-10-25 15:40 | 2019-10-27 08:40 | 13.8KV CENTRAL DURI FEEDER #8 | Rain and Lightning | Unidentified | 904 | Patrolled the line but found nothing. Cause : Unidentified. |  | 1 | 15:40 | Afternoon | Friday | 2019 | 10
12232 | 2019-10-25 15:40 | 2019-10-25 15:40 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Corrosion | 5858 | 15:40 C.Duri ACB fdr#9 T/LO Ctr:401-404 R/F:51@1@3. Patrolled the line & found fall Down Pole at 04-00-12- 04-00-20. Isolated one Road with Opened LBS 04-00-01B and Recl 04-00-25. 16:46 Block & closed C.Duri ACB fdr#9, then release the block. 19:05 Cut and Isolate Jumper O/P 04.00.13, then Closed LBS 04.00.01B Cause: Broken Pole. - At Area 4 still well down : BOPD = 417 / 34 wells . due to fallen pole at road 4M80. |  | 1 | 15:40 | Afternoon | Friday | 2019 | 10
12233 | 2019-10-25 15:40 | 2019-10-27 10:15 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Corrosion | 5858 | 10:15 Manually Opened LBS 04-01-01. Installed Guy Line at Pole 04-00-13. (S/D 9Txs for 30 wells). 15:44 Manually Closed LBS 04-01-01. Cause: Corrosion (Plan Maintenance). |  | 1 | 15:40 | Afternoon | Friday | 2019 | 10
12234 | 2019-10-25 15:40 | 2019-09-11 16:09 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Corrosion | 5858 | 16:09 Manual Open LBS: 04-00-01A d/s: C. Duri feeder #9. Connected Conductor o/p: 04-00-12 to 04-00-13. 18:41 Closed LBS: 04-00-01A. Cause: Corrosive. |  | 1 | 15:40 | Afternoon | Friday | 2019 | 10
12235 | 2019-10-25 15:40 | 2019-10-11 09:25 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Corrosion | 5858 | 09:25 Blocked C. Duri feeder #9. To connected Jumper o/p: 04-00-13 to 04-00-16. 14:40 some wells (13 wells) have re run again after completed The JOB. There are wells: 4M-75B, 4M-69B, 4M-87A, 4M-87B, 4M-89B, 4M-76A- 4M-88C, 4M-69A, 4M-78A, 4M-85C, 4M-C12, 4M-76B- and 4M-75A. Cause:Corrosion. |  | 1 | 15:40 | Afternoon | Friday | 2019 | 10
12236 | 2019-10-25 15:40 | 2019-12-11 08:42 | 13.8KV CENTRAL DURI FEEDER #9 | Rain and Lightning | Corrosion | 5858 | 08:42 Manual Open 13.8KV ACB C. Duri feeder #8. Open By Pass of Recloser: 04-00-25. 08:45 Closed 13.8KV ACB C. Duri feeder #8. 13:11 Open LBS: 04-01-01A. Instaled Conductor o/p 04-00-20 to 04-00-21. 13:11 Closed LBS: 04-01-01A. (Load Road 04-00-xx defeed from C. Duri feeder #9). Cause: Plan Maintenance. |  | 1 | 15:40 | Afternoon | Friday | 2019 | 10
12237 | 2019-10-25 17:00 | 2019-10-25 17:00 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Unidentified | 0 | 17:00 It was reported no power at area 13-G71 (N.Duri fdr#2). Checked & found Recl. 13-G71-10 (Block Position). 17:45 Blocked & closed Recl. 13-G71-10. Not Patrolled yet. |  | 1 | 17:00 | Afternoon | Friday | 2019 | 10
12238 | 2019-10-25 17:00 | 2019-10-29 06:57 | 13.8KV NORTH DURI FEEDER #2 | Rain and Lightning | Unidentified | 0 | Checked and found: 5441-RCL T/O, Counter : 76 - 76, Relay Flag : NONE Patrolled the line found : Tidak ada temuan, Recloser 13 G7. 1.10 dalam keadaan Block Cause : Unidentified |  | 1 | 17:00 | Afternoon | Friday | 2019 | 10
12239 | 2019-10-25 17:26 | 2019-10-25 17:26 | 13.8KV BEKASAP FEEDER #2 | Rain and Lightning | Emergency | 0 | 17:26 Manually Opened Bekasap fdr#2. Maintain Tank level. 18:04 Blocked & closed Bekasap VCB fdr#2, then Release the block. Cause: Emergency. |  | 1 | 17:26 | Afternoon | Friday | 2019 | 10
12240 | 2019-10-25 17:53 | 2019-10-25 17:53 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Unidentified | 74 | 17:53 It was reported no Power at NBS. 18:55 Checked & foun Recl 4B-148 (block Position) D/S 4B fdr#6. 18:56 Blocked & closed Recl. 4B-148. Not patrolled yet. |  | 1 | 17:53 | Afternoon | Friday | 2019 | 10
12241 | 2019-10-25 17:53 | 2019-10-27 14:56 | 13.8KV 4B FEEDER #6 | Rain and Lightning | Unidentified | 74 | Checked & found Recloser 4B 148 T/O (In Block Position, Ctr: 85 - 85, R/F: None Patrolled the Line, but found nothing Cause : Unidentified |  | 1 | 17:53 | Afternoon | Friday | 2019 | 10
12242 | 2019-10-25 18:04 | 2019-10-25 18:04 | 13.8KV BEKASAP FEEDER #6 | Rain and Lightning | Emergency | - | 18:04 Manually Opened Bekasap fdr#6. maintaining the level in the tank. 21:06 Manually blocked & closed Bekasap feeder#6. and then release the block. Cause: Emergency. |  | 1 | 18:04 | Afternoon | Friday | 2019 | 10